## Intro
| PNNL | 2019-03-26 | PNNL Codes Team
This spreadsheet contains detailed end use data results from the Progress Indicator analysis
of ASHRAE Standard 90.1 conducted by PNNL.
The spreadsheet includes a list (DetPri tab) of all detailed ECIs by end use and prototype,
sorted by remaining use after 90.1-2016 and sorted by savings of 90.1-2016 vs. 90.1-2004.
Data includes detailed results for each of the prototypes at the detailed end use level. A tab
for each prototype includes a matrix of tables with a summary and detail for each climate
zone. In addition to ECI, both site and source energy use index (EUI) results are included as is
end use for gas and electric. Vertically, tables are included for:
US average summary results, based on construction weighting
Separate climate zone detail tables for energy cost and use after Standard 90.1 in 2004, 2007, 2010, 2013 and 2016
Percentage savings from Standard 90.1-2004 to 90.1-2016
End uses are from energy plus simulation of the prototype models, and are defined as follows:
| Simple Breakdown | Detailed Breakdown | End Use Description
| Light.int | Light.int | Interior Lighting
| Light.ext | Light.ext | Exterior Lighting
| SHW | SHW | Service Hot Water
| Heat | Heat | Space Heating
|  | Humidify | Humidification (Dehumidification in Heat and Cool)
| Cool | Cool | Mechanical Cooling (including unitary heat rejection)
|  | Ht.Rej | Heat rejection, cooling towers (unitary is in cool)
| Fan.Aux | Fans | HVAC supply, return and exhaust fans
|  | Ht.Rcvy | Heat recovery fan and wheel energy
|  | Pumps | Hydronic pumping, including SHW recirculation
| Misc | Refrig | Refrigeration equipment and kitchen refrigerators and freezers
|  | Elevator | Elevators
|  | Txfmr | In-building transformers
| Equip | Cook | Cooking and Laundry Equipment
|  | IT | Computer room IT equipment and telephone equipment
|  | Equip | Other plug loads and equipment
The 16 building prototypes are listed below and further detail and description can be found at:
http://www.energycodes.gov/commercial-prototype-building-models
Related analysis results can be found here:
http://www.energycodes.gov/development/commercial/
(Rounded)
|  |  |  | TSD | E+
|  |  |  | Floor area | Floor area
|  | Tab | Building Prototype | (ft²) | (ft²)
|  | OffS | Small Office | 5500 | 5502
|  | OffM | Medium Office | 53630 | 53628
|  | OffL | Large Office | 498640 | 498588
|  | RtlStA | Standalone Retail | 24690 | 24692
|  | RtlMall | Strip Mall | 22500 | 22500
|  | SchPri | Primary School | 73970 | 73959
|  | SchSec | Secondary School | 210910 | 210887
|  | MedOP | Outpatient Healthcare | 40950 | 40946
|  | MedHos | Hospital | 241410 | 241501
|  | HotSml | Small Hotel | 43210 | 43202
|  | HotLrg | Large Hotel | 122120 | 122120
|  | Whse | Warehouse | 52050 | 52045
|  | RestQS | Quick-service Restaurant | 2500 | 2501
|  | RestFS | Full-service Restaurant | 5500 | 5502
|  | AptMR | Mid-rise Apartment | 33740 | 33741
|  | AptHR | High-rise Apartment | 84360 | 84352

## DetPri
Priority sort by remaining ECI (after 90.1-2016) by end use and Prototype |  |  |  |  | Priority sort by past cost savings (90.1-2016 vs. 90.1-2004) by end use and Prototype
Prototype | End Use | ECI | Bar - Remaining ECI |  | Prototype | End Use | ECI Savings | Bar - unsaved
Fast Food | Cook | 4.435 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++++ | Lg Office | Humidfy | -1062%
Restaurant | Cook | 2.9421 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++ | Fast Food | SHW | -0.05656% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Heat | 1.323 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Restaurant | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Refrig | 0.96082 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Lg Hotel | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | SHW | 0.91773 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Md Office | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Clinic | Equip | 0.86149 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Lg Office | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Lg Office | IT | 0.84214 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Sm Hotel | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | Heat | 0.81467 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Hospital | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Cool | 0.74461 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Lg Hotel | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Fans | 0.72968 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Pri School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | SHW | 0.67183 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Sec School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Equip | 0.63669 | XXXXXXXXXXXXXXXXXXXXXXXXX |  | Hi Apartment | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | Cool | 0.61795 | XXXXXXXXXXXXXXXXXXXXXXXX |  | Mid Apartment | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Light.Int | 0.56389 | XXXXXXXXXXXXXXXXXXXXXX |  | Hospital | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | Fans | 0.51877 | XXXXXXXXXXXXXXXXXXXX |  | Retail Store | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Clinic | Cool | 0.50061 | XXXXXXXXXXXXXXXXXXXX |  | Lg Office | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Clinic | Elevator | 0.43932 | XXXXXXXXXXXXXXXXX |  | Md Office | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | Refrig | 0.42917 | XXXXXXXXXXXXXXXXX |  | Fast Food | Cook | 0.07352% | XXXXXXXXXXXXXXXXXXX
Hospital | Light.Int | 0.39609 | XXXXXXXXXXXXXXX |  | Restaurant | Cook | 0.09725% | XXXXXXXXXXXXXXXXXXX
Pri School | Equip | 0.36051 | XXXXXXXXXXXXXX |  | Mid Apartment | SHW | 0.1373% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Cool | 0.35556 | XXXXXXXXXXXXXX |  | Sec School | SHW | 0.1553% | XXXXXXXXXXXXXXXXXXX
Retail Store | Light.Int | 0.3411 | XXXXXXXXXXXXX |  | Sm Office | SHW | 0.167% | XXXXXXXXXXXXXXXXXXX
Hospital | Fans | 0.33976 | XXXXXXXXXXXXX |  | Hi Apartment | Equip | 0.2001% | XXXXXXXXXXXXXXXXXXX
Hi Apartment | Equip | 0.32437 | XXXXXXXXXXXX |  | Sm Hotel | SHW | 0.3374% | XXXXXXXXXXXXXXXXXXX
Mid Apartment | Equip | 0.32202 | XXXXXXXXXXXX |  | Hi Apartment | SHW | 0.3552% | XXXXXXXXXXXXXXXXXXX
Clinic | Light.Int | 0.3173 | XXXXXXXXXXXX |  | Retail Store | Equip | 0.4407% | XXXXXXXXXXXXXXXXXXX
Mid Apartment | SHW | 0.3129 | XXXXXXXXXXXX |  | Strip Mall | Equip | 0.4428% | XXXXXXXXXXXXXXXXXXX
Fast Food | Light.Int | 0.31021 | XXXXXXXXXXXX |  | Mid Apartment | Equip | 0.5025% | XXXXXXXXXXXXXXXXXXX
Md Office | Equip | 0.30678 | XXXXXXXXXXXX |  | Clinic | Equip | 0.9059% | XXXXXXXXXXXXXXXXXXX
Clinic | Heat | 0.30504 | XXXXXXXXXXXX |  | Restaurant | SHW | 1.121% | XXXXXXXXXXXXXXXXXXX
Lg Office | Equip | 0.30109 | XXXXXXXXXXXX |  | Hospital | Elevator | 1.297% | XXXXXXXXXXXXXXXXXXX
Hospital | Elevator | 0.29215 | XXXXXXXXXXX |  | Lg Hotel | SHW | 1.489% | XXXXXXXXXXXXXXXXXXX
Hospital | Heat | 0.29008 | XXXXXXXXXXX |  | Clinic | Elevator | 1.955% | XXXXXXXXXXXXXXXXXXX
Hospital | Cool | 0.28568 | XXXXXXXXXXX |  | Warehouse | Equip | 1.996% | XXXXXXXXXXXXXXXXXXX
Restaurant | Light.Int | 0.2851 | XXXXXXXXXXX |  | Retail Store | SHW | 2.148% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Cook | 0.27391 | XXXXXXXXXX |  | Fast Food | Heat | 2.741% | XXXXXXXXXXXXXXXXXXX
Hospital | Cook | 0.27223 | XXXXXXXXXX |  | Hi Apartment | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Sec School | Equip | 0.25606 | XXXXXXXXXX |  | Lg Office | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Sm Office | Equip | 0.24697 | XXXXXXXXX |  | Sm Hotel | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Clinic | Fans | 0.24582 | XXXXXXXXX |  | Hospital | Equip | 3.09% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Equip | 0.24162 | XXXXXXXXX |  | Warehouse | SHW | 3.192% | XXXXXXXXXXXXXXXXXXX
Retail Store | Equip | 0.22142 | XXXXXXXX |  | Lg Office | SHW | 3.234% | XXXXXXXXXXXXXXXXXXX
Lg Office | Cool | 0.22074 | XXXXXXXX |  | Mid Apartment | Elevator | 3.565% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Elevator | 0.219 | XXXXXXXX |  | Lg Hotel | Elevator | 3.566% | XXXXXXXXXXXXXXXXXXX
Retail Store | Fans | 0.1989 | XXXXXXX |  | Pri School | SHW | 3.8% | XXXXXXXXXXXXXXXXXXX
Sec School | Cool | 0.19639 | XXXXXXX |  | Md Office | SHW | 3.948% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Light.Int | 0.19079 | XXXXXXX |  | Hospital | SHW | 4.039% | XXXXXXXXXXXXXXXXXXX
Hi Apartment | Cool | 0.18918 | XXXXXXX |  | Md Office | Elevator | 5.47% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Light.Int | 0.18905 | XXXXXXX |  | Sm Hotel | Fans | 6.717% | XXXXXXXXXXXXXXXXXX
Strip Mall | Fans | 0.18464 | XXXXXXX |  | Sm Hotel | Equip | 7.647% | XXXXXXXXXXXXXXXXXX
Strip Mall | Cool | 0.18419 | XXXXXXX |  | Strip Mall | SHW | 8.31% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Equip | 0.18191 | XXXXXXX |  | Sm Office | Equip | 8.542% | XXXXXXXXXXXXXXXXXX
Sm Hotel | SHW | 0.18143 | XXXXXXX |  | Md Office | Equip | 8.826% | XXXXXXXXXXXXXXXXXX
Pri School | Cool | 0.18036 | XXXXXXX |  | Lg Office | Equip | 9.145% | XXXXXXXXXXXXXXXXXX
Lg Office | Light.Int | 0.17877 | XXXXXXX |  | Sec School | Equip | 9.58% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Cool | 0.17781 | XXXXXXX |  | Lg Hotel | Equip | 11.14% | XXXXXXXXXXXXXXXXX
Hi Apartment | Fans | 0.17245 | XXXXXX |  | Clinic | SHW | 11.9% | XXXXXXXXXXXXXXXXX
Sm Office | Light.Int | 0.16929 | XXXXXX |  | Lg Office | Fans | 12.89% | XXXXXXXXXXXXXXXXX
Retail Store | Cool | 0.16335 | XXXXXX |  | Sec School | Elevator | 13.14% | XXXXXXXXXXXXXXXXX
Md Office | Cool | 0.16323 | XXXXXX |  | Pri School | Equip | 13.6% | XXXXXXXXXXXXXXXXX
Lg Hotel | Elevator | 0.16277 | XXXXXX |  | Sec School | Refrig | 15.71% | XXXXXXXXXXXXXXXX
Mid Apartment | Fans | 0.16073 | XXXXXX |  | Pri School | Pumps | 18.14% | XXXXXXXXXXXXXXXX
Strip Mall | Equip | 0.16027 | XXXXXX |  | Hospital | Light.Int | 18.73% | XXXXXXXXXXXXXXXX
Md Office | Light.Int | 0.15895 | XXXXXX |  | Sm Hotel | Refrig | 19.38% | XXXXXXXXXXXXXXXX
Sm Hotel | Fans | 0.14446 | XXXXX |  | Pri School | Refrig | 19.84% | XXXXXXXXXXXXXXXX
Pri School | Light.Int | 0.13781 | XXXXX |  | Hi Apartment | Fans | 20.19% | XXXXXXXXXXXXXXX
Lg Office | Fans | 0.13258 | XXXXX |  | Mid Apartment | Fans | 20.22% | XXXXXXXXXXXXXXX
Sec School | Light.Int | 0.12815 | XXXXX |  | Fast Food | Refrig | 21.13% | XXXXXXXXXXXXXXX
Lg Hotel | SHW | 0.12811 | XXXXX |  | Hospital | Refrig | 21.91% | XXXXXXXXXXXXXXX
Mid Apartment | Cool | 0.12212 | XXXX |  | Restaurant | Refrig | 22.32% | XXXXXXXXXXXXXXX
Lg Hotel | Fans | 0.11817 | XXXX |  | Restaurant | Heat | 22.77% | XXXXXXXXXXXXXXX
Hi Apartment | SHW | 0.11539 | XXXX |  | Hi Apartment | Light.Int | 23.62% | XXXXXXXXXXXXXXX
Clinic | Humidfy | 0.1145 | XXXX |  | Clinic | Humidfy | 23.95% | XXXXXXXXXXXXXXX
Lg Hotel | Cook | 0.11102 | XXXX |  | Clinic | Light.Int | 24.47% | XXXXXXXXXXXXXXX
Lg Office | Elevator | 0.10728 | XXXX |  | Hi Apartment | Cool | 24.74% | XXXXXXXXXXXXXXX
Mid Apartment | Elevator | 0.10421 | XXXX |  | Sm Office | Fans | 26.32% | XXXXXXXXXXXXXX
Pri School | Cook | 0.10323 | XXXX |  | Mid Apartment | Light.Int | 26.5% | XXXXXXXXXXXXXX
Strip Mall | Heat | 0.10145 | XXXX |  | Clinic | Pumps | 27.88% | XXXXXXXXXXXXXX
Warehouse | Light.Int | 0.1 | XXXX |  | Strip Mall | Light.Int | 28.66% | XXXXXXXXXXXXXX
Sm Office | Fans | 0.099614 | XXX |  | Sm Hotel | Cool | 30.8% | XXXXXXXXXXXXX
Fast Food | Light.Ext | 0.098927 | XXX |  | Md Office | Fans | 30.92% | XXXXXXXXXXXXX
Sec School | Fans | 0.095701 | XXX |  | Clinic | Cool | 30.96% | XXXXXXXXXXXXX
Restaurant | Light.Ext | 0.09532 | XXX |  | Lg Office | Cool | 31.62% | XXXXXXXXXXXXX
Sm Office | Cool | 0.094484 | XXX |  | Fast Food | Cool | 32.09% | XXXXXXXXXXXXX
Mid Apartment | Light.Int | 0.092829 | XXX |  | Hospital | Fans | 34.59% | XXXXXXXXXXXXX
Sm Office | SHW | 0.092109 | XXX |  | Hi Apartment | Pumps | 35% | XXXXXXXXXXXXX
Hi Apartment | Light.Int | 0.09162 | XXX |  | Md Office | Cool | 36.1% | XXXXXXXXXXXX
Pri School | Fans | 0.090009 | XXX |  | Lg Hotel | Cool | 36.5% | XXXXXXXXXXXX
Md Office | Elevator | 0.086781 | XXX |  | Mid Apartment | Cool | 36.83% | XXXXXXXXXXXX
Md Office | Heat | 0.080397 | XXX |  | Clinic | Fans | 36.9% | XXXXXXXXXXXX
Strip Mall | SHW | 0.078107 | XXX |  | Restaurant | Cool | 37.08% | XXXXXXXXXXXX
Hospital | Humidfy | 0.077457 | XXX |  | Pri School | Fans | 37.13% | XXXXXXXXXXXX
Lg Office | Humidfy | 0.075709 | XXX |  | Sm Hotel | Ht.Rcvy | 38.23% | XXXXXXXXXXXX
Lg Hotel | Heat | 0.074891 | XX |  | Lg Office | Light.Int | 38.36% | XXXXXXXXXXXX
Warehouse | Equip | 0.073801 | XX |  | Warehouse | Heat | 38.48% | XXXXXXXXXXXX
Sec School | Cook | 0.072419 | XX |  | Hospital | Cool | 38.82% | XXXXXXXXXXXX
Sm Hotel | Heat | 0.069016 | XX |  | Retail Store | Light.Int | 39.17% | XXXXXXXXXXXX
Strip Mall | Light.Ext | 0.068758 | XX |  | Sm Hotel | Light.Ext | 40.28% | XXXXXXXXXXX
Warehouse | Heat | 0.065002 | XX |  | Hospital | Light.Ext | 40.71% | XXXXXXXXXXX
Pri School | Heat | 0.064724 | XX |  | Strip Mall | Heat | 40.94% | XXXXXXXXXXX
Hospital | Pumps | 0.056989 | XX |  | Lg Hotel | Light.Int | 41.71% | XXXXXXXXXXX
Hi Apartment | Elevator | 0.052844 | XX |  | Sm Office | Heat | 41.83% | XXXXXXXXXXX
Clinic | SHW | 0.050432 | XX |  | Sm Hotel | Light.Int | 42.99% | XXXXXXXXXXX
Retail Store | Heat | 0.050328 | XX |  | Lg Hotel | Fans | 43.98% | XXXXXXXXXXX
Hospital | SHW | 0.050157 | XX |  | Hi Apartment | Light.Ext | 44.74% | XXXXXXXXXXX
Sm Hotel | Ht.Rcvy | 0.047113 | X |  | Md Office | Light.Int | 45.2% | XXXXXXXXXX
Sec School | Heat | 0.04409 | X |  | Pri School | Cool | 45.62% | XXXXXXXXXX
Retail Store | Light.Ext | 0.043922 | X |  | Pri School | Ht.Rcvy | 45.71% | XXXXXXXXXX
Md Office | Fans | 0.042516 | X |  | Warehouse | Cool | 46.27% | XXXXXXXXXX
Sm Hotel | Light.Ext | 0.042116 | X |  | Strip Mall | Fans | 47.73% | XXXXXXXXXX
Sec School | SHW | 0.04202 | X |  | Hospital | Heat | 48.12% | XXXXXXXXXX
Hi Apartment | Heat | 0.041876 | X |  | Fast Food | Fans | 48.41% | XXXXXXXXXX
Pri School | Refrig | 0.041532 | X |  | Strip Mall | Cool | 49.29% | XXXXXXXXXX
Hi Apartment | Light.Ext | 0.03934 | X |  | Retail Store | Cool | 50.39% | XXXXXXXXX
Clinic | Light.Ext | 0.037575 | X |  | Warehouse | Fans | 50.58% | XXXXXXXXX
Retail Store | SHW | 0.035632 | X |  | Sec School | Cool | 51.75% | XXXXXXXXX
Lg Office | Heat | 0.031105 | X |  | Sm Office | Cool | 52.39% | XXXXXXXXX
Warehouse | Light.Ext | 0.03073 | X |  | Sm Office | Light.Int | 53.35% | XXXXXXXXX
Mid Apartment | Heat | 0.029273 | X |  | Lg Hotel | Light.Ext | 53.49% | XXXXXXXXX
Sm Office | Heat | 0.029255 | X |  | Warehouse | Light.Ext | 53.96% | XXXXXXXXX
Sm Office | Light.Ext | 0.029161 | X |  | Retail Store | Fans | 54.39% | XXXXXXXXX
Hospital | Ht.Rej | 0.028979 | X |  | Sec School | Fans | 55.38% | XXXXXXXX
Lg Hotel | Light.Ext | 0.028854 | X |  | Hospital | Pumps | 55.38% | XXXXXXXX
Pri School | Ht.Rcvy | 0.027835 | X |  | Md Office | Heat | 55.54% | XXXXXXXX
Hi Apartment | Ht.Rcvy | 0.024658 |  |  | Hospital | Txfmr | 59.05% | XXXXXXXX
Md Office | Light.Ext | 0.0246 |  |  | Sec School | Heat | 59.14% | XXXXXXXX
Pri School | SHW | 0.02443 |  |  | Pri School | Heat | 59.33% | XXXXXXXX
Hospital | Refrig | 0.024318 |  |  | Hi Apartment | Txfmr | 59.98% | XXXXXXXX
Sec School | Ht.Rcvy | 0.024194 |  |  | Lg Office | Pumps | 60.43% | XXXXXXX
Lg Office | Pumps | 0.023974 |  |  | Hi Apartment | Ht.Rej | 60.95% | XXXXXXX
Sec School | Refrig | 0.02377 |  |  | Hospital | Ht.Rej | 61.35% | XXXXXXX
Mid Apartment | Ht.Rcvy | 0.023109 |  |  | Clinic | Heat | 61.52% | XXXXXXX
Mid Apartment | Light.Ext | 0.021634 |  |  | Warehouse | Light.Int | 61.62% | XXXXXXX
Hospital | Ht.Rcvy | 0.021383 |  |  | Lg Office | Ht.Rej | 61.7% | XXXXXXX
Sm Hotel | Refrig | 0.019529 |  |  | Lg Office | Txfmr | 61.77% | XXXXXXX
Lg Office | Light.Ext | 0.019414 |  |  | Sm Hotel | Txfmr | 61.9% | XXXXXXX
Lg Office | Ht.Rej | 0.018842 |  |  | Restaurant | Fans | 62.26% | XXXXXXX
Hospital | Light.Ext | 0.018054 |  |  | Sec School | Txfmr | 62.59% | XXXXXXX
Retail Store | Ht.Rcvy | 0.01756 |  |  | Hospital | Humidfy | 62.74% | XXXXXXX
Warehouse | Fans | 0.016801 |  |  | Fast Food | Light.Int | 63.28% | XXXXXXX
Hi Apartment | Pumps | 0.015573 |  |  | Pri School | Txfmr | 63.92% | XXXXXXX
Sm Hotel | Pumps | 0.014285 |  |  | Lg Hotel | Heat | 64.25% | XXXXXXX
Md Office | SHW | 0.014181 |  |  | Mid Apartment | Light.Ext | 64.43% | XXXXXXX
Warehouse | SHW | 0.013415 |  |  | Lg Office | Light.Ext | 65.13% | XXXXXX
Warehouse | Cool | 0.010542 |  |  | Md Office | Txfmr | 65.15% | XXXXXX
Lg Office | SHW | 0.010437 |  |  | Mid Apartment | Heat | 65.16% | XXXXXX
Pri School | Light.Ext | 0.0097508 |  |  | Lg Office | Heat | 65.92% | XXXXXX
Sec School | Light.Ext | 0.0090796 |  |  | Retail Store | Light.Ext | 66.5% | XXXXXX
Sec School | Elevator | 0.0087798 |  |  | Hi Apartment | Heat | 66.58% | XXXXXX
Hospital | Txfmr | 0.0082805 |  |  | Sec School | Ht.Rcvy | 66.96% | XXXXXX
Pri School | Txfmr | 0.006592 |  |  | Strip Mall | Light.Ext | 67.35% | XXXXXX
Md Office | Txfmr | 0.006172 |  |  | Fast Food | Light.Ext | 67.89% | XXXXXX
Sm Hotel | Txfmr | 0.0050268 |  |  | Restaurant | Light.Ext | 67.9% | XXXXXX
Hi Apartment | Txfmr | 0.0048288 |  |  | Sec School | Light.Ext | 68.61% | XXXXXX
Hi Apartment | Ht.Rej | 0.0046632 |  |  | Pri School | Light.Ext | 69.21% | XXXXXX
Sec School | Pumps | 0.0042554 |  |  | Restaurant | Light.Int | 69.97% | XXXXXX
Sec School | Txfmr | 0.0039621 |  |  | Pri School | Light.Int | 70.07% | XXXXX
Lg Office | Txfmr | 0.0031026 |  |  | Sm Hotel | Heat | 70.31% | XXXXX
Restaurant | Pumps | 0.0023014 |  |  | Sec School | Light.Int | 70.85% | New Use not required in 2004
Clinic | Pumps | 0.0016858 |  |  | Retail Store | Heat | 71.2% | New Use not required in 2004
Lg Office | Ht.Rcvy | 0.0014499 |  |  | Sm Hotel | Pumps | 73.11% | New Use not required in 2004
Pri School | Pumps | 0.0007941 |  |  | Clinic | Light.Ext | 75.9% | New Use not required in 2004
Md Office | Ht.Rcvy | 0.00036446 |  |  | Sm Office | Light.Ext | 77.07% | New Use not required in 2004
#REF!
#REF!

## National
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | US All Buildings |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [8 empty] | Building Type: | US All Buildings |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [8 empty] | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | US All Buildings |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [15 empty] | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2016 | 0.20487 | 0.032098 | 0.082418 | 0.086705 | 0.010194 | 0.17573 | 0.0020442 | 0.13717 | 0.013618 | 0.0054434 | 0.01481 | 0.065012 | 0.0021835 | 0.082941 | 0.02802 | 0.26951 | 1.2128 |  | STD2016 | 6.9023 | 1.0814 | 5.5195 | 7.5094 | 0.34346 | 5.9207 | 0.068874 | 4.6216 | 0.45882 | 0.1834 | 0.49896 | 2.1904 | 0.073567 | 4.985 | 0.94403 | 9.2066 | 50.5079 |  | STD2016 | 2.0224 | 0.31686 | 0.40527 | 0.17286 | 0.10063 | 1.7348 | 0.02018 | 1.3541 | 0.13444 | 0.053735 | 0.1462 | 0.64178 | 0.021555 | 0.49265 | 0.2766 | 2.6417 | 10.5357 |  | STD2016 | 0 | 0 | 0.041364 | 0.069194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.1455 |  | STD2016 | 21.1722 | 3.3172 | 8.7638 | 9.3726 | 1.0535 | 18.1613 | 0.21127 | 14.1763 | 1.4074 | 0.56256 | 1.5305 | 6.7188 | 0.22566 | 8.7684 | 2.8957 | 27.8641 | 126.2013
STD2013 | 0.2667 | 0.052393 | 0.082826 | 0.090102 | 0.00704 | 0.18827 | 0.0025229 | 0.14567 | 0.014718 | 0.0061976 | 0.014813 | 0.065012 | 0.0031081 | 0.082941 | 0.02802 | 0.26951 | 1.3198 |  | STD2013 | 8.9854 | 1.7652 | 5.5607 | 7.7594 | 0.23719 | 6.3432 | 0.085002 | 4.9079 | 0.49588 | 0.20881 | 0.49909 | 2.1904 | 0.10472 | 4.985 | 0.94403 | 9.2066 | 54.2784 |  | STD2013 | 2.6327 | 0.51721 | 0.40522 | 0.18623 | 0.069497 | 1.8586 | 0.024905 | 1.438 | 0.14529 | 0.06118 | 0.14623 | 0.64178 | 0.030683 | 0.49265 | 0.2766 | 2.6417 | 11.5685 |  | STD2013 | 0 | 0 | 0.041777 | 0.071238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.14796 |  | STD2013 | 27.562 | 5.4147 | 8.8085 | 9.7359 | 0.72756 | 19.4573 | 0.26074 | 15.0547 | 1.5211 | 0.6405 | 1.5309 | 6.7188 | 0.32122 | 8.7684 | 2.8957 | 27.8641 | 137.2819
STD2010 | 0.30641 | 0.052393 | 0.082857 | 0.10657 | 0.010767 | 0.22222 | 0.0030755 | 0.17268 | 0.010491 | 0.0070674 | 0.018519 | 0.065172 | 0.0032462 | 0.082947 | 0.02802 | 0.27686 | 1.4493 |  | STD2010 | 10.3236 | 1.7652 | 5.5618 | 8.9541 | 0.36276 | 7.4871 | 0.10362 | 5.8178 | 0.35344 | 0.23811 | 0.62395 | 2.1958 | 0.10937 | 4.9851 | 0.94403 | 9.4543 | 59.2801 |  | STD2010 | 3.0248 | 0.51721 | 0.40552 | 0.25349 | 0.10629 | 2.1937 | 0.03036 | 1.7046 | 0.10356 | 0.069767 | 0.18282 | 0.64336 | 0.032046 | 0.49271 | 0.2766 | 2.7143 | 12.7511 |  | STD2010 | 0 | 0 | 0.041778 | 0.080889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.15761 |  | STD2010 | 31.6667 | 5.4147 | 8.8117 | 11.495 | 1.1127 | 22.9661 | 0.31784 | 17.8456 | 1.0842 | 0.73039 | 1.9139 | 6.7353 | 0.33549 | 8.7689 | 2.8957 | 28.6241 | 150.7182
STD2007 | 0.38202 | 0.09083 | 0.083689 | 0.1569 | 0.012779 | 0.29238 | 0.0052704 | 0.2198 | 0.0070367 | 0.013361 | 0.018539 | 0.066913 | 0.005783 | 0.082979 | 0.02802 | 0.2823 | 1.7486 |  | STD2007 | 12.871 | 3.0602 | 5.6032 | 13.0557 | 0.43054 | 9.8509 | 0.17757 | 7.4055 | 0.23708 | 0.45016 | 0.6246 | 2.2544 | 0.19484 | 4.9862 | 0.94403 | 9.6374 | 71.7834 |  | STD2007 | 3.7712 | 0.89665 | 0.41174 | 0.39222 | 0.12615 | 2.8863 | 0.052028 | 2.1698 | 0.069464 | 0.1319 | 0.18301 | 0.66054 | 0.057088 | 0.49303 | 0.2766 | 2.7679 | 15.3457 |  | STD2007 | 0 | 0 | 0.04198 | 0.11717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.19409 |  | STD2007 | 39.4808 | 9.387 | 8.8989 | 16.9129 | 1.3206 | 30.2169 | 0.54468 | 22.7158 | 0.72722 | 1.3808 | 1.9159 | 6.9152 | 0.59766 | 8.7723 | 2.8957 | 29.1857 | 181.868
STD2004 | 0.37853 | 0.09083 | 0.083692 | 0.19134 | 0.013965 | 0.3182 | 0.0052926 | 0.24995 | 0.013922 | 0.013889 | 0.018573 | 0.066913 | 0.005783 | 0.082979 | 0.02802 | 0.2823 | 1.8442 |  | STD2004 | 12.7534 | 3.0602 | 5.6031 | 15.9095 | 0.47051 | 10.7208 | 0.17832 | 8.4212 | 0.46907 | 0.46793 | 0.62577 | 2.2544 | 0.19484 | 4.9862 | 0.94403 | 9.6374 | 76.6968 |  | STD2004 | 3.7367 | 0.89665 | 0.4118 | 0.48004 | 0.13786 | 3.1412 | 0.052247 | 2.4674 | 0.13744 | 0.1371 | 0.18335 | 0.66054 | 0.057088 | 0.49303 | 0.2766 | 2.7679 | 16.037 |  | STD2004 | 0 | 0 | 0.041976 | 0.14271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.21963 |  | STD2004 | 39.12 | 9.387 | 8.8991 | 20.624 | 1.4433 | 32.885 | 0.54697 | 25.8315 | 1.4388 | 1.4353 | 1.9195 | 6.9152 | 0.59766 | 8.7723 | 2.8957 | 29.1857 | 191.8971
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | -0.0034905 | 0 | 2.9407e-06 | 0.034438 | 0.0011864 | 0.025818 | 2.2188e-05 | 0.030148 | 0.0068856 | 0.00052738 | 3.4743e-05 | 0 | -1.1199e-08 | 0 | 0 | 0 | 0.095572 |  | 2004-2007 | -0.1176 | 0 | -0.0001316 | 2.8539 | 0.039972 | 0.86984 | 0.00074755 | 1.0157 | 0.23199 | 0.017768 | 0.0011706 | 0 | -3.7731e-07 | 0 | 0 | 0 | 4.9134 |  | 2004-2007 | -0.034457 | 0 | 6.3372e-05 | 0.087819 | 0.011712 | 0.25486 | 0.00021903 | 0.29761 | 0.067973 | 0.0052061 | 0.00034297 | 0 | -1.1055e-07 | 0 | 0 | 0 | 0.69135 |  | 2004-2007 | 0 | 0 | -3.4789e-06 | 0.025542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025538 |  | 2004-2007 | -0.36073 | 0 | 0.0002832 | 3.7111 | 0.12261 | 2.6682 | 0.0022931 | 3.1157 | 0.71161 | 0.054502 | 0.0035906 | 0 | -1.1574e-06 | 0 | 0 | 0 | 10.0291
2007-2010 | 0.07561 | 0.038437 | 0.00083194 | 0.050334 | 0.0020116 | 0.07016 | 0.0021949 | 0.047125 | -0.0034538 | 0.0062938 | 1.923e-05 | 0.0017407 | 0.0025368 | 3.2635e-05 | 0 | 0.0054344 | 0.29931 |  | 2007-2010 | 2.5474 | 1.295 | 0.041414 | 4.1016 | 0.067775 | 2.3638 | 0.073951 | 1.5877 | -0.11636 | 0.21205 | 0.00064789 | 0.058649 | 0.085469 | 0.0010995 | 0 | 0.1831 | 12.5034 |  | 2007-2010 | 0.7464 | 0.37944 | 0.0062199 | 0.13873 | 0.019858 | 0.6926 | 0.021668 | 0.4652 | -0.034095 | 0.062131 | 0.00018983 | 0.017184 | 0.025042 | 0.00032216 | 0 | 0.053647 | 2.5945 |  | 2007-2010 | 0 | 0 | 0.00020186 | 0.036281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036483 |  | 2007-2010 | 7.8141 | 3.9723 | 0.08718 | 5.4179 | 0.20789 | 7.2508 | 0.22684 | 4.8702 | -0.35694 | 0.65045 | 0.0019874 | 0.1799 | 0.26217 | 0.0033727 | 0 | 0.56163 | 31.1498
2010-2013 | 0.039718 | 0 | 3.1023e-05 | 0.016465 | 0.0037272 | 0.033952 | 0.00055254 | 0.027005 | -0.0042278 | 0.00086983 | 0.003706 | 0.00015989 | 0.0001381 | 5.3986e-06 | 0 | 0.0073535 | 0.12946 |  | 2010-2013 | 1.3382 | 0 | 0.0011046 | 1.1947 | 0.12557 | 1.1439 | 0.018616 | 0.90986 | -0.14244 | 0.029306 | 0.12486 | 0.0053869 | 0.0046529 | 0.00018189 | 0 | 0.24775 | 5.0016 |  | 2010-2013 | 0.39208 | 0 | 0.0002974 | 0.067263 | 0.036793 | 0.33516 | 0.0054545 | 0.26659 | -0.041735 | 0.0085866 | 0.036585 | 0.0015784 | 0.0013633 | 5.3293e-05 | 0 | 0.072591 | 1.1827 |  | 2010-2013 | 0 | 0 | 8.962e-07 | 0.0096516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096525 |  | 2010-2013 | 4.1047 | 0 | 0.0032114 | 1.7591 | 0.38519 | 3.5088 | 0.057103 | 2.7909 | -0.43692 | 0.089894 | 0.383 | 0.016524 | 0.014272 | 0.00055792 | 0 | 0.75996 | 13.4363
2013-2016 | 0.061829 | 0.020295 | 0.00040807 | 0.0033975 | -0.0031541 | 0.01254 | 0.00047868 | 0.0084993 | 0.0011 | 0.00075418 | 3.8844e-06 | 0 | 0.0009246 | 0 | 0 | 0 | 0.10708 |  | 2013-2016 | 2.0831 | 0.68378 | 0.04115 | 0.24995 | -0.10627 | 0.4225 | 0.016128 | 0.28636 | 0.03706 | 0.02541 | 0.00013087 | 0 | 0.031151 | 0 | 0 | 0 | 3.7705 |  | 2013-2016 | 0.61036 | 0.20035 | -5.115e-05 | 0.013369 | -0.031136 | 0.12379 | 0.0047254 | 0.083903 | 0.010859 | 0.007445 | 3.8345e-05 | 0 | 0.0091274 | 0 | 0 | 0 | 1.0328 |  | 2013-2016 | 0 | 0 | 0.00041325 | 0.0020433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024565 |  | 2013-2016 | 6.3899 | 2.0975 | 0.044633 | 0.36329 | -0.32596 | 1.296 | 0.04947 | 0.87838 | 0.11368 | 0.077942 | 0.00040144 | 0 | 0.095554 | 0 | 0 | 0 | 11.0807
2004-2016 | 0.17367 | 0.058733 | 0.001274 | 0.10464 | 0.0037711 | 0.14247 | 0.0032483 | 0.11278 | 0.00030403 | 0.0084452 | 0.0037639 | 0.0019006 | 0.0035995 | 3.8034e-05 | 0 | 0.012788 | 0.63141 |  | 2004-2016 | 5.8511 | 1.9788 | 0.083538 | 8.4001 | 0.12706 | 4.8 | 0.10944 | 3.7997 | 0.010243 | 0.28453 | 0.12681 | 0.064036 | 0.12127 | 0.0012814 | 0 | 0.43085 | 26.1889 |  | 2004-2013 | 1.7144 | 0.57979 | 0.0065296 | 0.30718 | 0.037227 | 1.4064 | 0.032067 | 1.1133 | 0.0030013 | 0.083369 | 0.037156 | 0.018762 | 0.035533 | 0.00037546 | 0 | 0.12624 | 5.5013 |  | 2004-2016 | 0 | 0 | 0.00061252 | 0.073517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07413 |  | 2004-2016 | 17.9479 | 6.0698 | 0.13531 | 11.2514 | 0.38973 | 14.7237 | 0.33571 | 11.6552 | 0.031421 | 0.87278 | 0.38898 | 0.19642 | 0.37199 | 0.0039307 | 0 | 1.3216 | 65.6958
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | -0.9221% | 0% | 0.003514% | 18% | 8.496% | 8.114% | 0.4192% | 12.06% | 49.46% | 3.797% | 0.1871% | 0% | -0.0001937% | 0% | 0% | 0% | 5.182% |  | 2004-2007 | -0.9221% | 0% | -0.002349% | 17.94% | 8.496% | 8.114% | 0.4192% | 12.06% | 49.46% | 3.797% | 0.1871% | 0% | -0.0001937% | 0% | 0% | 0% | 6.406% |  | 2004-2007 | -0.9221% | 0% | 0.01539% | 18.29% | 8.496% | 8.114% | 0.4192% | 12.06% | 49.46% | 3.797% | 0.1871% | 0% | -0.0001937% | 0% | 0% | 0% | 4.311% |  | 2004-2007 |  |  | -0.008288% | 17.9% | [9 empty] | 0% |  | 0% | 11.63% |  | 2004-2007 | -0.9221% | 0% | 0.003182% | 17.99% | 8.496% | 8.114% | 0.4192% | 12.06% | 49.46% | 3.797% | 0.1871% | 0% | -0.0001937% | 0% | 0% | 0% | 5.226%
2007-2010 | 19.79% | 42.32% | 0.9941% | 32.08% | 15.74% | 24% | 41.65% | 21.44% | -49.08% | 47.11% | 0.1037% | 2.602% | 43.87% | 0.03933% | 0% | 1.925% | 17.12% |  | 2007-2010 | 19.79% | 42.32% | 0.7391% | 31.42% | 15.74% | 24% | 41.65% | 21.44% | -49.08% | 47.11% | 0.1037% | 2.602% | 43.87% | 0.02205% | 0% | 1.9% | 17.42% |  | 2007-2010 | 19.79% | 42.32% | 1.511% | 35.37% | 15.74% | 24% | 41.65% | 21.44% | -49.08% | 47.11% | 0.1037% | 2.602% | 43.87% | 0.06534% | 0% | 1.938% | 16.91% |  | 2007-2010 |  |  | 0.4809% | 30.96% | [9 empty] | 0% |  | 0% | 18.8% |  | 2007-2010 | 19.79% | 42.32% | 0.9797% | 32.03% | 15.74% | 24% | 41.65% | 21.44% | -49.08% | 47.11% | 0.1037% | 2.602% | 43.87% | 0.03845% | 0% | 1.924% | 17.13%
2010-2013 | 12.96% | 0% | 0.03744% | 15.45% | 34.62% | 15.28% | 17.97% | 15.64% | -40.3% | 12.31% | 20.01% | 0.2453% | 4.254% | 0.006508% | 0% | 2.656% | 8.932% |  | 2010-2013 | 12.96% | 0% | 0.01986% | 13.34% | 34.62% | 15.28% | 17.97% | 15.64% | -40.3% | 12.31% | 20.01% | 0.2453% | 4.254% | 0.003649% | 0% | 2.621% | 8.437% |  | 2010-2013 | 12.96% | 0% | 0.07334% | 26.53% | 34.62% | 15.28% | 17.97% | 15.64% | -40.3% | 12.31% | 20.01% | 0.2453% | 4.254% | 0.01082% | 0% | 2.674% | 9.275% |  | 2010-2013 |  |  | 0.002145% | 11.93% | [9 empty] | 0% |  | 0% | 6.124% |  | 2010-2013 | 12.96% | 0% | 0.03644% | 15.3% | 34.62% | 15.28% | 17.97% | 15.64% | -40.3% | 12.31% | 20.01% | 0.2453% | 4.254% | 0.006363% | 0% | 2.655% | 8.915%
2013-2016 | 23.18% | 22.34% | 0.4876% | 2.165% | -24.68% | 4.289% | 9.082% | 3.867% | 15.63% | 5.645% | 0.02095% | 0% | 15.99% | 0% | 0% | 0% | 6.124% |  | 2013-2016 | 23.18% | 22.34% | 0.7344% | 1.915% | -24.68% | 4.289% | 9.082% | 3.867% | 15.63% | 5.645% | 0.02095% | 0% | 15.99% | 0% | 0% | 0% | 5.253% |  | 2013-2016 | 23.18% | 22.34% | -0.01242% | 3.408% | -24.68% | 4.289% | 9.082% | 3.867% | 15.63% | 5.645% | 0.02095% | 0% | 15.99% | 0% | 0% | 0% | 6.73% |  | 2013-2016 |  |  | 0.9844% | 1.744% | [9 empty] | 0% |  | 0% | 1.266% |  | 2013-2016 | 23.18% | 22.34% | 0.5016% | 2.148% | -24.68% | 4.289% | 9.082% | 3.867% | 15.63% | 5.645% | 0.02095% | 0% | 15.99% | 0% | 0% | 0% | 6.093%
2004-2016 | 45.88% | 64.66% | 1.522% | 54.69% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.04584% | 0% | 4.53% | 34.24% |  | 2004-2016 | 45.88% | 64.66% | 1.491% | 52.8% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.0257% | 0% | 4.471% | 34.15% |  | 2004-2013 | 45.88% | 64.66% | 1.586% | 63.99% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.07615% | 0% | 4.561% | 34.3% |  | 2004-2016 |  |  | 1.459% | 51.51% | [9 empty] | 0% |  | 0% | 33.75% |  | 2004-2016 | 45.88% | 64.66% | 1.52% | 54.55% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.04481% | 0% | 4.528% | 34.23%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.16929 | 0.029161 | 0.092109 | 0.029255 | 0 | 0.094484 | 0 | 0.099614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.76088 | 5.608% | Small Office | 5.7037 | 0.98247 | 3.1033 | 1.3103 | 0 | 3.1833 | 0 | 3.3562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.9602 | 5.608% | Small Office | 1.6712 | 0.28786 | 0.90927 | 0.24046 | 0 | 0.93271 | 0 | 0.98336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.4629 | 5.608% | Small Office | 0 | 0 | 0 | 0.0048967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048967 | 5.608% | Small Office | 17.4957 | 3.0137 | 9.5191 | 3.0526 | 0 | 9.7646 | 0 | 10.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 78.6638 | 5.608%
Medium Office | 0.15895 | 0.0246 | 0.014181 | 0.080397 | 0 | 0.16323 | 0 | 0.042516 | 0.00036446 | 7.8706e-05 | 0 | 0.086781 | 0.006172 | 0 | 0 | 0.30678 | 0.88406 | 6.047% | Medium Office | 5.3552 | 0.82883 | 1.4181 | 3.7558 | 0 | 5.4996 | 0 | 1.4324 | 0.012279 | 0.0026517 | 0 | 2.9238 | 0.20795 | 0 | 0 | 10.3361 | 31.7728 | 6.047% | Medium Office | 1.5691 | 0.24285 | 0 | 0.63777 | 0 | 1.6114 | 0 | 0.41971 | 0.0035978 | 0.00077696 | 0 | 0.85667 | 0.060928 | 0 | 0 | 3.0285 | 8.4312 | 6.047% | Medium Office | 0 | 0 | 0.014181 | 0.015791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029972 | 6.047% | Medium Office | 16.4267 | 2.5424 | 1.55 | 8.4028 | 0 | 16.8697 | 0 | 4.3939 | 0.037666 | 0.008134 | 0 | 8.9685 | 0.63785 | 0 | 0 | 31.7051 | 91.5427 | 6.047%
Large Office | 0.17877 | 0.019414 | 0.010437 | 0.031105 | 0.075709 | 0.22074 | 0.018842 | 0.13258 | 0.0014499 | 0.023974 | 0 | 0.10728 | 0.0031026 | 0 | 0.84214 | 0.30109 | 1.9666 | 3.327% | Large Office | 6.0231 | 0.6541 | 1.0437 | 3.0832 | 2.5508 | 7.437 | 0.63482 | 4.4668 | 0.048848 | 0.80773 | 0 | 3.6145 | 0.10453 | 0 | 28.3732 | 10.1441 | 68.9865 | 3.327% | Large Office | 1.7648 | 0.19165 | 0 | 0.0040651 | 0.74738 | 2.1791 | 0.186 | 1.3088 | 0.014313 | 0.23667 | 0 | 1.0591 | 0.030628 | 0 | 8.3133 | 2.9722 | 19.0079 | 3.327% | Large Office | 0 | 0 | 0.010437 | 0.030693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04113 | 3.327% | Large Office | 18.4754 | 2.0064 | 1.1408 | 3.3973 | 7.8243 | 22.8125 | 1.9473 | 13.7017 | 0.14984 | 2.4776 | 0 | 11.0872 | 0.32064 | 0 | 87.0323 | 31.1161 | 203.4894 | 3.327%
Standalone Retail | 0.3411 | 0.043922 | 0.035632 | 0.050328 | 0 | 0.16335 | 0 | 0.1989 | 0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0722 | 15.25% | Standalone Retail | 11.4922 | 1.4798 | 3.5632 | 5.0328 | 0 | 5.5034 | 0 | 6.7014 | 0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.8246 | 15.25% | Standalone Retail | 3.3672 | 0.43359 | 0 | 0 | 0 | 1.6125 | 0 | 1.9635 | 0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.736 | 15.25% | Standalone Retail | 0 | 0 | 0.035632 | 0.050328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08596 | 15.25% | Standalone Retail | 35.2513 | 4.5392 | 3.8946 | 5.5009 | 0 | 16.8814 | 0 | 20.556 | 1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 111.3214 | 15.25%
Strip Mall | 0.56389 | 0.068758 | 0.078107 | 0.10145 | 0 | 0.18419 | 0 | 0.18464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3413 | 5.669% | Strip Mall | 18.9984 | 2.3166 | 2.6315 | 10.1448 | 0 | 6.2055 | 0 | 6.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.9175 | 5.669% | Strip Mall | 5.5665 | 0.67875 | 0.77104 | 0 | 0 | 1.8182 | 0 | 1.8227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2394 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 | 5.669% | Strip Mall | 58.2761 | 7.1059 | 8.072 | 11.0883 | 0 | 19.035 | 0 | 19.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 139.2226 | 5.669%
Primary School | 0.13781 | 0.0097508 | 0.02443 | 0.064724 | 0 | 0.18036 | 0 | 0.090009 | 0.027835 | 0.0007941 | 0.041532 | 0 | 0.006592 | 0.10323 | 0 | 0.36051 | 1.0476 | 4.994% | Primary School | 4.6431 | 0.32852 | 1.7912 | 6.4724 | 0 | 6.0768 | 0 | 3.0326 | 0.9378 | 0.026754 | 1.3993 | 0 | 0.2221 | 6.5458 | 0 | 12.1461 | 43.6224 | 4.994% | Primary School | 1.3604 | 0.096257 | 0.097037 | 0 | 0 | 1.7805 | 0 | 0.88854 | 0.27477 | 0.007839 | 0.40999 | 0 | 0.065074 | 0.56229 | 0 | 3.5588 | 9.1015 | 4.994% | Primary School | 0 | 0 | 0.0146 | 0.064724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12559 | 4.994% | Primary School | 14.2424 | 1.0077 | 2.6116 | 7.0743 | 0 | 18.64 | 0 | 9.3022 | 2.8766 | 0.082067 | 4.2922 | 0 | 0.68126 | 10.9436 | 0 | 37.2571 | 109.0111 | 4.994%
Secondary School | 0.12815 | 0.0090796 | 0.04202 | 0.04409 | 0 | 0.19639 | 0 | 0.095701 | 0.024194 | 0.0042554 | 0.02377 | 0.0087798 | 0.0039621 | 0.072419 | 0 | 0.25606 | 0.90888 | 10.36% | Secondary School | 4.3177 | 0.30591 | 2.836 | 4.409 | 0 | 6.6168 | 0 | 3.2243 | 0.81514 | 0.14337 | 0.80084 | 0.29581 | 0.13349 | 4.0625 | 0 | 8.6272 | 36.588 | 10.36% | Secondary School | 1.2651 | 0.089631 | 0.20338 | 0 | 0 | 1.9387 | 0 | 0.94473 | 0.23884 | 0.042007 | 0.23465 | 0.086671 | 0.039112 | 0.47333 | 0 | 2.5278 | 8.0839 | 10.36% | Secondary School | 0 | 0 | 0.021418 | 0.04409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.089978 | 10.36% | Secondary School | 13.2442 | 0.93835 | 4.4702 | 4.819 | 0 | 20.2966 | 0 | 9.8904 | 2.5004 | 0.43978 | 2.4565 | 0.90736 | 0.40946 | 7.6299 | 0 | 26.4631 | 94.4653 | 10.36%
Outpatient Healthcare | 0.3173 | 0.037575 | 0.050432 | 0.30504 | 0.1145 | 0.50061 | 0 | 0.24582 | 0 | 0.0016858 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8738 | 4.371% | Outpatient Healthcare | 10.6905 | 1.266 | 5.0432 | 19.3407 | 3.8577 | 16.8663 | 0 | 8.282 | 0 | 0.056797 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.1209 | 4.371% | Outpatient Healthcare | 3.1323 | 0.37093 | 0 | 1.662 | 1.1303 | 4.9418 | 0 | 2.4266 | 0 | 0.016642 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.0913 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.050432 | 0.13668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23072 | 4.371% | Outpatient Healthcare | 32.7921 | 3.8833 | 5.5123 | 32.339 | 11.833 | 51.736 | 0 | 25.4042 | 0 | 0.17422 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 298.3679 | 4.371%
Hospital | 0.39609 | 0.018054 | 0.050157 | 0.29008 | 0.077457 | 0.28568 | 0.028979 | 0.33976 | 0.021383 | 0.056989 | 0.024318 | 0.29215 | 0.0082805 | 0.27223 | 0 | 0.63669 | 2.7983 | 3.448% | Hospital | 13.3448 | 0.60826 | 4.8112 | 25.1823 | 2.6096 | 9.6251 | 0.97634 | 11.4471 | 0.72045 | 1.9201 | 0.81931 | 9.843 | 0.27898 | 16.4378 | 0 | 21.4513 | 120.0757 | 3.448% | Hospital | 3.91 | 0.17822 | 0.030447 | 0.56951 | 0.76463 | 2.8202 | 0.28607 | 3.354 | 0.21109 | 0.56258 | 0.24006 | 2.884 | 0.081742 | 1.6057 | 0 | 6.2852 | 23.7834 | 3.448% | Hospital | 0 | 0 | 0.047073 | 0.23239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38904 | 3.448% | Hospital | 40.9341 | 1.8658 | 5.4638 | 31.362 | 8.0049 | 29.5242 | 2.9948 | 35.1131 | 2.2099 | 5.8896 | 2.5132 | 30.1926 | 0.85576 | 28.7866 | 0 | 65.8001 | 291.5104 | 3.448%
Small Hotel | 0.18905 | 0.028854 | 0.12811 | 0.074891 | 0 | 0.17781 | 0 | 0.11817 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1728 | 1.721% | Small Hotel | 6.3694 | 0.97213 | 12.8112 | 3.425 | 0 | 5.9909 | 0 | 3.9815 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 55.0409 | 1.721% | Small Hotel | 1.8662 | 0.28483 | 0 | 0.60505 | 0 | 1.7553 | 0 | 1.1666 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.2654 | 1.721% | Small Hotel | 0 | 0 | 0.12811 | 0.013599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23418 | 1.721% | Small Hotel | 19.5377 | 2.9819 | 14.0027 | 7.8207 | 0 | 18.3765 | 0 | 12.2128 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 122.5961 | 1.721%
Large Hotel | 0.19079 | 0.042116 | 0.18143 | 0.069016 | 0 | 0.35556 | 0 | 0.14446 | 0.047113 | 0.014285 | 0.019529 | 0.219 | 0.0050268 | 0.27391 | 0 | 0.24162 | 1.8038 | 4.951% | Large Hotel | 6.4279 | 1.4189 | 16.7562 | 6.9016 | 0 | 11.9794 | 0 | 4.8671 | 1.5873 | 0.48129 | 0.65798 | 7.3786 | 0.16936 | 18.4346 | 0 | 8.1405 | 85.2008 | 4.951% | Large Hotel | 1.8834 | 0.41575 | 0.2064 | 0 | 0 | 3.51 | 0 | 1.4261 | 0.46509 | 0.14102 | 0.19279 | 2.1619 | 0.049623 | 1.3333 | 0 | 2.3852 | 14.1705 | 4.951% | Large Hotel | 0 | 0 | 0.16052 | 0.069016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36837 | 4.951% | Large Hotel | 19.717 | 4.3525 | 19.7054 | 7.5435 | 0 | 36.7459 | 0 | 14.9295 | 4.869 | 1.4763 | 2.0183 | 22.6332 | 0.5195 | 29.1339 | 0 | 24.9702 | 188.6141 | 4.951%
Quick-service Restaurant | 0.31021 | 0.098927 | 0.67183 | 1.323 | 0 | 0.74461 | 0 | 0.72968 | 0 | 0 | 0.96082 | 0 | 0 | 4.435 | 0 | 0 | 9.2741 | 0.5866% | Quick-service Restaurant | 10.4516 | 3.333 | 67.1828 | 132.3043 | 0 | 25.0871 | 0 | 24.5841 | 0 | 0 | 32.3716 | 0 | 0 | 269.3289 | 0 | 0 | 564.6434 | 0.5866% | Quick-service Restaurant | 3.0623 | 0.97657 | 0 | 0 | 0 | 7.3505 | 0 | 7.2032 | 0 | 0 | 9.4849 | 0 | 0 | 25.9296 | 0 | 0 | 54.0071 | 0.5866% | Quick-service Restaurant | 0 | 0 | 0.67183 | 1.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8032 | 0.5866% | Quick-service Restaurant | 32.0593 | 10.2237 | 73.4309 | 144.6086 | 0 | 76.9525 | 0 | 75.4098 | 0 | 0 | 99.2973 | 0 | 0 | 469.1065 | 0 | 0 | 981.0885 | 0.5866%
Full-service Restaurant | 0.2851 | 0.09532 | 0.91773 | 0.81467 | 0 | 0.61795 | 0 | 0.51877 | 0 | 0.0023014 | 0.42917 | 0 | 0 | 2.9421 | 0 | 0 | 6.6231 | 0.6597% | Full-service Restaurant | 9.6055 | 3.2115 | 66.1897 | 81.4672 | 0 | 20.8198 | 0 | 17.4782 | 0 | 0.077539 | 14.4593 | 0 | 0 | 152.7879 | 0 | 0 | 366.0967 | 0.6597% | Full-service Restaurant | 2.8144 | 0.94097 | 3.8088 | 0 | 0 | 6.1002 | 0 | 5.1211 | 0 | 0.022719 | 4.2366 | 0 | 0 | 21.0545 | 0 | 0 | 44.0993 | 0.6597% | Full-service Restaurant | 0 | 0 | 0.5319 | 0.81467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1559 | 0.6597% | Full-service Restaurant | 29.4642 | 9.851 | 98.0114 | 89.0436 | 0 | 63.8629 | 0 | 53.613 | 0 | 0.23785 | 44.3528 | 0 | 0 | 308.8753 | 0 | 0 | 697.3122 | 0.6597%
Mid-rise Apartment | 0.092829 | 0.021634 | 0.3129 | 0.029273 | 0 | 0.12212 | 0 | 0.16073 | 0.023109 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1888 | 7.321% | Mid-rise Apartment | 3.1276 | 0.72887 | 10.5421 | 2.9273 | 0 | 4.1144 | 0 | 5.4153 | 0.77859 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.9945 | 7.321% | Mid-rise Apartment | 0.91638 | 0.21356 | 3.0888 | 0 | 0 | 1.2055 | 0 | 1.5867 | 0.22813 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.4467 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.029273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029273 | 7.321% | Mid-rise Apartment | 9.5935 | 2.2358 | 32.3369 | 3.1995 | 0 | 12.6205 | 0 | 16.6109 | 2.3883 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 123.035 | 7.321%
High-rise Apartment | 0.09162 | 0.03934 | 0.11539 | 0.041876 | 0 | 0.18918 | 0.0046632 | 0.17245 | 0.024658 | 0.015573 | 0 | 0.052844 | 0.0048288 | 0 | 0 | 0.32437 | 1.0768 | 8.967% | High-rise Apartment | 3.0868 | 1.3254 | 11.5391 | 2.8403 | 0 | 6.3739 | 0.15711 | 5.8101 | 0.83076 | 0.52469 | 0 | 1.7804 | 0.16269 | 0 | 0 | 10.9284 | 45.3598 | 8.967% | High-rise Apartment | 0.90444 | 0.38835 | 0 | 0.20057 | 0 | 1.8676 | 0.046033 | 1.7024 | 0.24341 | 0.15373 | 0 | 0.52166 | 0.047668 | 0 | 0 | 3.202 | 9.2778 | 8.967% | High-rise Apartment | 0 | 0 | 0.11539 | 0.021558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13695 | 8.967% | High-rise Apartment | 9.4686 | 4.0657 | 12.6122 | 4.456 | 0 | 19.5515 | 0.48192 | 17.8221 | 2.5483 | 1.6094 | 0 | 5.4612 | 0.49904 | 0 | 0 | 33.522 | 112.0981 | 8.967%
Warehouse | 0.1 | 0.03073 | 0.013415 | 0.065002 | 0 | 0.010542 | 0 | 0.016801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.31029 | 16.72% | Warehouse | 3.3693 | 1.0353 | 0.45196 | 6.5002 | 0 | 0.35519 | 0 | 0.56606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.7645 | 16.72% | Warehouse | 0.98721 | 0.30335 | 0.13243 | 0 | 0 | 0.10407 | 0 | 0.16586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.4215 | 16.72% | Warehouse | 0 | 0 | 0 | 0.065002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065002 | 16.72% | Warehouse | 10.3351 | 3.1758 | 1.3864 | 7.1047 | 0 | 1.0895 | 0 | 1.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 32.4548 | 16.72%
US Weighted | 0.20487 | 0.032098 | 0.082418 | 0.086705 | 0.010194 | 0.17573 | 0.0020442 | 0.13717 | 0.013618 | 0.0054434 | 0.01481 | 0.065012 | 0.0021835 | 0.082941 | 0.02802 | 0.26951 | 1.2128 | 100% | US Weighted | 6.9023 | 1.0814 | 5.5195 | 7.5094 | 0.34346 | 5.9207 | 0.068874 | 4.6216 | 0.45882 | 0.1834 | 0.49896 | 2.1904 | 0.073567 | 4.985 | 0.94403 | 9.2066 | 50.5079 | 100% | US Weighted | 2.0224 | 0.31686 | 0.40527 | 0.17286 | 0.10063 | 1.7348 | 0.02018 | 1.3541 | 0.13444 | 0.053735 | 0.1462 | 0.64178 | 0.021555 | 0.49265 | 0.2766 | 2.6417 | 10.5357 | 100% | US Weighted | 0 | 0 | 0.041364 | 0.069194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.1455 | 100% | US Weighted | 21.1722 | 3.3172 | 8.7638 | 9.3726 | 1.0535 | 18.1613 | 0.21127 | 14.1763 | 1.4074 | 0.56256 | 1.5305 | 6.7188 | 0.22566 | 8.7684 | 2.8957 | 27.8641 | 126.2013 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: |  | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
Small Office | 0.23359 | 0.060911 | 0.092109 | 0.027689 | 0 | 0.098899 | 0 | 0.10249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.86266 | 5.608% | Small Office | 7.8701 | 2.0522 | 3.1033 | 1.2347 | 0 | 3.3321 | 0 | 3.4531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.3663 | 5.608% | Small Office | 2.3059 | 0.6013 | 0.90927 | 0.2284 | 0 | 0.9763 | 0 | 1.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.471 | 5.608% | Small Office | 0 | 0 | 0 | 0.0045519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045519 | 5.608% | Small Office | 24.1408 | 6.295 | 9.5191 | 2.8886 | 0 | 10.2209 | 0 | 10.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 89.1801 | 5.608%
Medium Office | 0.1722 | 0.054071 | 0.014465 | 0.082159 | 0 | 0.1671 | 0 | 0.043959 | 6.7252e-05 | 7.8706e-05 | 0 | 0.086781 | 0.0089492 | 0 | 0 | 0.30678 | 0.93661 | 6.047% | Medium Office | 5.8016 | 1.8217 | 1.4465 | 3.7912 | 0 | 5.6298 | 0 | 1.4811 | 0.0022658 | 0.0026517 | 0 | 2.9238 | 0.30151 | 0 | 0 | 10.3361 | 33.5381 | 6.047% | Medium Office | 1.6999 | 0.53377 | 0 | 0.65874 | 0 | 1.6495 | 0 | 0.43395 | 0.00066389 | 0.00077696 | 0 | 0.85667 | 0.088343 | 0 | 0 | 3.0285 | 8.9508 | 6.047% | Medium Office | 0 | 0 | 0.014465 | 0.015429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029894 | 6.047% | Medium Office | 17.7959 | 5.588 | 1.581 | 8.5827 | 0 | 17.2688 | 0 | 4.543 | 0.0069502 | 0.008134 | 0 | 8.9685 | 0.92486 | 0 | 0 | 31.7051 | 96.9731 | 6.047%
Large Office | 0.19252 | 0.038475 | 0.010711 | 0.052782 | 0.037292 | 0.2729 | 0.020271 | 0.13364 | 0.0014603 | 0.026836 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.0419 | 3.327% | Large Office | 6.4864 | 1.2963 | 1.0711 | 5.2498 | 1.2564 | 9.1945 | 0.68298 | 4.5027 | 0.049199 | 0.90413 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 72.9771 | 3.327% | Large Office | 1.9005 | 0.37982 | 0 | 0.0042215 | 0.36813 | 2.694 | 0.20011 | 1.3193 | 0.014415 | 0.26491 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.5345 | 3.327% | Large Office | 0 | 0 | 0.010711 | 0.052354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063065 | 3.327% | Large Office | 19.8965 | 3.9763 | 1.1707 | 5.7665 | 3.854 | 28.2033 | 2.095 | 13.8117 | 0.15092 | 2.7734 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 211.3996 | 3.327%
Standalone Retail | 0.4182 | 0.068757 | 0.035631 | 0.047726 | 0 | 0.17206 | 0 | 0.20937 | 0.017763 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1909 | 15.25% | Standalone Retail | 14.0898 | 2.3165 | 3.5631 | 4.7726 | 0 | 5.7971 | 0 | 7.054 | 0.59846 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.6518 | 15.25% | Standalone Retail | 4.1283 | 0.67874 | 0 | 0 | 0 | 1.6986 | 0 | 2.0668 | 0.17535 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.9336 | 15.25% | Standalone Retail | 0 | 0 | 0.035631 | 0.047726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083358 | 15.25% | Standalone Retail | 43.2193 | 7.1057 | 3.8945 | 5.2165 | 0 | 17.7821 | 0 | 21.6376 | 1.8357 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 123.5748 | 15.25%
Strip Mall | 0.6889 | 0.11568 | 0.078068 | 0.092785 | 0 | 0.19779 | 0 | 0.19211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5256 | 5.669% | Strip Mall | 23.2103 | 3.8975 | 2.6303 | 9.2785 | 0 | 6.6638 | 0 | 6.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.5525 | 5.669% | Strip Mall | 6.8006 | 1.142 | 0.77066 | 0 | 0 | 1.9525 | 0 | 1.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.1443 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.092785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092785 | 5.669% | Strip Mall | 71.1957 | 11.9553 | 8.0681 | 10.1414 | 0 | 20.4406 | 0 | 19.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 158.2179 | 5.669%
Primary School | 0.26938 | 0.016881 | 0.024467 | 0.067829 | 0 | 0.20811 | 0 | 0.11507 | 0.028145 | 0.00067896 | 0.041539 | 0 | 0.0092017 | 0.10323 | 0 | 0.36051 | 1.245 | 4.994% | Primary School | 9.0758 | 0.56876 | 1.7949 | 6.7829 | 0 | 7.0115 | 0 | 3.877 | 0.94824 | 0.022875 | 1.3995 | 0 | 0.31002 | 6.5458 | 0 | 12.1461 | 50.4833 | 4.994% | Primary School | 2.6592 | 0.16665 | 0.097037 | 0 | 0 | 2.0544 | 0 | 1.1359 | 0.27783 | 0.0067025 | 0.41006 | 0 | 0.090836 | 0.56229 | 0 | 3.5588 | 11.0197 | 4.994% | Primary School | 0 | 0 | 0.014638 | 0.067829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12873 | 4.994% | Primary School | 27.8392 | 1.7446 | 2.6158 | 7.4137 | 0 | 21.5071 | 0 | 11.8923 | 2.9086 | 0.070169 | 4.293 | 0 | 0.95096 | 10.9436 | 0 | 37.2571 | 129.436 | 4.994%
Secondary School | 0.24658 | 0.015715 | 0.042024 | 0.045064 | 0 | 0.21383 | 0 | 0.10932 | 0.02766 | 0.0058638 | 0.023777 | 0.0087798 | 0.0054567 | 0.072419 | 0 | 0.25606 | 1.0725 | 10.36% | Secondary School | 8.3077 | 0.52948 | 2.8363 | 4.5064 | 0 | 7.2043 | 0 | 3.683 | 0.9319 | 0.19756 | 0.80109 | 0.29581 | 0.18385 | 4.0625 | 0 | 8.6272 | 42.1671 | 10.36% | Secondary School | 2.4342 | 0.15514 | 0.20337 | 0 | 0 | 2.1108 | 0 | 1.0791 | 0.27305 | 0.057885 | 0.23472 | 0.086671 | 0.053867 | 0.47333 | 0 | 2.5278 | 9.6899 | 10.36% | Secondary School | 0 | 0 | 0.021422 | 0.045064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090956 | 10.36% | Secondary School | 25.4833 | 1.6241 | 4.4706 | 4.9255 | 0 | 22.0985 | 0 | 11.2974 | 2.8585 | 0.606 | 2.4573 | 0.90736 | 0.56394 | 7.6299 | 0 | 26.4631 | 111.3855 | 10.36%
Outpatient Healthcare | 0.34511 | 0.077156 | 0.056464 | 0.33484 | 0.070894 | 0.56647 | 0 | 0.26354 | 0.012571 | 0.0018147 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.0297 | 4.371% | Outpatient Healthcare | 11.6272 | 2.5995 | 5.6464 | 21.3854 | 2.3885 | 19.0852 | 0 | 8.8792 | 0.42353 | 0.06114 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 118.8139 | 4.371% | Outpatient Healthcare | 3.4068 | 0.76166 | 0 | 1.8012 | 0.69984 | 5.592 | 0 | 2.6016 | 0.1241 | 0.017914 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.4158 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.056464 | 0.15238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25245 | 4.371% | Outpatient Healthcare | 35.6655 | 7.9738 | 6.1715 | 35.5117 | 7.3267 | 58.5423 | 0 | 27.2362 | 1.2992 | 0.18754 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 314.6081 | 4.371%
Hospital | 0.40432 | 0.024723 | 0.051803 | 0.29584 | 0.078325 | 0.29192 | 0.028853 | 0.34038 | 0.027866 | 0.063272 | 0.024315 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.8447 | 3.448% | Hospital | 13.6223 | 0.83296 | 4.9758 | 25.7233 | 2.6389 | 9.8352 | 0.97209 | 11.4681 | 0.93887 | 2.1317 | 0.81923 | 9.843 | 0.40475 | 16.4378 | 0 | 21.4513 | 122.0953 | 3.448% | Hospital | 3.9913 | 0.24406 | 0.030447 | 0.57472 | 0.77319 | 2.8817 | 0.28482 | 3.3602 | 0.27509 | 0.6246 | 0.24003 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 24.1737 | 3.448% | Hospital | 0 | 0 | 0.048719 | 0.23762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.39591 | 3.448% | Hospital | 41.7854 | 2.555 | 5.6437 | 31.9885 | 8.0946 | 30.1685 | 2.9818 | 35.1775 | 2.8799 | 6.5389 | 2.5129 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 296.3475 | 3.448%
Small Hotel | 0.2115 | 0.042854 | 0.12971 | 0.11499 | 0 | 0.19522 | 0 | 0.18128 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3314 | 1.721% | Small Hotel | 7.1259 | 1.4438 | 12.9709 | 4.802 | 0 | 6.5772 | 0 | 6.1076 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 60.5182 | 1.721% | Small Hotel | 2.0879 | 0.42304 | 0 | 0.99699 | 0 | 1.9271 | 0 | 1.7895 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.812 | 1.721% | Small Hotel | 0 | 0 | 0.12971 | 0.013993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23617 | 1.721% | Small Hotel | 21.8581 | 4.4288 | 14.1772 | 11.9669 | 0 | 20.1749 | 0 | 18.7346 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 139.0042 | 1.721%
Large Hotel | 0.21046 | 0.056718 | 0.18151 | 0.091197 | 0 | 0.36437 | 0 | 0.15241 | 0.049054 | 0.01898 | 0.019526 | 0.219 | 0.0071744 | 0.27391 | 0 | 0.24162 | 1.8859 | 4.951% | Large Hotel | 7.0906 | 1.9109 | 16.7642 | 9.1197 | 0 | 12.2762 | 0 | 5.1349 | 1.6527 | 0.63946 | 0.65787 | 7.3786 | 0.24172 | 18.4346 | 0 | 8.1405 | 89.4419 | 4.951% | Large Hotel | 2.0776 | 0.5599 | 0.2064 | 0 | 0 | 3.5969 | 0 | 1.5045 | 0.48424 | 0.18736 | 0.19276 | 2.1619 | 0.070823 | 1.3333 | 0 | 2.3852 | 14.7609 | 4.951% | Large Hotel | 0 | 0 | 0.1606 | 0.091197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39063 | 4.951% | Large Hotel | 21.7499 | 5.8616 | 19.7141 | 9.9679 | 0 | 37.6563 | 0 | 15.7508 | 5.0695 | 1.9615 | 2.018 | 22.6332 | 0.74145 | 29.1339 | 0 | 24.9702 | 197.2282 | 4.951%
Quick-service Restaurant | 0.36364 | 0.1728 | 0.67178 | 1.324 | 0 | 0.75235 | 0 | 0.73434 | 0 | 0 | 0.96114 | 0 | 0 | 4.435 | 0 | 0 | 9.4151 | 0.5866% | Quick-service Restaurant | 12.2515 | 5.8218 | 67.178 | 132.4045 | 0 | 25.3479 | 0 | 24.7413 | 0 | 0 | 32.3824 | 0 | 0 | 269.3289 | 0 | 0 | 569.4564 | 0.5866% | Quick-service Restaurant | 3.5897 | 1.7058 | 0 | 0 | 0 | 7.4269 | 0 | 7.2492 | 0 | 0 | 9.4881 | 0 | 0 | 25.9296 | 0 | 0 | 55.3893 | 0.5866% | Quick-service Restaurant | 0 | 0 | 0.67178 | 1.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8041 | 0.5866% | Quick-service Restaurant | 37.5806 | 17.858 | 73.4256 | 144.7182 | 0 | 77.7527 | 0 | 75.8918 | 0 | 0 | 99.3305 | 0 | 0 | 469.1065 | 0 | 0 | 995.6638 | 0.5866%
Full-service Restaurant | 0.36468 | 0.16886 | 0.91804 | 0.80978 | 0 | 0.62673 | 0 | 0.52415 | 0 | 0.0023014 | 0.42933 | 0 | 0 | 2.9421 | 0 | 0 | 6.786 | 0.6597% | Full-service Restaurant | 12.2867 | 5.6893 | 66.2199 | 80.9781 | 0 | 21.1158 | 0 | 17.6596 | 0 | 0.077539 | 14.4649 | 0 | 0 | 152.7879 | 0 | 0 | 371.2798 | 0.6597% | Full-service Restaurant | 3.6 | 1.667 | 3.8088 | 0 | 0 | 6.1869 | 0 | 5.1743 | 0 | 0.022719 | 4.2382 | 0 | 0 | 21.0545 | 0 | 0 | 45.7524 | 0.6597% | Full-service Restaurant | 0 | 0 | 0.53221 | 0.80978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1513 | 0.6597% | Full-service Restaurant | 37.6885 | 17.4515 | 98.0443 | 88.509 | 0 | 64.7709 | 0 | 54.1694 | 0 | 0.23785 | 44.37 | 0 | 0 | 308.8753 | 0 | 0 | 714.1168 | 0.6597%
Mid-rise Apartment | 0.11767 | 0.032866 | 0.31286 | 0.028713 | 0 | 0.12795 | 0 | 0.16832 | 0.022032 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2366 | 7.321% | Mid-rise Apartment | 3.9646 | 1.1073 | 10.5407 | 2.8713 | 0 | 4.3109 | 0 | 5.6709 | 0.74228 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.5684 | 7.321% | Mid-rise Apartment | 1.1616 | 0.32444 | 3.0884 | 0 | 0 | 1.2631 | 0 | 1.6616 | 0.21749 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9243 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.028713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028713 | 7.321% | Mid-rise Apartment | 12.1611 | 3.3966 | 32.3327 | 3.1383 | 0 | 13.2232 | 0 | 17.3949 | 2.2769 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 127.9733 | 7.321%
High-rise Apartment | 0.11511 | 0.056198 | 0.11574 | 0.041163 | 0 | 0.19479 | 0.0095199 | 0.1784 | 0.023788 | 0.016057 | 0 | 0.052844 | 0.0069449 | 0 | 0 | 0.32437 | 1.1349 | 8.967% | High-rise Apartment | 3.8783 | 1.8934 | 11.574 | 2.7867 | 0 | 6.5628 | 0.32074 | 6.0107 | 0.80147 | 0.54099 | 0 | 1.7804 | 0.23399 | 0 | 0 | 10.9284 | 47.3119 | 8.967% | High-rise Apartment | 1.1363 | 0.55477 | 0 | 0.19796 | 0 | 1.9229 | 0.093977 | 1.7611 | 0.23483 | 0.15851 | 0 | 0.52166 | 0.068558 | 0 | 0 | 3.202 | 9.8527 | 8.967% | High-rise Apartment | 0 | 0 | 0.11574 | 0.02111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13685 | 8.967% | High-rise Apartment | 11.8964 | 5.8079 | 12.6504 | 4.3798 | 0 | 20.1308 | 0.98384 | 18.4374 | 2.4584 | 1.6594 | 0 | 5.4612 | 0.71773 | 0 | 0 | 33.522 | 118.1053 | 8.967%
Warehouse | 0.16972 | 0.045269 | 0.013414 | 0.065791 | 0 | 0.011554 | 0 | 0.017433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.39698 | 16.72% | Warehouse | 5.718 | 1.5252 | 0.45196 | 6.5791 | 0 | 0.38927 | 0 | 0.58734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.7374 | 16.72% | Warehouse | 1.6754 | 0.44688 | 0.13242 | 0 | 0 | 0.11406 | 0 | 0.17209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2694 | 16.72% | Warehouse | 0 | 0 | 0 | 0.065791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065791 | 16.72% | Warehouse | 17.5396 | 4.6784 | 1.3863 | 7.191 | 0 | 1.194 | 0 | 1.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 41.418 | 16.72%
US Weighted | 0.2667 | 0.052393 | 0.082826 | 0.090102 | 0.00704 | 0.18827 | 0.0025229 | 0.14567 | 0.014718 | 0.0061976 | 0.014813 | 0.065012 | 0.0031081 | 0.082941 | 0.02802 | 0.26951 | 1.3198 | 100% | US Weighted | 8.9854 | 1.7652 | 5.5607 | 7.7594 | 0.23719 | 6.3432 | 0.085002 | 4.9079 | 0.49588 | 0.20881 | 0.49909 | 2.1904 | 0.10472 | 4.985 | 0.94403 | 9.2066 | 54.2784 | 100% | US Weighted | 2.6327 | 0.51721 | 0.40522 | 0.18623 | 0.069497 | 1.8586 | 0.024905 | 1.438 | 0.14529 | 0.06118 | 0.14623 | 0.64178 | 0.030683 | 0.49265 | 0.2766 | 2.6417 | 11.5685 | 100% | US Weighted | 0 | 0 | 0.041777 | 0.071238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.14796 | 100% | US Weighted | 27.562 | 5.4147 | 8.8085 | 9.7359 | 0.72756 | 19.4573 | 0.26074 | 15.0547 | 1.5211 | 0.6405 | 1.5309 | 6.7188 | 0.32122 | 8.7684 | 2.8957 | 27.8641 | 137.2819 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.27431 | 0.060911 | 0.092109 | 0.031705 | 0 | 0.14059 | 0 | 0.11968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.97087 | 5.608% | Small Office | 9.2418 | 2.0522 | 3.1033 | 1.4201 | 0 | 4.7366 | 0 | 4.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.0622 | 5.608% | Small Office | 2.7079 | 0.6013 | 0.90927 | 0.26058 | 0 | 1.3878 | 0 | 1.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.5317 | 5.608% | Small Office | 0 | 0 | 0 | 0.005308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005308 | 5.608% | Small Office | 28.3485 | 6.295 | 9.5191 | 3.3082 | 0 | 14.5293 | 0 | 12.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 100.3677 | 5.608%
Medium Office | 0.19973 | 0.054071 | 0.014467 | 0.096166 | 0 | 0.19044 | 0 | 0.049396 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091254 | 0 | 0 | 0.31054 | 1.011 | 6.047% | Medium Office | 6.7292 | 1.8217 | 1.4467 | 4.2909 | 0 | 6.4163 | 0 | 1.6642 | 0 | 0.0026517 | 0 | 2.9318 | 0.30745 | 0 | 0 | 10.4627 | 36.0736 | 6.047% | Medium Office | 1.9717 | 0.53377 | 0 | 0.79286 | 0 | 1.88 | 0 | 0.48762 | 0 | 0.00077696 | 0 | 0.859 | 0.090083 | 0 | 0 | 3.0656 | 9.6813 | 6.047% | Medium Office | 0 | 0 | 0.014467 | 0.015849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030316 | 6.047% | Medium Office | 20.6412 | 5.588 | 1.5813 | 10.0328 | 0 | 19.6816 | 0 | 5.1049 | 0 | 0.008134 | 0 | 8.9929 | 0.94308 | 0 | 0 | 32.0934 | 104.6673 | 6.047%
Large Office | 0.21522 | 0.038475 | 0.01071 | 0.035305 | 0.037841 | 0.29212 | 0.025422 | 0.13843 | 0 | 0.032705 | 0 | 0.10751 | 0.004535 | 0 | 0.84214 | 0.30216 | 2.0826 | 3.327% | Large Office | 7.2511 | 1.2963 | 1.071 | 3.4086 | 1.2749 | 9.8421 | 0.85651 | 4.6639 | 0 | 1.1019 | 0 | 3.6222 | 0.15279 | 0 | 28.3732 | 10.1802 | 73.0946 | 3.327% | Large Office | 2.1246 | 0.37982 | 0 | 0.018156 | 0.37355 | 2.8837 | 0.25096 | 1.3665 | 0 | 0.32285 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9828 | 20.1224 | 3.327% | Large Office | 0 | 0 | 0.01071 | 0.033466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044176 | 3.327% | Large Office | 22.242 | 3.9763 | 1.1706 | 3.8479 | 3.9107 | 30.1899 | 2.6273 | 14.3061 | 0 | 3.3799 | 0 | 11.1107 | 0.46868 | 0 | 87.0323 | 31.227 | 215.4894 | 3.327%
Standalone Retail | 0.50779 | 0.068757 | 0.035631 | 0.070745 | 0 | 0.19528 | 0 | 0.25841 | 0.016448 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3748 | 15.25% | Standalone Retail | 17.1082 | 2.3165 | 3.5631 | 7.0745 | 0 | 6.5792 | 0 | 8.7061 | 0.55417 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.3746 | 15.25% | Standalone Retail | 5.0127 | 0.67874 | 0 | 0 | 0 | 1.9277 | 0 | 2.5509 | 0.16237 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.5219 | 15.25% | Standalone Retail | 0 | 0 | 0.035631 | 0.070745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10638 | 15.25% | Standalone Retail | 52.4779 | 7.1057 | 3.8945 | 7.7325 | 0 | 20.1811 | 0 | 26.7053 | 1.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 142.7191 | 15.25%
Strip Mall | 0.76333 | 0.11568 | 0.078109 | 0.092782 | 0 | 0.2344 | 0 | 0.24108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6856 | 5.669% | Strip Mall | 25.7178 | 3.8975 | 2.6316 | 9.2782 | 0 | 7.8975 | 0 | 8.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.9445 | 5.669% | Strip Mall | 7.5353 | 1.142 | 0.77107 | 0 | 0 | 2.314 | 0 | 2.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.7242 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.092782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092782 | 5.669% | Strip Mall | 78.8871 | 11.9553 | 8.0723 | 10.1411 | 0 | 24.2249 | 0 | 24.9143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 174.758 | 5.669%
Primary School | 0.307 | 0.016881 | 0.024471 | 0.079251 | 0 | 0.25997 | 0 | 0.15103 | 0.037928 | 0.00093886 | 0.051607 | 0 | 0.010319 | 0.10323 | 0 | 0.41273 | 1.4553 | 4.994% | Primary School | 10.3434 | 0.56876 | 1.7953 | 7.9251 | 0 | 8.7587 | 0 | 5.0884 | 1.2779 | 0.031632 | 1.7387 | 0 | 0.34768 | 6.5458 | 0 | 13.9054 | 58.3269 | 4.994% | Primary School | 3.0306 | 0.16665 | 0.09703 | 0 | 0 | 2.5663 | 0 | 1.4909 | 0.37441 | 0.0092681 | 0.50945 | 0 | 0.10187 | 0.56229 | 0 | 4.0743 | 12.9831 | 4.994% | Primary School | 0 | 0 | 0.014642 | 0.079251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14016 | 4.994% | Primary School | 31.7275 | 1.7446 | 2.6162 | 8.6622 | 0 | 26.8665 | 0 | 15.6084 | 3.9197 | 0.097027 | 5.3334 | 0 | 1.0665 | 10.9436 | 0 | 42.6538 | 151.2394 | 4.994%
Secondary School | 0.28426 | 0.015715 | 0.042057 | 0.049631 | 0 | 0.29791 | 0 | 0.13697 | 0.032326 | 0.0079145 | 0.02813 | 0.0088025 | 0.005922 | 0.072419 | 0 | 0.28192 | 1.264 | 10.36% | Secondary School | 9.5772 | 0.52948 | 2.8385 | 4.9631 | 0 | 10.0371 | 0 | 4.6147 | 1.0891 | 0.26665 | 0.94774 | 0.29657 | 0.19952 | 4.0625 | 0 | 9.4984 | 48.9207 | 10.36% | Secondary School | 2.8061 | 0.15514 | 0.20354 | 0 | 0 | 2.9409 | 0 | 1.3521 | 0.31911 | 0.078129 | 0.27769 | 0.086895 | 0.05846 | 0.47333 | 0 | 2.783 | 11.5344 | 10.36% | Secondary School | 0 | 0 | 0.021439 | 0.049631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.095541 | 10.36% | Secondary School | 29.3774 | 1.6241 | 4.4741 | 5.4247 | 0 | 30.7879 | 0 | 14.1551 | 3.3408 | 0.81793 | 2.9071 | 0.9097 | 0.61202 | 7.6299 | 0 | 29.1356 | 131.1964 | 10.36%
Outpatient Healthcare | 0.37216 | 0.077156 | 0.056466 | 0.38331 | 0.096876 | 0.5829 | 0 | 0.28688 | 0.0029554 | 0.0018838 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.1644 | 4.371% | Outpatient Healthcare | 12.5387 | 2.5995 | 5.6466 | 23.146 | 3.2639 | 19.6387 | 0 | 9.6653 | 0.099572 | 0.063468 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 123.4801 | 4.371% | Outpatient Healthcare | 3.6738 | 0.76166 | 0 | 2.2607 | 0.95633 | 5.7541 | 0 | 2.8319 | 0.029175 | 0.018596 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 28.7265 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.056466 | 0.1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25437 | 4.371% | Outpatient Healthcare | 38.4613 | 7.9738 | 6.1718 | 40.5323 | 10.0118 | 60.2402 | 0 | 29.6476 | 0.30543 | 0.19468 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 328.5409 | 4.371%
Hospital | 0.41794 | 0.024723 | 0.051802 | 0.37364 | 0.15295 | 0.30912 | 0.035546 | 0.34835 | 0.02223 | 0.069945 | 0.031067 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.0532 | 3.448% | Hospital | 14.081 | 0.83296 | 4.9757 | 28.7195 | 5.1533 | 10.4148 | 1.1976 | 11.7366 | 0.74897 | 2.3566 | 1.0467 | 9.8645 | 0.40737 | 16.4378 | 0 | 21.5211 | 129.4944 | 3.448% | Hospital | 4.1257 | 0.24406 | 0.030453 | 1.2869 | 1.5099 | 3.0516 | 0.35089 | 3.4388 | 0.21945 | 0.69048 | 0.30669 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 26.176 | 3.448% | Hospital | 0 | 0 | 0.048717 | 0.24327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40157 | 3.448% | Hospital | 43.1922 | 2.555 | 5.6436 | 40.0627 | 15.8074 | 31.9467 | 3.6735 | 36.001 | 2.2974 | 7.2286 | 3.2107 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 317.9276 | 3.448%
Small Hotel | 0.27062 | 0.042854 | 0.12969 | 0.11059 | 0 | 0.21914 | 0 | 0.18327 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4338 | 1.721% | Small Hotel | 9.1178 | 1.4438 | 12.9694 | 4.62 | 0 | 7.3833 | 0 | 6.1748 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.9316 | 1.721% | Small Hotel | 2.6715 | 0.42304 | 0 | 0.95857 | 0 | 2.1633 | 0 | 1.8092 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.8274 | 1.721% | Small Hotel | 0 | 0 | 0.12969 | 0.013484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23565 | 1.721% | Small Hotel | 27.968 | 4.4288 | 14.1756 | 11.509 | 0 | 22.6477 | 0 | 18.9408 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 149.5778 | 1.721%
Large Hotel | 0.29253 | 0.056718 | 0.18151 | 0.11568 | 0 | 0.43676 | 0 | 0.18975 | 0.037212 | 0.021037 | 0.024189 | 0.21947 | 0.0075745 | 0.27391 | 0 | 0.26025 | 2.1166 | 4.951% | Large Hotel | 9.8557 | 1.9109 | 16.7642 | 11.5675 | 0 | 14.7153 | 0 | 6.3931 | 1.2537 | 0.70878 | 0.81497 | 7.3943 | 0.2552 | 18.4346 | 0 | 8.7683 | 98.8365 | 4.951% | Large Hotel | 2.8877 | 0.5599 | 0.2064 | 0 | 0 | 4.3116 | 0 | 1.8732 | 0.36734 | 0.20767 | 0.23879 | 2.1665 | 0.074773 | 1.3333 | 0 | 2.5691 | 16.7963 | 4.951% | Large Hotel | 0 | 0 | 0.1606 | 0.11568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41511 | 4.951% | Large Hotel | 30.2314 | 5.8616 | 19.7141 | 12.6433 | 0 | 45.138 | 0 | 19.6103 | 3.8457 | 2.1741 | 2.4999 | 22.6813 | 0.7828 | 29.1339 | 0 | 26.8962 | 221.2125 | 4.951%
Quick-service Restaurant | 0.39235 | 0.1728 | 0.67168 | 1.3206 | 0 | 0.82149 | 0 | 1.1817 | 0 | 0 | 1.2196 | 0 | 0 | 4.435 | 0 | 0 | 10.2152 | 0.5866% | Quick-service Restaurant | 13.2189 | 5.8218 | 67.1684 | 132.0622 | 0 | 27.6776 | 0 | 39.8148 | 0 | 0 | 41.089 | 0 | 0 | 269.3289 | 0 | 0 | 596.1816 | 0.5866% | Quick-service Restaurant | 3.8732 | 1.7058 | 0 | 0 | 0 | 8.1095 | 0 | 11.6657 | 0 | 0 | 12.0391 | 0 | 0 | 25.9296 | 0 | 0 | 63.3229 | 0.5866% | Quick-service Restaurant | 0 | 0 | 0.67168 | 1.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8006 | 0.5866% | Quick-service Restaurant | 40.548 | 17.858 | 73.4151 | 144.344 | 0 | 84.8986 | 0 | 122.1287 | 0 | 0 | 126.037 | 0 | 0 | 469.1065 | 0 | 0 | 1078.3358 | 0.5866%
Full-service Restaurant | 0.39218 | 0.16886 | 0.91799 | 0.84055 | 0 | 0.6705 | 0 | 0.79228 | 0 | 0.0023014 | 0.54646 | 0 | 0 | 2.9429 | 0 | 0 | 7.2741 | 0.6597% | Full-service Restaurant | 13.2131 | 5.6893 | 66.2157 | 84.0554 | 0 | 22.5901 | 0 | 26.6933 | 0 | 0.077539 | 18.4111 | 0 | 0 | 152.8155 | 0 | 0 | 389.7611 | 0.6597% | Full-service Restaurant | 3.8714 | 1.667 | 3.8088 | 0 | 0 | 6.6189 | 0 | 7.8211 | 0 | 0.022719 | 5.3945 | 0 | 0 | 21.0625 | 0 | 0 | 50.2669 | 0.6597% | Full-service Restaurant | 0 | 0 | 0.53217 | 0.84055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.182 | 0.6597% | Full-service Restaurant | 40.53 | 17.4515 | 98.0396 | 91.8725 | 0 | 69.2934 | 0 | 81.8796 | 0 | 0.23785 | 56.4746 | 0 | 0 | 308.9599 | 0 | 0 | 764.7389 | 0.6597%
Mid-rise Apartment | 0.1376 | 0.032866 | 0.31321 | 0.054862 | 0 | 0.15099 | 0 | 0.18035 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2964 | 7.321% | Mid-rise Apartment | 4.6361 | 1.1073 | 10.5526 | 5.4862 | 0 | 5.0872 | 0 | 6.0764 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 47.3157 | 7.321% | Mid-rise Apartment | 1.3584 | 0.32444 | 3.0919 | 0 | 0 | 1.4906 | 0 | 1.7804 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.256 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.054862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054862 | 7.321% | Mid-rise Apartment | 14.221 | 3.3966 | 32.3694 | 5.9964 | 0 | 15.6047 | 0 | 18.6387 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 134.3048 | 7.321%
High-rise Apartment | 0.13891 | 0.056198 | 0.11574 | 0.073858 | 0 | 0.2447 | 0.011197 | 0.1961 | 0 | 0.01733 | 0 | 0.052954 | 0.0069446 | 0 | 0 | 0.32437 | 1.2383 | 8.967% | High-rise Apartment | 4.6802 | 1.8934 | 11.5738 | 5.0894 | 0 | 8.2444 | 0.37725 | 6.6071 | 0 | 0.58386 | 0 | 1.7841 | 0.23397 | 0 | 0 | 10.9284 | 51.996 | 8.967% | High-rise Apartment | 1.3713 | 0.55477 | 0 | 0.34188 | 0 | 2.4156 | 0.11053 | 1.9359 | 0 | 0.17107 | 0 | 0.52274 | 0.068554 | 0 | 0 | 3.202 | 10.6944 | 8.967% | High-rise Apartment | 0 | 0 | 0.11574 | 0.039226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15496 | 8.967% | High-rise Apartment | 14.3562 | 5.8079 | 12.6502 | 7.8665 | 0 | 25.2891 | 1.1572 | 20.2667 | 0 | 1.791 | 0 | 5.4726 | 0.7177 | 0 | 0 | 33.522 | 128.897 | 8.967%
Warehouse | 0.17373 | 0.045269 | 0.013416 | 0.068505 | 0 | 0.014427 | 0 | 0.021008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.41046 | 16.72% | Warehouse | 5.8533 | 1.5252 | 0.45199 | 6.8505 | 0 | 0.48607 | 0 | 0.70779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 18.3715 | 16.72% | Warehouse | 1.715 | 0.44688 | 0.13243 | 0 | 0 | 0.14242 | 0 | 0.20738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.3757 | 16.72% | Warehouse | 0 | 0 | 0 | 0.068505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068505 | 16.72% | Warehouse | 17.9546 | 4.6784 | 1.3864 | 7.4876 | 0 | 1.491 | 0 | 2.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 42.8274 | 16.72%
US Weighted | 0.30641 | 0.052393 | 0.082857 | 0.10657 | 0.010767 | 0.22222 | 0.0030755 | 0.17268 | 0.010491 | 0.0070674 | 0.018519 | 0.065172 | 0.0032462 | 0.082947 | 0.02802 | 0.27686 | 1.4493 | 100% | US Weighted | 10.3236 | 1.7652 | 5.5618 | 8.9541 | 0.36276 | 7.4871 | 0.10362 | 5.8178 | 0.35344 | 0.23811 | 0.62395 | 2.1958 | 0.10937 | 4.9851 | 0.94403 | 9.4543 | 59.2801 | 100% | US Weighted | 3.0248 | 0.51721 | 0.40552 | 0.25349 | 0.10629 | 2.1937 | 0.03036 | 1.7046 | 0.10356 | 0.069767 | 0.18282 | 0.64336 | 0.032046 | 0.49271 | 0.2766 | 2.7143 | 12.7511 | 100% | US Weighted | 0 | 0 | 0.041778 | 0.080889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.15761 | 100% | US Weighted | 31.6667 | 5.4147 | 8.8117 | 11.495 | 1.1127 | 22.9661 | 0.31784 | 17.8456 | 1.0842 | 0.73039 | 1.9139 | 6.7353 | 0.33549 | 8.7689 | 2.8957 | 28.6241 | 150.7182 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.36291 | 0.12719 | 0.092263 | 0.035691 | 0 | 0.15605 | 0 | 0.13046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1746 | 5.608% | Small Office | 12.2271 | 4.2852 | 3.1085 | 1.6997 | 0 | 5.2576 | 0 | 4.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0714 | 5.608% | Small Office | 3.5825 | 1.2556 | 0.91079 | 0.27829 | 0 | 1.5405 | 0 | 1.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5212 | 5.608% | Small Office | 0 | 0 | 0 | 0.0074994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074994 | 5.608% | Small Office | 37.5056 | 13.1444 | 9.535 | 3.7331 | 0 | 16.1272 | 0 | 13.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 121.435 | 5.608%
Medium Office | 0.29004 | 0.11821 | 0.014763 | 0.13367 | 0 | 0.25229 | 0 | 0.054388 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017712 | 0 | 0 | 0.33648 | 1.3094 | 6.047% | Medium Office | 9.772 | 3.9826 | 1.4763 | 5.8577 | 0 | 8.5001 | 0 | 1.8324 | 0 | 0.0026517 | 0 | 3.093 | 0.59674 | 0 | 0 | 11.3367 | 46.4501 | 6.047% | Medium Office | 2.8632 | 1.1669 | 0 | 1.118 | 0 | 2.4905 | 0 | 0.5369 | 0 | 0.00077696 | 0 | 0.90624 | 0.17484 | 0 | 0 | 3.3216 | 12.579 | 6.047% | Medium Office | 0 | 0 | 0.014763 | 0.020421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035184 | 6.047% | Medium Office | 29.9747 | 12.2163 | 1.6136 | 13.936 | 0 | 26.0733 | 0 | 5.6208 | 0 | 0.008134 | 0 | 9.4875 | 1.8304 | 0 | 0 | 34.7743 | 135.5351 | 6.047%
Large Office | 0.29004 | 0.055673 | 0.010785 | 0.069173 | 0.0063533 | 0.37604 | 0.047071 | 0.14764 | 0 | 0.05818 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.353 | 3.327% | Large Office | 9.772 | 1.8757 | 1.0785 | 6.5616 | 0.21405 | 12.6695 | 1.5859 | 4.9744 | 0 | 1.9602 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 84.2235 | 3.327% | Large Office | 2.8632 | 0.54958 | 0 | 0.052955 | 0.062718 | 3.7122 | 0.46467 | 1.4575 | 0 | 0.57433 | 0 | 1.0899 | 0.08012 | 0 | 8.3133 | 3.2714 | 22.4919 | 3.327% | Large Office | 0 | 0 | 0.010785 | 0.063809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074594 | 3.327% | Large Office | 29.9749 | 5.7536 | 1.1788 | 7.5287 | 0.65659 | 38.8626 | 4.8646 | 15.2585 | 0 | 6.0127 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 243.6207 | 3.327%
Standalone Retail | 0.56074 | 0.13109 | 0.036401 | 0.11532 | 0 | 0.29702 | 0 | 0.37375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7367 | 15.25% | Standalone Retail | 18.8922 | 4.4168 | 3.6401 | 11.5321 | 0 | 10.0072 | 0 | 12.5923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.5738 | 15.25% | Standalone Retail | 5.5354 | 1.2941 | 0 | 0 | 0 | 2.9321 | 0 | 3.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6467 | 15.25% | Standalone Retail | 0 | 0 | 0.036401 | 0.11532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15172 | 15.25% | Standalone Retail | 57.9503 | 13.5481 | 3.9786 | 12.6046 | 0 | 30.6962 | 0 | 38.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 180.3883 | 15.25%
Strip Mall | 0.85202 | 0.21058 | 0.085052 | 0.099783 | 0 | 0.3414 | 0 | 0.30044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0502 | 5.669% | Strip Mall | 28.706 | 7.0948 | 2.8655 | 9.9783 | 0 | 11.5022 | 0 | 10.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.6928 | 5.669% | Strip Mall | 8.4109 | 2.0788 | 0.8396 | 0 | 0 | 3.3701 | 0 | 2.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2543 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.099783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099783 | 5.669% | Strip Mall | 88.0533 | 21.7628 | 8.7898 | 10.9063 | 0 | 35.282 | 0 | 31.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 212.4801 | 5.669%
Primary School | 0.46049 | 0.031672 | 0.025387 | 0.12482 | 0 | 0.36377 | 0 | 0.16863 | 0.042085 | 0.00078202 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.8082 | 4.994% | Primary School | 15.5148 | 1.0671 | 1.8331 | 12.4821 | 0 | 12.2559 | 0 | 5.6814 | 1.4179 | 0.026348 | 1.7455 | 0 | 0.61547 | 6.5458 | 0 | 14.0576 | 73.2431 | 4.994% | Primary School | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.591 | 0 | 1.6646 | 0.41545 | 0.0077199 | 0.51144 | 0 | 0.18033 | 0.56229 | 0 | 4.1189 | 16.0152 | 4.994% | Primary School | 0 | 0 | 0.014746 | 0.12482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.18584 | 4.994% | Primary School | 47.5904 | 3.2732 | 2.7114 | 13.643 | 0 | 37.594 | 0 | 17.4271 | 4.3493 | 0.080819 | 5.3543 | 0 | 1.8879 | 10.9436 | 0 | 43.1205 | 187.9754 | 4.994%
Secondary School | 0.43965 | 0.028922 | 0.042081 | 0.077919 | 0 | 0.40373 | 0 | 0.18222 | 0.04763 | 0.022544 | 0.028205 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6492 | 10.36% | Secondary School | 14.8126 | 0.97442 | 2.8409 | 7.7919 | 0 | 13.6023 | 0 | 6.1394 | 1.6047 | 0.75954 | 0.95026 | 0.34054 | 0.35679 | 4.0625 | 0 | 9.5412 | 63.777 | 10.36% | Secondary School | 4.3401 | 0.28551 | 0.20354 | 0 | 0 | 3.9855 | 0 | 1.7988 | 0.47019 | 0.22254 | 0.27843 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 15.0578 | 10.36% | Secondary School | 0 | 0 | 0.021462 | 0.077919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12385 | 10.36% | Secondary School | 45.4364 | 2.989 | 4.4767 | 8.5166 | 0 | 41.7238 | 0 | 18.832 | 4.9224 | 2.3298 | 2.9148 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 171.1773 | 10.36%
Outpatient Healthcare | 0.42008 | 0.15592 | 0.05724 | 0.6701 | 0.1241 | 0.7853 | 0 | 0.37453 | 0 | 0.0021423 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9069 | 4.371% | Outpatient Healthcare | 14.1533 | 5.2532 | 5.724 | 35.2107 | 4.1813 | 26.4581 | 0 | 12.6187 | 0 | 0.072177 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.9499 | 4.371% | Outpatient Healthcare | 4.1469 | 1.5392 | 0 | 4.7341 | 1.2251 | 7.7522 | 0 | 3.6973 | 0 | 0.021148 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.691 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.05724 | 0.19053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29138 | 4.371% | Outpatient Healthcare | 43.4142 | 16.1138 | 6.2564 | 70.3869 | 12.8257 | 81.158 | 0 | 38.7068 | 0 | 0.2214 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 405.4964 | 4.371%
Hospital | 0.48738 | 0.030451 | 0.052276 | 0.59829 | 0.20717 | 0.47027 | 0.077453 | 0.5042 | 0 | 0.13213 | 0.031174 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.8362 | 3.448% | Hospital | 16.4205 | 1.026 | 5.0054 | 52.7178 | 6.9798 | 15.8442 | 2.6095 | 16.9872 | 0 | 4.4516 | 1.0503 | 9.9723 | 0.68134 | 16.4378 | 0 | 22.1353 | 172.3191 | 3.448% | Hospital | 4.8112 | 0.3006 | 0.033081 | 1.0587 | 2.0451 | 4.6424 | 0.76459 | 4.9773 | 0 | 1.3043 | 0.30774 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.4578 | 3.448% | Hospital | 0 | 0 | 0.048925 | 0.49105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64955 | 3.448% | Hospital | 50.3685 | 3.147 | 5.6938 | 64.7548 | 21.4099 | 48.6008 | 8.0045 | 52.1069 | 0 | 13.6549 | 3.2217 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 400.3269 | 3.448%
Small Hotel | 0.32434 | 0.06204 | 0.13 | 0.12099 | 0 | 0.25144 | 0 | 0.19289 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5664 | 1.721% | Small Hotel | 10.9277 | 2.0902 | 12.9996 | 4.9113 | 0 | 8.4713 | 0 | 6.4987 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.3612 | 1.721% | Small Hotel | 3.2018 | 0.61244 | 0 | 1.0701 | 0 | 2.4821 | 0 | 1.9041 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.1426 | 1.721% | Small Hotel | 0 | 0 | 0.13 | 0.012592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23506 | 1.721% | Small Hotel | 33.5198 | 6.4116 | 14.2086 | 12.5787 | 0 | 25.985 | 0 | 19.9344 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 163.2818 | 1.721%
Large Hotel | 0.33467 | 0.07052 | 0.18202 | 0.24177 | 0 | 0.53511 | 0 | 0.19548 | 0 | 0.046941 | 0.024314 | 0.22539 | 0.013193 | 0.27391 | 0 | 0.26162 | 2.4049 | 4.951% | Large Hotel | 11.2757 | 2.3759 | 16.7819 | 24.1765 | 0 | 18.0288 | 0 | 6.586 | 0 | 1.5815 | 0.81918 | 7.5938 | 0.44451 | 18.4346 | 0 | 8.8145 | 116.9129 | 4.951% | Large Hotel | 3.3038 | 0.69615 | 0.21137 | 0 | 0 | 5.2824 | 0 | 1.9297 | 0 | 0.46339 | 0.24002 | 2.225 | 0.13024 | 1.3333 | 0 | 2.5827 | 18.3981 | 4.951% | Large Hotel | 0 | 0 | 0.1606 | 0.24177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.54121 | 4.951% | Large Hotel | 34.5873 | 7.288 | 19.7669 | 26.4249 | 0 | 55.3019 | 0 | 20.202 | 0 | 4.8512 | 2.5128 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 251.7635 | 4.951%
Quick-service Restaurant | 0.84473 | 0.30807 | 0.67168 | 1.2767 | 0 | 1.1315 | 0 | 1.4887 | 0 | 0 | 1.22 | 0 | 0 | 4.4383 | 0 | 0 | 11.3796 | 0.5866% | Quick-service Restaurant | 28.4604 | 10.3794 | 67.1684 | 127.6707 | 0 | 38.1207 | 0 | 50.1562 | 0 | 0 | 41.1029 | 0 | 0 | 269.4388 | 0 | 0 | 632.4975 | 0.5866% | Quick-service Restaurant | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.1694 | 0 | 14.6958 | 0 | 0 | 12.0432 | 0 | 0 | 25.9618 | 0 | 0 | 75.2502 | 0.5866% | Quick-service Restaurant | 0 | 0 | 0.67168 | 1.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.7567 | 0.5866% | Quick-service Restaurant | 87.2998 | 31.8381 | 73.4151 | 139.5441 | 0 | 116.9321 | 0 | 153.85 | 0 | 0 | 126.0798 | 0 | 0 | 469.4437 | 0 | 0 | 1198.4026 | 0.5866%
Full-service Restaurant | 0.94947 | 0.29693 | 0.92972 | 0.86576 | 0 | 0.97855 | 0 | 1.2692 | 0 | 0.0023014 | 0.54481 | 0 | 0 | 2.945 | 0 | 0 | 8.7817 | 0.6597% | Full-service Restaurant | 31.9893 | 10.004 | 66.6533 | 86.5756 | 0 | 32.969 | 0 | 42.76 | 0 | 0.077539 | 18.3555 | 0 | 0 | 152.8844 | 0 | 0 | 442.2687 | 0.6597% | Full-service Restaurant | 9.3729 | 2.9312 | 3.9182 | 0 | 0 | 9.6599 | 0 | 12.5287 | 0 | 0.022719 | 5.3782 | 0 | 0 | 21.0827 | 0 | 0 | 64.8945 | 0.6597% | Full-service Restaurant | 0 | 0 | 0.53281 | 0.86576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2079 | 0.6597% | Full-service Restaurant | 98.1244 | 30.6864 | 99.2552 | 94.6272 | 0 | 101.1297 | 0 | 131.1629 | 0 | 0.23785 | 56.3041 | 0 | 0 | 309.1713 | 0 | 0 | 920.699 | 0.6597%
Mid-rise Apartment | 0.1263 | 0.060824 | 0.3133 | 0.074881 | 0 | 0.15226 | 0 | 0.19351 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3528 | 7.321% | Mid-rise Apartment | 4.2551 | 2.0493 | 10.5555 | 7.4881 | 0 | 5.1298 | 0 | 6.5198 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.5427 | 7.321% | Mid-rise Apartment | 1.2468 | 0.60043 | 3.0928 | 0 | 0 | 1.503 | 0 | 1.9103 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.615 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.074881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074881 | 7.321% | Mid-rise Apartment | 13.0522 | 6.286 | 32.3782 | 8.1845 | 0 | 15.7352 | 0 | 19.999 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 140.251 | 7.321%
High-rise Apartment | 0.11995 | 0.071191 | 0.1158 | 0.11381 | 0 | 0.2464 | 0.011528 | 0.21059 | 0 | 0.022911 | 0 | 0.054385 | 0.012067 | 0 | 0 | 0.32502 | 1.3036 | 8.967% | High-rise Apartment | 4.0414 | 2.3985 | 11.5803 | 7.9784 | 0 | 8.3016 | 0.38839 | 7.095 | 0 | 0.77192 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 55.7447 | 8.967% | High-rise Apartment | 1.1841 | 0.70277 | 0 | 0.50656 | 0 | 2.4324 | 0.1138 | 2.0788 | 0 | 0.22617 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 11.1091 | 8.967% | High-rise Apartment | 0 | 0 | 0.1158 | 0.062495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1783 | 8.967% | High-rise Apartment | 12.3966 | 7.3573 | 12.6572 | 12.1339 | 0 | 25.4644 | 1.1914 | 21.7635 | 0 | 2.3678 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 135.7889 | 8.967%
Warehouse | 0.26058 | 0.066751 | 0.013857 | 0.084382 | 0 | 0.021034 | 0 | 0.036092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.558 | 16.72% | Warehouse | 8.7793 | 2.2489 | 0.46686 | 8.4382 | 0 | 0.70868 | 0 | 1.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 24.3951 | 16.72% | Warehouse | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.20764 | 0 | 0.35629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6754 | 16.72% | Warehouse | 0 | 0 | 0 | 0.084382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084382 | 16.72% | Warehouse | 26.9299 | 6.8984 | 1.4321 | 9.223 | 0 | 2.1738 | 0 | 3.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 58.1695 | 16.72%
US Weighted | 0.38202 | 0.09083 | 0.083689 | 0.1569 | 0.012779 | 0.29238 | 0.0052704 | 0.2198 | 0.0070367 | 0.013361 | 0.018539 | 0.066913 | 0.005783 | 0.082979 | 0.02802 | 0.2823 | 1.7486 | 100% | US Weighted | 12.871 | 3.0602 | 5.6032 | 13.0557 | 0.43054 | 9.8509 | 0.17757 | 7.4055 | 0.23708 | 0.45016 | 0.6246 | 2.2544 | 0.19484 | 4.9862 | 0.94403 | 9.6374 | 71.7834 | 100% | US Weighted | 3.7712 | 0.89665 | 0.41174 | 0.39222 | 0.12615 | 2.8863 | 0.052028 | 2.1698 | 0.069464 | 0.1319 | 0.18301 | 0.66054 | 0.057088 | 0.49303 | 0.2766 | 2.7679 | 15.3457 | 100% | US Weighted | 0 | 0 | 0.04198 | 0.11717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.19409 | 100% | US Weighted | 39.4808 | 9.387 | 8.8989 | 16.9129 | 1.3206 | 30.2169 | 0.54468 | 22.7158 | 0.72722 | 1.3808 | 1.9159 | 6.9152 | 0.59766 | 8.7723 | 2.8957 | 29.1857 | 181.868 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.36291 | 0.12719 | 0.092263 | 0.050289 | 0 | 0.19846 | 0 | 0.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2363 | 5.608% | Small Office | 12.2271 | 4.2852 | 3.1085 | 2.41 | 0 | 6.6864 | 0 | 4.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.3704 | 5.608% | Small Office | 3.5825 | 1.2556 | 0.91079 | 0.38989 | 0 | 1.9591 | 0 | 1.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.0983 | 5.608% | Small Office | 0 | 0 | 0 | 0.010793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010793 | 5.608% | Small Office | 37.5056 | 13.1444 | 9.535 | 5.2615 | 0 | 20.5101 | 0 | 13.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 127.8366 | 5.608%
Medium Office | 0.29004 | 0.11821 | 0.014764 | 0.18081 | 0 | 0.26519 | 0 | 0.063859 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017711 | 0 | 0 | 0.33648 | 1.3789 | 6.047% | Medium Office | 9.772 | 3.9826 | 1.4764 | 8.0745 | 0 | 8.9346 | 0 | 2.1515 | 0 | 0.0026517 | 0 | 3.093 | 0.59671 | 0 | 0 | 11.3367 | 49.4206 | 6.047% | Medium Office | 2.8632 | 1.1669 | 0 | 1.4898 | 0 | 2.6178 | 0 | 0.6304 | 0 | 0.00077696 | 0 | 0.90624 | 0.17483 | 0 | 0 | 3.3216 | 13.1716 | 6.047% | Medium Office | 0 | 0 | 0.014764 | 0.029899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044663 | 6.047% | Medium Office | 29.9747 | 12.2163 | 1.6137 | 18.8645 | 0 | 27.4061 | 0 | 6.5996 | 0 | 0.008134 | 0 | 9.4875 | 1.8303 | 0 | 0 | 34.7743 | 142.7753 | 6.047%
Large Office | 0.29004 | 0.055673 | 0.010786 | 0.091268 | 0.0065171 | 0.38285 | 0.049194 | 0.15071 | 0 | 0.060583 | 0 | 0.11041 | 0.0081161 | 0 | 0.84214 | 0.33139 | 2.3897 | 3.327% | Large Office | 9.772 | 1.8757 | 1.0786 | 8.7746 | 0.21957 | 12.8987 | 1.6574 | 5.0778 | 0 | 2.0411 | 0 | 3.7199 | 0.27344 | 0 | 28.3732 | 11.1651 | 86.9272 | 3.327% | Large Office | 2.8632 | 0.54958 | 0 | 0.052428 | 0.064335 | 3.7793 | 0.48563 | 1.4878 | 0 | 0.59805 | 0 | 1.0899 | 0.080119 | 0 | 8.3133 | 3.2714 | 22.6351 | 3.327% | Large Office | 0 | 0 | 0.010786 | 0.085957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096743 | 3.327% | Large Office | 29.9749 | 5.7536 | 1.1789 | 9.9439 | 0.67352 | 39.5658 | 5.0841 | 15.5756 | 0 | 6.261 | 0 | 11.4106 | 0.83877 | 0 | 87.0323 | 34.2481 | 247.5411 | 3.327%
Standalone Retail | 0.56074 | 0.13109 | 0.036414 | 0.17476 | 0 | 0.3464 | 0 | 0.46217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.934 | 15.25% | Standalone Retail | 18.8922 | 4.4168 | 3.6414 | 17.4762 | 0 | 11.6708 | 0 | 15.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.1618 | 15.25% | Standalone Retail | 5.5354 | 1.2941 | 0 | 0 | 0 | 3.4195 | 0 | 4.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0069 | 15.25% | Standalone Retail | 0 | 0 | 0.036414 | 0.17476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21118 | 15.25% | Standalone Retail | 57.9503 | 13.5481 | 3.9801 | 19.1015 | 0 | 35.7991 | 0 | 47.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 201.1271 | 15.25%
Strip Mall | 0.79045 | 0.21058 | 0.085185 | 0.17178 | 0 | 0.37521 | 0 | 0.32996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1241 | 5.669% | Strip Mall | 26.6317 | 7.0948 | 2.87 | 17.1776 | 0 | 12.6416 | 0 | 11.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 82.9563 | 5.669% | Strip Mall | 7.8031 | 2.0788 | 0.84092 | 0 | 0 | 3.704 | 0 | 3.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2732 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.17178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17178 | 5.669% | Strip Mall | 81.6905 | 21.7628 | 8.8036 | 18.7752 | 0 | 38.777 | 0 | 34.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 220.5458 | 5.669%
Primary School | 0.46049 | 0.031672 | 0.025395 | 0.15915 | 0 | 0.39183 | 0 | 0.19339 | 0.051266 | 0.00097001 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.9047 | 4.994% | Primary School | 15.5148 | 1.0671 | 1.8339 | 15.9148 | 0 | 13.2015 | 0 | 6.5155 | 1.7272 | 0.032681 | 1.7455 | 0 | 0.61549 | 6.5458 | 0 | 14.0576 | 78.772 | 4.994% | Primary School | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.8681 | 0 | 1.9091 | 0.50608 | 0.0095756 | 0.51144 | 0 | 0.18034 | 0.56229 | 0 | 4.1189 | 16.6292 | 4.994% | Primary School | 0 | 0 | 0.014754 | 0.15915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22017 | 4.994% | Primary School | 47.5904 | 3.2732 | 2.7123 | 17.3949 | 0 | 40.4946 | 0 | 19.9859 | 5.2982 | 0.10025 | 5.3542 | 0 | 1.888 | 10.9436 | 0 | 43.1205 | 198.156 | 4.994%
Secondary School | 0.43965 | 0.028922 | 0.042086 | 0.10791 | 0 | 0.44641 | 0 | 0.24316 | 0.073218 | 0.024298 | 0.0282 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.8102 | 10.36% | Secondary School | 14.8126 | 0.97442 | 2.8414 | 10.7907 | 0 | 15.0403 | 0 | 8.1925 | 2.4668 | 0.81864 | 0.95009 | 0.34054 | 0.3568 | 4.0625 | 0 | 9.5412 | 71.1886 | 10.36% | Secondary School | 4.3401 | 0.28551 | 0.20355 | 0 | 0 | 4.4068 | 0 | 2.4004 | 0.72279 | 0.23986 | 0.27838 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 16.3506 | 10.36% | Secondary School | 0 | 0 | 0.021467 | 0.10791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15384 | 10.36% | Secondary School | 45.4364 | 2.989 | 4.4772 | 11.7943 | 0 | 46.1348 | 0 | 25.1299 | 7.5668 | 2.5111 | 2.9143 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 187.9898 | 10.36%
Outpatient Healthcare | 0.42008 | 0.15592 | 0.057242 | 0.79271 | 0.15057 | 0.82063 | 0 | 0.41446 | 0 | 0.0023374 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1314 | 4.371% | Outpatient Healthcare | 14.1533 | 5.2532 | 5.7242 | 40.8476 | 5.0728 | 27.6483 | 0 | 13.9638 | 0 | 0.078751 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 160.0203 | 4.371% | Outpatient Healthcare | 4.1469 | 1.5392 | 0 | 5.7203 | 1.4863 | 8.101 | 0 | 4.0914 | 0 | 0.023074 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.6831 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.057242 | 0.21325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.31409 | 4.371% | Outpatient Healthcare | 43.4142 | 16.1138 | 6.2565 | 83.1931 | 15.5604 | 84.8089 | 0 | 42.8327 | 0 | 0.24156 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 428.8344 | 4.371%
Hospital | 0.48738 | 0.030451 | 0.052268 | 0.55914 | 0.20787 | 0.47749 | 0.074972 | 0.51945 | 0 | 0.12772 | 0.03114 | 0.29599 | 0.020222 | 0.27223 | 0 | 0.657 | 3.8133 | 3.448% | Hospital | 16.4205 | 1.026 | 5.0046 | 48.7892 | 7.0036 | 16.0876 | 2.526 | 17.5013 | 0 | 4.303 | 1.0492 | 9.9723 | 0.68131 | 16.4378 | 0 | 22.1353 | 168.9374 | 3.448% | Hospital | 4.8112 | 0.3006 | 0.033092 | 1.0607 | 2.0521 | 4.7137 | 0.7401 | 5.1279 | 0 | 1.2608 | 0.3074 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.6203 | 3.448% | Hospital | 0 | 0 | 0.048916 | 0.45169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61018 | 3.448% | Hospital | 50.3685 | 3.147 | 5.693 | 60.4739 | 21.4831 | 49.3473 | 7.7481 | 53.6837 | 0 | 13.199 | 3.2182 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 397.7258 | 3.448%
Small Hotel | 0.32434 | 0.06204 | 0.13005 | 0.20947 | 0 | 0.27029 | 0 | 0.19398 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6749 | 1.721% | Small Hotel | 10.9277 | 2.0902 | 13.0049 | 9.3443 | 0 | 9.1065 | 0 | 6.5356 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.4716 | 1.721% | Small Hotel | 3.2018 | 0.61244 | 0 | 1.7273 | 0 | 2.6682 | 0 | 1.9149 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.9968 | 1.721% | Small Hotel | 0 | 0 | 0.13005 | 0.034491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25701 | 1.721% | Small Hotel | 33.5198 | 6.4116 | 14.2143 | 21.853 | 0 | 27.9335 | 0 | 20.0476 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 174.6234 | 1.721%
Large Hotel | 0.33467 | 0.07052 | 0.18204 | 0.23248 | 0 | 0.54367 | 0 | 0.23284 | 0.076267 | 0.053122 | 0.024224 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.524 | 4.951% | Large Hotel | 11.2757 | 2.3759 | 16.784 | 23.248 | 0 | 18.3173 | 0 | 7.8447 | 2.5696 | 1.7898 | 0.81615 | 7.5938 | 0.44453 | 18.4346 | 0 | 8.8145 | 120.3085 | 4.951% | Large Hotel | 3.3038 | 0.69615 | 0.21142 | 0 | 0 | 5.367 | 0 | 2.2985 | 0.75288 | 0.5244 | 0.23913 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 19.6644 | 4.951% | Large Hotel | 0 | 0 | 0.16062 | 0.23248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.53194 | 4.951% | Large Hotel | 34.5873 | 7.288 | 19.7695 | 25.4101 | 0 | 56.1867 | 0 | 24.0629 | 7.8819 | 5.49 | 2.5035 | 23.2933 | 1.3636 | 29.1339 | 0 | 27.0379 | 264.0085 | 4.951%
Quick-service Restaurant | 0.84473 | 0.30807 | 0.67145 | 1.3603 | 0 | 1.1555 | 0 | 1.4612 | 0 | 0 | 1.2183 | 0 | 0 | 4.4383 | 0 | 0 | 11.4578 | 0.5866% | Quick-service Restaurant | 28.4604 | 10.3794 | 67.1449 | 136.0332 | 0 | 38.9292 | 0 | 49.2294 | 0 | 0 | 41.0466 | 0 | 0 | 269.4388 | 0 | 0 | 640.6619 | 0.5866% | Quick-service Restaurant | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.4063 | 0 | 14.4242 | 0 | 0 | 12.0267 | 0 | 0 | 25.9618 | 0 | 0 | 75.199 | 0.5866% | Quick-service Restaurant | 0 | 0 | 0.67145 | 1.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8401 | 0.5866% | Quick-service Restaurant | 87.2998 | 31.8381 | 73.3893 | 148.6843 | 0 | 119.4121 | 0 | 151.0071 | 0 | 0 | 125.9072 | 0 | 0 | 469.4437 | 0 | 0 | 1206.9815 | 0.5866%
Full-service Restaurant | 0.94947 | 0.29693 | 0.92814 | 1.0548 | 0 | 1.0686 | 0 | 1.3067 | 0 | 0.0023014 | 0.5525 | 0 | 0 | 2.945 | 0 | 0 | 9.1044 | 0.6597% | Full-service Restaurant | 31.9893 | 10.004 | 66.5328 | 105.4827 | 0 | 36.0027 | 0 | 44.0252 | 0 | 0.077539 | 18.6145 | 0 | 0 | 152.8844 | 0 | 0 | 465.6131 | 0.6597% | Full-service Restaurant | 9.3729 | 2.9312 | 3.9126 | 0 | 0 | 10.5488 | 0 | 12.8994 | 0 | 0.022719 | 5.4541 | 0 | 0 | 21.0827 | 0 | 0 | 66.2244 | 0.6597% | Full-service Restaurant | 0 | 0 | 0.53179 | 1.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3959 | 0.6597% | Full-service Restaurant | 98.1244 | 30.6864 | 99.0862 | 115.2926 | 0 | 110.4354 | 0 | 135.0436 | 0 | 0.23785 | 57.0985 | 0 | 0 | 309.1713 | 0 | 0 | 955.1762 | 0.6597%
Mid-rise Apartment | 0.1263 | 0.060824 | 0.31333 | 0.084013 | 0 | 0.19457 | 0 | 0.20917 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4199 | 7.321% | Mid-rise Apartment | 4.2551 | 2.0493 | 10.5565 | 8.4013 | 0 | 6.5554 | 0 | 7.0472 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 53.4099 | 7.321% | Mid-rise Apartment | 1.2468 | 0.60043 | 3.0931 | 0 | 0 | 1.9207 | 0 | 2.0648 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.1875 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.084013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084013 | 7.321% | Mid-rise Apartment | 13.0522 | 6.286 | 32.3813 | 9.1826 | 0 | 20.108 | 0 | 21.6167 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 147.2427 | 7.321%
High-rise Apartment | 0.11995 | 0.071191 | 0.1158 | 0.12529 | 0 | 0.25413 | 0.011941 | 0.22257 | 0 | 0.023958 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3363 | 8.967% | High-rise Apartment | 4.0414 | 2.3985 | 11.5802 | 8.7804 | 0 | 8.5619 | 0.40231 | 7.4988 | 0 | 0.80718 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 57.26 | 8.967% | High-rise Apartment | 1.1841 | 0.70277 | 0 | 0.55808 | 0 | 2.5086 | 0.11788 | 2.1972 | 0 | 0.2365 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 11.3696 | 8.967% | High-rise Apartment | 0 | 0 | 0.1158 | 0.068757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18456 | 8.967% | High-rise Apartment | 12.3966 | 7.3573 | 12.6572 | 13.3577 | 0 | 26.2629 | 1.2341 | 23.002 | 0 | 2.476 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 139.2006 | 8.967%
Warehouse | 0.26058 | 0.066751 | 0.013857 | 0.10565 | 0 | 0.021594 | 0 | 0.036386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.58013 | 16.72% | Warehouse | 8.7793 | 2.2489 | 0.46687 | 10.5655 | 0 | 0.72755 | 0 | 1.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 26.5512 | 16.72% | Warehouse | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.21317 | 0 | 0.35919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6838 | 16.72% | Warehouse | 0 | 0 | 0 | 0.10565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10565 | 16.72% | Warehouse | 26.9299 | 6.8984 | 1.4321 | 11.5481 | 0 | 2.2317 | 0 | 3.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 60.5829 | 16.72%
US Weighted | 0.37853 | 0.09083 | 0.083692 | 0.19134 | 0.013965 | 0.3182 | 0.0052926 | 0.24995 | 0.013922 | 0.013889 | 0.018573 | 0.066913 | 0.005783 | 0.082979 | 0.02802 | 0.2823 | 1.8442 | 100% | US Weighted | 12.7534 | 3.0602 | 5.6031 | 15.9095 | 0.47051 | 10.7208 | 0.17832 | 8.4212 | 0.46907 | 0.46793 | 0.62577 | 2.2544 | 0.19484 | 4.9862 | 0.94403 | 9.6374 | 76.6968 | 100% | US Weighted | 3.7367 | 0.89665 | 0.4118 | 0.48004 | 0.13786 | 3.1412 | 0.052247 | 2.4674 | 0.13744 | 0.1371 | 0.18335 | 0.66054 | 0.057088 | 0.49303 | 0.2766 | 2.7679 | 16.037 | 100% | US Weighted | 0 | 0 | 0.041976 | 0.14271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033036 | 0 | 0.0019058 | 0.21963 | 100% | US Weighted | 39.12 | 9.387 | 8.8991 | 20.624 | 1.4433 | 32.885 | 0.54697 | 25.8315 | 1.4388 | 1.4353 | 1.9195 | 6.9152 | 0.59766 | 8.7723 | 2.8957 | 29.1857 | 191.8971 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | US All Buildings |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 | [17 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE |  | US All Buildings | [13 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.19362 | 0.098027 | 0.00015412 | 0.021034 | 0 | 0.10398 | 0 | 0.03559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.47547 | 5.608% | Small Office | 6.5234 | 3.3027 | 0.0051927 | 1.0996 | 0 | 3.5031 | 0 | 1.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.4102 | 5.608% | Small Office | 1.9113 | 0.96769 | 0.0015215 | 0.14943 | 0 | 1.0264 | 0 | 0.35133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.6354 | 5.608% | Small Office | 0 | 0 | 0 | 0.0058963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058963 | 5.608% | Small Office | 20.0099 | 10.1308 | 0.015928 | 2.2089 | 0 | 10.7455 | 0 | 3.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 49.1728 | 5.608%
Medium Office | 0.13109 | 0.093607 | 0.00058285 | 0.10042 | 0 | 0.10195 | 0 | 0.021343 | -0.00036446 | 0 | 0 | 0.0050214 | 0.011539 | 0 | 0 | 0.029698 | 0.49489 | 6.047% | Medium Office | 4.4168 | 3.1538 | 0.058285 | 4.3187 | 0 | 3.435 | 0 | 0.71908 | -0.012279 | 0 | 0 | 0.16918 | 0.38876 | 0 | 0 | 1.0006 | 17.6478 | 6.047% | Medium Office | 1.2941 | 0.92406 | 0 | 0.85201 | 0 | 1.0064 | 0 | 0.21069 | -0.0035978 | 0 | 0 | 0.04957 | 0.11391 | 0 | 0 | 0.29317 | 4.7404 | 6.047% | Medium Office | 0 | 0 | 0.00058285 | 0.014108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014691 | 6.047% | Medium Office | 13.5481 | 9.674 | 0.063705 | 10.4618 | 0 | 10.5364 | 0 | 2.2057 | -0.037666 | 0 | 0 | 0.51895 | 1.1925 | 0 | 0 | 3.0692 | 51.2327 | 6.047%
Large Office | 0.11127 | 0.036259 | 0.00034878 | 0.060163 | -0.069192 | 0.16211 | 0.030352 | 0.018133 | -0.0014499 | 0.036609 | 0 | 0.0031289 | 0.0050135 | 0 | 0 | 0.030306 | 0.42305 | 3.327% | Large Office | 3.7489 | 1.2216 | 0.034878 | 5.6914 | -2.3312 | 5.4617 | 1.0226 | 0.61093 | -0.048848 | 1.2334 | 0 | 0.10542 | 0.16891 | 0 | 0 | 1.021 | 17.9408 | 3.327% | Large Office | 1.0984 | 0.35793 | 0 | 0.048363 | -0.68304 | 1.6003 | 0.29963 | 0.179 | -0.014313 | 0.36139 | 0 | 0.030887 | 0.049491 | 0 | 0 | 0.29917 | 3.6272 | 3.327% | Large Office | 0 | 0 | 0.00034878 | 0.055264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055612 | 3.327% | Large Office | 11.4995 | 3.7472 | 0.038121 | 6.5466 | -7.1508 | 16.7533 | 3.1368 | 1.874 | -0.14984 | 3.7834 | 0 | 0.32336 | 0.51812 | 0 | 0 | 3.132 | 44.0517 | 3.327%
Standalone Retail | 0.21964 | 0.087172 | 0.0007823 | 0.12443 | 0 | 0.18305 | 0 | 0.26326 | -0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.86176 | 15.25% | Standalone Retail | 7.4 | 2.937 | 0.07823 | 12.4434 | 0 | 6.1673 | 0 | 8.8698 | -0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.3371 | 15.25% | Standalone Retail | 2.1682 | 0.86053 | 0 | 0 | 0 | 1.807 | 0 | 2.5989 | -0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.2709 | 15.25% | Standalone Retail | 0 | 0 | 0.0007823 | 0.12443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12522 | 15.25% | Standalone Retail | 22.699 | 9.0089 | 0.085506 | 13.6006 | 0 | 18.9177 | 0 | 27.2074 | -1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 89.8057 | 15.25%
Strip Mall | 0.22656 | 0.14182 | 0.0070789 | 0.070328 | 0 | 0.19103 | 0 | 0.14532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.78285 | 5.669% | Strip Mall | 7.6333 | 4.7783 | 0.2385 | 7.0328 | 0 | 6.436 | 0 | 4.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 31.0388 | 5.669% | Strip Mall | 2.2365 | 1.4 | 0.06988 | 0 | 0 | 1.8858 | 0 | 1.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.0338 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.070328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070328 | 5.669% | Strip Mall | 23.4144 | 14.6569 | 0.73158 | 7.6869 | 0 | 19.742 | 0 | 15.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 81.3232 | 5.669%
Primary School | 0.32268 | 0.021921 | 0.00096492 | 0.094424 | 0 | 0.21147 | 0 | 0.10338 | 0.023432 | 0.00017592 | 0.010277 | 0 | 0.011676 | 0 | 0 | 0.056735 | 0.85713 | 4.994% | Primary School | 10.8717 | 0.73857 | 0.04275 | 9.4424 | 0 | 7.1248 | 0 | 3.483 | 0.78945 | 0.005927 | 0.34625 | 0 | 0.39339 | 0 | 0 | 1.9115 | 35.1496 | 4.994% | Primary School | 3.1854 | 0.2164 | 0.0080009 | 0 | 0 | 2.0876 | 0 | 1.0205 | 0.23131 | 0.0017366 | 0.10145 | 0 | 0.11526 | 0 | 0 | 0.56007 | 7.5277 | 4.994% | Primary School | 0 | 0 | 0.00015443 | 0.094424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094578 | 4.994% | Primary School | 33.348 | 2.2655 | 0.10064 | 10.3205 | 0 | 21.8546 | 0 | 10.6837 | 2.4216 | 0.01818 | 1.0621 | 0 | 1.2067 | 0 | 0 | 5.8634 | 89.1449 | 4.994%
Secondary School | 0.3115 | 0.019842 | 6.5368e-05 | 0.063818 | 0 | 0.25002 | 0 | 0.14746 | 0.049024 | 0.020043 | 0.0044299 | 0.0013276 | 0.006628 | 0 | 0 | 0.027131 | 0.90128 | 10.36% | Secondary School | 10.4949 | 0.66851 | 0.0054047 | 6.3818 | 0 | 8.4234 | 0 | 4.9682 | 1.6517 | 0.67527 | 0.14925 | 0.04473 | 0.22331 | 0 | 0 | 0.91407 | 34.6006 | 10.36% | Secondary School | 3.075 | 0.19587 | 0.00016854 | 0 | 0 | 2.4681 | 0 | 1.4557 | 0.48395 | 0.19785 | 0.043731 | 0.013106 | 0.06543 | 0 | 0 | 0.26782 | 8.2667 | 10.36% | Secondary School | 0 | 0 | 4.8294e-05 | 0.063818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063866 | 10.36% | Secondary School | 32.1922 | 2.0506 | 0.007043 | 6.9753 | 0 | 25.8382 | 0 | 15.2395 | 5.0665 | 2.0713 | 0.45782 | 0.13721 | 0.68498 | 0 | 0 | 2.8038 | 93.5245 | 10.36%
Outpatient Healthcare | 0.10278 | 0.11835 | 0.0068091 | 0.48766 | 0.036067 | 0.32002 | 0 | 0.16864 | 0 | 0.00065162 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2576 | 4.371% | Outpatient Healthcare | 3.4629 | 3.9872 | 0.68091 | 21.5069 | 1.2152 | 10.782 | 0 | 5.6818 | 0 | 0.021954 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.8994 | 4.371% | Outpatient Healthcare | 1.0146 | 1.1683 | 0 | 4.0582 | 0.35604 | 3.1591 | 0 | 1.6648 | 0 | 0.0064325 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.5917 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.0068091 | 0.076563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083372 | 4.371% | Outpatient Healthcare | 10.6221 | 12.2306 | 0.74424 | 50.854 | 3.7274 | 33.0729 | 0 | 17.4285 | 0 | 0.067342 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 130.4665 | 4.371%
Hospital | 0.091289 | 0.012398 | 0.0021111 | 0.26906 | 0.13042 | 0.19181 | 0.045994 | 0.17969 | -0.021383 | 0.070727 | 0.0068221 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 1.015 | 3.448% | Hospital | 3.0757 | 0.41769 | 0.19334 | 23.6068 | 4.394 | 6.4625 | 1.5496 | 6.0542 | -0.72045 | 2.3829 | 0.22985 | 0.12931 | 0.40232 | 0 | 0 | 0.684 | 48.8618 | 3.448% | Hospital | 0.90117 | 0.12238 | 0.0026454 | 0.49115 | 1.2874 | 1.8935 | 0.45404 | 1.7739 | -0.21109 | 0.69819 | 0.067346 | 0.037888 | 0.11788 | 0 | 0 | 0.20041 | 7.8368 | 3.448% | Hospital | 0 | 0 | 0.0018431 | 0.21931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22115 | 3.448% | Hospital | 9.4344 | 1.2812 | 0.22915 | 29.1119 | 13.4782 | 19.8231 | 4.7533 | 18.5707 | -2.2099 | 7.3094 | 0.70504 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 106.2154 | 3.448%
Small Hotel | 0.13529 | 0.033186 | 0.0019364 | 0.13458 | 0 | 0.092475 | 0 | 0.07581 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50211 | 1.721% | Small Hotel | 4.5583 | 1.1181 | 0.19364 | 5.9194 | 0 | 3.1156 | 0 | 2.5542 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 18.4307 | 1.721% | Small Hotel | 1.3356 | 0.3276 | 0 | 1.1222 | 0 | 0.91288 | 0 | 0.74837 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.7313 | 1.721% | Small Hotel | 0 | 0 | 0.0019364 | 0.020892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022828 | 1.721% | Small Hotel | 13.9822 | 3.4297 | 0.21165 | 14.0323 | 0 | 9.5569 | 0 | 7.8347 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.0274 | 1.721%
Large Hotel | 0.14389 | 0.028405 | 0.00061413 | 0.16346 | 0 | 0.18811 | 0 | 0.088376 | 0.029154 | 0.038837 | 0.0046947 | 0.0063872 | 0.0081673 | 0 | 0 | 0.020007 | 0.72011 | 4.951% | Large Hotel | 4.8478 | 0.957 | 0.027724 | 16.3464 | 0 | 6.3378 | 0 | 2.9776 | 0.98224 | 1.3085 | 0.15817 | 0.2152 | 0.27517 | 0 | 0 | 0.67408 | 35.1077 | 4.951% | Large Hotel | 1.4204 | 0.2804 | 0.0050155 | 0 | 0 | 1.857 | 0 | 0.87242 | 0.2878 | 0.38338 | 0.046344 | 0.063053 | 0.080625 | 0 | 0 | 0.19751 | 5.4939 | 4.951% | Large Hotel | 0 | 0 | 0.00010606 | 0.16346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16357 | 4.951% | Large Hotel | 14.8703 | 2.9355 | 0.0641 | 17.8666 | 0 | 19.4408 | 0 | 9.1334 | 3.013 | 4.0137 | 0.48518 | 0.6601 | 0.84407 | 0 | 0 | 2.0677 | 75.3944 | 4.951%
Quick-service Restaurant | 0.53452 | 0.20914 | -0.00037974 | 0.037289 | 0 | 0.41085 | 0 | 0.73149 | 0 | 0 | 0.25748 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1837 | 0.5866% | Quick-service Restaurant | 18.0088 | 7.0464 | -0.037974 | 3.7289 | 0 | 13.8421 | 0 | 24.6452 | 0 | 0 | 8.675 | 0 | 0 | 0.10993 | 0 | 0 | 76.0185 | 0.5866% | Quick-service Restaurant | 5.2766 | 2.0646 | 0 | 0 | 0 | 4.0557 | 0 | 7.2211 | 0 | 0 | 2.5418 | 0 | 0 | 0.032209 | 0 | 0 | 21.192 | 0.5866% | Quick-service Restaurant | 0 | 0 | -0.00037974 | 0.037289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036909 | 0.5866% | Quick-service Restaurant | 55.2405 | 21.6144 | -0.041506 | 4.0757 | 0 | 42.4596 | 0 | 75.5972 | 0 | 0 | 26.6099 | 0 | 0 | 0.3372 | 0 | 0 | 225.893 | 0.5866%
Full-service Restaurant | 0.66437 | 0.20161 | 0.010407 | 0.24016 | 0 | 0.45064 | 0 | 0.78794 | 0 | 0 | 0.12333 | 0 | 0 | 0.002864 | 0 | 0 | 2.4813 | 0.6597% | Full-service Restaurant | 22.3837 | 6.7925 | 0.34304 | 24.0155 | 0 | 15.183 | 0 | 26.547 | 0 | 0 | 4.1552 | 0 | 0 | 0.096493 | 0 | 0 | 99.5163 | 0.6597% | Full-service Restaurant | 6.5584 | 1.9902 | 0.10386 | 0 | 0 | 4.4486 | 0 | 7.7783 | 0 | 0 | 1.2175 | 0 | 0 | 0.028273 | 0 | 0 | 22.1251 | 0.6597% | Full-service Restaurant | 0 | 0 | -0.00011429 | 0.24016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24004 | 0.6597% | Full-service Restaurant | 68.6602 | 20.8353 | 1.0748 | 26.249 | 0 | 46.5725 | 0 | 81.4306 | 0 | 0 | 12.7456 | 0 | 0 | 0.29599 | 0 | 0 | 257.864 | 0.6597%
Mid-rise Apartment | 0.033467 | 0.03919 | 0.00043011 | 0.05474 | 0 | 0.07245 | 0 | 0.048437 | -0.023109 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.23108 | 7.321% | Mid-rise Apartment | 1.1276 | 1.3204 | 0.014491 | 5.474 | 0 | 2.441 | 0 | 1.6319 | -0.77859 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 11.4154 | 7.321% | Mid-rise Apartment | 0.33038 | 0.38688 | 0.0042459 | 0 | 0 | 0.71521 | 0 | 0.47815 | -0.22813 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.7408 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.05474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05474 | 7.321% | Mid-rise Apartment | 3.4587 | 4.0502 | 0.044451 | 5.9831 | 0 | 7.4875 | 0 | 5.0058 | -2.3883 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 24.2077 | 7.321%
High-rise Apartment | 0.028332 | 0.031851 | 0.00041133 | 0.083415 | 0 | 0.064941 | 0.0072778 | 0.050122 | -0.024658 | 0.0083847 | 0 | 0.0015412 | 0.0072376 | 0 | 0 | 0.0006505 | 0.25951 | 8.967% | High-rise Apartment | 0.95454 | 1.0731 | 0.041133 | 5.9401 | 0 | 2.188 | 0.2452 | 1.6887 | -0.83076 | 0.28249 | 0 | 0.051925 | 0.24385 | 0 | 0 | 0.021916 | 11.9002 | 8.967% | High-rise Apartment | 0.27968 | 0.31442 | 0 | 0.35751 | 0 | 0.64108 | 0.071844 | 0.49479 | -0.24341 | 0.082771 | 0 | 0.015214 | 0.071447 | 0 | 0 | 0.0064215 | 2.0918 | 8.967% | High-rise Apartment | 0 | 0 | 0.00041133 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047611 | 8.967% | High-rise Apartment | 2.928 | 3.2917 | 0.044958 | 8.9017 | 0 | 6.7114 | 0.75213 | 5.18 | -2.5483 | 0.86653 | 0 | 0.15928 | 0.74798 | 0 | 0 | 0.067227 | 27.1025 | 8.967%
Warehouse | 0.16057 | 0.036021 | 0.00044234 | 0.040653 | 0 | 0.011052 | 0 | 0.019584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.26983 | 16.72% | Warehouse | 5.41 | 1.2136 | 0.014903 | 4.0653 | 0 | 0.37236 | 0 | 0.65983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.7867 | 16.72% | Warehouse | 1.5851 | 0.35559 | 0.0043666 | 0 | 0 | 0.1091 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2624 | 16.72% | Warehouse | 0 | 0 | 0 | 0.040653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040653 | 16.72% | Warehouse | 16.5948 | 3.7226 | 0.045714 | 4.4434 | 0 | 1.1422 | 0 | 2.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 28.1281 | 16.72%
US Weighted | 0.17367 | 0.058733 | 0.001274 | 0.10464 | 0.0037711 | 0.14247 | 0.0032483 | 0.11278 | 0.00030403 | 0.0084452 | 0.0037639 | 0.0019006 | 0.0035995 | 3.8034e-05 | 0 | 0.012788 | 0.63141 | 100% | US Weighted | 5.8511 | 1.9788 | 0.083538 | 8.4001 | 0.12706 | 4.8 | 0.10944 | 3.7997 | 0.010243 | 0.28453 | 0.12681 | 0.064036 | 0.12127 | 0.0012814 | 0 | 0.43085 | 26.1889 | 100% | US Weighted | 1.7144 | 0.57979 | 0.0065296 | 0.30718 | 0.037227 | 1.4064 | 0.032067 | 1.1133 | 0.0030013 | 0.083369 | 0.037156 | 0.018762 | 0.035533 | 0.00037546 | 0 | 0.12624 | 5.5013 | 100% | US Weighted | 0 | 0 | 0.00061252 | 0.073517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07413 | 100% | US Weighted | 17.9479 | 6.0698 | 0.13531 | 11.2514 | 0.38973 | 14.7237 | 0.33571 | 11.6552 | 0.031421 | 0.87278 | 0.38898 | 0.19642 | 0.37199 | 0.0039307 | 0 | 1.3216 | 65.6958 | 100%
Building Type: | US All Buildings |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | US All Buildings |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | US All Buildings |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 | [17 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | WAREHOUSE | [15 empty] | Prototype Floor Area: | 52050 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.53352 | 0.77073 | 0.0016705 | 0.41826 | 0 | 0.52391 | 0 | 0.26323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085417 | 0.38457 | 5.608% | Small Office | 0.53352 | 0.77073 | 0.0016705 | 0.45629 | 0 | 0.52391 | 0 | 0.26323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085417 | 0.3873 | 5.608% | Small Office | 0.53352 | 0.77073 | 0.0016705 | 0.38327 | 0 | 0.52391 | 0 | 0.26323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085417 | 0.38315 | 5.608% | Small Office | 0 | 0 | 0 | 0.54631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54631 | 5.608% | Small Office | 0.53352 | 0.77073 | 0.0016705 | 0.41982 | 0 | 0.52391 | 0 | 0.26323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085417 | 0.38465 | 5.608%
Medium Office | 0.45198 | 0.79189 | 0.039478 | 0.55536 | 0 | 0.38446 | 0 | 0.33422 | 0 | 0 | 0 | 0.054698 | 0.65151 | 0 | 0 | 0.088261 | 0.35889 | 6.047% | Medium Office | 0.45198 | 0.79189 | 0.039478 | 0.53486 | 0 | 0.38446 | 0 | 0.33422 | 0 | 0 | 0 | 0.054698 | 0.65151 | 0 | 0 | 0.088261 | 0.35709 | 6.047% | Medium Office | 0.45198 | 0.79189 | 0 | 0.57191 | 0 | 0.38446 | 0 | 0.33422 | 0 | 0 | 0 | 0.054698 | 0.65151 | 0 | 0 | 0.088261 | 0.35989 | 6.047% | Medium Office | 0 | 0 | 0.039478 | 0.47185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32893 | 6.047% | Medium Office | 0.45198 | 0.79189 | 0.039478 | 0.55457 | 0 | 0.38446 | 0 | 0.33422 | 0 | 0 | 0 | 0.054698 | 0.65151 | 0 | 0 | 0.088261 | 0.35883 | 6.047%
Large Office | 0.38364 | 0.65128 | 0.032336 | 0.65919 | -10.617 | 0.42343 | 0.61699 | 0.12031 | 0 | 0.60428 | 0 | 0.028338 | 0.61772 | 0 | 0 | 0.09145 | 0.17703 | 3.327% | Large Office | 0.38364 | 0.65128 | 0.032336 | 0.64862 | -10.617 | 0.42343 | 0.61699 | 0.12031 | 0 | 0.60428 | 0 | 0.028338 | 0.61772 | 0 | 0 | 0.09145 | 0.20639 | 3.327% | Large Office | 0.38364 | 0.65128 | 0 | 0.92246 | -10.617 | 0.42343 | 0.61699 | 0.12031 | 0 | 0.60428 | 0 | 0.028338 | 0.61772 | 0 | 0 | 0.09145 | 0.16025 | 3.327% | Large Office | 0 | 0 | 0.032336 | 0.64292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57485 | 3.327% | Large Office | 0.38364 | 0.65128 | 0.032336 | 0.65835 | -10.617 | 0.42343 | 0.61699 | 0.12031 | 0 | 0.60428 | 0 | 0.028338 | 0.61772 | 0 | 0 | 0.09145 | 0.17796 | 3.327%
Standalone Retail | 0.3917 | 0.66496 | 0.021484 | 0.71202 | 0 | 0.52844 | 0 | 0.56963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044066 | 0.44559 | 15.25% | Standalone Retail | 0.3917 | 0.66496 | 0.021484 | 0.71202 | 0 | 0.52844 | 0 | 0.56963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044066 | 0.47166 | 15.25% | Standalone Retail | 0.3917 | 0.66496 | 0 | 0 | 0 | 0.52844 | 0 | 0.56963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044066 | 0.42753 | 15.25% | Standalone Retail | 0 | 0 | 0.021484 | 0.71202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59295 | 15.25% | Standalone Retail | 0.3917 | 0.66496 | 0.021484 | 0.71202 | 0 | 0.52844 | 0 | 0.56963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044066 | 0.44651 | 15.25%
Strip Mall | 0.28662 | 0.67349 | 0.0831 | 0.40942 | 0 | 0.50912 | 0 | 0.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044282 | 0.36855 | 5.669% | Strip Mall | 0.28662 | 0.67349 | 0.0831 | 0.40942 | 0 | 0.50912 | 0 | 0.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044282 | 0.37416 | 5.669% | Strip Mall | 0.28662 | 0.67349 | 0.0831 | 0 | 0 | 0.50912 | 0 | 0.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044282 | 0.36495 | 5.669% | Strip Mall | 0 | 0 | 0 | 0.40942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40942 | 5.669% | Strip Mall | 0.28662 | 0.67349 | 0.0831 | 0.40942 | 0 | 0.50912 | 0 | 0.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044282 | 0.36874 | 5.669%
Primary School | 0.70073 | 0.69213 | 0.037997 | 0.59331 | 0 | 0.53969 | 0 | 0.53456 | 0.45706 | 0.18136 | 0.19837 | 0 | 0.63915 | 0 | 0 | 0.13598 | 0.45001 | 4.994% | Primary School | 0.70073 | 0.69213 | 0.023311 | 0.59331 | 0 | 0.53969 | 0 | 0.53456 | 0.45706 | 0.18136 | 0.19837 | 0 | 0.63915 | 0 | 0 | 0.13598 | 0.44622 | 4.994% | Primary School | 0.70073 | 0.69213 | 0.076171 | 0 | 0 | 0.53969 | 0 | 0.53456 | 0.45706 | 0.18136 | 0.19837 | 0 | 0.63915 | 0 | 0 | 0.13598 | 0.45268 | 4.994% | Primary School | 0 | 0 | 0.010467 | 0.59331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42957 | 4.994% | Primary School | 0.70073 | 0.69213 | 0.037106 | 0.59331 | 0 | 0.53969 | 0 | 0.53456 | 0.45706 | 0.18136 | 0.19837 | 0 | 0.63915 | 0 | 0 | 0.13598 | 0.44987 | 4.994%
Secondary School | 0.70851 | 0.68606 | 0.0015532 | 0.59141 | 0 | 0.56006 | 0 | 0.60643 | 0.66956 | 0.82487 | 0.15709 | 0.13135 | 0.62587 | 0 | 0 | 0.095802 | 0.4979 | 10.36% | Secondary School | 0.70851 | 0.68606 | 0.0019021 | 0.59141 | 0 | 0.56006 | 0 | 0.60643 | 0.66956 | 0.82487 | 0.15709 | 0.13135 | 0.62587 | 0 | 0 | 0.095802 | 0.48604 | 10.36% | Secondary School | 0.70851 | 0.68606 | 0.00082802 | 0 | 0 | 0.56006 | 0 | 0.60643 | 0.66956 | 0.82487 | 0.15709 | 0.13135 | 0.62587 | 0 | 0 | 0.095802 | 0.50559 | 10.36% | Secondary School | 0 | 0 | 0.0022497 | 0.59141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41513 | 10.36% | Secondary School | 0.70851 | 0.68606 | 0.0015731 | 0.59141 | 0 | 0.56006 | 0 | 0.60643 | 0.66956 | 0.82487 | 0.15709 | 0.13135 | 0.62587 | 0 | 0 | 0.095802 | 0.4975 | 10.36%
Outpatient Healthcare | 0.24467 | 0.75901 | 0.11895 | 0.61519 | 0.23954 | 0.38997 | 0 | 0.4069 | 0 | 0.27878 | 0 | 0.019555 | 0 | 0 | 0 | 0.0090589 | 0.3044 | 4.371% | Outpatient Healthcare | 0.24467 | 0.75901 | 0.11895 | 0.52652 | 0.23954 | 0.38997 | 0 | 0.4069 | 0 | 0.27878 | 0 | 0.019555 | 0 | 0 | 0 | 0.0082451 | 0.29933 | 4.371% | Outpatient Healthcare | 0.24467 | 0.75901 | 0 | 0.70945 | 0.23954 | 0.38997 | 0 | 0.4069 | 0 | 0.27878 | 0 | 0.019555 | 0 | 0 | 0 | 0.0095373 | 0.30761 | 4.371% | Outpatient Healthcare | 0 | 0 | 0.11895 | 0.35904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26544 | 4.371% | Outpatient Healthcare | 0.24467 | 0.75901 | 0.11895 | 0.61128 | 0.23954 | 0.38997 | 0 | 0.4069 | 0 | 0.27878 | 0 | 0.019555 | 0 | 0 | 0 | 0.0090328 | 0.30424 | 4.371%
Hospital | 0.18731 | 0.40713 | 0.040389 | 0.4812 | 0.62739 | 0.40171 | 0.61348 | 0.34593 | 0 | 0.55378 | 0.21908 | 0.012967 | 0.59052 | 0 | 0 | 0.030901 | 0.26618 | 3.448% | Hospital | 0.18731 | 0.40713 | 0.038633 | 0.48385 | 0.62739 | 0.40171 | 0.61348 | 0.34593 | 0 | 0.55378 | 0.21908 | 0.012967 | 0.59052 | 0 | 0 | 0.030901 | 0.28923 | 3.448% | Hospital | 0.18731 | 0.40713 | 0.079941 | 0.46306 | 0.62739 | 0.40171 | 0.61348 | 0.34593 | 0 | 0.55378 | 0.21908 | 0.012967 | 0.59052 | 0 | 0 | 0.030901 | 0.24784 | 3.448% | Hospital | 0 | 0 | 0.037679 | 0.48552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36243 | 3.448% | Hospital | 0.18731 | 0.40713 | 0.040251 | 0.4814 | 0.62739 | 0.40171 | 0.61348 | 0.34593 | 0 | 0.55378 | 0.21908 | 0.012967 | 0.59052 | 0 | 0 | 0.030901 | 0.26706 | 3.448%
Small Hotel | 0.41713 | 0.53492 | 0.01489 | 0.64247 | 0 | 0.34213 | 0 | 0.39081 | 0 | 0 | 0 | 0.035655 | 0 | 0 | 0 | 0.11145 | 0.29979 | 1.721% | Small Hotel | 0.41713 | 0.53492 | 0.01489 | 0.63347 | 0 | 0.34213 | 0 | 0.39081 | 0 | 0 | 0 | 0.035655 | 0 | 0 | 0 | 0.11145 | 0.25085 | 1.721% | Small Hotel | 0.41713 | 0.53492 | 0 | 0.64971 | 0 | 0.34213 | 0 | 0.39081 | 0 | 0 | 0 | 0.035655 | 0 | 0 | 0 | 0.11145 | 0.33803 | 1.721% | Small Hotel | 0 | 0 | 0.01489 | 0.60572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088822 | 1.721% | Small Hotel | 0.41713 | 0.53492 | 0.01489 | 0.64212 | 0 | 0.34213 | 0 | 0.39081 | 0 | 0 | 0 | 0.035655 | 0 | 0 | 0 | 0.11145 | 0.29794 | 1.721%
Large Hotel | 0.42994 | 0.40279 | 0.0033736 | 0.70313 | 0 | 0.346 | 0 | 0.37956 | 0.38226 | 0.73109 | 0.1938 | 0.028339 | 0.61901 | 0 | 0 | 0.076474 | 0.28531 | 4.951% | Large Hotel | 0.42994 | 0.40279 | 0.0016518 | 0.70313 | 0 | 0.346 | 0 | 0.37956 | 0.38226 | 0.73109 | 0.1938 | 0.028339 | 0.61901 | 0 | 0 | 0.076474 | 0.29181 | 4.951% | Large Hotel | 0.42994 | 0.40279 | 0.023723 | 0 | 0 | 0.346 | 0 | 0.37956 | 0.38226 | 0.73109 | 0.1938 | 0.028339 | 0.61901 | 0 | 0 | 0.076474 | 0.27938 | 4.951% | Large Hotel | 0 | 0 | 0.0006603 | 0.70313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3075 | 4.951% | Large Hotel | 0.42994 | 0.40279 | 0.0032423 | 0.70313 | 0 | 0.346 | 0 | 0.37956 | 0.38226 | 0.73109 | 0.1938 | 0.028339 | 0.61901 | 0 | 0 | 0.076474 | 0.28558 | 4.951%
Quick-service Restaurant | 0.63277 | 0.67888 | -0.00056555 | 0.027412 | 0 | 0.35557 | 0 | 0.50062 | 0 | 0 | 0.21135 | 0 | 0 | 0.00073516 | 0 | 0 | 0.19058 | 0.5866% | Quick-service Restaurant | 0.63277 | 0.67888 | -0.00056555 | 0.027412 | 0 | 0.35557 | 0 | 0.50062 | 0 | 0 | 0.21135 | 0 | 0 | 0.00040799 | 0 | 0 | 0.11866 | 0.5866% | Quick-service Restaurant | 0.63277 | 0.67888 | 0 | 0 | 0 | 0.35557 | 0 | 0.50062 | 0 | 0 | 0.21135 | 0 | 0 | 0.0012406 | 0 | 0 | 0.28181 | 0.5866% | Quick-service Restaurant | 0 | 0 | -0.00056555 | 0.027412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096115 | 0.5866% | Quick-service Restaurant | 0.63277 | 0.67888 | -0.00056555 | 0.027412 | 0 | 0.35557 | 0 | 0.50062 | 0 | 0 | 0.21135 | 0 | 0 | 0.0007183 | 0 | 0 | 0.18716 | 0.5866%
Full-service Restaurant | 0.69973 | 0.67898 | 0.011212 | 0.22767 | 0 | 0.42172 | 0 | 0.603 | 0 | 0 | 0.22322 | 0 | 0 | 0.00097251 | 0 | 0 | 0.27254 | 0.6597% | Full-service Restaurant | 0.69973 | 0.67898 | 0.005156 | 0.22767 | 0 | 0.42172 | 0 | 0.603 | 0 | 0 | 0.22322 | 0 | 0 | 0.00063115 | 0 | 0 | 0.21373 | 0.6597% | Full-service Restaurant | 0.69973 | 0.67898 | 0.026545 | 0 | 0 | 0.42172 | 0 | 0.603 | 0 | 0 | 0.22322 | 0 | 0 | 0.001341 | 0 | 0 | 0.33409 | 0.6597% | Full-service Restaurant | 0 | 0 | -0.00021491 | 0.22767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10019 | 0.6597% | Full-service Restaurant | 0.69973 | 0.67898 | 0.010847 | 0.22767 | 0 | 0.42172 | 0 | 0.603 | 0 | 0 | 0.22322 | 0 | 0 | 0.00095735 | 0 | 0 | 0.26996 | 0.6597%
Mid-rise Apartment | 0.26499 | 0.64433 | 0.0013727 | 0.65157 | 0 | 0.37236 | 0 | 0.23157 | 0 | 0 | 0 | 0.035654 | 0 | 0 | 0 | 0.0050247 | 0.16275 | 7.321% | Mid-rise Apartment | 0.26499 | 0.64433 | 0.0013727 | 0.65157 | 0 | 0.37236 | 0 | 0.23157 | 0 | 0 | 0 | 0.035654 | 0 | 0 | 0 | 0.0050247 | 0.21373 | 7.321% | Mid-rise Apartment | 0.26499 | 0.64433 | 0.0013727 | 0 | 0 | 0.37236 | 0 | 0.23157 | 0 | 0 | 0 | 0.035654 | 0 | 0 | 0 | 0.0050247 | 0.132 | 7.321% | Mid-rise Apartment | 0 | 0 | 0 | 0.65157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65157 | 7.321% | Mid-rise Apartment | 0.26499 | 0.64433 | 0.0013727 | 0.65157 | 0 | 0.37236 | 0 | 0.23157 | 0 | 0 | 0 | 0.035654 | 0 | 0 | 0 | 0.0050247 | 0.16441 | 7.321%
High-rise Apartment | 0.23619 | 0.4474 | 0.003552 | 0.66577 | 0 | 0.25555 | 0.60948 | 0.2252 | 0 | 0.34998 | 0 | 0.028338 | 0.59981 | 0 | 0 | 0.0020014 | 0.1942 | 8.967% | High-rise Apartment | 0.23619 | 0.4474 | 0.003552 | 0.67652 | 0 | 0.25555 | 0.60948 | 0.2252 | 0 | 0.34998 | 0 | 0.028338 | 0.59981 | 0 | 0 | 0.0020014 | 0.20783 | 8.967% | High-rise Apartment | 0.23619 | 0.4474 | 0 | 0.6406 | 0 | 0.25555 | 0.60948 | 0.2252 | 0 | 0.34998 | 0 | 0.028338 | 0.59981 | 0 | 0 | 0.0020014 | 0.18398 | 8.967% | High-rise Apartment | 0 | 0 | 0.003552 | 0.68647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25797 | 8.967% | High-rise Apartment | 0.23619 | 0.4474 | 0.003552 | 0.66641 | 0 | 0.25555 | 0.60948 | 0.2252 | 0 | 0.34998 | 0 | 0.028338 | 0.59981 | 0 | 0 | 0.0020014 | 0.1947 | 8.967%
Warehouse | 0.61622 | 0.53963 | 0.031921 | 0.38477 | 0 | 0.5118 | 0 | 0.53824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01996 | 0.46512 | 16.72% | Warehouse | 0.61622 | 0.53963 | 0.031921 | 0.38477 | 0 | 0.5118 | 0 | 0.53824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01996 | 0.44392 | 16.72% | Warehouse | 0.61622 | 0.53963 | 0.031921 | 0 | 0 | 0.5118 | 0 | 0.53824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01996 | 0.48302 | 16.72% | Warehouse | 0 | 0 | 0 | 0.38477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38477 | 16.72% | Warehouse | 0.61622 | 0.53963 | 0.031921 | 0.38477 | 0 | 0.5118 | 0 | 0.53824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01996 | 0.46429 | 16.72%
US Weighted | 45.88% | 64.66% | 1.522% | 54.69% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.04584% | 0% | 4.53% | 34.24% | 100% | US Weighted | 45.88% | 64.66% | 1.491% | 52.8% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.0257% | 0% | 4.471% | 34.15% | 100% | US Weighted | 45.88% | 64.66% | 1.586% | 63.99% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.07615% | 0% | 4.561% | 34.3% | 100% | US Weighted | 0% | 0% | 1.459% | 51.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.75% | 100% | US Weighted | 45.88% | 64.66% | 1.52% | 54.55% | 27% | 44.77% | 61.38% | 45.12% | 2.184% | 60.81% | 20.26% | 2.84% | 62.24% | 0.04481% | 0% | 4.528% | 34.23% | 100%

## OffS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Office |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Small Office | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.16929 | 0.029161 | 0.092109 | 0.029255 | 0 | 0.094484 | 0 | 0.099614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.76088 |  | STD2016 | 5.7037 | 0.98247 | 3.1033 | 1.3103 | 0 | 3.1833 | 0 | 3.3562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.9602 |  | STD2016 | 1.6712 | 0.28786 | 0.90927 | 0.24046 | 0 | 0.93271 | 0 | 0.98336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.4629 |  | STD2016 | 0 | 0 | 0 | 0.0048967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048967 |  | STD2016 | 17.4957 | 3.0137 | 9.5191 | 3.0526 | 0 | 9.7646 | 0 | 10.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 78.6638
STD2013 | 0.23359 | 0.060911 | 0.092109 | 0.027689 | 0 | 0.098899 | 0 | 0.10249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.86266 |  | STD2013 | 7.8701 | 2.0522 | 3.1033 | 1.2347 | 0 | 3.3321 | 0 | 3.4531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.3663 |  | STD2013 | 2.3059 | 0.6013 | 0.90927 | 0.2284 | 0 | 0.9763 | 0 | 1.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.471 |  | STD2013 | 0 | 0 | 0 | 0.0045519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045519 |  | STD2013 | 24.1408 | 6.295 | 9.5191 | 2.8886 | 0 | 10.2209 | 0 | 10.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 89.1801
STD2010 | 0.27431 | 0.060911 | 0.092109 | 0.031705 | 0 | 0.14059 | 0 | 0.11968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.97087 |  | STD2010 | 9.2418 | 2.0522 | 3.1033 | 1.4201 | 0 | 4.7366 | 0 | 4.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.0622 |  | STD2010 | 2.7079 | 0.6013 | 0.90927 | 0.26058 | 0 | 1.3878 | 0 | 1.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.5317 |  | STD2010 | 0 | 0 | 0 | 0.005308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005308 |  | STD2010 | 28.3485 | 6.295 | 9.5191 | 3.3082 | 0 | 14.5293 | 0 | 12.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 100.3677
STD2007 | 0.36291 | 0.12719 | 0.092263 | 0.035691 | 0 | 0.15605 | 0 | 0.13046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1746 |  | STD2007 | 12.2271 | 4.2852 | 3.1085 | 1.6997 | 0 | 5.2576 | 0 | 4.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0714 |  | STD2007 | 3.5825 | 1.2556 | 0.91079 | 0.27829 | 0 | 1.5405 | 0 | 1.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5212 |  | STD2007 | 0 | 0 | 0 | 0.0074994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074994 |  | STD2007 | 37.5056 | 13.1444 | 9.535 | 3.7331 | 0 | 16.1272 | 0 | 13.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 121.435
STD2004 | 0.36291 | 0.12719 | 0.092263 | 0.050289 | 0 | 0.19846 | 0 | 0.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2363 |  | STD2004 | 12.2271 | 4.2852 | 3.1085 | 2.41 | 0 | 6.6864 | 0 | 4.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.3704 |  | STD2004 | 3.5825 | 1.2556 | 0.91079 | 0.38989 | 0 | 1.9591 | 0 | 1.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.0983 |  | STD2004 | 0 | 0 | 0 | 0.010793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010793 |  | STD2004 | 37.5056 | 13.1444 | 9.535 | 5.2615 | 0 | 20.5101 | 0 | 13.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 127.8366
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 4.1851e-08 | 0.014598 | 0 | 0.04241 | 0 | 0.0047446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061753 |  | 2004-2007 | 0 | 0 | 1.41e-06 | 0.71024 | 0 | 1.4289 | 0 | 0.15985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.299 |  | 2004-2007 | 0 | 0 | 4.1314e-07 | 0.1116 | 0 | 0.41865 | 0 | 0.046837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57709 |  | 2004-2007 | 0 | 0 | 0 | 0.0032937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032937 |  | 2004-2007 | 0 | 0 | 4.3251e-06 | 1.5283 | 0 | 4.3829 | 0 | 0.49034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4015
2007-2010 | 0.088605 | 0.066276 | 0.00015408 | 0.003986 | 0 | 0.015462 | 0 | 0.01078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018463 | 0.20373 |  | 2007-2010 | 2.9853 | 2.233 | 0.0051913 | 0.2796 | 0 | 0.52093 | 0 | 0.36318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62204 | 7.0092 |  | 2007-2010 | 0.87468 | 0.65426 | 0.001521 | 0.017717 | 0 | 0.15263 | 0 | 0.10641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18226 | 1.9895 |  | 2007-2010 | 0 | 0 | 0 | 0.0021913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021913 |  | 2007-2010 | 9.157 | 6.8494 | 0.015924 | 0.42499 | 0 | 1.5979 | 0 | 1.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.908 | 21.0674
2010-2013 | 0.040715 | 0 | 0 | 0.004016 | 0 | 0.041689 | 0 | 0.017187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046029 | 0.10821 |  | 2010-2013 | 1.3717 | 0 | 0 | 0.18544 | 0 | 1.4046 | 0 | 0.57907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 | 3.6959 |  | 2010-2013 | 0.40192 | 0 | 0 | 0.032181 | 0 | 0.41154 | 0 | 0.16967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045438 | 1.0607 |  | 2010-2013 | 0 | 0 | 0 | 0.00075609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00075609 |  | 2010-2013 | 4.2077 | 0 | 0 | 0.41954 | 0 | 4.3084 | 0 | 1.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47569 | 11.1876
2013-2016 | 0.064299 | 0.031751 | 0 | -0.0015666 | 0 | 0.0044151 | 0 | 0.0028782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10178 |  | 2013-2016 | 2.1664 | 1.0697 | 0 | -0.075641 | 0 | 0.14875 | 0 | 0.096971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4062 |  | 2013-2016 | 0.63474 | 0.31343 | 0 | -0.012061 | 0 | 0.043585 | 0 | 0.028413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0081 |  | 2013-2016 | 0 | 0 | 0 | -0.00034477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00034477 |  | 2013-2016 | 6.6451 | 3.2813 | 0 | -0.16395 | 0 | 0.45629 | 0 | 0.29745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5163
2004-2016 | 0.19362 | 0.098027 | 0.00015412 | 0.021034 | 0 | 0.10398 | 0 | 0.03559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.47547 |  | 2004-2016 | 6.5234 | 3.3027 | 0.0051927 | 1.0996 | 0 | 3.5031 | 0 | 1.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.4102 |  | 2004-2016 | 1.9113 | 0.96769 | 0.0015215 | 0.14943 | 0 | 1.0264 | 0 | 0.35133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.6354 |  | 2004-2016 | 0 | 0 | 0 | 0.0058963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058963 |  | 2004-2016 | 20.0099 | 10.1308 | 0.015928 | 2.2089 | 0 | 10.7455 | 0 | 3.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 49.1728
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 4.536e-05% | 29.03% |  | 21.37% |  | 3.509% | [7 empty] | 0% | 4.995% |  | 2004-2007 | 0% | 0% | 4.536e-05% | 29.47% |  | 21.37% |  | 3.509% | [7 empty] | 0% | 5.426% |  | 2004-2007 | 0% | 0% | 4.536e-05% | 28.62% |  | 21.37% |  | 3.509% | [7 empty] | 0% | 4.77% |  | 2004-2007 |  |  |  | 30.52% | [12 empty] | 30.52% |  | 2004-2007 | 0% | 0% | 4.536e-05% | 29.05% |  | 21.37% |  | 3.509% | [7 empty] | 0% | 5.008%
2007-2010 | 24.42% | 52.11% | 0.167% | 11.17% |  | 9.908% |  | 8.263% | [7 empty] | 6.837% | 17.34% |  | 2007-2010 | 24.42% | 52.11% | 0.167% | 16.45% |  | 9.908% |  | 8.263% | [7 empty] | 6.837% | 17.49% |  | 2007-2010 | 24.42% | 52.11% | 0.167% | 6.366% |  | 9.908% |  | 8.263% | [7 empty] | 6.837% | 17.27% |  | 2007-2010 |  |  |  | 29.22% | [12 empty] | 29.22% |  | 2007-2010 | 24.42% | 52.11% | 0.167% | 11.38% |  | 9.908% |  | 8.263% | [7 empty] | 6.837% | 17.35%
2010-2013 | 14.84% | 0% | 0% | 12.67% |  | 29.65% |  | 14.36% | [7 empty] | 1.83% | 11.15% |  | 2010-2013 | 14.84% | 0% | 0% | 13.06% |  | 29.65% |  | 14.36% | [7 empty] | 1.83% | 11.18% |  | 2010-2013 | 14.84% | 0% | 0% | 12.35% |  | 29.65% |  | 14.36% | [7 empty] | 1.83% | 11.13% |  | 2010-2013 |  |  |  | 14.24% | [12 empty] | 14.24% |  | 2010-2013 | 14.84% | 0% | 0% | 12.68% |  | 29.65% |  | 14.36% | [7 empty] | 1.83% | 11.15%
2013-2016 | 27.53% | 52.13% | 0% | -5.658% |  | 4.464% |  | 2.808% | [7 empty] | 0% | 11.8% |  | 2013-2016 | 27.53% | 52.13% | 0% | -6.126% |  | 4.464% |  | 2.808% | [7 empty] | 0% | 11.6% |  | 2013-2016 | 27.53% | 52.13% | 0% | -5.281% |  | 4.464% |  | 2.808% | [7 empty] | 0% | 11.9% |  | 2013-2016 |  |  |  | -7.574% | [12 empty] | -7.574% |  | 2013-2016 | 27.53% | 52.13% | 0% | -5.676% |  | 4.464% |  | 2.808% | [7 empty] | 0% | 11.79%
2004-2016 | 53.35% | 77.07% | 0.167% | 41.83% |  | 52.39% |  | 26.32% | [7 empty] | 8.542% | 38.46% |  | 2004-2016 | 53.35% | 77.07% | 0.167% | 45.63% |  | 52.39% |  | 26.32% | [7 empty] | 8.542% | 38.73% |  | 2004-2016 | 53.35% | 77.07% | 0.167% | 38.33% |  | 52.39% |  | 26.32% | [7 empty] | 8.542% | 38.31% |  | 2004-2016 |  |  |  | 54.63% | [12 empty] | 54.63% |  | 2004-2016 | 53.35% | 77.07% | 0.167% | 41.98% |  | 52.39% |  | 26.32% | [7 empty] | 8.542% | 38.47%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1701 | 0.0291 | 0.092109 | 0 | 0 | 0.18013 | 0 | 0.096098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.8145 | 2.974% | CZ 1A | 5.731 | 0.98044 | 3.1033 | 0 | 0 | 6.0687 | 0 | 3.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.442 | 2.974% | CZ 1A | 1.6792 | 0.28727 | 0.90927 | 0 | 0 | 1.7781 | 0 | 0.94864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.0405 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 17.5794 | 3.0074 | 9.5191 | 0 | 0 | 18.6154 | 0 | 9.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 84.1761 | 2.974%
CZ 1B | 0.16964 | 0.028998 | 0.092109 | 0.0013809 | 0 | 0.19475 | 0 | 0.10893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.84279 | 0% | CZ 1B | 5.7155 | 0.97699 | 3.1033 | 0.046524 | 0 | 6.5615 | 0 | 3.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.3949 | 0% | CZ 1B | 1.6746 | 0.28626 | 0.90927 | 0.013631 | 0 | 1.9225 | 0 | 1.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.3197 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 17.5318 | 2.9969 | 9.5191 | 0.14271 | 0 | 20.127 | 0 | 11.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 87.099 | 0%
CZ 2A | 0.17005 | 0.0291 | 0.092109 | 0.0037001 | 0 | 0.15445 | 0 | 0.098246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.79463 | 20.09% | CZ 2A | 5.7293 | 0.98044 | 3.1033 | 0.12923 | 0 | 5.2037 | 0 | 3.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.7769 | 20.09% | CZ 2A | 1.6787 | 0.28727 | 0.90927 | 0.035846 | 0 | 1.5247 | 0 | 0.96985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.8436 | 20.09% | CZ 2A | 0 | 0 | 0 | 6.8907e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8907e-05 | 20.09% | CZ 2A | 17.5741 | 3.0074 | 9.5191 | 0.3828 | 0 | 15.9621 | 0 | 10.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 82.1223 | 20.09%
CZ 2B | 0.17066 | 0.0291 | 0.092109 | 0.0046034 | 0 | 0.1364 | 0 | 0.11809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.79793 | 5.157% | CZ 2B | 5.75 | 0.98044 | 3.1033 | 0.15852 | 0 | 4.5955 | 0 | 3.9786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.8872 | 5.157% | CZ 2B | 1.6847 | 0.28727 | 0.90927 | 0.044933 | 0 | 1.3465 | 0 | 1.1657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.8764 | 5.157% | CZ 2B | 0 | 0 | 0 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.168e-05 | 5.157% | CZ 2B | 17.6376 | 3.0074 | 9.5191 | 0.47605 | 0 | 14.0963 | 0 | 12.2041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 82.464 | 5.157%
CZ 3A | 0.17046 | 0.029305 | 0.092109 | 0.024265 | 0 | 0.092569 | 0 | 0.09799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.75367 | 18.18% | CZ 3A | 5.7431 | 0.98733 | 3.1033 | 0.96832 | 0 | 3.1188 | 0 | 3.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.5431 | 18.18% | CZ 3A | 1.6827 | 0.28929 | 0.90927 | 0.21709 | 0 | 0.91381 | 0 | 0.96733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.4175 | 18.18% | CZ 3A | 0 | 0 | 0 | 0.0022739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022739 | 18.18% | CZ 3A | 17.6164 | 3.0286 | 9.5191 | 2.5213 | 0 | 9.5667 | 0 | 10.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 77.9024 | 18.18%
CZ 3B | 0.1702 | 0.028845 | 0.092109 | 0.013679 | 0 | 0.099422 | 0 | 0.11451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.76574 | 8.466% | CZ 3B | 5.7345 | 0.97183 | 3.1033 | 0.50313 | 0 | 3.3497 | 0 | 3.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.8412 | 8.466% | CZ 3B | 1.6802 | 0.28474 | 0.90927 | 0.12874 | 0 | 0.98146 | 0 | 1.1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.5528 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00063739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00063739 | 8.466% | CZ 3B | 17.59 | 2.981 | 9.5191 | 1.4175 | 0 | 10.2749 | 0 | 11.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 79.14 | 8.466%
CZ 3C | 0.17036 | 0.028794 | 0.092109 | 0.0037846 | 0 | 0.065565 | 0 | 0.091341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.69892 | 1.386% | CZ 3C | 5.7396 | 0.9701 | 3.1033 | 0.12751 | 0 | 2.209 | 0 | 3.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.5478 | 1.386% | CZ 3C | 1.6817 | 0.28424 | 0.90927 | 0.03736 | 0 | 0.64724 | 0 | 0.90169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 6.8995 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 17.6058 | 2.9757 | 9.5191 | 0.39112 | 0 | 6.7759 | 0 | 9.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 72.231 | 1.386%
CZ 4A | 0.16795 | 0.0291 | 0.092109 | 0.03419 | 0 | 0.07247 | 0 | 0.095024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.73782 | 14.95% | CZ 4A | 5.6586 | 0.98044 | 3.1033 | 1.3198 | 0 | 2.4416 | 0 | 3.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.0262 | 14.95% | CZ 4A | 1.658 | 0.28727 | 0.90927 | 0.31251 | 0 | 0.7154 | 0 | 0.93804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.2585 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0025323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025323 | 14.95% | CZ 4A | 17.3574 | 3.0074 | 9.5191 | 3.5485 | 0 | 7.4895 | 0 | 9.8204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 76.2657 | 14.95%
CZ 4B | 0.16754 | 0.028896 | 0.092109 | 0.019185 | 0 | 0.083159 | 0 | 0.11855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.75641 | 0.9871% | CZ 4B | 5.6449 | 0.97355 | 3.1033 | 0.68405 | 0 | 2.8018 | 0 | 3.9941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.5225 | 0.9871% | CZ 4B | 1.6539 | 0.28525 | 0.90927 | 0.18377 | 0 | 0.82091 | 0 | 1.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.4614 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.00056848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056848 | 0.9871% | CZ 4B | 17.3151 | 2.9863 | 9.5191 | 1.986 | 0 | 8.5941 | 0 | 12.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 78.1758 | 0.9871%
CZ 4C | 0.16933 | 0.02951 | 0.092109 | 0.017954 | 0 | 0.036465 | 0 | 0.09753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.68987 | 2.091% | CZ 4C | 5.7052 | 0.99423 | 3.1033 | 0.62548 | 0 | 1.2286 | 0 | 3.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.2635 | 2.091% | CZ 4C | 1.6716 | 0.29131 | 0.90927 | 0.17418 | 0 | 0.35997 | 0 | 0.96278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 6.8071 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00031008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00031008 | 2.091% | CZ 4C | 17.5001 | 3.0497 | 9.5191 | 1.8574 | 0 | 3.7685 | 0 | 10.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 71.2976 | 2.091%
CZ 5A | 0.16836 | 0.029305 | 0.092109 | 0.06558 | 0 | 0.045057 | 0 | 0.089961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.73734 | 15.83% | CZ 5A | 5.6724 | 0.98733 | 3.1033 | 2.9566 | 0 | 1.518 | 0 | 3.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.5894 | 15.83% | CZ 5A | 1.662 | 0.28929 | 0.90927 | 0.53617 | 0 | 0.44479 | 0 | 0.88806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.1676 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.011266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011266 | 15.83% | CZ 5A | 17.3997 | 3.0286 | 9.5191 | 6.8446 | 0 | 4.6565 | 0 | 9.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 76.269 | 15.83%
CZ 5B | 0.16724 | 0.029049 | 0.092109 | 0.042014 | 0 | 0.060707 | 0 | 0.11113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.74922 | 5.655% | CZ 5B | 5.6345 | 0.97872 | 3.1033 | 1.9021 | 0 | 2.0453 | 0 | 3.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.7291 | 5.655% | CZ 5B | 1.6509 | 0.28676 | 0.90927 | 0.3423 | 0 | 0.59928 | 0 | 1.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.3236 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.0073386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073386 | 5.655% | CZ 5B | 17.2834 | 3.0021 | 9.5191 | 4.3856 | 0 | 6.2738 | 0 | 11.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 77.4729 | 5.655%
CZ 5C | 0.16877 | 0.029561 | 0.092109 | 0.023412 | 0 | 0.028794 | 0 | 0.091904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.68152 | 0.09374% | CZ 5C | 5.6862 | 0.99595 | 3.1033 | 0.8219 | 0 | 0.9701 | 0 | 3.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 22.9947 | 0.09374% | CZ 5C | 1.6661 | 0.29181 | 0.90927 | 0.22618 | 0 | 0.28424 | 0 | 0.90725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 6.7228 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.00049958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00049958 | 0.09374% | CZ 5C | 17.442 | 3.055 | 9.5191 | 2.4225 | 0 | 2.9757 | 0 | 9.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 70.4357 | 0.09374%
CZ 6A | 0.16775 | 0.029305 | 0.092109 | 0.10342 | 0 | 0.04741 | 0 | 0.097785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.78475 | 3.229% | CZ 6A | 5.6518 | 0.98733 | 3.1033 | 6.3572 | 0 | 1.5973 | 0 | 3.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.3122 | 3.229% | CZ 6A | 1.656 | 0.28929 | 0.90927 | 0.59322 | 0 | 0.46801 | 0 | 0.96531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.3191 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.043325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043325 | 3.229% | CZ 6A | 17.3363 | 3.0286 | 9.5191 | 10.9459 | 0 | 4.8996 | 0 | 10.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 81.3587 | 3.229%
CZ 6B | 0.16765 | 0.029561 | 0.092109 | 0.067921 | 0 | 0.040608 | 0 | 0.10909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.7539 | 0.4789% | CZ 6B | 5.6483 | 0.99595 | 3.1033 | 3.9367 | 0 | 1.3681 | 0 | 3.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.0485 | 0.4789% | CZ 6B | 1.655 | 0.29181 | 0.90927 | 0.4251 | 0 | 0.40086 | 0 | 1.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.1969 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.024858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024858 | 0.4789% | CZ 6B | 17.3257 | 3.055 | 9.5191 | 7.1674 | 0 | 4.1966 | 0 | 11.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 78.0611 | 0.4789%
CZ 7 | 0.1655 | 0.029561 | 0.092109 | 0.11325 | 0 | 0.042091 | 0 | 0.10234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.79181 | 0.3515% | CZ 7 | 5.5759 | 0.99595 | 3.1033 | 7.8489 | 0 | 1.4181 | 0 | 3.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.711 | 0.3515% | CZ 7 | 1.6337 | 0.29181 | 0.90927 | 0.51749 | 0 | 0.41551 | 0 | 1.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.2161 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.060828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060828 | 0.3515% | CZ 7 | 17.1037 | 3.055 | 9.5191 | 12.0661 | 0 | 4.3499 | 0 | 10.5762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 82.1934 | 0.3515%
CZ 8 | 0.16857 | 0.031658 | 0.092109 | 0.16636 | 0 | 0.027924 | 0 | 0.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.84098 | 0.08183% | CZ 8 | 5.6793 | 1.0666 | 3.1033 | 13.0273 | 0 | 0.94081 | 0 | 3.6185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 35.7567 | 0.08183% | CZ 8 | 1.664 | 0.31251 | 0.90927 | 0.53718 | 0 | 0.27566 | 0 | 1.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.1969 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.11194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11194 | 0.08183% | CZ 8 | 17.4208 | 3.2717 | 9.5191 | 17.8587 | 0 | 2.8859 | 0 | 11.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 87.5791 | 0.08183%
US Weighted | 0.16929 | 0.029161 | 0.092109 | 0.029255 | 0 | 0.094484 | 0 | 0.099614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.76088 | 100% | US Weighted | 5.7037 | 0.98247 | 3.1033 | 1.3103 | 0 | 3.1833 | 0 | 3.3562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.9602 | 100% | US Weighted | 1.6712 | 0.28786 | 0.90927 | 0.24046 | 0 | 0.93271 | 0 | 0.98336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.4629 | 100% | US Weighted | 0 | 0 | 0 | 0.0048967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048967 | 100% | US Weighted | 17.4957 | 3.0137 | 9.5191 | 3.0526 | 0 | 9.7646 | 0 | 10.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 78.6638 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.23505 | 0.060962 | 0.092109 | 0 | 0 | 0.18585 | 0 | 0.097479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.91843 | 2.974% | CZ 1A | 7.9193 | 2.0539 | 3.1033 | 0 | 0 | 6.2617 | 0 | 3.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.9433 | 2.974% | CZ 1A | 2.3204 | 0.6018 | 0.90927 | 0 | 0 | 1.8347 | 0 | 0.96228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 9.0664 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 24.2919 | 6.3003 | 9.5191 | 0 | 0 | 19.2073 | 0 | 10.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 94.9161 | 2.974%
CZ 1B | 0.23449 | 0.06086 | 0.092109 | 0.0011251 | 0 | 0.20069 | 0 | 0.11072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.94696 | 0% | CZ 1B | 7.9004 | 2.0505 | 3.1033 | 0.037908 | 0 | 6.7614 | 0 | 3.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.9048 | 0% | CZ 1B | 2.3148 | 0.60079 | 0.90927 | 0.011107 | 0 | 1.9811 | 0 | 1.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 9.3481 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 24.2338 | 6.2897 | 9.5191 | 0.11628 | 0 | 20.7401 | 0 | 11.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 97.8654 | 0%
CZ 2A | 0.23485 | 0.06086 | 0.092109 | 0.0033932 | 0 | 0.15977 | 0 | 0.099985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.89794 | 20.09% | CZ 2A | 7.9125 | 2.0505 | 3.1033 | 0.11889 | 0 | 5.3829 | 0 | 3.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.2575 | 20.09% | CZ 2A | 2.3183 | 0.60079 | 0.90927 | 0.032816 | 0 | 1.5772 | 0 | 0.98701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.8634 | 20.09% | CZ 2A | 0 | 0 | 0 | 6.8907e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8907e-05 | 20.09% | CZ 2A | 24.2708 | 6.2897 | 9.5191 | 0.35109 | 0 | 16.5118 | 0 | 10.3331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 92.7989 | 20.09%
CZ 2B | 0.23546 | 0.060911 | 0.092109 | 0.0041259 | 0 | 0.14156 | 0 | 0.12034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.90148 | 5.157% | CZ 2B | 7.9331 | 2.0522 | 3.1033 | 0.14129 | 0 | 4.7695 | 0 | 4.0544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.3747 | 5.157% | CZ 2B | 2.3244 | 0.6013 | 0.90927 | 0.040389 | 0 | 1.3975 | 0 | 1.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.8988 | 5.157% | CZ 2B | 0 | 0 | 0 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4454e-05 | 5.157% | CZ 2B | 24.3342 | 6.295 | 9.5191 | 0.4266 | 0 | 14.6301 | 0 | 12.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 93.1651 | 5.157%
CZ 3A | 0.23536 | 0.06086 | 0.092109 | 0.023275 | 0 | 0.096251 | 0 | 0.09978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.8546 | 18.18% | CZ 3A | 7.9297 | 2.0505 | 3.1033 | 0.92353 | 0 | 3.2429 | 0 | 3.3618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.9324 | 18.18% | CZ 3A | 2.3234 | 0.60079 | 0.90927 | 0.20901 | 0 | 0.95016 | 0 | 0.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.4156 | 18.18% | CZ 3A | 0 | 0 | 0 | 0.0021017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021017 | 18.18% | CZ 3A | 24.3236 | 6.2897 | 9.5191 | 2.4179 | 0 | 9.9472 | 0 | 10.3119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 88.3329 | 18.18%
CZ 3B | 0.235 | 0.06086 | 0.092109 | 0.012996 | 0 | 0.10341 | 0 | 0.11635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.8677 | 8.466% | CZ 3B | 7.9176 | 2.0505 | 3.1033 | 0.47556 | 0 | 3.4841 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.2719 | 8.466% | CZ 3B | 2.3199 | 0.60079 | 0.90927 | 0.12268 | 0 | 1.0208 | 0 | 1.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.56 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00056848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056848 | 8.466% | CZ 3B | 24.2867 | 6.2897 | 9.5191 | 1.3465 | 0 | 10.6872 | 0 | 12.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 89.677 | 8.466%
CZ 3C | 0.2351 | 0.060962 | 0.092109 | 0.0032732 | 0 | 0.069248 | 0 | 0.092927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.80059 | 1.386% | CZ 3C | 7.9211 | 2.0539 | 3.1033 | 0.11028 | 0 | 2.3331 | 0 | 3.1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.9733 | 1.386% | CZ 3C | 2.3209 | 0.6018 | 0.90927 | 0.032311 | 0 | 0.68359 | 0 | 0.91734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.9032 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 24.2972 | 6.3003 | 9.5191 | 0.33827 | 0 | 7.1565 | 0 | 9.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 82.7385 | 1.386%
CZ 4A | 0.23132 | 0.061014 | 0.092109 | 0.032073 | 0 | 0.074976 | 0 | 0.095791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.83425 | 14.95% | CZ 4A | 7.7936 | 2.0557 | 3.1033 | 1.2302 | 0 | 2.5261 | 0 | 3.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.257 | 14.95% | CZ 4A | 2.2835 | 0.60231 | 0.90927 | 0.29434 | 0 | 0.74013 | 0 | 0.94562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2132 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0022567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022567 | 14.95% | CZ 4A | 23.9061 | 6.3055 | 9.5191 | 3.3281 | 0 | 7.7485 | 0 | 9.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 86.2304 | 14.95%
CZ 4B | 0.23076 | 0.06086 | 0.092109 | 0.017888 | 0 | 0.086176 | 0 | 0.11957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.85433 | 0.9871% | CZ 4B | 7.7746 | 2.0505 | 3.1033 | 0.63237 | 0 | 2.9034 | 0 | 4.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.8136 | 0.9871% | CZ 4B | 2.278 | 0.60079 | 0.90927 | 0.17216 | 0 | 0.8507 | 0 | 1.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.4293 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.0004479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0004479 | 0.9871% | CZ 4B | 23.848 | 6.2897 | 9.5191 | 1.8513 | 0 | 8.906 | 0 | 12.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 88.2949 | 0.9871%
CZ 4C | 0.23321 | 0.061014 | 0.092109 | 0.015874 | 0 | 0.041682 | 0 | 0.10479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.79565 | 2.091% | CZ 4C | 7.8573 | 2.0557 | 3.1033 | 0.54966 | 0 | 1.4043 | 0 | 3.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.8217 | 2.091% | CZ 4C | 2.3022 | 0.60231 | 0.90927 | 0.15449 | 0 | 0.41147 | 0 | 1.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.8522 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00022395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00022395 | 2.091% | CZ 4C | 24.1017 | 6.3055 | 9.5191 | 1.6418 | 0 | 4.3076 | 0 | 10.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 82.2291 | 2.091%
CZ 5A | 0.23209 | 0.060911 | 0.092109 | 0.061903 | 0 | 0.049813 | 0 | 0.095842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.83964 | 15.83% | CZ 5A | 7.8194 | 2.0522 | 3.1033 | 2.7584 | 0 | 1.6783 | 0 | 3.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.9615 | 15.83% | CZ 5A | 2.2911 | 0.6013 | 0.90927 | 0.51093 | 0 | 0.49174 | 0 | 0.94612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.1884 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.010147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010147 | 15.83% | CZ 5A | 23.9854 | 6.295 | 9.5191 | 6.4579 | 0 | 5.148 | 0 | 9.9049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 86.8338 | 15.83%
CZ 5B | 0.23091 | 0.060962 | 0.092109 | 0.039365 | 0 | 0.067765 | 0 | 0.11824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.85632 | 5.655% | CZ 5B | 7.7798 | 2.0539 | 3.1033 | 1.7729 | 0 | 2.2831 | 0 | 3.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.2976 | 5.655% | CZ 5B | 2.2795 | 0.6018 | 0.90927 | 0.32211 | 0 | 0.66895 | 0 | 1.1673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.3868 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.0067357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067357 | 5.655% | CZ 5B | 23.8638 | 6.3003 | 9.5191 | 4.1083 | 0 | 7.0032 | 0 | 12.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 88.5381 | 5.655%
CZ 5C | 0.23255 | 0.060962 | 0.092109 | 0.021006 | 0 | 0.03355 | 0 | 0.099217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.78636 | 0.09374% | CZ 5C | 7.8349 | 2.0539 | 3.1033 | 0.73058 | 0 | 1.1304 | 0 | 3.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.5167 | 0.09374% | CZ 5C | 2.2956 | 0.6018 | 0.90927 | 0.20397 | 0 | 0.33119 | 0 | 0.97944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.7593 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.00034454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034454 | 0.09374% | CZ 5C | 24.0329 | 6.3003 | 9.5191 | 2.173 | 0 | 3.4673 | 0 | 10.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 81.2698 | 0.09374%
CZ 6A | 0.23183 | 0.060962 | 0.092109 | 0.099256 | 0 | 0.052064 | 0 | 0.10397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.88717 | 3.229% | CZ 6A | 7.8108 | 2.0539 | 3.1033 | 6.0901 | 0 | 1.7541 | 0 | 3.5031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.6361 | 3.229% | CZ 6A | 2.2886 | 0.6018 | 0.90927 | 0.571 | 0 | 0.51395 | 0 | 1.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.349 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.041413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041413 | 3.229% | CZ 6A | 23.959 | 6.3003 | 9.5191 | 10.5043 | 0 | 5.3806 | 0 | 10.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 91.932 | 3.229%
CZ 6B | 0.23168 | 0.06086 | 0.092109 | 0.064686 | 0 | 0.045671 | 0 | 0.11625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.85822 | 0.4789% | CZ 6B | 7.8056 | 2.0505 | 3.1033 | 3.7489 | 0 | 1.5387 | 0 | 3.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.4844 | 0.4789% | CZ 6B | 2.287 | 0.60079 | 0.90927 | 0.4049 | 0 | 0.45085 | 0 | 1.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2384 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.02367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02367 | 0.4789% | CZ 6B | 23.9431 | 6.2897 | 9.5191 | 6.826 | 0 | 4.7199 | 0 | 12.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 88.8351 | 0.4789%
CZ 7 | 0.22769 | 0.060962 | 0.092109 | 0.11761 | 0 | 0.043778 | 0 | 0.10638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.8955 | 0.3515% | CZ 7 | 7.6712 | 2.0539 | 3.1033 | 8.2142 | 0 | 1.475 | 0 | 3.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 34.4224 | 0.3515% | CZ 7 | 2.2477 | 0.6018 | 0.90927 | 0.52809 | 0 | 0.43217 | 0 | 1.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2071 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.064118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064118 | 0.3515% | CZ 7 | 23.5308 | 6.3003 | 9.5191 | 12.5367 | 0 | 4.5243 | 0 | 10.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 92.9284 | 0.3515%
CZ 8 | 0.23127 | 0.061372 | 0.092109 | 0.17368 | 0 | 0.029305 | 0 | 0.11185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.94655 | 0.08183% | CZ 8 | 7.7918 | 2.0677 | 3.1033 | 13.6647 | 0 | 0.98733 | 0 | 3.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 39.7041 | 0.08183% | CZ 8 | 2.283 | 0.60584 | 0.90927 | 0.55131 | 0 | 0.28929 | 0 | 1.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.1809 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.11783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11783 | 0.08183% | CZ 8 | 23.9008 | 6.3425 | 9.5191 | 18.6507 | 0 | 3.0286 | 0 | 11.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 98.5244 | 0.08183%
US Weighted | 0.23359 | 0.060911 | 0.092109 | 0.027689 | 0 | 0.098899 | 0 | 0.10249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24697 | 0.86266 | 100% | US Weighted | 7.8701 | 2.0522 | 3.1033 | 1.2347 | 0 | 3.3321 | 0 | 3.4531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.3663 | 100% | US Weighted | 2.3059 | 0.6013 | 0.90927 | 0.2284 | 0 | 0.9763 | 0 | 1.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.471 | 100% | US Weighted | 0 | 0 | 0 | 0.0045519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045519 | 100% | US Weighted | 24.1408 | 6.295 | 9.5191 | 2.8886 | 0 | 10.2209 | 0 | 10.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5234 | 89.1801 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.27663 | 0.060962 | 0.092109 | 0 | 0 | 0.28374 | 0 | 0.13139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 1.0964 | 2.974% | CZ 1A | 9.3202 | 2.0539 | 3.1033 | 0 | 0 | 9.5597 | 0 | 4.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 36.9397 | 2.974% | CZ 1A | 2.7308 | 0.6018 | 0.90927 | 0 | 0 | 2.801 | 0 | 1.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.8233 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 28.589 | 6.3003 | 9.5191 | 0 | 0 | 29.3237 | 0 | 13.5783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 113.3095 | 2.974%
CZ 1B | 0.27627 | 0.06086 | 0.092109 | 0.0014831 | 0 | 0.23971 | 0 | 0.13067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 1.0527 | 0% | CZ 1B | 9.3082 | 2.0505 | 3.1033 | 0.04997 | 0 | 8.0761 | 0 | 4.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 35.4665 | 0% | CZ 1B | 2.7273 | 0.60079 | 0.90927 | 0.014641 | 0 | 2.3663 | 0 | 1.2899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.3917 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 28.552 | 6.2897 | 9.5191 | 0.15328 | 0 | 24.7729 | 0 | 13.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 108.7905 | 0%
CZ 2A | 0.27668 | 0.06086 | 0.092109 | 0.0035294 | 0 | 0.2438 | 0 | 0.12898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 1.0575 | 20.09% | CZ 2A | 9.3219 | 2.0505 | 3.1033 | 0.12234 | 0 | 8.214 | 0 | 4.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 35.6336 | 20.09% | CZ 2A | 2.7313 | 0.60079 | 0.90927 | 0.034331 | 0 | 2.4067 | 0 | 1.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.4391 | 20.09% | CZ 2A | 0 | 0 | 0 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.168e-05 | 20.09% | CZ 2A | 28.5943 | 6.2897 | 9.5191 | 0.36506 | 0 | 25.1957 | 0 | 13.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 109.2929 | 20.09%
CZ 2B | 0.27673 | 0.060911 | 0.092109 | 0.0042793 | 0 | 0.17107 | 0 | 0.13665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.99333 | 5.157% | CZ 2B | 9.3237 | 2.0522 | 3.1033 | 0.14646 | 0 | 5.7638 | 0 | 4.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.4694 | 5.157% | CZ 2B | 2.7318 | 0.6013 | 0.90927 | 0.041904 | 0 | 1.6888 | 0 | 1.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.8055 | 5.157% | CZ 2B | 0 | 0 | 0 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4454e-05 | 5.157% | CZ 2B | 28.5996 | 6.295 | 9.5191 | 0.44246 | 0 | 17.6798 | 0 | 14.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 102.6578 | 5.157%
CZ 3A | 0.27474 | 0.06086 | 0.092109 | 0.020747 | 0 | 0.14453 | 0 | 0.11609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.96065 | 18.18% | CZ 3A | 9.2565 | 2.0505 | 3.1033 | 0.80981 | 0 | 4.8695 | 0 | 3.9114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.4769 | 18.18% | CZ 3A | 2.7121 | 0.60079 | 0.90927 | 0.18832 | 0 | 1.4268 | 0 | 1.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.4668 | 18.18% | CZ 3A | 0 | 0 | 0 | 0.001671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001671 | 18.18% | CZ 3A | 28.3934 | 6.2897 | 9.5191 | 2.1541 | 0 | 14.9367 | 0 | 11.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 99.2901 | 18.18%
CZ 3B | 0.27464 | 0.06086 | 0.092109 | 0.01163 | 0 | 0.12034 | 0 | 0.12412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.93527 | 8.466% | CZ 3B | 9.253 | 2.0505 | 3.1033 | 0.41698 | 0 | 4.0544 | 0 | 4.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 31.5361 | 8.466% | CZ 3B | 2.7111 | 0.60079 | 0.90927 | 0.11107 | 0 | 1.188 | 0 | 1.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.229 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00037899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037899 | 8.466% | CZ 3B | 28.3829 | 6.2897 | 9.5191 | 1.2042 | 0 | 12.4367 | 0 | 12.8278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 96.6595 | 8.466%
CZ 3C | 0.27464 | 0.060962 | 0.092109 | 0.0027106 | 0 | 0.098348 | 0 | 0.10469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.88503 | 1.386% | CZ 3C | 9.253 | 2.0539 | 3.1033 | 0.091324 | 0 | 3.3135 | 0 | 3.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 29.8182 | 1.386% | CZ 3C | 2.7111 | 0.6018 | 0.90927 | 0.026758 | 0 | 0.97086 | 0 | 1.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.7367 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 28.3829 | 6.3003 | 9.5191 | 0.28013 | 0 | 10.1639 | 0 | 10.8193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 91.4647 | 1.386%
CZ 4A | 0.27234 | 0.061014 | 0.092109 | 0.041032 | 0 | 0.1028 | 0 | 0.11057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.93143 | 14.95% | CZ 4A | 9.1755 | 2.0557 | 3.1033 | 1.5903 | 0 | 3.4634 | 0 | 3.7253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 31.5894 | 14.95% | CZ 4A | 2.6884 | 0.60231 | 0.90927 | 0.37411 | 0 | 1.0148 | 0 | 1.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.1638 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0031353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031353 | 14.95% | CZ 4A | 28.145 | 6.3055 | 9.5191 | 4.2592 | 0 | 10.6238 | 0 | 11.4271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 96.2789 | 14.95%
CZ 4B | 0.27203 | 0.06086 | 0.092109 | 0.022886 | 0 | 0.12249 | 0 | 0.13936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.96131 | 0.9871% | CZ 4B | 9.1651 | 2.0505 | 3.1033 | 0.82018 | 0 | 4.1268 | 0 | 4.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.4372 | 0.9871% | CZ 4B | 2.6854 | 0.60079 | 0.90927 | 0.21861 | 0 | 1.2092 | 0 | 1.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.4824 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.00074075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074075 | 0.9871% | CZ 4B | 28.1133 | 6.2897 | 9.5191 | 2.3696 | 0 | 12.6587 | 0 | 14.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 99.3523 | 0.9871%
CZ 4C | 0.27331 | 0.061014 | 0.092109 | 0.021552 | 0 | 0.05457 | 0 | 0.11446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.86858 | 2.091% | CZ 4C | 9.2082 | 2.0557 | 3.1033 | 0.75126 | 0 | 1.8385 | 0 | 3.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 29.2892 | 2.091% | CZ 4C | 2.698 | 0.60231 | 0.90927 | 0.20901 | 0 | 0.53869 | 0 | 1.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.5706 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00037899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037899 | 2.091% | CZ 4C | 28.2455 | 6.3055 | 9.5191 | 2.2296 | 0 | 5.6396 | 0 | 11.8288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 89.7673 | 2.091%
CZ 5A | 0.27275 | 0.060911 | 0.092109 | 0.075501 | 0 | 0.067662 | 0 | 0.10745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.92795 | 15.83% | CZ 5A | 9.1893 | 2.0522 | 3.1033 | 3.3959 | 0 | 2.2797 | 0 | 3.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.1165 | 15.83% | CZ 5A | 2.6925 | 0.6013 | 0.90927 | 0.61846 | 0 | 0.66794 | 0 | 1.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.0336 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.012851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012851 | 15.83% | CZ 5A | 28.1873 | 6.295 | 9.5191 | 7.8793 | 0 | 6.9927 | 0 | 11.1047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 95.9772 | 15.83%
CZ 5B | 0.27203 | 0.060962 | 0.092109 | 0.04847 | 0 | 0.092262 | 0 | 0.13318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.95058 | 5.655% | CZ 5B | 9.1651 | 2.0539 | 3.1033 | 2.2019 | 0 | 3.1085 | 0 | 4.4869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.5956 | 5.655% | CZ 5B | 2.6854 | 0.6018 | 0.90927 | 0.3938 | 0 | 0.91078 | 0 | 1.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.2991 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.0085789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085789 | 5.655% | CZ 5B | 28.1133 | 6.3003 | 9.5191 | 5.0603 | 0 | 9.535 | 0 | 13.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 98.2904 | 5.655%
CZ 5C | 0.27295 | 0.060962 | 0.092109 | 0.026771 | 0 | 0.041937 | 0 | 0.10546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.85176 | 0.09374% | CZ 5C | 9.1962 | 2.0539 | 3.1033 | 0.9408 | 0 | 1.4129 | 0 | 3.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 28.736 | 0.09374% | CZ 5C | 2.6945 | 0.6018 | 0.90927 | 0.25849 | 0 | 0.41399 | 0 | 1.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.4025 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.00058571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00058571 | 0.09374% | CZ 5C | 28.2085 | 6.3003 | 9.5191 | 2.7702 | 0 | 4.3341 | 0 | 10.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 88.0298 | 0.09374%
CZ 6A | 0.27259 | 0.060962 | 0.092109 | 0.10816 | 0 | 0.071038 | 0 | 0.11451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.97094 | 3.229% | CZ 6A | 9.1841 | 2.0539 | 3.1033 | 6.6552 | 0 | 2.3934 | 0 | 3.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 35.7238 | 3.229% | CZ 6A | 2.6909 | 0.6018 | 0.90927 | 0.61947 | 0 | 0.70126 | 0 | 1.1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.1366 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.04541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04541 | 3.229% | CZ 6A | 28.1715 | 6.3003 | 9.5191 | 11.4485 | 0 | 7.3415 | 0 | 11.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 100.6141 | 3.229%
CZ 6B | 0.27244 | 0.06086 | 0.092109 | 0.070851 | 0 | 0.063929 | 0 | 0.1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.93946 | 0.4789% | CZ 6B | 9.1789 | 2.0505 | 3.1033 | 4.1348 | 0 | 2.1539 | 0 | 4.3026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.3998 | 0.4789% | CZ 6B | 2.6894 | 0.60079 | 0.90927 | 0.43923 | 0 | 0.63108 | 0 | 1.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.0139 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.026357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026357 | 0.4789% | CZ 6B | 28.1556 | 6.2897 | 9.5191 | 7.4792 | 0 | 6.6068 | 0 | 13.1978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 97.2473 | 0.4789%
CZ 7 | 0.2729 | 0.060962 | 0.092109 | 0.13323 | 0 | 0.057229 | 0 | 0.11492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.98292 | 0.3515% | CZ 7 | 9.1944 | 2.0539 | 3.1033 | 9.365 | 0 | 1.9281 | 0 | 3.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 37.9925 | 0.3515% | CZ 7 | 2.694 | 0.6018 | 0.90927 | 0.58918 | 0 | 0.56495 | 0 | 1.1344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.977 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.073541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073541 | 0.3515% | CZ 7 | 28.2032 | 6.3003 | 9.5191 | 14.2062 | 0 | 5.9144 | 0 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 102.0187 | 0.3515%
CZ 8 | 0.27408 | 0.061372 | 0.092109 | 0.18799 | 0 | 0.036874 | 0 | 0.11666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 1.0207 | 0.08183% | CZ 8 | 9.2341 | 2.0677 | 3.1033 | 14.862 | 0 | 1.2424 | 0 | 3.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 42.9157 | 0.08183% | CZ 8 | 2.7056 | 0.60584 | 0.90927 | 0.58615 | 0 | 0.36401 | 0 | 1.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.8059 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.12862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12862 | 0.08183% | CZ 8 | 28.3247 | 6.3425 | 9.5191 | 20.194 | 0 | 3.8108 | 0 | 12.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 106.2465 | 0.08183%
US Weighted | 0.27431 | 0.060911 | 0.092109 | 0.031705 | 0 | 0.14059 | 0 | 0.11968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25157 | 0.97087 | 100% | US Weighted | 9.2418 | 2.0522 | 3.1033 | 1.4201 | 0 | 4.7366 | 0 | 4.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.0622 | 100% | US Weighted | 2.7079 | 0.6013 | 0.90927 | 0.26058 | 0 | 1.3878 | 0 | 1.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.5317 | 100% | US Weighted | 0 | 0 | 0 | 0.005308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005308 | 100% | US Weighted | 28.3485 | 6.295 | 9.5191 | 3.3082 | 0 | 14.5293 | 0 | 12.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9991 | 100.3677 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.36291 | 0.1274 | 0.092262 | 0 | 0 | 0.31095 | 0 | 0.14305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.3066 | 2.974% | CZ 1A | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 10.4764 | 0 | 4.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.0216 | 2.974% | CZ 1A | 3.5825 | 1.2576 | 0.91078 | 0 | 0 | 3.0696 | 0 | 1.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.8983 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 37.5056 | 13.1661 | 9.535 | 0 | 0 | 32.1355 | 0 | 14.7834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 135.0327 | 2.974%
CZ 1B | 0.36291 | 0.12724 | 0.092262 | 0.0011763 | 0 | 0.25771 | 0 | 0.13998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2513 | 0% | CZ 1B | 12.2271 | 4.2871 | 3.1085 | 0.039631 | 0 | 8.6827 | 0 | 4.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.159 | 0% | CZ 1B | 3.5825 | 1.2561 | 0.91078 | 0.011612 | 0 | 2.544 | 0 | 1.3818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.3526 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5056 | 13.1502 | 9.535 | 0.12157 | 0 | 26.6334 | 0 | 14.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 129.3191 | 0%
CZ 2A | 0.36291 | 0.12719 | 0.092262 | 0.003376 | 0 | 0.26727 | 0 | 0.13967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2627 | 20.09% | CZ 2A | 12.2271 | 4.2853 | 3.1085 | 0.11717 | 0 | 9.0049 | 0 | 4.7058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.5467 | 20.09% | CZ 2A | 3.5825 | 1.2556 | 0.91078 | 0.032816 | 0 | 2.6384 | 0 | 1.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.4647 | 20.09% | CZ 2A | 0 | 0 | 0 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.168e-05 | 20.09% | CZ 2A | 37.5056 | 13.1449 | 9.535 | 0.3492 | 0 | 27.6218 | 0 | 14.4346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 130.4982 | 20.09%
CZ 2B | 0.36291 | 0.12729 | 0.092262 | 0.0039725 | 0 | 0.18672 | 0 | 0.14658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1898 | 5.157% | CZ 2B | 12.2271 | 4.2888 | 3.1085 | 0.13612 | 0 | 6.291 | 0 | 4.9384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0878 | 5.157% | CZ 2B | 3.5825 | 1.2566 | 0.91078 | 0.038875 | 0 | 1.8433 | 0 | 1.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.7447 | 5.157% | CZ 2B | 0 | 0 | 0 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4454e-05 | 5.157% | CZ 2B | 37.5056 | 13.1555 | 9.535 | 0.41075 | 0 | 19.2972 | 0 | 15.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 122.9592 | 5.157%
CZ 3A | 0.36291 | 0.12729 | 0.092262 | 0.020425 | 0 | 0.161 | 0 | 0.12637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1603 | 18.18% | CZ 3A | 12.2271 | 4.2888 | 3.1085 | 0.80809 | 0 | 5.4243 | 0 | 4.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.2124 | 18.18% | CZ 3A | 3.5825 | 1.2566 | 0.91078 | 0.18377 | 0 | 1.5893 | 0 | 1.2475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.4362 | 18.18% | CZ 3A | 0 | 0 | 0 | 0.0018088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018088 | 18.18% | CZ 3A | 37.5056 | 13.1555 | 9.535 | 2.1216 | 0 | 16.6386 | 0 | 13.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 119.9238 | 18.18%
CZ 3B | 0.36291 | 0.12724 | 0.092262 | 0.01117 | 0 | 0.13384 | 0 | 0.13399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1315 | 8.466% | CZ 3B | 12.2271 | 4.2871 | 3.1085 | 0.39803 | 0 | 4.5093 | 0 | 4.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.1424 | 8.466% | CZ 3B | 3.5825 | 1.2561 | 0.91078 | 0.10703 | 0 | 1.3212 | 0 | 1.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.1661 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00032731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00032731 | 8.466% | CZ 3B | 37.5056 | 13.1502 | 9.535 | 1.1563 | 0 | 13.832 | 0 | 13.8479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 116.9341 | 8.466%
CZ 3C | 0.36291 | 0.12724 | 0.092262 | 0.0024549 | 0 | 0.11318 | 0 | 0.11333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.0814 | 1.386% | CZ 3C | 12.2271 | 4.2871 | 3.1085 | 0.082709 | 0 | 3.8132 | 0 | 3.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.4348 | 1.386% | CZ 3C | 3.5825 | 1.2561 | 0.91078 | 0.024234 | 0 | 1.1173 | 0 | 1.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.6754 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 37.5056 | 13.1502 | 9.535 | 0.2537 | 0 | 11.6967 | 0 | 11.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 111.7609 | 1.386%
CZ 4A | 0.36291 | 0.12709 | 0.092262 | 0.049175 | 0 | 0.11671 | 0 | 0.12157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1397 | 14.95% | CZ 4A | 12.2271 | 4.2819 | 3.1085 | 2.0452 | 0 | 3.9321 | 0 | 4.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.7885 | 14.95% | CZ 4A | 3.5825 | 1.2546 | 0.91078 | 0.42762 | 0 | 1.1521 | 0 | 1.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.1934 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0058571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058571 | 14.95% | CZ 4A | 37.5056 | 13.1343 | 9.535 | 5.117 | 0 | 12.0614 | 0 | 12.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 117.8239 | 14.95%
CZ 4B | 0.36291 | 0.12719 | 0.092262 | 0.02678 | 0 | 0.13619 | 0 | 0.15143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1668 | 0.9871% | CZ 4B | 12.2271 | 4.2853 | 3.1085 | 0.99936 | 0 | 4.5886 | 0 | 5.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.4089 | 0.9871% | CZ 4B | 3.5825 | 1.2556 | 0.91078 | 0.24991 | 0 | 1.3445 | 0 | 1.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5039 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.0014643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014643 | 0.9871% | CZ 4B | 37.5056 | 13.1449 | 9.535 | 2.7763 | 0 | 14.0752 | 0 | 15.6502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 120.5943 | 0.9871%
CZ 4C | 0.36291 | 0.12694 | 0.092262 | 0.025084 | 0 | 0.061167 | 0 | 0.12371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.0621 | 2.091% | CZ 4C | 12.2271 | 4.2767 | 3.1085 | 0.88738 | 0 | 2.0608 | 0 | 4.1682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 35.8266 | 2.091% | CZ 4C | 3.5825 | 1.2531 | 0.91078 | 0.24133 | 0 | 0.60382 | 0 | 1.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.4785 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00063739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00063739 | 2.091% | CZ 4C | 37.5056 | 13.1185 | 9.535 | 2.5961 | 0 | 6.3214 | 0 | 12.7855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 109.7692 | 2.091%
CZ 5A | 0.36291 | 0.12714 | 0.092262 | 0.085032 | 0 | 0.076766 | 0 | 0.1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1327 | 15.83% | CZ 5A | 12.2271 | 4.2836 | 3.1085 | 4.0471 | 0 | 2.5864 | 0 | 3.9959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.3464 | 15.83% | CZ 5A | 3.5825 | 1.2551 | 0.91078 | 0.6634 | 0 | 0.75781 | 0 | 1.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.0061 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.01783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01783 | 15.83% | CZ 5A | 37.5056 | 13.1396 | 9.535 | 8.8939 | 0 | 7.9335 | 0 | 12.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 117.1716 | 15.83%
CZ 5B | 0.36291 | 0.12714 | 0.092262 | 0.053286 | 0 | 0.10321 | 0 | 0.14514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.154 | 5.655% | CZ 5B | 12.2271 | 4.2836 | 3.1085 | 2.5241 | 0 | 3.4772 | 0 | 4.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.6085 | 5.655% | CZ 5B | 3.5825 | 1.2551 | 0.91078 | 0.41752 | 0 | 1.0188 | 0 | 1.4328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.2833 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.010991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010991 | 5.655% | CZ 5B | 37.5056 | 13.1396 | 9.535 | 5.5724 | 0 | 10.666 | 0 | 15.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 119.3258 | 5.655%
CZ 5C | 0.36291 | 0.12694 | 0.092262 | 0.027079 | 0 | 0.04833 | 0 | 0.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.0417 | 0.09374% | CZ 5C | 12.2271 | 4.2767 | 3.1085 | 0.96147 | 0 | 1.6283 | 0 | 3.8442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 35.1442 | 0.09374% | CZ 5C | 3.5825 | 1.2531 | 0.91078 | 0.26001 | 0 | 0.4771 | 0 | 1.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.2756 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.00074075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074075 | 0.09374% | CZ 5C | 37.5056 | 13.1185 | 9.535 | 2.803 | 0 | 4.9948 | 0 | 11.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 107.6558 | 0.09374%
CZ 6A | 0.36291 | 0.12704 | 0.092262 | 0.13436 | 0 | 0.080346 | 0 | 0.12781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1948 | 3.229% | CZ 6A | 12.2271 | 4.2802 | 3.1085 | 8.912 | 0 | 2.707 | 0 | 4.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.6386 | 3.229% | CZ 6A | 3.5825 | 1.2541 | 0.91078 | 0.67349 | 0 | 0.79315 | 0 | 1.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.1414 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.066134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066134 | 3.229% | CZ 6A | 37.5056 | 13.1291 | 9.535 | 14.2792 | 0 | 8.3034 | 0 | 13.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 123.8678 | 3.229%
CZ 6B | 0.36291 | 0.12699 | 0.092262 | 0.08359 | 0 | 0.0716 | 0 | 0.13977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1472 | 0.4789% | CZ 6B | 12.2271 | 4.2784 | 3.1085 | 5.2425 | 0 | 2.4123 | 0 | 4.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.076 | 0.4789% | CZ 6B | 3.5825 | 1.2536 | 0.91078 | 0.46397 | 0 | 0.70681 | 0 | 1.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.9632 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.03659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03659 | 0.4789% | CZ 6B | 37.5056 | 13.1238 | 9.535 | 8.8566 | 0 | 7.3996 | 0 | 14.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 118.7728 | 0.4789%
CZ 7 | 0.36291 | 0.12689 | 0.092364 | 0.16102 | 0 | 0.064747 | 0 | 0.12811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2061 | 0.3515% | CZ 7 | 12.2271 | 4.275 | 3.1119 | 11.9921 | 0 | 2.1814 | 0 | 4.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 47.2018 | 0.3515% | CZ 7 | 3.5825 | 1.2526 | 0.91179 | 0.6119 | 0 | 0.63916 | 0 | 1.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.9283 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.099037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099037 | 0.3515% | CZ 7 | 37.5056 | 13.1132 | 9.5455 | 17.2307 | 0 | 6.6914 | 0 | 13.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 125.2336 | 0.3515%
CZ 8 | 0.36291 | 0.12617 | 0.09262 | 0.21091 | 0 | 0.041784 | 0 | 0.12852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2329 | 0.08183% | CZ 8 | 12.2271 | 4.2509 | 3.1205 | 17.167 | 0 | 1.4078 | 0 | 4.3301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 51.6013 | 0.08183% | CZ 8 | 3.5825 | 1.2455 | 0.91431 | 0.58413 | 0 | 0.41248 | 0 | 1.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.6734 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.15173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15173 | 0.08183% | CZ 8 | 37.5056 | 13.0392 | 9.572 | 22.6997 | 0 | 4.3182 | 0 | 13.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 128.3242 | 0.08183%
US Weighted | 0.36291 | 0.12719 | 0.092263 | 0.035691 | 0 | 0.15605 | 0 | 0.13046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1746 | 100% | US Weighted | 12.2271 | 4.2852 | 3.1085 | 1.6997 | 0 | 5.2576 | 0 | 4.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0714 | 100% | US Weighted | 3.5825 | 1.2556 | 0.91079 | 0.27829 | 0 | 1.5405 | 0 | 1.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5212 | 100% | US Weighted | 0 | 0 | 0 | 0.0074994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074994 | 100% | US Weighted | 37.5056 | 13.1444 | 9.535 | 3.7331 | 0 | 16.1272 | 0 | 13.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 121.435 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.36291 | 0.1274 | 0.092262 | 0 | 0 | 0.39549 | 0 | 0.14289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.391 | 2.974% | CZ 1A | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 13.3247 | 0 | 4.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 46.8647 | 2.974% | CZ 1A | 3.5825 | 1.2576 | 0.91078 | 0 | 0 | 3.9041 | 0 | 1.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 13.7314 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 37.5056 | 13.1661 | 9.535 | 0 | 0 | 40.8724 | 0 | 14.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 143.7537 | 2.974%
CZ 1B | 0.36291 | 0.12724 | 0.092262 | 0.0015343 | 0 | 0.32757 | 0 | 0.13998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.3215 | 0% | CZ 1B | 12.2271 | 4.2871 | 3.1085 | 0.051693 | 0 | 11.0364 | 0 | 4.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.5248 | 0% | CZ 1B | 3.5825 | 1.2561 | 0.91078 | 0.015146 | 0 | 3.2337 | 0 | 1.3818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 13.0458 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5056 | 13.1502 | 9.535 | 0.15856 | 0 | 33.8533 | 0 | 14.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 136.5761 | 0%
CZ 2A | 0.36291 | 0.12719 | 0.092262 | 0.0047741 | 0 | 0.34522 | 0 | 0.1431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.3455 | 20.09% | CZ 2A | 12.2271 | 4.2853 | 3.1085 | 0.16542 | 0 | 11.6309 | 0 | 4.8212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 45.3364 | 20.09% | CZ 2A | 3.5825 | 1.2556 | 0.91078 | 0.046448 | 0 | 3.4079 | 0 | 1.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 13.2815 | 20.09% | CZ 2A | 0 | 0 | 0 | 6.8907e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8907e-05 | 20.09% | CZ 2A | 37.5056 | 13.1449 | 9.535 | 0.49379 | 0 | 35.6768 | 0 | 14.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 139.0519 | 20.09%
CZ 2B | 0.36291 | 0.12729 | 0.092262 | 0.0057797 | 0 | 0.23679 | 0 | 0.15184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2469 | 5.157% | CZ 2B | 12.2271 | 4.2888 | 3.1085 | 0.19815 | 0 | 7.9779 | 0 | 5.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.0142 | 5.157% | CZ 2B | 3.5825 | 1.2566 | 0.91078 | 0.056545 | 0 | 2.3375 | 0 | 1.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.3087 | 5.157% | CZ 2B | 0 | 0 | 0 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.168e-05 | 5.157% | CZ 2B | 37.5056 | 13.1555 | 9.535 | 0.59762 | 0 | 24.4716 | 0 | 15.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 128.865 | 5.157%
CZ 3A | 0.36291 | 0.12729 | 0.092262 | 0.025422 | 0 | 0.20544 | 0 | 0.12929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2127 | 18.18% | CZ 3A | 12.2271 | 4.2888 | 3.1085 | 0.99245 | 0 | 6.9217 | 0 | 4.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.9924 | 18.18% | CZ 3A | 3.5825 | 1.2566 | 0.91078 | 0.23072 | 0 | 2.0281 | 0 | 1.2763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.9507 | 18.18% | CZ 3A | 0 | 0 | 0 | 0.00205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00205 | 18.18% | CZ 3A | 37.5056 | 13.1555 | 9.535 | 2.6395 | 0 | 21.2317 | 0 | 13.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 125.336 | 18.18%
CZ 3B | 0.36291 | 0.12724 | 0.092262 | 0.013711 | 0 | 0.168 | 0 | 0.13727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1714 | 8.466% | CZ 3B | 12.2271 | 4.2871 | 3.1085 | 0.48935 | 0 | 5.6604 | 0 | 4.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.4951 | 8.466% | CZ 3B | 3.5825 | 1.2561 | 0.91078 | 0.13127 | 0 | 1.6585 | 0 | 1.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5599 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00041344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00041344 | 8.466% | CZ 3B | 37.5056 | 13.1502 | 9.535 | 1.4194 | 0 | 17.3627 | 0 | 14.1862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 121.0662 | 8.466%
CZ 3C | 0.36291 | 0.12724 | 0.092262 | 0.0041937 | 0 | 0.15338 | 0 | 0.12939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1394 | 1.386% | CZ 3C | 12.2271 | 4.2871 | 3.1085 | 0.14129 | 0 | 5.1676 | 0 | 4.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.3888 | 1.386% | CZ 3C | 3.5825 | 1.2561 | 0.91078 | 0.041399 | 0 | 1.5141 | 0 | 1.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.2479 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 37.5056 | 13.1502 | 9.535 | 0.43341 | 0 | 15.8511 | 0 | 13.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 117.7546 | 1.386%
CZ 4A | 0.36291 | 0.12709 | 0.092262 | 0.064019 | 0 | 0.14729 | 0 | 0.12499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1886 | 14.95% | CZ 4A | 12.2271 | 4.2819 | 3.1085 | 2.6241 | 0 | 4.9625 | 0 | 4.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.5132 | 14.95% | CZ 4A | 3.5825 | 1.2546 | 0.91078 | 0.56242 | 0 | 1.454 | 0 | 1.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.6639 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0070458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070458 | 14.95% | CZ 4A | 37.5056 | 13.1343 | 9.535 | 6.6581 | 0 | 15.2221 | 0 | 12.9176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 122.8799 | 14.95%
CZ 4B | 0.36291 | 0.12719 | 0.092262 | 0.033792 | 0 | 0.16954 | 0 | 0.15568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2114 | 0.9871% | CZ 4B | 12.2271 | 4.2853 | 3.1085 | 1.2699 | 0 | 5.7121 | 0 | 5.2451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.9459 | 0.9871% | CZ 4B | 3.5825 | 1.2556 | 0.91078 | 0.31403 | 0 | 1.6736 | 0 | 1.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.9391 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.0019811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019811 | 0.9871% | CZ 4B | 37.5056 | 13.1449 | 9.535 | 3.5041 | 0 | 17.5213 | 0 | 16.0889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 125.2069 | 0.9871%
CZ 4C | 0.36291 | 0.12694 | 0.092262 | 0.034105 | 0 | 0.072214 | 0 | 0.12607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.0845 | 2.091% | CZ 4C | 12.2271 | 4.2767 | 3.1085 | 1.2096 | 0 | 2.433 | 0 | 4.2474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.6002 | 2.091% | CZ 4C | 3.5825 | 1.2531 | 0.91078 | 0.32766 | 0 | 0.71287 | 0 | 1.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.6971 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00091302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091302 | 2.091% | CZ 4C | 37.5056 | 13.1185 | 9.535 | 3.5301 | 0 | 7.4631 | 0 | 13.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 112.0879 | 2.091%
CZ 5A | 0.36291 | 0.12714 | 0.092262 | 0.12513 | 0 | 0.094666 | 0 | 0.12602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.1982 | 15.83% | CZ 5A | 12.2271 | 4.2836 | 3.1085 | 5.9578 | 0 | 3.1894 | 0 | 4.2457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.1101 | 15.83% | CZ 5A | 3.5825 | 1.2551 | 0.91078 | 0.97591 | 0 | 0.93451 | 0 | 1.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5685 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.026271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026271 | 15.83% | CZ 5A | 37.5056 | 13.1396 | 9.535 | 13.0882 | 0 | 9.7834 | 0 | 13.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 123.9822 | 15.83%
CZ 5B | 0.36291 | 0.12714 | 0.092262 | 0.078841 | 0 | 0.12837 | 0 | 0.15394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2135 | 5.655% | CZ 5B | 12.2271 | 4.2836 | 3.1085 | 3.8214 | 0 | 4.325 | 0 | 5.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.05 | 5.655% | CZ 5B | 3.5825 | 1.2551 | 0.91078 | 0.60483 | 0 | 1.2672 | 0 | 1.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.8058 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.017571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017571 | 5.655% | CZ 5B | 37.5056 | 13.1396 | 9.535 | 8.2525 | 0 | 13.2665 | 0 | 15.9092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 125.5155 | 5.655%
CZ 5C | 0.36291 | 0.12694 | 0.092262 | 0.043983 | 0 | 0.054007 | 0 | 0.11824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.0684 | 0.09374% | CZ 5C | 12.2271 | 4.2767 | 3.1085 | 1.5904 | 0 | 1.8196 | 0 | 3.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.104 | 0.09374% | CZ 5C | 3.5825 | 1.2531 | 0.91078 | 0.41803 | 0 | 0.53314 | 0 | 1.1673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.5305 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.0016365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016365 | 0.09374% | CZ 5C | 37.5056 | 13.1185 | 9.535 | 4.5552 | 0 | 5.5814 | 0 | 12.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 110.4228 | 0.09374%
CZ 6A | 0.36291 | 0.12704 | 0.092262 | 0.20234 | 0 | 0.098501 | 0 | 0.13798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2911 | 3.229% | CZ 6A | 12.2271 | 4.2802 | 3.1085 | 13.262 | 0 | 3.3187 | 0 | 4.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 49.9433 | 3.229% | CZ 6A | 3.5825 | 1.2541 | 0.91078 | 1.038 | 0 | 0.97237 | 0 | 1.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.7856 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.097193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097193 | 3.229% | CZ 6A | 37.5056 | 13.1291 | 9.535 | 21.4901 | 0 | 10.1798 | 0 | 14.2601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 134.0068 | 3.229%
CZ 6B | 0.36291 | 0.12699 | 0.092262 | 0.13039 | 0 | 0.084897 | 0 | 0.14929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2168 | 0.4789% | CZ 6B | 12.2271 | 4.2784 | 3.1085 | 8.2298 | 0 | 2.8603 | 0 | 5.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.8318 | 0.4789% | CZ 6B | 3.5825 | 1.2536 | 0.91078 | 0.7159 | 0 | 0.83808 | 0 | 1.4737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.4403 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.057865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057865 | 0.4789% | CZ 6B | 37.5056 | 13.1238 | 9.535 | 13.8194 | 0 | 8.7738 | 0 | 15.4282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 126.093 | 0.4789%
CZ 7 | 0.36291 | 0.12689 | 0.092364 | 0.24838 | 0 | 0.084744 | 0 | 0.15322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.3385 | 0.3515% | CZ 7 | 12.2271 | 4.275 | 3.1119 | 18.4627 | 0 | 2.8552 | 0 | 5.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 55.1922 | 0.3515% | CZ 7 | 3.5825 | 1.2526 | 0.91179 | 0.94915 | 0 | 0.83656 | 0 | 1.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.7109 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.15223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15223 | 0.3515% | CZ 7 | 37.5056 | 13.1132 | 9.5455 | 26.5757 | 0 | 8.758 | 0 | 15.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 139.2404 | 0.3515%
CZ 8 | 0.36291 | 0.12617 | 0.092671 | 0.29092 | 0 | 0.053751 | 0 | 0.15113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.3476 | 0.08183% | CZ 8 | 12.2271 | 4.2509 | 3.1222 | 23.8115 | 0 | 1.811 | 0 | 5.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 59.4124 | 0.08183% | CZ 8 | 3.5825 | 1.2455 | 0.91482 | 0.78608 | 0 | 0.53062 | 0 | 1.4919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.2171 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.21129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21129 | 0.08183% | CZ 8 | 37.5056 | 13.0392 | 9.5772 | 31.3231 | 0 | 5.555 | 0 | 15.6185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 140.5258 | 0.08183%
US Weighted | 0.36291 | 0.12719 | 0.092263 | 0.050289 | 0 | 0.19846 | 0 | 0.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27004 | 1.2363 | 100% | US Weighted | 12.2271 | 4.2852 | 3.1085 | 2.41 | 0 | 6.6864 | 0 | 4.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.3704 | 100% | US Weighted | 3.5825 | 1.2556 | 0.91079 | 0.38989 | 0 | 1.9591 | 0 | 1.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.0983 | 100% | US Weighted | 0 | 0 | 0 | 0.010793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010793 | 100% | US Weighted | 37.5056 | 13.1444 | 9.535 | 5.2615 | 0 | 20.5101 | 0 | 13.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9072 | 127.8366 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.19281 | 0.098297 | 0.00015343 | 0 | 0 | 0.21536 | 0 | 0.046796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.57648 | 2.974% | CZ 1A | 6.4961 | 3.3118 | 0.0051693 | 0 | 0 | 7.256 | 0 | 1.5766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 19.4227 | 2.974% | CZ 1A | 1.9033 | 0.97035 | 0.0015146 | 0 | 0 | 2.126 | 0 | 0.46195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 5.6909 | 2.974% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.974% | CZ 1A | 19.9262 | 10.1586 | 0.015856 | 0 | 0 | 22.257 | 0 | 4.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 59.5776 | 2.974%
CZ 1B | 0.19327 | 0.098246 | 0.00015343 | 0.00015343 | 0 | 0.13282 | 0 | 0.031044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.47875 | 0% | CZ 1B | 6.5116 | 3.3101 | 0.0051693 | 0.0051693 | 0 | 4.4749 | 0 | 1.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.1299 | 0% | CZ 1B | 1.9079 | 0.96985 | 0.0015146 | 0.0015146 | 0 | 1.3111 | 0 | 0.30645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.7261 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 19.9737 | 10.1534 | 0.015856 | 0.015856 | 0 | 13.7263 | 0 | 3.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 49.4771 | 0%
CZ 2A | 0.19286 | 0.098092 | 0.00015343 | 0.001074 | 0 | 0.19076 | 0 | 0.044852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.55086 | 20.09% | CZ 2A | 6.4978 | 3.3049 | 0.0051693 | 0.036185 | 0 | 6.4271 | 0 | 1.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.5595 | 20.09% | CZ 2A | 1.9039 | 0.96833 | 0.0015146 | 0.010602 | 0 | 1.8832 | 0 | 0.44277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 5.4379 | 20.09% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.09% | CZ 2A | 19.9314 | 10.1375 | 0.015856 | 0.11099 | 0 | 19.7147 | 0 | 4.6353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 56.9296 | 20.09%
CZ 2B | 0.19225 | 0.098195 | 0.00015343 | 0.0011763 | 0 | 0.10039 | 0 | 0.033754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.44898 | 5.157% | CZ 2B | 6.4771 | 3.3083 | 0.0051693 | 0.039631 | 0 | 3.3824 | 0 | 1.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 15.1271 | 5.157% | CZ 2B | 1.8978 | 0.96934 | 0.0015146 | 0.011612 | 0 | 0.99105 | 0 | 0.33321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4322 | 5.157% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.157% | CZ 2B | 19.868 | 10.1481 | 0.015856 | 0.12157 | 0 | 10.3753 | 0 | 3.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 46.401 | 5.157%
CZ 3A | 0.19245 | 0.09799 | 0.00015343 | 0.0011569 | 0 | 0.11287 | 0 | 0.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.45899 | 18.18% | CZ 3A | 6.484 | 3.3015 | 0.0051693 | 0.024129 | 0 | 3.8029 | 0 | 1.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 15.4493 | 18.18% | CZ 3A | 1.8998 | 0.96733 | 0.0015146 | 0.013631 | 0 | 1.1142 | 0 | 0.30898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.5332 | 18.18% | CZ 3A | 0 | 0 | 0 | -0.00022395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00022395 | 18.18% | CZ 3A | 19.8892 | 10.1269 | 0.015856 | 0.11823 | 0 | 11.665 | 0 | 3.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 47.4336 | 18.18%
CZ 3B | 0.19271 | 0.098399 | 0.00015343 | 3.1767e-05 | 0 | 0.068583 | 0 | 0.022759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.4057 | 8.466% | CZ 3B | 6.4926 | 3.3152 | 0.0051693 | -0.013779 | 0 | 2.3107 | 0 | 0.76678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 13.6538 | 8.466% | CZ 3B | 1.9023 | 0.97136 | 0.0015146 | 0.0025243 | 0 | 0.67703 | 0 | 0.22467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.0071 | 8.466% | CZ 3B | 0 | 0 | 0 | -0.00022395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00022395 | 8.466% | CZ 3B | 19.9156 | 10.1692 | 0.015856 | 0.0019497 | 0 | 7.0878 | 0 | 2.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 41.9262 | 8.466%
CZ 3C | 0.19255 | 0.09845 | 0.00015343 | 0.00040914 | 0 | 0.087813 | 0 | 0.03805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.44049 | 1.386% | CZ 3C | 6.4875 | 3.317 | 0.0051693 | 0.013785 | 0 | 2.9586 | 0 | 1.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 14.841 | 1.386% | CZ 3C | 1.9008 | 0.97187 | 0.0015146 | 0.0040389 | 0 | 0.86686 | 0 | 0.37562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.3484 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 19.8997 | 10.1745 | 0.015856 | 0.042284 | 0 | 9.0751 | 0 | 3.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 45.5236 | 1.386%
CZ 4A | 0.19496 | 0.09799 | 0.00015343 | 0.029829 | 0 | 0.074822 | 0 | 0.02997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.45079 | 14.95% | CZ 4A | 6.5684 | 3.3015 | 0.0051693 | 1.3043 | 0 | 2.5209 | 0 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 15.4871 | 14.95% | CZ 4A | 1.9246 | 0.96733 | 0.0015146 | 0.24991 | 0 | 0.73862 | 0 | 0.29585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4055 | 14.95% | CZ 4A | 0 | 0 | 0 | 0.0045134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045134 | 14.95% | CZ 4A | 20.1481 | 10.1269 | 0.015856 | 3.1096 | 0 | 7.7326 | 0 | 3.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 46.6142 | 14.95%
CZ 4B | 0.19537 | 0.098297 | 0.00015343 | 0.014607 | 0 | 0.086381 | 0 | 0.03713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.455 | 0.9871% | CZ 4B | 6.5822 | 3.3118 | 0.0051693 | 0.58582 | 0 | 2.9103 | 0 | 1.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 15.4234 | 0.9871% | CZ 4B | 1.9286 | 0.97035 | 0.0015146 | 0.13026 | 0 | 0.85272 | 0 | 0.36653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4777 | 0.9871% | CZ 4B | 0 | 0 | 0 | 0.0014126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014126 | 0.9871% | CZ 4B | 20.1904 | 10.1586 | 0.015856 | 1.518 | 0 | 8.9271 | 0 | 3.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 47.0311 | 0.9871%
CZ 4C | 0.19358 | 0.097427 | 0.00015343 | 0.01615 | 0 | 0.035749 | 0 | 0.028538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.39466 | 2.091% | CZ 4C | 6.5219 | 3.2825 | 0.0051693 | 0.58411 | 0 | 1.2044 | 0 | 0.96149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 13.3367 | 2.091% | CZ 4C | 1.9109 | 0.96177 | 0.0015146 | 0.15348 | 0 | 0.3529 | 0 | 0.28172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.89 | 2.091% | CZ 4C | 0 | 0 | 0 | 0.00060294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00060294 | 2.091% | CZ 4C | 20.0054 | 10.0688 | 0.015856 | 1.6727 | 0 | 3.6945 | 0 | 2.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 40.7903 | 2.091%
CZ 5A | 0.19455 | 0.097837 | 0.00015343 | 0.05955 | 0 | 0.049609 | 0 | 0.036056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.46082 | 15.83% | CZ 5A | 6.5547 | 3.2963 | 0.0051693 | 3.0013 | 0 | 1.6714 | 0 | 1.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.5207 | 15.83% | CZ 5A | 1.9205 | 0.96581 | 0.0015146 | 0.43974 | 0 | 0.48972 | 0 | 0.35593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4009 | 15.83% | CZ 5A | 0 | 0 | 0 | 0.015005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015005 | 15.83% | CZ 5A | 20.1059 | 10.1111 | 0.015856 | 6.2436 | 0 | 5.1269 | 0 | 3.7262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 47.7133 | 15.83%
CZ 5B | 0.19567 | 0.098092 | 0.00015343 | 0.036827 | 0 | 0.067662 | 0 | 0.042807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.46428 | 5.655% | CZ 5B | 6.5926 | 3.3049 | 0.0051693 | 1.9193 | 0 | 2.2797 | 0 | 1.4422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.3209 | 5.655% | CZ 5B | 1.9316 | 0.96833 | 0.0015146 | 0.26253 | 0 | 0.66794 | 0 | 0.42257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4822 | 5.655% | CZ 5B | 0 | 0 | 0 | 0.010233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010233 | 5.655% | CZ 5B | 20.2221 | 10.1375 | 0.015856 | 3.8669 | 0 | 6.9927 | 0 | 4.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 48.0427 | 5.655%
CZ 5C | 0.19414 | 0.097376 | 0.00015343 | 0.020571 | 0 | 0.025214 | 0 | 0.026339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.38686 | 0.09374% | CZ 5C | 6.5409 | 3.2808 | 0.0051693 | 0.76847 | 0 | 0.84949 | 0 | 0.88739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 13.1093 | 0.09374% | CZ 5C | 1.9165 | 0.96127 | 0.0015146 | 0.19185 | 0 | 0.2489 | 0 | 0.26001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.8077 | 0.09374% | CZ 5C | 0 | 0 | 0 | 0.001137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001137 | 0.09374% | CZ 5C | 20.0636 | 10.0635 | 0.015856 | 2.1327 | 0 | 2.6057 | 0 | 2.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 39.9871 | 0.09374%
CZ 6A | 0.19516 | 0.097734 | 0.00015343 | 0.098925 | 0 | 0.051092 | 0 | 0.040198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.50633 | 3.229% | CZ 6A | 6.5753 | 3.2928 | 0.0051693 | 6.9049 | 0 | 1.7214 | 0 | 1.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 20.631 | 3.229% | CZ 6A | 1.9266 | 0.9648 | 0.0015146 | 0.44479 | 0 | 0.50436 | 0 | 0.39683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4666 | 3.229% | CZ 6A | 0 | 0 | 0 | 0.053868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053868 | 3.229% | CZ 6A | 20.1693 | 10.1005 | 0.015856 | 10.5443 | 0 | 5.2802 | 0 | 4.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 52.6482 | 3.229%
CZ 6B | 0.19526 | 0.097427 | 0.00015343 | 0.062465 | 0 | 0.04429 | 0 | 0.040198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.46286 | 0.4789% | CZ 6B | 6.5788 | 3.2825 | 0.0051693 | 4.2932 | 0 | 1.4922 | 0 | 1.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 17.7833 | 0.4789% | CZ 6B | 1.9276 | 0.96177 | 0.0015146 | 0.2908 | 0 | 0.43721 | 0 | 0.39683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.2434 | 0.4789% | CZ 6B | 0 | 0 | 0 | 0.033006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033006 | 0.4789% | CZ 6B | 20.1799 | 10.0688 | 0.015856 | 6.652 | 0 | 4.5772 | 0 | 4.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 48.0318 | 0.4789%
CZ 7 | 0.19741 | 0.097325 | 0.00025572 | 0.13513 | 0 | 0.042653 | 0 | 0.050887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.54673 | 0.3515% | CZ 7 | 6.6511 | 3.2791 | 0.0086155 | 10.6138 | 0 | 1.4371 | 0 | 1.7145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 24.4812 | 0.3515% | CZ 7 | 1.9488 | 0.96076 | 0.0025243 | 0.43166 | 0 | 0.42106 | 0 | 0.50234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.4948 | 0.3515% | CZ 7 | 0 | 0 | 0 | 0.091405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091405 | 0.3515% | CZ 7 | 20.4018 | 10.0582 | 0.026427 | 14.5097 | 0 | 4.4081 | 0 | 5.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 57.047 | 0.3515%
CZ 8 | 0.19434 | 0.094512 | 0.00056257 | 0.12456 | 0 | 0.025827 | 0 | 0.043727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.5066 | 0.08183% | CZ 8 | 6.5478 | 3.1843 | 0.018954 | 10.7842 | 0 | 0.87016 | 0 | 1.4732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 23.6557 | 0.08183% | CZ 8 | 1.9185 | 0.93299 | 0.0055535 | 0.2489 | 0 | 0.25496 | 0 | 0.43166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.0203 | 0.08183% | CZ 8 | 0 | 0 | 0 | 0.099347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099347 | 0.08183% | CZ 8 | 20.0847 | 9.7675 | 0.05814 | 13.4643 | 0 | 2.6692 | 0 | 4.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 52.9467 | 0.08183%
US Weighted | 0.19362 | 0.098027 | 0.00015412 | 0.021034 | 0 | 0.10398 | 0 | 0.03559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023066 | 0.47547 | 100% | US Weighted | 6.5234 | 3.3027 | 0.0051927 | 1.0996 | 0 | 3.5031 | 0 | 1.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.4102 | 100% | US Weighted | 1.9113 | 0.96769 | 0.0015215 | 0.14943 | 0 | 1.0264 | 0 | 0.35133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.6354 | 100% | US Weighted | 0 | 0 | 0 | 0.0058963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058963 | 100% | US Weighted | 20.0099 | 10.1308 | 0.015928 | 2.2089 | 0 | 10.7455 | 0 | 3.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 49.1728 | 100%
Building Type: | Small Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 53.13% | 77.16% | 0.1663% | 0% | 0% | 54.45% | 0% | 32.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.44% | 2.974% | CZ 1A | 53.13% | 77.16% | 0.1663% | 0% | 0% | 54.45% | 0% | 32.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.44% | 2.974% | CZ 1A | 53.13% | 77.16% | 0.1663% | 0% | 0% | 54.45% | 0% | 32.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.44% | 2.974% | CZ 1A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.974% | CZ 1A | 53.13% | 77.16% | 0.1663% | 0% | 0% | 54.45% | 0% | 32.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.44% | 2.974%
CZ 1B | 53.26% | 77.21% | 0.1663% | 10% | 0% | 40.55% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.23% | 0% | CZ 1B | 53.26% | 77.21% | 0.1663% | 10% | 0% | 40.55% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.23% | 0% | CZ 1B | 53.26% | 77.21% | 0.1663% | 10% | 0% | 40.55% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.23% | 0% | CZ 1B | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | CZ 1B | 53.26% | 77.21% | 0.1663% | 10% | 0% | 40.55% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.23% | 0%
CZ 2A | 53.14% | 77.12% | 0.1663% | 22.5% | 0% | 55.26% | 0% | 31.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.94% | 20.09% | CZ 2A | 53.14% | 77.12% | 0.1663% | 21.88% | 0% | 55.26% | 0% | 31.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.94% | 20.09% | CZ 2A | 53.14% | 77.12% | 0.1663% | 22.83% | 0% | 55.26% | 0% | 31.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.94% | 20.09% | CZ 2A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.09% | CZ 2A | 53.14% | 77.12% | 0.1663% | 22.48% | 0% | 55.26% | 0% | 31.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.94% | 20.09%
CZ 2B | 52.97% | 77.14% | 0.1663% | 20.35% | 0% | 42.4% | 0% | 22.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.01% | 5.157% | CZ 2B | 52.97% | 77.14% | 0.1663% | 20% | 0% | 42.4% | 0% | 22.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36% | 5.157% | CZ 2B | 52.97% | 77.14% | 0.1663% | 20.54% | 0% | 42.4% | 0% | 22.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.01% | 5.157% | CZ 2B | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.157% | CZ 2B | 52.97% | 77.14% | 0.1663% | 20.34% | 0% | 42.4% | 0% | 22.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.01% | 5.157%
CZ 3A | 53.03% | 76.98% | 0.1663% | 4.551% | 0% | 54.94% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.85% | 18.18% | CZ 3A | 53.03% | 76.98% | 0.1663% | 2.431% | 0% | 54.94% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.69% | 18.18% | CZ 3A | 53.03% | 76.98% | 0.1663% | 5.908% | 0% | 54.94% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.93% | 18.18% | CZ 3A | 0% | 0% | 0% | -10.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -10.92% | 18.18% | CZ 3A | 53.03% | 76.98% | 0.1663% | 4.479% | 0% | 54.94% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.85% | 18.18%
CZ 3B | 53.1% | 77.33% | 0.1663% | 0.2317% | 0% | 40.82% | 0% | 16.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.63% | 8.466% | CZ 3B | 53.1% | 77.33% | 0.1663% | -2.816% | 0% | 40.82% | 0% | 16.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.57% | 8.466% | CZ 3B | 53.1% | 77.33% | 0.1663% | 1.923% | 0% | 40.82% | 0% | 16.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.66% | 8.466% | CZ 3B | 0% | 0% | 0% | -54.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -54.17% | 8.466% | CZ 3B | 53.1% | 77.33% | 0.1663% | 0.1374% | 0% | 40.82% | 0% | 16.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.63% | 8.466%
CZ 3C | 53.06% | 77.37% | 0.1663% | 9.756% | 0% | 57.25% | 0% | 29.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.66% | 1.386% | CZ 3C | 53.06% | 77.37% | 0.1663% | 9.756% | 0% | 57.25% | 0% | 29.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.66% | 1.386% | CZ 3C | 53.06% | 77.37% | 0.1663% | 9.756% | 0% | 57.25% | 0% | 29.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.66% | 1.386% | CZ 3C | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.386% | CZ 3C | 53.06% | 77.37% | 0.1663% | 9.756% | 0% | 57.25% | 0% | 29.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.66% | 1.386%
CZ 4A | 53.72% | 77.1% | 0.1663% | 46.59% | 0% | 50.8% | 0% | 23.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.93% | 14.95% | CZ 4A | 53.72% | 77.1% | 0.1663% | 49.7% | 0% | 50.8% | 0% | 23.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.23% | 14.95% | CZ 4A | 53.72% | 77.1% | 0.1663% | 44.43% | 0% | 50.8% | 0% | 23.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.77% | 14.95% | CZ 4A | 0% | 0% | 0% | 64.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 64.06% | 14.95% | CZ 4A | 53.72% | 77.1% | 0.1663% | 46.7% | 0% | 50.8% | 0% | 23.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.93% | 14.95%
CZ 4B | 53.83% | 77.28% | 0.1663% | 43.23% | 0% | 50.95% | 0% | 23.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.56% | 0.9871% | CZ 4B | 53.83% | 77.28% | 0.1663% | 46.13% | 0% | 50.95% | 0% | 23.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.67% | 0.9871% | CZ 4B | 53.83% | 77.28% | 0.1663% | 41.48% | 0% | 50.95% | 0% | 23.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.5% | 0.9871% | CZ 4B | 0% | 0% | 0% | 71.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 71.3% | 0.9871% | CZ 4B | 53.83% | 77.28% | 0.1663% | 43.32% | 0% | 50.95% | 0% | 23.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.56% | 0.9871%
CZ 4C | 53.34% | 76.75% | 0.1663% | 47.36% | 0% | 49.5% | 0% | 22.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.39% | 2.091% | CZ 4C | 53.34% | 76.75% | 0.1663% | 48.29% | 0% | 49.5% | 0% | 22.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.44% | 2.091% | CZ 4C | 53.34% | 76.75% | 0.1663% | 46.84% | 0% | 49.5% | 0% | 22.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.36% | 2.091% | CZ 4C | 0% | 0% | 0% | 66.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 66.04% | 2.091% | CZ 4C | 53.34% | 76.75% | 0.1663% | 47.38% | 0% | 49.5% | 0% | 22.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.39% | 2.091%
CZ 5A | 53.61% | 76.95% | 0.1663% | 47.59% | 0% | 52.4% | 0% | 28.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.46% | 15.83% | CZ 5A | 53.61% | 76.95% | 0.1663% | 50.38% | 0% | 52.4% | 0% | 28.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 39.23% | 15.83% | CZ 5A | 53.61% | 76.95% | 0.1663% | 45.06% | 0% | 52.4% | 0% | 28.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.04% | 15.83% | CZ 5A | 0% | 0% | 0% | 57.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.11% | 15.83% | CZ 5A | 53.61% | 76.95% | 0.1663% | 47.7% | 0% | 52.4% | 0% | 28.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.48% | 15.83%
CZ 5B | 53.92% | 77.15% | 0.1663% | 46.71% | 0% | 52.71% | 0% | 27.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.26% | 5.655% | CZ 5B | 53.92% | 77.15% | 0.1663% | 50.22% | 0% | 52.71% | 0% | 27.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.81% | 5.655% | CZ 5B | 53.92% | 77.15% | 0.1663% | 43.41% | 0% | 52.71% | 0% | 27.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.97% | 5.655% | CZ 5B | 0% | 0% | 0% | 58.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.24% | 5.655% | CZ 5B | 53.92% | 77.15% | 0.1663% | 46.86% | 0% | 52.71% | 0% | 27.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.28% | 5.655%
CZ 5C | 53.49% | 76.71% | 0.1663% | 46.77% | 0% | 46.69% | 0% | 22.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.21% | 0.09374% | CZ 5C | 53.49% | 76.71% | 0.1663% | 48.32% | 0% | 46.69% | 0% | 22.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.31% | 0.09374% | CZ 5C | 53.49% | 76.71% | 0.1663% | 45.89% | 0% | 46.69% | 0% | 22.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.16% | 0.09374% | CZ 5C | 0% | 0% | 0% | 69.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 69.47% | 0.09374% | CZ 5C | 53.49% | 76.71% | 0.1663% | 46.82% | 0% | 46.69% | 0% | 22.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.21% | 0.09374%
CZ 6A | 53.78% | 76.93% | 0.1663% | 48.89% | 0% | 51.87% | 0% | 29.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 39.22% | 3.229% | CZ 6A | 53.78% | 76.93% | 0.1663% | 52.06% | 0% | 51.87% | 0% | 29.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.31% | 3.229% | CZ 6A | 53.78% | 76.93% | 0.1663% | 42.85% | 0% | 51.87% | 0% | 29.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.9% | 3.229% | CZ 6A | 0% | 0% | 0% | 55.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.42% | 3.229% | CZ 6A | 53.78% | 76.93% | 0.1663% | 49.07% | 0% | 51.87% | 0% | 29.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 39.29% | 3.229%
CZ 6B | 53.8% | 76.72% | 0.1663% | 47.91% | 0% | 52.17% | 0% | 26.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.04% | 0.4789% | CZ 6B | 53.8% | 76.72% | 0.1663% | 52.17% | 0% | 52.17% | 0% | 26.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 39.67% | 0.4789% | CZ 6B | 53.8% | 76.72% | 0.1663% | 40.62% | 0% | 52.17% | 0% | 26.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.09% | 0.4789% | CZ 6B | 0% | 0% | 0% | 57.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.04% | 0.4789% | CZ 6B | 53.8% | 76.72% | 0.1663% | 48.14% | 0% | 52.17% | 0% | 26.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.09% | 0.4789%
CZ 7 | 54.4% | 76.7% | 0.2769% | 54.41% | 0% | 50.33% | 0% | 33.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.85% | 0.3515% | CZ 7 | 54.4% | 76.7% | 0.2769% | 57.49% | 0% | 50.33% | 0% | 33.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 44.36% | 0.3515% | CZ 7 | 54.4% | 76.7% | 0.2769% | 45.48% | 0% | 50.33% | 0% | 33.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.38% | 0.3515% | CZ 7 | 0% | 0% | 0% | 60.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.04% | 0.3515% | CZ 7 | 54.4% | 76.7% | 0.2769% | 54.6% | 0% | 50.33% | 0% | 33.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 40.97% | 0.3515%
CZ 8 | 53.55% | 74.91% | 0.6071% | 42.82% | 0% | 48.05% | 0% | 28.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.59% | 0.08183% | CZ 8 | 53.55% | 74.91% | 0.6071% | 45.29% | 0% | 48.05% | 0% | 28.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 39.82% | 0.08183% | CZ 8 | 53.55% | 74.91% | 0.6071% | 31.66% | 0% | 48.05% | 0% | 28.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 35.84% | 0.08183% | CZ 8 | 0% | 0% | 0% | 47.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 47.02% | 0.08183% | CZ 8 | 53.55% | 74.91% | 0.6071% | 42.99% | 0% | 48.05% | 0% | 28.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 37.68% | 0.08183%
US Weighted | 53.35% | 77.07% | 0.167% | 41.83% | 0% | 52.39% | 0% | 26.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.46% | 100% | US Weighted | 53.35% | 77.07% | 0.167% | 45.63% | 0% | 52.39% | 0% | 26.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.73% | 100% | US Weighted | 53.35% | 77.07% | 0.167% | 38.33% | 0% | 52.39% | 0% | 26.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.31% | 100% | US Weighted | 0% | 0% | 0% | 54.63% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.63% | 100% | US Weighted | 53.35% | 77.07% | 0.167% | 41.98% | 0% | 52.39% | 0% | 26.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 38.47% | 100%

## OffM
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Medium Office |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Medium Office | [14 empty] | Prototype Floor Area: | 53628 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.15895 | 0.0246 | 0.014181 | 0.080397 | 0 | 0.16323 | 0 | 0.042516 | 0.00036446 | 7.8706e-05 | 0 | 0.086781 | 0.006172 | 0 | 0 | 0.30678 | 0.88406 |  | STD2016 | 5.3552 | 0.82883 | 1.4181 | 3.7558 | 0 | 5.4996 | 0 | 1.4324 | 0.012279 | 0.0026517 | 0 | 2.9238 | 0.20795 | 0 | 0 | 10.3361 | 31.7728 |  | STD2016 | 1.5691 | 0.24285 | 0 | 0.63777 | 0 | 1.6114 | 0 | 0.41971 | 0.0035978 | 0.00077696 | 0 | 0.85667 | 0.060928 | 0 | 0 | 3.0285 | 8.4312 |  | STD2016 | 0 | 0 | 0.014181 | 0.015791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029972 |  | STD2016 | 16.4267 | 2.5424 | 1.55 | 8.4028 | 0 | 16.8697 | 0 | 4.3939 | 0.037666 | 0.008134 | 0 | 8.9685 | 0.63785 | 0 | 0 | 31.7051 | 91.5427
STD2013 | 0.1722 | 0.054071 | 0.014465 | 0.082159 | 0 | 0.1671 | 0 | 0.043959 | 6.7252e-05 | 7.8706e-05 | 0 | 0.086781 | 0.0089492 | 0 | 0 | 0.30678 | 0.93661 |  | STD2013 | 5.8016 | 1.8217 | 1.4465 | 3.7912 | 0 | 5.6298 | 0 | 1.4811 | 0.0022658 | 0.0026517 | 0 | 2.9238 | 0.30151 | 0 | 0 | 10.3361 | 33.5381 |  | STD2013 | 1.6999 | 0.53377 | 0 | 0.65874 | 0 | 1.6495 | 0 | 0.43395 | 0.00066389 | 0.00077696 | 0 | 0.85667 | 0.088343 | 0 | 0 | 3.0285 | 8.9508 |  | STD2013 | 0 | 0 | 0.014465 | 0.015429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029894 |  | STD2013 | 17.7959 | 5.588 | 1.581 | 8.5827 | 0 | 17.2688 | 0 | 4.543 | 0.0069502 | 0.008134 | 0 | 8.9685 | 0.92486 | 0 | 0 | 31.7051 | 96.9731
STD2010 | 0.19973 | 0.054071 | 0.014467 | 0.096166 | 0 | 0.19044 | 0 | 0.049396 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091254 | 0 | 0 | 0.31054 | 1.011 |  | STD2010 | 6.7292 | 1.8217 | 1.4467 | 4.2909 | 0 | 6.4163 | 0 | 1.6642 | 0 | 0.0026517 | 0 | 2.9318 | 0.30745 | 0 | 0 | 10.4627 | 36.0736 |  | STD2010 | 1.9717 | 0.53377 | 0 | 0.79286 | 0 | 1.88 | 0 | 0.48762 | 0 | 0.00077696 | 0 | 0.859 | 0.090083 | 0 | 0 | 3.0656 | 9.6813 |  | STD2010 | 0 | 0 | 0.014467 | 0.015849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030316 |  | STD2010 | 20.6412 | 5.588 | 1.5813 | 10.0328 | 0 | 19.6816 | 0 | 5.1049 | 0 | 0.008134 | 0 | 8.9929 | 0.94308 | 0 | 0 | 32.0934 | 104.6673
STD2007 | 0.29004 | 0.11821 | 0.014763 | 0.13367 | 0 | 0.25229 | 0 | 0.054388 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017712 | 0 | 0 | 0.33648 | 1.3094 |  | STD2007 | 9.772 | 3.9826 | 1.4763 | 5.8577 | 0 | 8.5001 | 0 | 1.8324 | 0 | 0.0026517 | 0 | 3.093 | 0.59674 | 0 | 0 | 11.3367 | 46.4501 |  | STD2007 | 2.8632 | 1.1669 | 0 | 1.118 | 0 | 2.4905 | 0 | 0.5369 | 0 | 0.00077696 | 0 | 0.90624 | 0.17484 | 0 | 0 | 3.3216 | 12.579 |  | STD2007 | 0 | 0 | 0.014763 | 0.020421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035184 |  | STD2007 | 29.9747 | 12.2163 | 1.6136 | 13.936 | 0 | 26.0733 | 0 | 5.6208 | 0 | 0.008134 | 0 | 9.4875 | 1.8304 | 0 | 0 | 34.7743 | 135.5351
STD2004 | 0.29004 | 0.11821 | 0.014764 | 0.18081 | 0 | 0.26519 | 0 | 0.063859 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017711 | 0 | 0 | 0.33648 | 1.3789 |  | STD2004 | 9.772 | 3.9826 | 1.4764 | 8.0745 | 0 | 8.9346 | 0 | 2.1515 | 0 | 0.0026517 | 0 | 3.093 | 0.59671 | 0 | 0 | 11.3367 | 49.4206 |  | STD2004 | 2.8632 | 1.1669 | 0 | 1.4898 | 0 | 2.6178 | 0 | 0.6304 | 0 | 0.00077696 | 0 | 0.90624 | 0.17483 | 0 | 0 | 3.3216 | 13.1716 |  | STD2004 | 0 | 0 | 0.014764 | 0.029899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044663 |  | STD2004 | 29.9747 | 12.2163 | 1.6137 | 18.8645 | 0 | 27.4061 | 0 | 6.5996 | 0 | 0.008134 | 0 | 9.4875 | 1.8303 | 0 | 0 | 34.7743 | 142.7753
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.0893e-06 | 0.047144 | 0 | 0.012897 | 0 | 0.009471 | 0 | 0 | 0 | 0 | -1.0031e-06 | 0 | 0 | 0 | 0.069512 |  | 2004-2007 | 0 | 0 | 0.00010893 | 2.2169 | 0 | 0.43453 | 0 | 0.31909 | 0 | 0 | 0 | 0 | -3.3796e-05 | 0 | 0 | 0 | 2.9706 |  | 2004-2007 | 0 | 0 | 0 | 0.37182 | 0 | 0.12732 | 0 | 0.093494 | 0 | 0 | 0 | 0 | -9.9023e-06 | 0 | 0 | 0 | 0.59262 |  | 2004-2007 | 0 | 0 | 1.0893e-06 | 0.0094786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094797 |  | 2004-2007 | 0 | 0 | 0.00011906 | 4.9286 | 0 | 1.3329 | 0 | 0.97879 | 0 | 0 | 0 | 0 | -0.00010367 | 0 | 0 | 0 | 7.2403
2007-2010 | 0.090313 | 0.064137 | 0.00029557 | 0.037505 | 0 | 0.061847 | 0 | 0.0049924 | 0 | 0 | 0 | 0.0047853 | 0.0085864 | 0 | 0 | 0.025941 | 0.2984 |  | 2007-2010 | 3.0428 | 2.1609 | 0.029557 | 1.5668 | 0 | 2.0837 | 0 | 0.1682 | 0 | 0 | 0 | 0.16123 | 0.28929 | 0 | 0 | 0.87401 | 10.3764 |  | 2007-2010 | 0.89154 | 0.63314 | 0 | 0.3251 | 0 | 0.61053 | 0 | 0.049283 | 0 | 0 | 0 | 0.047239 | 0.084762 | 0 | 0 | 0.25609 | 2.8977 |  | 2007-2010 | 0 | 0 | 0.00029557 | 0.004572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048676 |  | 2007-2010 | 9.3335 | 6.6283 | 0.032306 | 3.9032 | 0 | 6.3916 | 0 | 0.51595 | 0 | 0 | 0 | 0.49455 | 0.88737 | 0 | 0 | 2.681 | 30.8678
2010-2013 | 0.027531 | 0 | 2.3296e-06 | 0.014007 | 0 | 0.023347 | 0 | 0.0054366 | -6.7252e-05 | 0 | 0 | 0.00023612 | 0.00017626 | 0 | 0 | 0.0037569 | 0.074426 |  | 2010-2013 | 0.92758 | 0 | 0.00023296 | 0.49973 | 0 | 0.78659 | 0 | 0.18317 | -0.0022658 | 0 | 0 | 0.0079552 | 0.0059384 | 0 | 0 | 0.12658 | 2.5355 |  | 2010-2013 | 0.27178 | 0 | 0 | 0.13412 | 0 | 0.23047 | 0 | 0.053668 | -0.00066389 | 0 | 0 | 0.0023309 | 0.0017399 | 0 | 0 | 0.037087 | 0.73054 |  | 2010-2013 | 0 | 0 | 2.3296e-06 | 0.00041972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00042205 |  | 2010-2013 | 2.8453 | 0 | 0.00025463 | 1.45 | 0 | 2.4128 | 0 | 0.56185 | -0.0069502 | 0 | 0 | 0.024402 | 0.018215 | 0 | 0 | 0.38826 | 7.6941
2013-2016 | 0.013249 | 0.02947 | 0.00028386 | 0.0017622 | 0 | 0.0038617 | 0 | 0.001443 | -0.00029721 | 0 | 0 | 0 | 0.0027772 | 0 | 0 | 0 | 0.052551 |  | 2013-2016 | 0.4464 | 0.99291 | 0.028386 | 0.035351 | 0 | 0.13011 | 0 | 0.048616 | -0.010013 | 0 | 0 | 0 | 0.093567 | 0 | 0 | 0 | 1.7653 |  | 2013-2016 | 0.13079 | 0.29092 | 0 | 0.020972 | 0 | 0.038121 | 0 | 0.014245 | -0.0029339 | 0 | 0 | 0 | 0.027415 | 0 | 0 | 0 | 0.51954 |  | 2013-2016 | 0 | 0 | 0.00028386 | -0.00036227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.8411e-05 |  | 2013-2016 | 1.3693 | 3.0457 | 0.031026 | 0.17996 | 0 | 0.39909 | 0 | 0.14913 | -0.030715 | 0 | 0 | 0 | 0.28701 | 0 | 0 | 0 | 5.4305
2004-2016 | 0.13109 | 0.093607 | 0.00058285 | 0.10042 | 0 | 0.10195 | 0 | 0.021343 | -0.00036446 | 0 | 0 | 0.0050214 | 0.011539 | 0 | 0 | 0.029698 | 0.49489 |  | 2004-2016 | 4.4168 | 3.1538 | 0.058285 | 4.3187 | 0 | 3.435 | 0 | 0.71908 | -0.012279 | 0 | 0 | 0.16918 | 0.38876 | 0 | 0 | 1.0006 | 17.6478 |  | 2004-2016 | 1.2941 | 0.92406 | 0 | 0.85201 | 0 | 1.0064 | 0 | 0.21069 | -0.0035978 | 0 | 0 | 0.04957 | 0.11391 | 0 | 0 | 0.29317 | 4.7404 |  | 2004-2016 | 0 | 0 | 0.00058285 | 0.014108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014691 |  | 2004-2016 | 13.5481 | 9.674 | 0.063705 | 10.4618 | 0 | 10.5364 | 0 | 2.2057 | -0.037666 | 0 | 0 | 0.51895 | 1.1925 | 0 | 0 | 3.0692 | 51.2327
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.007378% | 26.07% |  | 4.863% |  | 14.83% |  | 0% |  | 0% | -0.005664% |  |  | 0% | 5.041% |  | 2004-2007 | 0% | 0% | 0.007378% | 27.46% |  | 4.863% |  | 14.83% |  | 0% |  | 0% | -0.005664% |  |  | 0% | 6.011% |  | 2004-2007 | 0% | 0% |  | 24.96% |  | 4.863% |  | 14.83% |  | 0% |  | 0% | -0.005664% |  |  | 0% | 4.499% |  | 2004-2007 |  |  | 0.007378% | 31.7% | [12 empty] | 21.22% |  | 2004-2007 | 0% | 0% | 0.007378% | 26.13% |  | 4.863% |  | 14.83% |  | 0% |  | 0% | -0.005664% |  |  | 0% | 5.071%
2007-2010 | 31.14% | 54.26% | 2.002% | 28.06% |  | 24.51% |  | 9.179% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 22.79% |  | 2007-2010 | 31.14% | 54.26% | 2.002% | 26.75% |  | 24.51% |  | 9.179% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 22.34% |  | 2007-2010 | 31.14% | 54.26% |  | 29.08% |  | 24.51% |  | 9.179% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 23.04% |  | 2007-2010 |  |  | 2.002% | 22.39% | [12 empty] | 13.83% |  | 2007-2010 | 31.14% | 54.26% | 2.002% | 28.01% |  | 24.51% |  | 9.179% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 22.77%
2010-2013 | 13.78% | 0% | 0.0161% | 14.56% |  | 12.26% |  | 11.01% |  | 0% |  | 0.2713% | 1.931% |  |  | 1.21% | 7.361% |  | 2010-2013 | 13.78% | 0% | 0.0161% | 11.65% |  | 12.26% |  | 11.01% |  | 0% |  | 0.2713% | 1.931% |  |  | 1.21% | 7.029% |  | 2010-2013 | 13.78% | 0% |  | 16.92% |  | 12.26% |  | 11.01% |  | 0% |  | 0.2713% | 1.931% |  |  | 1.21% | 7.546% |  | 2010-2013 |  |  | 0.0161% | 2.648% | [12 empty] | 1.392% |  | 2010-2013 | 13.78% | 0% | 0.0161% | 14.45% |  | 12.26% |  | 11.01% |  | 0% |  | 0.2713% | 1.931% |  |  | 1.21% | 7.351%
2013-2016 | 7.694% | 54.5% | 1.962% | 2.145% |  | 2.311% |  | 3.283% | -441.9% | 0% |  | 0% | 31.03% |  |  | 0% | 5.611% |  | 2013-2016 | 7.694% | 54.5% | 1.962% | 0.9325% |  | 2.311% |  | 3.283% | -441.9% | 0% |  | 0% | 31.03% |  |  | 0% | 5.264% |  | 2013-2016 | 7.694% | 54.5% |  | 3.184% |  | 2.311% |  | 3.283% | -441.9% | 0% |  | 0% | 31.03% |  |  | 0% | 5.804% |  | 2013-2016 |  |  | 1.962% | -2.348% | [12 empty] | -0.2623% |  | 2013-2016 | 7.694% | 54.5% | 1.962% | 2.097% |  | 2.311% |  | 3.283% | -441.9% | 0% |  | 0% | 31.03% |  |  | 0% | 5.6%
2004-2016 | 45.2% | 79.19% | 3.948% | 55.54% |  | 38.45% |  | 33.42% |  | 0% |  | 5.47% | 65.15% |  |  | 8.826% | 35.89% |  | 2004-2016 | 45.2% | 79.19% | 3.948% | 53.49% |  | 38.45% |  | 33.42% |  | 0% |  | 5.47% | 65.15% |  |  | 8.826% | 35.71% |  | 2004-2016 | 45.2% | 79.19% |  | 57.19% |  | 38.45% |  | 33.42% |  | 0% |  | 5.47% | 65.15% |  |  | 8.826% | 35.99% |  | 2004-2016 |  |  | 3.948% | 47.19% | [12 empty] | 32.89% |  | 2004-2016 | 45.2% | 79.19% | 3.948% | 55.46% |  | 38.45% |  | 33.42% |  | 0% |  | 5.47% | 65.15% |  |  | 8.826% | 35.88%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1585 | 0.024504 | 0.011937 | 0.00049847 | 0 | 0.33214 | 0 | 0.049233 | 0.0086629 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.98529 | 3.52% | CZ 1A | 5.3401 | 0.82557 | 1.1937 | 0.016794 | 0 | 11.1905 | 0 | 1.6587 | 0.29187 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 33.9877 | 3.52% | CZ 1A | 1.5646 | 0.24189 | 0 | 0.0049207 | 0 | 3.2788 | 0 | 0.48601 | 0.085517 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 9.6086 | 3.52% | CZ 1A | 0 | 0 | 0.011937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011937 | 3.52% | CZ 1A | 16.3802 | 2.5324 | 1.3047 | 0.051515 | 0 | 34.3259 | 0 | 5.0881 | 0.89528 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 101.8975 | 3.52%
CZ 1B | 0.15857 | 0.024446 | 0.011986 | 0.0096432 | 0 | 0.38395 | 0 | 0.050335 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061653 | 0 | 0 | 0.30678 | 1.0387 | 0% | CZ 1B | 5.3425 | 0.82363 | 1.1986 | 0.34154 | 0 | 12.9359 | 0 | 1.6959 | 0 | 0.0026517 | 0 | 2.9238 | 0.20772 | 0 | 0 | 10.3361 | 35.8083 | 0% | CZ 1B | 1.5654 | 0.24132 | 0 | 0.092717 | 0 | 3.7902 | 0 | 0.49689 | 0 | 0.00077696 | 0 | 0.85667 | 0.060862 | 0 | 0 | 3.0285 | 10.1333 | 0% | CZ 1B | 0 | 0 | 0.011986 | 0.00025097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012237 | 0% | CZ 1B | 16.3878 | 2.5264 | 1.3101 | 0.99808 | 0 | 39.6797 | 0 | 5.2019 | 0 | 0.008134 | 0 | 8.9685 | 0.63716 | 0 | 0 | 31.7051 | 107.4229 | 0%
CZ 2A | 0.15843 | 0.024519 | 0.012612 | 0.019701 | 0 | 0.29606 | 0 | 0.042753 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061653 | 0 | 0 | 0.30678 | 0.95389 | 14.08% | CZ 2A | 5.3378 | 0.8261 | 1.2612 | 0.67513 | 0 | 9.9749 | 0 | 1.4404 | 0 | 0.0026517 | 0 | 2.9238 | 0.20772 | 0 | 0 | 10.3361 | 32.9858 | 14.08% | CZ 2A | 1.564 | 0.24205 | 0 | 0.19279 | 0 | 2.9227 | 0 | 0.42204 | 0 | 0.00077696 | 0 | 0.85667 | 0.060862 | 0 | 0 | 3.0285 | 9.2903 | 14.08% | CZ 2A | 0 | 0 | 0.012612 | 0.00017144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012784 | 14.08% | CZ 2A | 16.3731 | 2.534 | 1.3785 | 2.037 | 0 | 30.5973 | 0 | 4.4184 | 0 | 0.008134 | 0 | 8.9685 | 0.63716 | 0 | 0 | 31.7051 | 98.6572 | 14.08%
CZ 2B | 0.15861 | 0.024519 | 0.012658 | 0.016391 | 0 | 0.23953 | 0 | 0.050896 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.90242 | 4.829% | CZ 2B | 5.3439 | 0.8261 | 1.2658 | 0.60475 | 0 | 8.0701 | 0 | 1.7148 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 31.2959 | 4.829% | CZ 2B | 1.5658 | 0.24205 | 0 | 0.15399 | 0 | 2.3645 | 0 | 0.50243 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 8.7756 | 4.829% | CZ 2B | 0 | 0 | 0.012658 | 0.00079179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01345 | 4.829% | CZ 2B | 16.3921 | 2.534 | 1.3835 | 1.6987 | 0 | 24.7544 | 0 | 5.26 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 93.3421 | 4.829%
CZ 3A | 0.15922 | 0.024808 | 0.013796 | 0.082512 | 0 | 0.17943 | 0 | 0.03855 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.89814 | 13.71% | CZ 3A | 5.3643 | 0.83583 | 1.3796 | 3.1176 | 0 | 6.0454 | 0 | 1.2988 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 31.5122 | 13.71% | CZ 3A | 1.5717 | 0.2449 | 0 | 0.76427 | 0 | 1.7713 | 0 | 0.38055 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 8.6796 | 13.71% | CZ 3A | 0 | 0 | 0.013796 | 0.0050919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018888 | 13.71% | CZ 3A | 16.4545 | 2.5638 | 1.5079 | 8.5577 | 0 | 18.5438 | 0 | 3.984 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 92.9317 | 13.71%
CZ 3B | 0.15869 | 0.024304 | 0.013487 | 0.029611 | 0 | 0.17273 | 0 | 0.045602 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.84423 | 11.83% | CZ 3B | 5.3464 | 0.81885 | 1.3487 | 1.2872 | 0 | 5.8195 | 0 | 1.5364 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 29.6275 | 11.83% | CZ 3B | 1.5665 | 0.23992 | 0 | 0.2492 | 0 | 1.7051 | 0 | 0.45017 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 8.1577 | 11.83% | CZ 3B | 0 | 0 | 0.013487 | 0.0043672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017854 | 11.83% | CZ 3B | 16.3997 | 2.5118 | 1.4741 | 3.0862 | 0 | 17.8508 | 0 | 4.7128 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 87.3549 | 11.83%
CZ 3C | 0.15898 | 0.024236 | 0.013924 | 0.011171 | 0 | 0.11231 | 0 | 0.034394 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.75483 | 2.246% | CZ 3C | 5.3561 | 0.81656 | 1.3924 | 0.40942 | 0 | 3.784 | 0 | 1.1588 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 26.3879 | 2.246% | CZ 3C | 1.5694 | 0.23925 | 0 | 0.10536 | 0 | 1.1087 | 0 | 0.33953 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 7.3091 | 2.246% | CZ 3C | 0 | 0 | 0.013924 | 0.0004984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014422 | 2.246% | CZ 3C | 16.4295 | 2.5047 | 1.5218 | 1.1574 | 0 | 11.6072 | 0 | 3.5545 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 78.0952 | 2.246%
CZ 4A | 0.15923 | 0.024561 | 0.014729 | 0.097353 | 0 | 0.13028 | 0 | 0.042291 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.86826 | 19.19% | CZ 4A | 5.3646 | 0.82752 | 1.4729 | 4.6354 | 0 | 4.3893 | 0 | 1.4249 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 31.5853 | 19.19% | CZ 4A | 1.5718 | 0.24246 | 0 | 0.75924 | 0 | 1.2861 | 0 | 0.41749 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 8.224 | 19.19% | CZ 4A | 0 | 0 | 0.014729 | 0.020442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035171 | 19.19% | CZ 4A | 16.4556 | 2.5383 | 1.6099 | 10.1828 | 0 | 13.4639 | 0 | 4.3707 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 89.9411 | 19.19%
CZ 4B | 0.15826 | 0.024394 | 0.014457 | 0.037702 | 0 | 0.135 | 0 | 0.05523 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.82485 | 0.6394% | CZ 4B | 5.3319 | 0.82186 | 1.4457 | 1.6966 | 0 | 4.5482 | 0 | 1.8608 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 29.1756 | 0.6394% | CZ 4B | 1.5623 | 0.2408 | 0 | 0.30871 | 0 | 1.3326 | 0 | 0.54522 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 7.9365 | 0.6394% | CZ 4B | 0 | 0 | 0.014457 | 0.0064298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020887 | 0.6394% | CZ 4B | 16.3552 | 2.521 | 1.5802 | 3.9347 | 0 | 13.9514 | 0 | 5.7079 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 85.3698 | 0.6394%
CZ 4C | 0.16007 | 0.02496 | 0.015016 | 0.07132 | 0 | 0.052518 | 0 | 0.036771 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.76047 | 3.137% | CZ 4C | 5.3929 | 0.84095 | 1.5016 | 3.0196 | 0 | 1.7694 | 0 | 1.2389 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 27.2339 | 3.137% | CZ 4C | 1.5801 | 0.2464 | 0 | 0.61224 | 0 | 0.51844 | 0 | 0.36299 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 7.2671 | 3.137% | CZ 4C | 0 | 0 | 0.015016 | 0.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024316 | 3.137% | CZ 4C | 16.5423 | 2.5796 | 1.6412 | 7.4261 | 0 | 5.4275 | 0 | 3.8002 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 78.7369 | 3.137%
CZ 5A | 0.15899 | 0.024735 | 0.015532 | 0.15598 | 0 | 0.08399 | 0 | 0.039285 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.87833 | 16.56% | CZ 5A | 5.3567 | 0.83335 | 1.5532 | 7.9019 | 0 | 2.8298 | 0 | 1.3236 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 33.2689 | 16.56% | CZ 5A | 1.5695 | 0.24417 | 0 | 1.1458 | 0 | 0.82912 | 0 | 0.38781 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 8.1232 | 16.56% | CZ 5A | 0 | 0 | 0.015532 | 0.039913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055445 | 16.56% | CZ 5A | 16.4312 | 2.5562 | 1.6976 | 16.3579 | 0 | 8.68 | 0 | 4.0599 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 91.1024 | 16.56%
CZ 5B | 0.15883 | 0.024525 | 0.015309 | 0.086415 | 0 | 0.096005 | 0 | 0.048903 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.8298 | 5.726% | CZ 5B | 5.3512 | 0.82628 | 1.5309 | 4.2684 | 0 | 3.2346 | 0 | 1.6476 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 30.3295 | 5.726% | CZ 5B | 1.5679 | 0.2421 | 0 | 0.65104 | 0 | 0.94773 | 0 | 0.48275 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 7.8384 | 5.726% | CZ 5B | 0 | 0 | 0.015309 | 0.020465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035774 | 5.726% | CZ 5B | 16.4143 | 2.5345 | 1.6733 | 9.0525 | 0 | 9.9218 | 0 | 5.0539 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 85.9699 | 5.726%
CZ 5C | 0.16029 | 0.025007 | 0.01547 | 0.072221 | 0 | 0.03016 | 0 | 0.037296 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.74026 | 0.1011% | CZ 5C | 5.4003 | 0.84254 | 1.547 | 3.2832 | 0 | 1.0161 | 0 | 1.2566 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 26.8164 | 0.1011% | CZ 5C | 1.5823 | 0.24687 | 0 | 0.5864 | 0 | 0.29773 | 0 | 0.36817 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 7.0284 | 0.1011% | CZ 5C | 0 | 0 | 0.01547 | 0.012819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028289 | 0.1011% | CZ 5C | 16.5651 | 2.5844 | 1.6909 | 7.5401 | 0 | 3.1169 | 0 | 3.8544 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 76.6718 | 0.1011%
CZ 6A | 0.15909 | 0.024777 | 0.016147 | 0.23105 | 0 | 0.091272 | 0 | 0.041746 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061758 | 0 | 0 | 0.30678 | 0.96391 | 3.488% | CZ 6A | 5.36 | 0.83476 | 1.6147 | 11.9315 | 0 | 3.0751 | 0 | 1.4065 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 37.6932 | 3.488% | CZ 6A | 1.5705 | 0.24459 | 0 | 1.6635 | 0 | 0.90101 | 0 | 0.4121 | 0 | 0.00077696 | 0 | 0.85667 | 0.060965 | 0 | 0 | 3.0285 | 8.7386 | 3.488% | CZ 6A | 0 | 0 | 0.016147 | 0.062539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078686 | 3.488% | CZ 6A | 16.4415 | 2.5606 | 1.7649 | 24.2509 | 0 | 9.4327 | 0 | 4.3143 | 0 | 0.008134 | 0 | 8.9685 | 0.63825 | 0 | 0 | 31.7051 | 100.0847 | 3.488%
CZ 6B | 0.15922 | 0.025034 | 0.015991 | 0.15885 | 0 | 0.064303 | 0 | 0.045592 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.86881 | 0.4679% | CZ 6B | 5.3645 | 0.84343 | 1.5991 | 7.9673 | 0 | 2.1665 | 0 | 1.5361 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 32.9473 | 0.4679% | CZ 6B | 1.5718 | 0.24712 | 0 | 1.1788 | 0 | 0.63477 | 0 | 0.45007 | 0 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 8.0294 | 0.4679% | CZ 6B | 0 | 0 | 0.015991 | 0.039441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055432 | 0.4679% | CZ 6B | 16.455 | 2.5871 | 1.7479 | 16.6518 | 0 | 6.6455 | 0 | 4.7117 | 0 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 90.1184 | 0.4679%
CZ 7 | 0.15879 | 0.025055 | 0.01688 | 0.17247 | 0 | 0.073868 | 0 | 0.045613 | 0.012184 | 7.8706e-05 | 0 | 0.086781 | 0.0061705 | 0 | 0 | 0.30678 | 0.90468 | 0.3712% | CZ 7 | 5.35 | 0.84413 | 1.688 | 6.7255 | 0 | 2.4887 | 0 | 1.5368 | 0.41049 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 32.5141 | 0.3712% | CZ 7 | 1.5675 | 0.24733 | 0 | 1.5664 | 0 | 0.7292 | 0 | 0.45027 | 0.12027 | 0.00077696 | 0 | 0.85667 | 0.060913 | 0 | 0 | 3.0285 | 8.6279 | 0.3712% | CZ 7 | 0 | 0 | 0.01688 | 0.013794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030675 | 0.3712% | CZ 7 | 16.4105 | 2.5893 | 1.845 | 17.9064 | 0 | 7.634 | 0 | 4.7139 | 1.2591 | 0.008134 | 0 | 8.9685 | 0.6377 | 0 | 0 | 31.7051 | 93.6777 | 0.3712%
CZ 8 | 0.16461 | 0.027064 | 0.01787 | 0.26505 | 0 | 0.034289 | 0 | 0.046489 | 0.012672 | 7.8706e-05 | 0 | 0.086781 | 0.006181 | 0 | 0 | 0.30678 | 0.96787 | 0.113% | CZ 8 | 5.546 | 0.91184 | 1.787 | 11.1101 | 0 | 1.1553 | 0 | 1.5663 | 0.42693 | 0.0026517 | 0 | 2.9238 | 0.20825 | 0 | 0 | 10.3361 | 35.9743 | 0.113% | CZ 8 | 1.625 | 0.26717 | 0 | 2.2919 | 0 | 0.33849 | 0 | 0.45892 | 0.12509 | 0.00077696 | 0 | 0.85667 | 0.061017 | 0 | 0 | 3.0285 | 9.0535 | 0.113% | CZ 8 | 0 | 0 | 0.01787 | 0.032881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050751 | 0.113% | CZ 8 | 17.0119 | 2.797 | 1.9532 | 27.5874 | 0 | 3.5437 | 0 | 4.8045 | 1.3096 | 0.008134 | 0 | 8.9685 | 0.63879 | 0 | 0 | 31.7051 | 100.3278 | 0.113%
US Weighted | 0.15895 | 0.0246 | 0.014181 | 0.080397 | 0 | 0.16323 | 0 | 0.042516 | 0.00036446 | 7.8706e-05 | 0 | 0.086781 | 0.006172 | 0 | 0 | 0.30678 | 0.88406 | 100% | US Weighted | 5.3552 | 0.82883 | 1.4181 | 3.7558 | 0 | 5.4996 | 0 | 1.4324 | 0.012279 | 0.0026517 | 0 | 2.9238 | 0.20795 | 0 | 0 | 10.3361 | 31.7728 | 100% | US Weighted | 1.5691 | 0.24285 | 0 | 0.63777 | 0 | 1.6114 | 0 | 0.41971 | 0.0035978 | 0.00077696 | 0 | 0.85667 | 0.060928 | 0 | 0 | 3.0285 | 8.4312 | 100% | US Weighted | 0 | 0 | 0.014181 | 0.015791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029972 | 100% | US Weighted | 16.4267 | 2.5424 | 1.55 | 8.4028 | 0 | 16.8697 | 0 | 4.3939 | 0.037666 | 0.008134 | 0 | 8.9685 | 0.63785 | 0 | 0 | 31.7051 | 91.5427 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.17183 | 0.054092 | 0.012266 | 0.00055094 | 0 | 0.35212 | 0 | 0.050041 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 1.0435 | 3.52% | CZ 1A | 5.7893 | 1.8224 | 1.2266 | 0.018562 | 0 | 11.8635 | 0 | 1.686 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 35.9703 | 3.52% | CZ 1A | 1.6963 | 0.53398 | 0 | 0.0054387 | 0 | 3.476 | 0 | 0.49399 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 10.1799 | 3.52% | CZ 1A | 0 | 0 | 0.012266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012266 | 3.52% | CZ 1A | 17.7581 | 5.5902 | 1.3406 | 0.056938 | 0 | 36.3903 | 0 | 5.1716 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 107.914 | 3.52%
CZ 1B | 0.1719 | 0.054013 | 0.01237 | 0.0097813 | 0 | 0.38807 | 0 | 0.051206 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 1.0899 | 0% | CZ 1B | 5.7916 | 1.8198 | 1.237 | 0.3456 | 0 | 13.0746 | 0 | 1.7252 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 37.5578 | 0% | CZ 1B | 1.6969 | 0.5332 | 0 | 0.094167 | 0 | 3.8309 | 0 | 0.50549 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 10.6349 | 0% | CZ 1B | 0 | 0 | 0.01237 | 0.00024213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012612 | 0% | CZ 1B | 17.7651 | 5.5821 | 1.352 | 1.0123 | 0 | 40.1053 | 0 | 5.292 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 112.7151 | 0%
CZ 2A | 0.1718 | 0.053961 | 0.012918 | 0.020799 | 0 | 0.3001 | 0 | 0.043613 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 1.0058 | 14.08% | CZ 2A | 5.7882 | 1.818 | 1.2918 | 0.7119 | 0 | 10.1109 | 0 | 1.4694 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 34.7543 | 14.08% | CZ 2A | 1.6959 | 0.53268 | 0 | 0.20367 | 0 | 2.9625 | 0 | 0.43054 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 9.7996 | 14.08% | CZ 2A | 0 | 0 | 0.012918 | 0.0001679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013086 | 14.08% | CZ 2A | 17.7548 | 5.5766 | 1.4119 | 2.1505 | 0 | 31.0143 | 0 | 4.5073 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 104.0224 | 14.08%
CZ 2B | 0.17206 | 0.054003 | 0.012981 | 0.017365 | 0 | 0.24287 | 0 | 0.05192 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 0.95379 | 4.829% | CZ 2B | 5.7969 | 1.8194 | 1.2981 | 0.63604 | 0 | 8.1827 | 0 | 1.7493 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 33.0466 | 4.829% | CZ 2B | 1.6985 | 0.5331 | 0 | 0.16383 | 0 | 2.3975 | 0 | 0.51253 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 9.2798 | 4.829% | CZ 2B | 0 | 0 | 0.012981 | 0.00076882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01375 | 4.829% | CZ 2B | 17.7814 | 5.581 | 1.4189 | 1.7992 | 0 | 25.0998 | 0 | 5.3657 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 98.6528 | 4.829%
CZ 3A | 0.17272 | 0.054066 | 0.014081 | 0.086401 | 0 | 0.18183 | 0 | 0.039253 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 0.95095 | 13.71% | CZ 3A | 5.8193 | 1.8216 | 1.4081 | 3.2543 | 0 | 6.1262 | 0 | 1.3225 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 33.3159 | 13.71% | CZ 3A | 1.7051 | 0.53372 | 0 | 0.80182 | 0 | 1.795 | 0 | 0.38749 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 9.1973 | 13.71% | CZ 3A | 0 | 0 | 0.014081 | 0.0051767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019258 | 13.71% | CZ 3A | 17.8503 | 5.5875 | 1.539 | 8.9601 | 0 | 18.7916 | 0 | 4.0567 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 98.3915 | 13.71%
CZ 3B | 0.17207 | 0.054024 | 0.01377 | 0.031805 | 0 | 0.17503 | 0 | 0.046421 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 0.89571 | 11.83% | CZ 3B | 5.7974 | 1.8201 | 1.377 | 1.3585 | 0 | 5.8969 | 0 | 1.564 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 31.3779 | 11.83% | CZ 3B | 1.6986 | 0.5333 | 0 | 0.27126 | 0 | 1.7278 | 0 | 0.45825 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 8.6635 | 11.83% | CZ 3B | 0 | 0 | 0.01377 | 0.0043266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018096 | 11.83% | CZ 3B | 17.783 | 5.5832 | 1.505 | 3.3127 | 0 | 18.0883 | 0 | 4.7974 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 92.676 | 11.83%
CZ 3C | 0.17233 | 0.054144 | 0.014194 | 0.012441 | 0 | 0.11439 | 0 | 0.035061 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 0.80516 | 2.246% | CZ 3C | 5.8061 | 1.8242 | 1.4194 | 0.45149 | 0 | 3.854 | 0 | 1.1813 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 28.1006 | 2.246% | CZ 3C | 1.7012 | 0.53449 | 0 | 0.11799 | 0 | 1.1292 | 0 | 0.34611 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 7.8033 | 2.246% | CZ 3C | 0 | 0 | 0.014194 | 0.0004878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014682 | 2.246% | CZ 3C | 17.8096 | 5.5956 | 1.5514 | 1.2886 | 0 | 11.8219 | 0 | 3.6234 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 83.2974 | 2.246%
CZ 4A | 0.17225 | 0.054181 | 0.015 | 0.095263 | 0 | 0.13134 | 0 | 0.042685 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 0.91331 | 19.19% | CZ 4A | 5.8034 | 1.8255 | 1.5 | 4.5458 | 0 | 4.425 | 0 | 1.4381 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 33.1019 | 19.19% | CZ 4A | 1.7004 | 0.53486 | 0 | 0.74148 | 0 | 1.2965 | 0 | 0.42137 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 8.6689 | 19.19% | CZ 4A | 0 | 0 | 0.015 | 0.020152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035152 | 19.19% | CZ 4A | 17.8015 | 5.5994 | 1.6395 | 9.9651 | 0 | 13.5734 | 0 | 4.4113 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 94.5971 | 19.19%
CZ 4B | 0.17127 | 0.054018 | 0.014735 | 0.036589 | 0 | 0.13623 | 0 | 0.055881 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089357 | 0 | 0 | 0.30678 | 0.87131 | 0.6394% | CZ 4B | 5.7703 | 1.82 | 1.4735 | 1.6437 | 0 | 4.59 | 0 | 1.8827 | 0 | 0.0026517 | 0 | 2.9238 | 0.30106 | 0 | 0 | 10.3361 | 30.7438 | 0.6394% | CZ 4B | 1.6907 | 0.53325 | 0 | 0.30001 | 0 | 1.3449 | 0 | 0.55164 | 0 | 0.00077696 | 0 | 0.85667 | 0.088211 | 0 | 0 | 3.0285 | 8.3946 | 0.6394% | CZ 4B | 0 | 0 | 0.014735 | 0.0061982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020933 | 0.6394% | CZ 4B | 17.7001 | 5.5826 | 1.6105 | 3.8183 | 0 | 14.0794 | 0 | 5.7751 | 0 | 0.008134 | 0 | 8.9685 | 0.92348 | 0 | 0 | 31.7051 | 90.1711 | 0.6394%
CZ 4C | 0.17324 | 0.054186 | 0.015286 | 0.074701 | 0 | 0.056369 | 0 | 0.039641 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 0.81602 | 3.137% | CZ 4C | 5.8366 | 1.8256 | 1.5286 | 3.0564 | 0 | 1.8992 | 0 | 1.3356 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 29.0461 | 3.137% | CZ 4C | 1.7101 | 0.53491 | 0 | 0.6571 | 0 | 0.55646 | 0 | 0.39133 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 7.8242 | 3.137% | CZ 4C | 0 | 0 | 0.015286 | 0.0081371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023423 | 3.137% | CZ 4C | 17.9034 | 5.6 | 1.6708 | 7.7685 | 0 | 5.8255 | 0 | 4.0968 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 84.4719 | 3.137%
CZ 5A | 0.1721 | 0.054024 | 0.015809 | 0.1585 | 0 | 0.089289 | 0 | 0.042181 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 0.9345 | 16.56% | CZ 5A | 5.7985 | 1.8201 | 1.5809 | 7.9044 | 0 | 3.0083 | 0 | 1.4212 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 35.0975 | 16.56% | CZ 5A | 1.6989 | 0.5333 | 0 | 1.1828 | 0 | 0.88143 | 0 | 0.4164 | 0 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 8.6872 | 16.56% | CZ 5A | 0 | 0 | 0.015809 | 0.038674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054483 | 16.56% | CZ 5A | 17.7863 | 5.5832 | 1.728 | 16.6102 | 0 | 9.2277 | 0 | 4.3593 | 0 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 96.9015 | 16.56%
CZ 5B | 0.17192 | 0.054129 | 0.015576 | 0.087797 | 0 | 0.10222 | 0 | 0.053326 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 0.88756 | 5.726% | CZ 5B | 5.7923 | 1.8237 | 1.5576 | 4.1972 | 0 | 3.4439 | 0 | 1.7966 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 32.1753 | 5.726% | CZ 5B | 1.6971 | 0.53434 | 0 | 0.68222 | 0 | 1.0091 | 0 | 0.52641 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 8.4234 | 5.726% | CZ 5B | 0 | 0 | 0.015576 | 0.018688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034264 | 5.726% | CZ 5B | 17.7673 | 5.594 | 1.7025 | 9.1848 | 0 | 10.5639 | 0 | 5.511 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 91.9298 | 5.726%
CZ 5C | 0.17345 | 0.054155 | 0.01574 | 0.075177 | 0 | 0.033413 | 0 | 0.039689 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 0.79422 | 0.1011% | CZ 5C | 5.8439 | 1.8246 | 1.574 | 3.2835 | 0 | 1.1257 | 0 | 1.3372 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 28.5528 | 0.1011% | CZ 5C | 1.7123 | 0.5346 | 0 | 0.63037 | 0 | 0.32984 | 0 | 0.39179 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 7.5731 | 0.1011% | CZ 5C | 0 | 0 | 0.01574 | 0.01132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027061 | 0.1011% | CZ 5C | 17.9256 | 5.5967 | 1.7204 | 7.8366 | 0 | 3.4531 | 0 | 4.1017 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 82.2406 | 0.1011%
CZ 6A | 0.1723 | 0.054123 | 0.016407 | 0.23823 | 0 | 0.096593 | 0 | 0.044878 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.008941 | 0 | 0 | 0.30678 | 1.0251 | 3.488% | CZ 6A | 5.805 | 1.8235 | 1.6407 | 12.113 | 0 | 3.2544 | 0 | 1.512 | 0 | 0.0026517 | 0 | 2.9238 | 0.30124 | 0 | 0 | 10.3361 | 39.7124 | 3.488% | CZ 6A | 1.7009 | 0.53429 | 0 | 1.7434 | 0 | 0.95353 | 0 | 0.44302 | 0 | 0.00077696 | 0 | 0.85667 | 0.088262 | 0 | 0 | 3.0285 | 9.3493 | 3.488% | CZ 6A | 0 | 0 | 0.016407 | 0.061629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078036 | 3.488% | CZ 6A | 17.8063 | 5.5935 | 1.7933 | 24.9876 | 0 | 9.9825 | 0 | 4.638 | 0 | 0.008134 | 0 | 8.9685 | 0.92402 | 0 | 0 | 31.7051 | 106.4069 | 3.488%
CZ 6B | 0.17244 | 0.05405 | 0.016255 | 0.16426 | 0 | 0.068437 | 0 | 0.04907 | 0 | 7.8706e-05 | 0 | 0.086781 | 0.0089462 | 0 | 0 | 0.30678 | 0.9271 | 0.4679% | CZ 6B | 5.8098 | 1.821 | 1.6255 | 8.0619 | 0 | 2.3058 | 0 | 1.6533 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 34.8412 | 0.4679% | CZ 6B | 1.7023 | 0.53356 | 0 | 1.2452 | 0 | 0.67559 | 0 | 0.48441 | 0 | 0.00077696 | 0 | 0.85667 | 0.088314 | 0 | 0 | 3.0285 | 8.6153 | 0.4679% | CZ 6B | 0 | 0 | 0.016255 | 0.038121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054376 | 0.4679% | CZ 6B | 17.821 | 5.5859 | 1.7766 | 17.2026 | 0 | 7.0728 | 0 | 5.0713 | 0 | 0.008134 | 0 | 8.9685 | 0.92456 | 0 | 0 | 31.7051 | 96.1365 | 0.4679%
CZ 7 | 0.17168 | 0.054207 | 0.017122 | 0.2213 | 0 | 0.075914 | 0 | 0.046688 | 0.013857 | 7.8706e-05 | 0 | 0.086781 | 0.0089515 | 0 | 0 | 0.30678 | 1.0034 | 0.3712% | CZ 7 | 5.7841 | 1.8263 | 1.7122 | 9.1678 | 0 | 2.5577 | 0 | 1.573 | 0.46688 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 36.6522 | 0.3712% | CZ 7 | 1.6948 | 0.53512 | 0 | 1.9298 | 0 | 0.7494 | 0 | 0.46089 | 0.1368 | 0.00077696 | 0 | 0.85667 | 0.088366 | 0 | 0 | 3.0285 | 9.481 | 0.3712% | CZ 7 | 0 | 0 | 0.017122 | 0.025816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042939 | 0.3712% | CZ 7 | 17.7423 | 5.6021 | 1.8715 | 23.0243 | 0 | 7.8455 | 0 | 4.8251 | 1.4321 | 0.008134 | 0 | 8.9685 | 0.9251 | 0 | 0 | 31.7051 | 103.9498 | 0.3712%
CZ 8 | 0.17746 | 0.054512 | 0.018098 | 0.3396 | 0 | 0.034856 | 0 | 0.047596 | 0.013989 | 7.8706e-05 | 0 | 0.086781 | 0.0089567 | 0 | 0 | 0.30678 | 1.0887 | 0.113% | CZ 8 | 5.9789 | 1.8366 | 1.8098 | 15.2653 | 0 | 1.1744 | 0 | 1.6036 | 0.4713 | 0.0026517 | 0 | 2.9238 | 0.30177 | 0 | 0 | 10.3361 | 41.7042 | 0.113% | CZ 8 | 1.7518 | 0.53812 | 0 | 2.7832 | 0 | 0.34409 | 0 | 0.46985 | 0.13809 | 0.00077696 | 0 | 0.85667 | 0.088418 | 0 | 0 | 3.0285 | 9.9995 | 0.113% | CZ 8 | 0 | 0 | 0.018098 | 0.057665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075763 | 0.113% | CZ 8 | 18.3399 | 5.6336 | 1.9781 | 35.4397 | 0 | 3.6023 | 0 | 4.9189 | 1.4457 | 0.008134 | 0 | 8.9685 | 0.92565 | 0 | 0 | 31.7051 | 112.9656 | 0.113%
US Weighted | 0.1722 | 0.054071 | 0.014465 | 0.082159 | 0 | 0.1671 | 0 | 0.043959 | 6.7252e-05 | 7.8706e-05 | 0 | 0.086781 | 0.0089492 | 0 | 0 | 0.30678 | 0.93661 | 100% | US Weighted | 5.8016 | 1.8217 | 1.4465 | 3.7912 | 0 | 5.6298 | 0 | 1.4811 | 0.0022658 | 0.0026517 | 0 | 2.9238 | 0.30151 | 0 | 0 | 10.3361 | 33.5381 | 100% | US Weighted | 1.6999 | 0.53377 | 0 | 0.65874 | 0 | 1.6495 | 0 | 0.43395 | 0.00066389 | 0.00077696 | 0 | 0.85667 | 0.088343 | 0 | 0 | 3.0285 | 8.9508 | 100% | US Weighted | 0 | 0 | 0.014465 | 0.015429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029894 | 100% | US Weighted | 17.7959 | 5.588 | 1.581 | 8.5827 | 0 | 17.2688 | 0 | 4.543 | 0.0069502 | 0.008134 | 0 | 8.9685 | 0.92486 | 0 | 0 | 31.7051 | 96.9731 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.2028 | 0.054092 | 0.012266 | 0.0025396 | 0 | 0.42254 | 0 | 0.060415 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091299 | 0 | 0 | 0.31054 | 1.1614 | 3.52% | CZ 1A | 6.8326 | 1.8224 | 1.2266 | 0.085563 | 0 | 14.2361 | 0 | 2.0355 | 0 | 0.0026517 | 0 | 2.9318 | 0.3076 | 0 | 0 | 10.4627 | 39.9434 | 3.52% | CZ 1A | 2.002 | 0.53398 | 0 | 0.02507 | 0 | 4.1712 | 0 | 0.59639 | 0 | 0.00077696 | 0 | 0.859 | 0.090127 | 0 | 0 | 3.0656 | 11.344 | 3.52% | CZ 1A | 0 | 0 | 0.012266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012266 | 3.52% | CZ 1A | 20.9585 | 5.5902 | 1.3406 | 0.26246 | 0 | 43.668 | 0 | 6.2436 | 0 | 0.008134 | 0 | 8.9929 | 0.94354 | 0 | 0 | 32.0934 | 120.1014 | 3.52%
CZ 1B | 0.20216 | 0.054013 | 0.012374 | 0.017149 | 0 | 0.4395 | 0 | 0.063101 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091299 | 0 | 0 | 0.31054 | 1.1951 | 0% | CZ 1B | 6.8111 | 1.8198 | 1.2374 | 0.58691 | 0 | 14.8074 | 0 | 2.126 | 0 | 0.0026517 | 0 | 2.9318 | 0.3076 | 0 | 0 | 10.4627 | 41.0932 | 0% | CZ 1B | 1.9956 | 0.5332 | 0 | 0.16793 | 0 | 4.3386 | 0 | 0.62291 | 0 | 0.00077696 | 0 | 0.859 | 0.090127 | 0 | 0 | 3.0656 | 11.6737 | 0% | CZ 1B | 0 | 0 | 0.012374 | 0.00013786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012511 | 0% | CZ 1B | 20.8924 | 5.5821 | 1.3524 | 1.7731 | 0 | 45.4206 | 0 | 6.5213 | 0 | 0.008134 | 0 | 8.9929 | 0.94354 | 0 | 0 | 32.0934 | 123.5798 | 0%
CZ 2A | 0.20378 | 0.053961 | 0.01292 | 0.036157 | 0 | 0.36747 | 0 | 0.054664 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091351 | 0 | 0 | 0.31054 | 1.1357 | 14.08% | CZ 2A | 6.8659 | 1.818 | 1.292 | 1.2272 | 0 | 12.3806 | 0 | 1.8417 | 0 | 0.0026517 | 0 | 2.9318 | 0.30778 | 0 | 0 | 10.4627 | 39.1302 | 14.08% | CZ 2A | 2.0117 | 0.53268 | 0 | 0.35559 | 0 | 3.6275 | 0 | 0.53962 | 0 | 0.00077696 | 0 | 0.859 | 0.090179 | 0 | 0 | 3.0656 | 11.0826 | 14.08% | CZ 2A | 0 | 0 | 0.01292 | 0.00013609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013056 | 14.08% | CZ 2A | 21.0605 | 5.5766 | 1.4121 | 3.7375 | 0 | 37.9764 | 0 | 5.6493 | 0 | 0.008134 | 0 | 8.9929 | 0.94408 | 0 | 0 | 32.0934 | 117.451 | 14.08%
CZ 2B | 0.20652 | 0.054003 | 0.01298 | 0.027864 | 0 | 0.28349 | 0 | 0.065934 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091404 | 0 | 0 | 0.31054 | 1.0576 | 4.829% | CZ 2B | 6.958 | 1.8194 | 1.298 | 0.98484 | 0 | 9.5512 | 0 | 2.2214 | 0 | 0.0026517 | 0 | 2.9318 | 0.30795 | 0 | 0 | 10.4627 | 36.5379 | 4.829% | CZ 2B | 2.0387 | 0.5331 | 0 | 0.26821 | 0 | 2.7985 | 0 | 0.65088 | 0 | 0.00077696 | 0 | 0.859 | 0.090231 | 0 | 0 | 3.0656 | 10.3049 | 4.829% | CZ 2B | 0 | 0 | 0.01298 | 0.00069459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013674 | 4.829% | CZ 2B | 21.343 | 5.581 | 1.4187 | 2.8838 | 0 | 29.2975 | 0 | 6.8141 | 0 | 0.008134 | 0 | 8.9929 | 0.94462 | 0 | 0 | 32.0934 | 109.377 | 4.829%
CZ 3A | 0.19995 | 0.054066 | 0.014081 | 0.08581 | 0 | 0.20945 | 0 | 0.044605 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091246 | 0 | 0 | 0.31054 | 1.0147 | 13.71% | CZ 3A | 6.7366 | 1.8216 | 1.4081 | 3.1906 | 0 | 7.0566 | 0 | 1.5028 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 35.4208 | 13.71% | CZ 3A | 1.9738 | 0.53372 | 0 | 0.80249 | 0 | 2.0676 | 0 | 0.44033 | 0 | 0.00077696 | 0 | 0.859 | 0.090075 | 0 | 0 | 3.0656 | 9.8334 | 13.71% | CZ 3A | 0 | 0 | 0.014081 | 0.0045175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018598 | 13.71% | CZ 3A | 20.6641 | 5.5875 | 1.539 | 8.8951 | 0 | 21.6456 | 0 | 4.6098 | 0 | 0.008134 | 0 | 8.9929 | 0.943 | 0 | 0 | 32.0934 | 104.9784 | 13.71%
CZ 3B | 0.19927 | 0.054024 | 0.013772 | 0.027428 | 0 | 0.19127 | 0 | 0.054742 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 0.94725 | 11.83% | CZ 3B | 6.7137 | 1.8201 | 1.3772 | 1.1789 | 0 | 6.4441 | 0 | 1.8444 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 33.0826 | 11.83% | CZ 3B | 1.9671 | 0.5333 | 0 | 0.23283 | 0 | 1.8881 | 0 | 0.5404 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 9.1771 | 11.83% | CZ 3B | 0 | 0 | 0.013772 | 0.0038423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017614 | 11.83% | CZ 3B | 20.5936 | 5.5832 | 1.5052 | 2.8574 | 0 | 19.7666 | 0 | 5.6574 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 98.0003 | 11.83%
CZ 3C | 0.19895 | 0.054144 | 0.014192 | 0.016128 | 0 | 0.13045 | 0 | 0.042868 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091246 | 0 | 0 | 0.31054 | 0.86349 | 2.246% | CZ 3C | 6.7029 | 1.8242 | 1.4192 | 0.57594 | 0 | 4.3952 | 0 | 1.4443 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 30.0662 | 2.246% | CZ 3C | 1.9639 | 0.53449 | 0 | 0.15436 | 0 | 1.2878 | 0 | 0.42318 | 0 | 0.00077696 | 0 | 0.859 | 0.090075 | 0 | 0 | 3.0656 | 8.3792 | 2.246% | CZ 3C | 0 | 0 | 0.014192 | 0.00049134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014683 | 2.246% | CZ 3C | 20.5605 | 5.5956 | 1.5512 | 1.6697 | 0 | 13.4818 | 0 | 4.4303 | 0 | 0.008134 | 0 | 8.9929 | 0.943 | 0 | 0 | 32.0934 | 89.3265 | 2.246%
CZ 4A | 0.19765 | 0.054181 | 0.015005 | 0.11216 | 0 | 0.13972 | 0 | 0.044826 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091246 | 0 | 0 | 0.31054 | 0.97029 | 19.19% | CZ 4A | 6.659 | 1.8255 | 1.5005 | 5.1276 | 0 | 4.7074 | 0 | 1.5102 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 35.0347 | 19.19% | CZ 4A | 1.9511 | 0.53486 | 0 | 0.90635 | 0 | 1.3793 | 0 | 0.4425 | 0 | 0.00077696 | 0 | 0.859 | 0.090075 | 0 | 0 | 3.0656 | 9.2295 | 19.19% | CZ 4A | 0 | 0 | 0.015005 | 0.020343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035348 | 19.19% | CZ 4A | 20.426 | 5.5994 | 1.6401 | 11.712 | 0 | 14.4394 | 0 | 4.6326 | 0 | 0.008134 | 0 | 8.9929 | 0.943 | 0 | 0 | 32.0934 | 100.4869 | 19.19%
CZ 4B | 0.19659 | 0.054018 | 0.014735 | 0.047411 | 0 | 0.14571 | 0 | 0.059591 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 0.92481 | 0.6394% | CZ 4B | 6.6233 | 1.82 | 1.4735 | 2.0033 | 0 | 4.9092 | 0 | 2.0077 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 32.5414 | 0.6394% | CZ 4B | 1.9406 | 0.53325 | 0 | 0.40759 | 0 | 1.4384 | 0 | 0.58826 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 8.9235 | 0.6394% | CZ 4B | 0 | 0 | 0.014735 | 0.0061222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020857 | 0.6394% | CZ 4B | 20.3165 | 5.5826 | 1.6105 | 4.9362 | 0 | 15.0587 | 0 | 6.1585 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 95.6999 | 0.6394%
CZ 4C | 0.19957 | 0.054186 | 0.01529 | 0.088229 | 0 | 0.058993 | 0 | 0.042742 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 0.86577 | 3.137% | CZ 4C | 6.7239 | 1.8256 | 1.529 | 3.5285 | 0 | 1.9876 | 0 | 1.4401 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 30.739 | 3.137% | CZ 4C | 1.9701 | 0.53491 | 0 | 0.7882 | 0 | 0.58236 | 0 | 0.42194 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 8.3129 | 3.137% | CZ 4C | 0 | 0 | 0.01529 | 0.0083845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023674 | 3.137% | CZ 4C | 20.625 | 5.6 | 1.6712 | 9.1681 | 0 | 6.0967 | 0 | 4.4173 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 89.6151 | 3.137%
CZ 5A | 0.19761 | 0.054024 | 0.015811 | 0.18629 | 0 | 0.095612 | 0 | 0.043225 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091246 | 0 | 0 | 0.31054 | 0.99934 | 16.56% | CZ 5A | 6.658 | 1.8201 | 1.5811 | 8.9062 | 0 | 3.2213 | 0 | 1.4563 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 37.3476 | 16.56% | CZ 5A | 1.9508 | 0.5333 | 0 | 1.4475 | 0 | 0.94385 | 0 | 0.4267 | 0 | 0.00077696 | 0 | 0.859 | 0.090075 | 0 | 0 | 3.0656 | 9.3176 | 16.56% | CZ 5A | 0 | 0 | 0.015811 | 0.039659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05547 | 16.56% | CZ 5A | 20.4228 | 5.5832 | 1.7282 | 19.4888 | 0 | 9.8811 | 0 | 4.4672 | 0 | 0.008134 | 0 | 8.9929 | 0.943 | 0 | 0 | 32.0934 | 103.6086 | 16.56%
CZ 5B | 0.19748 | 0.054129 | 0.015583 | 0.11017 | 0 | 0.10756 | 0 | 0.056479 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091141 | 0 | 0 | 0.31054 | 0.94816 | 5.726% | CZ 5B | 6.6535 | 1.8237 | 1.5583 | 4.9599 | 0 | 3.624 | 0 | 1.9029 | 0 | 0.0026517 | 0 | 2.9318 | 0.30707 | 0 | 0 | 10.4627 | 34.2265 | 5.726% | CZ 5B | 1.9495 | 0.53434 | 0 | 0.90179 | 0 | 1.0618 | 0 | 0.55754 | 0 | 0.00077696 | 0 | 0.859 | 0.089972 | 0 | 0 | 3.0656 | 9.0203 | 5.726% | CZ 5B | 0 | 0 | 0.015583 | 0.018821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034404 | 5.726% | CZ 5B | 20.4092 | 5.594 | 1.7032 | 11.498 | 0 | 11.1164 | 0 | 5.8369 | 0 | 0.008134 | 0 | 8.9929 | 0.94191 | 0 | 0 | 32.0934 | 98.1941 | 5.726%
CZ 5C | 0.19962 | 0.054155 | 0.015744 | 0.093175 | 0 | 0.033786 | 0 | 0.042323 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091246 | 0 | 0 | 0.31054 | 0.84557 | 0.1011% | CZ 5C | 6.7257 | 1.8246 | 1.5744 | 3.9275 | 0 | 1.1383 | 0 | 1.4259 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 30.3208 | 0.1011% | CZ 5C | 1.9706 | 0.5346 | 0 | 0.80244 | 0 | 0.33352 | 0 | 0.4178 | 0 | 0.00077696 | 0 | 0.859 | 0.090075 | 0 | 0 | 3.0656 | 8.0744 | 0.1011% | CZ 5C | 0 | 0 | 0.015744 | 0.011887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027631 | 0.1011% | CZ 5C | 20.6304 | 5.5967 | 1.7208 | 9.7001 | 0 | 3.4916 | 0 | 4.3739 | 0 | 0.008134 | 0 | 8.9929 | 0.943 | 0 | 0 | 32.0934 | 87.551 | 0.1011%
CZ 6A | 0.19802 | 0.054123 | 0.01641 | 0.27855 | 0 | 0.10303 | 0 | 0.046442 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 1.1033 | 3.488% | CZ 6A | 6.6718 | 1.8235 | 1.641 | 13.5905 | 0 | 3.4711 | 0 | 1.5647 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 42.467 | 3.488% | CZ 6A | 1.9548 | 0.53429 | 0 | 2.1236 | 0 | 1.017 | 0 | 0.45846 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 10.1036 | 3.488% | CZ 6A | 0 | 0 | 0.01641 | 0.063426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079837 | 3.488% | CZ 6A | 20.4651 | 5.5935 | 1.7936 | 29.1648 | 0 | 10.6474 | 0 | 4.7996 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 114.5008 | 3.488%
CZ 6B | 0.19832 | 0.05405 | 0.016258 | 0.20002 | 0 | 0.072047 | 0 | 0.050634 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 0.99808 | 0.4679% | CZ 6B | 6.6817 | 1.821 | 1.6258 | 9.3522 | 0 | 2.4274 | 0 | 1.7059 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 37.3184 | 0.4679% | CZ 6B | 1.9577 | 0.53356 | 0 | 1.5855 | 0 | 0.71123 | 0 | 0.49984 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 9.3032 | 0.4679% | CZ 6B | 0 | 0 | 0.016258 | 0.039411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055669 | 0.4679% | CZ 6B | 20.4954 | 5.5859 | 1.777 | 20.9058 | 0 | 7.4458 | 0 | 5.2329 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 103.4797 | 0.4679%
CZ 7 | 0.19867 | 0.054207 | 0.017128 | 0.32947 | 0 | 0.078186 | 0 | 0.045702 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091194 | 0 | 0 | 0.31054 | 1.1301 | 0.3712% | CZ 7 | 6.6935 | 1.8263 | 1.7128 | 16.6275 | 0 | 2.6342 | 0 | 1.5398 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 44.7385 | 0.3712% | CZ 7 | 1.9612 | 0.53512 | 0 | 2.4295 | 0 | 0.77183 | 0 | 0.45115 | 0 | 0.00077696 | 0 | 0.859 | 0.090023 | 0 | 0 | 3.0656 | 10.1642 | 0.3712% | CZ 7 | 0 | 0 | 0.017128 | 0.083356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10048 | 0.3712% | CZ 7 | 20.5318 | 5.6021 | 1.8721 | 34.5457 | 0 | 8.0803 | 0 | 4.7231 | 0 | 0.008134 | 0 | 8.9929 | 0.94246 | 0 | 0 | 32.0934 | 117.3919 | 0.3712%
CZ 8 | 0.20655 | 0.054512 | 0.018105 | 0.49055 | 0 | 0.034568 | 0 | 0.047066 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091351 | 0 | 0 | 0.31054 | 1.2581 | 0.113% | CZ 8 | 6.959 | 1.8366 | 1.8105 | 24.923 | 0 | 1.1646 | 0 | 1.5857 | 0 | 0.0026517 | 0 | 2.9318 | 0.30778 | 0 | 0 | 10.4627 | 51.9844 | 0.113% | CZ 8 | 2.039 | 0.53812 | 0 | 3.5927 | 0 | 0.34124 | 0 | 0.46462 | 0 | 0.00077696 | 0 | 0.859 | 0.090179 | 0 | 0 | 3.0656 | 10.9911 | 0.113% | CZ 8 | 0 | 0 | 0.018105 | 0.12661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14472 | 0.113% | CZ 8 | 21.3462 | 5.6336 | 1.9789 | 51.4504 | 0 | 3.5724 | 0 | 4.8641 | 0 | 0.008134 | 0 | 8.9929 | 0.94408 | 0 | 0 | 32.0934 | 130.8842 | 0.113%
US Weighted | 0.19973 | 0.054071 | 0.014467 | 0.096166 | 0 | 0.19044 | 0 | 0.049396 | 0 | 7.8706e-05 | 0 | 0.087017 | 0.0091254 | 0 | 0 | 0.31054 | 1.011 | 100% | US Weighted | 6.7292 | 1.8217 | 1.4467 | 4.2909 | 0 | 6.4163 | 0 | 1.6642 | 0 | 0.0026517 | 0 | 2.9318 | 0.30745 | 0 | 0 | 10.4627 | 36.0736 | 100% | US Weighted | 1.9717 | 0.53377 | 0 | 0.79286 | 0 | 1.88 | 0 | 0.48762 | 0 | 0.00077696 | 0 | 0.859 | 0.090083 | 0 | 0 | 3.0656 | 9.6813 | 100% | US Weighted | 0 | 0 | 0.014467 | 0.015849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030316 | 100% | US Weighted | 20.6412 | 5.588 | 1.5813 | 10.0328 | 0 | 19.6816 | 0 | 5.1049 | 0 | 0.008134 | 0 | 8.9929 | 0.94308 | 0 | 0 | 32.0934 | 104.6673 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.29004 | 0.11843 | 0.012656 | 0.0021093 | 0 | 0.52525 | 0 | 0.069418 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.464 | 3.52% | CZ 1A | 9.772 | 3.99 | 1.2656 | 0.071066 | 0 | 17.6964 | 0 | 2.3388 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 50.1628 | 3.52% | CZ 1A | 2.8632 | 1.1691 | 0 | 0.020822 | 0 | 5.1851 | 0 | 0.68528 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.3269 | 3.52% | CZ 1A | 0 | 0 | 0.012656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012656 | 3.52% | CZ 1A | 29.9747 | 12.2389 | 1.3833 | 0.21799 | 0 | 54.2823 | 0 | 7.1742 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 151.3715 | 3.52%
CZ 1B | 0.29004 | 0.11828 | 0.012784 | 0.02396 | 0 | 0.54053 | 0 | 0.079771 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.5114 | 0% | CZ 1B | 9.772 | 3.9852 | 1.2784 | 0.80984 | 0 | 18.2112 | 0 | 2.6876 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 51.7732 | 0% | CZ 1B | 2.8632 | 1.1677 | 0 | 0.23614 | 0 | 5.3359 | 0 | 0.78747 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.7938 | 0% | CZ 1B | 0 | 0 | 0.012784 | 3.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012822 | 0% | CZ 1B | 29.9747 | 12.2243 | 1.3972 | 2.4764 | 0 | 55.8614 | 0 | 8.244 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 156.2782 | 0%
CZ 2A | 0.29004 | 0.11819 | 0.013275 | 0.032414 | 0 | 0.47039 | 0 | 0.061627 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.432 | 14.08% | CZ 2A | 9.772 | 3.982 | 1.3275 | 1.1448 | 0 | 15.8483 | 0 | 2.0763 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 49.1801 | 14.08% | CZ 2A | 2.8632 | 1.1667 | 0 | 0.31213 | 0 | 4.6436 | 0 | 0.60836 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 13.9975 | 14.08% | CZ 2A | 0 | 0 | 0.013275 | 0.00079533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01407 | 14.08% | CZ 2A | 29.9747 | 12.2145 | 1.4509 | 3.3546 | 0 | 48.6135 | 0 | 6.3689 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 148.0778 | 14.08%
CZ 2B | 0.29004 | 0.11826 | 0.013324 | 0.042104 | 0 | 0.35477 | 0 | 0.074886 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.3395 | 4.829% | CZ 2B | 9.772 | 3.9845 | 1.3324 | 1.4259 | 0 | 11.9529 | 0 | 2.523 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.0199 | 4.829% | CZ 2B | 2.8632 | 1.1675 | 0 | 0.41453 | 0 | 3.5022 | 0 | 0.73925 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 13.0902 | 4.829% | CZ 2B | 0 | 0 | 0.013324 | 0.00011135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013436 | 4.829% | CZ 2B | 29.9747 | 12.2221 | 1.4564 | 4.3519 | 0 | 36.6647 | 0 | 7.7392 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 138.5096 | 4.829%
CZ 3A | 0.29004 | 0.11838 | 0.014383 | 0.091028 | 0 | 0.27772 | 0 | 0.050734 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.2884 | 13.71% | CZ 3A | 9.772 | 3.9884 | 1.4383 | 4.0416 | 0 | 9.3567 | 0 | 1.7093 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 45.3352 | 13.71% | CZ 3A | 2.8632 | 1.1686 | 0 | 0.75349 | 0 | 2.7415 | 0 | 0.50083 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 12.4311 | 13.71% | CZ 3A | 0 | 0 | 0.014383 | 0.014699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029082 | 13.71% | CZ 3A | 29.9747 | 12.234 | 1.5721 | 9.495 | 0 | 28.701 | 0 | 5.2432 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 133.32 | 13.71%
CZ 3B | 0.29004 | 0.1183 | 0.014084 | 0.040708 | 0 | 0.24521 | 0 | 0.060813 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2152 | 11.83% | CZ 3B | 9.772 | 3.9857 | 1.4084 | 1.4941 | 0 | 8.2616 | 0 | 2.0489 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 41.9999 | 11.83% | CZ 3B | 2.8632 | 1.1678 | 0 | 0.38361 | 0 | 2.4206 | 0 | 0.60033 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.8391 | 11.83% | CZ 3B | 0 | 0 | 0.014084 | 0.0018487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015933 | 11.83% | CZ 3B | 29.9747 | 12.2259 | 1.5394 | 4.2181 | 0 | 25.3416 | 0 | 6.2848 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 125.6852 | 11.83%
CZ 3C | 0.29004 | 0.11829 | 0.01448 | 0.021152 | 0 | 0.20132 | 0 | 0.04652 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.1379 | 2.246% | CZ 3C | 9.772 | 3.9856 | 1.448 | 0.72038 | 0 | 6.7828 | 0 | 1.5673 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 39.3052 | 2.246% | CZ 3C | 2.8632 | 1.1678 | 0 | 0.20765 | 0 | 1.9874 | 0 | 0.45923 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.0887 | 2.246% | CZ 3C | 0 | 0 | 0.01448 | 0.00011665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014597 | 2.246% | CZ 3C | 29.9747 | 12.2254 | 1.5827 | 2.1867 | 0 | 20.8056 | 0 | 4.8077 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 117.6834 | 2.246%
CZ 4A | 0.29004 | 0.11816 | 0.015279 | 0.16987 | 0 | 0.2018 | 0 | 0.048582 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2898 | 19.19% | CZ 4A | 9.772 | 3.981 | 1.5279 | 7.402 | 0 | 6.799 | 0 | 1.6368 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.1478 | 19.19% | CZ 4A | 2.8632 | 1.1664 | 0 | 1.4269 | 0 | 1.9921 | 0 | 0.47959 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 12.3318 | 19.19% | CZ 4A | 0 | 0 | 0.015279 | 0.02532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040599 | 19.19% | CZ 4A | 29.9747 | 12.2113 | 1.67 | 17.7057 | 0 | 20.8555 | 0 | 5.0208 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 133.5387 | 19.19%
CZ 4B | 0.29004 | 0.11821 | 0.015016 | 0.073518 | 0 | 0.19495 | 0 | 0.062744 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2006 | 0.6394% | CZ 4B | 9.772 | 3.9825 | 1.5016 | 2.8121 | 0 | 6.5682 | 0 | 2.114 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 41.7795 | 0.6394% | CZ 4B | 2.8632 | 1.1669 | 0 | 0.67585 | 0 | 1.9245 | 0 | 0.61939 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.6533 | 0.6394% | CZ 4B | 0 | 0 | 0.015016 | 0.0050547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020071 | 0.6394% | CZ 4B | 29.9747 | 12.2161 | 1.6412 | 7.6279 | 0 | 20.1473 | 0 | 6.4844 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 124.1924 | 0.6394%
CZ 4C | 0.29004 | 0.11806 | 0.015542 | 0.1363 | 0 | 0.10453 | 0 | 0.044012 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.1546 | 3.137% | CZ 4C | 9.772 | 3.9778 | 1.5542 | 5.1408 | 0 | 3.5219 | 0 | 1.4828 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 40.4786 | 3.137% | CZ 4C | 2.8632 | 1.1655 | 0 | 1.2639 | 0 | 1.0319 | 0 | 0.43447 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.1625 | 3.137% | CZ 4C | 0 | 0 | 0.015542 | 0.0082714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023814 | 3.137% | CZ 4C | 29.9747 | 12.2015 | 1.6988 | 14.1359 | 0 | 10.803 | 0 | 4.5485 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 119.463 | 3.137%
CZ 5A | 0.29004 | 0.11806 | 0.016066 | 0.27368 | 0 | 0.12779 | 0 | 0.046352 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.3181 | 16.56% | CZ 5A | 9.772 | 3.9778 | 1.6066 | 12.5448 | 0 | 4.3055 | 0 | 1.5617 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 48.7973 | 16.56% | CZ 5A | 2.8632 | 1.1655 | 0 | 2.2068 | 0 | 1.2615 | 0 | 0.45758 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 12.358 | 16.56% | CZ 5A | 0 | 0 | 0.016066 | 0.050132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066198 | 16.56% | CZ 5A | 29.9747 | 12.2015 | 1.756 | 28.5821 | 0 | 13.2068 | 0 | 4.7904 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 136.6116 | 16.56%
CZ 5B | 0.29004 | 0.11817 | 0.015832 | 0.15509 | 0 | 0.15158 | 0 | 0.059486 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.2363 | 5.726% | CZ 5B | 9.772 | 3.9813 | 1.5832 | 6.4146 | 0 | 5.1071 | 0 | 2.0042 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 43.8913 | 5.726% | CZ 5B | 2.8632 | 1.1665 | 0 | 1.3539 | 0 | 1.4964 | 0 | 0.58722 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 11.8707 | 5.726% | CZ 5B | 0 | 0 | 0.015832 | 0.017937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03377 | 5.726% | CZ 5B | 29.9747 | 12.2123 | 1.7305 | 16.1348 | 0 | 15.6655 | 0 | 6.1477 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 127.9655 | 5.726%
CZ 5C | 0.29004 | 0.11803 | 0.015998 | 0.1427 | 0 | 0.072792 | 0 | 0.042323 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.128 | 0.1011% | CZ 5C | 9.772 | 3.9767 | 1.5998 | 5.65 | 0 | 2.4525 | 0 | 1.4259 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 39.9059 | 0.1011% | CZ 5C | 2.8632 | 1.1652 | 0 | 1.2834 | 0 | 0.71858 | 0 | 0.4178 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 10.8516 | 0.1011% | CZ 5C | 0 | 0 | 0.015998 | 0.012699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028697 | 0.1011% | CZ 5C | 29.9747 | 12.1982 | 1.7486 | 14.8237 | 0 | 7.5228 | 0 | 4.3739 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 116.7421 | 0.1011%
CZ 6A | 0.29004 | 0.11815 | 0.016667 | 0.39792 | 0 | 0.13511 | 0 | 0.050099 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.4541 | 3.488% | CZ 6A | 9.772 | 3.9808 | 1.6667 | 18.7219 | 0 | 4.552 | 0 | 1.6879 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 55.4102 | 3.488% | CZ 6A | 2.8632 | 1.1664 | 0 | 3.1368 | 0 | 1.3337 | 0 | 0.49456 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 13.3981 | 3.488% | CZ 6A | 0 | 0 | 0.016667 | 0.080162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096828 | 3.488% | CZ 6A | 29.9747 | 12.2107 | 1.8216 | 41.6007 | 0 | 13.9628 | 0 | 5.1775 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 150.8482 | 3.488%
CZ 6B | 0.29004 | 0.11806 | 0.016511 | 0.27716 | 0 | 0.10669 | 0 | 0.053016 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.3076 | 0.4679% | CZ 6B | 9.772 | 3.9776 | 1.6511 | 12.1812 | 0 | 3.5947 | 0 | 1.7862 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 47.9919 | 0.4679% | CZ 6B | 2.8632 | 1.1654 | 0 | 2.3128 | 0 | 1.0532 | 0 | 0.52336 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 12.3216 | 0.4679% | CZ 6B | 0 | 0 | 0.016511 | 0.042877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059388 | 0.4679% | CZ 6B | 29.9747 | 12.2009 | 1.8046 | 28.8991 | 0 | 11.0264 | 0 | 5.479 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 135.4855 | 0.4679%
CZ 7 | 0.29004 | 0.11811 | 0.017373 | 0.44843 | 0 | 0.10735 | 0 | 0.048845 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.4762 | 0.3712% | CZ 7 | 9.772 | 3.9794 | 1.7373 | 22.139 | 0 | 3.617 | 0 | 1.6457 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 57.9193 | 0.3712% | CZ 7 | 2.8632 | 1.166 | 0 | 3.38 | 0 | 1.0598 | 0 | 0.48218 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 13.3546 | 0.3712% | CZ 7 | 0 | 0 | 0.017373 | 0.10603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1234 | 0.3712% | CZ 7 | 29.9747 | 12.2064 | 1.8989 | 46.9747 | 0 | 11.0947 | 0 | 5.0479 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 153.2974 | 0.3712%
CZ 8 | 0.29004 | 0.11729 | 0.018342 | 0.62705 | 0 | 0.063495 | 0 | 0.048378 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.6107 | 0.113% | CZ 8 | 9.772 | 3.9518 | 1.8342 | 32.0173 | 0 | 2.1392 | 0 | 1.6299 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 66.3735 | 0.113% | CZ 8 | 2.8632 | 1.1579 | 0 | 4.5686 | 0 | 0.6268 | 0 | 0.47757 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 14.0976 | 0.113% | CZ 8 | 0 | 0 | 0.018342 | 0.16425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18259 | 0.113% | CZ 8 | 29.9747 | 12.1218 | 2.0048 | 65.781 | 0 | 6.5619 | 0 | 4.9997 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 167.5446 | 0.113%
US Weighted | 0.29004 | 0.11821 | 0.014763 | 0.13367 | 0 | 0.25229 | 0 | 0.054388 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017712 | 0 | 0 | 0.33648 | 1.3094 | 100% | US Weighted | 9.772 | 3.9826 | 1.4763 | 5.8577 | 0 | 8.5001 | 0 | 1.8324 | 0 | 0.0026517 | 0 | 3.093 | 0.59674 | 0 | 0 | 11.3367 | 46.4501 | 100% | US Weighted | 2.8632 | 1.1669 | 0 | 1.118 | 0 | 2.4905 | 0 | 0.5369 | 0 | 0.00077696 | 0 | 0.90624 | 0.17484 | 0 | 0 | 3.3216 | 12.579 | 100% | US Weighted | 0 | 0 | 0.014763 | 0.020421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035184 | 100% | US Weighted | 29.9747 | 12.2163 | 1.6136 | 13.936 | 0 | 26.0733 | 0 | 5.6208 | 0 | 0.008134 | 0 | 9.4875 | 1.8304 | 0 | 0 | 34.7743 | 135.5351 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.29004 | 0.11843 | 0.012656 | 0.002167 | 0 | 0.55322 | 0 | 0.078821 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.5014 | 3.52% | CZ 1A | 9.772 | 3.99 | 1.2656 | 0.073011 | 0 | 18.6388 | 0 | 2.6556 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 51.424 | 3.52% | CZ 1A | 2.8632 | 1.1691 | 0 | 0.021392 | 0 | 5.4612 | 0 | 0.7781 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.6964 | 3.52% | CZ 1A | 0 | 0 | 0.012656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012656 | 3.52% | CZ 1A | 29.9747 | 12.2389 | 1.3833 | 0.22396 | 0 | 57.1731 | 0 | 8.1459 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 155.24 | 3.52%
CZ 1B | 0.29004 | 0.11828 | 0.012784 | 0.025265 | 0 | 0.574 | 0 | 0.094541 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.561 | 0% | CZ 1B | 9.772 | 3.9852 | 1.2784 | 0.86729 | 0 | 19.3389 | 0 | 3.1853 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 53.4559 | 0% | CZ 1B | 2.8632 | 1.1677 | 0 | 0.24702 | 0 | 5.6663 | 0 | 0.93328 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 15.2809 | 0% | CZ 1B | 0 | 0 | 0.012784 | 0.00024213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013026 | 0% | CZ 1B | 29.9747 | 12.2243 | 1.3972 | 2.6125 | 0 | 59.3205 | 0 | 9.7705 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 161.3998 | 0%
CZ 2A | 0.29004 | 0.11819 | 0.013275 | 0.042365 | 0 | 0.50356 | 0 | 0.070195 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.4837 | 14.08% | CZ 2A | 9.772 | 3.982 | 1.3275 | 1.5655 | 0 | 16.966 | 0 | 2.365 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 51.0071 | 14.08% | CZ 2A | 2.8632 | 1.1667 | 0 | 0.39765 | 0 | 4.971 | 0 | 0.69294 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 14.4951 | 14.08% | CZ 2A | 0 | 0 | 0.013275 | 0.0020838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015359 | 14.08% | CZ 2A | 29.9747 | 12.2145 | 1.4509 | 4.3907 | 0 | 52.0417 | 0 | 7.2544 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 153.4276 | 14.08%
CZ 2B | 0.29004 | 0.11826 | 0.013324 | 0.054206 | 0 | 0.37153 | 0 | 0.090029 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.3835 | 4.829% | CZ 2B | 9.772 | 3.9845 | 1.3324 | 1.8527 | 0 | 12.5176 | 0 | 3.0332 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 47.5213 | 4.829% | CZ 2B | 2.8632 | 1.1675 | 0 | 0.53118 | 0 | 3.6677 | 0 | 0.88874 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 13.5217 | 4.829% | CZ 2B | 0 | 0 | 0.013324 | 0.00039766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013722 | 4.829% | CZ 2B | 29.9747 | 12.2221 | 1.4564 | 5.6044 | 0 | 38.3967 | 0 | 9.3042 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 143.0585 | 4.829%
CZ 3A | 0.29004 | 0.11838 | 0.014385 | 0.12132 | 0 | 0.2929 | 0 | 0.059575 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017704 | 0 | 0 | 0.33648 | 1.3427 | 13.71% | CZ 3A | 9.772 | 3.9884 | 1.4385 | 5.637 | 0 | 9.8682 | 0 | 2.0072 | 0 | 0.0026517 | 0 | 3.093 | 0.59646 | 0 | 0 | 11.3367 | 47.74 | 13.71% | CZ 3A | 2.8632 | 1.1686 | 0 | 0.9669 | 0 | 2.8914 | 0 | 0.5881 | 0 | 0.00077696 | 0 | 0.90624 | 0.17476 | 0 | 0 | 3.3216 | 12.8816 | 13.71% | CZ 3A | 0 | 0 | 0.014385 | 0.02337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037755 | 13.71% | CZ 3A | 29.9747 | 12.234 | 1.5723 | 12.6768 | 0 | 30.2697 | 0 | 6.1569 | 0 | 0.008134 | 0 | 9.4875 | 1.8296 | 0 | 0 | 34.7743 | 138.984 | 13.71%
CZ 3B | 0.29004 | 0.1183 | 0.014084 | 0.056778 | 0 | 0.25738 | 0 | 0.070347 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.253 | 11.83% | CZ 3B | 9.772 | 3.9857 | 1.4084 | 2.1906 | 0 | 8.6717 | 0 | 2.3701 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 43.4277 | 11.83% | CZ 3B | 2.8632 | 1.1678 | 0 | 0.51916 | 0 | 2.5408 | 0 | 0.69444 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 12.189 | 11.83% | CZ 3B | 0 | 0 | 0.014084 | 0.004187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018271 | 11.83% | CZ 3B | 29.9747 | 12.2259 | 1.5394 | 5.8928 | 0 | 26.5997 | 0 | 7.2701 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 129.6033 | 11.83%
CZ 3C | 0.29004 | 0.11829 | 0.01448 | 0.051838 | 0 | 0.22359 | 0 | 0.05957 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2039 | 2.246% | CZ 3C | 9.772 | 3.9856 | 1.448 | 1.7588 | 0 | 7.5332 | 0 | 2.007 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 41.5337 | 2.246% | CZ 3C | 2.8632 | 1.1678 | 0 | 0.50989 | 0 | 2.2072 | 0 | 0.58805 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.7397 | 2.246% | CZ 3C | 0 | 0 | 0.01448 | 0.00018558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014666 | 2.246% | CZ 3C | 29.9747 | 12.2254 | 1.5827 | 5.3583 | 0 | 23.1075 | 0 | 6.1563 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 124.5056 | 2.246%
CZ 4A | 0.29004 | 0.11816 | 0.015281 | 0.24695 | 0 | 0.21008 | 0 | 0.058384 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.385 | 19.19% | CZ 4A | 9.772 | 3.981 | 1.5281 | 10.8491 | 0 | 7.0778 | 0 | 1.9671 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 50.2041 | 19.19% | CZ 4A | 2.8632 | 1.1664 | 0 | 2.0613 | 0 | 2.0738 | 0 | 0.57635 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 13.1446 | 19.19% | CZ 4A | 0 | 0 | 0.015281 | 0.03814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053421 | 19.19% | CZ 4A | 29.9747 | 12.2113 | 1.6702 | 25.7481 | 0 | 21.7106 | 0 | 6.0338 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 143.4494 | 19.19%
CZ 4B | 0.29004 | 0.11821 | 0.015018 | 0.12004 | 0 | 0.20298 | 0 | 0.072882 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2652 | 0.6394% | CZ 4B | 9.772 | 3.9825 | 1.5018 | 4.7891 | 0 | 6.8388 | 0 | 2.4555 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 44.3688 | 0.6394% | CZ 4B | 2.8632 | 1.1669 | 0 | 1.0742 | 0 | 2.0038 | 0 | 0.71946 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 12.231 | 0.6394% | CZ 4B | 0 | 0 | 0.015018 | 0.01123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026248 | 0.6394% | CZ 4B | 29.9747 | 12.2161 | 1.6414 | 12.4729 | 0 | 20.9775 | 0 | 7.5321 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 130.9154 | 0.6394%
CZ 4C | 0.29004 | 0.11806 | 0.015546 | 0.20313 | 0 | 0.10393 | 0 | 0.051899 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017714 | 0 | 0 | 0.33648 | 1.2287 | 3.137% | CZ 4C | 9.772 | 3.9778 | 1.5546 | 7.8936 | 0 | 3.5017 | 0 | 1.7486 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 43.4774 | 3.137% | CZ 4C | 2.8632 | 1.1655 | 0 | 1.849 | 0 | 1.026 | 0 | 0.51233 | 0 | 0.00077696 | 0 | 0.90624 | 0.17487 | 0 | 0 | 3.3216 | 11.8195 | 3.137% | CZ 4C | 0 | 0 | 0.015546 | 0.015831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031377 | 3.137% | CZ 4C | 29.9747 | 12.2015 | 1.6992 | 21.0875 | 0 | 10.7412 | 0 | 5.3635 | 0 | 0.008134 | 0 | 9.4875 | 1.8307 | 0 | 0 | 34.7743 | 127.1682 | 3.137%
CZ 5A | 0.29004 | 0.11806 | 0.016067 | 0.35347 | 0 | 0.13053 | 0 | 0.05479 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.409 | 16.56% | CZ 5A | 9.772 | 3.9778 | 1.6067 | 16.4815 | 0 | 4.3978 | 0 | 1.846 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 53.1107 | 16.56% | CZ 5A | 2.8632 | 1.1655 | 0 | 2.8086 | 0 | 1.2886 | 0 | 0.54087 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 13.0702 | 16.56% | CZ 5A | 0 | 0 | 0.016067 | 0.068957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085024 | 16.56% | CZ 5A | 29.9747 | 12.2015 | 1.7562 | 36.9407 | 0 | 13.4899 | 0 | 5.6623 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 146.1254 | 16.56%
CZ 5B | 0.29004 | 0.11817 | 0.015832 | 0.21493 | 0 | 0.15421 | 0 | 0.06882 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.3081 | 5.726% | CZ 5B | 9.772 | 3.9813 | 1.5832 | 9.3915 | 0 | 5.1954 | 0 | 2.3187 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 47.2711 | 5.726% | CZ 5B | 2.8632 | 1.1665 | 0 | 1.8016 | 0 | 1.5223 | 0 | 0.67937 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 12.4364 | 5.726% | CZ 5B | 0 | 0 | 0.015832 | 0.032428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04826 | 5.726% | CZ 5B | 29.9747 | 12.2123 | 1.7305 | 22.4049 | 0 | 15.9366 | 0 | 7.1123 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 135.4715 | 5.726%
CZ 5C | 0.29004 | 0.11803 | 0.016 | 0.20036 | 0 | 0.071161 | 0 | 0.049527 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.1912 | 0.1011% | CZ 5C | 9.772 | 3.9767 | 1.6 | 8.3043 | 0 | 2.3975 | 0 | 1.6686 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 42.7481 | 0.1011% | CZ 5C | 2.8632 | 1.1652 | 0 | 1.7465 | 0 | 0.70247 | 0 | 0.48891 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 11.3698 | 0.1011% | CZ 5C | 0 | 0 | 0.016 | 0.023434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039434 | 0.1011% | CZ 5C | 29.9747 | 12.1982 | 1.7488 | 20.8459 | 0 | 7.3542 | 0 | 5.1184 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 123.3404 | 0.1011%
CZ 6A | 0.29004 | 0.11815 | 0.016668 | 0.5003 | 0 | 0.13904 | 0 | 0.059507 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.5698 | 3.488% | CZ 6A | 9.772 | 3.9808 | 1.6668 | 23.8508 | 0 | 4.6845 | 0 | 2.0049 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 60.9888 | 3.488% | CZ 6A | 2.8632 | 1.1664 | 0 | 3.8974 | 0 | 1.3726 | 0 | 0.58743 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.2905 | 3.488% | CZ 6A | 0 | 0 | 0.016668 | 0.10549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12216 | 3.488% | CZ 6A | 29.9747 | 12.2107 | 1.8218 | 52.3322 | 0 | 14.3695 | 0 | 6.1498 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 162.9589 | 3.488%
CZ 6B | 0.29004 | 0.11806 | 0.016515 | 0.36898 | 0 | 0.10816 | 0 | 0.06191 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.4097 | 0.4679% | CZ 6B | 9.772 | 3.9776 | 1.6515 | 16.7556 | 0 | 3.644 | 0 | 2.0859 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 52.9154 | 0.4679% | CZ 6B | 2.8632 | 1.1654 | 0 | 2.9987 | 0 | 1.0677 | 0 | 0.61115 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 13.1097 | 0.4679% | CZ 6B | 0 | 0 | 0.016515 | 0.06521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081724 | 0.4679% | CZ 6B | 29.9747 | 12.2009 | 1.805 | 38.5213 | 0 | 11.1777 | 0 | 6.3982 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 146.178 | 0.4679%
CZ 7 | 0.29004 | 0.11811 | 0.017377 | 0.56442 | 0 | 0.11818 | 0 | 0.063232 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.6174 | 0.3712% | CZ 7 | 9.772 | 3.9794 | 1.7377 | 27.7417 | 0 | 3.9818 | 0 | 2.1304 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 64.3719 | 0.3712% | CZ 7 | 2.8632 | 1.166 | 0 | 4.2728 | 0 | 1.1667 | 0 | 0.62421 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.4963 | 0.3712% | CZ 7 | 0 | 0 | 0.017377 | 0.13159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14896 | 0.3712% | CZ 7 | 29.9747 | 12.2064 | 1.8993 | 59.1145 | 0 | 12.214 | 0 | 6.5348 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 168.0438 | 0.3712%
CZ 8 | 0.29004 | 0.11729 | 0.018342 | 0.71695 | 0 | 0.067776 | 0 | 0.061474 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017709 | 0 | 0 | 0.33648 | 1.7179 | 0.113% | CZ 8 | 9.772 | 3.9518 | 1.8342 | 37.3676 | 0 | 2.2835 | 0 | 2.0712 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 72.3092 | 0.113% | CZ 8 | 2.8632 | 1.1579 | 0 | 5.1105 | 0 | 0.66906 | 0 | 0.60686 | 0 | 0.00077696 | 0 | 0.90624 | 0.17482 | 0 | 0 | 3.3216 | 14.8109 | 0.113% | CZ 8 | 0 | 0 | 0.018342 | 0.19926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2176 | 0.113% | CZ 8 | 29.9747 | 12.1218 | 2.0048 | 75.2803 | 0 | 7.0044 | 0 | 6.3532 | 0 | 0.008134 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7743 | 178.8393 | 0.113%
US Weighted | 0.29004 | 0.11821 | 0.014764 | 0.18081 | 0 | 0.26519 | 0 | 0.063859 | 0 | 7.8706e-05 | 0 | 0.091802 | 0.017711 | 0 | 0 | 0.33648 | 1.3789 | 100% | US Weighted | 9.772 | 3.9826 | 1.4764 | 8.0745 | 0 | 8.9346 | 0 | 2.1515 | 0 | 0.0026517 | 0 | 3.093 | 0.59671 | 0 | 0 | 11.3367 | 49.4206 | 100% | US Weighted | 2.8632 | 1.1669 | 0 | 1.4898 | 0 | 2.6178 | 0 | 0.6304 | 0 | 0.00077696 | 0 | 0.90624 | 0.17483 | 0 | 0 | 3.3216 | 13.1716 | 100% | US Weighted | 0 | 0 | 0.014764 | 0.029899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044663 | 100% | US Weighted | 29.9747 | 12.2163 | 1.6137 | 18.8645 | 0 | 27.4061 | 0 | 6.5996 | 0 | 0.008134 | 0 | 9.4875 | 1.8303 | 0 | 0 | 34.7743 | 142.7753 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Medium Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 53628 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 53628 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.13154 | 0.093922 | 0.00071933 | 0.0016686 | 0 | 0.22107 | 0 | 0.029588 | -0.0086629 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.51611 | 3.52% | CZ 1A | 4.4319 | 3.1644 | 0.071933 | 0.056217 | 0 | 7.4484 | 0 | 0.99687 | -0.29187 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 17.4364 | 3.52% | CZ 1A | 1.2986 | 0.92717 | 0 | 0.016471 | 0 | 2.1824 | 0 | 0.29208 | -0.085517 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 5.0878 | 3.52% | CZ 1A | 0 | 0 | 0.00071933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071933 | 3.52% | CZ 1A | 13.5946 | 9.7065 | 0.078623 | 0.17244 | 0 | 22.8472 | 0 | 3.0578 | -0.89528 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 53.3425 | 3.52%
CZ 1B | 0.13147 | 0.093838 | 0.00079709 | 0.015622 | 0 | 0.19005 | 0 | 0.044206 | 0 | 0 | 0 | 0.0050214 | 0.011544 | 0 | 0 | 0.029698 | 0.52225 | 0% | CZ 1B | 4.4295 | 3.1616 | 0.079709 | 0.52575 | 0 | 6.403 | 0 | 1.4894 | 0 | 0 | 0 | 0.16918 | 0.38892 | 0 | 0 | 1.0006 | 17.6476 | 0% | CZ 1B | 1.2978 | 0.92634 | 0 | 0.1543 | 0 | 1.8761 | 0 | 0.43639 | 0 | 0 | 0 | 0.04957 | 0.11395 | 0 | 0 | 0.29317 | 5.1477 | 0% | CZ 1B | 0 | 0 | 0.00079709 | -8.837e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00078826 | 0% | CZ 1B | 13.587 | 9.6979 | 0.087122 | 1.6144 | 0 | 19.6408 | 0 | 4.5686 | 0 | 0 | 0 | 0.51895 | 1.193 | 0 | 0 | 3.0692 | 53.9769 | 0%
CZ 2A | 0.13161 | 0.09367 | 0.00066277 | 0.022664 | 0 | 0.2075 | 0 | 0.027442 | 0 | 0 | 0 | 0.0050214 | 0.011549 | 0 | 0 | 0.029698 | 0.52982 | 14.08% | CZ 2A | 4.4342 | 3.1559 | 0.066277 | 0.8904 | 0 | 6.991 | 0 | 0.92457 | 0 | 0 | 0 | 0.16918 | 0.3891 | 0 | 0 | 1.0006 | 18.0213 | 14.08% | CZ 2A | 1.2992 | 0.92468 | 0 | 0.20486 | 0 | 2.0484 | 0 | 0.2709 | 0 | 0 | 0 | 0.04957 | 0.11401 | 0 | 0 | 0.29317 | 5.2048 | 14.08% | CZ 2A | 0 | 0 | 0.00066277 | 0.0019123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025751 | 14.08% | CZ 2A | 13.6016 | 9.6805 | 0.072441 | 2.3537 | 0 | 21.4444 | 0 | 2.836 | 0 | 0 | 0 | 0.51895 | 1.1935 | 0 | 0 | 3.0692 | 54.7704 | 14.08%
CZ 2B | 0.13143 | 0.093744 | 0.00066631 | 0.037815 | 0 | 0.13201 | 0 | 0.039133 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.48105 | 4.829% | CZ 2B | 4.428 | 3.1584 | 0.066631 | 1.2479 | 0 | 4.4475 | 0 | 1.3184 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 16.2254 | 4.829% | CZ 2B | 1.2974 | 0.92541 | 0 | 0.37719 | 0 | 1.3031 | 0 | 0.3863 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.7461 | 4.829% | CZ 2B | 0 | 0 | 0.00066631 | -0.00039413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00027218 | 4.829% | CZ 2B | 13.5826 | 9.6881 | 0.072827 | 3.9057 | 0 | 13.6423 | 0 | 4.0442 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 49.7164 | 4.829%
CZ 3A | 0.13082 | 0.093571 | 0.00058854 | 0.038805 | 0 | 0.11346 | 0 | 0.021025 | 0 | 0 | 0 | 0.0050214 | 0.011528 | 0 | 0 | 0.029698 | 0.44452 | 13.71% | CZ 3A | 4.4077 | 3.1526 | 0.058854 | 2.5194 | 0 | 3.8227 | 0 | 0.70837 | 0 | 0 | 0 | 0.16918 | 0.38839 | 0 | 0 | 1.0006 | 16.2278 | 13.71% | CZ 3A | 1.2915 | 0.9237 | 0 | 0.20263 | 0 | 1.1201 | 0 | 0.20755 | 0 | 0 | 0 | 0.04957 | 0.1138 | 0 | 0 | 0.29317 | 4.2019 | 13.71% | CZ 3A | 0 | 0 | 0.00058854 | 0.018278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018867 | 13.71% | CZ 3A | 13.5203 | 9.6702 | 0.064328 | 4.1192 | 0 | 11.7259 | 0 | 2.1729 | 0 | 0 | 0 | 0.51895 | 1.1914 | 0 | 0 | 3.0692 | 46.0523 | 13.71%
CZ 3B | 0.13135 | 0.093996 | 0.00059738 | 0.027167 | 0 | 0.084656 | 0 | 0.024745 | 0 | 0 | 0 | 0.0050214 | 0.011544 | 0 | 0 | 0.029698 | 0.40878 | 11.83% | CZ 3B | 4.4256 | 3.1669 | 0.059738 | 0.90336 | 0 | 2.8522 | 0 | 0.8337 | 0 | 0 | 0 | 0.16918 | 0.38892 | 0 | 0 | 1.0006 | 13.8001 | 11.83% | CZ 3B | 1.2967 | 0.92789 | 0 | 0.26997 | 0 | 0.8357 | 0 | 0.24428 | 0 | 0 | 0 | 0.04957 | 0.11395 | 0 | 0 | 0.29317 | 4.0312 | 11.83% | CZ 3B | 0 | 0 | 0.00059738 | -0.00018027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0004171 | 11.83% | CZ 3B | 13.575 | 9.7141 | 0.065293 | 2.8066 | 0 | 8.7489 | 0 | 2.5573 | 0 | 0 | 0 | 0.51895 | 1.193 | 0 | 0 | 3.0692 | 42.2484 | 11.83%
CZ 3C | 0.13107 | 0.094059 | 0.00055673 | 0.040667 | 0 | 0.11128 | 0 | 0.025175 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.44906 | 2.246% | CZ 3C | 4.4158 | 3.169 | 0.055673 | 1.3494 | 0 | 3.7492 | 0 | 0.8482 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 15.1458 | 2.246% | CZ 3C | 1.2938 | 0.92852 | 0 | 0.40454 | 0 | 1.0985 | 0 | 0.24852 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.4306 | 2.246% | CZ 3C | 0 | 0 | 0.00055673 | -0.00031283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002439 | 2.246% | CZ 3C | 13.5452 | 9.7206 | 0.06085 | 4.2009 | 0 | 11.5003 | 0 | 2.6018 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 46.4103 | 2.246%
CZ 4A | 0.13081 | 0.093597 | 0.00055143 | 0.14959 | 0 | 0.079797 | 0 | 0.016093 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.5167 | 19.19% | CZ 4A | 4.4074 | 3.1534 | 0.055143 | 6.2136 | 0 | 2.6885 | 0 | 0.54219 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 18.6188 | 19.19% | CZ 4A | 1.2914 | 0.92396 | 0 | 1.302 | 0 | 0.78773 | 0 | 0.15886 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.9206 | 19.19% | CZ 4A | 0 | 0 | 0.00055143 | 0.017699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01825 | 19.19% | CZ 4A | 13.5192 | 9.6729 | 0.060271 | 15.5654 | 0 | 8.2468 | 0 | 1.6631 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 53.5082 | 19.19%
CZ 4B | 0.13178 | 0.093812 | 0.00056026 | 0.082341 | 0 | 0.067986 | 0 | 0.017651 | 0 | 0 | 0 | 0.0050214 | 0.011544 | 0 | 0 | 0.029698 | 0.4404 | 0.6394% | CZ 4B | 4.4401 | 3.1607 | 0.056026 | 3.0925 | 0 | 2.2906 | 0 | 0.59469 | 0 | 0 | 0 | 0.16918 | 0.38892 | 0 | 0 | 1.0006 | 15.1932 | 0.6394% | CZ 4B | 1.3009 | 0.92608 | 0 | 0.76546 | 0 | 0.67114 | 0 | 0.17425 | 0 | 0 | 0 | 0.04957 | 0.11395 | 0 | 0 | 0.29317 | 4.2946 | 0.6394% | CZ 4B | 0 | 0 | 0.00056026 | 0.0048002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053605 | 0.6394% | CZ 4B | 13.6195 | 9.6951 | 0.061237 | 8.5382 | 0 | 7.0261 | 0 | 1.8242 | 0 | 0 | 0 | 0.51895 | 1.193 | 0 | 0 | 3.0692 | 45.5456 | 0.6394%
CZ 4C | 0.12997 | 0.093104 | 0.00053022 | 0.13181 | 0 | 0.051416 | 0 | 0.015127 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.46822 | 3.137% | CZ 4C | 4.3791 | 3.1368 | 0.053022 | 4.8741 | 0 | 1.7323 | 0 | 0.50966 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 16.2435 | 3.137% | CZ 4C | 1.2831 | 0.91909 | 0 | 1.2368 | 0 | 0.50756 | 0 | 0.14933 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.5525 | 3.137% | CZ 4C | 0 | 0 | 0.00053022 | 0.0065305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070607 | 3.137% | CZ 4C | 13.4324 | 9.6219 | 0.057953 | 13.6614 | 0 | 5.3136 | 0 | 1.5633 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 48.4314 | 3.137%
CZ 5A | 0.13105 | 0.093329 | 0.00053552 | 0.19749 | 0 | 0.046541 | 0 | 0.015505 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.53071 | 16.56% | CZ 5A | 4.4153 | 3.1444 | 0.053552 | 8.5796 | 0 | 1.5681 | 0 | 0.52239 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 19.8418 | 16.56% | CZ 5A | 1.2937 | 0.92132 | 0 | 1.6628 | 0 | 0.45944 | 0 | 0.15306 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.947 | 16.56% | CZ 5A | 0 | 0 | 0.00053552 | 0.029044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029579 | 16.56% | CZ 5A | 13.5436 | 9.6453 | 0.058532 | 20.5828 | 0 | 4.8099 | 0 | 1.6024 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 55.023 | 16.56%
CZ 5B | 0.13121 | 0.093644 | 0.00052315 | 0.12851 | 0 | 0.0582 | 0 | 0.019918 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.47827 | 5.726% | CZ 5B | 4.4208 | 3.155 | 0.052315 | 5.123 | 0 | 1.9609 | 0 | 0.67106 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 16.9416 | 5.726% | CZ 5B | 1.2953 | 0.92442 | 0 | 1.1505 | 0 | 0.57453 | 0 | 0.19662 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 4.598 | 5.726% | CZ 5B | 0 | 0 | 0.00052315 | 0.011963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012487 | 5.726% | CZ 5B | 13.5604 | 9.6778 | 0.05718 | 13.3524 | 0 | 6.0148 | 0 | 2.0584 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 49.5016 | 5.726%
CZ 5C | 0.12975 | 0.093025 | 0.00053022 | 0.12814 | 0 | 0.041 | 0 | 0.012231 | 0 | 0 | 0 | 0.0050214 | 0.011533 | 0 | 0 | 0.029698 | 0.45093 | 0.1011% | CZ 5C | 4.3716 | 3.1342 | 0.053022 | 5.0211 | 0 | 1.3814 | 0 | 0.41208 | 0 | 0 | 0 | 0.16918 | 0.38857 | 0 | 0 | 1.0006 | 15.9317 | 0.1011% | CZ 5C | 1.2809 | 0.91831 | 0 | 1.1602 | 0 | 0.40474 | 0 | 0.12074 | 0 | 0 | 0 | 0.04957 | 0.11385 | 0 | 0 | 0.29317 | 4.3414 | 0.1011% | CZ 5C | 0 | 0 | 0.00053022 | 0.010615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011145 | 0.1011% | CZ 5C | 13.4097 | 9.6138 | 0.057953 | 13.3059 | 0 | 4.2373 | 0 | 1.264 | 0 | 0 | 0 | 0.51895 | 1.1919 | 0 | 0 | 3.0692 | 46.6686 | 0.1011%
CZ 6A | 0.13095 | 0.093377 | 0.00052138 | 0.26925 | 0 | 0.047769 | 0 | 0.017761 | 0 | 0 | 0 | 0.0050214 | 0.011533 | 0 | 0 | 0.029698 | 0.60588 | 3.488% | CZ 6A | 4.412 | 3.146 | 0.052138 | 11.9194 | 0 | 1.6094 | 0 | 0.59841 | 0 | 0 | 0 | 0.16918 | 0.38857 | 0 | 0 | 1.0006 | 23.2956 | 3.488% | CZ 6A | 1.2927 | 0.92178 | 0 | 2.2339 | 0 | 0.47156 | 0 | 0.17533 | 0 | 0 | 0 | 0.04957 | 0.11385 | 0 | 0 | 0.29317 | 5.5519 | 3.488% | CZ 6A | 0 | 0 | 0.00052138 | 0.042951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043473 | 3.488% | CZ 6A | 13.5333 | 9.6501 | 0.056987 | 28.0813 | 0 | 4.9368 | 0 | 1.8356 | 0 | 0 | 0 | 0.51895 | 1.1919 | 0 | 0 | 3.0692 | 62.8742 | 3.488%
CZ 6B | 0.13082 | 0.093025 | 0.00052315 | 0.21013 | 0 | 0.043855 | 0 | 0.016318 | 0 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.54093 | 0.4679% | CZ 6B | 4.4075 | 3.1342 | 0.052315 | 8.7883 | 0 | 1.4775 | 0 | 0.54979 | 0 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 19.9681 | 0.4679% | CZ 6B | 1.2914 | 0.91831 | 0 | 1.8199 | 0 | 0.43292 | 0 | 0.16109 | 0 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 5.0803 | 0.4679% | CZ 6B | 0 | 0 | 0.00052315 | 0.025769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026292 | 0.4679% | CZ 6B | 13.5197 | 9.6138 | 0.05718 | 21.8695 | 0 | 4.5322 | 0 | 1.6864 | 0 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 56.0595 | 0.4679%
CZ 7 | 0.13125 | 0.093056 | 0.00049664 | 0.39195 | 0 | 0.044317 | 0 | 0.01762 | -0.012184 | 0 | 0 | 0.0050214 | 0.011538 | 0 | 0 | 0.029698 | 0.71277 | 0.3712% | CZ 7 | 4.422 | 3.1352 | 0.049664 | 21.0162 | 0 | 1.4931 | 0 | 0.59363 | -0.41049 | 0 | 0 | 0.16918 | 0.38874 | 0 | 0 | 1.0006 | 31.8579 | 0.3712% | CZ 7 | 1.2957 | 0.91862 | 0 | 2.7064 | 0 | 0.43748 | 0 | 0.17393 | -0.12027 | 0 | 0 | 0.04957 | 0.1139 | 0 | 0 | 0.29317 | 5.8685 | 0.3712% | CZ 7 | 0 | 0 | 0.00049664 | 0.11779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11829 | 0.3712% | CZ 7 | 13.5642 | 9.6171 | 0.054282 | 41.2081 | 0 | 4.58 | 0 | 1.8209 | -1.2591 | 0 | 0 | 0.51895 | 1.1924 | 0 | 0 | 3.0692 | 74.366 | 0.3712%
CZ 8 | 0.12543 | 0.090228 | 0.00047189 | 0.4519 | 0 | 0.033487 | 0 | 0.014986 | -0.012672 | 0 | 0 | 0.0050214 | 0.011528 | 0 | 0 | 0.029698 | 0.75008 | 0.113% | CZ 8 | 4.226 | 3.0399 | 0.047189 | 26.2575 | 0 | 1.1282 | 0 | 0.50489 | -0.42693 | 0 | 0 | 0.16918 | 0.38839 | 0 | 0 | 1.0006 | 36.3349 | 0.113% | CZ 8 | 1.2382 | 0.8907 | 0 | 2.8186 | 0 | 0.33057 | 0 | 0.14793 | -0.12509 | 0 | 0 | 0.04957 | 0.1138 | 0 | 0 | 0.29317 | 5.7575 | 0.113% | CZ 8 | 0 | 0 | 0.00047189 | 0.16638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16685 | 0.113% | CZ 8 | 12.9628 | 9.3248 | 0.051578 | 47.6929 | 0 | 3.4607 | 0 | 1.5487 | -1.3096 | 0 | 0 | 0.51895 | 1.1914 | 0 | 0 | 3.0692 | 78.5114 | 0.113%
US Weighted | 0.13109 | 0.093607 | 0.00058285 | 0.10042 | 0 | 0.10195 | 0 | 0.021343 | -0.00036446 | 0 | 0 | 0.0050214 | 0.011539 | 0 | 0 | 0.029698 | 0.49489 | 100% | US Weighted | 4.4168 | 3.1538 | 0.058285 | 4.3187 | 0 | 3.435 | 0 | 0.71908 | -0.012279 | 0 | 0 | 0.16918 | 0.38876 | 0 | 0 | 1.0006 | 17.6478 | 100% | US Weighted | 1.2941 | 0.92406 | 0 | 0.85201 | 0 | 1.0064 | 0 | 0.21069 | -0.0035978 | 0 | 0 | 0.04957 | 0.11391 | 0 | 0 | 0.29317 | 4.7404 | 100% | US Weighted | 0 | 0 | 0.00058285 | 0.014108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014691 | 100% | US Weighted | 13.5481 | 9.674 | 0.063705 | 10.4618 | 0 | 10.5364 | 0 | 2.2057 | -0.037666 | 0 | 0 | 0.51895 | 1.1925 | 0 | 0 | 3.0692 | 51.2327 | 100%
Building Type: | Medium Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 53628 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 53628 | [17 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 45.35% | 79.31% | 5.684% | 77% | 0% | 39.96% | 0% | 37.54% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.38% | 3.52% | CZ 1A | 45.35% | 79.31% | 5.684% | 77% | 0% | 39.96% | 0% | 37.54% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 33.91% | 3.52% | CZ 1A | 45.35% | 79.31% | 0% | 77% | 0% | 39.96% | 0% | 37.54% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.62% | 3.52% | CZ 1A | 0% | 0% | 5.684% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.684% | 3.52% | CZ 1A | 45.35% | 79.31% | 5.684% | 77% | 0% | 39.96% | 0% | 37.54% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.36% | 3.52%
CZ 1B | 45.33% | 79.33% | 6.235% | 61.83% | 0% | 33.11% | 0% | 46.76% | 0% | 0% | 0% | 5.47% | 65.19% | 0% | 0% | 8.826% | 33.46% | 0% | CZ 1B | 45.33% | 79.33% | 6.235% | 60.62% | 0% | 33.11% | 0% | 46.76% | 0% | 0% | 0% | 5.47% | 65.19% | 0% | 0% | 8.826% | 33.01% | 0% | CZ 1B | 45.33% | 79.33% | 0% | 62.47% | 0% | 33.11% | 0% | 46.76% | 0% | 0% | 0% | 5.47% | 65.19% | 0% | 0% | 8.826% | 33.69% | 0% | CZ 1B | 0% | 0% | 6.235% | -3.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.052% | 0% | CZ 1B | 45.33% | 79.33% | 6.235% | 61.8% | 0% | 33.11% | 0% | 46.76% | 0% | 0% | 0% | 5.47% | 65.19% | 0% | 0% | 8.826% | 33.44% | 0%
CZ 2A | 45.38% | 79.25% | 4.993% | 53.5% | 0% | 41.21% | 0% | 39.09% | 0% | 0% | 0% | 5.47% | 65.2% | 0% | 0% | 8.826% | 35.71% | 14.08% | CZ 2A | 45.38% | 79.25% | 4.993% | 56.88% | 0% | 41.21% | 0% | 39.09% | 0% | 0% | 0% | 5.47% | 65.2% | 0% | 0% | 8.826% | 35.33% | 14.08% | CZ 2A | 45.38% | 79.25% | 0% | 51.52% | 0% | 41.21% | 0% | 39.09% | 0% | 0% | 0% | 5.47% | 65.2% | 0% | 0% | 8.826% | 35.91% | 14.08% | CZ 2A | 0% | 0% | 4.993% | 91.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 16.77% | 14.08% | CZ 2A | 45.38% | 79.25% | 4.993% | 53.61% | 0% | 41.21% | 0% | 39.09% | 0% | 0% | 0% | 5.47% | 65.2% | 0% | 0% | 8.826% | 35.7% | 14.08%
CZ 2B | 45.31% | 79.27% | 5.001% | 69.76% | 0% | 35.53% | 0% | 43.47% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.77% | 4.829% | CZ 2B | 45.31% | 79.27% | 5.001% | 67.36% | 0% | 35.53% | 0% | 43.47% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.14% | 4.829% | CZ 2B | 45.31% | 79.27% | 0% | 71.01% | 0% | 35.53% | 0% | 43.47% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 35.1% | 4.829% | CZ 2B | 0% | 0% | 5.001% | -99.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.984% | 4.829% | CZ 2B | 45.31% | 79.27% | 5.001% | 69.69% | 0% | 35.53% | 0% | 43.47% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 34.75% | 4.829%
CZ 3A | 45.11% | 79.04% | 4.091% | 31.99% | 0% | 38.74% | 0% | 35.29% | 0% | 0% | 0% | 5.47% | 65.12% | 0% | 0% | 8.826% | 33.11% | 13.71% | CZ 3A | 45.11% | 79.04% | 4.091% | 44.69% | 0% | 38.74% | 0% | 35.29% | 0% | 0% | 0% | 5.47% | 65.12% | 0% | 0% | 8.826% | 33.99% | 13.71% | CZ 3A | 45.11% | 79.04% | 0% | 20.96% | 0% | 38.74% | 0% | 35.29% | 0% | 0% | 0% | 5.47% | 65.12% | 0% | 0% | 8.826% | 32.62% | 13.71% | CZ 3A | 0% | 0% | 4.091% | 78.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 49.97% | 13.71% | CZ 3A | 45.11% | 79.04% | 4.091% | 32.49% | 0% | 38.74% | 0% | 35.29% | 0% | 0% | 0% | 5.47% | 65.12% | 0% | 0% | 8.826% | 33.13% | 13.71%
CZ 3B | 45.29% | 79.46% | 4.241% | 47.85% | 0% | 32.89% | 0% | 35.18% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 32.62% | 11.83% | CZ 3B | 45.29% | 79.46% | 4.241% | 41.24% | 0% | 32.89% | 0% | 35.18% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 31.78% | 11.83% | CZ 3B | 45.29% | 79.46% | 0% | 52% | 0% | 32.89% | 0% | 35.18% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 33.07% | 11.83% | CZ 3B | 0% | 0% | 4.241% | -4.306% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.283% | 11.83% | CZ 3B | 45.29% | 79.46% | 4.241% | 47.63% | 0% | 32.89% | 0% | 35.18% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 32.6% | 11.83%
CZ 3C | 45.19% | 79.51% | 3.845% | 78.45% | 0% | 49.77% | 0% | 42.26% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.3% | 2.246% | CZ 3C | 45.19% | 79.51% | 3.845% | 76.72% | 0% | 49.77% | 0% | 42.26% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 36.47% | 2.246% | CZ 3C | 45.19% | 79.51% | 0% | 79.34% | 0% | 49.77% | 0% | 42.26% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.74% | 2.246% | CZ 3C | 0% | 0% | 3.845% | -168.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.663% | 2.246% | CZ 3C | 45.19% | 79.51% | 3.845% | 78.4% | 0% | 49.77% | 0% | 42.26% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.28% | 2.246%
CZ 4A | 45.1% | 79.21% | 3.609% | 60.58% | 0% | 37.98% | 0% | 27.56% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.31% | 19.19% | CZ 4A | 45.1% | 79.21% | 3.609% | 57.27% | 0% | 37.98% | 0% | 27.56% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.09% | 19.19% | CZ 4A | 45.1% | 79.21% | 0% | 63.17% | 0% | 37.98% | 0% | 27.56% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.43% | 19.19% | CZ 4A | 0% | 0% | 3.609% | 46.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.16% | 19.19% | CZ 4A | 45.1% | 79.21% | 3.609% | 60.45% | 0% | 37.98% | 0% | 27.56% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.3% | 19.19%
CZ 4B | 45.44% | 79.36% | 3.731% | 68.59% | 0% | 33.49% | 0% | 24.22% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 34.81% | 0.6394% | CZ 4B | 45.44% | 79.36% | 3.731% | 64.57% | 0% | 33.49% | 0% | 24.22% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 34.24% | 0.6394% | CZ 4B | 45.44% | 79.36% | 0% | 71.26% | 0% | 33.49% | 0% | 24.22% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 35.11% | 0.6394% | CZ 4B | 0% | 0% | 3.731% | 42.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.42% | 0.6394% | CZ 4B | 45.44% | 79.36% | 3.731% | 68.45% | 0% | 33.49% | 0% | 24.22% | 0% | 0% | 0% | 5.47% | 65.17% | 0% | 0% | 8.826% | 34.79% | 0.6394%
CZ 4C | 44.81% | 78.86% | 3.411% | 64.89% | 0% | 49.47% | 0% | 29.15% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 38.11% | 3.137% | CZ 4C | 44.81% | 78.86% | 3.411% | 61.75% | 0% | 49.47% | 0% | 29.15% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 37.36% | 3.137% | CZ 4C | 44.81% | 78.86% | 0% | 66.89% | 0% | 49.47% | 0% | 29.15% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 38.52% | 3.137% | CZ 4C | 0% | 0% | 3.411% | 41.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.5% | 3.137% | CZ 4C | 44.81% | 78.86% | 3.411% | 64.78% | 0% | 49.47% | 0% | 29.15% | 0% | 0% | 0% | 5.47% | 65.14% | 0% | 0% | 8.826% | 38.08% | 3.137%
CZ 5A | 45.18% | 79.05% | 3.333% | 55.87% | 0% | 35.66% | 0% | 28.3% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 37.66% | 16.56% | CZ 5A | 45.18% | 79.05% | 3.333% | 52.06% | 0% | 35.66% | 0% | 28.3% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 37.36% | 16.56% | CZ 5A | 45.18% | 79.05% | 0% | 59.2% | 0% | 35.66% | 0% | 28.3% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 37.85% | 16.56% | CZ 5A | 0% | 0% | 3.333% | 42.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.79% | 16.56% | CZ 5A | 45.18% | 79.05% | 3.333% | 55.72% | 0% | 35.66% | 0% | 28.3% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 37.65% | 16.56%
CZ 5B | 45.24% | 79.25% | 3.304% | 59.79% | 0% | 37.74% | 0% | 28.94% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 36.56% | 5.726% | CZ 5B | 45.24% | 79.25% | 3.304% | 54.55% | 0% | 37.74% | 0% | 28.94% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 35.84% | 5.726% | CZ 5B | 45.24% | 79.25% | 0% | 63.86% | 0% | 37.74% | 0% | 28.94% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 36.97% | 5.726% | CZ 5B | 0% | 0% | 3.304% | 36.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.87% | 5.726% | CZ 5B | 45.24% | 79.25% | 3.304% | 59.6% | 0% | 37.74% | 0% | 28.94% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 36.54% | 5.726%
CZ 5C | 44.74% | 78.81% | 3.314% | 63.95% | 0% | 57.62% | 0% | 24.7% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 37.86% | 0.1011% | CZ 5C | 44.74% | 78.81% | 3.314% | 60.46% | 0% | 57.62% | 0% | 24.7% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 37.27% | 0.1011% | CZ 5C | 44.74% | 78.81% | 0% | 66.43% | 0% | 57.62% | 0% | 24.7% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 38.18% | 0.1011% | CZ 5C | 0% | 0% | 3.314% | 45.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.26% | 0.1011% | CZ 5C | 44.74% | 78.81% | 3.314% | 63.83% | 0% | 57.62% | 0% | 24.7% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 37.84% | 0.1011%
CZ 6A | 45.15% | 79.03% | 3.128% | 53.82% | 0% | 34.36% | 0% | 29.85% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 38.6% | 3.488% | CZ 6A | 45.15% | 79.03% | 3.128% | 49.97% | 0% | 34.36% | 0% | 29.85% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 38.2% | 3.488% | CZ 6A | 45.15% | 79.03% | 0% | 57.32% | 0% | 34.36% | 0% | 29.85% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 38.85% | 3.488% | CZ 6A | 0% | 0% | 3.128% | 40.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.59% | 3.488% | CZ 6A | 45.15% | 79.03% | 3.128% | 53.66% | 0% | 34.36% | 0% | 29.85% | 0% | 0% | 0% | 5.47% | 65.13% | 0% | 0% | 8.826% | 38.58% | 3.488%
CZ 6B | 45.1% | 78.8% | 3.168% | 56.95% | 0% | 40.55% | 0% | 26.36% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 38.37% | 0.4679% | CZ 6B | 45.1% | 78.8% | 3.168% | 52.45% | 0% | 40.55% | 0% | 26.36% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 37.74% | 0.4679% | CZ 6B | 45.1% | 78.8% | 0% | 60.69% | 0% | 40.55% | 0% | 26.36% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 38.75% | 0.4679% | CZ 6B | 0% | 0% | 3.168% | 39.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.17% | 0.4679% | CZ 6B | 45.1% | 78.8% | 3.168% | 56.77% | 0% | 40.55% | 0% | 26.36% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 38.35% | 0.4679%
CZ 7 | 45.25% | 78.79% | 2.858% | 69.44% | 0% | 37.5% | 0% | 27.86% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 44.07% | 0.3712% | CZ 7 | 45.25% | 78.79% | 2.858% | 75.76% | 0% | 37.5% | 0% | 27.86% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 49.49% | 0.3712% | CZ 7 | 45.25% | 78.79% | 0% | 63.34% | 0% | 37.5% | 0% | 27.86% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 40.48% | 0.3712% | CZ 7 | 0% | 0% | 2.858% | 89.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.41% | 0.3712% | CZ 7 | 45.25% | 78.79% | 2.858% | 69.71% | 0% | 37.5% | 0% | 27.86% | 0% | 0% | 0% | 5.47% | 65.16% | 0% | 0% | 8.826% | 44.25% | 0.3712%
CZ 8 | 43.25% | 76.93% | 2.573% | 63.03% | 0% | 49.41% | 0% | 24.38% | 0% | 0% | 0% | 5.47% | 65.1% | 0% | 0% | 8.826% | 43.66% | 0.113% | CZ 8 | 43.25% | 76.93% | 2.573% | 70.27% | 0% | 49.41% | 0% | 24.38% | 0% | 0% | 0% | 5.47% | 65.1% | 0% | 0% | 8.826% | 50.25% | 0.113% | CZ 8 | 43.25% | 76.93% | 0% | 55.15% | 0% | 49.41% | 0% | 24.38% | 0% | 0% | 0% | 5.47% | 65.1% | 0% | 0% | 8.826% | 38.87% | 0.113% | CZ 8 | 0% | 0% | 2.573% | 83.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 76.68% | 0.113% | CZ 8 | 43.25% | 76.93% | 2.573% | 63.35% | 0% | 49.41% | 0% | 24.38% | 0% | 0% | 0% | 5.47% | 65.1% | 0% | 0% | 8.826% | 43.9% | 0.113%
US Weighted | 45.2% | 79.19% | 3.948% | 55.54% | 0% | 38.45% | 0% | 33.42% | 0% | 0% | 0% | 5.47% | 65.15% | 0% | 0% | 8.826% | 35.89% | 100% | US Weighted | 45.2% | 79.19% | 3.948% | 53.49% | 0% | 38.45% | 0% | 33.42% | 0% | 0% | 0% | 5.47% | 65.15% | 0% | 0% | 8.826% | 35.71% | 100% | US Weighted | 45.2% | 79.19% | 0% | 57.19% | 0% | 38.45% | 0% | 33.42% | 0% | 0% | 0% | 5.47% | 65.15% | 0% | 0% | 8.826% | 35.99% | 100% | US Weighted | 0% | 0% | 3.948% | 47.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.89% | 100% | US Weighted | 45.2% | 79.19% | 3.948% | 55.46% | 0% | 38.45% | 0% | 33.42% | 0% | 0% | 0% | 5.47% | 65.15% | 0% | 0% | 8.826% | 35.88% | 100%

## OffL
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Office |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Large Office | [14 empty] | Prototype Floor Area: | 498588 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.17877 | 0.019414 | 0.010437 | 0.031105 | 0.075709 | 0.22074 | 0.018842 | 0.13258 | 0.0014499 | 0.023974 | 0 | 0.10728 | 0.0031026 | 0 | 0.84214 | 0.30109 | 1.9666 |  | STD2016 | 6.0231 | 0.6541 | 1.0437 | 3.0832 | 2.5508 | 7.437 | 0.63482 | 4.4668 | 0.048848 | 0.80773 | 0 | 3.6145 | 0.10453 | 0 | 28.3732 | 10.1441 | 68.9865 |  | STD2016 | 1.7648 | 0.19165 | 0 | 0.0040651 | 0.74738 | 2.1791 | 0.186 | 1.3088 | 0.014313 | 0.23667 | 0 | 1.0591 | 0.030628 | 0 | 8.3133 | 2.9722 | 19.0079 |  | STD2016 | 0 | 0 | 0.010437 | 0.030693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04113 |  | STD2016 | 18.4754 | 2.0064 | 1.1408 | 3.3973 | 7.8243 | 22.8125 | 1.9473 | 13.7017 | 0.14984 | 2.4776 | 0 | 11.0872 | 0.32064 | 0 | 87.0323 | 31.1161 | 203.4894
STD2013 | 0.19252 | 0.019414 | 0.010437 | 0.031105 | 0.075709 | 0.22074 | 0.018842 | 0.13258 | 0.0014499 | 0.023974 | 0 | 0.10728 | 0.0031026 | 0 | 0.84214 | 0.30109 | 1.9666 |  | STD2013 | 6.4864 | 1.2963 | 1.0711 | 5.2498 | 1.2564 | 9.1945 | 0.68298 | 4.5027 | 0.049199 | 0.90413 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 72.9771 |  | STD2013 | 1.9005 | 0.37982 | 0 | 0.0042215 | 0.36813 | 2.694 | 0.20011 | 1.3193 | 0.014415 | 0.26491 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.5345 |  | STD2013 | 0 | 0 | 0.010711 | 0.052354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063065 |  | STD2013 | 19.8965 | 3.9763 | 1.1707 | 5.7665 | 3.854 | 28.2033 | 2.095 | 13.8117 | 0.15092 | 2.7734 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 211.3996
STD2010 | 0.21522 | 0.038475 | 0.01071 | 0.035305 | 0.037841 | 0.29212 | 0.025422 | 0.13843 | 0 | 0.032705 | 0 | 0.10751 | 0.004535 | 0 | 0.84214 | 0.30216 | 2.0826 |  | STD2010 | 7.2511 | 1.2963 | 1.071 | 3.4086 | 1.2749 | 9.8421 | 0.85651 | 4.6639 | 0 | 1.1019 | 0 | 3.6222 | 0.15279 | 0 | 28.3732 | 10.1802 | 73.0946 |  | STD2010 | 2.1246 | 0.37982 | 0 | 0.018156 | 0.37355 | 2.8837 | 0.25096 | 1.3665 | 0 | 0.32285 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9828 | 20.1224 |  | STD2010 | 0 | 0 | 0.01071 | 0.033466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044176 |  | STD2010 | 22.242 | 3.9763 | 1.1706 | 3.8479 | 3.9107 | 30.1899 | 2.6273 | 14.3061 | 0 | 3.3799 | 0 | 11.1107 | 0.46868 | 0 | 87.0323 | 31.227 | 215.4894
STD2007 | 0.29004 | 0.055673 | 0.010785 | 0.069173 | 0.0063533 | 0.37604 | 0.047071 | 0.14764 | 0 | 0.05818 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.353 |  | STD2007 | 9.772 | 1.8757 | 1.0785 | 6.5616 | 0.21405 | 12.6695 | 1.5859 | 4.9744 | 0 | 1.9602 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 84.2235 |  | STD2007 | 2.8632 | 0.54958 | 0 | 0.052955 | 0.062718 | 3.7122 | 0.46467 | 1.4575 | 0 | 0.57433 | 0 | 1.0899 | 0.08012 | 0 | 8.3133 | 3.2714 | 22.4919 |  | STD2007 | 0 | 0 | 0.010785 | 0.063809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074594 |  | STD2007 | 29.9749 | 5.7536 | 1.1788 | 7.5287 | 0.65659 | 38.8626 | 4.8646 | 15.2585 | 0 | 6.0127 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 243.6207
STD2004 | 0.29004 | 0.055673 | 0.010786 | 0.091268 | 0.0065171 | 0.38285 | 0.049194 | 0.15071 | 0 | 0.060583 | 0 | 0.11041 | 0.0081161 | 0 | 0.84214 | 0.33139 | 2.3897 |  | STD2004 | 9.772 | 1.8757 | 1.0786 | 8.7746 | 0.21957 | 12.8987 | 1.6574 | 5.0778 | 0 | 2.0411 | 0 | 3.7199 | 0.27344 | 0 | 28.3732 | 11.1651 | 86.9272 |  | STD2004 | 2.8632 | 0.54958 | 0 | 0.052428 | 0.064335 | 3.7793 | 0.48563 | 1.4878 | 0 | 0.59805 | 0 | 1.0899 | 0.080119 | 0 | 8.3133 | 3.2714 | 22.6351 |  | STD2004 | 0 | 0 | 0.010786 | 0.085957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096743 |  | STD2004 | 29.9749 | 5.7536 | 1.1789 | 9.9439 | 0.67352 | 39.5658 | 5.0841 | 15.5756 | 0 | 6.261 | 0 | 11.4106 | 0.83877 | 0 | 87.0323 | 34.2481 | 247.5411
Savings between versions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 5.5736e-07 | 0.022095 | 0.00016381 | 0.006804 | 0.0021236 | 0.0030685 | 0 | 0.0024031 | 0 | 0 | -8.6572e-08 | 0 | 0 | 0 | 0.036658 |  | 2004-2007 | 0 | 0 | 5.5736e-05 | 2.213 | 0.005519 | 0.22924 | 0.071548 | 0.10338 | 0 | 0.080966 | 0 | 0 | -2.9168e-06 | 0 | 0 | 0 | 2.7037 |  | 2004-2007 | 0 | 0 | 0 | -0.00052753 | 0.0016171 | 0.067167 | 0.020963 | 0.030291 | 0 | 0.023723 | 0 | 0 | -8.5461e-07 | 0 | 0 | 0 | 0.14323 |  | 2004-2007 | 0 | 0 | 5.5736e-07 | 0.022148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022149 |  | 2004-2007 | 0 | 0 | 6.0919e-05 | 2.4153 | 0.016929 | 0.70317 | 0.21947 | 0.31711 | 0 | 0.24836 | 0 | 0 | -8.9469e-06 | 0 | 0 | 0 | 3.9203
2007-2010 | 0.074825 | 0.017197 | 7.5158e-05 | 0.033868 | -0.031487 | 0.083918 | 0.021649 | 0.009216 | 0 | 0.025475 | 0 | 0.002902 | 0.0035811 | 0 | 0 | 0.029233 | 0.27045 |  | 2007-2010 | 2.521 | 0.57941 | 0.0075158 | 3.153 | -1.0609 | 2.8274 | 0.72939 | 0.3105 | 0 | 0.8583 | 0 | 0.097773 | 0.12065 | 0 | 0 | 0.9849 | 11.1289 |  | 2007-2010 | 0.73864 | 0.16977 | 0 | 0.034799 | -0.31083 | 0.82841 | 0.21371 | 0.090978 | 0 | 0.25148 | 0 | 0.028648 | 0.035352 | 0 | 0 | 0.28858 | 2.3695 |  | 2007-2010 | 0 | 0 | 7.5158e-05 | 0.030343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030418 |  | 2007-2010 | 7.7329 | 1.7773 | 0.0082147 | 3.6808 | -3.2541 | 8.6727 | 2.2373 | 0.95244 | 0 | 2.6328 | 0 | 0.29991 | 0.3701 | 0 | 0 | 3.0211 | 28.1313
2010-2013 | 0.022695 | 0.019061 | 0.00027306 | 0.0042003 | -0.037869 | 0.071385 | 0.0065798 | 0.0058483 | -0.0014499 | 0.0087305 | 0 | 0.00022688 | 0.0014324 | 0 | 0 | 0.0010729 | 0.11594 |  | 2010-2013 | 0.76464 | 0 | -6.9022e-05 | -1.8413 | 0.018492 | 0.64767 | 0.17353 | 0.16118 | -0.049199 | 0.19774 | 0 | 0.0076439 | 0.00097987 | 0 | 0 | 0.036147 | 0.11748 |  | 2010-2013 | 0.22404 | 0 | 0 | 0.013934 | 0.005418 | 0.18977 | 0.050845 | 0.047225 | -0.014415 | 0.057939 | 0 | 0.0022397 | 0.0002871 | 0 | 0 | 0.010591 | 0.58787 |  | 2010-2013 | 0 | 0 | -6.9022e-07 | -0.018888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.018889 |  | 2010-2013 | 2.3455 | 0 | -7.5441e-05 | -1.9186 | 0.056721 | 1.9867 | 0.53229 | 0.4944 | -0.15092 | 0.60656 | 0 | 0.023447 | 0.0030057 | 0 | 0 | 0.11088 | 4.0898
2013-2016 | 0.013751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2013-2016 | 0.46331 | 0.64221 | 0.027375 | 2.1667 | -1.2944 | 1.7574 | 0.048154 | 0.035863 | 0.0003512 | 0.096404 | 0 | 0 | 0.047281 | 0 | 0 | 0 | 3.9907 |  | 2013-2016 | 0.13575 | 0.18817 | 0 | 0.00015639 | -0.37924 | 0.51492 | 0.014109 | 0.010508 | 0.0001029 | 0.028246 | 0 | 0 | 0.013853 | 0 | 0 | 0 | 0.52657 |  | 2013-2016 | 0 | 0 | 0.00027375 | 0.021661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021935 |  | 2013-2016 | 1.4212 | 1.9699 | 0.029921 | 2.3692 | -3.9703 | 5.3907 | 0.14771 | 0.11001 | 0.0010773 | 0.29571 | 0 | 0 | 0.14503 | 0 | 0 | 0 | 7.9102
2004-2016 | 0.11127 | 0.036259 | 0.00034878 | 0.060163 | -0.069192 | 0.16211 | 0.030352 | 0.018133 | -0.0014499 | 0.036609 | 0 | 0.0031289 | 0.0050135 | 0 | 0 | 0.030306 | 0.42305 |  | 2004-2016 | 3.7489 | 1.2216 | 0.034878 | 5.6914 | -2.3312 | 5.4617 | 1.0226 | 0.61093 | -0.048848 | 1.2334 | 0 | 0.10542 | 0.16891 | 0 | 0 | 1.021 | 17.9408 |  | 2004-2016 | 1.0984 | 0.35793 | 0 | 0.048363 | -0.68304 | 1.6003 | 0.29963 | 0.179 | -0.014313 | 0.36139 | 0 | 0.030887 | 0.049491 | 0 | 0 | 0.29917 | 3.6272 |  | 2004-2016 | 0 | 0 | 0.00034878 | 0.055264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055612 |  | 2004-2016 | 11.4995 | 3.7472 | 0.038121 | 6.5466 | -7.1508 | 16.7533 | 3.1368 | 1.874 | -0.14984 | 3.7834 | 0 | 0.32336 | 0.51812 | 0 | 0 | 3.132 | 44.0517
Percentage savings between versions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.005167% | 24.21% | 2.514% | 1.777% | 4.317% | 2.036% |  | 3.967% |  | 0% | -0.001067% |  | 0% | 0% | 1.534% |  | 2004-2007 | 0% | 0% | 0.005167% | 25.22% | 2.514% | 1.777% | 4.317% | 2.036% |  | 3.967% |  | 0% | -0.001067% |  | 0% | 0% | 3.11% |  | 2004-2007 | 0% | 0% |  | -1.006% | 2.514% | 1.777% | 4.317% | 2.036% |  | 3.967% |  | 0% | -0.001067% |  | 0% | 0% | 0.6328% |  | 2004-2007 |  |  | 0.005167% | 25.77% | [12 empty] | 22.89% |  | 2004-2007 | 0% | 0% | 0.005167% | 24.29% | 2.514% | 1.777% | 4.317% | 2.036% |  | 3.967% |  | 0% | -0.001067% |  | 0% | 0% | 1.584%
2007-2010 | 25.8% | 30.89% | 0.6968% | 48.96% | -495.6% | 22.32% | 45.99% | 6.242% |  | 43.79% |  | 2.628% | 44.12% |  | 0% | 8.821% | 11.49% |  | 2007-2010 | 25.8% | 30.89% | 0.6968% | 48.05% | -495.6% | 22.32% | 45.99% | 6.242% |  | 43.79% |  | 2.628% | 44.12% |  | 0% | 8.821% | 13.21% |  | 2007-2010 | 25.8% | 30.89% |  | 65.71% | -495.6% | 22.32% | 45.99% | 6.242% |  | 43.79% |  | 2.628% | 44.12% |  | 0% | 8.821% | 10.54% |  | 2007-2010 |  |  | 0.6968% | 47.55% | [12 empty] | 40.78% |  | 2007-2010 | 25.8% | 30.89% | 0.6968% | 48.89% | -495.6% | 22.32% | 45.99% | 6.242% |  | 43.79% |  | 2.628% | 44.12% |  | 0% | 8.821% | 11.55%
2010-2013 | 10.55% | 49.54% | 2.55% | 11.9% | -100.1% | 24.44% | 25.88% | 4.225% |  | 26.69% |  | 0.211% | 31.59% |  | 0% | 0.3551% | 5.567% |  | 2010-2013 | 10.55% | 0% | -0.006445% | -54.02% | 1.45% | 6.581% | 20.26% | 3.456% |  | 17.95% |  | 0.211% | 0.6413% |  | 0% | 0.3551% | 0.1607% |  | 2010-2013 | 10.55% | 0% |  | 76.75% | 1.45% | 6.581% | 20.26% | 3.456% |  | 17.95% |  | 0.211% | 0.6413% |  | 0% | 0.3551% | 2.921% |  | 2010-2013 |  |  | -0.006445% | -56.44% | [12 empty] | -42.76% |  | 2010-2013 | 10.55% | 0% | -0.006445% | -49.86% | 1.45% | 6.581% | 20.26% | 3.456% |  | 17.95% |  | 0.211% | 0.6413% |  | 0% | 0.3551% | 1.898%
2013-2016 | 7.143% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | 0% |  | 0% | 0% |  | 0% | 0% | 0% |  | 2013-2016 | 7.143% | 49.54% | 2.556% | 41.27% | -103% | 19.11% | 7.051% | 0.7965% | 0.7138% | 10.66% |  | 0% | 31.14% |  | 0% | 0% | 5.468% |  | 2013-2016 | 7.143% | 49.54% |  | 3.705% | -103% | 19.11% | 7.051% | 0.7965% | 0.7138% | 10.66% |  | 0% | 31.14% |  | 0% | 0% | 2.696% |  | 2013-2016 |  |  | 2.556% | 41.37% | [12 empty] | 34.78% |  | 2013-2016 | 7.143% | 49.54% | 2.556% | 41.09% | -103% | 19.11% | 7.051% | 0.7965% | 0.7138% | 10.66% |  | 0% | 31.14% |  | 0% | 0% | 3.742%
2004-2016 | 38.36% | 65.13% | 3.234% | 65.92% | -1062% | 42.34% | 61.7% | 12.03% |  | 60.43% |  | 2.834% | 61.77% |  | 0% | 9.145% | 17.7% |  | 2004-2016 | 38.36% | 65.13% | 3.234% | 64.86% | -1062% | 42.34% | 61.7% | 12.03% |  | 60.43% |  | 2.834% | 61.77% |  | 0% | 9.145% | 20.64% |  | 2004-2016 | 38.36% | 65.13% |  | 92.25% | -1062% | 42.34% | 61.7% | 12.03% |  | 60.43% |  | 2.834% | 61.77% |  | 0% | 9.145% | 16.02% |  | 2004-2016 |  |  | 3.234% | 64.29% | [12 empty] | 57.48% |  | 2004-2016 | 38.36% | 65.13% | 3.234% | 65.84% | -1062% | 42.34% | 61.7% | 12.03% |  | 60.43% |  | 2.834% | 61.77% |  | 0% | 9.145% | 17.8%
Humidification increases were less than increased savings through increased outside air economizer requirements.
They could have been avoided through a lockout control, reduced humidification setpoints, or water economizer; however, that is not currently required.
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.17844 | 0.019321 | 0.0081443 | 0 | 0 | 0.44619 | 0.047707 | 0.13873 | 0.0065179 | 0.041986 | 0 | 0.10728 | 0.0031018 | 0 | 0.84214 | 0.30109 | 2.1406 | 3.896% | CZ 1A | 6.0118 | 0.65097 | 0.81443 | 0 | 0 | 15.0329 | 1.6073 | 4.674 | 0.2196 | 1.4146 | 0 | 3.6145 | 0.1045 | 0 | 28.3732 | 10.1441 | 72.6618 | 3.896% | CZ 1A | 1.7615 | 0.19073 | 0 | 0 | 0 | 4.4046 | 0.47095 | 1.3695 | 0.064343 | 0.41447 | 0 | 1.0591 | 0.03062 | 0 | 8.3133 | 2.9722 | 21.0513 | 3.896% | CZ 1A | 0 | 0 | 0.0081443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081443 | 3.896% | CZ 1A | 18.4406 | 1.9968 | 0.89017 | 0 | 0 | 46.1122 | 4.9304 | 14.337 | 0.6736 | 4.3391 | 0 | 11.0872 | 0.32056 | 0 | 87.0323 | 31.1161 | 221.2762 | 3.896%
CZ 1B | 0.17849 | 0.019274 | 0.0081787 | 0.0017148 | 0.00087083 | 0.5234 | 0.043084 | 0.14168 | 0 | 0.045738 | 0 | 0.10728 | 0.0031035 | 0 | 0.84214 | 0.30109 | 2.216 | 0% | CZ 1B | 6.0136 | 0.64937 | 0.81787 | 0.16459 | 0.02934 | 17.6342 | 1.4516 | 4.7733 | 0 | 1.541 | 0 | 3.6145 | 0.10456 | 0 | 28.3732 | 10.1441 | 75.3111 | 0% | CZ 1B | 1.762 | 0.19027 | 0 | 0.0010251 | 0.0085965 | 5.1668 | 0.42531 | 1.3986 | 0 | 0.45151 | 0 | 1.0591 | 0.030637 | 0 | 8.3133 | 2.9722 | 21.7793 | 0% | CZ 1B | 0 | 0 | 0.0081787 | 0.0016109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097896 | 0% | CZ 1B | 18.4464 | 1.9919 | 0.89393 | 0.1868 | 0.089997 | 54.0914 | 4.4526 | 14.6416 | 0 | 4.7268 | 0 | 11.0872 | 0.32073 | 0 | 87.0323 | 31.1161 | 229.0778 | 0%
CZ 2A | 0.17835 | 0.019314 | 0.0088235 | 0.002827 | 0.023706 | 0.35132 | 0.040061 | 0.12982 | 0.0034647 | 0.036851 | 0 | 0.10728 | 0.0031024 | 0 | 0.84214 | 0.30109 | 2.0482 | 11.87% | CZ 2A | 6.009 | 0.65074 | 0.88235 | 0.27682 | 0.79869 | 11.8364 | 1.3497 | 4.374 | 0.11673 | 1.2416 | 0 | 3.6145 | 0.10452 | 0 | 28.3732 | 10.1441 | 69.7724 | 11.87% | CZ 2A | 1.7606 | 0.19067 | 0 | 0.00087469 | 0.23402 | 3.4681 | 0.39547 | 1.2816 | 0.034202 | 0.36378 | 0 | 1.0591 | 0.030625 | 0 | 8.3133 | 2.9722 | 20.1045 | 11.87% | CZ 2A | 0 | 0 | 0.0088235 | 0.0027384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011562 | 11.87% | CZ 2A | 18.4322 | 1.9961 | 0.96441 | 0.30846 | 2.4499 | 36.3073 | 4.1401 | 13.4169 | 0.35806 | 3.8084 | 0 | 11.0872 | 0.32062 | 0 | 87.0323 | 31.1161 | 211.7382 | 11.87%
CZ 2B | 0.17844 | 0.01932 | 0.0088655 | 0.0053467 | 0.099795 | 0.32253 | 0.016916 | 0.14574 | 0 | 0.030152 | 0 | 0.10728 | 0.0031029 | 0 | 0.84214 | 0.30109 | 2.0807 | 1.826% | CZ 2B | 6.0121 | 0.65093 | 0.88655 | 0.32567 | 3.3623 | 10.8664 | 0.56994 | 4.9101 | 0 | 1.0159 | 0 | 3.6145 | 0.10454 | 0 | 28.3732 | 10.1441 | 70.8361 | 1.826% | CZ 2B | 1.7615 | 0.19072 | 0 | 0.031116 | 0.98514 | 3.1839 | 0.16699 | 1.4387 | 0 | 0.29765 | 0 | 1.0591 | 0.030631 | 0 | 8.3133 | 2.9722 | 20.4309 | 1.826% | CZ 2B | 0 | 0 | 0.0088655 | 0.0021947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01106 | 1.826% | CZ 2B | 18.4416 | 1.9967 | 0.969 | 0.56563 | 10.3135 | 33.3319 | 1.7483 | 15.0613 | 0 | 3.1161 | 0 | 11.0872 | 0.32068 | 0 | 87.0323 | 31.1161 | 215.1002 | 1.826%
CZ 3A | 0.17883 | 0.019513 | 0.009993 | 0.019042 | 0.063316 | 0.24182 | 0.02194 | 0.12922 | 0.0020075 | 0.026676 | 0 | 0.10728 | 0.0031035 | 0 | 0.84214 | 0.30109 | 1.966 | 14.76% | CZ 3A | 6.0251 | 0.65743 | 0.9993 | 1.8941 | 2.1332 | 8.1474 | 0.73919 | 4.3535 | 0.067635 | 0.89875 | 0 | 3.6145 | 0.10456 | 0 | 28.3732 | 10.1441 | 68.152 | 14.76% | CZ 3A | 1.7654 | 0.19263 | 0 | 0.0014931 | 0.62504 | 2.3872 | 0.21658 | 1.2756 | 0.019817 | 0.26333 | 0 | 1.0591 | 0.030637 | 0 | 8.3133 | 2.9722 | 19.1223 | 14.76% | CZ 3A | 0 | 0 | 0.009993 | 0.01889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028883 | 14.76% | CZ 3A | 18.4815 | 2.0166 | 1.0922 | 2.0804 | 6.5435 | 24.9916 | 2.2674 | 13.3539 | 0.20746 | 2.7568 | 0 | 11.0872 | 0.32073 | 0 | 87.0323 | 31.1161 | 203.3478 | 14.76%
CZ 3B | 0.17853 | 0.019183 | 0.0096904 | 0.0082382 | 0.10195 | 0.27764 | 0.014461 | 0.14685 | 0 | 0.025012 | 0 | 0.10728 | 0.0031012 | 0 | 0.84214 | 0.30109 | 2.0352 | 8.555% | CZ 3B | 6.0151 | 0.64631 | 0.96904 | 0.73397 | 3.435 | 9.3541 | 0.48723 | 4.9476 | 0 | 0.84271 | 0 | 3.6145 | 0.10449 | 0 | 28.3732 | 10.1441 | 69.6674 | 8.555% | CZ 3B | 1.7624 | 0.18937 | 0 | 0.013377 | 1.0065 | 2.7408 | 0.14276 | 1.4497 | 0 | 0.24691 | 0 | 1.0591 | 0.030614 | 0 | 8.3133 | 2.9722 | 19.9269 | 8.555% | CZ 3B | 0 | 0 | 0.0096904 | 0.0068832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016574 | 8.555% | CZ 3B | 18.4509 | 1.9825 | 1.0592 | 0.89237 | 10.5366 | 28.6929 | 1.4945 | 15.1764 | 0 | 2.5849 | 0 | 11.0872 | 0.3205 | 0 | 87.0323 | 31.1161 | 210.4266 | 8.555%
CZ 3C | 0.17876 | 0.019185 | 0.010122 | 0.0011849 | 0.031981 | 0.16912 | 0.012174 | 0.12511 | 0 | 0.019752 | 0 | 0.10728 | 0.0031024 | 0 | 0.84214 | 0.30109 | 1.821 | 3.506% | CZ 3C | 6.0228 | 0.64636 | 1.0122 | 0.099254 | 1.0775 | 5.6978 | 0.41016 | 4.2153 | 0 | 0.66549 | 0 | 3.6145 | 0.10452 | 0 | 28.3732 | 10.1441 | 62.083 | 3.506% | CZ 3C | 1.7647 | 0.18938 | 0 | 0.0028636 | 0.3157 | 1.6694 | 0.12018 | 1.2351 | 0 | 0.19499 | 0 | 1.0591 | 0.030625 | 0 | 8.3133 | 2.9722 | 17.8675 | 3.506% | CZ 3C | 0 | 0 | 0.010122 | 0.0008948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011017 | 3.506% | CZ 3C | 18.4743 | 1.9827 | 1.1063 | 0.12778 | 3.3051 | 17.4774 | 1.2581 | 12.93 | 0 | 2.0413 | 0 | 11.0872 | 0.32062 | 0 | 87.0323 | 31.1161 | 188.2594 | 3.506%
CZ 4A | 0.17894 | 0.019427 | 0.010927 | 0.03975 | 0.08561 | 0.18541 | 0.015916 | 0.1295 | 0.0013534 | 0.021477 | 0 | 0.10728 | 0.0031029 | 0 | 0.84214 | 0.30109 | 1.9419 | 31.46% | CZ 4A | 6.0287 | 0.65454 | 1.0927 | 3.9593 | 2.8843 | 6.2466 | 0.53625 | 4.363 | 0.045597 | 0.72358 | 0 | 3.6145 | 0.10454 | 0 | 28.3732 | 10.1441 | 68.7709 | 31.46% | CZ 4A | 1.7664 | 0.19178 | 0 | 0.0023399 | 0.84511 | 1.8303 | 0.15712 | 1.2784 | 0.01336 | 0.21201 | 0 | 1.0591 | 0.030631 | 0 | 8.3133 | 2.9722 | 18.672 | 31.46% | CZ 4A | 0 | 0 | 0.010927 | 0.039513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05044 | 31.46% | CZ 4A | 18.4924 | 2.0077 | 1.1943 | 4.3433 | 8.8475 | 19.161 | 1.6449 | 13.3832 | 0.13987 | 2.2195 | 0 | 11.0872 | 0.32068 | 0 | 87.0323 | 31.1161 | 200.9901 | 31.46%
CZ 4B | 0.1783 | 0.019251 | 0.010659 | 0.015009 | 0.12717 | 0.19935 | 0.0091005 | 0.16821 | 0 | 0.017867 | 0 | 0.10728 | 0.0031029 | 0 | 0.84214 | 0.30109 | 1.9985 | 0.05451% | CZ 4B | 6.0072 | 0.64861 | 1.0659 | 1.365 | 4.2847 | 6.7163 | 0.30661 | 5.6672 | 0 | 0.60198 | 0 | 3.6145 | 0.10454 | 0 | 28.3732 | 10.1441 | 68.8997 | 0.05451% | CZ 4B | 1.7601 | 0.19004 | 0 | 0.02024 | 1.2554 | 1.9679 | 0.089837 | 1.6605 | 0 | 0.17638 | 0 | 1.0591 | 0.030631 | 0 | 8.3133 | 2.9722 | 19.4956 | 0.05451% | CZ 4B | 0 | 0 | 0.010659 | 0.012959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023618 | 0.05451% | CZ 4B | 18.4266 | 1.9896 | 1.165 | 1.6283 | 13.1428 | 20.6017 | 0.9405 | 17.3837 | 0 | 1.8465 | 0 | 11.0872 | 0.32068 | 0 | 87.0323 | 31.1161 | 206.6811 | 0.05451%
CZ 4C | 0.17945 | 0.019698 | 0.011207 | 0.02075 | 0.079565 | 0.09034 | 0.0051409 | 0.12745 | 0 | 0.012325 | 0 | 0.10728 | 0.0031035 | 0 | 0.84214 | 0.30109 | 1.7995 | 4.546% | CZ 4C | 6.046 | 0.66365 | 1.1207 | 2.0469 | 2.6807 | 3.0437 | 0.1732 | 4.2939 | 0 | 0.41526 | 0 | 3.6145 | 0.10456 | 0 | 28.3732 | 10.1441 | 62.7203 | 4.546% | CZ 4C | 1.7715 | 0.19445 | 0 | 0.004184 | 0.78543 | 0.89181 | 0.050749 | 1.2581 | 0 | 0.12167 | 0 | 1.0591 | 0.030637 | 0 | 8.3133 | 2.9722 | 17.4531 | 4.546% | CZ 4C | 0 | 0 | 0.011207 | 0.020326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031533 | 4.546% | CZ 4C | 18.5457 | 2.0357 | 1.2249 | 2.2655 | 8.2227 | 9.3363 | 0.53129 | 13.1712 | 0 | 1.2738 | 0 | 11.0872 | 0.32073 | 0 | 87.0323 | 31.1161 | 186.1635 | 4.546%
CZ 5A | 0.17876 | 0.019492 | 0.011722 | 0.071189 | 0.10064 | 0.13885 | 0.0096936 | 0.12809 | 0.00036853 | 0.017062 | 0 | 0.10728 | 0.0031018 | 0 | 0.84214 | 0.30109 | 1.9295 | 13.22% | CZ 5A | 6.0229 | 0.65673 | 1.1722 | 7.1071 | 3.3909 | 4.6782 | 0.3266 | 4.3155 | 0.012417 | 0.57483 | 0 | 3.6145 | 0.1045 | 0 | 28.3732 | 10.1441 | 70.4936 | 13.22% | CZ 5A | 1.7647 | 0.19242 | 0 | 0.001755 | 0.99352 | 1.3707 | 0.095692 | 1.2645 | 0.0036381 | 0.16843 | 0 | 1.0591 | 0.03062 | 0 | 8.3133 | 2.9722 | 18.2305 | 13.22% | CZ 5A | 0 | 0 | 0.011722 | 0.071011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082733 | 13.22% | CZ 5A | 18.4747 | 2.0145 | 1.2813 | 7.7799 | 10.4012 | 14.3499 | 1.0018 | 13.2376 | 0.038087 | 1.7632 | 0 | 11.0872 | 0.32056 | 0 | 87.0323 | 31.1161 | 199.8983 | 13.22%
CZ 5B | 0.17868 | 0.019381 | 0.011496 | 0.03712 | 0.14187 | 0.15844 | 0.0060597 | 0.16476 | 0 | 0.016203 | 0 | 0.10728 | 0.0031035 | 0 | 0.84214 | 0.30109 | 1.9876 | 3.582% | CZ 5B | 6.0201 | 0.65298 | 1.1496 | 3.5776 | 4.7798 | 5.3382 | 0.20416 | 5.551 | 0 | 0.54589 | 0 | 3.6145 | 0.10456 | 0 | 28.3732 | 10.1441 | 70.0555 | 3.582% | CZ 5B | 1.7639 | 0.19132 | 0 | 0.020012 | 1.4005 | 1.5641 | 0.059819 | 1.6264 | 0 | 0.15995 | 0 | 1.0591 | 0.030637 | 0 | 8.3133 | 2.9722 | 19.1612 | 3.582% | CZ 5B | 0 | 0 | 0.011496 | 0.035093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046589 | 3.582% | CZ 5B | 18.4662 | 2.003 | 1.2565 | 4.0452 | 14.6616 | 16.3744 | 0.62624 | 17.0271 | 0 | 1.6745 | 0 | 11.0872 | 0.32073 | 0 | 87.0323 | 31.1161 | 205.691 | 3.582%
CZ 5C | 0.17963 | 0.01972 | 0.011656 | 0.022201 | 0.089323 | 0.066301 | 0.0029618 | 0.12843 | 0 | 0.010024 | 0 | 0.10728 | 0.003104 | 0 | 0.84214 | 0.30109 | 1.7839 | 0.07377% | CZ 5C | 6.0519 | 0.66439 | 1.1656 | 2.1789 | 3.0094 | 2.2338 | 0.099789 | 4.327 | 0 | 0.33772 | 0 | 3.6145 | 0.10458 | 0 | 28.3732 | 10.1441 | 62.3048 | 0.07377% | CZ 5C | 1.7732 | 0.19467 | 0 | 0.006134 | 0.88177 | 0.6545 | 0.029238 | 1.2678 | 0 | 0.098952 | 0 | 1.0591 | 0.030642 | 0 | 8.3133 | 2.9722 | 17.2815 | 0.07377% | CZ 5C | 0 | 0 | 0.011656 | 0.02158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033236 | 0.07377% | CZ 5C | 18.5637 | 2.038 | 1.274 | 2.4229 | 9.2312 | 6.8519 | 0.30609 | 13.2726 | 0 | 1.0359 | 0 | 11.0872 | 0.32079 | 0 | 87.0323 | 31.1161 | 184.5527 | 0.07377%
CZ 6A | 0.17884 | 0.019542 | 0.012316 | 0.10816 | 0.10434 | 0.14464 | 0.010575 | 0.13253 | 0.00047238 | 0.018097 | 0 | 0.10728 | 0.0031024 | 0 | 0.84214 | 0.30109 | 1.9831 | 2.328% | CZ 6A | 6.0254 | 0.6584 | 1.2316 | 10.8077 | 3.5155 | 4.8731 | 0.3563 | 4.4652 | 0.015915 | 0.60972 | 0 | 3.6145 | 0.10452 | 0 | 28.3732 | 10.1441 | 74.7952 | 2.328% | CZ 6A | 1.7654 | 0.19291 | 0 | 0.0012981 | 1.03 | 1.4278 | 0.10439 | 1.3083 | 0.0046632 | 0.17865 | 0 | 1.0591 | 0.030625 | 0 | 8.3133 | 2.9722 | 18.3888 | 2.328% | CZ 6A | 0 | 0 | 0.012316 | 0.10803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12035 | 2.328% | CZ 6A | 18.4825 | 2.0196 | 1.3461 | 11.8215 | 10.7836 | 14.9479 | 1.0929 | 13.6967 | 0.048819 | 1.8703 | 0 | 11.0872 | 0.32062 | 0 | 87.0323 | 31.1161 | 205.6662 | 2.328%
CZ 6B | 0.17892 | 0.019695 | 0.012164 | 0.069875 | 0.15131 | 0.1136 | 0.0044264 | 0.15701 | 0 | 0.013814 | 0 | 0.10728 | 0.0031029 | 0 | 0.84214 | 0.30109 | 1.9744 | 0% | CZ 6B | 6.0281 | 0.66357 | 1.2164 | 6.8865 | 5.0978 | 3.8275 | 0.14913 | 5.2901 | 0 | 0.4654 | 0 | 3.6145 | 0.10454 | 0 | 28.3732 | 10.1441 | 71.8607 | 0% | CZ 6B | 1.7662 | 0.19443 | 0 | 0.015031 | 1.4937 | 1.1214 | 0.043696 | 1.55 | 0 | 0.13636 | 0 | 1.0591 | 0.030631 | 0 | 8.3133 | 2.9722 | 18.6961 | 0% | CZ 6B | 0 | 0 | 0.012164 | 0.068352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080516 | 0% | CZ 6B | 18.4906 | 2.0355 | 1.3295 | 7.6282 | 15.6372 | 11.7404 | 0.45745 | 16.2269 | 0 | 1.4276 | 0 | 11.0872 | 0.32068 | 0 | 87.0323 | 31.1161 | 204.5298 | 0%
CZ 7 | 0.17869 | 0.019759 | 0.013021 | 0.11772 | 0.11836 | 0.12436 | 0.0075716 | 0.1367 | 0.00090243 | 0.016471 | 0 | 0.10728 | 0.0031024 | 0 | 0.84214 | 0.30109 | 1.9872 | 0.3244% | CZ 7 | 6.0202 | 0.66572 | 1.3021 | 11.7572 | 3.9877 | 4.1897 | 0.2551 | 4.6055 | 0.030404 | 0.55494 | 0 | 3.6145 | 0.10452 | 0 | 28.3732 | 10.1441 | 75.605 | 0.3244% | CZ 7 | 1.7639 | 0.19506 | 0 | 0.0021672 | 1.1684 | 1.2276 | 0.074744 | 1.3494 | 0.0089085 | 0.1626 | 0 | 1.0591 | 0.030625 | 0 | 8.3133 | 2.9722 | 18.3281 | 0.3244% | CZ 7 | 0 | 0 | 0.013021 | 0.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13052 | 0.3244% | CZ 7 | 18.4666 | 2.042 | 1.4232 | 12.8652 | 12.232 | 12.8517 | 0.7825 | 14.127 | 0.093263 | 1.7022 | 0 | 11.0872 | 0.32062 | 0 | 87.0323 | 31.1161 | 206.1421 | 0.3244%
CZ 8 | 0.18263 | 0.021276 | 0.013971 | 0.17318 | 0.14273 | 0.082409 | 0.0028997 | 0.13564 | 0.00067499 | 0.012212 | 0 | 0.10728 | 0.0031046 | 0 | 0.84214 | 0.30109 | 2.0212 | 0% | CZ 8 | 6.1531 | 0.71681 | 1.3971 | 17.3051 | 4.8089 | 2.7765 | 0.097697 | 4.5701 | 0.022742 | 0.41144 | 0 | 3.6145 | 0.1046 | 0 | 28.3732 | 10.1441 | 80.4959 | 0% | CZ 8 | 1.8029 | 0.21003 | 0 | 0.001989 | 1.409 | 0.81351 | 0.028625 | 1.339 | 0.0066633 | 0.12055 | 0 | 1.0591 | 0.030648 | 0 | 8.3133 | 2.9722 | 18.1075 | 0% | CZ 8 | 0 | 0 | 0.013971 | 0.17298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18695 | 0% | CZ 8 | 18.8741 | 2.1988 | 1.527 | 18.9279 | 14.751 | 8.5167 | 0.29968 | 14.0184 | 0.069758 | 1.2621 | 0 | 11.0872 | 0.32085 | 0 | 87.0323 | 31.1161 | 210.0019 | 0%
US Weighted | 0.17877 | 0.019414 | 0.010437 | 0.031105 | 0.075709 | 0.22074 | 0.018842 | 0.13258 | 0.0014499 | 0.023974 | 0 | 0.10728 | 0.0031026 | 0 | 0.84214 | 0.30109 | 1.9666 | 100% | US Weighted | 6.0231 | 0.6541 | 1.0437 | 3.0832 | 2.5508 | 7.437 | 0.63482 | 4.4668 | 0.048848 | 0.80773 | 0 | 3.6145 | 0.10453 | 0 | 28.3732 | 10.1441 | 68.9865 | 100% | US Weighted | 1.7648 | 0.19165 | 0 | 0.0040651 | 0.74738 | 2.1791 | 0.186 | 1.3088 | 0.014313 | 0.23667 | 0 | 1.0591 | 0.030628 | 0 | 8.3133 | 2.9722 | 19.0079 | 100% | US Weighted | 0 | 0 | 0.010437 | 0.030693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04113 | 100% | US Weighted | 18.4754 | 2.0064 | 1.1408 | 3.3973 | 7.8243 | 22.8125 | 1.9473 | 13.7017 | 0.14984 | 2.4776 | 0 | 11.0872 | 0.32064 | 0 | 87.0323 | 31.1161 | 203.4894 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.19224 | 0.038443 | 0.008427 | 0 | 0 | 0.45783 | 0.048416 | 0.13942 | 0.0065145 | 0.044903 | 0 | 0.10728 | 0.0045065 | 0 | 0.84214 | 0.30109 | 2.1912 | 3.896% | CZ 1A | 6.477 | 1.2952 | 0.8427 | 0 | 0 | 15.425 | 1.6312 | 4.6973 | 0.21949 | 1.5129 | 0 | 3.6145 | 0.15183 | 0 | 28.3732 | 10.1441 | 74.3844 | 3.896% | CZ 1A | 1.8978 | 0.3795 | 0 | 0 | 0 | 4.5195 | 0.47795 | 1.3763 | 0.064309 | 0.44327 | 0 | 1.0591 | 0.044487 | 0 | 8.3133 | 2.9722 | 21.5477 | 3.896% | CZ 1A | 0 | 0 | 0.008427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008427 | 3.896% | CZ 1A | 19.8676 | 3.973 | 0.92107 | 0 | 0 | 47.3148 | 5.0037 | 14.4086 | 0.67325 | 4.6406 | 0 | 11.0872 | 0.46573 | 0 | 87.0323 | 31.1161 | 226.5041 | 3.896%
CZ 1B | 0.19231 | 0.038383 | 0.0084699 | 0.0016634 | 0.00087083 | 0.52692 | 0.043218 | 0.14229 | 0 | 0.048347 | 0 | 0.10728 | 0.0045054 | 0 | 0.84214 | 0.30109 | 2.2575 | 0% | CZ 1B | 6.4792 | 1.2932 | 0.84699 | 0.15953 | 0.02934 | 17.753 | 1.4561 | 4.794 | 0 | 1.6289 | 0 | 3.6145 | 0.15179 | 0 | 28.3732 | 10.1441 | 76.7238 | 0% | CZ 1B | 1.8984 | 0.37891 | 0 | 0.001014 | 0.0085965 | 5.2016 | 0.42663 | 1.4046 | 0 | 0.47726 | 0 | 1.0591 | 0.044476 | 0 | 8.3133 | 2.9722 | 22.1862 | 0% | CZ 1B | 0 | 0 | 0.0084699 | 0.0015607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010031 | 0% | CZ 1B | 19.8745 | 3.9668 | 0.92576 | 0.1812 | 0.089997 | 54.4558 | 4.4664 | 14.7051 | 0 | 4.9965 | 0 | 11.0872 | 0.46562 | 0 | 87.0323 | 31.1161 | 233.3634 | 0%
CZ 2A | 0.19219 | 0.038343 | 0.0090984 | 0.00579 | 0.00025227 | 0.40363 | 0.041556 | 0.13058 | 0.0034737 | 0.040096 | 0 | 0.10728 | 0.0045054 | 0 | 0.84214 | 0.30109 | 2.12 | 11.87% | CZ 2A | 6.4752 | 1.2919 | 0.90984 | 0.57855 | 0.0084995 | 13.5991 | 1.4001 | 4.3995 | 0.11704 | 1.3509 | 0 | 3.6145 | 0.15179 | 0 | 28.3732 | 10.1441 | 72.4142 | 11.87% | CZ 2A | 1.8972 | 0.37851 | 0 | 6.6855e-05 | 0.0024904 | 3.9845 | 0.41023 | 1.2891 | 0.034291 | 0.39582 | 0 | 1.0591 | 0.044476 | 0 | 8.3133 | 2.9722 | 20.7813 | 11.87% | CZ 2A | 0 | 0 | 0.0090984 | 0.0057832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014882 | 11.87% | CZ 2A | 19.8621 | 3.9627 | 0.99445 | 0.63281 | 0.026072 | 41.7142 | 4.2947 | 13.4953 | 0.359 | 4.1438 | 0 | 11.0872 | 0.46562 | 0 | 87.0323 | 31.1161 | 219.1863 | 11.87%
CZ 2B | 0.19229 | 0.038374 | 0.0091482 | 0.0054257 | 0.09982 | 0.32414 | 0.017014 | 0.14652 | 0 | 0.031617 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.1194 | 1.826% | CZ 2B | 6.4786 | 1.2929 | 0.91482 | 0.3354 | 3.3631 | 10.9207 | 0.57322 | 4.9364 | 0 | 1.0652 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 72.1639 | 1.826% | CZ 2B | 1.8982 | 0.37882 | 0 | 0.030843 | 0.98539 | 3.1998 | 0.16795 | 1.4464 | 0 | 0.31211 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 20.8085 | 1.826% | CZ 2B | 0 | 0 | 0.0091482 | 0.0023014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01145 | 1.826% | CZ 2B | 19.8725 | 3.9659 | 0.9999 | 0.57443 | 10.316 | 33.4983 | 1.7583 | 15.142 | 0 | 3.2675 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 219.0961 | 1.826%
CZ 3A | 0.19275 | 0.038424 | 0.010265 | 0.036742 | 0.00096282 | 0.3241 | 0.024294 | 0.12981 | 0.0020272 | 0.028936 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.0433 | 14.76% | CZ 3A | 6.494 | 1.2946 | 1.0265 | 3.6738 | 0.032439 | 10.9193 | 0.8185 | 4.3735 | 0.068301 | 0.97492 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 71.9595 | 14.76% | CZ 3A | 1.9028 | 0.3793 | 0 | 5.5713e-05 | 0.0095046 | 3.1994 | 0.23982 | 1.2814 | 0.020012 | 0.28565 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.707 | 14.76% | CZ 3A | 0 | 0 | 0.010265 | 0.036736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047002 | 14.76% | CZ 3A | 19.92 | 3.9709 | 1.122 | 4.0159 | 0.099504 | 33.4941 | 2.5107 | 13.4153 | 0.20951 | 2.9905 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 211.4498 | 14.76%
CZ 3B | 0.19237 | 0.038392 | 0.0099664 | 0.0086159 | 0.10203 | 0.27845 | 0.01448 | 0.14742 | 0 | 0.026047 | 0 | 0.10728 | 0.0045054 | 0 | 0.84214 | 0.30109 | 2.0728 | 8.555% | CZ 3B | 6.4812 | 1.2935 | 0.99664 | 0.77062 | 3.4375 | 9.3813 | 0.48786 | 4.9668 | 0 | 0.87756 | 0 | 3.6145 | 0.15179 | 0 | 28.3732 | 10.1441 | 70.9765 | 8.555% | CZ 3B | 1.899 | 0.37899 | 0 | 0.013544 | 1.0072 | 2.7487 | 0.14294 | 1.4553 | 0 | 0.25713 | 0 | 1.0591 | 0.044476 | 0 | 8.3133 | 2.9722 | 20.2918 | 8.555% | CZ 3B | 0 | 0 | 0.0099664 | 0.007244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01721 | 8.555% | CZ 3B | 19.8805 | 3.9677 | 1.0893 | 0.93355 | 10.5442 | 28.7764 | 1.4965 | 15.2352 | 0 | 2.6919 | 0 | 11.0872 | 0.46562 | 0 | 87.0323 | 31.1161 | 214.3165 | 8.555%
CZ 3C | 0.19258 | 0.038514 | 0.010403 | 0.0013079 | 0.031979 | 0.17006 | 0.011768 | 0.12549 | 0 | 0.021341 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 1.8585 | 3.506% | CZ 3C | 6.4884 | 1.2976 | 1.0403 | 0.1092 | 1.0774 | 5.7297 | 0.39647 | 4.228 | 0 | 0.71902 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 63.3697 | 3.506% | CZ 3C | 1.9011 | 0.3802 | 0 | 0.0032146 | 0.31569 | 1.6788 | 0.11617 | 1.2388 | 0 | 0.21067 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 18.2337 | 3.506% | CZ 3C | 0 | 0 | 0.010403 | 0.00098225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011385 | 3.506% | CZ 3C | 19.9025 | 3.9803 | 1.1371 | 0.14101 | 3.3049 | 17.5753 | 1.2162 | 12.9691 | 0 | 2.2055 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 192.1333 | 3.506%
CZ 4A | 0.19257 | 0.038573 | 0.011199 | 0.075393 | 0.0015661 | 0.2886 | 0.01881 | 0.13019 | 0.0013742 | 0.024677 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.038 | 31.46% | CZ 4A | 6.4881 | 1.2996 | 1.1199 | 7.5215 | 0.052766 | 9.7236 | 0.63374 | 4.3864 | 0.046301 | 0.8314 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 74.3868 | 31.46% | CZ 4A | 1.901 | 0.38078 | 0 | 0.0026575 | 0.01546 | 2.849 | 0.18569 | 1.2852 | 0.013566 | 0.2436 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.2661 | 31.46% | CZ 4A | 0 | 0 | 0.011199 | 0.075124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086323 | 31.46% | CZ 4A | 19.9016 | 3.9864 | 1.2241 | 8.2389 | 0.16185 | 29.8263 | 1.9439 | 13.4549 | 0.14202 | 2.5502 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 211.1315 | 31.46%
CZ 4B | 0.19193 | 0.038396 | 0.010933 | 0.014371 | 0.12715 | 0.20491 | 0.0090734 | 0.16775 | 0 | 0.020421 | 0 | 0.10728 | 0.0045065 | 0 | 0.84214 | 0.30109 | 2.04 | 0.05451% | CZ 4B | 6.4664 | 1.2936 | 1.0933 | 1.3049 | 4.2839 | 6.9038 | 0.3057 | 5.6518 | 0 | 0.68803 | 0 | 3.6145 | 0.15183 | 0 | 28.3732 | 10.1441 | 70.275 | 0.05451% | CZ 4B | 1.8947 | 0.37904 | 0 | 0.019689 | 1.2552 | 2.0228 | 0.08957 | 1.656 | 0 | 0.20159 | 0 | 1.0591 | 0.044487 | 0 | 8.3133 | 2.9722 | 19.9076 | 0.05451% | CZ 4B | 0 | 0 | 0.010933 | 0.012377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02331 | 0.05451% | CZ 4B | 19.8351 | 3.9681 | 1.195 | 1.5589 | 13.1405 | 21.1769 | 0.9377 | 17.3364 | 0 | 2.1105 | 0 | 11.0872 | 0.46573 | 0 | 87.0323 | 31.1161 | 210.9605 | 0.05451%
CZ 4C | 0.19319 | 0.038591 | 0.011478 | 0.020573 | 0.079564 | 0.092122 | 0.0050449 | 0.12842 | 0 | 0.013749 | 0 | 0.10728 | 0.0045071 | 0 | 0.84214 | 0.30109 | 1.8377 | 4.546% | CZ 4C | 6.5089 | 1.3002 | 1.1478 | 2.03 | 2.6806 | 3.1038 | 0.16997 | 4.3266 | 0 | 0.46323 | 0 | 3.6145 | 0.15185 | 0 | 28.3732 | 10.1441 | 64.0147 | 4.546% | CZ 4C | 1.9071 | 0.38096 | 0 | 0.004067 | 0.78543 | 0.9094 | 0.049802 | 1.2677 | 0 | 0.13573 | 0 | 1.0591 | 0.044492 | 0 | 8.3133 | 2.9722 | 17.8293 | 4.546% | CZ 4C | 0 | 0 | 0.011478 | 0.020161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031639 | 4.546% | CZ 4C | 19.9654 | 3.9883 | 1.2546 | 2.2461 | 8.2227 | 9.5205 | 0.52137 | 13.2716 | 0 | 1.4209 | 0 | 11.0872 | 0.46579 | 0 | 87.0323 | 31.1161 | 190.113 | 4.546%
CZ 5A | 0.19246 | 0.038426 | 0.011995 | 0.11641 | 0.10063 | 0.14211 | 0.0095813 | 0.13056 | 0.00036853 | 0.021136 | 0 | 0.10728 | 0.0045065 | 0 | 0.84214 | 0.30109 | 2.0187 | 13.22% | CZ 5A | 6.4843 | 1.2946 | 1.1995 | 11.6145 | 3.3904 | 4.7878 | 0.32281 | 4.3989 | 0.012417 | 0.71212 | 0 | 3.6145 | 0.15183 | 0 | 28.3732 | 10.1441 | 76.501 | 13.22% | CZ 5A | 1.8999 | 0.37933 | 0 | 0.0039779 | 0.9934 | 1.4028 | 0.094584 | 1.2889 | 0.0036381 | 0.20865 | 0 | 1.0591 | 0.044487 | 0 | 8.3133 | 2.9722 | 18.6643 | 13.22% | CZ 5A | 0 | 0 | 0.011995 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.128 | 13.22% | CZ 5A | 19.8902 | 3.9712 | 1.3111 | 12.7214 | 10.3999 | 14.6861 | 0.9902 | 13.4932 | 0.038087 | 2.1844 | 0 | 11.0872 | 0.46573 | 0 | 87.0323 | 31.1161 | 209.3871 | 13.22%
CZ 5B | 0.19236 | 0.038516 | 0.011767 | 0.036548 | 0.1419 | 0.16315 | 0.0059823 | 0.16842 | 0 | 0.019267 | 0 | 0.10728 | 0.0045048 | 0 | 0.84214 | 0.30109 | 2.0329 | 3.582% | CZ 5B | 6.4808 | 1.2977 | 1.1767 | 3.5224 | 4.781 | 5.4967 | 0.20156 | 5.6743 | 0 | 0.64912 | 0 | 3.6145 | 0.15177 | 0 | 28.3732 | 10.1441 | 71.5638 | 3.582% | CZ 5B | 1.8989 | 0.38021 | 0 | 0.019706 | 1.4008 | 1.6105 | 0.059056 | 1.6626 | 0 | 0.19019 | 0 | 1.0591 | 0.04447 | 0 | 8.3133 | 2.9722 | 19.611 | 3.582% | CZ 5B | 0 | 0 | 0.011767 | 0.034552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046319 | 3.582% | CZ 5B | 19.8793 | 3.9804 | 1.2862 | 3.9828 | 14.6653 | 16.8605 | 0.61825 | 17.4054 | 0 | 1.9911 | 0 | 11.0872 | 0.46556 | 0 | 87.0323 | 31.1161 | 210.3706 | 3.582%
CZ 5C | 0.19335 | 0.03856 | 0.011928 | 0.021721 | 0.089278 | 0.067355 | 0.0029635 | 0.13116 | 0 | 0.011103 | 0 | 0.10728 | 0.0045071 | 0 | 0.84214 | 0.30109 | 1.8224 | 0.07377% | CZ 5C | 6.5144 | 1.2991 | 1.1928 | 2.1265 | 3.0079 | 2.2693 | 0.099846 | 4.4189 | 0 | 0.37409 | 0 | 3.6145 | 0.15185 | 0 | 28.3732 | 10.1441 | 63.5866 | 0.07377% | CZ 5C | 1.9087 | 0.38065 | 0 | 0.0067803 | 0.88132 | 0.66491 | 0.029255 | 1.2947 | 0 | 0.10961 | 0 | 1.0591 | 0.044492 | 0 | 8.3133 | 2.9722 | 17.6651 | 0.07377% | CZ 5C | 0 | 0 | 0.011928 | 0.021034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032962 | 0.07377% | CZ 5C | 19.9824 | 3.985 | 1.3038 | 2.37 | 9.2266 | 6.9609 | 0.30627 | 13.5546 | 0 | 1.1475 | 0 | 11.0872 | 0.46579 | 0 | 87.0323 | 31.1161 | 188.5384 | 0.07377%
CZ 6A | 0.19259 | 0.038511 | 0.012587 | 0.16366 | 0.10433 | 0.14784 | 0.010558 | 0.13503 | 0.00047294 | 0.023235 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.0838 | 2.328% | CZ 6A | 6.4886 | 1.2975 | 1.2587 | 16.3428 | 3.5152 | 4.981 | 0.35573 | 4.5494 | 0.015934 | 0.78283 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 81.8712 | 2.328% | CZ 6A | 1.9012 | 0.38017 | 0 | 0.0034709 | 1.03 | 1.4594 | 0.10423 | 1.333 | 0.0046687 | 0.22937 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 18.8345 | 2.328% | CZ 6A | 0 | 0 | 0.012587 | 0.16331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1759 | 2.328% | CZ 6A | 19.9033 | 3.98 | 1.3758 | 17.8861 | 10.7826 | 15.2787 | 1.0912 | 13.9548 | 0.048877 | 2.4013 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 216.4038 | 2.328%
CZ 6B | 0.19267 | 0.03845 | 0.012435 | 0.069115 | 0.15057 | 0.1237 | 0.0047644 | 0.14854 | 0 | 0.01669 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.0119 | 0% | CZ 6B | 6.4915 | 1.2954 | 1.2435 | 6.884 | 5.0728 | 4.1678 | 0.16052 | 5.0045 | 0 | 0.5623 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 73.1659 | 0% | CZ 6B | 1.902 | 0.37957 | 0 | 0.0040949 | 1.4863 | 1.2212 | 0.047033 | 1.4663 | 0 | 0.16475 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.0604 | 0% | CZ 6B | 0 | 0 | 0.012435 | 0.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081135 | 0% | CZ 6B | 19.9121 | 3.9737 | 1.3591 | 7.5518 | 15.5605 | 12.7844 | 0.49239 | 15.3508 | 0 | 1.7248 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 208.4109 | 0%
CZ 7 | 0.19224 | 0.038606 | 0.013295 | 0.18562 | 0.11832 | 0.12555 | 0.0074971 | 0.13764 | 0.00089848 | 0.021426 | 0 | 0.10728 | 0.0045054 | 0 | 0.84214 | 0.30109 | 2.0961 | 0.3244% | CZ 7 | 6.4767 | 1.3007 | 1.3295 | 18.5174 | 3.9865 | 4.2299 | 0.25259 | 4.6372 | 0.030271 | 0.72189 | 0 | 3.6145 | 0.15179 | 0 | 28.3732 | 10.1441 | 83.7663 | 0.3244% | CZ 7 | 1.8977 | 0.3811 | 0 | 0.0066243 | 1.1681 | 1.2394 | 0.074009 | 1.3587 | 0.0088695 | 0.21151 | 0 | 1.0591 | 0.044476 | 0 | 8.3133 | 2.9722 | 18.735 | 0.3244% | CZ 7 | 0 | 0 | 0.013295 | 0.18495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19824 | 0.3244% | CZ 7 | 19.8669 | 3.9898 | 1.4531 | 20.2842 | 12.2284 | 12.9748 | 0.7748 | 14.2243 | 0.092855 | 2.2143 | 0 | 11.0872 | 0.46562 | 0 | 87.0323 | 31.1161 | 217.8047 | 0.3244%
CZ 8 | 0.19616 | 0.03903 | 0.014244 | 0.26104 | 0.14266 | 0.082136 | 0.0028862 | 0.13669 | 0.00067442 | 0.018785 | 0 | 0.10728 | 0.0045099 | 0 | 0.84214 | 0.30109 | 2.1493 | 0% | CZ 8 | 6.609 | 1.315 | 1.4244 | 26.0858 | 4.8066 | 2.7673 | 0.097241 | 4.6053 | 0.022722 | 0.63288 | 0 | 3.6145 | 0.15195 | 0 | 28.3732 | 10.1441 | 90.6499 | 0% | CZ 8 | 1.9364 | 0.38529 | 0 | 0.0027634 | 1.4083 | 0.81082 | 0.028492 | 1.3493 | 0.0066577 | 0.18543 | 0 | 1.0591 | 0.04452 | 0 | 8.3133 | 2.9722 | 18.5027 | 0% | CZ 8 | 0 | 0 | 0.014244 | 0.26076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27501 | 0% | CZ 8 | 20.2725 | 4.0336 | 1.5569 | 28.5304 | 14.7438 | 8.4884 | 0.29828 | 14.1263 | 0.069699 | 1.9413 | 0 | 11.0872 | 0.46608 | 0 | 87.0323 | 31.1161 | 223.7631 | 0%
US Weighted | 0.19252 | 0.038475 | 0.010711 | 0.052782 | 0.037292 | 0.2729 | 0.020271 | 0.13364 | 0.0014603 | 0.026836 | 0 | 0.10728 | 0.0045059 | 0 | 0.84214 | 0.30109 | 2.0419 | 100% | US Weighted | 6.4864 | 1.2963 | 1.0711 | 5.2498 | 1.2564 | 9.1945 | 0.68298 | 4.5027 | 0.049199 | 0.90413 | 0 | 3.6145 | 0.15181 | 0 | 28.3732 | 10.1441 | 72.9771 | 100% | US Weighted | 1.9005 | 0.37982 | 0 | 0.0042215 | 0.36813 | 2.694 | 0.20011 | 1.3193 | 0.014415 | 0.26491 | 0 | 1.0591 | 0.044481 | 0 | 8.3133 | 2.9722 | 19.5345 | 100% | US Weighted | 0 | 0 | 0.010711 | 0.052354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063065 | 100% | US Weighted | 19.8965 | 3.9763 | 1.1707 | 5.7665 | 3.854 | 28.2033 | 2.095 | 13.8117 | 0.15092 | 2.7734 | 0 | 11.0872 | 0.46567 | 0 | 87.0323 | 31.1161 | 211.3996 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.217 | 0.038443 | 0.0084252 | 1.958e-05 | 0 | 0.5234 | 0.063142 | 0.15007 | 0 | 0.058697 | 0 | 0.10751 | 0.0045359 | 0 | 0.84214 | 0.30216 | 2.3155 | 3.896% | CZ 1A | 7.3111 | 1.2952 | 0.84252 | 0.001958 | 0 | 17.6342 | 2.1274 | 5.0561 | 0 | 1.9776 | 0 | 3.6222 | 0.15282 | 0 | 28.3732 | 10.1802 | 78.5745 | 3.896% | CZ 1A | 2.1422 | 0.3795 | 0 | 0 | 0 | 5.1668 | 0.62332 | 1.4814 | 0 | 0.57944 | 0 | 1.0613 | 0.044776 | 0 | 8.3133 | 2.9828 | 22.7749 | 3.896% | CZ 1A | 0 | 0 | 0.0084252 | 1.958e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084448 | 3.896% | CZ 1A | 22.4262 | 3.973 | 0.92088 | 0.0021401 | 0 | 54.0915 | 6.5255 | 15.5092 | 0 | 6.0662 | 0 | 11.1107 | 0.46876 | 0 | 87.0323 | 31.227 | 239.3534 | 3.896%
CZ 1B | 0.21671 | 0.038383 | 0.0084707 | 0.0045006 | 0.0012964 | 0.55467 | 0.050636 | 0.15201 | 0 | 0.053409 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.3364 | 0% | CZ 1B | 7.3013 | 1.2932 | 0.84707 | 0.37451 | 0.043677 | 18.6876 | 1.706 | 5.1215 | 0 | 1.7994 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 79.5027 | 0% | CZ 1B | 2.1393 | 0.37891 | 0 | 0.011248 | 0.012797 | 5.4755 | 0.49986 | 1.5006 | 0 | 0.52723 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 22.9476 | 0% | CZ 1B | 0 | 0 | 0.0084707 | 0.0033612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011832 | 0% | CZ 1B | 22.3962 | 3.9668 | 0.92585 | 0.48513 | 0.13397 | 57.3227 | 5.2331 | 15.7098 | 0 | 5.5196 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 241.5319 | 0%
CZ 2A | 0.21772 | 0.038343 | 0.0090984 | 0.0055608 | 0.00021728 | 0.45102 | 0.052384 | 0.14017 | 0 | 0.052562 | 0 | 0.10751 | 0.0045364 | 0 | 0.84214 | 0.30216 | 2.2234 | 11.87% | CZ 2A | 7.3354 | 1.2919 | 0.90984 | 0.53916 | 0.0073206 | 15.1958 | 1.7649 | 4.7227 | 0 | 1.7709 | 0 | 3.6222 | 0.15284 | 0 | 28.3732 | 10.1802 | 75.8663 | 11.87% | CZ 2A | 2.1493 | 0.37851 | 0 | 0.0025182 | 0.0021449 | 4.4524 | 0.51712 | 1.3838 | 0 | 0.51888 | 0 | 1.0613 | 0.044782 | 0 | 8.3133 | 2.9828 | 21.8068 | 11.87% | CZ 2A | 0 | 0 | 0.0090984 | 0.0053057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014404 | 11.87% | CZ 2A | 22.5009 | 3.9627 | 0.99445 | 0.60628 | 0.022455 | 46.6118 | 5.4137 | 14.4865 | 0 | 5.4321 | 0 | 11.1107 | 0.46882 | 0 | 87.0323 | 31.227 | 229.8697 | 11.87%
CZ 2B | 0.21931 | 0.038374 | 0.0091476 | 0.0208 | 0.11035 | 0.34853 | 0.02249 | 0.1581 | 0 | 0.03538 | 0 | 0.10751 | 0.0045387 | 0 | 0.84214 | 0.30216 | 2.2188 | 1.826% | CZ 2B | 7.3888 | 1.2929 | 0.91476 | 0.95492 | 3.7178 | 11.7425 | 0.75771 | 5.3267 | 0 | 1.192 | 0 | 3.6222 | 0.15292 | 0 | 28.3732 | 10.1802 | 75.6167 | 1.826% | CZ 2B | 2.1649 | 0.37882 | 0 | 0.16749 | 1.0893 | 3.4406 | 0.22201 | 1.5607 | 0 | 0.34926 | 0 | 1.0613 | 0.044804 | 0 | 8.3133 | 2.9828 | 21.7754 | 1.826% | CZ 2B | 0 | 0 | 0.0091476 | 0.0038328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01298 | 1.826% | CZ 2B | 22.6646 | 3.9659 | 0.99984 | 2.1724 | 11.4041 | 36.0193 | 2.3242 | 16.3393 | 0 | 3.6564 | 0 | 11.1107 | 0.46906 | 0 | 87.0323 | 31.227 | 229.3851 | 1.826%
CZ 3A | 0.21551 | 0.038424 | 0.010264 | 0.0184 | 0.0006874 | 0.34651 | 0.030635 | 0.13466 | 0 | 0.037319 | 0 | 0.10751 | 0.0045353 | 0 | 0.84214 | 0.30216 | 2.0888 | 14.76% | CZ 3A | 7.2611 | 1.2946 | 1.0264 | 1.7914 | 0.02316 | 11.6745 | 1.0322 | 4.537 | 0 | 1.2573 | 0 | 3.6222 | 0.1528 | 0 | 28.3732 | 10.1802 | 72.226 | 14.76% | CZ 3A | 2.1275 | 0.3793 | 0 | 0.0072371 | 0.0067858 | 3.4206 | 0.30242 | 1.3294 | 0 | 0.3684 | 0 | 1.0613 | 0.044771 | 0 | 8.3133 | 2.9828 | 20.3438 | 14.76% | CZ 3A | 0 | 0 | 0.010264 | 0.017667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027931 | 14.76% | CZ 3A | 22.2727 | 3.9709 | 1.1219 | 2.0068 | 0.071041 | 35.8107 | 3.166 | 13.917 | 0 | 3.8567 | 0 | 11.1107 | 0.46871 | 0 | 87.0323 | 31.227 | 216.0326 | 14.76%
CZ 3B | 0.2149 | 0.038392 | 0.0099664 | 0.016077 | 0.1069 | 0.28961 | 0.018681 | 0.15665 | 0 | 0.028581 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.1361 | 8.555% | CZ 3B | 7.2403 | 1.2935 | 0.99664 | 0.92888 | 3.6017 | 9.7574 | 0.6294 | 5.2777 | 0 | 0.96294 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 73.0168 | 8.555% | CZ 3B | 2.1214 | 0.37899 | 0 | 0.10106 | 1.0553 | 2.8589 | 0.18442 | 1.5464 | 0 | 0.28214 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 20.9308 | 8.555% | CZ 3B | 0 | 0 | 0.0099664 | 0.0058397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015806 | 8.555% | CZ 3B | 22.2089 | 3.9677 | 1.0893 | 1.6963 | 11.048 | 29.9301 | 1.9306 | 16.1889 | 0 | 2.9537 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 220.8522 | 8.555%
CZ 3C | 0.21485 | 0.038514 | 0.010402 | 0.0025248 | 0.032024 | 0.17923 | 0.01516 | 0.13465 | 0 | 0.027037 | 0 | 0.10751 | 0.0045336 | 0 | 0.84214 | 0.30216 | 1.9107 | 3.506% | CZ 3C | 7.2388 | 1.2976 | 1.0402 | 0.15825 | 1.0789 | 6.0384 | 0.51077 | 4.5365 | 0 | 0.91092 | 0 | 3.6222 | 0.15274 | 0 | 28.3732 | 10.1802 | 65.1386 | 3.506% | CZ 3C | 2.121 | 0.3802 | 0 | 0.014029 | 0.31613 | 1.7693 | 0.14966 | 1.3292 | 0 | 0.2669 | 0 | 1.0613 | 0.044754 | 0 | 8.3133 | 2.9828 | 18.7485 | 3.506% | CZ 3C | 0 | 0 | 0.010402 | 0.0011037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011505 | 3.506% | CZ 3C | 22.2043 | 3.9803 | 1.1369 | 0.2675 | 3.3095 | 18.5224 | 1.5667 | 13.9152 | 0 | 2.7942 | 0 | 11.1107 | 0.46853 | 0 | 87.0323 | 31.227 | 197.5356 | 3.506%
CZ 4A | 0.21433 | 0.038573 | 0.011198 | 0.042887 | 0.0010887 | 0.30017 | 0.022737 | 0.13241 | 0 | 0.029289 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.049 | 31.46% | CZ 4A | 7.2212 | 1.2996 | 1.1198 | 4.2801 | 0.036679 | 10.1131 | 0.76606 | 4.4612 | 0 | 0.98678 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 72.6128 | 31.46% | CZ 4A | 2.1158 | 0.38078 | 0 | 0.001287 | 0.010747 | 2.9631 | 0.22446 | 1.3071 | 0 | 0.28913 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 19.6947 | 31.46% | CZ 4A | 0 | 0 | 0.011198 | 0.042757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053955 | 31.46% | CZ 4A | 22.1503 | 3.9864 | 1.2239 | 4.6868 | 0.11251 | 31.0211 | 2.3498 | 13.6843 | 0 | 3.0269 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 212.0807 | 31.46%
CZ 4B | 0.21346 | 0.038396 | 0.010934 | 0.025852 | 0.1307 | 0.23195 | 0.012195 | 0.17064 | 0 | 0.02659 | 0 | 0.10751 | 0.0045342 | 0 | 0.84214 | 0.30216 | 2.1171 | 0.05451% | CZ 4B | 7.1919 | 1.2936 | 1.0934 | 1.9231 | 4.4036 | 7.8148 | 0.41087 | 5.7492 | 0 | 0.89586 | 0 | 3.6222 | 0.15276 | 0 | 28.3732 | 10.1802 | 73.1048 | 0.05451% | CZ 4B | 2.1072 | 0.37904 | 0 | 0.098567 | 1.2903 | 2.2897 | 0.12038 | 1.6845 | 0 | 0.26249 | 0 | 1.0613 | 0.04476 | 0 | 8.3133 | 2.9828 | 20.6344 | 0.05451% | CZ 4B | 0 | 0 | 0.010934 | 0.015867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026801 | 0.05451% | CZ 4B | 22.0606 | 3.9681 | 1.1951 | 2.7661 | 13.5078 | 23.9713 | 1.2603 | 17.6353 | 0 | 2.748 | 0 | 11.1107 | 0.46859 | 0 | 87.0323 | 31.227 | 218.9512 | 0.05451%
CZ 4C | 0.21551 | 0.038591 | 0.011478 | 0.025073 | 0.079093 | 0.095031 | 0.0061855 | 0.13279 | 0 | 0.016475 | 0 | 0.10751 | 0.0045353 | 0 | 0.84214 | 0.30216 | 1.8766 | 4.546% | CZ 4C | 7.261 | 1.3002 | 1.1478 | 2.4529 | 2.6648 | 3.2017 | 0.2084 | 4.474 | 0 | 0.55506 | 0 | 3.6222 | 0.1528 | 0 | 28.3732 | 10.1802 | 65.5942 | 4.546% | CZ 4C | 2.1275 | 0.38096 | 0 | 0.0081007 | 0.78078 | 0.93811 | 0.061061 | 1.3109 | 0 | 0.16263 | 0 | 1.0613 | 0.044771 | 0 | 8.3133 | 2.9828 | 18.1722 | 4.546% | CZ 4C | 0 | 0 | 0.011478 | 0.024252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03573 | 4.546% | CZ 4C | 22.2726 | 3.9883 | 1.2545 | 2.7356 | 8.174 | 9.8211 | 0.63925 | 13.7235 | 0 | 1.7026 | 0 | 11.1107 | 0.46871 | 0 | 87.0323 | 31.227 | 194.1501 | 4.546%
CZ 5A | 0.2143 | 0.038426 | 0.011995 | 0.078481 | 0.10022 | 0.15218 | 0.012143 | 0.13258 | 0 | 0.023789 | 0 | 0.10751 | 0.0045342 | 0 | 0.84214 | 0.30216 | 2.0205 | 13.22% | CZ 5A | 7.2202 | 1.2946 | 1.1995 | 7.8096 | 3.3767 | 5.1271 | 0.40912 | 4.467 | 0 | 0.80149 | 0 | 3.6222 | 0.15276 | 0 | 28.3732 | 10.1802 | 74.0336 | 13.22% | CZ 5A | 2.1155 | 0.37933 | 0 | 0.0057329 | 0.98937 | 1.5022 | 0.11987 | 1.3088 | 0 | 0.23484 | 0 | 1.0613 | 0.04476 | 0 | 8.3133 | 2.9828 | 19.0579 | 13.22% | CZ 5A | 0 | 0 | 0.011995 | 0.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089894 | 13.22% | CZ 5A | 22.1474 | 3.9712 | 1.311 | 8.5745 | 10.3577 | 15.7269 | 1.2549 | 13.7022 | 0 | 2.4585 | 0 | 11.1107 | 0.46859 | 0 | 87.0323 | 31.227 | 209.3429 | 13.22%
CZ 5B | 0.21409 | 0.038516 | 0.011768 | 0.048936 | 0.14806 | 0.1795 | 0.0082246 | 0.16775 | 0 | 0.023227 | 0 | 0.10751 | 0.0045342 | 0 | 0.84214 | 0.30216 | 2.0964 | 3.582% | CZ 5B | 7.213 | 1.2977 | 1.1768 | 4.3482 | 4.9885 | 6.0476 | 0.2771 | 5.6518 | 0 | 0.78255 | 0 | 3.6222 | 0.15276 | 0 | 28.3732 | 10.1802 | 74.1115 | 3.582% | CZ 5B | 2.1134 | 0.38021 | 0 | 0.081196 | 1.4616 | 1.772 | 0.08119 | 1.656 | 0 | 0.22929 | 0 | 1.0613 | 0.04476 | 0 | 8.3133 | 2.9828 | 20.177 | 3.582% | CZ 5B | 0 | 0 | 0.011768 | 0.040711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052479 | 3.582% | CZ 5B | 22.1251 | 3.9804 | 1.2862 | 5.2997 | 15.3019 | 18.5506 | 0.84998 | 17.3363 | 0 | 2.4004 | 0 | 11.1107 | 0.46859 | 0 | 87.0323 | 31.227 | 216.9694 | 3.582%
CZ 5C | 0.21562 | 0.03856 | 0.01193 | 0.026489 | 0.088477 | 0.067976 | 0.0035883 | 0.13309 | 0 | 0.012263 | 0 | 0.10751 | 0.0045359 | 0 | 0.84214 | 0.30216 | 1.8543 | 0.07377% | CZ 5C | 7.2647 | 1.2991 | 1.193 | 2.593 | 2.9809 | 2.2902 | 0.1209 | 4.4842 | 0 | 0.41317 | 0 | 3.6222 | 0.15282 | 0 | 28.3732 | 10.1802 | 64.9675 | 0.07377% | CZ 5C | 2.1285 | 0.38065 | 0 | 0.0083291 | 0.87341 | 0.67103 | 0.035422 | 1.3139 | 0 | 0.12106 | 0 | 1.0613 | 0.044776 | 0 | 8.3133 | 2.9828 | 17.9345 | 0.07377% | CZ 5C | 0 | 0 | 0.01193 | 0.025645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037575 | 0.07377% | CZ 5C | 22.2838 | 3.985 | 1.3039 | 2.8902 | 9.1437 | 7.0251 | 0.37084 | 13.7548 | 0 | 1.2674 | 0 | 11.1107 | 0.46876 | 0 | 87.0323 | 31.227 | 191.8635 | 0.07377%
CZ 6A | 0.21452 | 0.038511 | 0.012587 | 0.12109 | 0.10381 | 0.16007 | 0.013296 | 0.13723 | 0 | 0.025654 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.0831 | 2.328% | CZ 6A | 7.2276 | 1.2975 | 1.2587 | 12.085 | 3.4976 | 5.3929 | 0.44797 | 4.6236 | 0 | 0.86433 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 79.0236 | 2.328% | CZ 6A | 2.1177 | 0.38017 | 0 | 0.0035935 | 1.0248 | 1.5801 | 0.13125 | 1.3547 | 0 | 0.25325 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 19.2478 | 2.328% | CZ 6A | 0 | 0 | 0.012587 | 0.12073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13331 | 2.328% | CZ 6A | 22.1702 | 3.98 | 1.3758 | 13.2331 | 10.7285 | 16.5424 | 1.3741 | 14.1826 | 0 | 2.6513 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 216.0766 | 2.328%
CZ 6B | 0.21465 | 0.03845 | 0.012435 | 0.081901 | 0.15067 | 0.13567 | 0.0062527 | 0.15091 | 0 | 0.01892 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.0662 | 0% | CZ 6B | 7.2318 | 1.2954 | 1.2435 | 7.9861 | 5.0762 | 4.571 | 0.21066 | 5.0844 | 0 | 0.63745 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 75.6649 | 0% | CZ 6B | 2.1189 | 0.37957 | 0 | 0.030369 | 1.4873 | 1.3393 | 0.061724 | 1.4897 | 0 | 0.18677 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 19.4959 | 0% | CZ 6B | 0 | 0 | 0.012435 | 0.078824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09126 | 0% | CZ 6B | 22.183 | 3.9737 | 1.3592 | 8.9334 | 15.5708 | 14.0211 | 0.64619 | 15.596 | 0 | 1.9553 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 214.0774 | 0%
CZ 7 | 0.21492 | 0.038606 | 0.013299 | 0.14517 | 0.11788 | 0.13389 | 0.0090706 | 0.13674 | 0 | 0.022039 | 0 | 0.10751 | 0.0045347 | 0 | 0.84214 | 0.30216 | 2.088 | 0.3244% | CZ 7 | 7.2409 | 1.3007 | 1.3299 | 14.4952 | 3.9717 | 4.5111 | 0.3056 | 4.607 | 0 | 0.74252 | 0 | 3.6222 | 0.15278 | 0 | 28.3732 | 10.1802 | 80.8331 | 0.3244% | CZ 7 | 2.1216 | 0.3811 | 0 | 0.0031868 | 1.1637 | 1.3217 | 0.089542 | 1.3499 | 0 | 0.21756 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9828 | 19.0505 | 0.3244% | CZ 7 | 0 | 0 | 0.013299 | 0.14484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15814 | 0.3244% | CZ 7 | 22.2109 | 3.9898 | 1.4536 | 15.8648 | 12.183 | 13.8373 | 0.93741 | 14.1317 | 0 | 2.2776 | 0 | 11.1107 | 0.46865 | 0 | 87.0323 | 31.227 | 216.7247 | 0.3244%
CZ 8 | 0.22035 | 0.03903 | 0.014251 | 0.21485 | 0.14105 | 0.09198 | 0.0036086 | 0.13534 | 0 | 0.017424 | 0 | 0.10751 | 0.0045392 | 0 | 0.84214 | 0.30216 | 2.1342 | 0% | CZ 8 | 7.4241 | 1.315 | 1.4251 | 21.4612 | 4.7522 | 3.0989 | 0.12158 | 4.5599 | 0 | 0.58706 | 0 | 3.6222 | 0.15293 | 0 | 28.3732 | 10.1802 | 87.0735 | 0% | CZ 8 | 2.1753 | 0.38529 | 0 | 0.0034821 | 1.3924 | 0.90799 | 0.035623 | 1.3361 | 0 | 0.17201 | 0 | 1.0613 | 0.04481 | 0 | 8.3133 | 2.9828 | 18.8103 | 0% | CZ 8 | 0 | 0 | 0.014251 | 0.21449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22874 | 0% | CZ 8 | 22.7729 | 4.0336 | 1.5576 | 23.4806 | 14.5768 | 9.5058 | 0.37294 | 13.9871 | 0 | 1.8008 | 0 | 11.1107 | 0.46911 | 0 | 87.0323 | 31.227 | 221.9272 | 0%
US Weighted | 0.21522 | 0.038475 | 0.01071 | 0.035305 | 0.037841 | 0.29212 | 0.025422 | 0.13843 | 0 | 0.032705 | 0 | 0.10751 | 0.004535 | 0 | 0.84214 | 0.30216 | 2.0826 | 100% | US Weighted | 7.2511 | 1.2963 | 1.071 | 3.4086 | 1.2749 | 9.8421 | 0.85651 | 4.6639 | 0 | 1.1019 | 0 | 3.6222 | 0.15279 | 0 | 28.3732 | 10.1802 | 73.0946 | 100% | US Weighted | 2.1246 | 0.37982 | 0 | 0.018156 | 0.37355 | 2.8837 | 0.25096 | 1.3665 | 0 | 0.32285 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9828 | 20.1224 | 100% | US Weighted | 0 | 0 | 0.01071 | 0.033466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044176 | 100% | US Weighted | 22.242 | 3.9763 | 1.1706 | 3.8479 | 3.9107 | 30.1899 | 2.6273 | 14.3061 | 0 | 3.3799 | 0 | 11.1107 | 0.46868 | 0 | 87.0323 | 31.227 | 215.4894 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.29004 | 0.055775 | 0.008507 | 0.00111 | 0 | 0.58741 | 0.11791 | 0.16278 | 0 | 0.093166 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.6088 | 3.896% | CZ 1A | 9.772 | 1.8791 | 0.8507 | 0.111 | 0 | 19.7908 | 3.9727 | 5.4844 | 0 | 3.1389 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 88.5314 | 3.896% | CZ 1A | 2.8632 | 0.55059 | 0 | 0 | 0 | 5.7987 | 1.164 | 1.6069 | 0 | 0.91971 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 25.6579 | 3.896% | CZ 1A | 0 | 0 | 0.008507 | 0.00111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009617 | 3.896% | CZ 1A | 29.9749 | 5.7641 | 0.92981 | 0.12132 | 0 | 60.7067 | 12.186 | 16.823 | 0 | 9.6284 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 269.6641 | 3.896%
CZ 1B | 0.29004 | 0.055708 | 0.0085465 | 0.010128 | 0.0013996 | 0.61344 | 0.091272 | 0.17151 | 0 | 0.083144 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.6173 | 0% | CZ 1B | 9.772 | 1.8769 | 0.85465 | 0.9395 | 0.047156 | 20.668 | 3.0751 | 5.7786 | 0 | 2.8013 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 89.3449 | 0% | CZ 1B | 2.8632 | 0.54993 | 0 | 0.010909 | 0.013817 | 6.0557 | 0.90101 | 1.6931 | 0 | 0.82077 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 25.6633 | 0% | CZ 1B | 0 | 0 | 0.0085465 | 0.0090227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017569 | 0% | CZ 1B | 29.9749 | 5.7572 | 0.93414 | 1.1004 | 0.14465 | 63.3974 | 9.4327 | 17.7253 | 0 | 8.5927 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 270.5891 | 0%
CZ 2A | 0.29004 | 0.055663 | 0.0091744 | 0.012541 | 0.00039901 | 0.53992 | 0.099139 | 0.15198 | 0 | 0.089146 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.5401 | 11.87% | CZ 2A | 9.772 | 1.8754 | 0.91744 | 1.2324 | 0.013443 | 18.1909 | 3.3401 | 5.1205 | 0 | 3.0035 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 86.9975 | 11.87% | CZ 2A | 2.8632 | 0.54949 | 0 | 0.0032258 | 0.0039389 | 5.3299 | 0.97866 | 1.5003 | 0 | 0.88002 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 24.8636 | 11.87% | CZ 2A | 0 | 0 | 0.0091744 | 0.012214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021389 | 11.87% | CZ 2A | 29.9749 | 5.7526 | 1.0028 | 1.3688 | 0.041236 | 55.7991 | 10.2456 | 15.7067 | 0 | 9.213 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 262.6345 | 11.87%
CZ 2B | 0.29004 | 0.055698 | 0.0092233 | 0.023081 | 0.0029579 | 0.44348 | 0.040974 | 0.16908 | 0 | 0.056851 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.3834 | 1.826% | CZ 2B | 9.772 | 1.8766 | 0.92233 | 1.6046 | 0.099656 | 14.9417 | 1.3805 | 5.6966 | 0 | 1.9154 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 81.741 | 1.826% | CZ 2B | 2.8632 | 0.54984 | 0 | 0.10473 | 0.029199 | 4.3779 | 0.40448 | 1.6691 | 0 | 0.56121 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 23.3145 | 1.826% | CZ 2B | 0 | 0 | 0.0092233 | 0.012471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021694 | 1.826% | CZ 2B | 29.9749 | 5.7562 | 1.0081 | 2.4595 | 0.30569 | 45.8325 | 4.2345 | 17.4737 | 0 | 5.8753 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 246.4503 | 1.826%
CZ 3A | 0.29004 | 0.055753 | 0.01034 | 0.046876 | 0.001416 | 0.3968 | 0.055713 | 0.14535 | 0 | 0.065511 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.3599 | 14.76% | CZ 3A | 9.772 | 1.8784 | 1.034 | 4.6123 | 0.047708 | 13.369 | 1.8771 | 4.8971 | 0 | 2.2072 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 83.2264 | 14.76% | CZ 3A | 2.8632 | 0.55037 | 0 | 0.011215 | 0.013978 | 3.9171 | 0.54998 | 1.4348 | 0 | 0.6467 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 22.7422 | 14.76% | CZ 3A | 0 | 0 | 0.01034 | 0.04574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05608 | 14.76% | CZ 3A | 29.9749 | 5.7618 | 1.1301 | 5.1168 | 0.14634 | 41.0083 | 5.7578 | 15.0214 | 0 | 6.7703 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 244.2176 | 14.76%
CZ 3B | 0.29004 | 0.055718 | 0.010038 | 0.052435 | 0.031372 | 0.39577 | 0.034204 | 0.16528 | 0 | 0.043196 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.3701 | 8.555% | CZ 3B | 9.772 | 1.8772 | 1.0038 | 2.7548 | 1.057 | 13.3341 | 1.1524 | 5.5684 | 0 | 1.4554 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 81.5069 | 8.555% | CZ 3B | 2.8632 | 0.55003 | 0 | 0.37051 | 0.3097 | 3.9069 | 0.33765 | 1.6315 | 0 | 0.42642 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 23.1507 | 8.555% | CZ 3B | 0 | 0 | 0.010038 | 0.014903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024941 | 8.555% | CZ 3B | 29.9749 | 5.7582 | 1.0972 | 5.5077 | 3.2422 | 40.9013 | 3.5348 | 17.0807 | 0 | 4.4642 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 245.0911 | 8.555%
CZ 3C | 0.29004 | 0.055714 | 0.010476 | 0.0087675 | 0.00034596 | 0.30522 | 0.029176 | 0.14183 | 0 | 0.045 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.1786 | 3.506% | CZ 3C | 9.772 | 1.8771 | 1.0476 | 0.78005 | 0.011656 | 10.2832 | 0.983 | 4.7784 | 0 | 1.5161 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 74.5809 | 3.506% | CZ 3C | 2.8632 | 0.54999 | 0 | 0.014396 | 0.0034152 | 3.013 | 0.28802 | 1.4001 | 0 | 0.44422 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 21.3311 | 3.506% | CZ 3C | 0 | 0 | 0.010476 | 0.0073092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017786 | 3.506% | CZ 3C | 29.9749 | 5.7579 | 1.1451 | 0.94961 | 0.035754 | 31.543 | 3.0153 | 14.6573 | 0 | 4.6506 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 225.2591 | 3.506%
CZ 4A | 0.29004 | 0.05565 | 0.011274 | 0.081567 | 0.00096225 | 0.34994 | 0.039986 | 0.1406 | 0 | 0.062017 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.3241 | 31.46% | CZ 4A | 9.772 | 1.875 | 1.1274 | 8.1463 | 0.03242 | 11.7902 | 1.3472 | 4.7369 | 0 | 2.0895 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 84.4485 | 31.46% | CZ 4A | 2.8632 | 0.54936 | 0 | 0.0015544 | 0.009499 | 3.4545 | 0.39473 | 1.3879 | 0 | 0.61221 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 22.0278 | 31.46% | CZ 4A | 0 | 0 | 0.011274 | 0.08141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092684 | 31.46% | CZ 4A | 29.9749 | 5.7513 | 1.2323 | 8.9144 | 0.099446 | 36.1655 | 4.1324 | 14.53 | 0 | 6.4092 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 240.7392 | 31.46%
CZ 4B | 0.29004 | 0.055673 | 0.011008 | 0.078691 | 0.066314 | 0.36472 | 0.022771 | 0.18071 | 0 | 0.039368 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.4014 | 0.05451% | CZ 4B | 9.772 | 1.8757 | 1.1008 | 4.8193 | 2.2342 | 12.2881 | 0.76718 | 6.0883 | 0 | 1.3264 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 83.8037 | 0.05451% | CZ 4B | 2.8632 | 0.54959 | 0 | 0.45404 | 0.65463 | 3.6004 | 0.22478 | 1.7839 | 0 | 0.38863 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 23.2739 | 0.05451% | CZ 4B | 0 | 0 | 0.011008 | 0.032697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043704 | 0.05451% | CZ 4B | 29.9749 | 5.7536 | 1.2031 | 8.3271 | 6.8533 | 37.6928 | 2.3533 | 18.6752 | 0 | 4.0686 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 248.4318 | 0.05451%
CZ 4C | 0.29004 | 0.055606 | 0.011551 | 0.05343 | 0.00052712 | 0.23828 | 0.014469 | 0.1391 | 0 | 0.026164 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.1212 | 4.546% | CZ 4C | 9.772 | 1.8735 | 1.1551 | 5.3121 | 0.01776 | 8.0281 | 0.4875 | 4.6864 | 0 | 0.88152 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 75.7456 | 4.546% | CZ 4C | 2.8632 | 0.54892 | 0 | 0.0046019 | 0.0052036 | 2.3522 | 0.14284 | 1.3731 | 0 | 0.25828 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 20.3032 | 4.546% | CZ 4C | 0 | 0 | 0.011551 | 0.052964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064514 | 4.546% | CZ 4C | 29.9749 | 5.7467 | 1.2625 | 5.8371 | 0.054476 | 24.6256 | 1.4954 | 14.3753 | 0 | 2.704 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 219.6056 | 4.546%
CZ 5A | 0.29004 | 0.055606 | 0.012068 | 0.13554 | 0.0010345 | 0.28055 | 0.024636 | 0.14095 | 0 | 0.037183 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.2697 | 13.22% | CZ 5A | 9.772 | 1.8735 | 1.2068 | 13.5345 | 0.034854 | 9.452 | 0.83003 | 4.7489 | 0 | 1.2528 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 86.237 | 13.22% | CZ 5A | 2.8632 | 0.54892 | 0 | 0.0028859 | 0.010212 | 2.7694 | 0.2432 | 1.3914 | 0 | 0.36706 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 20.9511 | 13.22% | CZ 5A | 0 | 0 | 0.012068 | 0.13525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14731 | 13.22% | CZ 5A | 29.9749 | 5.7467 | 1.319 | 14.8127 | 0.10691 | 28.9934 | 2.546 | 14.567 | 0 | 3.8427 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 235.439 | 13.22%
CZ 5B | 0.29004 | 0.055654 | 0.011841 | 0.11423 | 0.07854 | 0.33442 | 0.016411 | 0.17662 | 0 | 0.036519 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.4063 | 3.582% | CZ 5B | 9.772 | 1.8751 | 1.1841 | 8.5336 | 2.6461 | 11.2672 | 0.55293 | 5.9505 | 0 | 1.2304 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 86.5437 | 3.582% | CZ 5B | 2.8632 | 0.5494 | 0 | 0.43023 | 0.77532 | 3.3013 | 0.16201 | 1.7435 | 0 | 0.36051 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 22.9402 | 3.582% | CZ 5B | 0 | 0 | 0.011841 | 0.070652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082493 | 3.582% | CZ 5B | 29.9749 | 5.7516 | 1.2942 | 12.2264 | 8.1168 | 34.5613 | 1.6961 | 18.2527 | 0 | 3.7741 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 249.178 | 3.582%
CZ 5C | 0.29004 | 0.05559 | 0.012002 | 0.053073 | 0.0005734 | 0.21543 | 0.010345 | 0.13718 | 0 | 0.018919 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.0852 | 0.07377% | CZ 5C | 9.772 | 1.8729 | 1.2002 | 5.293 | 0.019319 | 7.2582 | 0.34854 | 4.6219 | 0 | 0.63743 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 74.5552 | 0.07377% | CZ 5C | 2.8632 | 0.54877 | 0 | 0.0021282 | 0.0056604 | 2.1266 | 0.10212 | 1.3542 | 0 | 0.18677 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 19.9443 | 0.07377% | CZ 5C | 0 | 0 | 0.012002 | 0.052857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064859 | 0.07377% | CZ 5C | 29.9749 | 5.745 | 1.3118 | 5.7996 | 0.059259 | 22.2638 | 1.0691 | 14.1774 | 0 | 1.9553 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 215.8859 | 0.07377%
CZ 6A | 0.29004 | 0.055647 | 0.012663 | 0.19716 | 0.001214 | 0.2852 | 0.026879 | 0.14706 | 0 | 0.039606 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.3475 | 2.328% | CZ 6A | 9.772 | 1.8748 | 1.2663 | 19.7031 | 0.0409 | 9.609 | 0.90561 | 4.9548 | 0 | 1.3344 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 92.9927 | 2.328% | CZ 6A | 2.8632 | 0.54933 | 0 | 0.0018831 | 0.011984 | 2.8154 | 0.26534 | 1.4517 | 0 | 0.39098 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 21.1047 | 2.328% | CZ 6A | 0 | 0 | 0.012663 | 0.19697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20963 | 2.328% | CZ 6A | 29.9749 | 5.7509 | 1.3841 | 21.5482 | 0.12546 | 29.4747 | 2.7779 | 15.1984 | 0 | 4.0932 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 243.8575 | 2.328%
CZ 6B | 0.29004 | 0.055602 | 0.01251 | 0.15006 | 0.044051 | 0.28414 | 0.013288 | 0.15933 | 0 | 0.028969 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.3301 | 0% | CZ 6B | 9.772 | 1.8733 | 1.251 | 13.7907 | 1.4842 | 9.5731 | 0.4477 | 5.3681 | 0 | 0.97602 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 88.0678 | 0% | CZ 6B | 2.8632 | 0.54889 | 0 | 0.18099 | 0.43486 | 2.8049 | 0.13118 | 1.5728 | 0 | 0.28597 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 21.5777 | 0% | CZ 6B | 0 | 0 | 0.01251 | 0.13173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14424 | 0% | CZ 6B | 29.9749 | 5.7463 | 1.3673 | 16.2929 | 4.5526 | 29.3648 | 1.3733 | 16.4661 | 0 | 2.9939 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 241.6619 | 0%
CZ 7 | 0.29004 | 0.055628 | 0.013371 | 0.22641 | 0.001591 | 0.26565 | 0.019079 | 0.14586 | 0 | 0.033395 | 0 | 0.11041 | 0.0081151 | 0 | 0.84214 | 0.33139 | 2.3431 | 0.3244% | CZ 7 | 9.772 | 1.8742 | 1.3371 | 22.6028 | 0.053602 | 8.9501 | 0.64279 | 4.9141 | 0 | 1.1251 | 0 | 3.7199 | 0.27341 | 0 | 28.3732 | 11.1651 | 94.8036 | 0.3244% | CZ 7 | 2.8632 | 0.54915 | 0 | 0.0056716 | 0.015705 | 2.6224 | 0.18834 | 1.4398 | 0 | 0.32966 | 0 | 1.0899 | 0.08011 | 0 | 8.3133 | 3.2714 | 20.7687 | 0.3244% | CZ 7 | 0 | 0 | 0.013371 | 0.22583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23921 | 0.3244% | CZ 7 | 29.9749 | 5.749 | 1.4615 | 24.7431 | 0.16442 | 27.4538 | 1.9717 | 15.0736 | 0 | 3.4513 | 0 | 11.4106 | 0.83867 | 0 | 87.0323 | 34.2481 | 243.5729 | 0.3244%
CZ 8 | 0.29004 | 0.055242 | 0.014332 | 0.31925 | 0.0072753 | 0.23151 | 0.0085734 | 0.1437 | 0 | 0.026069 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.388 | 0% | CZ 8 | 9.772 | 1.8612 | 1.4332 | 31.8412 | 0.24512 | 7.7999 | 0.28885 | 4.8414 | 0 | 0.87831 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 102.4928 | 0% | CZ 8 | 2.8632 | 0.54533 | 0 | 0.012418 | 0.071819 | 2.2854 | 0.084633 | 1.4185 | 0 | 0.25734 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 20.2934 | 0% | CZ 8 | 0 | 0 | 0.014332 | 0.31799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33232 | 0% | CZ 8 | 29.9749 | 5.7091 | 1.5665 | 34.8861 | 0.75188 | 23.9255 | 0.88603 | 14.8505 | 0 | 2.6941 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 248.7743 | 0%
US Weighted | 0.29004 | 0.055673 | 0.010785 | 0.069173 | 0.0063533 | 0.37604 | 0.047071 | 0.14764 | 0 | 0.05818 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.353 | 100% | US Weighted | 9.772 | 1.8757 | 1.0785 | 6.5616 | 0.21405 | 12.6695 | 1.5859 | 4.9744 | 0 | 1.9602 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 84.2235 | 100% | US Weighted | 2.8632 | 0.54958 | 0 | 0.052955 | 0.062718 | 3.7122 | 0.46467 | 1.4575 | 0 | 0.57433 | 0 | 1.0899 | 0.08012 | 0 | 8.3133 | 3.2714 | 22.4919 | 100% | US Weighted | 0 | 0 | 0.010785 | 0.063809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074594 | 100% | US Weighted | 29.9749 | 5.7536 | 1.1788 | 7.5287 | 0.65659 | 38.8626 | 4.8646 | 15.2585 | 0 | 6.0127 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 243.6207 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.29004 | 0.055775 | 0.0085051 | 0.0010533 | 0 | 0.60594 | 0.12345 | 0.16459 | 0 | 0.097812 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.6392 | 3.896% | CZ 1A | 9.772 | 1.8791 | 0.85051 | 0.10533 | 0 | 20.415 | 4.1592 | 5.5452 | 0 | 3.2955 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 89.5536 | 3.896% | CZ 1A | 2.8632 | 0.55059 | 0 | 0 | 0 | 5.9816 | 1.2187 | 1.6247 | 0 | 0.96557 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 25.9591 | 3.896% | CZ 1A | 0 | 0 | 0.0085051 | 0.0010533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095584 | 3.896% | CZ 1A | 29.9749 | 5.7641 | 0.92961 | 0.11513 | 0 | 62.6213 | 12.7581 | 17.0094 | 0 | 10.1086 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 272.8109 | 3.896%
CZ 1B | 0.29004 | 0.055708 | 0.0085465 | 0.010954 | 0.0013618 | 0.63184 | 0.094891 | 0.17435 | 0 | 0.08626 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.646 | 0% | CZ 1B | 9.772 | 1.8769 | 0.85465 | 1.0181 | 0.045882 | 21.2877 | 3.197 | 5.874 | 0 | 2.9062 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 90.3642 | 0% | CZ 1B | 2.8632 | 0.54993 | 0 | 0.01151 | 0.013444 | 6.2373 | 0.93673 | 1.7211 | 0 | 0.85153 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 25.9395 | 0% | CZ 1B | 0 | 0 | 0.0085465 | 0.0097883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018335 | 0% | CZ 1B | 29.9749 | 5.7572 | 0.93414 | 1.1904 | 0.14074 | 65.2982 | 9.8066 | 18.018 | 0 | 8.9146 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 273.5646 | 0%
CZ 2A | 0.29004 | 0.055663 | 0.0091752 | 0.020639 | 0.00047238 | 0.57113 | 0.10666 | 0.15596 | 0 | 0.095261 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.5971 | 11.87% | CZ 2A | 9.772 | 1.8754 | 0.91752 | 2.0422 | 0.015915 | 19.2422 | 3.5935 | 5.2547 | 0 | 3.2095 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 89.4546 | 11.87% | CZ 2A | 2.8632 | 0.54949 | 0 | 0.0032369 | 0.0046632 | 5.638 | 1.0529 | 1.5396 | 0 | 0.94038 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 25.3462 | 11.87% | CZ 2A | 0 | 0 | 0.0091752 | 0.020311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029487 | 11.87% | CZ 2A | 29.9749 | 5.7526 | 1.0028 | 2.2539 | 0.048819 | 59.024 | 11.0227 | 16.1182 | 0 | 9.8449 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 268.5727 | 11.87%
CZ 2B | 0.29004 | 0.055698 | 0.0092223 | 0.035117 | 0.0033845 | 0.46004 | 0.044374 | 0.17164 | 0 | 0.063345 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.4249 | 1.826% | CZ 2B | 9.772 | 1.8766 | 0.92223 | 2.7186 | 0.11403 | 15.4996 | 1.495 | 5.7828 | 0 | 2.1342 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 83.8468 | 1.826% | CZ 2B | 2.8632 | 0.54984 | 0 | 0.11807 | 0.033411 | 4.5414 | 0.43804 | 1.6944 | 0 | 0.62532 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 23.6184 | 1.826% | CZ 2B | 0 | 0 | 0.0092223 | 0.023157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032379 | 1.826% | CZ 2B | 29.9749 | 5.7562 | 1.008 | 3.7671 | 0.34978 | 47.5439 | 4.5859 | 17.7383 | 0 | 6.5464 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 250.8003 | 1.826%
CZ 3A | 0.29004 | 0.055753 | 0.010341 | 0.061211 | 0.0016954 | 0.4024 | 0.058118 | 0.14758 | 0 | 0.067365 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.3866 | 14.76% | CZ 3A | 9.772 | 1.8784 | 1.0341 | 6.0409 | 0.05712 | 13.5575 | 1.9581 | 4.9724 | 0 | 2.2696 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 85.0718 | 14.76% | CZ 3A | 2.8632 | 0.55037 | 0 | 0.011934 | 0.016736 | 3.9723 | 0.57372 | 1.4569 | 0 | 0.66501 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 22.865 | 14.76% | CZ 3A | 0 | 0 | 0.010341 | 0.060002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070343 | 14.76% | CZ 3A | 29.9749 | 5.7618 | 1.1302 | 6.6832 | 0.17521 | 41.5865 | 6.0063 | 15.2523 | 0 | 6.9619 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 247.0621 | 14.76%
CZ 3B | 0.29004 | 0.055718 | 0.010039 | 0.056705 | 0.03173 | 0.39901 | 0.035032 | 0.16622 | 0 | 0.044624 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.3812 | 8.555% | CZ 3B | 9.772 | 1.8772 | 1.0039 | 3.2341 | 1.069 | 13.4434 | 1.1803 | 5.6001 | 0 | 1.5034 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 82.2152 | 8.555% | CZ 3B | 2.8632 | 0.55003 | 0 | 0.36271 | 0.31323 | 3.9389 | 0.34582 | 1.6408 | 0 | 0.44051 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 23.21 | 8.555% | CZ 3B | 0 | 0 | 0.010039 | 0.019962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030001 | 8.555% | CZ 3B | 29.9749 | 5.7582 | 1.0973 | 5.9791 | 3.2792 | 41.2364 | 3.6204 | 17.1778 | 0 | 4.6117 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 246.2648 | 8.555%
CZ 3C | 0.29004 | 0.055714 | 0.010477 | 0.019149 | 0.00045996 | 0.31375 | 0.030674 | 0.14823 | 0 | 0.046907 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.2075 | 3.506% | CZ 3C | 9.772 | 1.8771 | 1.0477 | 1.7986 | 0.015497 | 10.5708 | 1.0334 | 4.994 | 0 | 1.5804 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 76.2212 | 3.506% | CZ 3C | 2.8632 | 0.54999 | 0 | 0.01731 | 0.0045406 | 3.0972 | 0.3028 | 1.4632 | 0 | 0.46305 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 21.5162 | 3.506% | CZ 3C | 0 | 0 | 0.010477 | 0.017395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027872 | 3.506% | CZ 3C | 29.9749 | 5.7579 | 1.1451 | 2.0825 | 0.047536 | 32.4251 | 3.17 | 15.3188 | 0 | 4.8477 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 228.2992 | 3.506%
CZ 4A | 0.29004 | 0.05565 | 0.011275 | 0.11169 | 0.0010644 | 0.35171 | 0.041274 | 0.14378 | 0 | 0.063873 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.3624 | 31.46% | CZ 4A | 9.772 | 1.875 | 1.1275 | 11.1579 | 0.035862 | 11.8496 | 1.3906 | 4.8442 | 0 | 2.152 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 87.7363 | 31.46% | CZ 4A | 2.8632 | 0.54936 | 0 | 0.001677 | 0.010507 | 3.4719 | 0.40745 | 1.4193 | 0 | 0.63053 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 22.1088 | 31.46% | CZ 4A | 0 | 0 | 0.011275 | 0.11152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1228 | 31.46% | CZ 4A | 29.9749 | 5.7513 | 1.2323 | 12.2069 | 0.11 | 36.3478 | 4.2655 | 14.8591 | 0 | 6.601 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 244.8786 | 31.46%
CZ 4B | 0.29004 | 0.055673 | 0.011007 | 0.09508 | 0.06674 | 0.3581 | 0.022963 | 0.18227 | 0 | 0.040449 | 0 | 0.11041 | 0.0081151 | 0 | 0.84214 | 0.33139 | 2.4144 | 0.05451% | CZ 4B | 9.772 | 1.8757 | 1.1007 | 6.4841 | 2.2486 | 12.0651 | 0.77367 | 6.1409 | 0 | 1.3628 | 0 | 3.7199 | 0.27341 | 0 | 28.3732 | 11.1651 | 85.3551 | 0.05451% | CZ 4B | 2.8632 | 0.54959 | 0 | 0.45018 | 0.65884 | 3.5351 | 0.22668 | 1.7993 | 0 | 0.3993 | 0 | 1.0899 | 0.08011 | 0 | 8.3133 | 3.2714 | 23.2369 | 0.05451% | CZ 4B | 0 | 0 | 0.011007 | 0.049476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060483 | 0.05451% | CZ 4B | 29.9749 | 5.7536 | 1.2031 | 10.1207 | 6.8974 | 37.0086 | 2.3732 | 18.8366 | 0 | 4.1803 | 0 | 11.4106 | 0.83867 | 0 | 87.0323 | 34.2481 | 249.8779 | 0.05451%
CZ 4C | 0.29004 | 0.055606 | 0.011551 | 0.075839 | 0.00061234 | 0.23803 | 0.014547 | 0.14161 | 0 | 0.026864 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.1468 | 4.546% | CZ 4C | 9.772 | 1.8735 | 1.1551 | 7.5487 | 0.020631 | 8.0197 | 0.4901 | 4.7711 | 0 | 0.9051 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 78.0875 | 4.546% | CZ 4C | 2.8632 | 0.54892 | 0 | 0.005237 | 0.0060448 | 2.3498 | 0.1436 | 1.3979 | 0 | 0.26519 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 20.3347 | 4.546% | CZ 4C | 0 | 0 | 0.011551 | 0.075309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08686 | 4.546% | CZ 4C | 29.9749 | 5.7467 | 1.2625 | 8.2861 | 0.063284 | 24.5997 | 1.5033 | 14.6348 | 0 | 2.7763 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 222.3774 | 4.546%
CZ 5A | 0.29004 | 0.055606 | 0.012068 | 0.17498 | 0.0011982 | 0.28132 | 0.024997 | 0.14486 | 0 | 0.038806 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.3159 | 13.22% | CZ 5A | 9.772 | 1.8735 | 1.2068 | 17.4804 | 0.040368 | 9.4782 | 0.84218 | 4.8807 | 0 | 1.3074 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 90.4133 | 13.22% | CZ 5A | 2.8632 | 0.54892 | 0 | 0.0025572 | 0.011828 | 2.7771 | 0.24676 | 1.43 | 0 | 0.38308 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 21.0183 | 13.22% | CZ 5A | 0 | 0 | 0.012068 | 0.17472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18679 | 13.22% | CZ 5A | 29.9749 | 5.7467 | 1.3191 | 19.1234 | 0.12383 | 29.0737 | 2.5833 | 14.9711 | 0 | 4.0104 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 240.4562 | 13.22%
CZ 5B | 0.29004 | 0.055654 | 0.011842 | 0.14368 | 0.078753 | 0.3341 | 0.016429 | 0.17856 | 0 | 0.037359 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.4385 | 3.582% | CZ 5B | 9.772 | 1.8751 | 1.1842 | 11.5412 | 2.6533 | 11.2563 | 0.55352 | 6.016 | 0 | 1.2587 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 89.642 | 3.582% | CZ 5B | 2.8632 | 0.5494 | 0 | 0.42078 | 0.77742 | 3.2981 | 0.16218 | 1.7627 | 0 | 0.3688 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 22.9573 | 3.582% | CZ 5B | 0 | 0 | 0.011842 | 0.10105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11289 | 3.582% | CZ 5B | 29.9749 | 5.7516 | 1.2943 | 15.45 | 8.1388 | 34.5278 | 1.6979 | 18.4535 | 0 | 3.8609 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 252.6796 | 3.582%
CZ 5C | 0.29004 | 0.05559 | 0.012003 | 0.077928 | 0.00065072 | 0.21478 | 0.01033 | 0.13939 | 0 | 0.019322 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.1121 | 0.07377% | CZ 5C | 9.772 | 1.8729 | 1.2003 | 7.7788 | 0.021924 | 7.2362 | 0.34804 | 4.6964 | 0 | 0.65099 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 77.1093 | 0.07377% | CZ 5C | 2.8632 | 0.54877 | 0 | 0.0020837 | 0.0064237 | 2.1202 | 0.10198 | 1.376 | 0 | 0.19074 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 19.9642 | 0.07377% | CZ 5C | 0 | 0 | 0.012003 | 0.077717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08972 | 0.07377% | CZ 5C | 29.9749 | 5.745 | 1.3119 | 8.5163 | 0.06725 | 22.1963 | 1.0676 | 14.4058 | 0 | 1.9968 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 218.8118 | 0.07377%
CZ 6A | 0.29004 | 0.055647 | 0.012663 | 0.24462 | 0.0014194 | 0.28643 | 0.027531 | 0.15175 | 0 | 0.041561 | 0 | 0.11041 | 0.0081162 | 0 | 0.84214 | 0.33139 | 2.4037 | 2.328% | CZ 6A | 9.772 | 1.8748 | 1.2663 | 24.4494 | 0.047822 | 9.6502 | 0.92755 | 5.1129 | 0 | 1.4003 | 0 | 3.7199 | 0.27345 | 0 | 28.3732 | 11.1651 | 98.033 | 2.328% | CZ 6A | 2.8632 | 0.54933 | 0 | 0.0018107 | 0.014012 | 2.8275 | 0.27177 | 1.4981 | 0 | 0.41028 | 0 | 1.0899 | 0.080121 | 0 | 8.3133 | 3.2714 | 21.1908 | 2.328% | CZ 6A | 0 | 0 | 0.012663 | 0.24443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2571 | 2.328% | CZ 6A | 29.9749 | 5.7509 | 1.3841 | 26.7354 | 0.14669 | 29.6012 | 2.8452 | 15.6833 | 0 | 4.2952 | 0 | 11.4106 | 0.83878 | 0 | 87.0323 | 34.2481 | 249.9467 | 2.328%
CZ 6B | 0.29004 | 0.055602 | 0.01251 | 0.18714 | 0.044884 | 0.283 | 0.013273 | 0.16264 | 0 | 0.029808 | 0 | 0.11041 | 0.0081168 | 0 | 0.84214 | 0.33139 | 2.371 | 0% | CZ 6B | 9.772 | 1.8733 | 1.251 | 17.5337 | 1.5122 | 9.5347 | 0.44719 | 5.4796 | 0 | 1.0043 | 0 | 3.7199 | 0.27347 | 0 | 28.3732 | 11.1651 | 91.9397 | 0% | CZ 6B | 2.8632 | 0.54889 | 0 | 0.17579 | 0.44308 | 2.7937 | 0.13103 | 1.6055 | 0 | 0.29425 | 0 | 1.0899 | 0.080126 | 0 | 8.3133 | 3.2714 | 21.6102 | 0% | CZ 6B | 0 | 0 | 0.01251 | 0.16934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18185 | 0% | CZ 6B | 29.9749 | 5.7463 | 1.3674 | 20.3489 | 4.6386 | 29.2468 | 1.3717 | 16.8081 | 0 | 3.0805 | 0 | 11.4106 | 0.83884 | 0 | 87.0323 | 34.2481 | 246.1131 | 0%
CZ 7 | 0.29004 | 0.055628 | 0.013371 | 0.28014 | 0.0019347 | 0.27007 | 0.019961 | 0.15505 | 0 | 0.036044 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.4143 | 0.3244% | CZ 7 | 9.772 | 1.8742 | 1.3371 | 27.9656 | 0.065182 | 9.0992 | 0.67251 | 5.2239 | 0 | 1.2144 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 100.7557 | 0.3244% | CZ 7 | 2.8632 | 0.54915 | 0 | 0.007226 | 0.019098 | 2.6661 | 0.19705 | 1.5306 | 0 | 0.35581 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 20.943 | 0.3244% | CZ 7 | 0 | 0 | 0.013371 | 0.27941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29278 | 0.3244% | CZ 7 | 29.9749 | 5.749 | 1.4615 | 30.6151 | 0.19994 | 27.911 | 2.0629 | 16.0237 | 0 | 3.725 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 251.2526 | 0.3244%
CZ 8 | 0.29004 | 0.055242 | 0.014332 | 0.37222 | 0.0079638 | 0.23247 | 0.0086941 | 0.15148 | 0 | 0.027768 | 0 | 0.11041 | 0.0081157 | 0 | 0.84214 | 0.33139 | 2.4523 | 0% | CZ 8 | 9.772 | 1.8612 | 1.4332 | 37.1341 | 0.26832 | 7.8323 | 0.29292 | 5.1038 | 0 | 0.93556 | 0 | 3.7199 | 0.27343 | 0 | 28.3732 | 11.1651 | 108.1651 | 0% | CZ 8 | 2.8632 | 0.54533 | 0 | 0.013015 | 0.078616 | 2.2949 | 0.085826 | 1.4954 | 0 | 0.27412 | 0 | 1.0899 | 0.080115 | 0 | 8.3133 | 3.2714 | 20.4051 | 0% | CZ 8 | 0 | 0 | 0.014332 | 0.3709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38523 | 0% | CZ 8 | 29.9749 | 5.7091 | 1.5665 | 40.6753 | 0.82304 | 24.0248 | 0.89851 | 15.6554 | 0 | 2.8697 | 0 | 11.4106 | 0.83873 | 0 | 87.0323 | 34.2481 | 255.727 | 0%
US Weighted | 0.29004 | 0.055673 | 0.010786 | 0.091268 | 0.0065171 | 0.38285 | 0.049194 | 0.15071 | 0 | 0.060583 | 0 | 0.11041 | 0.0081161 | 0 | 0.84214 | 0.33139 | 2.3897 | 100% | US Weighted | 9.772 | 1.8757 | 1.0786 | 8.7746 | 0.21957 | 12.8987 | 1.6574 | 5.0778 | 0 | 2.0411 | 0 | 3.7199 | 0.27344 | 0 | 28.3732 | 11.1651 | 86.9272 | 100% | US Weighted | 2.8632 | 0.54958 | 0 | 0.052428 | 0.064335 | 3.7793 | 0.48563 | 1.4878 | 0 | 0.59805 | 0 | 1.0899 | 0.080119 | 0 | 8.3133 | 3.2714 | 22.6351 | 100% | US Weighted | 0 | 0 | 0.010786 | 0.085957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096743 | 100% | US Weighted | 29.9749 | 5.7536 | 1.1789 | 9.9439 | 0.67352 | 39.5658 | 5.0841 | 15.5756 | 0 | 6.261 | 0 | 11.4106 | 0.83877 | 0 | 87.0323 | 34.2481 | 247.5411 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 498588 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 498588 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.11161 | 0.036453 | 0.00036081 | 0.0010533 | 0 | 0.15975 | 0.075743 | 0.025858 | -0.0065179 | 0.055827 | 0 | 0.0031289 | 0.0050144 | 0 | 0 | 0.030306 | 0.49858 | 3.896% | CZ 1A | 3.7602 | 1.2282 | 0.036081 | 0.10533 | 0 | 5.3821 | 2.5519 | 0.87121 | -0.2196 | 1.8809 | 0 | 0.10542 | 0.16895 | 0 | 0 | 1.021 | 16.8917 | 3.896% | CZ 1A | 1.1018 | 0.35986 | 0 | 0 | 0 | 1.577 | 0.74771 | 0.25527 | -0.064343 | 0.5511 | 0 | 0.030887 | 0.049501 | 0 | 0 | 0.29917 | 4.9078 | 3.896% | CZ 1A | 0 | 0 | 0.00036081 | 0.0010533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014142 | 3.896% | CZ 1A | 11.5342 | 3.7673 | 0.039437 | 0.11513 | 0 | 16.5091 | 7.8277 | 2.6724 | -0.6736 | 5.7695 | 0 | 0.32336 | 0.51822 | 0 | 0 | 3.132 | 51.5348 | 3.896%
CZ 1B | 0.11155 | 0.036434 | 0.00036784 | 0.0092395 | 0.000491 | 0.10844 | 0.051806 | 0.03267 | 0 | 0.040522 | 0 | 0.0031289 | 0.0050127 | 0 | 0 | 0.030306 | 0.42997 | 0% | CZ 1B | 3.7584 | 1.2275 | 0.036784 | 0.85352 | 0.016543 | 3.6535 | 1.7454 | 1.1007 | 0 | 1.3653 | 0 | 0.10542 | 0.16889 | 0 | 0 | 1.021 | 15.053 | 0% | CZ 1B | 1.1012 | 0.35967 | 0 | 0.010485 | 0.004847 | 1.0705 | 0.51142 | 0.32251 | 0 | 0.40002 | 0 | 0.030887 | 0.049484 | 0 | 0 | 0.29917 | 4.1602 | 0% | CZ 1B | 0 | 0 | 0.00036784 | 0.0081774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085452 | 0% | CZ 1B | 11.5285 | 3.7653 | 0.040205 | 1.0036 | 0.050743 | 11.2068 | 5.354 | 3.3764 | 0 | 4.1878 | 0 | 0.32336 | 0.51805 | 0 | 0 | 3.132 | 44.4868 | 0%
CZ 2A | 0.11169 | 0.036349 | 0.00035169 | 0.017812 | -0.023233 | 0.21981 | 0.066597 | 0.026139 | -0.0034647 | 0.05841 | 0 | 0.0031289 | 0.0050139 | 0 | 0 | 0.030306 | 0.54891 | 11.87% | CZ 2A | 3.763 | 1.2247 | 0.035169 | 1.7654 | -0.78278 | 7.4058 | 2.2438 | 0.88066 | -0.11673 | 1.9679 | 0 | 0.10542 | 0.16893 | 0 | 0 | 1.021 | 19.6822 | 11.87% | CZ 2A | 1.1026 | 0.35882 | 0 | 0.0023622 | -0.22935 | 2.1699 | 0.65742 | 0.25803 | -0.034202 | 0.57661 | 0 | 0.030887 | 0.049495 | 0 | 0 | 0.29917 | 5.2417 | 11.87% | CZ 2A | 0 | 0 | 0.00035169 | 0.017573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017925 | 11.87% | CZ 2A | 11.5426 | 3.7565 | 0.038439 | 1.9455 | -2.4011 | 22.7167 | 6.8826 | 2.7014 | -0.35806 | 6.0365 | 0 | 0.32336 | 0.51817 | 0 | 0 | 3.132 | 56.8345 | 11.87%
CZ 2B | 0.1116 | 0.036378 | 0.00035682 | 0.029771 | -0.09641 | 0.13752 | 0.027457 | 0.025903 | 0 | 0.033193 | 0 | 0.0031289 | 0.0050133 | 0 | 0 | 0.030306 | 0.34421 | 1.826% | CZ 2B | 3.7599 | 1.2256 | 0.035682 | 2.393 | -3.2482 | 4.6332 | 0.92508 | 0.87271 | 0 | 1.1183 | 0 | 0.10542 | 0.16891 | 0 | 0 | 1.021 | 13.0107 | 1.826% | CZ 2B | 1.1017 | 0.35911 | 0 | 0.086957 | -0.95173 | 1.3575 | 0.27105 | 0.25571 | 0 | 0.32767 | 0 | 0.030887 | 0.04949 | 0 | 0 | 0.29917 | 3.1875 | 1.826% | CZ 2B | 0 | 0 | 0.00035682 | 0.020962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021319 | 1.826% | CZ 2B | 11.5332 | 3.7596 | 0.039 | 3.2015 | -9.9637 | 14.212 | 2.8376 | 2.677 | 0 | 3.4304 | 0 | 0.32336 | 0.51811 | 0 | 0 | 3.132 | 35.7 | 1.826%
CZ 3A | 0.11121 | 0.036239 | 0.0003475 | 0.042169 | -0.061621 | 0.16058 | 0.036178 | 0.018369 | -0.0020075 | 0.040689 | 0 | 0.0031289 | 0.0050127 | 0 | 0 | 0.030306 | 0.4206 | 14.76% | CZ 3A | 3.7469 | 1.221 | 0.03475 | 4.1468 | -2.0761 | 5.4101 | 1.2189 | 0.61889 | -0.067635 | 1.3709 | 0 | 0.10542 | 0.16889 | 0 | 0 | 1.021 | 16.9198 | 14.76% | CZ 3A | 1.0979 | 0.35774 | 0 | 0.010441 | -0.6083 | 1.5851 | 0.35714 | 0.18133 | -0.019817 | 0.40167 | 0 | 0.030887 | 0.049484 | 0 | 0 | 0.29917 | 3.7427 | 14.76% | CZ 3A | 0 | 0 | 0.0003475 | 0.041112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041459 | 14.76% | CZ 3A | 11.4934 | 3.7452 | 0.037982 | 4.6028 | -6.3683 | 16.5949 | 3.7389 | 1.8984 | -0.20746 | 4.2051 | 0 | 0.32336 | 0.51805 | 0 | 0 | 3.132 | 43.7143 | 14.76%
CZ 3B | 0.11151 | 0.036535 | 0.00034864 | 0.048466 | -0.070224 | 0.12137 | 0.02057 | 0.019366 | 0 | 0.019611 | 0 | 0.0031289 | 0.0050156 | 0 | 0 | 0.030306 | 0.346 | 8.555% | CZ 3B | 3.7569 | 1.2309 | 0.034864 | 2.5002 | -2.366 | 4.0893 | 0.69305 | 0.65247 | 0 | 0.66074 | 0 | 0.10542 | 0.16898 | 0 | 0 | 1.021 | 12.5478 | 8.555% | CZ 3B | 1.1008 | 0.36066 | 0 | 0.34933 | -0.69323 | 1.1982 | 0.20306 | 0.19117 | 0 | 0.1936 | 0 | 0.030887 | 0.049512 | 0 | 0 | 0.29917 | 3.2831 | 8.555% | CZ 3B | 0 | 0 | 0.00034864 | 0.013079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013428 | 8.555% | CZ 3B | 11.524 | 3.7757 | 0.038107 | 5.0867 | -7.2574 | 12.5435 | 2.1259 | 2.0014 | 0 | 2.0268 | 0 | 0.32336 | 0.51834 | 0 | 0 | 3.132 | 35.8382 | 8.555%
CZ 3C | 0.11128 | 0.03653 | 0.00035473 | 0.017964 | -0.031521 | 0.14464 | 0.0185 | 0.023114 | 0 | 0.027155 | 0 | 0.0031289 | 0.0050139 | 0 | 0 | 0.030306 | 0.38646 | 3.506% | CZ 3C | 3.7493 | 1.2307 | 0.035473 | 1.6994 | -1.062 | 4.873 | 0.62328 | 0.77876 | 0 | 0.91489 | 0 | 0.10542 | 0.16893 | 0 | 0 | 1.021 | 14.1382 | 3.506% | CZ 3C | 1.0985 | 0.36061 | 0 | 0.014446 | -0.31116 | 1.4278 | 0.18262 | 0.22818 | 0 | 0.26806 | 0 | 0.030887 | 0.049495 | 0 | 0 | 0.29917 | 3.6486 | 3.506% | CZ 3C | 0 | 0 | 0.00035473 | 0.016501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016855 | 3.506% | CZ 3C | 11.5006 | 3.7752 | 0.038772 | 1.9547 | -3.2576 | 14.9476 | 1.9119 | 2.3888 | 0 | 2.8063 | 0 | 0.32336 | 0.51817 | 0 | 0 | 3.132 | 40.0399 | 3.506%
CZ 4A | 0.11111 | 0.036223 | 0.00034788 | 0.071941 | -0.084546 | 0.1663 | 0.025358 | 0.014281 | -0.0013534 | 0.042396 | 0 | 0.0031289 | 0.0050127 | 0 | 0 | 0.030306 | 0.4205 | 31.46% | CZ 4A | 3.7434 | 1.2204 | 0.034788 | 7.1986 | -2.8485 | 5.603 | 0.85435 | 0.48117 | -0.045597 | 1.4284 | 0 | 0.10542 | 0.16889 | 0 | 0 | 1.021 | 18.9653 | 31.46% | CZ 4A | 1.0968 | 0.35758 | 0 | -0.00066298 | -0.83461 | 1.6417 | 0.25032 | 0.14098 | -0.01336 | 0.41852 | 0 | 0.030887 | 0.049484 | 0 | 0 | 0.29917 | 3.4368 | 31.46% | CZ 4A | 0 | 0 | 0.00034788 | 0.072008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072356 | 31.46% | CZ 4A | 11.4824 | 3.7435 | 0.038024 | 7.8636 | -8.7375 | 17.1868 | 2.6206 | 1.4759 | -0.13987 | 4.3815 | 0 | 0.32336 | 0.51805 | 0 | 0 | 3.132 | 43.8885 | 31.46%
CZ 4B | 0.11174 | 0.036422 | 0.00034807 | 0.08007 | -0.060432 | 0.15876 | 0.013863 | 0.014058 | 0 | 0.022582 | 0 | 0.0031289 | 0.0050122 | 0 | 0 | 0.030306 | 0.41586 | 0.05451% | CZ 4B | 3.7648 | 1.2271 | 0.034807 | 5.1191 | -2.0361 | 5.3487 | 0.46706 | 0.47365 | 0 | 0.76081 | 0 | 0.10542 | 0.16887 | 0 | 0 | 1.021 | 16.4554 | 0.05451% | CZ 4B | 1.1031 | 0.35954 | 0 | 0.42994 | -0.59657 | 1.5672 | 0.13685 | 0.13878 | 0 | 0.22292 | 0 | 0.030887 | 0.049479 | 0 | 0 | 0.29917 | 3.7413 | 0.05451% | CZ 4B | 0 | 0 | 0.00034807 | 0.036517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036865 | 0.05451% | CZ 4B | 11.5483 | 3.7641 | 0.038044 | 8.4924 | -6.2455 | 16.4068 | 1.4327 | 1.4529 | 0 | 2.3337 | 0 | 0.32336 | 0.51799 | 0 | 0 | 3.132 | 43.1968 | 0.05451%
CZ 4C | 0.11059 | 0.035908 | 0.00034446 | 0.055089 | -0.078952 | 0.14769 | 0.0094058 | 0.014162 | 0 | 0.014539 | 0 | 0.0031289 | 0.0050127 | 0 | 0 | 0.030306 | 0.34723 | 4.546% | CZ 4C | 3.726 | 1.2098 | 0.034446 | 5.5018 | -2.66 | 4.976 | 0.3169 | 0.47715 | 0 | 0.48984 | 0 | 0.10542 | 0.16889 | 0 | 0 | 1.021 | 15.3672 | 4.546% | CZ 4C | 1.0917 | 0.35447 | 0 | 0.001053 | -0.77939 | 1.458 | 0.092851 | 0.13981 | 0 | 0.14352 | 0 | 0.030887 | 0.049484 | 0 | 0 | 0.29917 | 2.8815 | 4.546% | CZ 4C | 0 | 0 | 0.00034446 | 0.054982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055327 | 4.546% | CZ 4C | 11.4292 | 3.711 | 0.03765 | 6.0206 | -8.1594 | 15.2633 | 0.97206 | 1.4636 | 0 | 1.5025 | 0 | 0.32336 | 0.51805 | 0 | 0 | 3.132 | 36.2139 | 4.546%
CZ 5A | 0.11128 | 0.036114 | 0.00034598 | 0.10379 | -0.099446 | 0.14247 | 0.015303 | 0.016774 | -0.00036853 | 0.021744 | 0 | 0.0031289 | 0.0050144 | 0 | 0 | 0.030306 | 0.38645 | 13.22% | CZ 5A | 3.7491 | 1.2167 | 0.034598 | 10.3734 | -3.3505 | 4.8001 | 0.51558 | 0.56515 | -0.012417 | 0.7326 | 0 | 0.10542 | 0.16895 | 0 | 0 | 1.021 | 19.9197 | 13.22% | CZ 5A | 1.0985 | 0.3565 | 0 | 0.00080227 | -0.98169 | 1.4064 | 0.15107 | 0.16559 | -0.0036381 | 0.21465 | 0 | 0.030887 | 0.049501 | 0 | 0 | 0.29917 | 2.7878 | 13.22% | CZ 5A | 0 | 0 | 0.00034598 | 0.10371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10405 | 13.22% | CZ 5A | 11.5002 | 3.7322 | 0.037816 | 11.3435 | -10.2774 | 14.7238 | 1.5815 | 1.7336 | -0.038087 | 2.2472 | 0 | 0.32336 | 0.51822 | 0 | 0 | 3.132 | 40.5579 | 13.22%
CZ 5B | 0.11136 | 0.036273 | 0.00034636 | 0.10656 | -0.063115 | 0.17566 | 0.010369 | 0.013802 | 0 | 0.021157 | 0 | 0.0031289 | 0.0050122 | 0 | 0 | 0.030306 | 0.45085 | 3.582% | CZ 5B | 3.7519 | 1.2221 | 0.034636 | 7.9636 | -2.1265 | 5.9182 | 0.34936 | 0.46502 | 0 | 0.7128 | 0 | 0.10542 | 0.16887 | 0 | 0 | 1.021 | 19.5864 | 3.582% | CZ 5B | 1.0993 | 0.35807 | 0 | 0.40077 | -0.62305 | 1.734 | 0.10236 | 0.13625 | 0 | 0.20885 | 0 | 0.030887 | 0.049479 | 0 | 0 | 0.29917 | 3.7961 | 3.582% | CZ 5B | 0 | 0 | 0.00034636 | 0.065958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066304 | 3.582% | CZ 5B | 11.5087 | 3.7487 | 0.037857 | 11.4048 | -6.5228 | 18.1534 | 1.0716 | 1.4264 | 0 | 2.1865 | 0 | 0.32336 | 0.51799 | 0 | 0 | 3.132 | 46.9885 | 3.582%
CZ 5C | 0.11042 | 0.03587 | 0.00034674 | 0.055727 | -0.088672 | 0.14847 | 0.0073684 | 0.010965 | 0 | 0.009298 | 0 | 0.0031289 | 0.0050127 | 0 | 0 | 0.030306 | 0.32824 | 0.07377% | CZ 5C | 3.7201 | 1.2085 | 0.034674 | 5.6 | -2.9875 | 5.0024 | 0.24826 | 0.36944 | 0 | 0.31327 | 0 | 0.10542 | 0.16889 | 0 | 0 | 1.021 | 14.8045 | 0.07377% | CZ 5C | 1.09 | 0.3541 | 0 | -0.0040503 | -0.87534 | 1.4657 | 0.072739 | 0.10824 | 0 | 0.091787 | 0 | 0.030887 | 0.049484 | 0 | 0 | 0.29917 | 2.6827 | 0.07377% | CZ 5C | 0 | 0 | 0.00034674 | 0.056138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056484 | 0.07377% | CZ 5C | 11.4112 | 3.7071 | 0.037899 | 6.0935 | -9.164 | 15.3444 | 0.7615 | 1.1332 | 0 | 0.96092 | 0 | 0.32336 | 0.51805 | 0 | 0 | 3.132 | 34.259 | 0.07377%
CZ 6A | 0.1112 | 0.036105 | 0.00034712 | 0.13645 | -0.10292 | 0.14179 | 0.016955 | 0.019223 | -0.00047238 | 0.023464 | 0 | 0.0031289 | 0.0050139 | 0 | 0 | 0.030306 | 0.42059 | 2.328% | CZ 6A | 3.7466 | 1.2164 | 0.034712 | 13.6417 | -3.4677 | 4.7771 | 0.57126 | 0.64766 | -0.015915 | 0.79055 | 0 | 0.10542 | 0.16893 | 0 | 0 | 1.021 | 23.2378 | 2.328% | CZ 6A | 1.0978 | 0.35642 | 0 | 0.00051256 | -1.016 | 1.3997 | 0.16738 | 0.18976 | -0.0046632 | 0.23163 | 0 | 0.030887 | 0.049495 | 0 | 0 | 0.29917 | 2.802 | 2.328% | CZ 6A | 0 | 0 | 0.00034712 | 0.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13675 | 2.328% | CZ 6A | 11.4924 | 3.7313 | 0.037941 | 14.9139 | -10.6369 | 14.6533 | 1.7523 | 1.9866 | -0.048819 | 2.425 | 0 | 0.32336 | 0.51817 | 0 | 0 | 3.132 | 44.2805 | 2.328%
CZ 6B | 0.11112 | 0.035907 | 0.00034693 | 0.11727 | -0.10642 | 0.16939 | 0.0088465 | 0.0056234 | 0 | 0.015994 | 0 | 0.0031289 | 0.0050139 | 0 | 0 | 0.030306 | 0.39653 | 0% | CZ 6B | 3.7439 | 1.2098 | 0.034693 | 10.6472 | -3.5856 | 5.7072 | 0.29805 | 0.18946 | 0 | 0.53887 | 0 | 0.10542 | 0.16893 | 0 | 0 | 1.021 | 20.079 | 0% | CZ 6B | 1.097 | 0.35446 | 0 | 0.16075 | -1.0506 | 1.6722 | 0.08733 | 0.055512 | 0 | 0.15789 | 0 | 0.030887 | 0.049495 | 0 | 0 | 0.29917 | 2.9141 | 0% | CZ 6B | 0 | 0 | 0.00034693 | 0.10099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10133 | 0% | CZ 6B | 11.4842 | 3.7109 | 0.03792 | 12.7207 | -10.9986 | 17.5064 | 0.91426 | 0.58116 | 0 | 1.653 | 0 | 0.32336 | 0.51817 | 0 | 0 | 3.132 | 41.5833 | 0%
CZ 7 | 0.11136 | 0.035869 | 0.00034997 | 0.16242 | -0.11642 | 0.14572 | 0.012389 | 0.018353 | -0.00090243 | 0.019572 | 0 | 0.0031289 | 0.0050133 | 0 | 0 | 0.030306 | 0.42715 | 0.3244% | CZ 7 | 3.7518 | 1.2085 | 0.034997 | 16.2084 | -3.9225 | 4.9094 | 0.41741 | 0.61834 | -0.030404 | 0.65943 | 0 | 0.10542 | 0.16891 | 0 | 0 | 1.021 | 25.1507 | 0.3244% | CZ 7 | 1.0993 | 0.35409 | 0 | 0.0050587 | -1.1493 | 1.4385 | 0.1223 | 0.18117 | -0.0089085 | 0.19321 | 0 | 0.030887 | 0.04949 | 0 | 0 | 0.29917 | 2.6149 | 0.3244% | CZ 7 | 0 | 0 | 0.00034997 | 0.16191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16226 | 0.3244% | CZ 7 | 11.5083 | 3.707 | 0.038252 | 17.7499 | -12.0321 | 15.0593 | 1.2804 | 1.8967 | -0.093263 | 2.0227 | 0 | 0.32336 | 0.51811 | 0 | 0 | 3.132 | 45.1106 | 0.3244%
CZ 8 | 0.10741 | 0.033967 | 0.000361 | 0.19903 | -0.13477 | 0.15006 | 0.0057944 | 0.01584 | -0.00067499 | 0.015556 | 0 | 0.0031289 | 0.0050111 | 0 | 0 | 0.030306 | 0.43102 | 0% | CZ 8 | 3.6189 | 1.1444 | 0.0361 | 19.829 | -4.5406 | 5.0558 | 0.19522 | 0.53368 | -0.022742 | 0.52412 | 0 | 0.10542 | 0.16883 | 0 | 0 | 1.021 | 27.6692 | 0% | CZ 8 | 1.0603 | 0.33531 | 0 | 0.011026 | -1.3304 | 1.4813 | 0.0572 | 0.15637 | -0.0066633 | 0.15357 | 0 | 0.030887 | 0.049467 | 0 | 0 | 0.29917 | 2.2976 | 0% | CZ 8 | 0 | 0 | 0.000361 | 0.19791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19828 | 0% | CZ 8 | 11.1007 | 3.5103 | 0.039457 | 21.7474 | -13.928 | 15.5081 | 0.59883 | 1.637 | -0.069758 | 1.6077 | 0 | 0.32336 | 0.51787 | 0 | 0 | 3.132 | 45.7252 | 0%
US Weighted | 0.11127 | 0.036259 | 0.00034878 | 0.060163 | -0.069192 | 0.16211 | 0.030352 | 0.018133 | -0.0014499 | 0.036609 | 0 | 0.0031289 | 0.0050135 | 0 | 0 | 0.030306 | 0.42305 | 100% | US Weighted | 3.7489 | 1.2216 | 0.034878 | 5.6914 | -2.3312 | 5.4617 | 1.0226 | 0.61093 | -0.048848 | 1.2334 | 0 | 0.10542 | 0.16891 | 0 | 0 | 1.021 | 17.9408 | 100% | US Weighted | 1.0984 | 0.35793 | 0 | 0.048363 | -0.68304 | 1.6003 | 0.29963 | 0.179 | -0.014313 | 0.36139 | 0 | 0.030887 | 0.049491 | 0 | 0 | 0.29917 | 3.6272 | 100% | US Weighted | 0 | 0 | 0.00034878 | 0.055264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055612 | 100% | US Weighted | 11.4995 | 3.7472 | 0.038121 | 6.5466 | -7.1508 | 16.7533 | 3.1368 | 1.874 | -0.14984 | 3.7834 | 0 | 0.32336 | 0.51812 | 0 | 0 | 3.132 | 44.0517 | 100%
Building Type: | Large Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 498588 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 498588 | [17 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 38.48% | 65.36% | 4.242% | 100% | 0% | 26.36% | 61.35% | 15.71% | 0% | 57.08% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 18.89% | 3.896% | CZ 1A | 38.48% | 65.36% | 4.242% | 100% | 0% | 26.36% | 61.35% | 15.71% | 0% | 57.08% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 18.86% | 3.896% | CZ 1A | 38.48% | 65.36% | 0% | 0% | 0% | 26.36% | 61.35% | 15.71% | 0% | 57.08% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 18.91% | 3.896% | CZ 1A | 0% | 0% | 4.242% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.79% | 3.896% | CZ 1A | 38.48% | 65.36% | 4.242% | 100% | 0% | 26.36% | 61.35% | 15.71% | 0% | 57.08% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 18.89% | 3.896%
CZ 1B | 38.46% | 65.4% | 4.304% | 84.35% | 36.05% | 17.16% | 54.6% | 18.74% | 0% | 46.98% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.25% | 0% | CZ 1B | 38.46% | 65.4% | 4.304% | 83.83% | 36.05% | 17.16% | 54.6% | 18.74% | 0% | 46.98% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.66% | 0% | CZ 1B | 38.46% | 65.4% | 0% | 91.09% | 36.05% | 17.16% | 54.6% | 18.74% | 0% | 46.98% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.04% | 0% | CZ 1B | 0% | 0% | 4.304% | 83.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 46.61% | 0% | CZ 1B | 38.46% | 65.4% | 4.304% | 84.31% | 36.05% | 17.16% | 54.6% | 18.74% | 0% | 46.98% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.26% | 0%
CZ 2A | 38.51% | 65.3% | 3.833% | 86.3% | -4918% | 38.49% | 62.44% | 16.76% | 0% | 61.32% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 21.14% | 11.87% | CZ 2A | 38.51% | 65.3% | 3.833% | 86.44% | -4918% | 38.49% | 62.44% | 16.76% | 0% | 61.32% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 22% | 11.87% | CZ 2A | 38.51% | 65.3% | 0% | 72.98% | -4918% | 38.49% | 62.44% | 16.76% | 0% | 61.32% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 20.68% | 11.87% | CZ 2A | 0% | 0% | 3.833% | 86.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.79% | 11.87% | CZ 2A | 38.51% | 65.3% | 3.833% | 86.31% | -4918% | 38.49% | 62.44% | 16.76% | 0% | 61.32% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 21.16% | 11.87%
CZ 2B | 38.48% | 65.31% | 3.869% | 84.77% | -2849% | 29.89% | 61.88% | 15.09% | 0% | 52.4% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 14.19% | 1.826% | CZ 2B | 38.48% | 65.31% | 3.869% | 88.02% | -2849% | 29.89% | 61.88% | 15.09% | 0% | 52.4% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 15.52% | 1.826% | CZ 2B | 38.48% | 65.31% | 0% | 73.65% | -2849% | 29.89% | 61.88% | 15.09% | 0% | 52.4% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 13.5% | 1.826% | CZ 2B | 0% | 0% | 3.869% | 90.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.84% | 1.826% | CZ 2B | 38.48% | 65.31% | 3.869% | 84.99% | -2849% | 29.89% | 61.88% | 15.09% | 0% | 52.4% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 14.23% | 1.826%
CZ 3A | 38.34% | 65% | 3.361% | 68.89% | -3635% | 39.9% | 62.25% | 12.45% | 0% | 60.4% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 17.62% | 14.76% | CZ 3A | 38.34% | 65% | 3.361% | 68.64% | -3635% | 39.9% | 62.25% | 12.45% | 0% | 60.4% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 19.89% | 14.76% | CZ 3A | 38.34% | 65% | 0% | 87.49% | -3635% | 39.9% | 62.25% | 12.45% | 0% | 60.4% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.37% | 14.76% | CZ 3A | 0% | 0% | 3.361% | 68.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.94% | 14.76% | CZ 3A | 38.34% | 65% | 3.361% | 68.87% | -3635% | 39.9% | 62.25% | 12.45% | 0% | 60.4% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 17.69% | 14.76%
CZ 3B | 38.45% | 65.57% | 3.473% | 85.47% | -221.3% | 30.42% | 58.72% | 11.65% | 0% | 43.95% | 0% | 2.834% | 61.79% | 0% | 0% | 9.145% | 14.53% | 8.555% | CZ 3B | 38.45% | 65.57% | 3.473% | 77.31% | -221.3% | 30.42% | 58.72% | 11.65% | 0% | 43.95% | 0% | 2.834% | 61.79% | 0% | 0% | 9.145% | 15.26% | 8.555% | CZ 3B | 38.45% | 65.57% | 0% | 96.31% | -221.3% | 30.42% | 58.72% | 11.65% | 0% | 43.95% | 0% | 2.834% | 61.79% | 0% | 0% | 9.145% | 14.15% | 8.555% | CZ 3B | 0% | 0% | 3.473% | 65.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.76% | 8.555% | CZ 3B | 38.45% | 65.57% | 3.473% | 85.08% | -221.3% | 30.42% | 58.72% | 11.65% | 0% | 43.95% | 0% | 2.834% | 61.79% | 0% | 0% | 9.145% | 14.55% | 8.555%
CZ 3C | 38.37% | 65.57% | 3.386% | 93.81% | -6853% | 46.1% | 60.31% | 15.59% | 0% | 57.89% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 17.51% | 3.506% | CZ 3C | 38.37% | 65.57% | 3.386% | 94.48% | -6853% | 46.1% | 60.31% | 15.59% | 0% | 57.89% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 18.55% | 3.506% | CZ 3C | 38.37% | 65.57% | 0% | 83.46% | -6853% | 46.1% | 60.31% | 15.59% | 0% | 57.89% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 16.96% | 3.506% | CZ 3C | 0% | 0% | 3.386% | 94.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.47% | 3.506% | CZ 3C | 38.37% | 65.57% | 3.386% | 93.86% | -6853% | 46.1% | 60.31% | 15.59% | 0% | 57.89% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 17.54% | 3.506%
CZ 4A | 38.31% | 65.09% | 3.085% | 64.41% | -7943% | 47.28% | 61.44% | 9.933% | 0% | 66.38% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.8% | 31.46% | CZ 4A | 38.31% | 65.09% | 3.085% | 64.52% | -7943% | 47.28% | 61.44% | 9.933% | 0% | 66.38% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 21.62% | 31.46% | CZ 4A | 38.31% | 65.09% | 0% | -39.53% | -7943% | 47.28% | 61.44% | 9.933% | 0% | 66.38% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 15.54% | 31.46% | CZ 4A | 0% | 0% | 3.085% | 64.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.92% | 31.46% | CZ 4A | 38.31% | 65.09% | 3.085% | 64.42% | -7943% | 47.28% | 61.44% | 9.933% | 0% | 66.38% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.92% | 31.46%
CZ 4B | 38.53% | 65.42% | 3.162% | 84.21% | -90.55% | 44.33% | 60.37% | 7.713% | 0% | 55.83% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 17.22% | 0.05451% | CZ 4B | 38.53% | 65.42% | 3.162% | 78.95% | -90.55% | 44.33% | 60.37% | 7.713% | 0% | 55.83% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 19.28% | 0.05451% | CZ 4B | 38.53% | 65.42% | 0% | 95.5% | -90.55% | 44.33% | 60.37% | 7.713% | 0% | 55.83% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.1% | 0.05451% | CZ 4B | 0% | 0% | 3.162% | 73.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.95% | 0.05451% | CZ 4B | 38.53% | 65.42% | 3.162% | 83.91% | -90.55% | 44.33% | 60.37% | 7.713% | 0% | 55.83% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 17.29% | 0.05451%
CZ 4C | 38.13% | 64.58% | 2.982% | 72.64% | -12893% | 62.05% | 64.66% | 10% | 0% | 54.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.17% | 4.546% | CZ 4C | 38.13% | 64.58% | 2.982% | 72.88% | -12893% | 62.05% | 64.66% | 10% | 0% | 54.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 19.68% | 4.546% | CZ 4C | 38.13% | 64.58% | 0% | 20.11% | -12893% | 62.05% | 64.66% | 10% | 0% | 54.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 14.17% | 4.546% | CZ 4C | 0% | 0% | 2.982% | 73.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 63.7% | 4.546% | CZ 4C | 38.13% | 64.58% | 2.982% | 72.66% | -12893% | 62.05% | 64.66% | 10% | 0% | 54.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.28% | 4.546%
CZ 5A | 38.37% | 64.95% | 2.867% | 59.32% | -8300% | 50.64% | 61.22% | 11.58% | 0% | 56.03% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 16.69% | 13.22% | CZ 5A | 38.37% | 64.95% | 2.867% | 59.34% | -8300% | 50.64% | 61.22% | 11.58% | 0% | 56.03% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 22.03% | 13.22% | CZ 5A | 38.37% | 64.95% | 0% | 31.37% | -8300% | 50.64% | 61.22% | 11.58% | 0% | 56.03% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 13.26% | 13.22% | CZ 5A | 0% | 0% | 2.867% | 59.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.71% | 13.22% | CZ 5A | 38.37% | 64.95% | 2.867% | 59.32% | -8300% | 50.64% | 61.22% | 11.58% | 0% | 56.03% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 16.87% | 13.22%
CZ 5B | 38.39% | 65.18% | 2.925% | 74.16% | -80.14% | 52.58% | 63.12% | 7.73% | 0% | 56.63% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 18.49% | 3.582% | CZ 5B | 38.39% | 65.18% | 2.925% | 69% | -80.14% | 52.58% | 63.12% | 7.73% | 0% | 56.63% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 21.85% | 3.582% | CZ 5B | 38.39% | 65.18% | 0% | 95.24% | -80.14% | 52.58% | 63.12% | 7.73% | 0% | 56.63% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 16.54% | 3.582% | CZ 5B | 0% | 0% | 2.925% | 65.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.73% | 3.582% | CZ 5B | 38.39% | 65.18% | 2.925% | 73.82% | -80.14% | 52.58% | 63.12% | 7.73% | 0% | 56.63% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 18.6% | 3.582%
CZ 5C | 38.07% | 64.53% | 2.889% | 71.51% | -13627% | 69.13% | 71.33% | 7.866% | 0% | 48.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 15.54% | 0.07377% | CZ 5C | 38.07% | 64.53% | 2.889% | 71.99% | -13627% | 69.13% | 71.33% | 7.866% | 0% | 48.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 19.2% | 0.07377% | CZ 5C | 38.07% | 64.53% | 0% | -194.4% | -13627% | 69.13% | 71.33% | 7.866% | 0% | 48.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 13.44% | 0.07377% | CZ 5C | 0% | 0% | 2.889% | 72.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.96% | 0.07377% | CZ 5C | 38.07% | 64.53% | 2.889% | 71.55% | -13627% | 69.13% | 71.33% | 7.866% | 0% | 48.12% | 0% | 2.834% | 61.76% | 0% | 0% | 9.145% | 15.66% | 0.07377%
CZ 6A | 38.34% | 64.88% | 2.741% | 55.78% | -7251% | 49.5% | 61.59% | 12.67% | 0% | 56.46% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 17.5% | 2.328% | CZ 6A | 38.34% | 64.88% | 2.741% | 55.8% | -7251% | 49.5% | 61.59% | 12.67% | 0% | 56.46% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 23.7% | 2.328% | CZ 6A | 38.34% | 64.88% | 0% | 28.31% | -7251% | 49.5% | 61.59% | 12.67% | 0% | 56.46% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 13.22% | 2.328% | CZ 6A | 0% | 0% | 2.741% | 55.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 53.19% | 2.328% | CZ 6A | 38.34% | 64.88% | 2.741% | 55.78% | -7251% | 49.5% | 61.59% | 12.67% | 0% | 56.46% | 0% | 2.834% | 61.78% | 0% | 0% | 9.145% | 17.72% | 2.328%
CZ 6B | 38.31% | 64.58% | 2.773% | 62.66% | -237.1% | 59.86% | 66.65% | 3.458% | 0% | 53.66% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 16.72% | 0% | CZ 6B | 38.31% | 64.58% | 2.773% | 60.72% | -237.1% | 59.86% | 66.65% | 3.458% | 0% | 53.66% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 21.84% | 0% | CZ 6B | 38.31% | 64.58% | 0% | 91.45% | -237.1% | 59.86% | 66.65% | 3.458% | 0% | 53.66% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 13.48% | 0% | CZ 6B | 0% | 0% | 2.773% | 59.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.72% | 0% | CZ 6B | 38.31% | 64.58% | 2.773% | 62.51% | -237.1% | 59.86% | 66.65% | 3.458% | 0% | 53.66% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 16.9% | 0%
CZ 7 | 38.39% | 64.48% | 2.617% | 57.98% | -6018% | 53.95% | 62.07% | 11.84% | 0% | 54.3% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.69% | 0.3244% | CZ 7 | 38.39% | 64.48% | 2.617% | 57.96% | -6018% | 53.95% | 62.07% | 11.84% | 0% | 54.3% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 24.96% | 0.3244% | CZ 7 | 38.39% | 64.48% | 0% | 70.01% | -6018% | 53.95% | 62.07% | 11.84% | 0% | 54.3% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 12.49% | 0.3244% | CZ 7 | 0% | 0% | 2.617% | 57.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.42% | 0.3244% | CZ 7 | 38.39% | 64.48% | 2.617% | 57.98% | -6018% | 53.95% | 62.07% | 11.84% | 0% | 54.3% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.95% | 0.3244%
CZ 8 | 37.03% | 61.49% | 2.519% | 53.47% | -1692% | 64.55% | 66.65% | 10.46% | 0% | 56.02% | 0% | 2.834% | 61.75% | 0% | 0% | 9.145% | 17.58% | 0% | CZ 8 | 37.03% | 61.49% | 2.519% | 53.4% | -1692% | 64.55% | 66.65% | 10.46% | 0% | 56.02% | 0% | 2.834% | 61.75% | 0% | 0% | 9.145% | 25.58% | 0% | CZ 8 | 37.03% | 61.49% | 0% | 84.72% | -1692% | 64.55% | 66.65% | 10.46% | 0% | 56.02% | 0% | 2.834% | 61.75% | 0% | 0% | 9.145% | 11.26% | 0% | CZ 8 | 0% | 0% | 2.519% | 53.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.47% | 0% | CZ 8 | 37.03% | 61.49% | 2.519% | 53.47% | -1692% | 64.55% | 66.65% | 10.46% | 0% | 56.02% | 0% | 2.834% | 61.75% | 0% | 0% | 9.145% | 17.88% | 0%
US Weighted | 38.36% | 65.13% | 3.234% | 65.92% | -1062% | 42.34% | 61.7% | 12.03% | 0% | 60.43% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.7% | 100% | US Weighted | 38.36% | 65.13% | 3.234% | 64.86% | -1062% | 42.34% | 61.7% | 12.03% | 0% | 60.43% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 20.64% | 100% | US Weighted | 38.36% | 65.13% | 0% | 92.25% | -1062% | 42.34% | 61.7% | 12.03% | 0% | 60.43% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 16.02% | 100% | US Weighted | 0% | 0% | 3.234% | 64.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.48% | 100% | US Weighted | 38.36% | 65.13% | 3.234% | 65.84% | -1062% | 42.34% | 61.7% | 12.03% | 0% | 60.43% | 0% | 2.834% | 61.77% | 0% | 0% | 9.145% | 17.8% | 100%

## RtlStA
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Standalone Retail |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Standalone Retail | [14 empty] | Prototype Floor Area: | 24692 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.3411 | 0.043922 | 0.035632 | 0.050328 | 0 | 0.16335 | 0 | 0.1989 | 0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0722 |  | STD2016 | 11.4922 | 1.4798 | 3.5632 | 5.0328 | 0 | 5.5034 | 0 | 6.7014 | 0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.8246 |  | STD2016 | 3.3672 | 0.43359 | 0 | 0 | 0 | 1.6125 | 0 | 1.9635 | 0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.736 |  | STD2016 | 0 | 0 | 0.035632 | 0.050328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08596 |  | STD2016 | 35.2513 | 4.5392 | 3.8946 | 5.5009 | 0 | 16.8814 | 0 | 20.556 | 1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 111.3214
STD2013 | 0.4182 | 0.068757 | 0.035631 | 0.047726 | 0 | 0.17206 | 0 | 0.20937 | 0.017763 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1909 |  | STD2013 | 14.0898 | 2.3165 | 3.5631 | 4.7726 | 0 | 5.7971 | 0 | 7.054 | 0.59846 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.6518 |  | STD2013 | 4.1283 | 0.67874 | 0 | 0 | 0 | 1.6986 | 0 | 2.0668 | 0.17535 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.9336 |  | STD2013 | 0 | 0 | 0.035631 | 0.047726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083358 |  | STD2013 | 43.2193 | 7.1057 | 3.8945 | 5.2165 | 0 | 17.7821 | 0 | 21.6376 | 1.8357 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 123.5748
STD2010 | 0.50779 | 0.068757 | 0.035631 | 0.070745 | 0 | 0.19528 | 0 | 0.25841 | 0.016448 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3748 |  | STD2010 | 17.1082 | 2.3165 | 3.5631 | 7.0745 | 0 | 6.5792 | 0 | 8.7061 | 0.55417 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.3746 |  | STD2010 | 5.0127 | 0.67874 | 0 | 0 | 0 | 1.9277 | 0 | 2.5509 | 0.16237 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.5219 |  | STD2010 | 0 | 0 | 0.035631 | 0.070745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10638 |  | STD2010 | 52.4779 | 7.1057 | 3.8945 | 7.7325 | 0 | 20.1811 | 0 | 26.7053 | 1.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 142.7191
STD2007 | 0.56074 | 0.13109 | 0.036401 | 0.11532 | 0 | 0.29702 | 0 | 0.37375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7367 |  | STD2007 | 18.8922 | 4.4168 | 3.6401 | 11.5321 | 0 | 10.0072 | 0 | 12.5923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.5738 |  | STD2007 | 5.5354 | 1.2941 | 0 | 0 | 0 | 2.9321 | 0 | 3.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6467 |  | STD2007 | 0 | 0 | 0.036401 | 0.11532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15172 |  | STD2007 | 57.9503 | 13.5481 | 3.9786 | 12.6046 | 0 | 30.6962 | 0 | 38.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 180.3883
STD2004 | 0.56074 | 0.13109 | 0.036414 | 0.17476 | 0 | 0.3464 | 0 | 0.46217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.934 |  | STD2004 | 18.8922 | 4.4168 | 3.6414 | 17.4762 | 0 | 11.6708 | 0 | 15.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.1618 |  | STD2004 | 5.5354 | 1.2941 | 0 | 0 | 0 | 3.4195 | 0 | 4.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0069 |  | STD2004 | 0 | 0 | 0.036414 | 0.17476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21118 |  | STD2004 | 57.9503 | 13.5481 | 3.9801 | 19.1015 | 0 | 35.7991 | 0 | 47.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 201.1271
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.348e-05 | 0.059441 | 0 | 0.049376 | 0 | 0.088416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19725 |  | 2004-2007 | 0 | 0 | 0.001348 | 5.9441 | 0 | 1.6636 | 0 | 2.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5879 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | 0.48743 | 0 | 0.87282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3602 |  | 2004-2007 | 0 | 0 | 1.348e-05 | 0.059441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059455 |  | 2004-2007 | 0 | 0 | 0.0014734 | 6.4969 | 0 | 5.1029 | 0 | 9.1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7388
2007-2010 | 0.052952 | 0.062338 | 0.00076915 | 0.044576 | 0 | 0.10175 | 0 | 0.11535 | -0.016448 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00060399 | 0.36188 |  | 2007-2010 | 1.784 | 2.1003 | 0.076915 | 4.4576 | 0 | 3.428 | 0 | 3.8862 | -0.55417 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020349 | 15.1992 |  | 2007-2010 | 0.52272 | 0.61538 | 0 | 0 | 0 | 1.0044 | 0 | 1.1387 | -0.16237 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0059623 | 3.1247 |  | 2007-2010 | 0 | 0 | 0.00076915 | 0.044576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045345 |  | 2007-2010 | 5.4724 | 6.4424 | 0.084068 | 4.8722 | 0 | 10.5151 | 0 | 11.9206 | -1.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06242 | 37.6692
2010-2013 | 0.089588 | 0 | 3.099e-07 | 0.023019 | 0 | 0.023213 | 0 | 0.049036 | -0.0013145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037607 | 0.18392 |  | 2010-2013 | 3.0184 | 0 | 3.099e-05 | 2.3019 | 0 | 0.78208 | 0 | 1.6521 | -0.044289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01267 | 7.7228 |  | 2010-2013 | 0.88438 | 0 | 0 | 0 | 0 | 0.22915 | 0 | 0.48406 | -0.012977 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037124 | 1.5883 |  | 2010-2013 | 0 | 0 | 3.099e-07 | 0.023019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023019 |  | 2010-2013 | 9.2586 | 0 | 3.3872e-05 | 2.516 | 0 | 2.399 | 0 | 5.0677 | -0.13585 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038865 | 19.1442
2013-2016 | 0.0771 | 0.024834 | -6.3673e-07 | -0.0026021 | 0 | 0.0087158 | 0 | 0.010467 | 0.00020254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11872 |  | 2013-2016 | 2.5976 | 0.83671 | -6.3673e-05 | -0.26021 | 0 | 0.29365 | 0 | 0.35264 | 0.0068238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8272 |  | 2013-2016 | 0.76111 | 0.24516 | 0 | 0 | 0 | 0.08604 | 0 | 0.10332 | 0.0019994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1976 |  | 2013-2016 | 0 | 0 | -6.3673e-07 | -0.0026021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0026027 |  | 2013-2016 | 7.968 | 2.5665 | -6.9595e-05 | -0.28441 | 0 | 0.90075 | 0 | 1.0817 | 0.020932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2535
2004-2016 | 0.21964 | 0.087172 | 0.0007823 | 0.12443 | 0 | 0.18305 | 0 | 0.26326 | -0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.86176 |  | 2004-2016 | 7.4 | 2.937 | 0.07823 | 12.4434 | 0 | 6.1673 | 0 | 8.8698 | -0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.3371 |  | 2004-2016 | 2.1682 | 0.86053 | 0 | 0 | 0 | 1.807 | 0 | 2.5989 | -0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.2709 |  | 2004-2016 | 0 | 0 | 0.0007823 | 0.12443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12522 |  | 2004-2016 | 22.699 | 9.0089 | 0.085506 | 13.6006 | 0 | 18.9177 | 0 | 27.2074 | -1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 89.8057
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.03702% | 34.01% |  | 14.25% |  | 19.13% | [7 empty] | 0% | 10.2% |  | 2004-2007 | 0% | 0% | 0.03702% | 34.01% |  | 14.25% |  | 19.13% | [7 empty] | 0% | 13.38% |  | 2004-2007 | 0% | 0% |  |  |  | 14.25% |  | 19.13% | [7 empty] | 0% | 7.998% |  | 2004-2007 |  |  | 0.03702% | 34.01% | [12 empty] | 28.15% |  | 2004-2007 | 0% | 0% | 0.03702% | 34.01% |  | 14.25% |  | 19.13% | [7 empty] | 0% | 10.31%
2007-2010 | 9.443% | 47.55% | 2.113% | 38.65% |  | 34.26% |  | 30.86% | [7 empty] | 0.2716% | 20.84% |  | 2007-2010 | 9.443% | 47.55% | 2.113% | 38.65% |  | 34.26% |  | 30.86% | [7 empty] | 0.2716% | 22.16% |  | 2007-2010 | 9.443% | 47.55% |  |  |  | 34.26% |  | 30.86% | [7 empty] | 0.2716% | 19.97% |  | 2007-2010 |  |  | 2.113% | 38.65% | [12 empty] | 29.89% |  | 2007-2010 | 9.443% | 47.55% | 2.113% | 38.65% |  | 34.26% |  | 30.86% | [7 empty] | 0.2716% | 20.88%
2010-2013 | 17.64% | 0% | 0.0008697% | 32.54% |  | 11.89% |  | 18.98% | -7.992% | [6 empty] | 0.1696% | 13.38% |  | 2010-2013 | 17.64% | 0% | 0.0008697% | 32.54% |  | 11.89% |  | 18.98% | -7.992% | [6 empty] | 0.1696% | 14.47% |  | 2010-2013 | 17.64% | 0% |  |  |  | 11.89% |  | 18.98% | -7.992% | [6 empty] | 0.1696% | 12.68% |  | 2010-2013 |  |  | 0.0008697% | 32.54% | [12 empty] | 21.64% |  | 2010-2013 | 17.64% | 0% | 0.0008697% | 32.54% |  | 11.89% |  | 18.98% | -7.992% | [6 empty] | 0.1696% | 13.41%
2013-2016 | 18.44% | 36.12% | -0.001787% | -5.452% |  | 5.065% |  | 4.999% | 1.14% | [6 empty] | 0% | 9.968% |  | 2013-2016 | 18.44% | 36.12% | -0.001787% | -5.452% |  | 5.065% |  | 4.999% | 1.14% | [6 empty] | 0% | 8.383% |  | 2013-2016 | 18.44% | 36.12% |  |  |  | 5.065% |  | 4.999% | 1.14% | [6 empty] | 0% | 10.95% |  | 2013-2016 |  |  | -0.001787% | -5.452% | [12 empty] | -3.122% |  | 2013-2016 | 18.44% | 36.12% | -0.001787% | -5.452% |  | 5.065% |  | 4.999% | 1.14% | [6 empty] | 0% | 9.916%
2004-2016 | 39.17% | 66.5% | 2.148% | 71.2% |  | 52.84% |  | 56.96% | [7 empty] | 0.4407% | 44.56% |  | 2004-2016 | 39.17% | 66.5% | 2.148% | 71.2% |  | 52.84% |  | 56.96% | [7 empty] | 0.4407% | 47.17% |  | 2004-2016 | 39.17% | 66.5% |  |  |  | 52.84% |  | 56.96% | [7 empty] | 0.4407% | 42.75% |  | 2004-2016 |  |  | 2.148% | 71.2% | [12 empty] | 59.29% |  | 2004-2016 | 39.17% | 66.5% | 2.148% | 71.2% |  | 52.84% |  | 56.96% | [7 empty] | 0.4407% | 44.65%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.33228 | 0.043909 | 0.032774 | 0.00030325 | 0 | 0.41705 | 0 | 0.14872 | 0.03045 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.2269 | 2.683% | CZ 1A | 11.1952 | 1.4794 | 3.2774 | 0.030325 | 0 | 14.051 | 0 | 5.0105 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.5298 | 2.683% | CZ 1A | 3.2802 | 0.43345 | 0 | 0 | 0 | 4.1169 | 0 | 1.4681 | 0.30059 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.7851 | 2.683% | CZ 1A | 0 | 0 | 0.032774 | 0.00030325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033077 | 2.683% | CZ 1A | 34.3403 | 4.5378 | 3.5822 | 0.033145 | 0 | 43.1003 | 0 | 15.3694 | 3.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 126.9933 | 2.683%
CZ 1B | 0.32885 | 0.04384 | 0.032785 | 0.014506 | 0 | 0.51486 | 0 | 0.18645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.3427 | 0% | CZ 1B | 11.0796 | 1.4771 | 3.2785 | 1.4506 | 0 | 17.3464 | 0 | 6.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 48.3741 | 0% | CZ 1B | 3.2463 | 0.43278 | 0 | 0 | 0 | 5.0825 | 0 | 1.8406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 12.788 | 0% | CZ 1B | 0 | 0 | 0.032785 | 0.014506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047291 | 0% | CZ 1B | 33.9858 | 4.5307 | 3.5834 | 1.5855 | 0 | 53.2087 | 0 | 19.2689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 139.0464 | 0%
CZ 2A | 0.33227 | 0.043817 | 0.033618 | 0.0049671 | 0 | 0.30033 | 0 | 0.21328 | 0.024251 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.174 | 15.29% | CZ 2A | 11.1948 | 1.4763 | 3.3618 | 0.49671 | 0 | 10.1186 | 0 | 7.1856 | 0.81704 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 42.111 | 15.29% | CZ 2A | 3.2801 | 0.43255 | 0 | 0 | 0 | 2.9647 | 0 | 2.1054 | 0.23939 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.208 | 15.29% | CZ 2A | 0 | 0 | 0.033618 | 0.0049671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038585 | 15.29% | CZ 2A | 34.3391 | 4.5284 | 3.6745 | 0.5429 | 0 | 31.0379 | 0 | 22.0413 | 2.5062 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 121.5536 | 15.29%
CZ 2B | 0.34662 | 0.043863 | 0.033664 | 0.012614 | 0 | 0.27795 | 0 | 0.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1925 | 3.321% | CZ 2B | 11.6782 | 1.4778 | 3.3664 | 1.2614 | 0 | 9.3645 | 0 | 8.6385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.2469 | 3.321% | CZ 2B | 3.4217 | 0.433 | 0 | 0 | 0 | 2.7438 | 0 | 2.5311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.3154 | 3.321% | CZ 2B | 0 | 0 | 0.033664 | 0.012614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046278 | 3.321% | CZ 2B | 35.8219 | 4.5331 | 3.6795 | 1.3787 | 0 | 28.7249 | 0 | 26.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 123.5191 | 3.321%
CZ 3A | 0.33334 | 0.043852 | 0.03505 | 0.02687 | 0 | 0.18145 | 0 | 0.19031 | 0.021242 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0535 | 16.83% | CZ 3A | 11.2309 | 1.4774 | 3.505 | 2.687 | 0 | 6.1132 | 0 | 6.4119 | 0.71568 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 39.6013 | 16.83% | CZ 3A | 3.2907 | 0.43289 | 0 | 0 | 0 | 1.7912 | 0 | 1.8787 | 0.20969 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.7889 | 16.83% | CZ 3A | 0 | 0 | 0.03505 | 0.02687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06192 | 16.83% | CZ 3A | 34.4498 | 4.5319 | 3.831 | 2.9369 | 0 | 18.7518 | 0 | 19.6681 | 2.1953 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 109.2482 | 16.83%
CZ 3B | 0.34425 | 0.04384 | 0.034678 | 0.029906 | 0 | 0.19438 | 0 | 0.25497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1235 | 8.207% | CZ 3B | 11.5983 | 1.4771 | 3.4678 | 2.9906 | 0 | 6.549 | 0 | 8.5905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 42.1334 | 8.207% | CZ 3B | 3.3983 | 0.43278 | 0 | 0 | 0 | 1.9189 | 0 | 2.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.4528 | 8.207% | CZ 3B | 0 | 0 | 0.034678 | 0.029906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064584 | 8.207% | CZ 3B | 35.5769 | 4.5307 | 3.7903 | 3.2687 | 0 | 20.0886 | 0 | 26.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 116.4891 | 8.207%
CZ 3C | 0.34431 | 0.043988 | 0.035196 | 0.011949 | 0 | 0.080512 | 0 | 0.22403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 0.96141 | 1.253% | CZ 3C | 11.6003 | 1.482 | 3.5196 | 1.1949 | 0 | 2.7126 | 0 | 7.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 35.5176 | 1.253% | CZ 3C | 3.3989 | 0.43424 | 0 | 0 | 0 | 0.79479 | 0 | 2.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.0253 | 1.253% | CZ 3C | 0 | 0 | 0.035196 | 0.011949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047145 | 1.253% | CZ 3C | 35.5828 | 4.546 | 3.8469 | 1.3061 | 0 | 8.3207 | 0 | 23.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 99.6389 | 1.253%
CZ 4A | 0.34196 | 0.044068 | 0.036178 | 0.048615 | 0 | 0.12593 | 0 | 0.18159 | 0.022074 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0218 | 15.99% | CZ 4A | 11.5212 | 1.4847 | 3.6178 | 4.8615 | 0 | 4.2426 | 0 | 6.1182 | 0.74371 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.05 | 15.99% | CZ 4A | 3.3757 | 0.43503 | 0 | 0 | 0 | 1.2431 | 0 | 1.7926 | 0.21791 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.2502 | 15.99% | CZ 4A | 0 | 0 | 0.036178 | 0.048615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084794 | 15.99% | CZ 4A | 35.3402 | 4.5543 | 3.9543 | 5.3137 | 0 | 13.0139 | 0 | 18.7672 | 2.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 106.1081 | 15.99%
CZ 4B | 0.34351 | 0.04384 | 0.035848 | 0.054369 | 0 | 0.13932 | 0 | 0.26963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1079 | 0.8792% | CZ 4B | 11.5734 | 1.4771 | 3.5848 | 5.4369 | 0 | 4.6938 | 0 | 9.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.3103 | 0.8792% | CZ 4B | 3.391 | 0.43278 | 0 | 0 | 0 | 1.3753 | 0 | 2.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.0466 | 0.8792% | CZ 4B | 0 | 0 | 0.035848 | 0.054369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090218 | 0.8792% | CZ 4B | 35.5004 | 4.5307 | 3.9182 | 5.9426 | 0 | 14.3978 | 0 | 27.8651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 115.0381 | 0.8792%
CZ 4C | 0.34745 | 0.044102 | 0.03652 | 0.092813 | 0 | 0.041538 | 0 | 0.16071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 0.94455 | 2.698% | CZ 4C | 11.7062 | 1.4859 | 3.652 | 9.2813 | 0 | 1.3995 | 0 | 5.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.3994 | 2.698% | CZ 4C | 3.4299 | 0.43536 | 0 | 0 | 0 | 0.41005 | 0 | 1.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 8.0476 | 2.698% | CZ 4C | 0 | 0 | 0.03652 | 0.092813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12933 | 2.698% | CZ 4C | 35.9079 | 4.5578 | 3.9916 | 10.1444 | 0 | 4.2928 | 0 | 16.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 98.3863 | 2.698%
CZ 5A | 0.34206 | 0.04392 | 0.037123 | 0.079554 | 0 | 0.077891 | 0 | 0.17984 | 0.021379 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0032 | 22.02% | CZ 5A | 11.5246 | 1.4797 | 3.7123 | 7.9554 | 0 | 2.6243 | 0 | 6.0591 | 0.72029 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.5358 | 22.02% | CZ 5A | 3.3767 | 0.43356 | 0 | 0 | 0 | 0.76892 | 0 | 1.7753 | 0.21104 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 8.7514 | 22.02% | CZ 5A | 0 | 0 | 0.037123 | 0.079554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11668 | 22.02% | CZ 5A | 35.3508 | 4.539 | 4.0575 | 8.6953 | 0 | 8.0498 | 0 | 18.5858 | 2.2094 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 104.3709 | 22.02%
CZ 5B | 0.34521 | 0.044011 | 0.03685 | 0.11409 | 0 | 0.10186 | 0 | 0.23494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0984 | 5.18% | CZ 5B | 11.6306 | 1.4828 | 3.685 | 11.409 | 0 | 3.4317 | 0 | 7.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.0147 | 5.18% | CZ 5B | 3.4078 | 0.43446 | 0 | 0 | 0 | 1.0055 | 0 | 2.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.3528 | 5.18% | CZ 5B | 0 | 0 | 0.03685 | 0.11409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15094 | 5.18% | CZ 5B | 35.6759 | 4.5484 | 4.0277 | 12.47 | 0 | 10.5266 | 0 | 24.2801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 114.412 | 5.18%
CZ 5C | 0.34521 | 0.044057 | 0.037054 | 0.10683 | 0 | 0.020456 | 0 | 0.17348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 0.94851 | 0.1101% | CZ 5C | 11.6306 | 1.4843 | 3.7054 | 10.6831 | 0 | 0.68919 | 0 | 5.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.4976 | 0.1101% | CZ 5C | 3.4078 | 0.43491 | 0 | 0 | 0 | 0.20193 | 0 | 1.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 7.943 | 0.1101% | CZ 5C | 0 | 0 | 0.037054 | 0.10683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14388 | 0.1101% | CZ 5C | 35.6759 | 4.5531 | 4.05 | 11.6766 | 0 | 2.114 | 0 | 17.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 98.8815 | 0.1101%
CZ 6A | 0.37052 | 0.043988 | 0.037817 | 0.14059 | 0 | 0.087829 | 0 | 0.18639 | 0.022234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1108 | 4.525% | CZ 6A | 12.4833 | 1.482 | 3.7817 | 14.0591 | 0 | 2.9591 | 0 | 6.2799 | 0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 49.2544 | 4.525% | CZ 6A | 3.6576 | 0.43424 | 0 | 0 | 0 | 0.86701 | 0 | 1.84 | 0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.2042 | 4.525% | CZ 6A | 0 | 0 | 0.037817 | 0.14059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17841 | 4.525% | CZ 6A | 38.2916 | 4.546 | 4.1335 | 15.3666 | 0 | 9.0768 | 0 | 19.263 | 2.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 115.8585 | 4.525%
CZ 6B | 0.37216 | 0.043909 | 0.037641 | 0.083984 | 0 | 0.066062 | 0 | 0.19546 | 0.021983 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0426 | 0.5032% | CZ 6B | 12.5386 | 1.4794 | 3.7641 | 8.3984 | 0 | 2.2258 | 0 | 6.5855 | 0.74064 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.1925 | 0.5032% | CZ 6B | 3.6738 | 0.43345 | 0 | 0 | 0 | 0.65215 | 0 | 1.9295 | 0.21701 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.0918 | 0.5032% | CZ 6B | 0 | 0 | 0.037641 | 0.083984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12162 | 0.5032% | CZ 6B | 38.4612 | 4.5378 | 4.1142 | 9.1794 | 0 | 6.8273 | 0 | 20.2005 | 2.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 108.4755 | 0.5032%
CZ 7 | 0.37219 | 0.044068 | 0.038639 | 0.16425 | 0 | 0.058268 | 0 | 0.17808 | 0.020433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0974 | 0.4193% | CZ 7 | 12.5398 | 1.4847 | 3.8639 | 16.4248 | 0 | 1.9631 | 0 | 6 | 0.68842 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.4249 | 0.4193% | CZ 7 | 3.6742 | 0.43503 | 0 | 0 | 0 | 0.5752 | 0 | 1.758 | 0.20171 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 8.8299 | 0.4193% | CZ 7 | 0 | 0 | 0.038639 | 0.16425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20289 | 0.4193% | CZ 7 | 38.4647 | 4.5543 | 4.2232 | 17.9523 | 0 | 6.0217 | 0 | 18.4044 | 2.1117 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 114.6157 | 0.4193%
CZ 8 | 0.37647 | 0.044832 | 0.039748 | 0.26818 | 0 | 0.028376 | 0 | 0.17136 | 0.022678 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1731 | 0.0892% | CZ 8 | 12.6838 | 1.5105 | 3.9748 | 26.8177 | 0 | 0.95603 | 0 | 5.7734 | 0.76406 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 59.9404 | 0.0892% | CZ 8 | 3.7163 | 0.44256 | 0 | 0 | 0 | 0.28012 | 0 | 1.6916 | 0.22387 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 8.5403 | 0.0892% | CZ 8 | 0 | 0 | 0.039748 | 0.26818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30793 | 0.0892% | CZ 8 | 38.9064 | 4.6332 | 4.3445 | 29.3118 | 0 | 2.9326 | 0 | 17.7096 | 2.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 123.0649 | 0.0892%
US Weighted | 0.3411 | 0.043922 | 0.035632 | 0.050328 | 0 | 0.16335 | 0 | 0.1989 | 0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0722 | 100% | US Weighted | 11.4922 | 1.4798 | 3.5632 | 5.0328 | 0 | 5.5034 | 0 | 6.7014 | 0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.8246 | 100% | US Weighted | 3.3672 | 0.43359 | 0 | 0 | 0 | 1.6125 | 0 | 1.9635 | 0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.736 | 100% | US Weighted | 0 | 0 | 0.035632 | 0.050328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08596 | 100% | US Weighted | 35.2513 | 4.5392 | 3.8946 | 5.5009 | 0 | 16.8814 | 0 | 20.556 | 1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 111.3214 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.40776 | 0.068809 | 0.032774 | 0.00030708 | 0 | 0.43485 | 0 | 0.15532 | 0.03045 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.3517 | 2.683% | CZ 1A | 13.7381 | 2.3183 | 3.2774 | 0.030708 | 0 | 14.6507 | 0 | 5.2328 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.734 | 2.683% | CZ 1A | 4.0253 | 0.67926 | 0 | 0 | 0 | 4.2927 | 0 | 1.5332 | 0.30059 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 13.0168 | 2.683% | CZ 1A | 0 | 0 | 0.032774 | 0.00030708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033081 | 2.683% | CZ 1A | 42.1404 | 7.1111 | 3.5822 | 0.033564 | 0 | 44.9399 | 0 | 16.0513 | 3.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 139.8887 | 2.683%
CZ 1B | 0.40374 | 0.068706 | 0.032785 | 0.013458 | 0 | 0.53006 | 0 | 0.18533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.4555 | 0% | CZ 1B | 13.6025 | 2.3148 | 3.2785 | 1.3458 | 0 | 17.8586 | 0 | 6.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 52.1046 | 0% | CZ 1B | 3.9855 | 0.67824 | 0 | 0 | 0 | 5.2326 | 0 | 1.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 13.9117 | 0% | CZ 1B | 0 | 0 | 0.032785 | 0.013458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046243 | 0% | CZ 1B | 41.7247 | 7.1005 | 3.5834 | 1.471 | 0 | 54.7798 | 0 | 19.1535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 150.6962 | 0%
CZ 2A | 0.40778 | 0.068672 | 0.033618 | 0.0046562 | 0 | 0.31625 | 0 | 0.22586 | 0.023977 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.3022 | 15.29% | CZ 2A | 13.7388 | 2.3137 | 3.3618 | 0.46562 | 0 | 10.655 | 0 | 7.6095 | 0.80783 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.4124 | 15.29% | CZ 2A | 4.0255 | 0.67791 | 0 | 0 | 0 | 3.1219 | 0 | 2.2296 | 0.23669 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 12.4774 | 15.29% | CZ 2A | 0 | 0 | 0.033618 | 0.0046562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038274 | 15.29% | CZ 2A | 42.1428 | 7.097 | 3.6745 | 0.50892 | 0 | 32.6832 | 0 | 23.3415 | 2.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 134.8092 | 15.29%
CZ 2B | 0.42473 | 0.068729 | 0.033664 | 0.011508 | 0 | 0.2912 | 0 | 0.27157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.3228 | 3.321% | CZ 2B | 14.3098 | 2.3156 | 3.3664 | 1.1508 | 0 | 9.811 | 0 | 9.1495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.5633 | 3.321% | CZ 2B | 4.1928 | 0.67847 | 0 | 0 | 0 | 2.8746 | 0 | 2.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 12.6125 | 3.321% | CZ 2B | 0 | 0 | 0.033664 | 0.011508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045172 | 3.321% | CZ 2B | 43.8941 | 7.1029 | 3.6795 | 1.2578 | 0 | 30.0946 | 0 | 28.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 136.9776 | 3.321%
CZ 3A | 0.40905 | 0.068718 | 0.03505 | 0.025215 | 0 | 0.19209 | 0 | 0.20344 | 0.022461 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1774 | 16.83% | CZ 3A | 13.7815 | 2.3152 | 3.505 | 2.5215 | 0 | 6.4718 | 0 | 6.8543 | 0.75676 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.6662 | 16.83% | CZ 3A | 4.038 | 0.67836 | 0 | 0 | 0 | 1.8963 | 0 | 2.0083 | 0.22173 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.0284 | 16.83% | CZ 3A | 0 | 0 | 0.03505 | 0.025215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060265 | 16.83% | CZ 3A | 42.2735 | 7.1017 | 3.831 | 2.7561 | 0 | 19.8518 | 0 | 21.0249 | 2.3213 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 122.0436 | 16.83%
CZ 3B | 0.42191 | 0.068718 | 0.034674 | 0.028808 | 0 | 0.20346 | 0 | 0.25612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.2351 | 8.207% | CZ 3B | 14.2149 | 2.3152 | 3.4674 | 2.8808 | 0 | 6.855 | 0 | 8.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.8228 | 8.207% | CZ 3B | 4.165 | 0.67836 | 0 | 0 | 0 | 2.0085 | 0 | 2.5284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.566 | 8.207% | CZ 3B | 0 | 0 | 0.034674 | 0.028808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063482 | 8.207% | CZ 3B | 43.6032 | 7.1017 | 3.7898 | 3.1488 | 0 | 21.0272 | 0 | 26.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 128.0236 | 8.207%
CZ 3C | 0.42197 | 0.068832 | 0.035196 | 0.011462 | 0 | 0.086096 | 0 | 0.21846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0634 | 1.253% | CZ 3C | 14.2169 | 2.3191 | 3.5196 | 1.1462 | 0 | 2.9007 | 0 | 7.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 38.9229 | 1.253% | CZ 3C | 4.1655 | 0.67948 | 0 | 0 | 0 | 0.84992 | 0 | 2.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.0373 | 1.253% | CZ 3C | 0 | 0 | 0.035196 | 0.011462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046658 | 1.253% | CZ 3C | 43.6091 | 7.1135 | 3.8469 | 1.2528 | 0 | 8.8978 | 0 | 22.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 110.1805 | 1.253%
CZ 4A | 0.41921 | 0.068866 | 0.036178 | 0.045303 | 0 | 0.13372 | 0 | 0.19252 | 0.023122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1403 | 15.99% | CZ 4A | 14.1239 | 2.3202 | 3.6178 | 4.5303 | 0 | 4.5053 | 0 | 6.4864 | 0.77903 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.8231 | 15.99% | CZ 4A | 4.1383 | 0.67982 | 0 | 0 | 0 | 1.32 | 0 | 1.9005 | 0.22826 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.4528 | 15.99% | CZ 4A | 0 | 0 | 0.036178 | 0.045303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081481 | 15.99% | CZ 4A | 43.324 | 7.117 | 3.9543 | 4.9516 | 0 | 13.8195 | 0 | 19.8966 | 2.3896 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 118.336 | 15.99%
CZ 4B | 0.42105 | 0.068695 | 0.035848 | 0.05225 | 0 | 0.1463 | 0 | 0.26539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.211 | 0.8792% | CZ 4B | 14.1858 | 2.3144 | 3.5848 | 5.225 | 0 | 4.9291 | 0 | 8.9414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.6408 | 0.8792% | CZ 4B | 4.1564 | 0.67813 | 0 | 0 | 0 | 1.4442 | 0 | 2.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.0844 | 0.8792% | CZ 4B | 0 | 0 | 0.035848 | 0.05225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088099 | 0.8792% | CZ 4B | 43.5137 | 7.0994 | 3.9182 | 5.711 | 0 | 15.1197 | 0 | 27.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 125.6723 | 0.8792%
CZ 4C | 0.42571 | 0.068854 | 0.036516 | 0.08117 | 0 | 0.040752 | 0 | 0.20149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0759 | 2.698% | CZ 4C | 14.3428 | 2.3198 | 3.6516 | 8.117 | 0 | 1.373 | 0 | 6.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.053 | 2.698% | CZ 4C | 4.2024 | 0.67971 | 0 | 0 | 0 | 0.40229 | 0 | 1.9891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.4593 | 2.698% | CZ 4C | 0 | 0 | 0.036516 | 0.08117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11769 | 2.698% | CZ 4C | 43.9954 | 7.1159 | 3.9912 | 8.8719 | 0 | 4.2116 | 0 | 20.8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 111.8927 | 2.698%
CZ 5A | 0.41934 | 0.06874 | 0.037123 | 0.076506 | 0 | 0.081743 | 0 | 0.1844 | 0.020934 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1102 | 22.02% | CZ 5A | 14.1282 | 2.316 | 3.7123 | 7.6506 | 0 | 2.7541 | 0 | 6.2127 | 0.70531 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.9392 | 22.02% | CZ 5A | 4.1396 | 0.67858 | 0 | 0 | 0 | 0.80694 | 0 | 1.8203 | 0.20666 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.8379 | 22.02% | CZ 5A | 0 | 0 | 0.037123 | 0.076506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11363 | 22.02% | CZ 5A | 43.337 | 7.1041 | 4.0575 | 8.3621 | 0 | 8.4479 | 0 | 19.0569 | 2.1635 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 115.4123 | 22.02%
CZ 5B | 0.42304 | 0.06882 | 0.036846 | 0.10613 | 0 | 0.10883 | 0 | 0.25659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.2217 | 5.18% | CZ 5B | 14.253 | 2.3187 | 3.6846 | 10.6128 | 0 | 3.6667 | 0 | 8.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.6409 | 5.18% | CZ 5B | 4.1761 | 0.67937 | 0 | 0 | 0 | 1.0743 | 0 | 2.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.6486 | 5.18% | CZ 5B | 0 | 0 | 0.036846 | 0.10613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14297 | 5.18% | CZ 5B | 43.7198 | 7.1123 | 4.0273 | 11.5998 | 0 | 11.2473 | 0 | 26.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 127.1077 | 5.18%
CZ 5C | 0.42304 | 0.06882 | 0.037054 | 0.096774 | 0 | 0.016866 | 0 | 0.18873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.0527 | 0.1101% | CZ 5C | 14.253 | 2.3187 | 3.7054 | 9.6774 | 0 | 0.56824 | 0 | 6.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.3413 | 0.1101% | CZ 5C | 4.1761 | 0.67937 | 0 | 0 | 0 | 0.1665 | 0 | 1.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.0709 | 0.1101% | CZ 5C | 0 | 0 | 0.037054 | 0.096774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13383 | 0.1101% | CZ 5C | 43.7198 | 7.1123 | 4.05 | 10.5774 | 0 | 1.743 | 0 | 19.5044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 109.5902 | 0.1101%
CZ 6A | 0.45293 | 0.068786 | 0.037817 | 0.137 | 0 | 0.092945 | 0 | 0.19841 | 0.021812 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.2311 | 4.525% | CZ 6A | 15.2601 | 2.3175 | 3.7817 | 13.6998 | 0 | 3.1315 | 0 | 6.6849 | 0.73488 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 53.0706 | 4.525% | CZ 6A | 4.4712 | 0.67903 | 0 | 0 | 0 | 0.91753 | 0 | 1.9587 | 0.21532 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.4276 | 4.525% | CZ 6A | 0 | 0 | 0.037817 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17482 | 4.525% | CZ 6A | 46.809 | 7.1088 | 4.1335 | 14.9739 | 0 | 9.6056 | 0 | 20.5055 | 2.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 128.2737 | 4.525%
CZ 6B | 0.45488 | 0.068706 | 0.037637 | 0.08147 | 0 | 0.067886 | 0 | 0.21052 | 0.019282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1618 | 0.5032% | CZ 6B | 15.3257 | 2.3148 | 3.7637 | 8.147 | 0 | 2.2872 | 0 | 7.0927 | 0.64964 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.0409 | 0.5032% | CZ 6B | 4.4904 | 0.67824 | 0 | 0 | 0 | 0.67015 | 0 | 2.0782 | 0.19035 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.2931 | 0.5032% | CZ 6B | 0 | 0 | 0.037637 | 0.08147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11911 | 0.5032% | CZ 6B | 47.0103 | 7.1005 | 4.1137 | 8.9046 | 0 | 7.0157 | 0 | 21.7562 | 1.9927 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 120.7773 | 0.5032%
CZ 7 | 0.45493 | 0.06882 | 0.038639 | 0.16127 | 0 | 0.064216 | 0 | 0.19155 | 0.021356 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.2222 | 0.4193% | CZ 7 | 15.3272 | 2.3187 | 3.8639 | 16.1269 | 0 | 2.1636 | 0 | 6.4538 | 0.71952 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 54.4338 | 0.4193% | CZ 7 | 4.4909 | 0.67937 | 0 | 0 | 0 | 0.63392 | 0 | 1.891 | 0.21082 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.0918 | 0.4193% | CZ 7 | 0 | 0 | 0.038639 | 0.16127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19991 | 0.4193% | CZ 7 | 47.0151 | 7.1123 | 4.2232 | 17.6267 | 0 | 6.6365 | 0 | 19.7965 | 2.2071 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 127.5008 | 0.4193%
CZ 8 | 0.45985 | 0.069322 | 0.039748 | 0.26986 | 0 | 0.027749 | 0 | 0.17038 | 0.020672 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.279 | 0.0892% | CZ 8 | 15.4931 | 2.3356 | 3.9748 | 26.9858 | 0 | 0.93492 | 0 | 5.7404 | 0.69648 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 63.6213 | 0.0892% | CZ 8 | 4.5395 | 0.68432 | 0 | 0 | 0 | 0.27393 | 0 | 1.6819 | 0.20407 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.5696 | 0.0892% | CZ 8 | 0 | 0 | 0.039748 | 0.26986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30961 | 0.0892% | CZ 8 | 47.5238 | 7.1641 | 4.3445 | 29.4955 | 0 | 2.8678 | 0 | 17.6083 | 2.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 134.0238 | 0.0892%
US Weighted | 0.4182 | 0.068757 | 0.035631 | 0.047726 | 0 | 0.17206 | 0 | 0.20937 | 0.017763 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22142 | 1.1909 | 100% | US Weighted | 14.0898 | 2.3165 | 3.5631 | 4.7726 | 0 | 5.7971 | 0 | 7.054 | 0.59846 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.6518 | 100% | US Weighted | 4.1283 | 0.67874 | 0 | 0 | 0 | 1.6986 | 0 | 2.0668 | 0.17535 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.9336 | 100% | US Weighted | 0 | 0 | 0.035631 | 0.047726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083358 | 100% | US Weighted | 43.2193 | 7.1057 | 3.8945 | 5.2165 | 0 | 17.7821 | 0 | 21.6376 | 1.8357 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8833 | 123.5748 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.5029 | 0.068809 | 0.032774 | 0.00038769 | 0 | 0.5743 | 0 | 0.31518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.7161 | 2.683% | CZ 1A | 16.9437 | 2.3183 | 3.2774 | 0.038769 | 0 | 19.3491 | 0 | 10.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 60.0189 | 2.683% | CZ 1A | 4.9645 | 0.67926 | 0 | 0 | 0 | 5.6693 | 0 | 3.1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 16.6139 | 2.683% | CZ 1A | 0 | 0 | 0.032774 | 0.00038769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033161 | 2.683% | CZ 1A | 51.9733 | 7.1111 | 3.5822 | 0.042375 | 0 | 59.3518 | 0 | 32.5725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 177.5555 | 2.683%
CZ 1B | 0.4978 | 0.068706 | 0.032785 | 0.016713 | 0 | 0.5724 | 0 | 0.23268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.6429 | 0% | CZ 1B | 16.7717 | 2.3148 | 3.2785 | 1.6713 | 0 | 19.285 | 0 | 7.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 58.6336 | 0% | CZ 1B | 4.9141 | 0.67824 | 0 | 0 | 0 | 5.6505 | 0 | 2.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 15.7293 | 0% | CZ 1B | 0 | 0 | 0.032785 | 0.016713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049498 | 0% | CZ 1B | 51.4457 | 7.1005 | 3.5834 | 1.8267 | 0 | 59.1551 | 0 | 24.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 170.0806 | 0%
CZ 2A | 0.50378 | 0.068672 | 0.033622 | 0.011819 | 0 | 0.35307 | 0 | 0.25298 | 0.022234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.468 | 15.29% | CZ 2A | 16.9732 | 2.3137 | 3.3622 | 1.1819 | 0 | 11.8955 | 0 | 8.5233 | 0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.4717 | 15.29% | CZ 2A | 4.9732 | 0.67791 | 0 | 0 | 0 | 3.4854 | 0 | 2.4973 | 0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 14.0428 | 15.29% | CZ 2A | 0 | 0 | 0.033622 | 0.011819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045441 | 15.29% | CZ 2A | 52.064 | 7.097 | 3.6749 | 1.2918 | 0 | 36.4885 | 0 | 26.1445 | 2.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 151.9806 | 15.29%
CZ 2B | 0.51677 | 0.068729 | 0.03366 | 0.015519 | 0 | 0.31906 | 0 | 0.28809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.4636 | 3.321% | CZ 2B | 17.4109 | 2.3156 | 3.366 | 1.5519 | 0 | 10.7498 | 0 | 9.7062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.5733 | 3.321% | CZ 2B | 5.1014 | 0.67847 | 0 | 0 | 0 | 3.1497 | 0 | 2.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 13.963 | 3.321% | CZ 2B | 0 | 0 | 0.03366 | 0.015519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04918 | 3.321% | CZ 2B | 53.4066 | 7.1029 | 3.6791 | 1.6963 | 0 | 32.9741 | 0 | 29.7731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 151.5542 | 3.321%
CZ 3A | 0.5031 | 0.068718 | 0.035046 | 0.035637 | 0 | 0.21737 | 0 | 0.25094 | 0.022234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3548 | 16.83% | CZ 3A | 16.9502 | 2.3152 | 3.5046 | 3.5637 | 0 | 7.3234 | 0 | 8.4546 | 0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.3336 | 16.83% | CZ 3A | 4.9664 | 0.67836 | 0 | 0 | 0 | 2.1458 | 0 | 2.4772 | 0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.6767 | 16.83% | CZ 3A | 0 | 0 | 0.035046 | 0.035637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070683 | 16.83% | CZ 3A | 51.9933 | 7.1017 | 3.8305 | 3.8951 | 0 | 22.4641 | 0 | 25.9337 | 2.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 140.4384 | 16.83%
CZ 3B | 0.51403 | 0.068718 | 0.034674 | 0.033319 | 0 | 0.22265 | 0 | 0.27348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3687 | 8.207% | CZ 3B | 17.3184 | 2.3152 | 3.4674 | 3.3319 | 0 | 7.5016 | 0 | 9.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.6213 | 8.207% | CZ 3B | 5.0743 | 0.67836 | 0 | 0 | 0 | 2.198 | 0 | 2.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.8399 | 8.207% | CZ 3B | 0 | 0 | 0.034674 | 0.033319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067992 | 8.207% | CZ 3B | 53.1228 | 7.1017 | 3.7898 | 3.6417 | 0 | 23.0105 | 0 | 28.2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 141.852 | 8.207%
CZ 3C | 0.51447 | 0.068832 | 0.035192 | 0.016487 | 0 | 0.099361 | 0 | 0.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.166 | 1.253% | CZ 3C | 17.3334 | 2.3191 | 3.5192 | 1.6487 | 0 | 3.3477 | 0 | 7.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 42.7127 | 1.253% | CZ 3C | 5.0787 | 0.67948 | 0 | 0 | 0 | 0.98086 | 0 | 2.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.0006 | 1.253% | CZ 3C | 0 | 0 | 0.035192 | 0.016487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051679 | 1.253% | CZ 3C | 53.1687 | 7.1135 | 3.8465 | 1.802 | 0 | 10.2686 | 0 | 21.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 120.8142 | 1.253%
CZ 4A | 0.50567 | 0.068866 | 0.036178 | 0.077351 | 0 | 0.15258 | 0 | 0.25267 | 0.02294 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3381 | 15.99% | CZ 4A | 17.037 | 2.3202 | 3.6178 | 7.7351 | 0 | 5.1407 | 0 | 8.5129 | 0.77289 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.6094 | 15.99% | CZ 4A | 4.9918 | 0.67982 | 0 | 0 | 0 | 1.5062 | 0 | 2.4943 | 0.22646 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0881 | 15.99% | CZ 4A | 0 | 0 | 0.036178 | 0.077351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11353 | 15.99% | CZ 4A | 52.2595 | 7.117 | 3.9543 | 8.4544 | 0 | 15.7687 | 0 | 26.1127 | 2.3708 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 138.9596 | 15.99%
CZ 4B | 0.50599 | 0.068695 | 0.035848 | 0.068196 | 0 | 0.16761 | 0 | 0.29306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3612 | 0.8792% | CZ 4B | 17.0477 | 2.3144 | 3.5848 | 6.8196 | 0 | 5.6471 | 0 | 9.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.7601 | 0.8792% | CZ 4B | 4.995 | 0.67813 | 0 | 0 | 0 | 1.6546 | 0 | 2.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.4102 | 0.8792% | CZ 4B | 0 | 0 | 0.035848 | 0.068196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10404 | 0.8792% | CZ 4B | 52.2925 | 7.0994 | 3.9182 | 7.4538 | 0 | 17.3221 | 0 | 30.2866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 141.2947 | 0.8792%
CZ 4C | 0.51065 | 0.068854 | 0.03652 | 0.10971 | 0 | 0.045755 | 0 | 0.23016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.2235 | 2.698% | CZ 4C | 17.2048 | 2.3198 | 3.652 | 10.971 | 0 | 1.5416 | 0 | 7.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.9165 | 2.698% | CZ 4C | 5.041 | 0.67971 | 0 | 0 | 0 | 0.45168 | 0 | 2.2721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 10.634 | 2.698% | CZ 4C | 0 | 0 | 0.03652 | 0.10971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14623 | 2.698% | CZ 4C | 52.7742 | 7.1159 | 3.9916 | 11.9913 | 0 | 4.7286 | 0 | 23.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 127.3104 | 2.698%
CZ 5A | 0.50541 | 0.06874 | 0.037123 | 0.11934 | 0 | 0.092262 | 0 | 0.24776 | 0.020684 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3131 | 22.02% | CZ 5A | 17.0281 | 2.316 | 3.7123 | 11.9341 | 0 | 3.1085 | 0 | 8.3474 | 0.69687 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 54.616 | 22.02% | CZ 5A | 4.9892 | 0.67858 | 0 | 0 | 0 | 0.91078 | 0 | 2.4458 | 0.20418 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.4181 | 22.02% | CZ 5A | 0 | 0 | 0.037123 | 0.11934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15646 | 22.02% | CZ 5A | 52.2324 | 7.1041 | 4.0575 | 13.044 | 0 | 9.5349 | 0 | 25.6051 | 2.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 136.6377 | 22.02%
CZ 5B | 0.50893 | 0.06882 | 0.03685 | 0.13453 | 0 | 0.1233 | 0 | 0.29476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.389 | 5.18% | CZ 5B | 17.1468 | 2.3187 | 3.685 | 13.4526 | 0 | 4.1543 | 0 | 9.9308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 58.1611 | 5.18% | CZ 5B | 5.024 | 0.67937 | 0 | 0 | 0 | 1.2172 | 0 | 2.9097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0199 | 5.18% | CZ 5B | 0 | 0 | 0.03685 | 0.13453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17138 | 5.18% | CZ 5B | 52.5963 | 7.1123 | 4.0277 | 14.7037 | 0 | 12.7431 | 0 | 30.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 144.5674 | 5.18%
CZ 5C | 0.50742 | 0.06882 | 0.037054 | 0.13073 | 0 | 0.018781 | 0 | 0.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.203 | 0.1101% | CZ 5C | 17.0957 | 2.3187 | 3.7054 | 13.0726 | 0 | 0.63275 | 0 | 7.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 51.6563 | 0.1101% | CZ 5C | 5.009 | 0.67937 | 0 | 0 | 0 | 0.1854 | 0 | 2.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 10.2193 | 0.1101% | CZ 5C | 0 | 0 | 0.037054 | 0.13073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16778 | 0.1101% | CZ 5C | 52.4397 | 7.1123 | 4.05 | 14.2883 | 0 | 1.9409 | 0 | 22.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 125.3247 | 0.1101%
CZ 6A | 0.53381 | 0.068786 | 0.037821 | 0.17419 | 0 | 0.10277 | 0 | 0.26847 | 0.021538 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.4292 | 4.525% | CZ 6A | 17.9849 | 2.3175 | 3.7821 | 17.419 | 0 | 3.4625 | 0 | 9.0451 | 0.72566 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 62.2096 | 4.525% | CZ 6A | 5.2696 | 0.67903 | 0 | 0 | 0 | 1.0145 | 0 | 2.6502 | 0.21262 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0155 | 4.525% | CZ 6A | 0 | 0 | 0.037821 | 0.17419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21201 | 4.525% | CZ 6A | 55.1673 | 7.1088 | 4.1339 | 19.039 | 0 | 10.6208 | 0 | 27.745 | 2.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 148.9628 | 4.525%
CZ 6B | 0.53474 | 0.068706 | 0.037645 | 0.21191 | 0 | 0.076307 | 0 | 0.28483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.4359 | 0.5032% | CZ 6B | 18.0164 | 2.3148 | 3.7645 | 21.1908 | 0 | 2.5709 | 0 | 9.5964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 64.9266 | 0.5032% | CZ 6B | 5.2788 | 0.67824 | 0 | 0 | 0 | 0.75328 | 0 | 2.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.7116 | 0.5032% | CZ 6B | 0 | 0 | 0.037645 | 0.21191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24955 | 0.5032% | CZ 6B | 55.2639 | 7.1005 | 4.1146 | 23.1615 | 0 | 7.8861 | 0 | 29.4362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 149.885 | 0.5032%
CZ 7 | 0.51653 | 0.06882 | 0.038643 | 0.21316 | 0 | 0.070461 | 0 | 0.29854 | 0.021367 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.4493 | 0.4193% | CZ 7 | 17.4029 | 2.3187 | 3.8643 | 21.3163 | 0 | 2.374 | 0 | 10.0583 | 0.7199 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 65.5271 | 0.4193% | CZ 7 | 5.099 | 0.67937 | 0 | 0 | 0 | 0.69557 | 0 | 2.9471 | 0.21093 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.8215 | 0.4193% | CZ 7 | 0 | 0 | 0.038643 | 0.21316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25181 | 0.4193% | CZ 7 | 53.3819 | 7.1123 | 4.2237 | 23.2987 | 0 | 7.2819 | 0 | 30.853 | 2.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 151.282 | 0.4193%
CZ 8 | 0.54021 | 0.069322 | 0.039764 | 0.3461 | 0 | 0.030176 | 0 | 0.33864 | 0.0218 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.6078 | 0.0892% | CZ 8 | 18.2007 | 2.3356 | 3.9764 | 34.61 | 0 | 1.0167 | 0 | 11.4094 | 0.73449 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 79.7561 | 0.0892% | CZ 8 | 5.3328 | 0.68432 | 0 | 0 | 0 | 0.29789 | 0 | 3.343 | 0.21521 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0627 | 0.0892% | CZ 8 | 0 | 0 | 0.039764 | 0.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38586 | 0.0892% | CZ 8 | 55.8292 | 7.1641 | 4.3462 | 37.8287 | 0 | 3.1186 | 0 | 34.9975 | 2.253 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 168.4595 | 0.0892%
US Weighted | 0.50779 | 0.068757 | 0.035631 | 0.070745 | 0 | 0.19528 | 0 | 0.25841 | 0.016448 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2218 | 1.3748 | 100% | US Weighted | 17.1082 | 2.3165 | 3.5631 | 7.0745 | 0 | 6.5792 | 0 | 8.7061 | 0.55417 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.3746 | 100% | US Weighted | 5.0127 | 0.67874 | 0 | 0 | 0 | 1.9277 | 0 | 2.5509 | 0.16237 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.5219 | 100% | US Weighted | 0 | 0 | 0.035631 | 0.070745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10638 | 100% | US Weighted | 52.4779 | 7.1057 | 3.8945 | 7.7325 | 0 | 20.1811 | 0 | 26.7053 | 1.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9222 | 142.7191 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.56074 | 0.13134 | 0.033507 | 0.00016122 | 0 | 0.76892 | 0 | 0.43816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.1552 | 2.683% | CZ 1A | 18.8922 | 4.425 | 3.3507 | 0.016122 | 0 | 25.9062 | 0 | 14.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 74.8458 | 2.683% | CZ 1A | 5.5354 | 1.2965 | 0 | 0 | 0 | 7.5905 | 0 | 4.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 20.9434 | 2.683% | CZ 1A | 0 | 0 | 0.033507 | 0.00016122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033668 | 2.683% | CZ 1A | 57.9503 | 13.5734 | 3.6623 | 0.017621 | 0 | 79.4651 | 0 | 45.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 222.9359 | 2.683%
CZ 1B | 0.56074 | 0.13118 | 0.033511 | 0.0096808 | 0 | 0.79208 | 0 | 0.44423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.1938 | 0% | CZ 1B | 18.8922 | 4.4196 | 3.3511 | 0.96808 | 0 | 26.6864 | 0 | 14.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.7772 | 0% | CZ 1B | 5.5354 | 1.295 | 0 | 0 | 0 | 7.8191 | 0 | 4.3852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.2302 | 0% | CZ 1B | 0 | 0 | 0.033511 | 0.0096808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043191 | 0% | CZ 1B | 57.9503 | 13.5569 | 3.6627 | 1.0581 | 0 | 81.8583 | 0 | 45.9092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 226.98 | 0%
CZ 2A | 0.56074 | 0.13113 | 0.034363 | 0.017865 | 0 | 0.57123 | 0 | 0.36353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.9013 | 15.29% | CZ 2A | 18.8922 | 4.4181 | 3.4363 | 1.7865 | 0 | 19.2458 | 0 | 12.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 67.52 | 15.29% | CZ 2A | 5.5354 | 1.2945 | 0 | 0 | 0 | 5.639 | 0 | 3.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 18.2531 | 15.29% | CZ 2A | 0 | 0 | 0.034363 | 0.017865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052227 | 15.29% | CZ 2A | 57.9503 | 13.5522 | 3.7559 | 1.9526 | 0 | 59.035 | 0 | 37.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 196.8002 | 15.29%
CZ 2B | 0.56074 | 0.13122 | 0.034401 | 0.012387 | 0 | 0.4272 | 0 | 0.38194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7703 | 3.321% | CZ 2B | 18.8922 | 4.4212 | 3.4401 | 1.2387 | 0 | 14.3931 | 0 | 12.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 62.7465 | 3.321% | CZ 2B | 5.5354 | 1.2954 | 0 | 0 | 0 | 4.2172 | 0 | 3.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0138 | 3.321% | CZ 2B | 0 | 0 | 0.034401 | 0.012387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046788 | 3.321% | CZ 2B | 57.9503 | 13.5616 | 3.76 | 1.3539 | 0 | 44.1496 | 0 | 39.4717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 183.2318 | 3.321%
CZ 3A | 0.56074 | 0.1312 | 0.03581 | 0.068522 | 0 | 0.34656 | 0 | 0.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7289 | 16.83% | CZ 3A | 18.8922 | 4.4204 | 3.581 | 6.8522 | 0 | 11.6763 | 0 | 12.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 65.169 | 16.83% | CZ 3A | 5.5354 | 1.2952 | 0 | 0 | 0 | 3.4211 | 0 | 3.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.0376 | 16.83% | CZ 3A | 0 | 0 | 0.03581 | 0.068522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10433 | 16.83% | CZ 3A | 57.9503 | 13.5592 | 3.914 | 7.4895 | 0 | 35.816 | 0 | 37.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 179.301 | 16.83%
CZ 3B | 0.56074 | 0.1312 | 0.035422 | 0.024413 | 0 | 0.29511 | 0 | 0.38539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.6547 | 8.207% | CZ 3B | 18.8922 | 4.4204 | 3.5422 | 2.4413 | 0 | 9.9427 | 0 | 12.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 59.7164 | 8.207% | CZ 3B | 5.5354 | 1.2952 | 0 | 0 | 0 | 2.9132 | 0 | 3.8044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.7437 | 8.207% | CZ 3B | 0 | 0 | 0.035422 | 0.024413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059835 | 8.207% | CZ 3B | 57.9503 | 13.5592 | 3.8716 | 2.6684 | 0 | 30.4985 | 0 | 39.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 171.3612 | 8.207%
CZ 3C | 0.56074 | 0.13118 | 0.03594 | 0.012091 | 0 | 0.16104 | 0 | 0.32684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.4502 | 1.253% | CZ 3C | 18.8922 | 4.4196 | 3.594 | 1.2091 | 0 | 5.4256 | 0 | 11.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 52.0454 | 1.253% | CZ 3C | 5.5354 | 1.295 | 0 | 0 | 0 | 1.5897 | 0 | 3.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.842 | 1.253% | CZ 3C | 0 | 0 | 0.03594 | 0.012091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048032 | 1.253% | CZ 3C | 57.9503 | 13.5569 | 3.9283 | 1.3216 | 0 | 16.6425 | 0 | 33.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 150.1616 | 1.253%
CZ 4A | 0.56074 | 0.131 | 0.036961 | 0.15109 | 0 | 0.23398 | 0 | 0.36901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7052 | 15.99% | CZ 4A | 18.8922 | 4.4135 | 3.6961 | 15.1093 | 0 | 7.8832 | 0 | 12.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.9202 | 15.99% | CZ 4A | 5.5354 | 1.2932 | 0 | 0 | 0 | 2.3098 | 0 | 3.6428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.9766 | 15.99% | CZ 4A | 0 | 0 | 0.036961 | 0.15109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18805 | 15.99% | CZ 4A | 57.9503 | 13.538 | 4.0399 | 16.5145 | 0 | 24.1812 | 0 | 38.1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 177.3447 | 15.99%
CZ 4B | 0.56074 | 0.1311 | 0.036616 | 0.053652 | 0 | 0.21689 | 0 | 0.41968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.6411 | 0.8792% | CZ 4B | 18.8922 | 4.4169 | 3.6616 | 5.3652 | 0 | 7.3073 | 0 | 14.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 61.2761 | 0.8792% | CZ 4B | 5.5354 | 1.2942 | 0 | 0 | 0 | 2.141 | 0 | 4.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.3091 | 0.8792% | CZ 4B | 0 | 0 | 0.036616 | 0.053652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090268 | 0.8792% | CZ 4B | 57.9503 | 13.5486 | 4.0021 | 5.8641 | 0 | 22.4146 | 0 | 43.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 170.1367 | 0.8792%
CZ 4C | 0.56074 | 0.13085 | 0.037295 | 0.089158 | 0 | 0.066735 | 0 | 0.33921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.4464 | 2.698% | CZ 4C | 18.8922 | 4.4085 | 3.7295 | 8.9158 | 0 | 2.2484 | 0 | 11.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 57.1163 | 2.698% | CZ 4C | 5.5354 | 1.2917 | 0 | 0 | 0 | 0.65878 | 0 | 3.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.03 | 2.698% | CZ 4C | 0 | 0 | 0.037295 | 0.089158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12645 | 2.698% | CZ 4C | 57.9503 | 13.5227 | 4.0764 | 9.745 | 0 | 6.8968 | 0 | 35.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 150.2322 | 2.698%
CZ 5A | 0.56074 | 0.13104 | 0.037913 | 0.21956 | 0 | 0.14438 | 0 | 0.36584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.6819 | 22.02% | CZ 5A | 18.8922 | 4.415 | 3.7913 | 21.9558 | 0 | 4.8643 | 0 | 12.3259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 73.7377 | 22.02% | CZ 5A | 5.5354 | 1.2936 | 0 | 0 | 0 | 1.4252 | 0 | 3.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.0612 | 22.02% | CZ 5A | 0 | 0 | 0.037913 | 0.21956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25747 | 22.02% | CZ 5A | 57.9503 | 13.5427 | 4.1439 | 23.9977 | 0 | 14.9207 | 0 | 37.8087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 175.3487 | 22.02%
CZ 5B | 0.56074 | 0.13104 | 0.037629 | 0.10993 | 0 | 0.17592 | 0 | 0.42494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.6626 | 5.18% | CZ 5B | 18.8922 | 4.415 | 3.7629 | 10.9933 | 0 | 5.927 | 0 | 14.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 65.8007 | 5.18% | CZ 5B | 5.5354 | 1.2936 | 0 | 0 | 0 | 1.7366 | 0 | 4.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.956 | 5.18% | CZ 5B | 0 | 0 | 0.037629 | 0.10993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14756 | 5.18% | CZ 5B | 57.9503 | 13.5427 | 4.1129 | 12.0156 | 0 | 18.1806 | 0 | 43.9164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 172.7033 | 5.18%
CZ 5C | 0.56074 | 0.13084 | 0.037829 | 0.10768 | 0 | 0.038951 | 0 | 0.32826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.4267 | 0.1101% | CZ 5C | 18.8922 | 4.4081 | 3.7829 | 10.7675 | 0 | 1.3123 | 0 | 11.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 57.7159 | 0.1101% | CZ 5C | 5.5354 | 1.2916 | 0 | 0 | 0 | 0.38452 | 0 | 3.2405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 12.6475 | 0.1101% | CZ 5C | 0 | 0 | 0.037829 | 0.10768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1455 | 0.1101% | CZ 5C | 57.9503 | 13.5215 | 4.1347 | 11.7689 | 0 | 4.0255 | 0 | 33.9246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 148.3101 | 0.1101%
CZ 6A | 0.56074 | 0.13099 | 0.038616 | 0.3145 | 0 | 0.15689 | 0 | 0.39242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.8166 | 4.525% | CZ 6A | 18.8922 | 4.4131 | 3.8616 | 31.4505 | 0 | 5.2858 | 0 | 13.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 84.6176 | 4.525% | CZ 6A | 5.5354 | 1.293 | 0 | 0 | 0 | 1.5487 | 0 | 3.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.4465 | 4.525% | CZ 6A | 0 | 0 | 0.038616 | 0.3145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35312 | 4.525% | CZ 6A | 57.9503 | 13.5369 | 4.2207 | 34.3754 | 0 | 16.2138 | 0 | 40.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 189.8369 | 4.525%
CZ 6B | 0.56074 | 0.13088 | 0.038435 | 0.19394 | 0 | 0.11514 | 0 | 0.4104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.6719 | 0.5032% | CZ 6B | 18.8922 | 4.4097 | 3.8435 | 19.3939 | 0 | 3.8794 | 0 | 13.8272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 71.7391 | 0.5032% | CZ 6B | 5.5354 | 1.292 | 0 | 0 | 0 | 1.1367 | 0 | 4.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.211 | 0.5032% | CZ 6B | 0 | 0 | 0.038435 | 0.19394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23237 | 0.5032% | CZ 6B | 57.9503 | 13.5263 | 4.201 | 21.1976 | 0 | 11.8998 | 0 | 42.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 174.1732 | 0.5032%
CZ 7 | 0.56074 | 0.1308 | 0.039441 | 0.37676 | 0 | 0.1185 | 0 | 0.42306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.8717 | 0.4193% | CZ 7 | 18.8922 | 4.407 | 3.9441 | 37.6762 | 0 | 3.9923 | 0 | 14.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 90.6587 | 0.4193% | CZ 7 | 5.5354 | 1.2912 | 0 | 0 | 0 | 1.1697 | 0 | 4.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.3682 | 0.4193% | CZ 7 | 0 | 0 | 0.039441 | 0.37676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4162 | 0.4193% | CZ 7 | 57.9503 | 13.518 | 4.3109 | 41.1801 | 0 | 12.2461 | 0 | 43.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 195.9121 | 0.4193%
CZ 8 | 0.56074 | 0.13008 | 0.040562 | 0.55653 | 0 | 0.061584 | 0 | 0.45935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.0313 | 0.0892% | CZ 8 | 18.8922 | 4.3828 | 4.0562 | 55.6534 | 0 | 2.0749 | 0 | 15.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 108.0288 | 0.0892% | CZ 8 | 5.5354 | 1.2842 | 0 | 0 | 0 | 0.60793 | 0 | 4.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.1575 | 0.0892% | CZ 8 | 0 | 0 | 0.040562 | 0.55653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5971 | 0.0892% | CZ 8 | 57.9503 | 13.4438 | 4.4334 | 60.8291 | 0 | 6.3645 | 0 | 47.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 213.4778 | 0.0892%
US Weighted | 0.56074 | 0.13109 | 0.036401 | 0.11532 | 0 | 0.29702 | 0 | 0.37375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7367 | 100% | US Weighted | 18.8922 | 4.4168 | 3.6401 | 11.5321 | 0 | 10.0072 | 0 | 12.5923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.5738 | 100% | US Weighted | 5.5354 | 1.2941 | 0 | 0 | 0 | 2.9321 | 0 | 3.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6467 | 100% | US Weighted | 0 | 0 | 0.036401 | 0.11532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15172 | 100% | US Weighted | 57.9503 | 13.5481 | 3.9786 | 12.6046 | 0 | 30.6962 | 0 | 38.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 180.3883 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.56074 | 0.13134 | 0.033507 | 0.00018041 | 0 | 0.82355 | 0 | 0.46549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.2372 | 2.683% | CZ 1A | 18.8922 | 4.425 | 3.3507 | 0.018041 | 0 | 27.7468 | 0 | 15.6832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 77.6091 | 2.683% | CZ 1A | 5.5354 | 1.2965 | 0 | 0 | 0 | 8.1298 | 0 | 4.5952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.7524 | 2.683% | CZ 1A | 0 | 0 | 0.033507 | 0.00018041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033687 | 2.683% | CZ 1A | 57.9503 | 13.5734 | 3.6623 | 0.019719 | 0 | 85.1112 | 0 | 48.1068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 231.4082 | 2.683%
CZ 1B | 0.56074 | 0.13118 | 0.033511 | 0.012571 | 0 | 0.84568 | 0 | 0.47089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.277 | 0% | CZ 1B | 18.8922 | 4.4196 | 3.3511 | 1.2571 | 0 | 28.4925 | 0 | 15.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.7708 | 0% | CZ 1B | 5.5354 | 1.295 | 0 | 0 | 0 | 8.3483 | 0 | 4.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 22.0227 | 0% | CZ 1B | 0 | 0 | 0.033511 | 0.012571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046082 | 0% | CZ 1B | 57.9503 | 13.5569 | 3.6627 | 1.374 | 0 | 87.3983 | 0 | 48.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 235.5919 | 0%
CZ 2A | 0.56074 | 0.13113 | 0.034378 | 0.030367 | 0 | 0.73315 | 0 | 0.48684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.199 | 15.29% | CZ 2A | 18.8922 | 4.4181 | 3.4378 | 3.0367 | 0 | 24.701 | 0 | 16.4023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 78.3812 | 15.29% | CZ 2A | 5.5354 | 1.2945 | 0 | 0 | 0 | 7.2374 | 0 | 4.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.0687 | 15.29% | CZ 2A | 0 | 0 | 0.034378 | 0.030367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064745 | 15.29% | CZ 2A | 57.9503 | 13.5522 | 3.7575 | 3.3191 | 0 | 75.7682 | 0 | 50.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 227.6446 | 15.29%
CZ 2B | 0.56074 | 0.13122 | 0.034401 | 0.021515 | 0 | 0.54143 | 0 | 0.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.0075 | 3.321% | CZ 2B | 18.8922 | 4.4212 | 3.4401 | 2.1515 | 0 | 18.2418 | 0 | 16.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 71.3444 | 3.321% | CZ 2B | 5.5354 | 1.2954 | 0 | 0 | 0 | 5.3448 | 0 | 4.8944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 19.2656 | 3.321% | CZ 2B | 0 | 0 | 0.034401 | 0.021515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055916 | 3.321% | CZ 2B | 57.9503 | 13.5616 | 3.76 | 2.3516 | 0 | 55.9552 | 0 | 51.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 207.8029 | 3.321%
CZ 3A | 0.56074 | 0.1312 | 0.035821 | 0.10558 | 0 | 0.39324 | 0 | 0.43171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.8807 | 16.83% | CZ 3A | 18.8922 | 4.4204 | 3.5821 | 10.558 | 0 | 13.2489 | 0 | 14.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 72.7399 | 16.83% | CZ 3A | 5.5354 | 1.2952 | 0 | 0 | 0 | 3.8819 | 0 | 4.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.1698 | 16.83% | CZ 3A | 0 | 0 | 0.035821 | 0.10558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1414 | 16.83% | CZ 3A | 57.9503 | 13.5592 | 3.9153 | 11.5398 | 0 | 40.64 | 0 | 44.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 195.2053 | 16.83%
CZ 3B | 0.56074 | 0.1312 | 0.035434 | 0.037814 | 0 | 0.34163 | 0 | 0.45365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7829 | 8.207% | CZ 3B | 18.8922 | 4.4204 | 3.5434 | 3.7814 | 0 | 11.51 | 0 | 15.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 64.9248 | 8.207% | CZ 3B | 5.5354 | 1.2952 | 0 | 0 | 0 | 3.3724 | 0 | 4.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.8768 | 8.207% | CZ 3B | 0 | 0 | 0.035434 | 0.037814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073247 | 8.207% | CZ 3B | 57.9503 | 13.5592 | 3.8729 | 4.133 | 0 | 35.306 | 0 | 46.8832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 184.6893 | 8.207%
CZ 3C | 0.56074 | 0.13118 | 0.035952 | 0.018417 | 0 | 0.17428 | 0 | 0.39084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.5338 | 1.253% | CZ 3C | 18.8922 | 4.4196 | 3.5952 | 1.8417 | 0 | 5.8717 | 0 | 13.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 55.2816 | 1.253% | CZ 3C | 5.5354 | 1.295 | 0 | 0 | 0 | 1.7204 | 0 | 3.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.6045 | 1.253% | CZ 3C | 0 | 0 | 0.035952 | 0.018417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054369 | 1.253% | CZ 3C | 57.9503 | 13.5569 | 3.9295 | 2.013 | 0 | 18.0111 | 0 | 40.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 158.8369 | 1.253%
CZ 4A | 0.56074 | 0.131 | 0.036977 | 0.24478 | 0 | 0.24931 | 0 | 0.41864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.8639 | 15.99% | CZ 4A | 18.8922 | 4.4135 | 3.6977 | 24.4785 | 0 | 8.3997 | 0 | 14.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 81.4794 | 15.99% | CZ 4A | 5.5354 | 1.2932 | 0 | 0 | 0 | 2.4611 | 0 | 4.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6179 | 15.99% | CZ 4A | 0 | 0 | 0.036977 | 0.24478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28176 | 15.99% | CZ 4A | 57.9503 | 13.538 | 4.0416 | 26.755 | 0 | 25.7652 | 0 | 43.2652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 194.2999 | 15.99%
CZ 4B | 0.56074 | 0.1311 | 0.036635 | 0.088214 | 0 | 0.23643 | 0 | 0.49419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.7697 | 0.8792% | CZ 4B | 18.8922 | 4.4169 | 3.6635 | 8.8214 | 0 | 7.9658 | 0 | 16.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 67.903 | 0.8792% | CZ 4B | 5.5354 | 1.2942 | 0 | 0 | 0 | 2.334 | 0 | 4.8784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.2375 | 0.8792% | CZ 4B | 0 | 0 | 0.036635 | 0.088214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12485 | 0.8792% | CZ 4B | 57.9503 | 13.5486 | 4.0042 | 9.6418 | 0 | 24.4344 | 0 | 51.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 183.6363 | 0.8792%
CZ 4C | 0.56074 | 0.13085 | 0.037318 | 0.15473 | 0 | 0.07102 | 0 | 0.39723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.5743 | 2.698% | CZ 4C | 18.8922 | 4.4085 | 3.7318 | 15.4732 | 0 | 2.3928 | 0 | 13.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 65.775 | 2.698% | CZ 4C | 5.5354 | 1.2917 | 0 | 0 | 0 | 0.70108 | 0 | 3.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.645 | 2.698% | CZ 4C | 0 | 0 | 0.037318 | 0.15473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19205 | 2.698% | CZ 4C | 57.9503 | 13.5227 | 4.0789 | 16.9122 | 0 | 7.3396 | 0 | 41.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 163.8406 | 2.698%
CZ 5A | 0.56074 | 0.13104 | 0.037929 | 0.32096 | 0 | 0.15791 | 0 | 0.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.9049 | 22.02% | CZ 5A | 18.8922 | 4.415 | 3.7929 | 32.0957 | 0 | 5.3204 | 0 | 15.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 87.9759 | 22.02% | CZ 5A | 5.5354 | 1.2936 | 0 | 0 | 0 | 1.5589 | 0 | 4.6782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.2616 | 22.02% | CZ 5A | 0 | 0 | 0.037929 | 0.32096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35889 | 22.02% | CZ 5A | 57.9503 | 13.5427 | 4.1456 | 35.0806 | 0 | 16.3198 | 0 | 48.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 198.9997 | 22.02%
CZ 5B | 0.56074 | 0.13104 | 0.037645 | 0.16808 | 0 | 0.1951 | 0 | 0.54114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.8561 | 5.18% | CZ 5B | 18.8922 | 4.415 | 3.7645 | 16.8083 | 0 | 6.5732 | 0 | 18.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.1782 | 5.18% | CZ 5B | 5.5354 | 1.2936 | 0 | 0 | 0 | 1.9259 | 0 | 5.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.2924 | 5.18% | CZ 5B | 0 | 0 | 0.037645 | 0.16808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20573 | 5.18% | CZ 5B | 57.9503 | 13.5427 | 4.1146 | 18.3715 | 0 | 20.1628 | 0 | 55.9246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 193.051 | 5.18%
CZ 5C | 0.56074 | 0.13084 | 0.037856 | 0.1787 | 0 | 0.03633 | 0 | 0.39055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.5574 | 0.1101% | CZ 5C | 18.8922 | 4.4081 | 3.7856 | 17.8696 | 0 | 1.224 | 0 | 13.1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 66.8311 | 0.1101% | CZ 5C | 5.5354 | 1.2916 | 0 | 0 | 0 | 0.35864 | 0 | 3.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.2365 | 0.1101% | CZ 5C | 0 | 0 | 0.037856 | 0.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21655 | 0.1101% | CZ 5C | 57.9503 | 13.5215 | 4.1376 | 19.5315 | 0 | 3.7546 | 0 | 40.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 162.2423 | 0.1101%
CZ 6A | 0.56074 | 0.13099 | 0.038627 | 0.44729 | 0 | 0.17258 | 0 | 0.52107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.0937 | 4.525% | CZ 6A | 18.8922 | 4.4131 | 3.8627 | 44.7292 | 0 | 5.8145 | 0 | 17.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 102.7606 | 4.525% | CZ 6A | 5.5354 | 1.293 | 0 | 0 | 0 | 1.7037 | 0 | 5.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.8714 | 4.525% | CZ 6A | 0 | 0 | 0.038627 | 0.44729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48592 | 4.525% | CZ 6A | 57.9503 | 13.5369 | 4.222 | 48.889 | 0 | 17.8356 | 0 | 53.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 219.2689 | 4.525%
CZ 6B | 0.56074 | 0.13088 | 0.038451 | 0.28289 | 0 | 0.12671 | 0 | 0.55387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.9159 | 0.5032% | CZ 6B | 18.8922 | 4.4097 | 3.8451 | 28.289 | 0 | 4.2691 | 0 | 18.6607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 85.859 | 0.5032% | CZ 6B | 5.5354 | 1.292 | 0 | 0 | 0 | 1.2509 | 0 | 5.4676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.7414 | 0.5032% | CZ 6B | 0 | 0 | 0.038451 | 0.28289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32134 | 0.5032% | CZ 6B | 57.9503 | 13.5263 | 4.2027 | 30.9199 | 0 | 13.0952 | 0 | 57.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 199.9191 | 0.5032%
CZ 7 | 0.56074 | 0.1308 | 0.039453 | 0.54722 | 0 | 0.12879 | 0 | 0.54481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.1742 | 0.4193% | CZ 7 | 18.8922 | 4.407 | 3.9453 | 54.7217 | 0 | 4.339 | 0 | 18.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 112.1538 | 0.4193% | CZ 7 | 5.5354 | 1.2912 | 0 | 0 | 0 | 1.2713 | 0 | 5.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6716 | 0.4193% | CZ 7 | 0 | 0 | 0.039453 | 0.54722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58667 | 0.4193% | CZ 7 | 57.9503 | 13.518 | 4.3122 | 59.8109 | 0 | 13.3095 | 0 | 56.3038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 228.1893 | 0.4193%
CZ 8 | 0.56074 | 0.13008 | 0.04057 | 0.74005 | 0 | 0.059658 | 0 | 0.57434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 2.3278 | 0.0892% | CZ 8 | 18.8922 | 4.3828 | 4.057 | 74.0051 | 0 | 2.01 | 0 | 19.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 130.1909 | 0.0892% | CZ 8 | 5.5354 | 1.2842 | 0 | 0 | 0 | 0.58892 | 0 | 5.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.2737 | 0.0892% | CZ 8 | 0 | 0 | 0.04057 | 0.74005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78062 | 0.0892% | CZ 8 | 57.9503 | 13.4438 | 4.4343 | 80.8876 | 0 | 6.1654 | 0 | 59.3565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 245.2225 | 0.0892%
US Weighted | 0.56074 | 0.13109 | 0.036414 | 0.17476 | 0 | 0.3464 | 0 | 0.46217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2224 | 1.934 | 100% | US Weighted | 18.8922 | 4.4168 | 3.6414 | 17.4762 | 0 | 11.6708 | 0 | 15.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.1618 | 100% | US Weighted | 5.5354 | 1.2941 | 0 | 0 | 0 | 3.4195 | 0 | 4.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0069 | 100% | US Weighted | 0 | 0 | 0.036414 | 0.17476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21118 | 100% | US Weighted | 57.9503 | 13.5481 | 3.9801 | 19.1015 | 0 | 35.7991 | 0 | 47.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9846 | 201.1271 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 24692 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 24692 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.22845 | 0.08743 | 0.00073316 | -0.00012283 | 0 | 0.40651 | 0 | 0.31677 | -0.03045 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 1.0103 | 2.683% | CZ 1A | 7.697 | 2.9457 | 0.073316 | -0.012283 | 0 | 13.6958 | 0 | 10.6726 | -1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 34.0793 | 2.683% | CZ 1A | 2.2552 | 0.86308 | 0 | 0 | 0 | 4.0129 | 0 | 3.1271 | -0.30059 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 9.9674 | 2.683% | CZ 1A | 0 | 0 | 0.00073316 | -0.00012283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00061033 | 2.683% | CZ 1A | 23.61 | 9.0356 | 0.080135 | -0.013426 | 0 | 42.0109 | 0 | 32.7374 | -3.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 104.4149 | 2.683%
CZ 1B | 0.23188 | 0.087339 | 0.00072549 | -0.0019346 | 0 | 0.33082 | 0 | 0.28444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.93426 | 0% | CZ 1B | 7.8126 | 2.9426 | 0.072549 | -0.19346 | 0 | 11.146 | 0 | 9.5834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 31.3967 | 0% | CZ 1B | 2.2891 | 0.86218 | 0 | 0 | 0 | 3.2658 | 0 | 2.8079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 9.2347 | 0% | CZ 1B | 0 | 0 | 0.00072549 | -0.0019346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0012091 | 0% | CZ 1B | 23.9645 | 9.0261 | 0.079296 | -0.21146 | 0 | 34.1896 | 0 | 29.3962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 96.5455 | 0%
CZ 2A | 0.22847 | 0.087316 | 0.00076003 | 0.0254 | 0 | 0.43282 | 0 | 0.27356 | -0.024251 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 1.025 | 15.29% | CZ 2A | 7.6974 | 2.9418 | 0.076003 | 2.54 | 0 | 14.5824 | 0 | 9.2167 | -0.81704 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 36.2703 | 15.29% | CZ 2A | 2.2553 | 0.86195 | 0 | 0 | 0 | 4.2726 | 0 | 2.7005 | -0.23939 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 9.8607 | 15.29% | CZ 2A | 0 | 0 | 0.00076003 | 0.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02616 | 15.29% | CZ 2A | 23.6112 | 9.0238 | 0.083072 | 2.7762 | 0 | 44.7303 | 0 | 28.2715 | -2.5062 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 106.091 | 15.29%
CZ 2B | 0.21412 | 0.087361 | 0.000737 | 0.0089016 | 0 | 0.26349 | 0 | 0.23941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.81499 | 3.321% | CZ 2B | 7.214 | 2.9434 | 0.0737 | 0.89016 | 0 | 8.8773 | 0 | 8.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 28.0975 | 3.321% | CZ 2B | 2.1137 | 0.8624 | 0 | 0 | 0 | 2.601 | 0 | 2.3633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.9502 | 3.321% | CZ 2B | 0 | 0 | 0.000737 | 0.0089016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096386 | 3.321% | CZ 2B | 22.1284 | 9.0285 | 0.080554 | 0.97295 | 0 | 27.2303 | 0 | 24.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 84.2838 | 3.321%
CZ 3A | 0.22739 | 0.08735 | 0.00077155 | 0.07871 | 0 | 0.21179 | 0 | 0.2414 | -0.021242 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.82716 | 16.83% | CZ 3A | 7.6613 | 2.943 | 0.077155 | 7.871 | 0 | 7.1357 | 0 | 8.1332 | -0.71568 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 33.1386 | 16.83% | CZ 3A | 2.2448 | 0.86229 | 0 | 0 | 0 | 2.0908 | 0 | 2.383 | -0.20969 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.3808 | 16.83% | CZ 3A | 0 | 0 | 0.00077155 | 0.07871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079481 | 16.83% | CZ 3A | 23.5005 | 9.0273 | 0.08433 | 8.603 | 0 | 21.8881 | 0 | 24.9479 | -2.1953 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 85.9571 | 16.83%
CZ 3B | 0.21649 | 0.087361 | 0.0007562 | 0.0079074 | 0 | 0.14725 | 0 | 0.19868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.65942 | 8.207% | CZ 3B | 7.2939 | 2.9434 | 0.07562 | 0.79074 | 0 | 4.961 | 0 | 6.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 22.7914 | 8.207% | CZ 3B | 2.1371 | 0.8624 | 0 | 0 | 0 | 1.4536 | 0 | 1.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.424 | 8.207% | CZ 3B | 0 | 0 | 0.0007562 | 0.0079074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086636 | 8.207% | CZ 3B | 22.3734 | 9.0285 | 0.082652 | 0.86428 | 0 | 15.2175 | 0 | 20.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 68.2001 | 8.207%
CZ 3C | 0.21643 | 0.08719 | 0.0007562 | 0.006468 | 0 | 0.093766 | 0 | 0.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.5724 | 1.253% | CZ 3C | 7.292 | 2.9376 | 0.07562 | 0.6468 | 0 | 3.1591 | 0 | 5.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 19.764 | 1.253% | CZ 3C | 2.1365 | 0.86072 | 0 | 0 | 0 | 0.92563 | 0 | 1.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.5792 | 1.253% | CZ 3C | 0 | 0 | 0.0007562 | 0.006468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072242 | 1.253% | CZ 3C | 22.3675 | 9.0108 | 0.082652 | 0.70695 | 0 | 9.6904 | 0 | 17.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 59.198 | 1.253%
CZ 4A | 0.21878 | 0.086928 | 0.00079842 | 0.19617 | 0 | 0.12338 | 0 | 0.23705 | -0.022074 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.84201 | 15.99% | CZ 4A | 7.3711 | 2.9288 | 0.079842 | 19.617 | 0 | 4.157 | 0 | 7.9865 | -0.74371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 41.4295 | 15.99% | CZ 4A | 2.1597 | 0.85813 | 0 | 0 | 0 | 1.218 | 0 | 2.3401 | -0.21791 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.3677 | 15.99% | CZ 4A | 0 | 0 | 0.00079842 | 0.19617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19697 | 15.99% | CZ 4A | 22.6101 | 8.9837 | 0.087267 | 21.4413 | 0 | 12.7513 | 0 | 24.498 | -2.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 88.1918 | 15.99%
CZ 4B | 0.21723 | 0.087259 | 0.0007869 | 0.033845 | 0 | 0.097116 | 0 | 0.22456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.66177 | 0.8792% | CZ 4B | 7.3188 | 2.9399 | 0.07869 | 3.3845 | 0 | 3.272 | 0 | 7.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 24.5926 | 0.8792% | CZ 4B | 2.1444 | 0.86139 | 0 | 0 | 0 | 0.9587 | 0 | 2.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.1909 | 0.8792% | CZ 4B | 0 | 0 | 0.0007869 | 0.033845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034631 | 0.8792% | CZ 4B | 22.4499 | 9.0179 | 0.086009 | 3.6992 | 0 | 10.0366 | 0 | 23.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 68.5982 | 0.8792%
CZ 4C | 0.21329 | 0.086746 | 0.00079842 | 0.06192 | 0 | 0.029481 | 0 | 0.23652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.62974 | 2.698% | CZ 4C | 7.186 | 2.9226 | 0.079842 | 6.192 | 0 | 0.99328 | 0 | 7.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 25.3756 | 2.698% | CZ 4C | 2.1055 | 0.85633 | 0 | 0 | 0 | 0.29103 | 0 | 2.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.5974 | 2.698% | CZ 4C | 0 | 0 | 0.00079842 | 0.06192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062718 | 2.698% | CZ 4C | 22.0424 | 8.9649 | 0.087267 | 6.7678 | 0 | 3.0468 | 0 | 24.4438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 65.4543 | 2.698%
CZ 5A | 0.21868 | 0.087122 | 0.0008061 | 0.2414 | 0 | 0.080022 | 0 | 0.29406 | -0.021379 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.90169 | 22.02% | CZ 5A | 7.3676 | 2.9353 | 0.08061 | 24.1403 | 0 | 2.6961 | 0 | 9.9074 | -0.72029 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 46.4401 | 22.02% | CZ 5A | 2.1587 | 0.86004 | 0 | 0 | 0 | 0.78995 | 0 | 2.9029 | -0.21104 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.5102 | 22.02% | CZ 5A | 0 | 0 | 0.0008061 | 0.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24221 | 22.02% | CZ 5A | 22.5995 | 9.0038 | 0.088106 | 26.3854 | 0 | 8.27 | 0 | 30.3902 | -2.2094 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 94.6288 | 22.02%
CZ 5B | 0.21553 | 0.087031 | 0.00079458 | 0.053993 | 0 | 0.093242 | 0 | 0.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.75777 | 5.18% | CZ 5B | 7.2616 | 2.9322 | 0.079458 | 5.3993 | 0 | 3.1415 | 0 | 10.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 29.1634 | 5.18% | CZ 5B | 2.1277 | 0.85914 | 0 | 0 | 0 | 0.92045 | 0 | 3.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.9396 | 5.18% | CZ 5B | 0 | 0 | 0.00079458 | 0.053993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054788 | 5.18% | CZ 5B | 22.2744 | 8.9943 | 0.086848 | 5.9015 | 0 | 9.6362 | 0 | 31.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 78.639 | 5.18%
CZ 5C | 0.21553 | 0.08678 | 0.00080226 | 0.071866 | 0 | 0.015875 | 0 | 0.21707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.6089 | 0.1101% | CZ 5C | 7.2616 | 2.9238 | 0.080226 | 7.1866 | 0 | 0.53484 | 0 | 7.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 25.3335 | 0.1101% | CZ 5C | 2.1277 | 0.85667 | 0 | 0 | 0 | 0.15671 | 0 | 2.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.2935 | 0.1101% | CZ 5C | 0 | 0 | 0.00080226 | 0.071866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072668 | 0.1101% | CZ 5C | 22.2744 | 8.9684 | 0.087687 | 7.8549 | 0 | 1.6406 | 0 | 22.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 63.3608 | 0.1101%
CZ 6A | 0.19022 | 0.086997 | 0.00080994 | 0.3067 | 0 | 0.084752 | 0 | 0.33468 | -0.022234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.9829 | 4.525% | CZ 6A | 6.4089 | 2.9311 | 0.080994 | 30.6701 | 0 | 2.8554 | 0 | 11.2758 | -0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 53.5062 | 4.525% | CZ 6A | 1.8778 | 0.8588 | 0 | 0 | 0 | 0.83664 | 0 | 3.3038 | -0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.6673 | 4.525% | CZ 6A | 0 | 0 | 0.00080994 | 0.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30751 | 4.525% | CZ 6A | 19.6587 | 8.9908 | 0.088526 | 33.5224 | 0 | 8.7588 | 0 | 34.5876 | -2.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 103.4104 | 4.525%
CZ 6B | 0.18858 | 0.086974 | 0.00080994 | 0.19891 | 0 | 0.060649 | 0 | 0.3584 | -0.021983 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.87332 | 0.5032% | CZ 6B | 6.3536 | 2.9303 | 0.080994 | 19.8906 | 0 | 2.0434 | 0 | 12.0752 | -0.74064 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 42.6665 | 0.5032% | CZ 6B | 1.8616 | 0.85858 | 0 | 0 | 0 | 0.59871 | 0 | 3.538 | -0.21701 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.6496 | 0.5032% | CZ 6B | 0 | 0 | 0.00080994 | 0.19891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19972 | 0.5032% | CZ 6B | 19.4891 | 8.9884 | 0.088526 | 21.7405 | 0 | 6.2679 | 0 | 37.0397 | -2.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 91.4436 | 0.5032%
CZ 7 | 0.18855 | 0.086735 | 0.00081377 | 0.38297 | 0 | 0.070518 | 0 | 0.36672 | -0.020433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 1.0769 | 0.4193% | CZ 7 | 6.3524 | 2.9222 | 0.081377 | 38.2969 | 0 | 2.3759 | 0 | 12.3555 | -0.68842 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 61.7289 | 0.4193% | CZ 7 | 1.8613 | 0.85622 | 0 | 0 | 0 | 0.69613 | 0 | 3.6202 | -0.20171 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.8417 | 0.4193% | CZ 7 | 0 | 0 | 0.00081377 | 0.38297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38378 | 0.4193% | CZ 7 | 19.4856 | 8.9637 | 0.088946 | 41.8585 | 0 | 7.2878 | 0 | 37.8994 | -2.1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 113.5736 | 0.4193%
CZ 8 | 0.18427 | 0.085253 | 0.00082145 | 0.47187 | 0 | 0.031282 | 0 | 0.40298 | -0.022678 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 1.1548 | 0.0892% | CZ 8 | 6.2085 | 2.8723 | 0.082145 | 47.1874 | 0 | 1.0539 | 0 | 13.5772 | -0.76406 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 70.2504 | 0.0892% | CZ 8 | 1.8191 | 0.84159 | 0 | 0 | 0 | 0.3088 | 0 | 3.9781 | -0.22387 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.7334 | 0.0892% | CZ 8 | 0 | 0 | 0.00082145 | 0.47187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4727 | 0.0892% | CZ 8 | 19.0439 | 8.8106 | 0.089785 | 51.5758 | 0 | 3.2329 | 0 | 41.647 | -2.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 122.1576 | 0.0892%
US Weighted | 0.21964 | 0.087172 | 0.0007823 | 0.12443 | 0 | 0.18305 | 0 | 0.26326 | -0.01756 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00098005 | 0.86176 | 100% | US Weighted | 7.4 | 2.937 | 0.07823 | 12.4434 | 0 | 6.1673 | 0 | 8.8698 | -0.59163 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.3371 | 100% | US Weighted | 2.1682 | 0.86053 | 0 | 0 | 0 | 1.807 | 0 | 2.5989 | -0.17335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.2709 | 100% | US Weighted | 0 | 0 | 0.0007823 | 0.12443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12522 | 100% | US Weighted | 22.699 | 9.0089 | 0.085506 | 13.6006 | 0 | 18.9177 | 0 | 27.2074 | -1.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 89.8057 | 100%
Building Type: | Standalone Retail |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 24692 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 24692 | [17 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 40.74% | 66.57% | 2.188% | -68.09% | 0% | 49.36% | 0% | 68.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.16% | 2.683% | CZ 1A | 40.74% | 66.57% | 2.188% | -68.09% | 0% | 49.36% | 0% | 68.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 43.91% | 2.683% | CZ 1A | 40.74% | 66.57% | 0% | 0% | 0% | 49.36% | 0% | 68.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.82% | 2.683% | CZ 1A | 0% | 0% | 2.188% | -68.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.812% | 2.683% | CZ 1A | 40.74% | 66.57% | 2.188% | -68.09% | 0% | 49.36% | 0% | 68.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.12% | 2.683%
CZ 1B | 41.35% | 66.58% | 2.165% | -15.39% | 0% | 39.12% | 0% | 60.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.03% | 0% | CZ 1B | 41.35% | 66.58% | 2.165% | -15.39% | 0% | 39.12% | 0% | 60.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.36% | 0% | CZ 1B | 41.35% | 66.58% | 0% | 0% | 0% | 39.12% | 0% | 60.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.93% | 0% | CZ 1B | 0% | 0% | 2.165% | -15.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.624% | 0% | CZ 1B | 41.35% | 66.58% | 2.165% | -15.39% | 0% | 39.12% | 0% | 60.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.98% | 0%
CZ 2A | 40.74% | 66.59% | 2.211% | 83.64% | 0% | 59.04% | 0% | 56.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 46.61% | 15.29% | CZ 2A | 40.74% | 66.59% | 2.211% | 83.64% | 0% | 59.04% | 0% | 56.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 46.27% | 15.29% | CZ 2A | 40.74% | 66.59% | 0% | 0% | 0% | 59.04% | 0% | 56.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 46.8% | 15.29% | CZ 2A | 0% | 0% | 2.211% | 83.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.4% | 15.29% | CZ 2A | 40.74% | 66.59% | 2.211% | 83.64% | 0% | 59.04% | 0% | 56.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 46.6% | 15.29%
CZ 2B | 38.19% | 66.57% | 2.142% | 41.37% | 0% | 48.66% | 0% | 48.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.6% | 3.321% | CZ 2B | 38.19% | 66.57% | 2.142% | 41.37% | 0% | 48.66% | 0% | 48.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.38% | 3.321% | CZ 2B | 38.19% | 66.57% | 0% | 0% | 0% | 48.66% | 0% | 48.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.27% | 3.321% | CZ 2B | 0% | 0% | 2.142% | 41.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.24% | 3.321% | CZ 2B | 38.19% | 66.57% | 2.142% | 41.37% | 0% | 48.66% | 0% | 48.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.56% | 3.321%
CZ 3A | 40.55% | 66.58% | 2.154% | 74.55% | 0% | 53.86% | 0% | 55.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 43.98% | 16.83% | CZ 3A | 40.55% | 66.58% | 2.154% | 74.55% | 0% | 53.86% | 0% | 55.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.56% | 16.83% | CZ 3A | 40.55% | 66.58% | 0% | 0% | 0% | 53.86% | 0% | 55.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.99% | 16.83% | CZ 3A | 0% | 0% | 2.154% | 74.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 56.21% | 16.83% | CZ 3A | 40.55% | 66.58% | 2.154% | 74.55% | 0% | 53.86% | 0% | 55.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.03% | 16.83%
CZ 3B | 38.61% | 66.59% | 2.134% | 20.91% | 0% | 43.1% | 0% | 43.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.99% | 8.207% | CZ 3B | 38.61% | 66.59% | 2.134% | 20.91% | 0% | 43.1% | 0% | 43.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.1% | 8.207% | CZ 3B | 38.61% | 66.59% | 0% | 0% | 0% | 43.1% | 0% | 43.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.06% | 8.207% | CZ 3B | 0% | 0% | 2.134% | 20.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.83% | 8.207% | CZ 3B | 38.61% | 66.59% | 2.134% | 20.91% | 0% | 43.1% | 0% | 43.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.93% | 8.207%
CZ 3C | 38.6% | 66.47% | 2.103% | 35.12% | 0% | 53.8% | 0% | 42.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.32% | 1.253% | CZ 3C | 38.6% | 66.47% | 2.103% | 35.12% | 0% | 53.8% | 0% | 42.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.75% | 1.253% | CZ 3C | 38.6% | 66.47% | 0% | 0% | 0% | 53.8% | 0% | 42.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.2% | 1.253% | CZ 3C | 0% | 0% | 2.103% | 35.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.29% | 1.253% | CZ 3C | 38.6% | 66.47% | 2.103% | 35.12% | 0% | 53.8% | 0% | 42.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.27% | 1.253%
CZ 4A | 39.02% | 66.36% | 2.159% | 80.14% | 0% | 49.49% | 0% | 56.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.18% | 15.99% | CZ 4A | 39.02% | 66.36% | 2.159% | 80.14% | 0% | 49.49% | 0% | 56.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 50.85% | 15.99% | CZ 4A | 39.02% | 66.36% | 0% | 0% | 0% | 49.49% | 0% | 56.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.77% | 15.99% | CZ 4A | 0% | 0% | 2.159% | 80.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 69.91% | 15.99% | CZ 4A | 39.02% | 66.36% | 2.159% | 80.14% | 0% | 49.49% | 0% | 56.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.39% | 15.99%
CZ 4B | 38.74% | 66.56% | 2.148% | 38.37% | 0% | 41.08% | 0% | 45.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.39% | 0.8792% | CZ 4B | 38.74% | 66.56% | 2.148% | 38.37% | 0% | 41.08% | 0% | 45.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.22% | 0.8792% | CZ 4B | 38.74% | 66.56% | 0% | 0% | 0% | 41.08% | 0% | 45.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.13% | 0.8792% | CZ 4B | 0% | 0% | 2.148% | 38.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.74% | 0.8792% | CZ 4B | 38.74% | 66.56% | 2.148% | 38.37% | 0% | 41.08% | 0% | 45.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.36% | 0.8792%
CZ 4C | 38.04% | 66.3% | 2.139% | 40.02% | 0% | 41.51% | 0% | 59.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40% | 2.698% | CZ 4C | 38.04% | 66.3% | 2.139% | 40.02% | 0% | 41.51% | 0% | 59.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.58% | 2.698% | CZ 4C | 38.04% | 66.3% | 0% | 0% | 0% | 41.51% | 0% | 59.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.02% | 2.698% | CZ 4C | 0% | 0% | 2.139% | 40.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.66% | 2.698% | CZ 4C | 38.04% | 66.3% | 2.139% | 40.02% | 0% | 41.51% | 0% | 59.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.95% | 2.698%
CZ 5A | 39% | 66.48% | 2.125% | 75.21% | 0% | 50.67% | 0% | 62.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 47.34% | 22.02% | CZ 5A | 39% | 66.48% | 2.125% | 75.21% | 0% | 50.67% | 0% | 62.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 52.79% | 22.02% | CZ 5A | 39% | 66.48% | 0% | 0% | 0% | 50.67% | 0% | 62.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.66% | 22.02% | CZ 5A | 0% | 0% | 2.125% | 75.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 67.49% | 22.02% | CZ 5A | 39% | 66.48% | 2.125% | 75.21% | 0% | 50.67% | 0% | 62.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 47.55% | 22.02%
CZ 5B | 38.44% | 66.41% | 2.111% | 32.12% | 0% | 47.79% | 0% | 56.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.82% | 5.18% | CZ 5B | 38.44% | 66.41% | 2.111% | 32.12% | 0% | 47.79% | 0% | 56.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.28% | 5.18% | CZ 5B | 38.44% | 66.41% | 0% | 0% | 0% | 47.79% | 0% | 56.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.59% | 5.18% | CZ 5B | 0% | 0% | 2.111% | 32.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.63% | 5.18% | CZ 5B | 38.44% | 66.41% | 2.111% | 32.12% | 0% | 47.79% | 0% | 56.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.73% | 5.18%
CZ 5C | 38.44% | 66.33% | 2.119% | 40.22% | 0% | 43.7% | 0% | 55.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.1% | 0.1101% | CZ 5C | 38.44% | 66.33% | 2.119% | 40.22% | 0% | 43.7% | 0% | 55.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.91% | 0.1101% | CZ 5C | 38.44% | 66.33% | 0% | 0% | 0% | 43.7% | 0% | 55.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.99% | 0.1101% | CZ 5C | 0% | 0% | 2.119% | 40.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.56% | 0.1101% | CZ 5C | 38.44% | 66.33% | 2.119% | 40.22% | 0% | 43.7% | 0% | 55.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 39.05% | 0.1101%
CZ 6A | 33.92% | 66.42% | 2.097% | 68.57% | 0% | 49.11% | 0% | 64.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 46.95% | 4.525% | CZ 6A | 33.92% | 66.42% | 2.097% | 68.57% | 0% | 49.11% | 0% | 64.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 52.07% | 4.525% | CZ 6A | 33.92% | 66.42% | 0% | 0% | 0% | 49.11% | 0% | 64.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.01% | 4.525% | CZ 6A | 0% | 0% | 2.097% | 68.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 63.28% | 4.525% | CZ 6A | 33.92% | 66.42% | 2.097% | 68.57% | 0% | 49.11% | 0% | 64.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 47.16% | 4.525%
CZ 6B | 33.63% | 66.45% | 2.106% | 70.31% | 0% | 47.86% | 0% | 64.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.58% | 0.5032% | CZ 6B | 33.63% | 66.45% | 2.106% | 70.31% | 0% | 47.86% | 0% | 64.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 49.69% | 0.5032% | CZ 6B | 33.63% | 66.45% | 0% | 0% | 0% | 47.86% | 0% | 64.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.24% | 0.5032% | CZ 6B | 0% | 0% | 2.106% | 70.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.15% | 0.5032% | CZ 6B | 33.63% | 66.45% | 2.106% | 70.31% | 0% | 47.86% | 0% | 64.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.74% | 0.5032%
CZ 7 | 33.62% | 66.31% | 2.063% | 69.98% | 0% | 54.76% | 0% | 67.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 49.53% | 0.4193% | CZ 7 | 33.62% | 66.31% | 2.063% | 69.98% | 0% | 54.76% | 0% | 67.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 55.04% | 0.4193% | CZ 7 | 33.62% | 66.31% | 0% | 0% | 0% | 54.76% | 0% | 67.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 43.66% | 0.4193% | CZ 7 | 0% | 0% | 2.063% | 69.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.42% | 0.4193% | CZ 7 | 33.62% | 66.31% | 2.063% | 69.98% | 0% | 54.76% | 0% | 67.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 49.77% | 0.4193%
CZ 8 | 32.86% | 65.54% | 2.025% | 63.76% | 0% | 52.44% | 0% | 70.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 49.61% | 0.0892% | CZ 8 | 32.86% | 65.54% | 2.025% | 63.76% | 0% | 52.44% | 0% | 70.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 53.96% | 0.0892% | CZ 8 | 32.86% | 65.54% | 0% | 0% | 0% | 52.44% | 0% | 70.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.08% | 0.0892% | CZ 8 | 0% | 0% | 2.025% | 63.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.55% | 0.0892% | CZ 8 | 32.86% | 65.54% | 2.025% | 63.76% | 0% | 52.44% | 0% | 70.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 49.81% | 0.0892%
US Weighted | 39.17% | 66.5% | 2.148% | 71.2% | 0% | 52.84% | 0% | 56.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.56% | 100% | US Weighted | 39.17% | 66.5% | 2.148% | 71.2% | 0% | 52.84% | 0% | 56.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 47.17% | 100% | US Weighted | 39.17% | 66.5% | 0% | 0% | 0% | 52.84% | 0% | 56.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.75% | 100% | US Weighted | 0% | 0% | 2.148% | 71.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 59.29% | 100% | US Weighted | 39.17% | 66.5% | 2.148% | 71.2% | 0% | 52.84% | 0% | 56.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.65% | 100%

## RtlMall
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Strip Mall |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Strip Mall | [14 empty] | Prototype Floor Area: | 22500 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.56389 | 0.068758 | 0.078107 | 0.10145 | 0 | 0.18419 | 0 | 0.18464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3413 |  | STD2016 | 18.9984 | 2.3166 | 2.6315 | 10.1448 | 0 | 6.2055 | 0 | 6.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.9175 |  | STD2016 | 5.5665 | 0.67875 | 0.77104 | 0 | 0 | 1.8182 | 0 | 1.8227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2394 |  | STD2016 | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 |  | STD2016 | 58.2761 | 7.1059 | 8.072 | 11.0883 | 0 | 19.035 | 0 | 19.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 139.2226
STD2013 | 0.6889 | 0.11568 | 0.078068 | 0.092785 | 0 | 0.19779 | 0 | 0.19211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5256 |  | STD2013 | 23.2103 | 3.8975 | 2.6303 | 9.2785 | 0 | 6.6638 | 0 | 6.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.5525 |  | STD2013 | 6.8006 | 1.142 | 0.77066 | 0 | 0 | 1.9525 | 0 | 1.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.1443 |  | STD2013 | 0 | 0 | 0 | 0.092785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092785 |  | STD2013 | 71.1957 | 11.9553 | 8.0681 | 10.1414 | 0 | 20.4406 | 0 | 19.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 158.2179
STD2010 | 0.76333 | 0.11568 | 0.078109 | 0.092782 | 0 | 0.2344 | 0 | 0.24108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6856 |  | STD2010 | 25.7178 | 3.8975 | 2.6316 | 9.2782 | 0 | 7.8975 | 0 | 8.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.9445 |  | STD2010 | 7.5353 | 1.142 | 0.77107 | 0 | 0 | 2.314 | 0 | 2.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.7242 |  | STD2010 | 0 | 0 | 0 | 0.092782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092782 |  | STD2010 | 78.8871 | 11.9553 | 8.0723 | 10.1411 | 0 | 24.2249 | 0 | 24.9143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 174.758
STD2007 | 0.85202 | 0.21058 | 0.085052 | 0.099783 | 0 | 0.3414 | 0 | 0.30044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0502 |  | STD2007 | 28.706 | 7.0948 | 2.8655 | 9.9783 | 0 | 11.5022 | 0 | 10.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.6928 |  | STD2007 | 8.4109 | 2.0788 | 0.8396 | 0 | 0 | 3.3701 | 0 | 2.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2543 |  | STD2007 | 0 | 0 | 0 | 0.099783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099783 |  | STD2007 | 88.0533 | 21.7628 | 8.7898 | 10.9063 | 0 | 35.282 | 0 | 31.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 212.4801
STD2004 | 0.79045 | 0.21058 | 0.085185 | 0.17178 | 0 | 0.37521 | 0 | 0.32996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1241 |  | STD2004 | 26.6317 | 7.0948 | 2.87 | 17.1776 | 0 | 12.6416 | 0 | 11.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 82.9563 |  | STD2004 | 7.8031 | 2.0788 | 0.84092 | 0 | 0 | 3.704 | 0 | 3.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2732 |  | STD2004 | 0 | 0 | 0 | 0.17178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17178 |  | STD2004 | 81.6905 | 21.7628 | 8.8036 | 18.7752 | 0 | 38.777 | 0 | 34.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 220.5458
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | -0.061568 | 0 | 0.00013385 | 0.071993 | 0 | 0.033818 | 0 | 0.029522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073899 |  | 2004-2007 | -2.0743 | 0 | 0.0045097 | 7.1993 | 0 | 1.1394 | 0 | 0.99464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2635 |  | 2004-2007 | -0.60778 | 0 | 0.0013213 | 0 | 0 | 0.33384 | 0 | 0.29143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01881 |  | 2004-2007 | 0 | 0 | 0 | 0.071993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071993 |  | 2004-2007 | -6.3628 | 0 | 0.013833 | 7.8689 | 0 | 3.495 | 0 | 3.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0658
2007-2010 | 0.088694 | 0.0949 | 0.0069427 | 0.0070012 | 0 | 0.10699 | 0 | 0.059362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.3646 |  | 2007-2010 | 2.9882 | 3.1973 | 0.23391 | 0.70012 | 0 | 3.6047 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 12.7483 |  | 2007-2010 | 0.87556 | 0.93682 | 0.068536 | 0 | 0 | 1.0562 | 0 | 0.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 3.5301 |  | 2007-2010 | 0 | 0 | 0 | 0.0070012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070012 |  | 2007-2010 | 9.1662 | 9.8075 | 0.7175 | 0.76524 | 0 | 11.0571 | 0 | 6.1348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 37.7221
2010-2013 | 0.074424 | 0 | 4.0747e-05 | -2.7137e-06 | 0 | 0.036617 | 0 | 0.048966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16004 |  | 2010-2013 | 2.5075 | 0 | 0.0013728 | -0.00027137 | 0 | 1.2337 | 0 | 1.6497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.392 |  | 2010-2013 | 0.73469 | 0 | 0.00040224 | 0 | 0 | 0.36147 | 0 | 0.48337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5799 |  | 2010-2013 | 0 | 0 | 0 | -2.7137e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7137e-06 |  | 2010-2013 | 7.6915 | 0 | 0.0042111 | -0.0002966 | 0 | 3.7842 | 0 | 5.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5401
2013-2016 | 0.12501 | 0.046924 | -3.8405e-05 | -0.0086636 | 0 | 0.013601 | 0 | 0.0074663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1843 |  | 2013-2016 | 4.2119 | 1.5809 | -0.0012939 | -0.86636 | 0 | 0.45825 | 0 | 0.25155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6349 |  | 2013-2016 | 1.2341 | 0.46322 | -0.00037912 | 0 | 0 | 0.13427 | 0 | 0.073705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9049 |  | 2013-2016 | 0 | 0 | 0 | -0.0086636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0086636 |  | 2013-2016 | 12.9195 | 4.8494 | -0.003969 | -0.94693 | 0 | 1.4057 | 0 | 0.77162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9953
2004-2016 | 0.22656 | 0.14182 | 0.0070789 | 0.070328 | 0 | 0.19103 | 0 | 0.14532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.78285 |  | 2004-2016 | 7.6333 | 4.7783 | 0.2385 | 7.0328 | 0 | 6.436 | 0 | 4.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 31.0388 |  | 2004-2016 | 2.2365 | 1.4 | 0.06988 | 0 | 0 | 1.8858 | 0 | 1.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.0338 |  | 2004-2016 | 0 | 0 | 0 | 0.070328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070328 |  | 2004-2016 | 23.4144 | 14.6569 | 0.73158 | 7.6869 | 0 | 19.742 | 0 | 15.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 81.3232
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | -7.789% | 0% | 0.1571% | 41.91% |  | 9.013% |  | 8.947% | [7 empty] | 0% | 3.479% |  | 2004-2007 | -7.789% | 0% | 0.1571% | 41.91% |  | 9.013% |  | 8.947% | [7 empty] | 0% | 8.756% |  | 2004-2007 | -7.789% | 0% | 0.1571% |  |  | 9.013% |  | 8.947% | [7 empty] | 0% | 0.0976% |  | 2004-2007 |  |  |  | 41.91% | [12 empty] | 41.91% |  | 2004-2007 | -7.789% | 0% | 0.1571% | 41.91% |  | 9.013% |  | 8.947% | [7 empty] | 0% | 3.657%
2007-2010 | 10.41% | 45.07% | 8.163% | 7.016% |  | 31.34% |  | 19.76% | [7 empty] | 0.4428% | 17.78% |  | 2007-2010 | 10.41% | 45.07% | 8.163% | 7.016% |  | 31.34% |  | 19.76% | [7 empty] | 0.4428% | 16.84% |  | 2007-2010 | 10.41% | 45.07% | 8.163% |  |  | 31.34% |  | 19.76% | [7 empty] | 0.4428% | 18.33% |  | 2007-2010 |  |  |  | 7.016% | [12 empty] | 7.016% |  | 2007-2010 | 10.41% | 45.07% | 8.163% | 7.016% |  | 31.34% |  | 19.76% | [7 empty] | 0.4428% | 17.75%
2010-2013 | 9.75% | 0% | 0.05217% | -0.002925% |  | 15.62% |  | 20.31% | [7 empty] | 0% | 9.495% |  | 2010-2013 | 9.75% | 0% | 0.05217% | -0.002925% |  | 15.62% |  | 20.31% | [7 empty] | 0% | 8.566% |  | 2010-2013 | 9.75% | 0% | 0.05217% |  |  | 15.62% |  | 20.31% | [7 empty] | 0% | 10.05% |  | 2010-2013 |  |  |  | -0.002925% | [12 empty] | -0.002925% |  | 2010-2013 | 9.75% | 0% | 0.05217% | -0.002925% |  | 15.62% |  | 20.31% | [7 empty] | 0% | 9.465%
2013-2016 | 18.15% | 40.56% | -0.04919% | -9.337% |  | 6.877% |  | 3.886% | [7 empty] | 0% | 12.08% |  | 2013-2016 | 18.15% | 40.56% | -0.04919% | -9.337% |  | 6.877% |  | 3.886% | [7 empty] | 0% | 9.791% |  | 2013-2016 | 18.15% | 40.56% | -0.04919% |  |  | 6.877% |  | 3.886% | [7 empty] | 0% | 13.47% |  | 2013-2016 |  |  |  | -9.337% | [12 empty] | -9.337% |  | 2013-2016 | 18.15% | 40.56% | -0.04919% | -9.337% |  | 6.877% |  | 3.886% | [7 empty] | 0% | 12.01%
2004-2016 | 28.66% | 67.35% | 8.31% | 40.94% |  | 50.91% |  | 44.04% | [7 empty] | 0.4428% | 36.85% |  | 2004-2016 | 28.66% | 67.35% | 8.31% | 40.94% |  | 50.91% |  | 44.04% | [7 empty] | 0.4428% | 37.42% |  | 2004-2016 | 28.66% | 67.35% | 8.31% |  |  | 50.91% |  | 44.04% | [7 empty] | 0.4428% | 36.5% |  | 2004-2016 |  |  |  | 40.94% | [12 empty] | 40.94% |  | 2004-2016 | 28.66% | 67.35% | 8.31% | 40.94% |  | 50.91% |  | 44.04% | [7 empty] | 0.4428% | 36.87%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.56389 | 0.068759 | 0.073474 | 4.6338e-05 | 0 | 0.39921 | 0 | 0.17406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4397 | 3.475% | CZ 1A | 18.9984 | 2.3166 | 2.4755 | 0.0046338 | 0 | 13.45 | 0 | 5.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.5092 | 3.475% | CZ 1A | 5.5665 | 0.67877 | 0.72531 | 0 | 0 | 3.9409 | 0 | 1.7183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.2119 | 3.475% | CZ 1A | 0 | 0 | 0 | 4.6338e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6338e-05 | 3.475% | CZ 1A | 58.2761 | 7.106 | 7.5933 | 0.0050647 | 0 | 41.2569 | 0 | 17.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 148.7889 | 3.475%
CZ 1B | 0.56389 | 0.068646 | 0.073586 | 0.0085177 | 0 | 0.46034 | 0 | 0.20788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5431 | 0% | CZ 1B | 18.9984 | 2.3128 | 2.4792 | 0.85177 | 0 | 15.5096 | 0 | 7.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.5553 | 0% | CZ 1B | 5.5665 | 0.67765 | 0.72642 | 0 | 0 | 4.5443 | 0 | 2.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.1491 | 0% | CZ 1B | 0 | 0 | 0 | 0.0085177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085177 | 0% | CZ 1B | 58.2761 | 7.0944 | 7.6049 | 0.93099 | 0 | 47.5745 | 0 | 21.4834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 159.5273 | 0%
CZ 2A | 0.56389 | 0.068609 | 0.075062 | 0.016972 | 0 | 0.34605 | 0 | 0.15879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3896 | 19.08% | CZ 2A | 18.9984 | 2.3115 | 2.529 | 1.6972 | 0 | 11.6589 | 0 | 5.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 47.9446 | 19.08% | CZ 2A | 5.5665 | 0.67728 | 0.74099 | 0 | 0 | 3.416 | 0 | 1.5675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.5505 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.016972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016972 | 19.08% | CZ 2A | 58.2761 | 7.0905 | 7.7574 | 1.8551 | 0 | 35.7626 | 0 | 16.4105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 143.7152 | 19.08%
CZ 2B | 0.56389 | 0.068684 | 0.07515 | 0.0056321 | 0 | 0.28014 | 0 | 0.26503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4188 | 4.471% | CZ 2B | 18.9984 | 2.3141 | 2.5319 | 0.56321 | 0 | 9.4383 | 0 | 8.9293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.175 | 4.471% | CZ 2B | 5.5665 | 0.67802 | 0.74185 | 0 | 0 | 2.7654 | 0 | 2.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.9502 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.0056321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056321 | 4.471% | CZ 2B | 58.2761 | 7.0982 | 7.7664 | 0.61559 | 0 | 28.9513 | 0 | 27.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 146.6607 | 4.471%
CZ 3A | 0.56389 | 0.068659 | 0.077701 | 0.071954 | 0 | 0.1785 | 0 | 0.18615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3071 | 19.64% | CZ 3A | 18.9984 | 2.3132 | 2.6179 | 7.1954 | 0 | 6.014 | 0 | 6.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.8105 | 19.64% | CZ 3A | 5.5665 | 0.67778 | 0.76704 | 0 | 0 | 1.7621 | 0 | 1.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.1932 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.071954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071954 | 19.64% | CZ 3A | 58.2761 | 7.0957 | 8.0301 | 7.8646 | 0 | 18.4474 | 0 | 19.2384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 135.5153 | 19.64%
CZ 3B | 0.56389 | 0.068659 | 0.077026 | 0.030996 | 0 | 0.17592 | 0 | 0.21866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.2954 | 11.03% | CZ 3B | 18.9984 | 2.3132 | 2.5951 | 3.0996 | 0 | 5.9272 | 0 | 7.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 45.7002 | 11.03% | CZ 3B | 5.5665 | 0.67778 | 0.76037 | 0 | 0 | 1.7367 | 0 | 2.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.482 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.030996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030996 | 11.03% | CZ 3B | 58.2761 | 7.0957 | 7.9603 | 3.3878 | 0 | 18.1812 | 0 | 22.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 134.0616 | 11.03%
CZ 3C | 0.56389 | 0.068884 | 0.077963 | 0.011483 | 0 | 0.070022 | 0 | 0.16474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.1173 | 1.823% | CZ 3C | 18.9984 | 2.3208 | 2.6267 | 1.1483 | 0 | 2.3592 | 0 | 5.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 38.4036 | 1.823% | CZ 3C | 5.5665 | 0.68 | 0.76963 | 0 | 0 | 0.69123 | 0 | 1.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 10.9158 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.011483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011483 | 1.823% | CZ 3C | 58.2761 | 7.1189 | 8.0573 | 1.2551 | 0 | 7.2365 | 0 | 17.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 115.5327 | 1.823%
CZ 4A | 0.56389 | 0.069022 | 0.079777 | 0.15741 | 0 | 0.1177 | 0 | 0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3301 | 15.73% | CZ 4A | 18.9984 | 2.3255 | 2.6878 | 15.7413 | 0 | 3.9654 | 0 | 6.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.25 | 15.73% | CZ 4A | 5.5665 | 0.68136 | 0.78753 | 0 | 0 | 1.1619 | 0 | 1.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.576 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.15741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15741 | 15.73% | CZ 4A | 58.2761 | 7.1331 | 8.2447 | 17.2053 | 0 | 12.1634 | 0 | 18.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 138.395 | 15.73%
CZ 4B | 0.56389 | 0.068659 | 0.079114 | 0.0467 | 0 | 0.12507 | 0 | 0.21663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.2603 | 0.4211% | CZ 4B | 18.9984 | 2.3132 | 2.6655 | 4.67 | 0 | 4.214 | 0 | 7.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 45.5595 | 0.4211% | CZ 4B | 5.5665 | 0.67778 | 0.78099 | 0 | 0 | 1.2347 | 0 | 2.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.9806 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0467 | 0.4211% | CZ 4B | 58.2761 | 7.0957 | 8.1762 | 5.1043 | 0 | 12.926 | 0 | 22.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 130.5294 | 0.4211%
CZ 4C | 0.56389 | 0.069059 | 0.080427 | 0.11717 | 0 | 0.039319 | 0 | 0.16761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.1977 | 1.866% | CZ 4C | 18.9984 | 2.3267 | 2.7097 | 11.7171 | 0 | 1.3247 | 0 | 5.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.1234 | 1.866% | CZ 4C | 5.5665 | 0.68173 | 0.79395 | 0 | 0 | 0.38815 | 0 | 1.6546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 10.667 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.11717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11717 | 1.866% | CZ 4C | 58.2761 | 7.137 | 8.3119 | 12.8068 | 0 | 4.0635 | 0 | 17.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 124.48 | 1.866%
CZ 5A | 0.56389 | 0.068784 | 0.08149 | 0.24919 | 0 | 0.067208 | 0 | 0.17062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3614 | 16.97% | CZ 5A | 18.9984 | 2.3174 | 2.7455 | 24.9187 | 0 | 2.2644 | 0 | 5.7485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.3927 | 16.97% | CZ 5A | 5.5665 | 0.67901 | 0.80444 | 0 | 0 | 0.66346 | 0 | 1.6843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 10.9799 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.24919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24919 | 16.97% | CZ 5A | 58.2761 | 7.1086 | 8.4217 | 27.2362 | 0 | 6.9457 | 0 | 17.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 142.1845 | 16.97%
CZ 5B | 0.56389 | 0.068922 | 0.08094 | 0.12976 | 0 | 0.09561 | 0 | 0.21008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3095 | 3.575% | CZ 5B | 18.9984 | 2.3221 | 2.727 | 12.9762 | 0 | 3.2213 | 0 | 7.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.7226 | 3.575% | CZ 5B | 5.5665 | 0.68037 | 0.79901 | 0 | 0 | 0.94383 | 0 | 2.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.6457 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.12976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12976 | 3.575% | CZ 5B | 58.2761 | 7.1228 | 8.3649 | 14.183 | 0 | 9.8809 | 0 | 21.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 136.1017 | 3.575%
CZ 5C | 0.56389 | 0.068997 | 0.081403 | 0.14294 | 0 | 0.019835 | 0 | 0.15438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.1917 | 0.016% | CZ 5C | 18.9984 | 2.3246 | 2.7426 | 14.2935 | 0 | 0.66827 | 0 | 5.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.6283 | 0.016% | CZ 5C | 5.5665 | 0.68111 | 0.80358 | 0 | 0 | 0.1958 | 0 | 1.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 10.3531 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.14294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14294 | 0.016% | CZ 5C | 58.2761 | 7.1306 | 8.4127 | 15.6228 | 0 | 2.0499 | 0 | 15.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 124.0093 | 0.016%
CZ 6A | 0.56389 | 0.068884 | 0.082728 | 0.3272 | 0 | 0.078514 | 0 | 0.18752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.469 | 1.571% | CZ 6A | 18.9984 | 2.3208 | 2.7873 | 32.7199 | 0 | 2.6453 | 0 | 6.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 71.1891 | 1.571% | CZ 6A | 5.5665 | 0.68 | 0.81667 | 0 | 0 | 0.77506 | 0 | 1.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.2715 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3272 | 1.571% | CZ 6A | 58.2761 | 7.1189 | 8.5497 | 35.7629 | 0 | 8.1141 | 0 | 19.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 153.764 | 1.571%
CZ 6B | 0.56389 | 0.068759 | 0.082403 | 0.22385 | 0 | 0.065382 | 0 | 0.19822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3628 | 0.2327% | CZ 6B | 18.9984 | 2.3166 | 2.7763 | 22.3849 | 0 | 2.2028 | 0 | 6.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.7572 | 0.2327% | CZ 6B | 5.5665 | 0.67877 | 0.81346 | 0 | 0 | 0.64543 | 0 | 1.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.2431 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.22385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22385 | 0.2327% | CZ 6B | 58.2761 | 7.106 | 8.5161 | 24.4667 | 0 | 6.757 | 0 | 20.4856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 142.1706 | 0.2327%
CZ 7 | 0.56389 | 0.069022 | 0.084167 | 0.39625 | 0 | 0.056615 | 0 | 0.19293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5231 | 0.07923% | CZ 7 | 18.9984 | 2.3255 | 2.8357 | 39.6251 | 0 | 1.9075 | 0 | 6.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 77.592 | 0.07923% | CZ 7 | 5.5665 | 0.68136 | 0.83086 | 0 | 0 | 0.55889 | 0 | 1.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.1243 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.39625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39625 | 0.07923% | CZ 7 | 58.2761 | 7.1331 | 8.6983 | 43.3102 | 0 | 5.851 | 0 | 19.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 159.7707 | 0.07923%
CZ 8 | 0.56389 | 0.07091 | 0.086155 | 0.5703 | 0 | 0.02545 | 0 | 0.21727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6942 | 0.02367% | CZ 8 | 18.9984 | 2.3891 | 2.9027 | 57.0295 | 0 | 0.85746 | 0 | 7.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 94.897 | 0.02367% | CZ 8 | 5.5665 | 0.7 | 0.85049 | 0 | 0 | 0.25123 | 0 | 2.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.0952 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5703 | 0.02367% | CZ 8 | 58.2761 | 7.3283 | 8.9038 | 62.3333 | 0 | 2.6302 | 0 | 22.4541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 178.4888 | 0.02367%
US Weighted | 0.56389 | 0.068758 | 0.078107 | 0.10145 | 0 | 0.18419 | 0 | 0.18464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3413 | 100% | US Weighted | 18.9984 | 2.3166 | 2.6315 | 10.1448 | 0 | 6.2055 | 0 | 6.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.9175 | 100% | US Weighted | 5.5665 | 0.67875 | 0.77104 | 0 | 0 | 1.8182 | 0 | 1.8227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2394 | 100% | US Weighted | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 | 100% | US Weighted | 58.2761 | 7.1059 | 8.072 | 11.0883 | 0 | 19.035 | 0 | 19.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 139.2226 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.6889 | 0.11578 | 0.073449 | 5.055e-05 | 0 | 0.41982 | 0 | 0.16332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6216 | 3.475% | CZ 1A | 23.2103 | 3.9009 | 2.4746 | 0.005055 | 0 | 14.1444 | 0 | 5.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.6374 | 3.475% | CZ 1A | 6.8006 | 1.143 | 0.72506 | 0 | 0 | 4.1443 | 0 | 1.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 16.0073 | 3.475% | CZ 1A | 0 | 0 | 0 | 5.055e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.055e-05 | 3.475% | CZ 1A | 71.1957 | 11.9657 | 7.5907 | 0.0055251 | 0 | 43.3869 | 0 | 16.8784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 167.5858 | 3.475%
CZ 1B | 0.6889 | 0.11559 | 0.073549 | 0.0080375 | 0 | 0.48391 | 0 | 0.16728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6975 | 0% | CZ 1B | 23.2103 | 3.8946 | 2.478 | 0.80375 | 0 | 16.3039 | 0 | 5.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.7262 | 0% | CZ 1B | 6.8006 | 1.1411 | 0.72605 | 0 | 0 | 4.777 | 0 | 1.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 16.6783 | 0% | CZ 1B | 0 | 0 | 0 | 0.0080375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0080375 | 0% | CZ 1B | 71.1957 | 11.9463 | 7.601 | 0.8785 | 0 | 50.0108 | 0 | 17.2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 175.4833 | 0%
CZ 2A | 0.6889 | 0.11556 | 0.075025 | 0.014116 | 0 | 0.37047 | 0 | 0.16861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5929 | 19.08% | CZ 2A | 23.2103 | 3.8933 | 2.5277 | 1.4116 | 0 | 12.4818 | 0 | 5.6807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.6051 | 19.08% | CZ 2A | 6.8006 | 1.1407 | 0.74062 | 0 | 0 | 3.6572 | 0 | 1.6644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.5857 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.014116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014116 | 19.08% | CZ 2A | 71.1957 | 11.9424 | 7.7535 | 1.5429 | 0 | 38.2868 | 0 | 17.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 164.7094 | 19.08%
CZ 2B | 0.6889 | 0.11566 | 0.075125 | 0.0055605 | 0 | 0.30255 | 0 | 0.24143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5895 | 4.471% | CZ 2B | 23.2103 | 3.8967 | 2.5311 | 0.55605 | 0 | 10.1934 | 0 | 8.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 53.9214 | 4.471% | CZ 2B | 6.8006 | 1.1417 | 0.7416 | 0 | 0 | 2.9867 | 0 | 2.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.636 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.0055605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055605 | 4.471% | CZ 2B | 71.1957 | 11.9528 | 7.7639 | 0.60777 | 0 | 31.2674 | 0 | 24.9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 164.3016 | 4.471%
CZ 3A | 0.6889 | 0.11563 | 0.077663 | 0.065804 | 0 | 0.19256 | 0 | 0.18991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4907 | 19.64% | CZ 3A | 23.2103 | 3.8958 | 2.6166 | 6.5804 | 0 | 6.4876 | 0 | 6.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.5886 | 19.64% | CZ 3A | 6.8006 | 1.1415 | 0.76667 | 0 | 0 | 1.9009 | 0 | 1.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.0664 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.065804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065804 | 19.64% | CZ 3A | 71.1957 | 11.9502 | 8.0262 | 7.1924 | 0 | 19.9001 | 0 | 19.6261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 154.4537 | 19.64%
CZ 3B | 0.6889 | 0.11562 | 0.076975 | 0.022293 | 0 | 0.1868 | 0 | 0.22971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4806 | 11.03% | CZ 3B | 23.2103 | 3.8954 | 2.5934 | 2.2293 | 0 | 6.2938 | 0 | 7.7394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.3613 | 11.03% | CZ 3B | 6.8006 | 1.1414 | 0.75988 | 0 | 0 | 1.8441 | 0 | 2.2677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.3957 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.022293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022293 | 11.03% | CZ 3B | 71.1957 | 11.9489 | 7.9551 | 2.4366 | 0 | 19.3056 | 0 | 23.7401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 153.145 | 11.03%
CZ 3C | 0.6889 | 0.11582 | 0.077901 | 0.0085725 | 0 | 0.082003 | 0 | 0.17835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3118 | 1.823% | CZ 3C | 23.2103 | 3.9022 | 2.6246 | 0.85725 | 0 | 2.7628 | 0 | 6.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 44.7657 | 1.823% | CZ 3C | 6.8006 | 1.1433 | 0.76901 | 0 | 0 | 0.80951 | 0 | 1.7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8652 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.0085725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085725 | 1.823% | CZ 3C | 71.1957 | 11.9696 | 8.0508 | 0.93697 | 0 | 8.4747 | 0 | 18.4319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 135.6226 | 1.823%
CZ 4A | 0.6889 | 0.11587 | 0.079739 | 0.14486 | 0 | 0.12551 | 0 | 0.19287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.508 | 15.73% | CZ 4A | 23.2103 | 3.9038 | 2.6866 | 14.4856 | 0 | 4.2287 | 0 | 6.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.4128 | 15.73% | CZ 4A | 6.8006 | 1.1438 | 0.78716 | 0 | 0 | 1.239 | 0 | 1.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.4567 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.14486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14486 | 15.73% | CZ 4A | 71.1957 | 11.9747 | 8.2408 | 15.8328 | 0 | 12.9712 | 0 | 19.9325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 156.7106 | 15.73%
CZ 4B | 0.6889 | 0.11558 | 0.079064 | 0.040036 | 0 | 0.13374 | 0 | 0.22883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4464 | 0.4211% | CZ 4B | 23.2103 | 3.8942 | 2.6638 | 4.0036 | 0 | 4.506 | 0 | 7.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.387 | 0.4211% | CZ 4B | 6.8006 | 1.141 | 0.78049 | 0 | 0 | 1.3202 | 0 | 2.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.8833 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.040036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040036 | 0.4211% | CZ 4B | 71.1957 | 11.945 | 8.171 | 4.3759 | 0 | 13.8217 | 0 | 23.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 149.7205 | 0.4211%
CZ 4C | 0.6889 | 0.11584 | 0.080377 | 0.10128 | 0 | 0.046348 | 0 | 0.18068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3737 | 1.866% | CZ 4C | 23.2103 | 3.903 | 2.708 | 10.1282 | 0 | 1.5615 | 0 | 6.0873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.998 | 1.866% | CZ 4C | 6.8006 | 1.1436 | 0.79346 | 0 | 0 | 0.45753 | 0 | 1.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.5609 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.10128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 1.866% | CZ 4C | 71.1957 | 11.9721 | 8.3067 | 11.0701 | 0 | 4.7899 | 0 | 18.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 142.5698 | 1.866%
CZ 5A | 0.6889 | 0.11567 | 0.081453 | 0.23217 | 0 | 0.074774 | 0 | 0.18299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5362 | 16.97% | CZ 5A | 23.2103 | 3.8971 | 2.7443 | 23.2173 | 0 | 2.5193 | 0 | 6.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 67.1532 | 16.97% | CZ 5A | 6.8006 | 1.1419 | 0.80407 | 0 | 0 | 0.73815 | 0 | 1.8064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8732 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.23217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23217 | 16.97% | CZ 5A | 71.1957 | 11.954 | 8.4179 | 25.3765 | 0 | 7.7277 | 0 | 18.9114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 160.1462 | 16.97%
CZ 5B | 0.6889 | 0.11579 | 0.080902 | 0.11558 | 0 | 0.10311 | 0 | 0.22545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.49 | 3.575% | CZ 5B | 23.2103 | 3.9013 | 2.7257 | 11.5583 | 0 | 3.4741 | 0 | 7.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.8651 | 3.575% | CZ 5B | 6.8006 | 1.1431 | 0.79864 | 0 | 0 | 1.0179 | 0 | 2.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.5679 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.11558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11558 | 3.575% | CZ 5B | 71.1957 | 11.967 | 8.361 | 12.6332 | 0 | 10.6564 | 0 | 23.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 154.6756 | 3.575%
CZ 5C | 0.6889 | 0.11578 | 0.081365 | 0.12286 | 0 | 0.025275 | 0 | 0.16867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.3631 | 0.016% | CZ 5C | 23.2103 | 3.9009 | 2.7413 | 12.2862 | 0 | 0.85156 | 0 | 5.6828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.0728 | 0.016% | CZ 5C | 6.8006 | 1.143 | 0.80321 | 0 | 0 | 0.24951 | 0 | 1.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2435 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.12286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12286 | 0.016% | CZ 5C | 71.1957 | 11.9657 | 8.4088 | 13.4289 | 0 | 2.6121 | 0 | 17.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 141.6056 | 0.016%
CZ 6A | 0.6889 | 0.11574 | 0.082703 | 0.31703 | 0 | 0.083429 | 0 | 0.19573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6438 | 1.571% | CZ 6A | 23.2103 | 3.8996 | 2.7864 | 31.7034 | 0 | 2.8109 | 0 | 6.5946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 76.4049 | 1.571% | CZ 6A | 6.8006 | 1.1426 | 0.81642 | 0 | 0 | 0.82358 | 0 | 1.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.0975 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.31703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31703 | 1.571% | CZ 6A | 71.1957 | 11.9618 | 8.5471 | 34.6518 | 0 | 8.6221 | 0 | 20.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 171.7699 | 1.571%
CZ 6B | 0.6889 | 0.11559 | 0.082378 | 0.21295 | 0 | 0.069797 | 0 | 0.20975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5396 | 0.2327% | CZ 6B | 23.2103 | 3.8946 | 2.7755 | 21.2947 | 0 | 2.3516 | 0 | 7.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.9932 | 0.2327% | CZ 6B | 6.8006 | 1.1411 | 0.81321 | 0 | 0 | 0.68901 | 0 | 2.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.0967 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.21295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21295 | 0.2327% | CZ 6B | 71.1957 | 11.9463 | 8.5135 | 23.2751 | 0 | 7.2133 | 0 | 21.6773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 160.3841 | 0.2327%
CZ 7 | 0.6889 | 0.11579 | 0.084142 | 0.38368 | 0 | 0.064594 | 0 | 0.19982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6972 | 0.07923% | CZ 7 | 23.2103 | 3.9013 | 2.8349 | 38.3676 | 0 | 2.1763 | 0 | 6.7324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 82.6225 | 0.07923% | CZ 7 | 6.8006 | 1.1431 | 0.83062 | 0 | 0 | 0.63765 | 0 | 1.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.9667 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.38368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38368 | 0.07923% | CZ 7 | 71.1957 | 11.967 | 8.6957 | 41.9358 | 0 | 6.6756 | 0 | 20.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 177.6839 | 0.07923%
CZ 8 | 0.6889 | 0.1166 | 0.086143 | 0.55935 | 0 | 0.028139 | 0 | 0.22098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.8604 | 0.02367% | CZ 8 | 23.2103 | 3.9283 | 2.9023 | 55.9347 | 0 | 0.94805 | 0 | 7.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 99.7686 | 0.02367% | CZ 8 | 6.8006 | 1.151 | 0.85037 | 0 | 0 | 0.27778 | 0 | 2.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8433 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.55935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55935 | 0.02367% | CZ 8 | 71.1957 | 12.0497 | 8.9025 | 61.1366 | 0 | 2.9081 | 0 | 22.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 195.5935 | 0.02367%
US Weighted | 0.6889 | 0.11568 | 0.078068 | 0.092785 | 0 | 0.19779 | 0 | 0.19211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5256 | 100% | US Weighted | 23.2103 | 3.8975 | 2.6303 | 9.2785 | 0 | 6.6638 | 0 | 6.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.5525 | 100% | US Weighted | 6.8006 | 1.142 | 0.77066 | 0 | 0 | 1.9525 | 0 | 1.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.1443 | 100% | US Weighted | 0 | 0 | 0 | 0.092785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092785 | 100% | US Weighted | 71.1957 | 11.9553 | 8.0681 | 10.1414 | 0 | 20.4406 | 0 | 19.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 158.2179 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.76333 | 0.11578 | 0.073524 | 3.37e-05 | 0 | 0.51435 | 0 | 0.22532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.8526 | 3.475% | CZ 1A | 25.7178 | 3.9009 | 2.4771 | 0.00337 | 0 | 17.3295 | 0 | 7.5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.4198 | 3.475% | CZ 1A | 7.5353 | 1.143 | 0.7258 | 0 | 0 | 5.0775 | 0 | 2.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 18.288 | 3.475% | CZ 1A | 0 | 0 | 0 | 3.37e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37e-05 | 3.475% | CZ 1A | 78.8871 | 11.9657 | 7.5984 | 0.0036834 | 0 | 53.1567 | 0 | 23.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 191.461 | 3.475%
CZ 1B | 0.76333 | 0.11559 | 0.073536 | 0.0057417 | 0 | 0.54627 | 0 | 0.30675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.9715 | 0% | CZ 1B | 25.7178 | 3.8946 | 2.4776 | 0.57417 | 0 | 18.4048 | 0 | 10.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 66.8035 | 0% | CZ 1B | 7.5353 | 1.1411 | 0.72593 | 0 | 0 | 5.3926 | 0 | 3.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 19.4052 | 0% | CZ 1B | 0 | 0 | 0 | 0.0057417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0057417 | 0% | CZ 1B | 78.8871 | 11.9463 | 7.5997 | 0.62756 | 0 | 56.4551 | 0 | 31.7017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 203.7804 | 0%
CZ 2A | 0.76333 | 0.11556 | 0.075075 | 0.010367 | 0 | 0.44603 | 0 | 0.26809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.8387 | 19.08% | CZ 2A | 25.7178 | 3.8933 | 2.5294 | 1.0367 | 0 | 15.0276 | 0 | 9.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.637 | 19.08% | CZ 2A | 7.5353 | 1.1407 | 0.74111 | 0 | 0 | 4.4031 | 0 | 2.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 18.0489 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.010367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010367 | 19.08% | CZ 2A | 78.8871 | 11.9424 | 7.7587 | 1.1331 | 0 | 46.0959 | 0 | 27.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 190.0869 | 19.08%
CZ 2B | 0.76333 | 0.11566 | 0.0751 | 0.0049118 | 0 | 0.34962 | 0 | 0.30596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.7748 | 4.471% | CZ 2B | 25.7178 | 3.8967 | 2.5302 | 0.49118 | 0 | 11.7794 | 0 | 10.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.1233 | 4.471% | CZ 2B | 7.5353 | 1.1417 | 0.74136 | 0 | 0 | 3.4514 | 0 | 3.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 17.4722 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.0049118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049118 | 4.471% | CZ 2B | 78.8871 | 11.9528 | 7.7613 | 0.53686 | 0 | 36.1323 | 0 | 31.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 183.4536 | 4.471%
CZ 3A | 0.76333 | 0.11563 | 0.077701 | 0.060833 | 0 | 0.22839 | 0 | 0.22562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6318 | 19.64% | CZ 3A | 25.7178 | 3.8958 | 2.6179 | 6.0833 | 0 | 7.6948 | 0 | 7.6017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 59.0109 | 19.64% | CZ 3A | 7.5353 | 1.1415 | 0.76704 | 0 | 0 | 2.2546 | 0 | 2.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.5078 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.060833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060833 | 19.64% | CZ 3A | 78.8871 | 11.9502 | 8.0301 | 6.649 | 0 | 23.6031 | 0 | 23.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 169 | 19.64%
CZ 3B | 0.76333 | 0.11562 | 0.07695 | 0.01867 | 0 | 0.21095 | 0 | 0.26097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6068 | 11.03% | CZ 3B | 25.7178 | 3.8954 | 2.5926 | 1.867 | 0 | 7.1074 | 0 | 8.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.3722 | 11.03% | CZ 3B | 7.5353 | 1.1414 | 0.75963 | 0 | 0 | 2.0825 | 0 | 2.5762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.677 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.01867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01867 | 11.03% | CZ 3B | 78.8871 | 11.9489 | 7.9526 | 2.0406 | 0 | 21.8014 | 0 | 26.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 166.1635 | 11.03%
CZ 3C | 0.76333 | 0.11582 | 0.077888 | 0.0068496 | 0 | 0.10349 | 0 | 0.23003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4577 | 1.823% | CZ 3C | 25.7178 | 3.9022 | 2.6242 | 0.68496 | 0 | 3.4867 | 0 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.5654 | 1.823% | CZ 3C | 7.5353 | 1.1433 | 0.76889 | 0 | 0 | 1.0216 | 0 | 2.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.322 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.0068496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0068496 | 1.823% | CZ 3C | 78.8871 | 11.9696 | 8.0495 | 0.74866 | 0 | 10.6952 | 0 | 23.7724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 150.6854 | 1.823%
CZ 4A | 0.76333 | 0.11587 | 0.079802 | 0.14859 | 0 | 0.14672 | 0 | 0.21886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6334 | 15.73% | CZ 4A | 25.7178 | 3.9038 | 2.6887 | 14.8588 | 0 | 4.9433 | 0 | 7.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 64.8858 | 15.73% | CZ 4A | 7.5353 | 1.1438 | 0.78778 | 0 | 0 | 1.4484 | 0 | 2.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.6579 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.14859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14859 | 15.73% | CZ 4A | 78.8871 | 11.9747 | 8.2472 | 16.2407 | 0 | 15.1632 | 0 | 22.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 169.6943 | 15.73%
CZ 4B | 0.76333 | 0.11558 | 0.079127 | 0.040162 | 0 | 0.15884 | 0 | 0.27925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5966 | 0.4211% | CZ 4B | 25.7178 | 3.8942 | 2.6659 | 4.0162 | 0 | 5.3516 | 0 | 9.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 56.4537 | 0.4211% | CZ 4B | 7.5353 | 1.141 | 0.78111 | 0 | 0 | 1.568 | 0 | 2.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.3642 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.040162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040162 | 0.4211% | CZ 4B | 78.8871 | 11.945 | 8.1775 | 4.3897 | 0 | 16.4157 | 0 | 28.8595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 165.2375 | 0.4211%
CZ 4C | 0.76333 | 0.11584 | 0.080415 | 0.094933 | 0 | 0.058892 | 0 | 0.23894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.5126 | 1.866% | CZ 4C | 25.7178 | 3.903 | 2.7093 | 9.4933 | 0 | 1.9842 | 0 | 8.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.2576 | 1.866% | CZ 4C | 7.5353 | 1.1436 | 0.79383 | 0 | 0 | 0.58136 | 0 | 2.3588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.9949 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.094933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094933 | 1.866% | CZ 4C | 78.8871 | 11.9721 | 8.3106 | 10.3762 | 0 | 6.0862 | 0 | 24.6939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 156.8892 | 1.866%
CZ 5A | 0.76333 | 0.11567 | 0.081515 | 0.23939 | 0 | 0.087918 | 0 | 0.21813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6662 | 16.97% | CZ 5A | 25.7178 | 3.8971 | 2.7464 | 23.9393 | 0 | 2.9621 | 0 | 7.3493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 72.0116 | 16.97% | CZ 5A | 7.5353 | 1.1419 | 0.80469 | 0 | 0 | 0.8679 | 0 | 2.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.0852 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.23939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23939 | 16.97% | CZ 5A | 78.8871 | 11.954 | 8.4243 | 26.1657 | 0 | 9.0861 | 0 | 22.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 173.6235 | 16.97%
CZ 5B | 0.76333 | 0.11579 | 0.080977 | 0.11974 | 0 | 0.11838 | 0 | 0.27282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6313 | 3.575% | CZ 5B | 25.7178 | 3.9013 | 2.7283 | 11.9741 | 0 | 3.9885 | 0 | 9.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.9015 | 3.575% | CZ 5B | 7.5353 | 1.1431 | 0.79938 | 0 | 0 | 1.1686 | 0 | 2.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.9217 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.11974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11974 | 3.575% | CZ 5B | 78.8871 | 11.967 | 8.3687 | 13.0877 | 0 | 12.2345 | 0 | 28.1952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 169.3033 | 3.575%
CZ 5C | 0.76333 | 0.11578 | 0.081403 | 0.11973 | 0 | 0.033179 | 0 | 0.22101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.4947 | 0.016% | CZ 5C | 25.7178 | 3.9009 | 2.7426 | 11.9732 | 0 | 1.1179 | 0 | 7.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.2982 | 0.016% | CZ 5C | 7.5353 | 1.143 | 0.80358 | 0 | 0 | 0.32753 | 0 | 2.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.5732 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.11973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11973 | 0.016% | CZ 5C | 78.8871 | 11.9657 | 8.4127 | 13.0868 | 0 | 3.4289 | 0 | 22.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 155.1847 | 0.016%
CZ 6A | 0.76333 | 0.11574 | 0.082766 | 0.33314 | 0 | 0.098986 | 0 | 0.21772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.772 | 1.571% | CZ 6A | 25.7178 | 3.8996 | 2.7885 | 33.3143 | 0 | 3.335 | 0 | 7.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 81.7903 | 1.571% | CZ 6A | 7.5353 | 1.1426 | 0.81704 | 0 | 0 | 0.97716 | 0 | 2.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.2035 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.33314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33314 | 1.571% | CZ 6A | 78.8871 | 11.9618 | 8.5536 | 36.4125 | 0 | 10.2299 | 0 | 22.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 185.1085 | 1.571%
CZ 6B | 0.76333 | 0.11559 | 0.082441 | 0.21986 | 0 | 0.079214 | 0 | 0.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6785 | 0.2327% | CZ 6B | 25.7178 | 3.8946 | 2.7776 | 21.986 | 0 | 2.6689 | 0 | 8.6858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 71.1302 | 0.2327% | CZ 6B | 7.5353 | 1.1411 | 0.81383 | 0 | 0 | 0.78198 | 0 | 2.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.3993 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.21986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21986 | 0.2327% | CZ 6B | 78.8871 | 11.9463 | 8.52 | 24.0307 | 0 | 8.1865 | 0 | 26.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 174.7765 | 0.2327%
CZ 7 | 0.76333 | 0.11579 | 0.084242 | 0.41596 | 0 | 0.066883 | 0 | 0.22502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.8315 | 0.07923% | CZ 7 | 25.7178 | 3.9013 | 2.8382 | 41.5957 | 0 | 2.2534 | 0 | 7.5814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 89.2875 | 0.07923% | CZ 7 | 7.5353 | 1.1431 | 0.8316 | 0 | 0 | 0.66025 | 0 | 2.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.9737 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.41596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41596 | 0.07923% | CZ 7 | 78.8871 | 11.967 | 8.7061 | 45.4641 | 0 | 6.9121 | 0 | 23.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 191.7548 | 0.07923%
CZ 8 | 0.76333 | 0.1166 | 0.086268 | 0.61126 | 0 | 0.023787 | 0 | 0.27951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 2.041 | 0.02367% | CZ 8 | 25.7178 | 3.9283 | 2.9065 | 61.1262 | 0 | 0.80142 | 0 | 9.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 109.2971 | 0.02367% | CZ 8 | 7.5353 | 1.151 | 0.8516 | 0 | 0 | 0.23481 | 0 | 2.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.1141 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.61126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61126 | 0.02367% | CZ 8 | 78.8871 | 12.0497 | 8.9155 | 66.8109 | 0 | 2.4583 | 0 | 28.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 214.5712 | 0.02367%
US Weighted | 0.76333 | 0.11568 | 0.078109 | 0.092782 | 0 | 0.2344 | 0 | 0.24108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16027 | 1.6856 | 100% | US Weighted | 25.7178 | 3.8975 | 2.6316 | 9.2782 | 0 | 7.8975 | 0 | 8.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.9445 | 100% | US Weighted | 7.5353 | 1.142 | 0.77107 | 0 | 0 | 2.314 | 0 | 2.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.7242 | 100% | US Weighted | 0 | 0 | 0 | 0.092782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092782 | 100% | US Weighted | 78.8871 | 11.9553 | 8.0723 | 10.1411 | 0 | 24.2249 | 0 | 24.9143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.563 | 174.758 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.85202 | 0.21094 | 0.080227 | 1.2638e-05 | 0 | 0.73946 | 0 | 0.32285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3665 | 3.475% | CZ 1A | 28.706 | 7.107 | 2.703 | 0.0012638 | 0 | 24.9138 | 0 | 10.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.732 | 3.475% | CZ 1A | 8.4109 | 2.0823 | 0.79198 | 0 | 0 | 7.2998 | 0 | 3.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 23.3611 | 3.475% | CZ 1A | 0 | 0 | 0 | 1.2638e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2638e-05 | 3.475% | CZ 1A | 88.0533 | 21.8001 | 8.2912 | 0.0013813 | 0 | 76.4211 | 0 | 33.3651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 244.5689 | 3.475%
CZ 1B | 0.85202 | 0.21068 | 0.08019 | 0.003846 | 0 | 0.72311 | 0 | 0.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.4121 | 0% | CZ 1B | 28.706 | 7.0981 | 2.7017 | 0.3846 | 0 | 24.3627 | 0 | 12.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 81.5235 | 0% | CZ 1B | 8.4109 | 2.0798 | 0.7916 | 0 | 0 | 7.1383 | 0 | 3.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 23.7737 | 0% | CZ 1B | 0 | 0 | 0 | 0.003846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003846 | 0% | CZ 1B | 88.0533 | 21.7729 | 8.2873 | 0.42037 | 0 | 74.7306 | 0 | 39.4061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 249.3073 | 0%
CZ 2A | 0.85202 | 0.2106 | 0.081865 | 0.010881 | 0 | 0.65645 | 0 | 0.33863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3114 | 19.08% | CZ 2A | 28.706 | 7.0956 | 2.7582 | 1.0881 | 0 | 22.1169 | 0 | 11.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.5975 | 19.08% | CZ 2A | 8.4109 | 2.079 | 0.80815 | 0 | 0 | 6.4802 | 0 | 3.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.7102 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.010881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010881 | 19.08% | CZ 2A | 88.0533 | 21.7652 | 8.4605 | 1.1893 | 0 | 67.8417 | 0 | 34.9962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 238.9429 | 19.08%
CZ 2B | 0.85202 | 0.21075 | 0.08184 | 0.007136 | 0 | 0.49276 | 0 | 0.37817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1837 | 4.471% | CZ 2B | 28.706 | 7.1007 | 2.7573 | 0.7136 | 0 | 16.6018 | 0 | 12.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 74.0444 | 4.471% | CZ 2B | 8.4109 | 2.0805 | 0.8079 | 0 | 0 | 4.8643 | 0 | 3.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 21.4859 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.007136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007136 | 4.471% | CZ 2B | 88.0533 | 21.7807 | 8.4579 | 0.77997 | 0 | 50.9246 | 0 | 39.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 225.7161 | 4.471%
CZ 3A | 0.85202 | 0.21072 | 0.084629 | 0.063988 | 0 | 0.35061 | 0 | 0.29467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0176 | 19.64% | CZ 3A | 28.706 | 7.0994 | 2.8513 | 6.3988 | 0 | 11.8127 | 0 | 9.9279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.2198 | 19.64% | CZ 3A | 8.4109 | 2.0801 | 0.83543 | 0 | 0 | 3.4611 | 0 | 2.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2856 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.063988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063988 | 19.64% | CZ 3A | 88.0533 | 21.7768 | 8.7461 | 6.9939 | 0 | 36.2344 | 0 | 30.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 208.8944 | 19.64%
CZ 3B | 0.85202 | 0.2107 | 0.083741 | 0.015443 | 0 | 0.28852 | 0 | 0.31813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9295 | 11.03% | CZ 3B | 28.706 | 7.099 | 2.8214 | 1.5443 | 0 | 9.7206 | 0 | 10.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 66.0334 | 11.03% | CZ 3B | 8.4109 | 2.08 | 0.82667 | 0 | 0 | 2.8481 | 0 | 3.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.8953 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.015443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015443 | 11.03% | CZ 3B | 88.0533 | 21.7755 | 8.6544 | 1.6879 | 0 | 29.8173 | 0 | 32.8778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 199.5029 | 11.03%
CZ 3C | 0.85202 | 0.21068 | 0.084704 | 0.0056364 | 0 | 0.1492 | 0 | 0.25977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.723 | 1.823% | CZ 3C | 28.706 | 7.0981 | 2.8538 | 0.56364 | 0 | 5.0268 | 0 | 8.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 58.424 | 1.823% | CZ 3C | 8.4109 | 2.0798 | 0.83617 | 0 | 0 | 1.4728 | 0 | 2.5643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.9531 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.0056364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056364 | 1.823% | CZ 3C | 88.0533 | 21.7729 | 8.7539 | 0.61605 | 0 | 15.4192 | 0 | 26.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 178.0979 | 1.823%
CZ 4A | 0.85202 | 0.21039 | 0.08688 | 0.15847 | 0 | 0.20638 | 0 | 0.26905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9442 | 15.73% | CZ 4A | 28.706 | 7.0884 | 2.9271 | 15.8467 | 0 | 6.9532 | 0 | 9.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 76.0097 | 15.73% | CZ 4A | 8.4109 | 2.0769 | 0.85765 | 0 | 0 | 2.0373 | 0 | 2.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.6278 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.15847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15847 | 15.73% | CZ 4A | 88.0533 | 21.7432 | 8.9788 | 17.3204 | 0 | 21.3283 | 0 | 27.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 201.8656 | 15.73%
CZ 4B | 0.85202 | 0.21055 | 0.08608 | 0.040794 | 0 | 0.21142 | 0 | 0.32877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.8906 | 0.4211% | CZ 4B | 28.706 | 7.0939 | 2.9002 | 4.0794 | 0 | 7.123 | 0 | 11.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 66.4032 | 0.4211% | CZ 4B | 8.4109 | 2.0785 | 0.84975 | 0 | 0 | 2.087 | 0 | 3.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.2609 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.040794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040794 | 0.4211% | CZ 4B | 88.0533 | 21.76 | 8.8961 | 4.4588 | 0 | 21.8492 | 0 | 33.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 195.6318 | 0.4211%
CZ 4C | 0.85202 | 0.21015 | 0.087481 | 0.10045 | 0 | 0.071998 | 0 | 0.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.7391 | 1.866% | CZ 4C | 28.706 | 7.0804 | 2.9474 | 10.0452 | 0 | 2.4257 | 0 | 8.6251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 65.2535 | 1.866% | CZ 4C | 8.4109 | 2.0746 | 0.86358 | 0 | 0 | 0.71074 | 0 | 2.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.176 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.10045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10045 | 1.866% | CZ 4C | 88.0533 | 21.7187 | 9.0408 | 10.9794 | 0 | 7.4407 | 0 | 26.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 180.3264 | 1.866%
CZ 5A | 0.85202 | 0.21047 | 0.088669 | 0.26343 | 0 | 0.12803 | 0 | 0.26223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9658 | 16.97% | CZ 5A | 28.706 | 7.091 | 2.9874 | 26.3426 | 0 | 4.3134 | 0 | 8.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 83.699 | 16.97% | CZ 5A | 8.4109 | 2.0777 | 0.87531 | 0 | 0 | 1.2638 | 0 | 2.5886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.8054 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.26343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26343 | 16.97% | CZ 5A | 88.0533 | 21.751 | 9.1636 | 28.7924 | 0 | 13.231 | 0 | 27.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 204.7285 | 16.97%
CZ 5B | 0.85202 | 0.21047 | 0.088031 | 0.11992 | 0 | 0.16765 | 0 | 0.32356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9226 | 3.575% | CZ 5B | 28.706 | 7.091 | 2.9659 | 11.9918 | 0 | 5.6483 | 0 | 10.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.7279 | 3.575% | CZ 5B | 8.4109 | 2.0777 | 0.86901 | 0 | 0 | 1.6549 | 0 | 3.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.7957 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.11992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11992 | 3.575% | CZ 5B | 88.0533 | 21.751 | 9.0977 | 13.107 | 0 | 17.3255 | 0 | 33.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 199.41 | 3.575%
CZ 5C | 0.85202 | 0.21014 | 0.088519 | 0.12191 | 0 | 0.040745 | 0 | 0.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.7109 | 0.016% | CZ 5C | 28.706 | 7.08 | 2.9823 | 12.1906 | 0 | 1.3728 | 0 | 7.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 65.727 | 0.016% | CZ 5C | 8.4109 | 2.0744 | 0.87383 | 0 | 0 | 0.40222 | 0 | 2.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.6862 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.12191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12191 | 0.016% | CZ 5C | 88.0533 | 21.7174 | 9.1481 | 13.3243 | 0 | 4.2109 | 0 | 24.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 177.5429 | 0.016%
CZ 6A | 0.85202 | 0.21037 | 0.089957 | 0.37811 | 0 | 0.14385 | 0 | 0.28044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1157 | 1.571% | CZ 6A | 28.706 | 7.0876 | 3.0308 | 37.8112 | 0 | 4.8464 | 0 | 9.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 96.3541 | 1.571% | CZ 6A | 8.4109 | 2.0767 | 0.88802 | 0 | 0 | 1.42 | 0 | 2.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.1531 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.37811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37811 | 1.571% | CZ 6A | 88.0533 | 21.7406 | 9.2967 | 41.3276 | 0 | 14.866 | 0 | 28.9823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 220.9033 | 1.571%
CZ 6B | 0.85202 | 0.21022 | 0.089607 | 0.23757 | 0 | 0.11107 | 0 | 0.3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9688 | 0.2327% | CZ 6B | 28.706 | 7.0825 | 3.019 | 23.7569 | 0 | 3.742 | 0 | 10.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 82.0837 | 0.2327% | CZ 6B | 8.4109 | 2.0752 | 0.88457 | 0 | 0 | 1.0964 | 0 | 3.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.0898 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.23757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23757 | 0.2327% | CZ 6B | 88.0533 | 21.7251 | 9.2605 | 25.9663 | 0 | 11.4784 | 0 | 31.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 204.879 | 0.2327%
CZ 7 | 0.85202 | 0.21008 | 0.091458 | 0.48217 | 0 | 0.10839 | 0 | 0.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1923 | 0.07923% | CZ 7 | 28.706 | 7.0779 | 3.0814 | 48.2174 | 0 | 3.6519 | 0 | 9.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 105.8346 | 0.07923% | CZ 7 | 8.4109 | 2.0738 | 0.90284 | 0 | 0 | 1.07 | 0 | 2.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.8819 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.48217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48217 | 0.07923% | CZ 7 | 88.0533 | 21.7109 | 9.4518 | 52.7016 | 0 | 11.2018 | 0 | 29.6816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 229.4377 | 0.07923%
CZ 8 | 0.85202 | 0.20893 | 0.093534 | 0.69214 | 0 | 0.055065 | 0 | 0.32142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3841 | 0.02367% | CZ 8 | 28.706 | 7.0391 | 3.1513 | 69.2142 | 0 | 1.8552 | 0 | 10.8292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 126.2188 | 0.02367% | CZ 8 | 8.4109 | 2.0625 | 0.92333 | 0 | 0 | 0.54358 | 0 | 3.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.7023 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.69214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69214 | 0.02367% | CZ 8 | 88.0533 | 21.592 | 9.6664 | 75.6512 | 0 | 5.6907 | 0 | 33.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 250.508 | 0.02367%
US Weighted | 0.85202 | 0.21058 | 0.085052 | 0.099783 | 0 | 0.3414 | 0 | 0.30044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0502 | 100% | US Weighted | 28.706 | 7.0948 | 2.8655 | 9.9783 | 0 | 11.5022 | 0 | 10.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.6928 | 100% | US Weighted | 8.4109 | 2.0788 | 0.8396 | 0 | 0 | 3.3701 | 0 | 2.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2543 | 100% | US Weighted | 0 | 0 | 0 | 0.099783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099783 | 100% | US Weighted | 88.0533 | 21.7628 | 8.7898 | 10.9063 | 0 | 35.282 | 0 | 31.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 212.4801 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.79045 | 0.21094 | 0.08024 | 4.2125e-05 | 0 | 0.76155 | 0 | 0.31312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3173 | 3.475% | CZ 1A | 26.6317 | 7.107 | 2.7034 | 0.0042125 | 0 | 25.6579 | 0 | 10.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.0774 | 3.475% | CZ 1A | 7.8031 | 2.0823 | 0.7921 | 0 | 0 | 7.5178 | 0 | 3.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.8754 | 3.475% | CZ 1A | 0 | 0 | 0 | 4.2125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2125e-05 | 3.475% | CZ 1A | 81.6905 | 21.8001 | 8.2925 | 0.0046043 | 0 | 78.7036 | 0 | 32.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 239.4875 | 3.475%
CZ 1B | 0.79045 | 0.21068 | 0.080227 | 0.0060281 | 0 | 0.75338 | 0 | 0.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3766 | 0% | CZ 1B | 26.6317 | 7.0981 | 2.703 | 0.60281 | 0 | 25.3828 | 0 | 12.6309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 80.473 | 0% | CZ 1B | 7.8031 | 2.0798 | 0.79198 | 0 | 0 | 7.4372 | 0 | 3.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 23.402 | 0% | CZ 1B | 0 | 0 | 0 | 0.0060281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060281 | 0% | CZ 1B | 81.6905 | 21.7729 | 8.2912 | 0.65887 | 0 | 77.8596 | 0 | 38.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 245.6542 | 0%
CZ 2A | 0.79045 | 0.2106 | 0.081928 | 0.019007 | 0 | 0.69443 | 0 | 0.34626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3037 | 19.08% | CZ 2A | 26.6317 | 7.0956 | 2.7603 | 1.9007 | 0 | 23.3965 | 0 | 11.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.8745 | 19.08% | CZ 2A | 7.8031 | 2.079 | 0.80877 | 0 | 0 | 6.8552 | 0 | 3.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.5533 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.019007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019007 | 19.08% | CZ 2A | 81.6905 | 21.7652 | 8.467 | 2.0775 | 0 | 71.7669 | 0 | 35.7846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 238.1883 | 19.08%
CZ 2B | 0.79045 | 0.21075 | 0.081928 | 0.012006 | 0 | 0.51647 | 0 | 0.38835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1609 | 4.471% | CZ 2B | 26.6317 | 7.1007 | 2.7603 | 1.2006 | 0 | 17.4007 | 0 | 13.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 73.6019 | 4.471% | CZ 2B | 7.8031 | 2.0805 | 0.80877 | 0 | 0 | 5.0984 | 0 | 3.8337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 21.2136 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.012006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012006 | 4.471% | CZ 2B | 81.6905 | 21.7807 | 8.467 | 1.3122 | 0 | 53.3751 | 0 | 40.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 223.3972 | 4.471%
CZ 3A | 0.79045 | 0.21072 | 0.084767 | 0.11817 | 0 | 0.39851 | 0 | 0.33278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0964 | 19.64% | CZ 3A | 26.6317 | 7.0994 | 2.8559 | 11.8174 | 0 | 13.4265 | 0 | 11.2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.4663 | 19.64% | CZ 3A | 7.8031 | 2.0801 | 0.83679 | 0 | 0 | 3.934 | 0 | 3.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.5281 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.11817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11817 | 19.64% | CZ 3A | 81.6905 | 21.7768 | 8.7604 | 12.9164 | 0 | 41.1845 | 0 | 34.3913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 217.3566 | 19.64%
CZ 3B | 0.79045 | 0.2107 | 0.083904 | 0.02897 | 0 | 0.3363 | 0 | 0.36902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9803 | 11.03% | CZ 3B | 26.6317 | 7.099 | 2.8269 | 2.897 | 0 | 11.3306 | 0 | 12.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 68.6417 | 11.03% | CZ 3B | 7.8031 | 2.08 | 0.82827 | 0 | 0 | 3.3199 | 0 | 3.6428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2632 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.02897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02897 | 11.03% | CZ 3B | 81.6905 | 21.7755 | 8.6712 | 3.1664 | 0 | 34.7558 | 0 | 38.1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 204.8329 | 11.03%
CZ 3C | 0.79045 | 0.21068 | 0.084917 | 0.013868 | 0 | 0.17043 | 0 | 0.28959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.7209 | 1.823% | CZ 3C | 26.6317 | 7.0981 | 2.861 | 1.3868 | 0 | 5.7422 | 0 | 9.7569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 58.9003 | 1.823% | CZ 3C | 7.8031 | 2.0798 | 0.83827 | 0 | 0 | 1.6825 | 0 | 2.8588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.8515 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.013868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013868 | 1.823% | CZ 3C | 81.6905 | 21.7729 | 8.7759 | 1.5157 | 0 | 17.6138 | 0 | 29.9284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 177.9339 | 1.823%
CZ 4A | 0.79045 | 0.21039 | 0.087055 | 0.29253 | 0 | 0.24685 | 0 | 0.30694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0952 | 15.73% | CZ 4A | 26.6317 | 7.0884 | 2.933 | 29.2526 | 0 | 8.3167 | 0 | 10.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 89.9874 | 15.73% | CZ 4A | 7.8031 | 2.0769 | 0.85938 | 0 | 0 | 2.4368 | 0 | 3.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.7953 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.29253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29253 | 15.73% | CZ 4A | 81.6905 | 21.7432 | 8.9969 | 31.9731 | 0 | 25.5108 | 0 | 31.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 218.2722 | 15.73%
CZ 4B | 0.79045 | 0.21055 | 0.086318 | 0.083088 | 0 | 0.23872 | 0 | 0.37652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.9466 | 0.4211% | CZ 4B | 26.6317 | 7.0939 | 2.9082 | 8.3088 | 0 | 8.0428 | 0 | 12.6857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 71.0948 | 0.4211% | CZ 4B | 7.8031 | 2.0785 | 0.8521 | 0 | 0 | 2.3565 | 0 | 3.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.3963 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.083088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083088 | 0.4211% | CZ 4B | 81.6905 | 21.76 | 8.9206 | 9.0815 | 0 | 24.6707 | 0 | 38.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 201.6723 | 0.4211%
CZ 4C | 0.79045 | 0.21015 | 0.087731 | 0.20859 | 0 | 0.075287 | 0 | 0.27819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.8114 | 1.866% | CZ 4C | 26.6317 | 7.0804 | 2.9558 | 20.8591 | 0 | 2.5366 | 0 | 9.3726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 74.8599 | 1.866% | CZ 4C | 7.8031 | 2.0746 | 0.86605 | 0 | 0 | 0.74321 | 0 | 2.7462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.8222 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.20859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20859 | 1.866% | CZ 4C | 81.6905 | 21.7187 | 9.0667 | 22.799 | 0 | 7.7807 | 0 | 28.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 188.4419 | 1.866%
CZ 5A | 0.79045 | 0.21047 | 0.088819 | 0.42717 | 0 | 0.13933 | 0 | 0.28994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1072 | 16.97% | CZ 5A | 26.6317 | 7.091 | 2.9925 | 42.7175 | 0 | 4.6943 | 0 | 9.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 99.3193 | 16.97% | CZ 5A | 7.8031 | 2.0777 | 0.87679 | 0 | 0 | 1.3754 | 0 | 2.8622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.5843 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.42717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42717 | 16.97% | CZ 5A | 81.6905 | 21.751 | 9.1791 | 46.6902 | 0 | 14.3994 | 0 | 29.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 220.3115 | 16.97%
CZ 5B | 0.79045 | 0.21047 | 0.088219 | 0.21016 | 0 | 0.18859 | 0 | 0.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0094 | 3.575% | CZ 5B | 26.6317 | 7.091 | 2.9722 | 21.0158 | 0 | 6.354 | 0 | 12.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 81.6344 | 3.575% | CZ 5B | 7.8031 | 2.0777 | 0.87086 | 0 | 0 | 1.8617 | 0 | 3.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.7612 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.21016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21016 | 3.575% | CZ 5B | 81.6905 | 21.751 | 9.1171 | 22.9703 | 0 | 19.4904 | 0 | 37.2567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 208.9127 | 3.575%
CZ 5C | 0.79045 | 0.21014 | 0.088731 | 0.2472 | 0 | 0.033967 | 0 | 0.24236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 1.7738 | 0.016% | CZ 5C | 26.6317 | 7.08 | 2.9895 | 24.7199 | 0 | 1.1444 | 0 | 8.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 76.1546 | 0.016% | CZ 5C | 7.8031 | 2.0744 | 0.87593 | 0 | 0 | 0.33531 | 0 | 2.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.0704 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2472 | 0.016% | CZ 5C | 81.6905 | 21.7174 | 9.1701 | 27.0189 | 0 | 3.5103 | 0 | 25.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 184.7906 | 0.016%
CZ 6A | 0.79045 | 0.21037 | 0.090132 | 0.57856 | 0 | 0.17178 | 0 | 0.37057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.3728 | 1.571% | CZ 6A | 26.6317 | 7.0876 | 3.0367 | 57.856 | 0 | 5.7877 | 0 | 12.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 118.3086 | 1.571% | CZ 6A | 7.8031 | 2.0767 | 0.88975 | 0 | 0 | 1.6958 | 0 | 3.6581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.7126 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.57856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57856 | 1.571% | CZ 6A | 81.6905 | 21.7406 | 9.3148 | 63.2366 | 0 | 17.7534 | 0 | 38.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 248.6698 | 1.571%
CZ 6B | 0.79045 | 0.21022 | 0.089794 | 0.35041 | 0 | 0.11888 | 0 | 0.37789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.0986 | 0.2327% | CZ 6B | 26.6317 | 7.0825 | 3.0253 | 35.041 | 0 | 4.0054 | 0 | 12.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 93.9413 | 0.2327% | CZ 6B | 7.8031 | 2.0752 | 0.88642 | 0 | 0 | 1.1736 | 0 | 3.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.2578 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.35041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35041 | 0.2327% | CZ 6B | 81.6905 | 21.7251 | 9.2799 | 38.2998 | 0 | 12.2862 | 0 | 39.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 218.9715 | 0.2327%
CZ 7 | 0.79045 | 0.21008 | 0.091608 | 0.68822 | 0 | 0.12559 | 0 | 0.41132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.4782 | 0.07923% | CZ 7 | 26.6317 | 7.0779 | 3.0864 | 68.8221 | 0 | 4.2312 | 0 | 13.8579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 129.1309 | 0.07923% | CZ 7 | 7.8031 | 2.0738 | 0.90432 | 0 | 0 | 1.2398 | 0 | 4.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.6705 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.68822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68822 | 0.07923% | CZ 7 | 81.6905 | 21.7109 | 9.4673 | 75.2225 | 0 | 12.979 | 0 | 42.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 260.2149 | 0.07923%
CZ 8 | 0.79045 | 0.20893 | 0.093621 | 0.90704 | 0 | 0.050112 | 0 | 0.44082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.652 | 0.02367% | CZ 8 | 26.6317 | 7.0391 | 3.1543 | 90.7044 | 0 | 1.6884 | 0 | 14.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 149.4934 | 0.02367% | CZ 8 | 7.8031 | 2.0625 | 0.9242 | 0 | 0 | 0.49469 | 0 | 4.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.2252 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.90704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90704 | 0.02367% | CZ 8 | 81.6905 | 21.592 | 9.6754 | 99.1399 | 0 | 5.1789 | 0 | 45.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 279.4704 | 0.02367%
US Weighted | 0.79045 | 0.21058 | 0.085185 | 0.17178 | 0 | 0.37521 | 0 | 0.32996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16098 | 2.1241 | 100% | US Weighted | 26.6317 | 7.0948 | 2.87 | 17.1776 | 0 | 12.6416 | 0 | 11.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 82.9563 | 100% | US Weighted | 7.8031 | 2.0788 | 0.84092 | 0 | 0 | 3.704 | 0 | 3.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2732 | 100% | US Weighted | 0 | 0 | 0 | 0.17178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17178 | 100% | US Weighted | 81.6905 | 21.7628 | 8.8036 | 18.7752 | 0 | 38.777 | 0 | 34.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6367 | 220.5458 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Strip Mall |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 22500 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 22500 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.22656 | 0.14218 | 0.0067658 | -4.2125e-06 | 0 | 0.36234 | 0 | 0.13906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.87762 | 3.475% | CZ 1A | 7.6333 | 4.7904 | 0.22795 | -0.00042125 | 0 | 12.2079 | 0 | 4.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.5681 | 3.475% | CZ 1A | 2.2365 | 1.4036 | 0.06679 | 0 | 0 | 3.5769 | 0 | 1.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 8.6636 | 3.475% | CZ 1A | 0 | 0 | 0 | -4.2125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2125e-06 | 3.475% | CZ 1A | 23.4144 | 14.6941 | 0.69923 | -0.00046043 | 0 | 37.4467 | 0 | 14.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 90.6986 | 3.475%
CZ 1B | 0.22656 | 0.14203 | 0.0066408 | -0.0024896 | 0 | 0.29304 | 0 | 0.16702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.83352 | 0% | CZ 1B | 7.6333 | 4.7853 | 0.22374 | -0.24896 | 0 | 9.8732 | 0 | 5.6272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 27.9177 | 0% | CZ 1B | 2.2365 | 1.4021 | 0.065556 | 0 | 0 | 2.8928 | 0 | 1.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 8.2528 | 0% | CZ 1B | 0 | 0 | 0 | -0.0024896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0024896 | 0% | CZ 1B | 23.4144 | 14.6786 | 0.6863 | -0.27211 | 0 | 30.2851 | 0 | 17.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 86.1269 | 0%
CZ 2A | 0.22656 | 0.142 | 0.0068659 | 0.0020346 | 0 | 0.34838 | 0 | 0.18747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.91402 | 19.08% | CZ 2A | 7.6333 | 4.7841 | 0.23132 | 0.20346 | 0 | 11.7377 | 0 | 6.3161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 30.9299 | 19.08% | CZ 2A | 2.2365 | 1.4017 | 0.067778 | 0 | 0 | 3.4391 | 0 | 1.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 9.0028 | 19.08% | CZ 2A | 0 | 0 | 0 | 0.0020346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020346 | 19.08% | CZ 2A | 23.4144 | 14.6747 | 0.70957 | 0.22239 | 0 | 36.0043 | 0 | 19.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 94.4731 | 19.08%
CZ 2B | 0.22656 | 0.14207 | 0.0067783 | 0.0063735 | 0 | 0.23633 | 0 | 0.12332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.74215 | 4.471% | CZ 2B | 7.6333 | 4.7866 | 0.22837 | 0.63735 | 0 | 7.9623 | 0 | 4.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 25.4269 | 4.471% | CZ 2B | 2.2365 | 1.4025 | 0.066914 | 0 | 0 | 2.333 | 0 | 1.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.2633 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.0063735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063735 | 4.471% | CZ 2B | 23.4144 | 14.6824 | 0.70052 | 0.69663 | 0 | 24.4238 | 0 | 12.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 76.7365 | 4.471%
CZ 3A | 0.22656 | 0.14206 | 0.007066 | 0.04622 | 0 | 0.22001 | 0 | 0.14662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.78925 | 19.64% | CZ 3A | 7.6333 | 4.7862 | 0.23807 | 4.622 | 0 | 7.4125 | 0 | 4.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.6559 | 19.64% | CZ 3A | 2.2365 | 1.4023 | 0.069753 | 0 | 0 | 2.1719 | 0 | 1.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.3349 | 19.64% | CZ 3A | 0 | 0 | 0 | 0.04622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04622 | 19.64% | CZ 3A | 23.4144 | 14.6812 | 0.73025 | 5.0518 | 0 | 22.7371 | 0 | 15.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 81.8413 | 19.64%
CZ 3B | 0.22656 | 0.14205 | 0.0068784 | -0.0020262 | 0 | 0.16038 | 0 | 0.15036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.68491 | 11.03% | CZ 3B | 7.6333 | 4.7857 | 0.23174 | -0.20262 | 0 | 5.4034 | 0 | 5.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 22.9415 | 11.03% | CZ 3B | 2.2365 | 1.4022 | 0.067901 | 0 | 0 | 1.5832 | 0 | 1.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.7812 | 11.03% | CZ 3B | 0 | 0 | 0 | -0.0020262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0020262 | 11.03% | CZ 3B | 23.4144 | 14.6799 | 0.71086 | -0.22147 | 0 | 16.5746 | 0 | 15.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 70.7713 | 11.03%
CZ 3C | 0.22656 | 0.14179 | 0.0069534 | 0.0023843 | 0 | 0.10041 | 0 | 0.12485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.60367 | 1.823% | CZ 3C | 7.6333 | 4.7773 | 0.23427 | 0.23843 | 0 | 3.3831 | 0 | 4.2064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 20.4967 | 1.823% | CZ 3C | 2.2365 | 1.3998 | 0.068642 | 0 | 0 | 0.99123 | 0 | 1.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.9357 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.0023843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023843 | 1.823% | CZ 3C | 23.4144 | 14.654 | 0.71861 | 0.2606 | 0 | 10.3772 | 0 | 12.9027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 62.4012 | 1.823%
CZ 4A | 0.22656 | 0.14137 | 0.0072786 | 0.13511 | 0 | 0.12915 | 0 | 0.12494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.76512 | 15.73% | CZ 4A | 7.6333 | 4.763 | 0.24523 | 13.5112 | 0 | 4.3513 | 0 | 4.2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 34.7374 | 15.73% | CZ 4A | 2.2365 | 1.3956 | 0.071852 | 0 | 0 | 1.2749 | 0 | 1.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.2193 | 15.73% | CZ 4A | 0 | 0 | 0 | 0.13511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13511 | 15.73% | CZ 4A | 23.4144 | 14.6101 | 0.75222 | 14.7678 | 0 | 13.3473 | 0 | 12.9118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 79.8772 | 15.73%
CZ 4B | 0.22656 | 0.1419 | 0.0072036 | 0.036388 | 0 | 0.11364 | 0 | 0.15989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.6863 | 0.4211% | CZ 4B | 7.6333 | 4.7807 | 0.2427 | 3.6388 | 0 | 3.8288 | 0 | 5.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 25.5353 | 0.4211% | CZ 4B | 2.2365 | 1.4007 | 0.071111 | 0 | 0 | 1.1219 | 0 | 1.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.4157 | 0.4211% | CZ 4B | 0 | 0 | 0 | 0.036388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036388 | 0.4211% | CZ 4B | 23.4144 | 14.6644 | 0.74446 | 3.9772 | 0 | 11.7447 | 0 | 16.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 71.1429 | 0.4211%
CZ 4C | 0.22656 | 0.14109 | 0.0073036 | 0.09142 | 0 | 0.035968 | 0 | 0.11058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.61364 | 1.866% | CZ 4C | 7.6333 | 4.7537 | 0.24607 | 9.142 | 0 | 1.2118 | 0 | 3.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 26.7365 | 1.866% | CZ 4C | 2.2365 | 1.3928 | 0.072099 | 0 | 0 | 0.35506 | 0 | 1.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.1552 | 1.866% | CZ 4C | 0 | 0 | 0 | 0.09142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09142 | 1.866% | CZ 4C | 23.4144 | 14.5816 | 0.7548 | 9.9922 | 0 | 3.7171 | 0 | 11.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 63.9619 | 1.866%
CZ 5A | 0.22656 | 0.14168 | 0.0073286 | 0.17799 | 0 | 0.072123 | 0 | 0.11932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.74572 | 16.97% | CZ 5A | 7.6333 | 4.7735 | 0.24691 | 17.7987 | 0 | 2.4299 | 0 | 4.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.9265 | 16.97% | CZ 5A | 2.2365 | 1.3986 | 0.072346 | 0 | 0 | 0.71198 | 0 | 1.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.6044 | 16.97% | CZ 5A | 0 | 0 | 0 | 0.17799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17799 | 16.97% | CZ 5A | 23.4144 | 14.6424 | 0.75739 | 19.454 | 0 | 7.4537 | 0 | 12.3314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 78.127 | 16.97%
CZ 5B | 0.22656 | 0.14154 | 0.0072786 | 0.080396 | 0 | 0.092983 | 0 | 0.15042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.6999 | 3.575% | CZ 5B | 7.6333 | 4.7689 | 0.24523 | 8.0396 | 0 | 3.1328 | 0 | 5.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 28.9118 | 3.575% | CZ 5B | 2.2365 | 1.3973 | 0.071852 | 0 | 0 | 0.9179 | 0 | 1.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.1156 | 3.575% | CZ 5B | 0 | 0 | 0 | 0.080396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080396 | 3.575% | CZ 5B | 23.4144 | 14.6282 | 0.75222 | 8.7873 | 0 | 9.6095 | 0 | 15.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 72.811 | 3.575%
CZ 5C | 0.22656 | 0.14114 | 0.0073286 | 0.10426 | 0 | 0.014132 | 0 | 0.087981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.58212 | 0.016% | CZ 5C | 7.6333 | 4.7554 | 0.24691 | 10.4264 | 0 | 0.47613 | 0 | 2.9642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 26.5264 | 0.016% | CZ 5C | 2.2365 | 1.3933 | 0.072346 | 0 | 0 | 0.13951 | 0 | 0.86852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 4.7173 | 0.016% | CZ 5C | 0 | 0 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10426 | 0.016% | CZ 5C | 23.4144 | 14.5868 | 0.75739 | 11.3961 | 0 | 1.4605 | 0 | 9.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 60.7813 | 0.016%
CZ 6A | 0.22656 | 0.14148 | 0.0074037 | 0.25136 | 0 | 0.093271 | 0 | 0.18305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.90385 | 1.571% | CZ 6A | 7.6333 | 4.7668 | 0.24944 | 25.1361 | 0 | 3.1425 | 0 | 6.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 47.1194 | 1.571% | CZ 6A | 2.2365 | 1.3967 | 0.073086 | 0 | 0 | 0.92074 | 0 | 1.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.4411 | 1.571% | CZ 6A | 0 | 0 | 0 | 0.25136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25136 | 1.571% | CZ 6A | 23.4144 | 14.6217 | 0.76514 | 27.4738 | 0 | 9.6392 | 0 | 18.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 94.9058 | 1.571%
CZ 6B | 0.22656 | 0.14146 | 0.0073911 | 0.12656 | 0 | 0.053501 | 0 | 0.17966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.73585 | 0.2327% | CZ 6B | 7.6333 | 4.7659 | 0.24902 | 12.6561 | 0 | 1.8026 | 0 | 6.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 33.1841 | 0.2327% | CZ 6B | 2.2365 | 1.3964 | 0.072963 | 0 | 0 | 0.52815 | 0 | 1.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.0147 | 0.2327% | CZ 6B | 0 | 0 | 0 | 0.12656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12656 | 0.2327% | CZ 6B | 23.4144 | 14.6191 | 0.76385 | 13.8331 | 0 | 5.5292 | 0 | 18.5676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 76.8009 | 0.2327%
CZ 7 | 0.22656 | 0.14106 | 0.0074412 | 0.29197 | 0 | 0.068972 | 0 | 0.21838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.9551 | 0.07923% | CZ 7 | 7.6333 | 4.7525 | 0.25071 | 29.197 | 0 | 2.3238 | 0 | 7.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 51.5389 | 0.07923% | CZ 7 | 2.2365 | 1.3925 | 0.073457 | 0 | 0 | 0.68086 | 0 | 2.1558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.5462 | 0.07923% | CZ 7 | 0 | 0 | 0 | 0.29197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29197 | 0.07923% | CZ 7 | 23.4144 | 14.5778 | 0.76902 | 31.9123 | 0 | 7.128 | 0 | 22.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 100.4442 | 0.07923%
CZ 8 | 0.22656 | 0.13802 | 0.0074662 | 0.33675 | 0 | 0.024662 | 0 | 0.22355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.95772 | 0.02367% | CZ 8 | 7.6333 | 4.6501 | 0.25155 | 33.6749 | 0 | 0.83091 | 0 | 7.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 54.5964 | 0.02367% | CZ 8 | 2.2365 | 1.3625 | 0.073704 | 0 | 0 | 0.24346 | 0 | 2.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.13 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.33675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33675 | 0.02367% | CZ 8 | 23.4144 | 14.2637 | 0.7716 | 36.8067 | 0 | 2.5487 | 0 | 23.1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 100.9816 | 0.02367%
US Weighted | 0.22656 | 0.14182 | 0.0070789 | 0.070328 | 0 | 0.19103 | 0 | 0.14532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071285 | 0.78285 | 100% | US Weighted | 7.6333 | 4.7783 | 0.2385 | 7.0328 | 0 | 6.436 | 0 | 4.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 31.0388 | 100% | US Weighted | 2.2365 | 1.4 | 0.06988 | 0 | 0 | 1.8858 | 0 | 1.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.0338 | 100% | US Weighted | 0 | 0 | 0 | 0.070328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070328 | 100% | US Weighted | 23.4144 | 14.6569 | 0.73158 | 7.6869 | 0 | 19.742 | 0 | 15.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073671 | 81.3232 | 100%
Building Type: | Strip Mall |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 22500 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 22500 | [17 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 28.66% | 67.4% | 8.432% | -10% | 0% | 47.58% | 0% | 44.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.87% | 3.475% | CZ 1A | 28.66% | 67.4% | 8.432% | -10% | 0% | 47.58% | 0% | 44.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.87% | 3.475% | CZ 1A | 28.66% | 67.4% | 8.432% | 0% | 0% | 47.58% | 0% | 44.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.87% | 3.475% | CZ 1A | 0% | 0% | 0% | -10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -10% | 3.475% | CZ 1A | 28.66% | 67.4% | 8.432% | -10% | 0% | 47.58% | 0% | 44.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.87% | 3.475%
CZ 1B | 28.66% | 67.42% | 8.277% | -41.3% | 0% | 38.9% | 0% | 44.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.07% | 0% | CZ 1B | 28.66% | 67.42% | 8.277% | -41.3% | 0% | 38.9% | 0% | 44.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.69% | 0% | CZ 1B | 28.66% | 67.42% | 8.277% | 0% | 0% | 38.9% | 0% | 44.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.27% | 0% | CZ 1B | 0% | 0% | 0% | -41.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -41.3% | 0% | CZ 1B | 28.66% | 67.42% | 8.277% | -41.3% | 0% | 38.9% | 0% | 44.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.06% | 0%
CZ 2A | 28.66% | 67.42% | 8.38% | 10.7% | 0% | 50.17% | 0% | 54.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.68% | 19.08% | CZ 2A | 28.66% | 67.42% | 8.38% | 10.7% | 0% | 50.17% | 0% | 54.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.21% | 19.08% | CZ 2A | 28.66% | 67.42% | 8.38% | 0% | 0% | 50.17% | 0% | 54.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.92% | 19.08% | CZ 2A | 0% | 0% | 0% | 10.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.7% | 19.08% | CZ 2A | 28.66% | 67.42% | 8.38% | 10.7% | 0% | 50.17% | 0% | 54.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.66% | 19.08%
CZ 2B | 28.66% | 67.41% | 8.274% | 53.09% | 0% | 45.76% | 0% | 31.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.34% | 4.471% | CZ 2B | 28.66% | 67.41% | 8.274% | 53.09% | 0% | 45.76% | 0% | 31.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.55% | 4.471% | CZ 2B | 28.66% | 67.41% | 8.274% | 0% | 0% | 45.76% | 0% | 31.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.24% | 4.471% | CZ 2B | 0% | 0% | 0% | 53.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 53.09% | 4.471% | CZ 2B | 28.66% | 67.41% | 8.274% | 53.09% | 0% | 45.76% | 0% | 31.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.35% | 4.471%
CZ 3A | 28.66% | 67.42% | 8.336% | 39.11% | 0% | 55.21% | 0% | 44.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.65% | 19.64% | CZ 3A | 28.66% | 67.42% | 8.336% | 39.11% | 0% | 55.21% | 0% | 44.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.79% | 19.64% | CZ 3A | 28.66% | 67.42% | 8.336% | 0% | 0% | 55.21% | 0% | 44.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.56% | 19.64% | CZ 3A | 0% | 0% | 0% | 39.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.11% | 19.64% | CZ 3A | 28.66% | 67.42% | 8.336% | 39.11% | 0% | 55.21% | 0% | 44.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.65% | 19.64%
CZ 3B | 28.66% | 67.41% | 8.198% | -6.994% | 0% | 47.69% | 0% | 40.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.59% | 11.03% | CZ 3B | 28.66% | 67.41% | 8.198% | -6.994% | 0% | 47.69% | 0% | 40.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.42% | 11.03% | CZ 3B | 28.66% | 67.41% | 8.198% | 0% | 0% | 47.69% | 0% | 40.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.2% | 11.03% | CZ 3B | 0% | 0% | 0% | -6.994% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -6.994% | 11.03% | CZ 3B | 28.66% | 67.41% | 8.198% | -6.994% | 0% | 47.69% | 0% | 40.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.55% | 11.03%
CZ 3C | 28.66% | 67.3% | 8.189% | 17.19% | 0% | 58.92% | 0% | 43.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.08% | 1.823% | CZ 3C | 28.66% | 67.3% | 8.189% | 17.19% | 0% | 58.92% | 0% | 43.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.8% | 1.823% | CZ 3C | 28.66% | 67.3% | 8.189% | 0% | 0% | 58.92% | 0% | 43.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.22% | 1.823% | CZ 3C | 0% | 0% | 0% | 17.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.19% | 1.823% | CZ 3C | 28.66% | 67.3% | 8.189% | 17.19% | 0% | 58.92% | 0% | 43.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.07% | 1.823%
CZ 4A | 28.66% | 67.19% | 8.361% | 46.19% | 0% | 52.32% | 0% | 40.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.52% | 15.73% | CZ 4A | 28.66% | 67.19% | 8.361% | 46.19% | 0% | 52.32% | 0% | 40.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 38.6% | 15.73% | CZ 4A | 28.66% | 67.19% | 8.361% | 0% | 0% | 52.32% | 0% | 40.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.95% | 15.73% | CZ 4A | 0% | 0% | 0% | 46.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 46.19% | 15.73% | CZ 4A | 28.66% | 67.19% | 8.361% | 46.19% | 0% | 52.32% | 0% | 40.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.6% | 15.73%
CZ 4B | 28.66% | 67.39% | 8.345% | 43.79% | 0% | 47.61% | 0% | 42.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.26% | 0.4211% | CZ 4B | 28.66% | 67.39% | 8.345% | 43.79% | 0% | 47.61% | 0% | 42.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.92% | 0.4211% | CZ 4B | 28.66% | 67.39% | 8.345% | 0% | 0% | 47.61% | 0% | 42.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.87% | 0.4211% | CZ 4B | 0% | 0% | 0% | 43.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.79% | 0.4211% | CZ 4B | 28.66% | 67.39% | 8.345% | 43.79% | 0% | 47.61% | 0% | 42.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.28% | 0.4211%
CZ 4C | 28.66% | 67.14% | 8.325% | 43.83% | 0% | 47.77% | 0% | 39.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.88% | 1.866% | CZ 4C | 28.66% | 67.14% | 8.325% | 43.83% | 0% | 47.77% | 0% | 39.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.72% | 1.866% | CZ 4C | 28.66% | 67.14% | 8.325% | 0% | 0% | 47.77% | 0% | 39.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.58% | 1.866% | CZ 4C | 0% | 0% | 0% | 43.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.83% | 1.866% | CZ 4C | 28.66% | 67.14% | 8.325% | 43.83% | 0% | 47.77% | 0% | 39.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.94% | 1.866%
CZ 5A | 28.66% | 67.32% | 8.251% | 41.67% | 0% | 51.76% | 0% | 41.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.39% | 16.97% | CZ 5A | 28.66% | 67.32% | 8.251% | 41.67% | 0% | 51.76% | 0% | 41.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.18% | 16.97% | CZ 5A | 28.66% | 67.32% | 8.251% | 0% | 0% | 51.76% | 0% | 41.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.79% | 16.97% | CZ 5A | 0% | 0% | 0% | 41.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.67% | 16.97% | CZ 5A | 28.66% | 67.32% | 8.251% | 41.67% | 0% | 51.76% | 0% | 41.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.46% | 16.97%
CZ 5B | 28.66% | 67.25% | 8.251% | 38.25% | 0% | 49.3% | 0% | 41.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.83% | 3.575% | CZ 5B | 28.66% | 67.25% | 8.251% | 38.25% | 0% | 49.3% | 0% | 41.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.42% | 3.575% | CZ 5B | 28.66% | 67.25% | 8.251% | 0% | 0% | 49.3% | 0% | 41.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.43% | 3.575% | CZ 5B | 0% | 0% | 0% | 38.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.25% | 3.575% | CZ 5B | 28.66% | 67.25% | 8.251% | 38.25% | 0% | 49.3% | 0% | 41.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.85% | 3.575%
CZ 5C | 28.66% | 67.17% | 8.259% | 42.18% | 0% | 41.61% | 0% | 36.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.82% | 0.016% | CZ 5C | 28.66% | 67.17% | 8.259% | 42.18% | 0% | 41.61% | 0% | 36.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.83% | 0.016% | CZ 5C | 28.66% | 67.17% | 8.259% | 0% | 0% | 41.61% | 0% | 36.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.3% | 0.016% | CZ 5C | 0% | 0% | 0% | 42.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.18% | 0.016% | CZ 5C | 28.66% | 67.17% | 8.259% | 42.18% | 0% | 41.61% | 0% | 36.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.89% | 0.016%
CZ 6A | 28.66% | 67.26% | 8.214% | 43.45% | 0% | 54.3% | 0% | 49.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 38.09% | 1.571% | CZ 6A | 28.66% | 67.26% | 8.214% | 43.45% | 0% | 54.3% | 0% | 49.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.83% | 1.571% | CZ 6A | 28.66% | 67.26% | 8.214% | 0% | 0% | 54.3% | 0% | 49.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.36% | 1.571% | CZ 6A | 0% | 0% | 0% | 43.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.45% | 1.571% | CZ 6A | 28.66% | 67.26% | 8.214% | 43.45% | 0% | 54.3% | 0% | 49.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 38.17% | 1.571%
CZ 6B | 28.66% | 67.29% | 8.231% | 36.12% | 0% | 45% | 0% | 47.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.06% | 0.2327% | CZ 6B | 28.66% | 67.29% | 8.231% | 36.12% | 0% | 45% | 0% | 47.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.32% | 0.2327% | CZ 6B | 28.66% | 67.29% | 8.231% | 0% | 0% | 45% | 0% | 47.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.85% | 0.2327% | CZ 6B | 0% | 0% | 0% | 36.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.12% | 0.2327% | CZ 6B | 28.66% | 67.29% | 8.231% | 36.12% | 0% | 45% | 0% | 47.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.07% | 0.2327%
CZ 7 | 28.66% | 67.14% | 8.123% | 42.42% | 0% | 54.92% | 0% | 53.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 38.54% | 0.07923% | CZ 7 | 28.66% | 67.14% | 8.123% | 42.42% | 0% | 54.92% | 0% | 53.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 39.91% | 0.07923% | CZ 7 | 28.66% | 67.14% | 8.123% | 0% | 0% | 54.92% | 0% | 53.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.05% | 0.07923% | CZ 7 | 0% | 0% | 0% | 42.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.42% | 0.07923% | CZ 7 | 28.66% | 67.14% | 8.123% | 42.42% | 0% | 54.92% | 0% | 53.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 38.6% | 0.07923%
CZ 8 | 28.66% | 66.06% | 7.975% | 37.13% | 0% | 49.21% | 0% | 50.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.11% | 0.02367% | CZ 8 | 28.66% | 66.06% | 7.975% | 37.13% | 0% | 49.21% | 0% | 50.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.52% | 0.02367% | CZ 8 | 28.66% | 66.06% | 7.975% | 0% | 0% | 49.21% | 0% | 50.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.59% | 0.02367% | CZ 8 | 0% | 0% | 0% | 37.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.13% | 0.02367% | CZ 8 | 28.66% | 66.06% | 7.975% | 37.13% | 0% | 49.21% | 0% | 50.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.13% | 0.02367%
US Weighted | 28.66% | 67.35% | 8.31% | 40.94% | 0% | 50.91% | 0% | 44.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.85% | 100% | US Weighted | 28.66% | 67.35% | 8.31% | 40.94% | 0% | 50.91% | 0% | 44.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.42% | 100% | US Weighted | 28.66% | 67.35% | 8.31% | 0% | 0% | 50.91% | 0% | 44.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.5% | 100% | US Weighted | 0% | 0% | 0% | 40.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.94% | 100% | US Weighted | 28.66% | 67.35% | 8.31% | 40.94% | 0% | 50.91% | 0% | 44.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.87% | 100%

## SchPri
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Primary School |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Primary School | [14 empty] | Prototype Floor Area: | 73959 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.13781 | 0.0097508 | 0.02443 | 0.064724 | 0 | 0.18036 | 0 | 0.090009 | 0.027835 | 0.0007941 | 0.041532 | 0 | 0.006592 | 0.10323 | 0 | 0.36051 | 1.0476 |  | STD2016 | 4.6431 | 0.32852 | 1.7912 | 6.4724 | 0 | 6.0768 | 0 | 3.0326 | 0.9378 | 0.026754 | 1.3993 | 0 | 0.2221 | 6.5458 | 0 | 12.1461 | 43.6224 |  | STD2016 | 1.3604 | 0.096257 | 0.097037 | 0 | 0 | 1.7805 | 0 | 0.88854 | 0.27477 | 0.007839 | 0.40999 | 0 | 0.065074 | 0.56229 | 0 | 3.5588 | 9.1015 |  | STD2016 | 0 | 0 | 0.0146 | 0.064724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12559 |  | STD2016 | 14.2424 | 1.0077 | 2.6116 | 7.0743 | 0 | 18.64 | 0 | 9.3022 | 2.8766 | 0.082067 | 4.2922 | 0 | 0.68126 | 10.9436 | 0 | 37.2571 | 109.0111
STD2013 | 0.26938 | 0.016881 | 0.024467 | 0.067829 | 0 | 0.20811 | 0 | 0.11507 | 0.028145 | 0.00067896 | 0.041539 | 0 | 0.0092017 | 0.10323 | 0 | 0.36051 | 1.245 |  | STD2013 | 9.0758 | 0.56876 | 1.7949 | 6.7829 | 0 | 7.0115 | 0 | 3.877 | 0.94824 | 0.022875 | 1.3995 | 0 | 0.31002 | 6.5458 | 0 | 12.1461 | 50.4833 |  | STD2013 | 2.6592 | 0.16665 | 0.097037 | 0 | 0 | 2.0544 | 0 | 1.1359 | 0.27783 | 0.0067025 | 0.41006 | 0 | 0.090836 | 0.56229 | 0 | 3.5588 | 11.0197 |  | STD2013 | 0 | 0 | 0.014638 | 0.067829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12873 |  | STD2013 | 27.8392 | 1.7446 | 2.6158 | 7.4137 | 0 | 21.5071 | 0 | 11.8923 | 2.9086 | 0.070169 | 4.293 | 0 | 0.95096 | 10.9436 | 0 | 37.2571 | 129.436
STD2010 | 0.307 | 0.016881 | 0.024471 | 0.079251 | 0 | 0.25997 | 0 | 0.15103 | 0.037928 | 0.00093886 | 0.051607 | 0 | 0.010319 | 0.10323 | 0 | 0.41273 | 1.4553 |  | STD2010 | 10.3434 | 0.56876 | 1.7953 | 7.9251 | 0 | 8.7587 | 0 | 5.0884 | 1.2779 | 0.031632 | 1.7387 | 0 | 0.34768 | 6.5458 | 0 | 13.9054 | 58.3269 |  | STD2010 | 3.0306 | 0.16665 | 0.09703 | 0 | 0 | 2.5663 | 0 | 1.4909 | 0.37441 | 0.0092681 | 0.50945 | 0 | 0.10187 | 0.56229 | 0 | 4.0743 | 12.9831 |  | STD2010 | 0 | 0 | 0.014642 | 0.079251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14016 |  | STD2010 | 31.7275 | 1.7446 | 2.6162 | 8.6622 | 0 | 26.8665 | 0 | 15.6084 | 3.9197 | 0.097027 | 5.3334 | 0 | 1.0665 | 10.9436 | 0 | 42.6538 | 151.2394
STD2007 | 0.46049 | 0.031672 | 0.025387 | 0.12482 | 0 | 0.36377 | 0 | 0.16863 | 0.042085 | 0.00078202 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.8082 |  | STD2007 | 15.5148 | 1.0671 | 1.8331 | 12.4821 | 0 | 12.2559 | 0 | 5.6814 | 1.4179 | 0.026348 | 1.7455 | 0 | 0.61547 | 6.5458 | 0 | 14.0576 | 73.2431 |  | STD2007 | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.591 | 0 | 1.6646 | 0.41545 | 0.0077199 | 0.51144 | 0 | 0.18033 | 0.56229 | 0 | 4.1189 | 16.0152 |  | STD2007 | 0 | 0 | 0.014746 | 0.12482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.18584 |  | STD2007 | 47.5904 | 3.2732 | 2.7114 | 13.643 | 0 | 37.594 | 0 | 17.4271 | 4.3493 | 0.080819 | 5.3543 | 0 | 1.8879 | 10.9436 | 0 | 43.1205 | 187.9754
STD2004 | 0.46049 | 0.031672 | 0.025395 | 0.15915 | 0 | 0.39183 | 0 | 0.19339 | 0.051266 | 0.00097001 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.9047 |  | STD2004 | 15.5148 | 1.0671 | 1.8339 | 15.9148 | 0 | 13.2015 | 0 | 6.5155 | 1.7272 | 0.032681 | 1.7455 | 0 | 0.61549 | 6.5458 | 0 | 14.0576 | 78.772 |  | STD2004 | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.8681 | 0 | 1.9091 | 0.50608 | 0.0095756 | 0.51144 | 0 | 0.18034 | 0.56229 | 0 | 4.1189 | 16.6292 |  | STD2004 | 0 | 0 | 0.014754 | 0.15915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22017 |  | STD2004 | 47.5904 | 3.2732 | 2.7123 | 17.3949 | 0 | 40.4946 | 0 | 19.9859 | 5.2982 | 0.10025 | 5.3542 | 0 | 1.888 | 10.9436 | 0 | 43.1205 | 198.156
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 7.9621e-06 | 0.034326 | 0 | 0.028067 | 0 | 0.02476 | 0.0091815 | 0.00018799 | -2.5035e-07 | 0 | 5.2032e-07 | 0 | 0 | 0 | 0.096531 |  | 2004-2007 | 0 | 0 | 0.00078214 | 3.4326 | 0 | 0.94564 | 0 | 0.83419 | 0.30934 | 0.0063337 | -8.4346e-06 | 0 | 1.753e-05 | 0 | 0 | 0 | 5.5289 |  | 2004-2007 | 0 | 0 | 2.0947e-06 | 0 | 0 | 0.27707 | 0 | 0.24442 | 0.090636 | 0.0018558 | -2.4714e-06 | 0 | 5.1364e-06 | 0 | 0 | 0 | 0.61399 |  | 2004-2007 | 0 | 0 | 7.7499e-06 | 0.034326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034334 |  | 2004-2007 | 0 | 0 | 0.00086899 | 3.7519 | 0 | 2.9007 | 0 | 2.5588 | 0.94887 | 0.019428 | -2.5873e-05 | 0 | 5.3773e-05 | 0 | 0 | 0 | 10.1806
2007-2010 | 0.15349 | 0.014791 | 0.00091557 | 0.04557 | 0 | 0.1038 | 0 | 0.017598 | 0.0041566 | -0.00015683 | 0.00020155 | 0 | 0.0079485 | 0 | 0 | 0.0045161 | 0.35283 |  | 2007-2010 | 5.1714 | 0.49833 | 0.037778 | 4.557 | 0 | 3.4972 | 0 | 0.59292 | 0.14004 | -0.005284 | 0.0067904 | 0 | 0.2678 | 0 | 0 | 0.15216 | 14.9162 |  | 2007-2010 | 1.5152 | 0.14601 | 0.0080064 | 0 | 0 | 1.0247 | 0 | 0.17372 | 0.041033 | -0.0015482 | 0.0019896 | 0 | 0.078464 | 0 | 0 | 0.044582 | 3.0322 |  | 2007-2010 | 0 | 0 | 0.00010453 | 0.04557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045674 |  | 2007-2010 | 15.8629 | 1.5286 | 0.095244 | 4.9808 | 0 | 10.7275 | 0 | 1.8187 | 0.42957 | -0.016208 | 0.020829 | 0 | 0.82144 | 0 | 0 | 0.46673 | 36.736
2010-2013 | 0.037624 | 0 | 3.588e-06 | 0.011423 | 0 | 0.051859 | 0 | 0.035958 | 0.0097836 | 0.00025989 | 0.010068 | 0 | 0.0011176 | 0 | 0 | 0.052219 | 0.21032 |  | 2010-2013 | 1.2676 | 0 | 0.00040985 | 1.1423 | 0 | 1.7472 | 0 | 1.2115 | 0.32963 | 0.0087562 | 0.33921 | 0 | 0.037655 | 0 | 0 | 1.7593 | 7.8436 |  | 2010-2013 | 0.37141 | 0 | -7.6004e-06 | 0 | 0 | 0.51193 | 0 | 0.35496 | 0.09658 | 0.0025656 | 0.099388 | 0 | 0.011033 | 0 | 0 | 0.51549 | 1.9634 |  | 2010-2013 | 0 | 0 | 4.3579e-06 | 0.011423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011427 |  | 2010-2013 | 3.8883 | 0 | 0.00039675 | 1.2485 | 0 | 5.3594 | 0 | 3.7161 | 1.0111 | 0.026859 | 1.0405 | 0 | 0.1155 | 0 | 0 | 5.3966 | 21.8034
2013-2016 | 0.13157 | 0.0071304 | 3.7801e-05 | 0.0031044 | 0 | 0.027742 | 0 | 0.025062 | 0.00030989 | -0.00011513 | 7.7716e-06 | 0 | 0.0026097 | 0 | 0 | 0 | 0.19745 |  | 2013-2016 | 4.4327 | 0.24024 | 0.0037801 | 0.31044 | 0 | 0.93467 | 0 | 0.84439 | 0.010441 | -0.003879 | 0.00026184 | 0 | 0.087924 | 0 | 0 | 0 | 6.8609 |  | 2013-2016 | 1.2988 | 0.070389 | 0 | 0 | 0 | 0.27386 | 0 | 0.24741 | 0.0030592 | -0.0011365 | 7.6719e-05 | 0 | 0.025762 | 0 | 0 | 0 | 1.9182 |  | 2013-2016 | 0 | 0 | 3.7801e-05 | 0.0031044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031422 |  | 2013-2016 | 13.5969 | 0.7369 | 0.0041316 | 0.33931 | 0 | 2.867 | 0 | 2.5901 | 0.032027 | -0.011898 | 0.00080317 | 0 | 0.2697 | 0 | 0 | 0 | 20.4249
2004-2016 | 0.32268 | 0.021921 | 0.00096492 | 0.094424 | 0 | 0.21147 | 0 | 0.10338 | 0.023432 | 0.00017592 | 0.010277 | 0 | 0.011676 | 0 | 0 | 0.056735 | 0.85713 |  | 2004-2016 | 10.8717 | 0.73857 | 0.04275 | 9.4424 | 0 | 7.1248 | 0 | 3.483 | 0.78945 | 0.005927 | 0.34625 | 0 | 0.39339 | 0 | 0 | 1.9115 | 35.1496 |  | 2004-2016 | 3.1854 | 0.2164 | 0.0080009 | 0 | 0 | 2.0876 | 0 | 1.0205 | 0.23131 | 0.0017366 | 0.10145 | 0 | 0.11526 | 0 | 0 | 0.56007 | 7.5277 |  | 2004-2016 | 0 | 0 | 0.00015443 | 0.094424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094578 |  | 2004-2016 | 33.348 | 2.2655 | 0.10064 | 10.3205 | 0 | 21.8546 | 0 | 10.6837 | 2.4216 | 0.01818 | 1.0621 | 0 | 1.2067 | 0 | 0 | 5.8634 | 89.1449
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.03135% | 21.57% |  | 7.163% |  | 12.8% | 17.91% | 19.38% | -0.0004832% |  | 0.002848% | 0% |  | 0% | 5.068% |  | 2004-2007 | 0% | 0% | 0.04265% | 21.57% |  | 7.163% |  | 12.8% | 17.91% | 19.38% | -0.0004832% |  | 0.002848% | 0% |  | 0% | 7.019% |  | 2004-2007 | 0% | 0% | 0.001994% |  |  | 7.163% |  | 12.8% | 17.91% | 19.38% | -0.0004832% |  | 0.002848% | 0% |  | 0% | 3.692% |  | 2004-2007 |  |  | 0.05253% | 21.57% | [9 empty] | 0% |  |  | 15.59% |  | 2004-2007 | 0% | 0% | 0.03204% | 21.57% |  | 7.163% |  | 12.8% | 17.91% | 19.38% | -0.0004832% |  | 0.002848% | 0% |  | 0% | 5.138%
2007-2010 | 33.33% | 46.7% | 3.607% | 36.51% |  | 28.54% |  | 10.44% | 9.877% | -20.05% | 0.389% |  | 43.51% | 0% |  | 1.082% | 19.51% |  | 2007-2010 | 33.33% | 46.7% | 2.061% | 36.51% |  | 28.54% |  | 10.44% | 9.877% | -20.05% | 0.389% |  | 43.51% | 0% |  | 1.082% | 20.37% |  | 2007-2010 | 33.33% | 46.7% | 7.623% |  |  | 28.54% |  | 10.44% | 9.877% | -20.05% | 0.389% |  | 43.51% | 0% |  | 1.082% | 18.93% |  | 2007-2010 |  |  | 0.7088% | 36.51% | [9 empty] | 0% |  |  | 24.58% |  | 2007-2010 | 33.33% | 46.7% | 3.513% | 36.51% |  | 28.54% |  | 10.44% | 9.877% | -20.05% | 0.389% |  | 43.51% | 0% |  | 1.082% | 19.54%
2010-2013 | 12.26% | 0% | 0.01466% | 14.41% |  | 19.95% |  | 23.81% | 25.8% | 27.68% | 19.51% |  | 10.83% | 0% |  | 12.65% | 14.45% |  | 2010-2013 | 12.26% | 0% | 0.02283% | 14.41% |  | 19.95% |  | 23.81% | 25.8% | 27.68% | 19.51% |  | 10.83% | 0% |  | 12.65% | 13.45% |  | 2010-2013 | 12.26% | 0% | -0.007833% |  |  | 19.95% |  | 23.81% | 25.8% | 27.68% | 19.51% |  | 10.83% | 0% |  | 12.65% | 15.12% |  | 2010-2013 |  |  | 0.02976% | 14.41% | [9 empty] | 0% |  |  | 8.153% |  | 2010-2013 | 12.26% | 0% | 0.01517% | 14.41% |  | 19.95% |  | 23.81% | 25.8% | 27.68% | 19.51% |  | 10.83% | 0% |  | 12.65% | 14.42%
2013-2016 | 48.84% | 42.24% | 0.1545% | 4.577% |  | 13.33% |  | 21.78% | 1.101% | -16.96% | 0.01871% |  | 28.36% | 0% |  | 0% | 15.86% |  | 2013-2016 | 48.84% | 42.24% | 0.2106% | 4.577% |  | 13.33% |  | 21.78% | 1.101% | -16.96% | 0.01871% |  | 28.36% | 0% |  | 0% | 13.59% |  | 2013-2016 | 48.84% | 42.24% | 0% |  |  | 13.33% |  | 21.78% | 1.101% | -16.96% | 0.01871% |  | 28.36% | 0% |  | 0% | 17.41% |  | 2013-2016 |  |  | 0.2582% | 4.577% | [9 empty] | 0% |  |  | 2.441% |  | 2013-2016 | 48.84% | 42.24% | 0.158% | 4.577% |  | 13.33% |  | 21.78% | 1.101% | -16.96% | 0.01871% |  | 28.36% | 0% |  | 0% | 15.78%
2004-2016 | 70.07% | 69.21% | 3.8% | 59.33% |  | 53.97% |  | 53.46% | 45.71% | 18.14% | 19.84% |  | 63.92% | 0% |  | 13.6% | 45% |  | 2004-2016 | 70.07% | 69.21% | 2.331% | 59.33% |  | 53.97% |  | 53.46% | 45.71% | 18.14% | 19.84% |  | 63.92% | 0% |  | 13.6% | 44.62% |  | 2004-2016 | 70.07% | 69.21% | 7.617% |  |  | 53.97% |  | 53.46% | 45.71% | 18.14% | 19.84% |  | 63.92% | 0% |  | 13.6% | 45.27% |  | 2004-2016 |  |  | 1.047% | 59.33% | [9 empty] | 0% |  |  | 42.96% |  | 2004-2016 | 70.07% | 69.21% | 3.711% | 59.33% |  | 53.97% |  | 53.46% | 45.71% | 18.14% | 19.84% |  | 63.92% | 0% |  | 13.6% | 44.99%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.13764 | 0.0097551 | 0.021268 | 0.0057567 | 0 | 0.34562 | 0 | 0.10314 | 0.03848 | 6.4679e-05 | 0.041688 | 0 | 0.0066011 | 0.10323 | 0 | 0.36051 | 1.1738 | 3.243% | CZ 1A | 4.6374 | 0.32867 | 1.4751 | 0.57567 | 0 | 11.6446 | 0 | 3.475 | 1.2965 | 0.0021792 | 1.4045 | 0 | 0.2224 | 6.5458 | 0 | 12.1461 | 43.7539 | 3.243% | CZ 1A | 1.3587 | 0.0963 | 0.097013 | 0 | 0 | 3.4119 | 0 | 1.0182 | 0.37987 | 0.00063849 | 0.41153 | 0 | 0.065164 | 0.56229 | 0 | 3.5588 | 10.9604 | 3.243% | CZ 1A | 0 | 0 | 0.01144 | 0.0057567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.063465 | 3.243% | CZ 1A | 14.2247 | 1.0082 | 2.2661 | 0.62921 | 0 | 35.7189 | 0 | 10.6592 | 3.9768 | 0.0066844 | 4.3083 | 0 | 0.6822 | 10.9436 | 0 | 37.2571 | 121.681 | 3.243%
CZ 1B | 0.13574 | 0.0097247 | 0.021661 | 0.02101 | 0 | 0.42292 | 0 | 0.09498 | 0.042156 | 0.00011794 | 0.041657 | 0 | 0.0065973 | 0.10323 | 0 | 0.36051 | 1.2603 | 0% | CZ 1B | 4.5733 | 0.32764 | 1.5145 | 2.101 | 0 | 14.2488 | 0 | 3.2 | 1.4203 | 0.0039737 | 1.4035 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 47.7072 | 0% | CZ 1B | 1.34 | 0.095999 | 0.097013 | 0 | 0 | 4.1749 | 0 | 0.93761 | 0.41615 | 0.0011643 | 0.41123 | 0 | 0.065126 | 0.56229 | 0 | 3.5588 | 11.6603 | 0% | CZ 1B | 0 | 0 | 0.011834 | 0.02101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.079111 | 0% | CZ 1B | 14.0281 | 1.005 | 2.3091 | 2.2964 | 0 | 43.7071 | 0 | 9.8158 | 4.3566 | 0.012189 | 4.3051 | 0 | 0.68181 | 10.9436 | 0 | 37.2571 | 130.718 | 0%
CZ 2A | 0.13668 | 0.0097361 | 0.022408 | 0.02609 | 0 | 0.29917 | 0 | 0.097612 | 0.035817 | 0.00016741 | 0.041661 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.1397 | 19.73% | CZ 2A | 4.6049 | 0.32803 | 1.5892 | 2.609 | 0 | 10.0796 | 0 | 3.2887 | 1.2067 | 0.0056402 | 1.4036 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 44.0294 | 19.73% | CZ 2A | 1.3492 | 0.096112 | 0.097013 | 0 | 0 | 2.9533 | 0 | 0.9636 | 0.35357 | 0.0016526 | 0.41126 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 10.4119 | 19.73% | CZ 2A | 0 | 0 | 0.012581 | 0.02609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.084938 | 19.73% | CZ 2A | 14.1253 | 1.0062 | 2.3907 | 2.8516 | 0 | 30.9184 | 0 | 10.0879 | 3.7016 | 0.017301 | 4.3055 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 118.2862 | 19.73%
CZ 2B | 0.13932 | 0.0097399 | 0.022576 | 0.029605 | 0 | 0.25065 | 0 | 0.096269 | 0.036464 | 0.00014458 | 0.041482 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.0966 | 3.29% | CZ 2B | 4.694 | 0.32815 | 1.606 | 2.9605 | 0 | 8.445 | 0 | 3.2435 | 1.2285 | 0.004871 | 1.3976 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 42.8221 | 3.29% | CZ 2B | 1.3753 | 0.096149 | 0.097013 | 0 | 0 | 2.4744 | 0 | 0.95034 | 0.35996 | 0.0014272 | 0.4095 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 9.9503 | 3.29% | CZ 2B | 0 | 0 | 0.012749 | 0.029605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.088621 | 3.29% | CZ 2B | 14.3985 | 1.0066 | 2.4091 | 3.2358 | 0 | 25.9043 | 0 | 9.9491 | 3.7684 | 0.014942 | 4.287 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 113.8556 | 3.29%
CZ 3A | 0.14032 | 0.0097666 | 0.024128 | 0.056038 | 0 | 0.18971 | 0 | 0.089702 | 0.034371 | 0.00051363 | 0.041547 | 0 | 0.0065935 | 0.10323 | 0 | 0.36051 | 1.0564 | 19.28% | CZ 3A | 4.7276 | 0.32905 | 1.7609 | 5.6038 | 0 | 6.3916 | 0 | 3.0222 | 1.158 | 0.017305 | 1.3998 | 0 | 0.22215 | 6.5458 | 0 | 12.1461 | 43.3244 | 19.28% | CZ 3A | 1.3852 | 0.096412 | 0.097051 | 0 | 0 | 1.8727 | 0 | 0.88551 | 0.3393 | 0.0050704 | 0.41014 | 0 | 0.065089 | 0.56229 | 0 | 3.5588 | 9.2776 | 19.28% | CZ 3A | 0 | 0 | 0.014297 | 0.056038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1166 | 19.28% | CZ 3A | 14.5015 | 1.0093 | 2.5787 | 6.125 | 0 | 19.6057 | 0 | 9.2704 | 3.5522 | 0.053082 | 4.2937 | 0 | 0.68141 | 10.9436 | 0 | 37.2571 | 109.8717 | 19.28%
CZ 3B | 0.14187 | 0.0097057 | 0.023704 | 0.058701 | 0 | 0.18811 | 0 | 0.088477 | 0 | 0.00070006 | 0.04149 | 0 | 0.0065973 | 0.10323 | 0 | 0.36051 | 1.0231 | 8.936% | CZ 3B | 4.7798 | 0.327 | 1.7188 | 5.8701 | 0 | 6.3377 | 0 | 2.981 | 0 | 0.023586 | 1.3979 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 42.35 | 8.936% | CZ 3B | 1.4005 | 0.095811 | 0.097013 | 0 | 0 | 1.857 | 0 | 0.87342 | 0 | 0.0069107 | 0.40957 | 0 | 0.065126 | 0.56229 | 0 | 3.5588 | 8.9264 | 8.936% | CZ 3B | 0 | 0 | 0.013877 | 0.058701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11885 | 8.936% | CZ 3B | 14.6616 | 1.003 | 2.5323 | 6.416 | 0 | 19.4405 | 0 | 9.1438 | 0 | 0.072348 | 4.2878 | 0 | 0.68181 | 10.9436 | 0 | 37.2571 | 106.4401 | 8.936%
CZ 3C | 0.14146 | 0.0097133 | 0.024022 | 0.049327 | 0 | 0.13067 | 0 | 0.087484 | 0 | 0.00029676 | 0.041516 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 0.95482 | 0.953% | CZ 3C | 4.7661 | 0.32726 | 1.7503 | 4.9327 | 0 | 4.4025 | 0 | 2.9475 | 0 | 0.0099985 | 1.3988 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 39.449 | 0.953% | CZ 3C | 1.3965 | 0.095886 | 0.097051 | 0 | 0 | 1.2899 | 0 | 0.86362 | 0 | 0.0029296 | 0.40984 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 8.3419 | 0.953% | CZ 3C | 0 | 0 | 0.014191 | 0.049327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10978 | 0.953% | CZ 3C | 14.6195 | 1.0038 | 2.5671 | 5.3914 | 0 | 13.5044 | 0 | 9.0412 | 0 | 0.030669 | 4.2906 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 99.3304 | 0.953%
CZ 4A | 0.13678 | 0.009759 | 0.02537 | 0.070282 | 0 | 0.13703 | 0 | 0.087804 | 0.03183 | 0.00091312 | 0.041501 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.0116 | 17.51% | CZ 4A | 4.6083 | 0.3288 | 1.8851 | 7.0282 | 0 | 4.6169 | 0 | 2.9583 | 1.0724 | 0.030765 | 1.3982 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 42.8409 | 17.51% | CZ 4A | 1.3502 | 0.096337 | 0.097051 | 0 | 0 | 1.3527 | 0 | 0.86677 | 0.31421 | 0.009014 | 0.40969 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 8.6822 | 17.51% | CZ 4A | 0 | 0 | 0.015539 | 0.070282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13209 | 17.51% | CZ 4A | 14.1355 | 1.0086 | 2.7144 | 7.6819 | 0 | 14.1618 | 0 | 9.0742 | 3.2895 | 0.094368 | 4.289 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 105.331 | 17.51%
CZ 4B | 0.13581 | 0.0097133 | 0.024992 | 0.086494 | 0 | 0.12845 | 0 | 0.096604 | 0 | 0.0010767 | 0.041467 | 0 | 0.0065973 | 0.10323 | 0 | 0.36051 | 0.99493 | 0.665% | CZ 4B | 4.5756 | 0.32726 | 1.8476 | 8.6494 | 0 | 4.3275 | 0 | 3.2548 | 0 | 0.036276 | 1.3971 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.3296 | 0.665% | CZ 4B | 1.3406 | 0.095886 | 0.097013 | 0 | 0 | 1.268 | 0 | 0.95364 | 0 | 0.010629 | 0.40935 | 0 | 0.065126 | 0.56229 | 0 | 3.5588 | 8.3614 | 0.665% | CZ 4B | 0 | 0 | 0.015165 | 0.086494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14793 | 0.665% | CZ 4B | 14.0352 | 1.0038 | 2.6731 | 9.4538 | 0 | 13.2744 | 0 | 9.9837 | 0 | 0.11128 | 4.2855 | 0 | 0.68181 | 10.9436 | 0 | 37.2571 | 103.7033 | 0.665%
CZ 4C | 0.1389 | 0.0098046 | 0.02557 | 0.13068 | 0 | 0.053436 | 0 | 0.075534 | 0 | 0.0018719 | 0.041444 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 0.94757 | 1.872% | CZ 4C | 4.6799 | 0.33033 | 1.9051 | 13.0679 | 0 | 1.8004 | 0 | 2.5449 | 0 | 0.063067 | 1.3963 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 44.7018 | 1.872% | CZ 4C | 1.3712 | 0.096788 | 0.097051 | 0 | 0 | 0.52751 | 0 | 0.74565 | 0 | 0.018479 | 0.40912 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 7.452 | 1.872% | CZ 4C | 0 | 0 | 0.015739 | 0.13068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19269 | 1.872% | CZ 4C | 14.3553 | 1.0133 | 2.7363 | 14.2832 | 0 | 5.5225 | 0 | 7.8062 | 0 | 0.19345 | 4.2831 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 99.075 | 1.872%
CZ 5A | 0.13593 | 0.009759 | 0.0264 | 0.096017 | 0 | 0.085723 | 0 | 0.08376 | 0.030304 | 0.0014534 | 0.041452 | 0 | 0.0065935 | 0.10323 | 0 | 0.36051 | 0.98113 | 16.48% | CZ 5A | 4.5798 | 0.3288 | 1.9881 | 9.6017 | 0 | 2.8881 | 0 | 2.822 | 1.021 | 0.048967 | 1.3966 | 0 | 0.22215 | 6.5458 | 0 | 12.1461 | 43.5892 | 16.48% | CZ 5A | 1.3419 | 0.096337 | 0.097051 | 0 | 0 | 0.84623 | 0 | 0.82685 | 0.29915 | 0.014347 | 0.4092 | 0 | 0.065089 | 0.56229 | 0 | 3.5588 | 8.1172 | 16.48% | CZ 5A | 0 | 0 | 0.016569 | 0.096017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15885 | 16.48% | CZ 5A | 14.0482 | 1.0086 | 2.827 | 10.4947 | 0 | 8.8592 | 0 | 8.6563 | 3.1318 | 0.1502 | 4.2839 | 0 | 0.68141 | 10.9436 | 0 | 37.2571 | 102.3419 | 16.48%
CZ 5B | 0.13613 | 0.0097475 | 0.026076 | 0.13311 | 0 | 0.093545 | 0 | 0.088789 | 0 | 0.0018947 | 0.041444 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.0011 | 4.56% | CZ 5B | 4.5866 | 0.32841 | 1.9557 | 13.3108 | 0 | 3.1517 | 0 | 2.9915 | 0 | 0.063836 | 1.3963 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 46.6987 | 4.56% | CZ 5B | 1.3439 | 0.096224 | 0.097051 | 0 | 0 | 0.92345 | 0 | 0.8765 | 0 | 0.018704 | 0.40912 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 7.9511 | 4.56% | CZ 5B | 0 | 0 | 0.016245 | 0.13311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19562 | 4.56% | CZ 5B | 14.069 | 1.0074 | 2.7916 | 14.5487 | 0 | 9.6676 | 0 | 9.1761 | 0 | 0.19581 | 4.2831 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 104.621 | 4.56%
CZ 5C | 0.13777 | 0.0098046 | 0.026121 | 0.099944 | 0 | 0.042635 | 0 | 0.077299 | 0.027877 | 0.0009816 | 0.041429 | 0 | 0.0065935 | 0.10323 | 0 | 0.36051 | 0.93419 | 0.02421% | CZ 5C | 4.6417 | 0.33033 | 1.9602 | 9.9944 | 0 | 1.4364 | 0 | 2.6043 | 0.93921 | 0.033072 | 1.3958 | 0 | 0.22215 | 6.5458 | 0 | 12.1461 | 42.2496 | 0.02421% | CZ 5C | 1.36 | 0.096788 | 0.097051 | 0 | 0 | 0.42088 | 0 | 0.76307 | 0.27519 | 0.0096901 | 0.40897 | 0 | 0.065089 | 0.56229 | 0 | 3.5588 | 7.6178 | 0.02421% | CZ 5C | 0 | 0 | 0.01629 | 0.099944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1625 | 0.02421% | CZ 5C | 14.2381 | 1.0133 | 2.7965 | 10.9239 | 0 | 4.4062 | 0 | 7.9886 | 2.881 | 0.10145 | 4.2815 | 0 | 0.68141 | 10.9436 | 0 | 37.2571 | 97.5126 | 0.02421%
CZ 6A | 0.13385 | 0.0097704 | 0.027236 | 0.13469 | 0 | 0.093941 | 0 | 0.084277 | 0.031837 | 0.002104 | 0.041444 | 0 | 0.0065859 | 0.10323 | 0 | 0.36051 | 1.0295 | 2.494% | CZ 6A | 4.5096 | 0.32918 | 2.0717 | 13.4693 | 0 | 3.165 | 0 | 2.8394 | 1.0727 | 0.070887 | 1.3963 | 0 | 0.22189 | 6.5458 | 0 | 12.1461 | 47.8379 | 2.494% | CZ 6A | 1.3213 | 0.09645 | 0.097051 | 0 | 0 | 0.92735 | 0 | 0.83195 | 0.31429 | 0.02077 | 0.40912 | 0 | 0.065013 | 0.56229 | 0 | 3.5588 | 8.2044 | 2.494% | CZ 6A | 0 | 0 | 0.017405 | 0.13469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19837 | 2.494% | CZ 6A | 13.8327 | 1.0097 | 2.9184 | 14.7219 | 0 | 9.7085 | 0 | 8.7097 | 3.2903 | 0.21744 | 4.2831 | 0 | 0.68063 | 10.9436 | 0 | 37.2571 | 107.5731 | 2.494%
CZ 6B | 0.13316 | 0.0097856 | 0.026998 | 0.10978 | 0 | 0.065539 | 0 | 0.083098 | 0.034455 | 0.0012289 | 0.041406 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 0.97577 | 0.6028% | CZ 6B | 4.4864 | 0.32969 | 2.0479 | 10.9776 | 0 | 2.2081 | 0 | 2.7997 | 1.1608 | 0.041404 | 1.395 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 44.3605 | 0.6028% | CZ 6B | 1.3145 | 0.0966 | 0.097051 | 0 | 0 | 0.64698 | 0 | 0.82031 | 0.34013 | 0.012131 | 0.40875 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 7.9226 | 0.6028% | CZ 6B | 0 | 0 | 0.017166 | 0.10978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.17321 | 0.6028% | CZ 6B | 13.7615 | 1.0113 | 2.8923 | 11.9985 | 0 | 6.7732 | 0 | 8.5878 | 3.5608 | 0.127 | 4.2792 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 101.8735 | 0.6028%
CZ 7 | 0.13238 | 0.0098084 | 0.028134 | 0.16293 | 0 | 0.076074 | 0 | 0.083756 | 0.032203 | 0.00038047 | 0.041402 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.0374 | 0.3042% | CZ 7 | 4.4602 | 0.33046 | 2.1615 | 16.293 | 0 | 2.5631 | 0 | 2.8219 | 1.085 | 0.012819 | 1.3949 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 50.0368 | 0.3042% | CZ 7 | 1.3068 | 0.096825 | 0.097051 | 0 | 0 | 0.75098 | 0 | 0.82681 | 0.31789 | 0.0037558 | 0.40871 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 7.995 | 0.3042% | CZ 7 | 0 | 0 | 0.018303 | 0.16293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.2275 | 0.3042% | CZ 7 | 13.6813 | 1.0137 | 3.0165 | 17.8083 | 0 | 7.862 | 0 | 8.6559 | 3.328 | 0.03932 | 4.2788 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 108.5656 | 0.3042%
CZ 8 | 0.14185 | 0.010128 | 0.029253 | 0.25924 | 0 | 0.037316 | 0 | 0.077684 | 0.035056 | 0.00095497 | 0.041303 | 0 | 0.0065897 | 0.10323 | 0 | 0.36051 | 1.1031 | 0.05063% | CZ 8 | 4.779 | 0.34123 | 2.2732 | 25.9236 | 0 | 1.2572 | 0 | 2.6173 | 1.1811 | 0.032175 | 1.3916 | 0 | 0.22202 | 6.5458 | 0 | 12.1461 | 58.7103 | 0.05063% | CZ 8 | 1.4003 | 0.09998 | 0.097088 | 0 | 0 | 0.36837 | 0 | 0.76687 | 0.34606 | 0.0094271 | 0.40773 | 0 | 0.065051 | 0.56229 | 0 | 3.5588 | 7.6819 | 0.05063% | CZ 8 | 0 | 0 | 0.019418 | 0.25924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.32492 | 0.05063% | CZ 8 | 14.6592 | 1.0467 | 3.1388 | 28.3345 | 0 | 3.8565 | 0 | 8.0283 | 3.6229 | 0.098693 | 4.2686 | 0 | 0.68102 | 10.9436 | 0 | 37.2571 | 115.9359 | 0.05063%
US Weighted | 0.13781 | 0.0097508 | 0.02443 | 0.064724 | 0 | 0.18036 | 0 | 0.090009 | 0.027835 | 0.0007941 | 0.041532 | 0 | 0.006592 | 0.10323 | 0 | 0.36051 | 1.0476 | 100% | US Weighted | 4.6431 | 0.32852 | 1.7912 | 6.4724 | 0 | 6.0768 | 0 | 3.0326 | 0.9378 | 0.026754 | 1.3993 | 0 | 0.2221 | 6.5458 | 0 | 12.1461 | 43.6224 | 100% | US Weighted | 1.3604 | 0.096257 | 0.097037 | 0 | 0 | 1.7805 | 0 | 0.88854 | 0.27477 | 0.007839 | 0.40999 | 0 | 0.065074 | 0.56229 | 0 | 3.5588 | 9.1015 | 100% | US Weighted | 0 | 0 | 0.0146 | 0.064724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12559 | 100% | US Weighted | 14.2424 | 1.0077 | 2.6116 | 7.0743 | 0 | 18.64 | 0 | 9.3022 | 2.8766 | 0.082067 | 4.2922 | 0 | 0.68126 | 10.9436 | 0 | 37.2571 | 109.0111 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.2705 | 0.016896 | 0.02131 | 0.0066397 | 0 | 0.41906 | 0 | 0.13392 | 0.041456 | 7.2289e-05 | 0.041707 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.4245 | 3.243% | CZ 1A | 9.1135 | 0.56927 | 1.4794 | 0.66397 | 0 | 14.1189 | 0 | 4.5119 | 1.3967 | 0.0024355 | 1.4052 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 52.263 | 3.243% | CZ 1A | 2.6702 | 0.1668 | 0.097013 | 0 | 0 | 4.1368 | 0 | 1.322 | 0.40924 | 0.00071361 | 0.41171 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 13.4264 | 3.243% | CZ 1A | 0 | 0 | 0.011483 | 0.0066397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.06439 | 3.243% | CZ 1A | 27.9548 | 1.7462 | 2.2707 | 0.72572 | 0 | 43.3084 | 0 | 13.8398 | 4.2843 | 0.0074708 | 4.3102 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 147.5991 | 3.243%
CZ 1B | 0.26903 | 0.01687 | 0.021702 | 0.024315 | 0 | 0.48526 | 0 | 0.1284 | 0.04265 | 0.00014077 | 0.041672 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.503 | 0% | CZ 1B | 9.064 | 0.56837 | 1.5186 | 2.4315 | 0 | 16.3493 | 0 | 4.3259 | 1.437 | 0.0047429 | 1.404 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 56.1052 | 0% | CZ 1B | 2.6558 | 0.16653 | 0.097013 | 0 | 0 | 4.7903 | 0 | 1.2675 | 0.42103 | 0.0013897 | 0.41138 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 14.0228 | 0% | CZ 1B | 0 | 0 | 0.011875 | 0.024315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.082457 | 0% | CZ 1B | 27.8031 | 1.7434 | 2.3135 | 2.6576 | 0 | 50.1501 | 0 | 13.2693 | 4.4078 | 0.014548 | 4.3067 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 155.8175 | 0%
CZ 2A | 0.27085 | 0.016862 | 0.022448 | 0.026523 | 0 | 0.33691 | 0 | 0.11399 | 0.033766 | 0.0001636 | 0.041672 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.3361 | 19.73% | CZ 2A | 9.1255 | 0.56812 | 1.5932 | 2.6523 | 0 | 11.3511 | 0 | 3.8406 | 1.1376 | 0.005512 | 1.404 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 50.6799 | 19.73% | CZ 2A | 2.6738 | 0.16646 | 0.097013 | 0 | 0 | 3.3259 | 0 | 1.1253 | 0.33333 | 0.001615 | 0.41138 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 12.3467 | 19.73% | CZ 2A | 0 | 0 | 0.012621 | 0.026523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.085411 | 19.73% | CZ 2A | 27.9918 | 1.7427 | 2.3951 | 2.8989 | 0 | 34.8185 | 0 | 11.7806 | 3.4896 | 0.016908 | 4.3067 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 138.5927 | 19.73%
CZ 2B | 0.27459 | 0.016877 | 0.022616 | 0.029669 | 0 | 0.2908 | 0 | 0.12304 | 0.034029 | 0.00014838 | 0.041497 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.3062 | 3.29% | CZ 2B | 9.2513 | 0.56863 | 1.61 | 2.9669 | 0 | 9.7976 | 0 | 4.1453 | 1.1465 | 0.0049992 | 1.3981 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 49.8912 | 3.29% | CZ 2B | 2.7106 | 0.16661 | 0.097013 | 0 | 0 | 2.8707 | 0 | 1.2146 | 0.33592 | 0.0014648 | 0.40965 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 12.0185 | 3.29% | CZ 2B | 0 | 0 | 0.012789 | 0.029669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.088725 | 3.29% | CZ 2B | 28.3775 | 1.7442 | 2.4134 | 3.2428 | 0 | 30.0533 | 0 | 12.7152 | 3.5168 | 0.015335 | 4.2886 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 135.5192 | 3.29%
CZ 3A | 0.27397 | 0.016874 | 0.02417 | 0.058373 | 0 | 0.22537 | 0 | 0.11812 | 0.032568 | 0.00047178 | 0.041558 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.2644 | 19.28% | CZ 3A | 9.2306 | 0.5685 | 1.7652 | 5.8373 | 0 | 7.5932 | 0 | 3.9796 | 1.0973 | 0.015895 | 1.4002 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 50.4898 | 19.28% | CZ 3A | 2.7046 | 0.16657 | 0.097051 | 0 | 0 | 2.2248 | 0 | 1.166 | 0.3215 | 0.0046572 | 0.41025 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 11.3074 | 19.28% | CZ 3A | 0 | 0 | 0.014339 | 0.058373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11898 | 19.28% | CZ 3A | 28.3142 | 1.7438 | 2.5833 | 6.3802 | 0 | 23.2915 | 0 | 12.2072 | 3.3658 | 0.048757 | 4.2949 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 131.3816 | 19.28%
CZ 3B | 0.27332 | 0.016874 | 0.023741 | 0.057983 | 0 | 0.19821 | 0 | 0.090384 | 0 | 0.00066582 | 0.041497 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.1756 | 8.936% | CZ 3B | 9.2087 | 0.5685 | 1.7225 | 5.7983 | 0 | 6.678 | 0 | 3.0452 | 0 | 0.022432 | 1.3981 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 47.4437 | 8.936% | CZ 3B | 2.6982 | 0.16657 | 0.097013 | 0 | 0 | 1.9566 | 0 | 0.89224 | 0 | 0.0065727 | 0.40965 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 10.4388 | 8.936% | CZ 3B | 0 | 0 | 0.013914 | 0.057983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11816 | 8.936% | CZ 3B | 28.247 | 1.7438 | 2.5364 | 6.3376 | 0 | 20.4841 | 0 | 9.3408 | 0 | 0.06881 | 4.2886 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 122.199 | 8.936%
CZ 3C | 0.27222 | 0.0169 | 0.024053 | 0.046674 | 0 | 0.1364 | 0 | 0.08745 | 0 | 0.00027394 | 0.041528 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.0984 | 0.953% | CZ 3C | 9.1717 | 0.5694 | 1.7534 | 4.6674 | 0 | 4.5954 | 0 | 2.9463 | 0 | 0.0092294 | 1.3991 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 44.1138 | 0.953% | CZ 3C | 2.6873 | 0.16683 | 0.097051 | 0 | 0 | 1.3465 | 0 | 0.86328 | 0 | 0.0027042 | 0.40995 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 9.7855 | 0.953% | CZ 3C | 0 | 0 | 0.014221 | 0.046674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10716 | 0.953% | CZ 3C | 28.1333 | 1.7466 | 2.5704 | 5.1014 | 0 | 14.0962 | 0 | 9.0377 | 0 | 0.02831 | 4.2918 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 114.1572 | 0.953%
CZ 4A | 0.2648 | 0.016908 | 0.025407 | 0.075486 | 0 | 0.15865 | 0 | 0.1223 | 0.033641 | 0.00080659 | 0.041501 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.2124 | 17.51% | CZ 4A | 8.9216 | 0.56966 | 1.8888 | 7.5486 | 0 | 5.3451 | 0 | 4.1205 | 1.1334 | 0.027175 | 1.3982 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 49.9549 | 17.51% | CZ 4A | 2.614 | 0.16691 | 0.097051 | 0 | 0 | 1.5661 | 0 | 1.2073 | 0.33209 | 0.0079624 | 0.40969 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 10.613 | 17.51% | CZ 4A | 0 | 0 | 0.015576 | 0.075486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13733 | 17.51% | CZ 4A | 27.3662 | 1.7474 | 2.7185 | 8.2506 | 0 | 16.3956 | 0 | 12.6394 | 3.4767 | 0.083358 | 4.289 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 126.1181 | 17.51%
CZ 4B | 0.26307 | 0.016866 | 0.02503 | 0.086147 | 0 | 0.13445 | 0 | 0.10037 | 0 | 0.0010006 | 0.041478 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.1414 | 0.665% | CZ 4B | 8.8634 | 0.56825 | 1.8514 | 8.6147 | 0 | 4.5298 | 0 | 3.3818 | 0 | 0.033713 | 1.3975 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 48.2424 | 0.665% | CZ 4B | 2.597 | 0.1665 | 0.097013 | 0 | 0 | 1.3272 | 0 | 0.99086 | 0 | 0.0098778 | 0.40946 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 9.8098 | 0.665% | CZ 4B | 0 | 0 | 0.015203 | 0.086147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14762 | 0.665% | CZ 4B | 27.1877 | 1.743 | 2.6773 | 9.4158 | 0 | 13.8948 | 0 | 10.3734 | 0 | 0.10341 | 4.2866 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 118.8336 | 0.665%
CZ 4C | 0.27063 | 0.016904 | 0.025601 | 0.12805 | 0 | 0.057637 | 0 | 0.076036 | 0 | 0.0017806 | 0.041452 | 0 | 0.0091959 | 0.10323 | 0 | 0.36051 | 1.091 | 1.872% | CZ 4C | 9.1178 | 0.56953 | 1.9082 | 12.8053 | 0 | 1.9419 | 0 | 2.5618 | 0 | 0.059991 | 1.3966 | 0 | 0.30982 | 6.5458 | 0 | 12.1461 | 49.3628 | 1.872% | CZ 4C | 2.6715 | 0.16687 | 0.097051 | 0 | 0 | 0.56897 | 0 | 0.7506 | 0 | 0.017577 | 0.4092 | 0 | 0.090779 | 0.56229 | 0 | 3.5588 | 8.8937 | 1.872% | CZ 4C | 0 | 0 | 0.015769 | 0.12805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19009 | 1.872% | CZ 4C | 27.9682 | 1.747 | 2.7396 | 13.9962 | 0 | 5.9566 | 0 | 7.8581 | 0 | 0.18402 | 4.2839 | 0 | 0.95036 | 10.9436 | 0 | 37.2571 | 113.8846 | 1.872%
CZ 5A | 0.26586 | 0.016877 | 0.026434 | 0.10361 | 0 | 0.10821 | 0 | 0.12234 | 0.033957 | 0.00097399 | 0.041459 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.1927 | 16.48% | CZ 5A | 8.9573 | 0.56863 | 1.9915 | 10.3613 | 0 | 3.6457 | 0 | 4.1217 | 1.1441 | 0.032815 | 1.3968 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 51.2217 | 16.48% | CZ 5A | 2.6245 | 0.16661 | 0.097051 | 0 | 0 | 1.0682 | 0 | 1.2077 | 0.33521 | 0.0096149 | 0.40927 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 10.13 | 16.48% | CZ 5A | 0 | 0 | 0.016602 | 0.10361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16648 | 16.48% | CZ 5A | 27.4759 | 1.7442 | 2.8307 | 11.3249 | 0 | 11.183 | 0 | 12.6429 | 3.5093 | 0.10066 | 4.2847 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 124.2477 | 16.48%
CZ 5B | 0.26425 | 0.016896 | 0.026108 | 0.13198 | 0 | 0.10254 | 0 | 0.094725 | 0 | 0.0017616 | 0.041444 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.1526 | 4.56% | CZ 5B | 8.9029 | 0.56927 | 1.9589 | 13.1981 | 0 | 3.4546 | 0 | 3.1914 | 0 | 0.05935 | 1.3963 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 51.7329 | 4.56% | CZ 5B | 2.6085 | 0.1668 | 0.097051 | 0 | 0 | 1.0122 | 0 | 0.93509 | 0 | 0.01739 | 0.40912 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 9.4581 | 4.56% | CZ 5B | 0 | 0 | 0.016277 | 0.13198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19453 | 4.56% | CZ 5B | 27.3088 | 1.7462 | 2.7951 | 14.4255 | 0 | 10.5967 | 0 | 9.7895 | 0 | 0.18205 | 4.2831 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 120.2788 | 4.56%
CZ 5C | 0.26853 | 0.016893 | 0.026153 | 0.10447 | 0 | 0.057203 | 0 | 0.12813 | 0.031172 | 0.00094356 | 0.041437 | 0 | 0.0092035 | 0.10323 | 0 | 0.36051 | 1.1479 | 0.02421% | CZ 5C | 9.0473 | 0.56914 | 1.9634 | 10.4466 | 0 | 1.9273 | 0 | 4.317 | 1.0502 | 0.03179 | 1.3961 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 49.7509 | 0.02421% | CZ 5C | 2.6509 | 0.16676 | 0.097051 | 0 | 0 | 0.56469 | 0 | 1.2649 | 0.30772 | 0.0093145 | 0.40905 | 0 | 0.090854 | 0.56229 | 0 | 3.5588 | 9.6823 | 0.02421% | CZ 5C | 0 | 0 | 0.016322 | 0.10447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16706 | 0.02421% | CZ 5C | 27.7519 | 1.7458 | 2.8 | 11.4182 | 0 | 5.9117 | 0 | 13.2421 | 3.2215 | 0.097513 | 4.2823 | 0 | 0.95115 | 10.9436 | 0 | 37.2571 | 119.623 | 0.02421%
CZ 6A | 0.26621 | 0.016889 | 0.02727 | 0.14979 | 0 | 0.1158 | 0 | 0.12837 | 0.03525 | 0.0017692 | 0.04144 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.2557 | 2.494% | CZ 6A | 8.9691 | 0.56902 | 2.0752 | 14.9786 | 0 | 3.9015 | 0 | 4.3248 | 1.1876 | 0.059606 | 1.3962 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 56.4635 | 2.494% | CZ 6A | 2.628 | 0.16672 | 0.097051 | 0 | 0 | 1.1431 | 0 | 1.2672 | 0.34798 | 0.017465 | 0.40909 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 10.2885 | 2.494% | CZ 6A | 0 | 0 | 0.017439 | 0.14979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.21349 | 2.494% | CZ 6A | 27.5121 | 1.7454 | 2.9221 | 16.3716 | 0 | 11.9674 | 0 | 13.2661 | 3.643 | 0.18284 | 4.2827 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 131.0447 | 2.494%
CZ 6B | 0.26646 | 0.01687 | 0.027032 | 0.12473 | 0 | 0.086385 | 0 | 0.13526 | 0.039043 | 0.0018757 | 0.041414 | 0 | 0.0091959 | 0.10323 | 0 | 0.36051 | 1.212 | 0.6028% | CZ 6B | 8.9773 | 0.56837 | 2.0513 | 12.4731 | 0 | 2.9105 | 0 | 4.5572 | 1.3154 | 0.063195 | 1.3953 | 0 | 0.30982 | 6.5458 | 0 | 12.1461 | 53.3135 | 0.6028% | CZ 6B | 2.6304 | 0.16653 | 0.097051 | 0 | 0 | 0.85276 | 0 | 1.3353 | 0.38542 | 0.018516 | 0.40882 | 0 | 0.090779 | 0.56229 | 0 | 3.5588 | 10.1066 | 0.6028% | CZ 6B | 0 | 0 | 0.017201 | 0.12473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1882 | 0.6028% | CZ 6B | 27.5373 | 1.7434 | 2.8961 | 13.6331 | 0 | 8.9276 | 0 | 13.979 | 4.035 | 0.19385 | 4.28 | 0 | 0.95036 | 10.9436 | 0 | 37.2571 | 126.3764 | 0.6028%
CZ 7 | 0.25758 | 0.016896 | 0.028175 | 0.18718 | 0 | 0.095661 | 0 | 0.13078 | 0.036099 | 0.0021763 | 0.041399 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.2689 | 0.3042% | CZ 7 | 8.6783 | 0.56927 | 2.1656 | 18.7184 | 0 | 3.223 | 0 | 4.4061 | 1.2162 | 0.073322 | 1.3948 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 59.4468 | 0.3042% | CZ 7 | 2.5427 | 0.1668 | 0.097051 | 0 | 0 | 0.94433 | 0 | 1.291 | 0.35635 | 0.021483 | 0.40867 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 10.0403 | 0.3042% | CZ 7 | 0 | 0 | 0.018344 | 0.18718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.2518 | 0.3042% | CZ 7 | 26.6199 | 1.7462 | 3.021 | 20.4592 | 0 | 9.8862 | 0 | 13.5154 | 3.7307 | 0.22491 | 4.2784 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 132.6334 | 0.3042%
CZ 8 | 0.27128 | 0.017003 | 0.02929 | 0.31021 | 0 | 0.048331 | 0 | 0.13645 | 0.037849 | 0.0040177 | 0.0413 | 0 | 0.0091997 | 0.10323 | 0 | 0.36051 | 1.3687 | 0.05063% | CZ 8 | 9.1399 | 0.57286 | 2.2769 | 31.0205 | 0 | 1.6283 | 0 | 4.5971 | 1.2752 | 0.13536 | 1.3915 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 71.0395 | 0.05063% | CZ 8 | 2.678 | 0.16785 | 0.097088 | 0 | 0 | 0.4771 | 0 | 1.347 | 0.37363 | 0.039662 | 0.4077 | 0 | 0.090816 | 0.56229 | 0 | 3.5588 | 9.7999 | 0.05063% | CZ 8 | 0 | 0 | 0.019455 | 0.31021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.37593 | 0.05063% | CZ 8 | 28.0358 | 1.7572 | 3.1429 | 33.9055 | 0 | 4.9948 | 0 | 14.1013 | 3.9115 | 0.41522 | 4.2682 | 0 | 0.95075 | 10.9436 | 0 | 37.2571 | 143.6838 | 0.05063%
US Weighted | 0.26938 | 0.016881 | 0.024467 | 0.067829 | 0 | 0.20811 | 0 | 0.11507 | 0.028145 | 0.00067896 | 0.041539 | 0 | 0.0092017 | 0.10323 | 0 | 0.36051 | 1.245 | 100% | US Weighted | 9.0758 | 0.56876 | 1.7949 | 6.7829 | 0 | 7.0115 | 0 | 3.877 | 0.94824 | 0.022875 | 1.3995 | 0 | 0.31002 | 6.5458 | 0 | 12.1461 | 50.4833 | 100% | US Weighted | 2.6592 | 0.16665 | 0.097037 | 0 | 0 | 2.0544 | 0 | 1.1359 | 0.27783 | 0.0067025 | 0.41006 | 0 | 0.090836 | 0.56229 | 0 | 3.5588 | 11.0197 | 100% | US Weighted | 0 | 0 | 0.014638 | 0.067829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12873 | 100% | US Weighted | 27.8392 | 1.7446 | 2.6158 | 7.4137 | 0 | 21.5071 | 0 | 11.8923 | 2.9086 | 0.070169 | 4.293 | 0 | 0.95096 | 10.9436 | 0 | 37.2571 | 129.436 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.31245 | 0.016896 | 0.021313 | 0.011303 | 0 | 0.56971 | 0 | 0.1909 | 0.05887 | 0.00012555 | 0.051793 | 0 | 0.010326 | 0.10323 | 0 | 0.41273 | 1.7596 | 3.243% | CZ 1A | 10.5268 | 0.56927 | 1.4796 | 1.1303 | 0 | 19.1946 | 0 | 6.4317 | 1.9834 | 0.0042301 | 1.745 | 0 | 0.3479 | 6.5458 | 0 | 13.9054 | 63.8642 | 3.243% | CZ 1A | 3.0844 | 0.1668 | 0.097013 | 0 | 0 | 5.624 | 0 | 1.8845 | 0.58114 | 0.0012394 | 0.51128 | 0 | 0.10193 | 0.56229 | 0 | 4.0743 | 16.6889 | 3.243% | CZ 1A | 0 | 0 | 0.011485 | 0.011303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.069056 | 3.243% | CZ 1A | 32.2902 | 1.7462 | 2.271 | 1.2354 | 0 | 58.8779 | 0 | 19.7287 | 6.084 | 0.012976 | 5.3526 | 0 | 1.0671 | 10.9436 | 0 | 42.6538 | 182.2635 | 3.243%
CZ 1B | 0.31126 | 0.01687 | 0.021706 | 0.027629 | 0 | 0.55327 | 0 | 0.13933 | 0.044606 | 0.00014838 | 0.051766 | 0 | 0.010322 | 0.10323 | 0 | 0.41273 | 1.6929 | 0% | CZ 1B | 10.487 | 0.56837 | 1.519 | 2.7629 | 0 | 18.6405 | 0 | 4.6942 | 1.5028 | 0.0049992 | 1.7441 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 62.7228 | 0% | CZ 1B | 3.0727 | 0.16653 | 0.097013 | 0 | 0 | 5.4617 | 0 | 1.3754 | 0.44033 | 0.0014648 | 0.51102 | 0 | 0.1019 | 0.56229 | 0 | 4.0743 | 15.8646 | 0% | CZ 1B | 0 | 0 | 0.011879 | 0.027629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.085775 | 0% | CZ 1B | 32.1679 | 1.7434 | 2.314 | 3.0198 | 0 | 57.1781 | 0 | 14.3989 | 4.6099 | 0.015335 | 5.3499 | 0 | 1.0667 | 10.9436 | 0 | 42.6538 | 175.4614 | 0%
CZ 2A | 0.31326 | 0.016862 | 0.022447 | 0.036032 | 0 | 0.42825 | 0 | 0.14413 | 0.039584 | 0.00025491 | 0.051751 | 0 | 0.010322 | 0.10323 | 0 | 0.41273 | 1.5788 | 19.73% | CZ 2A | 10.5542 | 0.56812 | 1.593 | 3.6032 | 0 | 14.4284 | 0 | 4.8561 | 1.3336 | 0.0085884 | 1.7436 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 59.4878 | 19.73% | CZ 2A | 3.0924 | 0.16646 | 0.097013 | 0 | 0 | 4.2275 | 0 | 1.4228 | 0.39076 | 0.0025164 | 0.51087 | 0 | 0.1019 | 0.56229 | 0 | 4.0743 | 14.6488 | 19.73% | CZ 2A | 0 | 0 | 0.012619 | 0.036032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.094919 | 19.73% | CZ 2A | 32.374 | 1.7427 | 2.3949 | 3.9383 | 0 | 44.258 | 0 | 14.8955 | 4.0908 | 0.026344 | 5.3483 | 0 | 1.0667 | 10.9436 | 0 | 42.6538 | 163.733 | 19.73%
CZ 2B | 0.31737 | 0.016877 | 0.022616 | 0.036793 | 0 | 0.33456 | 0 | 0.14287 | 0.034075 | 0.00020545 | 0.051568 | 0 | 0.010326 | 0.10323 | 0 | 0.41273 | 1.4832 | 3.29% | CZ 2B | 10.6928 | 0.56863 | 1.61 | 3.6793 | 0 | 11.2717 | 0 | 4.8136 | 1.148 | 0.006922 | 1.7374 | 0 | 0.3479 | 6.5458 | 0 | 13.9054 | 56.3276 | 3.29% | CZ 2B | 3.133 | 0.16661 | 0.097013 | 0 | 0 | 3.3026 | 0 | 1.4104 | 0.33637 | 0.0020282 | 0.50907 | 0 | 0.10193 | 0.56229 | 0 | 4.0743 | 13.6956 | 3.29% | CZ 2B | 0 | 0 | 0.012789 | 0.036793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.095849 | 3.29% | CZ 2B | 32.7994 | 1.7442 | 2.4134 | 4.0215 | 0 | 34.5751 | 0 | 14.7654 | 3.5215 | 0.021233 | 5.3294 | 0 | 1.0671 | 10.9436 | 0 | 42.6538 | 153.8557 | 3.29%
CZ 3A | 0.30722 | 0.016874 | 0.024169 | 0.069617 | 0 | 0.27403 | 0 | 0.14868 | 0.03619 | 0.00063918 | 0.051622 | 0 | 0.010322 | 0.10323 | 0 | 0.41273 | 1.4553 | 19.28% | CZ 3A | 10.3508 | 0.5685 | 1.7653 | 6.9617 | 0 | 9.2324 | 0 | 5.0092 | 1.2193 | 0.021535 | 1.7392 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 57.6671 | 19.28% | CZ 3A | 3.0328 | 0.16657 | 0.097013 | 0 | 0 | 2.7051 | 0 | 1.4677 | 0.35725 | 0.0063098 | 0.50959 | 0 | 0.1019 | 0.56229 | 0 | 4.0743 | 13.0808 | 19.28% | CZ 3A | 0 | 0 | 0.014342 | 0.069617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13023 | 19.28% | CZ 3A | 31.7504 | 1.7438 | 2.5832 | 7.6092 | 0 | 28.3197 | 0 | 15.3654 | 3.7401 | 0.066057 | 5.3349 | 0 | 1.0667 | 10.9436 | 0 | 42.6538 | 151.1769 | 19.28%
CZ 3B | 0.30791 | 0.016874 | 0.023744 | 0.05168 | 0 | 0.23843 | 0 | 0.14587 | 0.034744 | 0.0004109 | 0.051568 | 0 | 0.010318 | 0.10323 | 0 | 0.41273 | 1.3975 | 8.936% | CZ 3B | 10.3739 | 0.5685 | 1.7227 | 5.168 | 0 | 8.033 | 0 | 4.9145 | 1.1706 | 0.013844 | 1.7374 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 54.5014 | 8.936% | CZ 3B | 3.0396 | 0.16657 | 0.097013 | 0 | 0 | 2.3537 | 0 | 1.4399 | 0.34298 | 0.0040563 | 0.50907 | 0 | 0.10186 | 0.56229 | 0 | 4.0743 | 12.6913 | 8.936% | CZ 3B | 0 | 0 | 0.013916 | 0.05168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11186 | 8.936% | CZ 3B | 31.8211 | 1.7438 | 2.5367 | 5.6486 | 0 | 24.6406 | 0 | 15.0748 | 3.5907 | 0.042465 | 5.3294 | 0 | 1.0664 | 10.9436 | 0 | 42.6538 | 145.0919 | 8.936%
CZ 3C | 0.30674 | 0.0169 | 0.02405 | 0.046862 | 0 | 0.20835 | 0 | 0.15297 | 0.030578 | 0.00019023 | 0.051595 | 0 | 0.010326 | 0.10323 | 0 | 0.41273 | 1.3645 | 0.953% | CZ 3C | 10.3347 | 0.5694 | 1.7534 | 4.6862 | 0 | 7.0198 | 0 | 5.1537 | 1.0302 | 0.0064093 | 1.7383 | 0 | 0.3479 | 6.5458 | 0 | 13.9054 | 53.0913 | 0.953% | CZ 3C | 3.0281 | 0.16683 | 0.097013 | 0 | 0 | 2.0568 | 0 | 1.51 | 0.30186 | 0.0018779 | 0.50933 | 0 | 0.10193 | 0.56229 | 0 | 4.0743 | 12.4103 | 0.953% | CZ 3C | 0 | 0 | 0.014223 | 0.046862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10735 | 0.953% | CZ 3C | 31.7008 | 1.7466 | 2.5702 | 5.122 | 0 | 21.5327 | 0 | 15.8085 | 3.1601 | 0.01966 | 5.3322 | 0 | 1.0671 | 10.9436 | 0 | 42.6538 | 141.6574 | 0.953%
CZ 4A | 0.30235 | 0.016908 | 0.025415 | 0.095643 | 0 | 0.19412 | 0 | 0.15473 | 0.038279 | 0.0012061 | 0.051568 | 0 | 0.010318 | 0.10323 | 0 | 0.41273 | 1.4065 | 17.51% | CZ 4A | 10.1866 | 0.56966 | 1.8896 | 9.5643 | 0 | 6.5402 | 0 | 5.2132 | 1.2897 | 0.040635 | 1.7374 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 57.8301 | 17.51% | CZ 4A | 2.9847 | 0.16691 | 0.097051 | 0 | 0 | 1.9163 | 0 | 1.5275 | 0.37787 | 0.011906 | 0.50907 | 0 | 0.10186 | 0.56229 | 0 | 4.0743 | 12.3297 | 17.51% | CZ 4A | 0 | 0 | 0.015584 | 0.095643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15749 | 17.51% | CZ 4A | 31.2467 | 1.7474 | 2.7193 | 10.4538 | 0 | 20.0614 | 0 | 15.991 | 3.956 | 0.12464 | 5.3294 | 0 | 1.0664 | 10.9436 | 0 | 42.6538 | 146.2933 | 17.51%
CZ 4B | 0.30242 | 0.016866 | 0.025038 | 0.074376 | 0 | 0.18704 | 0 | 0.15855 | 0.032598 | 0.00072289 | 0.051542 | 0 | 0.010318 | 0.10323 | 0 | 0.41273 | 1.3754 | 0.665% | CZ 4B | 10.1892 | 0.56825 | 1.8522 | 7.4376 | 0 | 6.3019 | 0 | 5.3417 | 1.0983 | 0.024355 | 1.7365 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 55.3489 | 0.665% | CZ 4B | 2.9854 | 0.1665 | 0.097013 | 0 | 0 | 1.8464 | 0 | 1.5651 | 0.3218 | 0.0071361 | 0.5088 | 0 | 0.10186 | 0.56229 | 0 | 4.0743 | 12.2367 | 0.665% | CZ 4B | 0 | 0 | 0.015211 | 0.074376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13585 | 0.665% | CZ 4B | 31.2545 | 1.743 | 2.6782 | 8.1293 | 0 | 19.3304 | 0 | 16.3854 | 3.3689 | 0.074708 | 5.3267 | 0 | 1.0664 | 10.9436 | 0 | 42.6538 | 142.9548 | 0.665%
CZ 4C | 0.30568 | 0.016904 | 0.025608 | 0.10582 | 0 | 0.10254 | 0 | 0.15692 | 0.034718 | 0.0010387 | 0.051511 | 0 | 0.010311 | 0.10323 | 0 | 0.41273 | 1.327 | 1.872% | CZ 4C | 10.2988 | 0.56953 | 1.9089 | 10.582 | 0 | 3.4546 | 0 | 5.2868 | 1.1697 | 0.034995 | 1.7355 | 0 | 0.34738 | 6.5458 | 0 | 13.9054 | 55.8394 | 1.872% | CZ 4C | 3.0176 | 0.16687 | 0.097051 | 0 | 0 | 1.0122 | 0 | 1.549 | 0.34272 | 0.010253 | 0.5085 | 0 | 0.10178 | 0.56229 | 0 | 4.0743 | 11.4425 | 1.872% | CZ 4C | 0 | 0 | 0.015777 | 0.10582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16786 | 1.872% | CZ 4C | 31.5907 | 1.747 | 2.7405 | 11.5661 | 0 | 10.5967 | 0 | 16.2167 | 3.5879 | 0.10734 | 5.3235 | 0 | 1.0656 | 10.9436 | 0 | 42.6538 | 138.1394 | 1.872%
CZ 5A | 0.30284 | 0.016877 | 0.026443 | 0.12936 | 0 | 0.13266 | 0 | 0.15238 | 0.038378 | 0.0019252 | 0.051519 | 0 | 0.010314 | 0.10323 | 0 | 0.41273 | 1.3786 | 16.48% | CZ 5A | 10.2032 | 0.56863 | 1.9924 | 12.9359 | 0 | 4.4697 | 0 | 5.1338 | 1.293 | 0.064862 | 1.7358 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 59.196 | 16.48% | CZ 5A | 2.9895 | 0.16661 | 0.097051 | 0 | 0 | 1.3096 | 0 | 1.5042 | 0.37885 | 0.019005 | 0.50858 | 0 | 0.10182 | 0.56229 | 0 | 4.0743 | 11.7119 | 16.48% | CZ 5A | 0 | 0 | 0.016611 | 0.12936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19224 | 16.48% | CZ 5A | 31.2974 | 1.7442 | 2.8316 | 14.1389 | 0 | 13.7104 | 0 | 15.7476 | 3.9662 | 0.19896 | 5.3243 | 0 | 1.066 | 10.9436 | 0 | 42.6538 | 143.623 | 16.48%
CZ 5B | 0.30278 | 0.016896 | 0.026117 | 0.10785 | 0 | 0.14026 | 0 | 0.15085 | 0.032446 | 0.0015257 | 0.051507 | 0 | 0.010314 | 0.10323 | 0 | 0.41273 | 1.3565 | 4.56% | CZ 5B | 10.2013 | 0.56927 | 1.9598 | 10.7855 | 0 | 4.7254 | 0 | 5.0824 | 1.0932 | 0.051402 | 1.7354 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 57.0024 | 4.56% | CZ 5B | 2.989 | 0.1668 | 0.097051 | 0 | 0 | 1.3846 | 0 | 1.4892 | 0.3203 | 0.015061 | 0.50846 | 0 | 0.10182 | 0.56229 | 0 | 4.0743 | 11.7087 | 4.56% | CZ 5B | 0 | 0 | 0.016286 | 0.10785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.17041 | 4.56% | CZ 5B | 31.2915 | 1.7462 | 2.7961 | 11.7885 | 0 | 14.4949 | 0 | 15.5899 | 3.3532 | 0.15767 | 5.3231 | 0 | 1.066 | 10.9436 | 0 | 42.6538 | 141.2044 | 4.56%
CZ 5C | 0.30444 | 0.016893 | 0.026157 | 0.12197 | 0 | 0.064748 | 0 | 0.16055 | 0.033759 | 0.0012441 | 0.051492 | 0 | 0.010322 | 0.10323 | 0 | 0.41273 | 1.3075 | 0.02421% | CZ 5C | 10.2571 | 0.56914 | 1.9638 | 12.1974 | 0 | 2.1815 | 0 | 5.4092 | 1.1374 | 0.041917 | 1.7349 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 56.2913 | 0.02421% | CZ 5C | 3.0053 | 0.16676 | 0.097051 | 0 | 0 | 0.63917 | 0 | 1.5849 | 0.33326 | 0.012282 | 0.50831 | 0 | 0.1019 | 0.56229 | 0 | 4.0743 | 11.0855 | 0.02421% | CZ 5C | 0 | 0 | 0.016326 | 0.12197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.18457 | 0.02421% | CZ 5C | 31.4629 | 1.7458 | 2.8004 | 13.3317 | 0 | 6.6914 | 0 | 16.5922 | 3.4888 | 0.12858 | 5.3215 | 0 | 1.0667 | 10.9436 | 0 | 42.6538 | 136.2276 | 0.02421%
CZ 6A | 0.30318 | 0.016889 | 0.027281 | 0.18799 | 0 | 0.13822 | 0 | 0.15915 | 0.039546 | 0.0026899 | 0.051504 | 0 | 0.010318 | 0.10323 | 0 | 0.41273 | 1.4527 | 2.494% | CZ 6A | 10.2147 | 0.56902 | 2.0762 | 18.7992 | 0 | 4.657 | 0 | 5.362 | 1.3324 | 0.090627 | 1.7352 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 65.6352 | 2.494% | CZ 6A | 2.9929 | 0.16672 | 0.097051 | 0 | 0 | 1.3645 | 0 | 1.5711 | 0.39038 | 0.026554 | 0.50843 | 0 | 0.10186 | 0.56229 | 0 | 4.0743 | 11.856 | 2.494% | CZ 6A | 0 | 0 | 0.01745 | 0.18799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.25171 | 2.494% | CZ 6A | 31.3328 | 1.7454 | 2.9233 | 20.5476 | 0 | 14.2849 | 0 | 16.4475 | 4.0869 | 0.27799 | 5.3227 | 0 | 1.0664 | 10.9436 | 0 | 42.6538 | 151.6327 | 2.494%
CZ 6B | 0.30387 | 0.01687 | 0.027041 | 0.16402 | 0 | 0.10113 | 0 | 0.14766 | 0.033884 | 0.0021725 | 0.051473 | 0 | 0.010314 | 0.10323 | 0 | 0.41273 | 1.3744 | 0.6028% | CZ 6B | 10.2378 | 0.56837 | 2.0522 | 16.4016 | 0 | 3.4072 | 0 | 4.975 | 1.1416 | 0.073194 | 1.7342 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 61.3899 | 0.6028% | CZ 6B | 2.9997 | 0.16653 | 0.097051 | 0 | 0 | 0.9983 | 0 | 1.4577 | 0.33449 | 0.021446 | 0.50813 | 0 | 0.10182 | 0.56229 | 0 | 4.0743 | 11.3217 | 0.6028% | CZ 6B | 0 | 0 | 0.01721 | 0.16402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22749 | 0.6028% | CZ 6B | 31.4036 | 1.7434 | 2.8971 | 17.9269 | 0 | 10.4512 | 0 | 15.2604 | 3.5018 | 0.22452 | 5.3196 | 0 | 1.066 | 10.9436 | 0 | 42.6538 | 143.3919 | 0.6028%
CZ 7 | 0.30254 | 0.016896 | 0.028188 | 0.2351 | 0 | 0.11006 | 0 | 0.15749 | 0.039576 | 0.003447 | 0.051466 | 0 | 0.010322 | 0.10323 | 0 | 0.41273 | 1.471 | 0.3042% | CZ 7 | 10.1931 | 0.56927 | 2.1669 | 23.5097 | 0 | 3.708 | 0 | 5.3061 | 1.3334 | 0.11614 | 1.734 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 69.4355 | 0.3042% | CZ 7 | 2.9866 | 0.1668 | 0.097051 | 0 | 0 | 1.0865 | 0 | 1.5547 | 0.39068 | 0.034028 | 0.50805 | 0 | 0.1019 | 0.56229 | 0 | 4.0743 | 11.5628 | 0.3042% | CZ 7 | 0 | 0 | 0.018357 | 0.2351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.29972 | 0.3042% | CZ 7 | 31.2663 | 1.7462 | 3.0224 | 25.6961 | 0 | 11.374 | 0 | 16.2761 | 4.09 | 0.35624 | 5.3188 | 0 | 1.0667 | 10.9436 | 0 | 42.6538 | 153.8103 | 0.3042%
CZ 8 | 0.31301 | 0.017003 | 0.029317 | 0.38202 | 0 | 0.055019 | 0 | 0.16334 | 0.039409 | 0.0052847 | 0.051371 | 0 | 0.010326 | 0.10323 | 0 | 0.41273 | 1.5821 | 0.05063% | CZ 8 | 10.5459 | 0.57286 | 2.2796 | 38.2021 | 0 | 1.8537 | 0 | 5.5031 | 1.3277 | 0.17805 | 1.7308 | 0 | 0.3479 | 6.5458 | 0 | 13.9054 | 82.993 | 0.05063% | CZ 8 | 3.09 | 0.16785 | 0.097088 | 0 | 0 | 0.54313 | 0 | 1.6124 | 0.38903 | 0.052169 | 0.50711 | 0 | 0.10193 | 0.56229 | 0 | 4.0743 | 11.1973 | 0.05063% | CZ 8 | 0 | 0 | 0.019482 | 0.38202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.44777 | 0.05063% | CZ 8 | 32.3488 | 1.7572 | 3.1458 | 41.7548 | 0 | 5.686 | 0 | 16.8804 | 4.0727 | 0.54615 | 5.309 | 0 | 1.0671 | 10.9436 | 0 | 42.6538 | 166.1655 | 0.05063%
US Weighted | 0.307 | 0.016881 | 0.024471 | 0.079251 | 0 | 0.25997 | 0 | 0.15103 | 0.037928 | 0.00093886 | 0.051607 | 0 | 0.010319 | 0.10323 | 0 | 0.41273 | 1.4553 | 100% | US Weighted | 10.3434 | 0.56876 | 1.7953 | 7.9251 | 0 | 8.7587 | 0 | 5.0884 | 1.2779 | 0.031632 | 1.7387 | 0 | 0.34768 | 6.5458 | 0 | 13.9054 | 58.3269 | 100% | US Weighted | 3.0306 | 0.16665 | 0.09703 | 0 | 0 | 2.5663 | 0 | 1.4909 | 0.37441 | 0.0092681 | 0.50945 | 0 | 0.10187 | 0.56229 | 0 | 4.0743 | 12.9831 | 100% | US Weighted | 0 | 0 | 0.014642 | 0.079251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14016 | 100% | US Weighted | 31.7275 | 1.7446 | 2.6162 | 8.6622 | 0 | 26.8665 | 0 | 15.6084 | 3.9197 | 0.097027 | 5.3334 | 0 | 1.0665 | 10.9436 | 0 | 42.6538 | 151.2394 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.46049 | 0.031727 | 0.022223 | 0.012774 | 0 | 0.7286 | 0 | 0.21022 | 0.050857 | 7.9898e-05 | 0.052432 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 2.1081 | 3.243% | CZ 1A | 15.5148 | 1.0689 | 1.5174 | 1.2774 | 0 | 24.5479 | 0 | 7.0826 | 1.7135 | 0.0026919 | 1.7665 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 75.7108 | 3.243% | CZ 1A | 4.5458 | 0.3132 | 0.10494 | 0 | 0 | 7.1925 | 0 | 2.0752 | 0.50204 | 0.00078873 | 0.51759 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 20.1137 | 3.243% | CZ 1A | 0 | 0 | 0.011593 | 0.012774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.070635 | 3.243% | CZ 1A | 47.5904 | 3.2789 | 2.3657 | 1.3962 | 0 | 75.2987 | 0 | 21.7254 | 5.2559 | 0.0082572 | 5.4187 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 218.2903 | 3.243%
CZ 1B | 0.46049 | 0.031689 | 0.022615 | 0.036255 | 0 | 0.81066 | 0 | 0.20057 | 0 | 0.00014458 | 0.052356 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 2.1535 | 0% | CZ 1B | 15.5148 | 1.0677 | 1.5569 | 3.6255 | 0 | 27.3124 | 0 | 6.7576 | 0 | 0.004871 | 1.764 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 78.8224 | 0% | CZ 1B | 4.5458 | 0.31282 | 0.1049 | 0 | 0 | 8.0025 | 0 | 1.98 | 0 | 0.0014272 | 0.51684 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 20.3258 | 0% | CZ 1B | 0 | 0 | 0.011989 | 0.036255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.094511 | 0% | CZ 1B | 47.5904 | 3.2749 | 2.4086 | 3.9627 | 0 | 83.7784 | 0 | 20.7282 | 0 | 0.014942 | 5.4108 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 223.1208 | 0%
CZ 2A | 0.46049 | 0.031678 | 0.023365 | 0.048768 | 0 | 0.62844 | 0 | 0.18214 | 0.051036 | 0.00018643 | 0.052337 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 2.0172 | 19.73% | CZ 2A | 15.5148 | 1.0673 | 1.6316 | 4.8768 | 0 | 21.1733 | 0 | 6.1366 | 1.7195 | 0.0062811 | 1.7633 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 75.1084 | 19.73% | CZ 2A | 4.5458 | 0.31271 | 0.10494 | 0 | 0 | 6.2038 | 0 | 1.798 | 0.50381 | 0.0018404 | 0.51665 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 18.8491 | 19.73% | CZ 2A | 0 | 0 | 0.012735 | 0.048768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10777 | 19.73% | CZ 2A | 47.5904 | 3.2738 | 2.4905 | 5.3303 | 0 | 64.9473 | 0 | 18.8236 | 5.2744 | 0.019267 | 5.4088 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 209.1106 | 19.73%
CZ 2B | 0.46049 | 0.0317 | 0.023525 | 0.056967 | 0 | 0.43749 | 0 | 0.17215 | 0.024312 | 0.00019784 | 0.051705 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.7973 | 3.29% | CZ 2B | 15.5148 | 1.068 | 1.6474 | 5.6967 | 0 | 14.7397 | 0 | 5.8001 | 0.81911 | 0.0066656 | 1.742 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 68.2535 | 3.29% | CZ 2B | 4.5458 | 0.31294 | 0.10498 | 0 | 0 | 4.3187 | 0 | 1.6994 | 0.24 | 0.001953 | 0.51042 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 16.5958 | 3.29% | CZ 2B | 0 | 0 | 0.012891 | 0.056967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11613 | 3.29% | CZ 2B | 47.5904 | 3.2761 | 2.508 | 6.2265 | 0 | 45.2127 | 0 | 17.7914 | 2.5125 | 0.020446 | 5.3436 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 186.4339 | 3.29%
CZ 3A | 0.46049 | 0.031697 | 0.02508 | 0.10043 | 0 | 0.39318 | 0 | 0.17029 | 0.046832 | 0.00045275 | 0.051877 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.8191 | 19.28% | CZ 3A | 15.5148 | 1.0679 | 1.8026 | 10.0426 | 0 | 13.2469 | 0 | 5.7373 | 1.5778 | 0.015254 | 1.7478 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 71.9719 | 19.28% | CZ 3A | 4.5458 | 0.3129 | 0.10501 | 0 | 0 | 3.8814 | 0 | 1.681 | 0.46231 | 0.0044694 | 0.51211 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 16.3665 | 19.28% | CZ 3A | 0 | 0 | 0.014442 | 0.10043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16113 | 19.28% | CZ 3A | 47.5904 | 3.2757 | 2.6779 | 10.9765 | 0 | 40.6339 | 0 | 17.5988 | 4.8399 | 0.046791 | 5.3613 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 188.9529 | 19.28%
CZ 3B | 0.46049 | 0.031693 | 0.02465 | 0.075136 | 0 | 0.31493 | 0 | 0.16149 | 0.034828 | 0.00026252 | 0.051637 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.6939 | 8.936% | CZ 3B | 15.5148 | 1.0678 | 1.7596 | 7.5136 | 0 | 10.6104 | 0 | 5.4408 | 1.1734 | 0.0088448 | 1.7397 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 66.048 | 8.936% | CZ 3B | 4.5458 | 0.31286 | 0.10501 | 0 | 0 | 3.1089 | 0 | 1.5942 | 0.34381 | 0.0025915 | 0.50974 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 15.3844 | 8.936% | CZ 3B | 0 | 0 | 0.014012 | 0.075136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13542 | 8.936% | CZ 3B | 47.5904 | 3.2753 | 2.6309 | 8.2123 | 0 | 32.5466 | 0 | 16.6893 | 3.5993 | 0.027131 | 5.3365 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 175.8601 | 8.936%
CZ 3C | 0.46049 | 0.031689 | 0.024962 | 0.077954 | 0 | 0.24682 | 0 | 0.13697 | 0 | 0.00018643 | 0.051918 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.5697 | 0.953% | CZ 3C | 15.5148 | 1.0677 | 1.791 | 7.7954 | 0 | 8.3158 | 0 | 4.6147 | 0 | 0.0062811 | 1.7492 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 62.0737 | 0.953% | CZ 3C | 4.5458 | 0.31282 | 0.10498 | 0 | 0 | 2.4365 | 0 | 1.3521 | 0 | 0.0018404 | 0.51252 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 14.1281 | 0.953% | CZ 3C | 0 | 0 | 0.014328 | 0.077954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13855 | 0.953% | CZ 3C | 47.5904 | 3.2749 | 2.665 | 8.5203 | 0 | 25.508 | 0 | 14.1551 | 0 | 0.019267 | 5.3656 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 163.0505 | 0.953%
CZ 4A | 0.46049 | 0.031647 | 0.026329 | 0.16289 | 0 | 0.27494 | 0 | 0.15566 | 0.045702 | 0.00092834 | 0.051663 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.749 | 17.51% | CZ 4A | 15.5148 | 1.0662 | 1.927 | 16.2887 | 0 | 9.2633 | 0 | 5.2446 | 1.5398 | 0.031277 | 1.7406 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 73.8353 | 17.51% | CZ 4A | 4.5458 | 0.31241 | 0.10509 | 0 | 0 | 2.7142 | 0 | 1.5367 | 0.45115 | 0.0091642 | 0.51 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 15.046 | 17.51% | CZ 4A | 0 | 0 | 0.015684 | 0.16289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22484 | 17.51% | CZ 4A | 47.5904 | 3.2706 | 2.8144 | 17.8035 | 0 | 28.4145 | 0 | 16.0873 | 4.7231 | 0.09594 | 5.3392 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 182.0912 | 17.51%
CZ 4B | 0.46049 | 0.03167 | 0.025956 | 0.10702 | 0 | 0.24668 | 0 | 0.16745 | 0.034714 | 0.00050602 | 0.051481 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.6647 | 0.665% | CZ 4B | 15.5148 | 1.067 | 1.89 | 10.7022 | 0 | 8.311 | 0 | 5.6417 | 1.1696 | 0.017049 | 1.7345 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 67.2666 | 0.665% | CZ 4B | 4.5458 | 0.31264 | 0.10505 | 0 | 0 | 2.4351 | 0 | 1.653 | 0.34268 | 0.0049953 | 0.5082 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 14.769 | 0.665% | CZ 4B | 0 | 0 | 0.015314 | 0.10702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1686 | 0.665% | CZ 4B | 47.5904 | 3.273 | 2.7736 | 11.6975 | 0 | 25.4934 | 0 | 17.3054 | 3.5875 | 0.052295 | 5.3204 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 173.0454 | 0.665%
CZ 4C | 0.46049 | 0.031609 | 0.026524 | 0.17369 | 0 | 0.1507 | 0 | 0.16119 | 0.034835 | 0.0008142 | 0.0515 | 0 | 0.018274 | 0.10323 | 0 | 0.41724 | 1.6301 | 1.872% | CZ 4C | 15.5148 | 1.065 | 1.9465 | 17.3685 | 0 | 5.0773 | 0 | 5.4308 | 1.1737 | 0.027432 | 1.7351 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 70.5582 | 1.872% | CZ 4C | 4.5458 | 0.31203 | 0.10509 | 0 | 0 | 1.4876 | 0 | 1.5912 | 0.34388 | 0.0080375 | 0.50839 | 0 | 0.18039 | 0.56229 | 0 | 4.1189 | 13.7637 | 1.872% | CZ 4C | 0 | 0 | 0.015878 | 0.17369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.23583 | 1.872% | CZ 4C | 47.5904 | 3.2667 | 2.8357 | 18.9838 | 0 | 15.5742 | 0 | 16.6586 | 3.6001 | 0.084144 | 5.3223 | 0 | 1.8885 | 10.9436 | 0 | 43.1205 | 169.8686 | 1.872%
CZ 5A | 0.46049 | 0.031655 | 0.027368 | 0.2201 | 0 | 0.17182 | 0 | 0.16483 | 0.034835 | 0.0018415 | 0.051488 | 0 | 0.018262 | 0.10323 | 0 | 0.41724 | 1.7032 | 16.48% | CZ 5A | 15.5148 | 1.0665 | 2.0307 | 22.0099 | 0 | 5.7889 | 0 | 5.5535 | 1.1737 | 0.062042 | 1.7347 | 0 | 0.61529 | 6.5458 | 0 | 14.0576 | 76.1534 | 16.48% | CZ 5A | 4.5458 | 0.31249 | 0.10513 | 0 | 0 | 1.6961 | 0 | 1.6272 | 0.34388 | 0.018178 | 0.50828 | 0 | 0.18028 | 0.56229 | 0 | 4.1189 | 14.0185 | 16.48% | CZ 5A | 0 | 0 | 0.016719 | 0.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.28309 | 16.48% | CZ 5A | 47.5904 | 3.2714 | 2.928 | 24.0568 | 0 | 17.7568 | 0 | 17.0349 | 3.6001 | 0.19031 | 5.3212 | 0 | 1.8874 | 10.9436 | 0 | 43.1205 | 177.7013 | 16.48%
CZ 5B | 0.46049 | 0.031659 | 0.027036 | 0.15658 | 0 | 0.19193 | 0 | 0.16078 | 0.034778 | 0.0010577 | 0.051382 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.6544 | 4.56% | CZ 5B | 15.5148 | 1.0666 | 1.9978 | 15.6579 | 0 | 6.4664 | 0 | 5.4171 | 1.1717 | 0.035636 | 1.7311 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 70.2781 | 4.56% | CZ 5B | 4.5458 | 0.31252 | 0.10509 | 0 | 0 | 1.8947 | 0 | 1.5872 | 0.34332 | 0.010441 | 0.50723 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 14.1678 | 4.56% | CZ 5B | 0 | 0 | 0.016391 | 0.15658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.21924 | 4.56% | CZ 5B | 47.5904 | 3.2718 | 2.8917 | 17.1141 | 0 | 19.8353 | 0 | 16.6166 | 3.5942 | 0.10931 | 5.3101 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 172.2857 | 4.56%
CZ 5C | 0.46049 | 0.031609 | 0.02708 | 0.20628 | 0 | 0.1099 | 0 | 0.16984 | 0.034835 | 0.0010044 | 0.05142 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.6312 | 0.02421% | CZ 5C | 15.5148 | 1.065 | 2.0019 | 20.6282 | 0 | 3.7026 | 0 | 5.7222 | 1.1737 | 0.033841 | 1.7324 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 72.7935 | 0.02421% | CZ 5C | 4.5458 | 0.31203 | 0.10513 | 0 | 0 | 1.0849 | 0 | 1.6766 | 0.34388 | 0.0099154 | 0.5076 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 13.4474 | 0.02421% | CZ 5C | 0 | 0 | 0.016431 | 0.20628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.26898 | 0.02421% | CZ 5C | 47.5904 | 3.2667 | 2.8964 | 22.5467 | 0 | 11.3575 | 0 | 17.5524 | 3.6001 | 0.1038 | 5.3141 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 170.1799 | 0.02421%
CZ 6A | 0.46049 | 0.031643 | 0.028201 | 0.29497 | 0 | 0.17745 | 0 | 0.16757 | 0.034835 | 0.0026823 | 0.05145 | 0 | 0.018262 | 0.10323 | 0 | 0.41724 | 1.788 | 2.494% | CZ 6A | 15.5148 | 1.0661 | 2.1137 | 29.4972 | 0 | 5.9787 | 0 | 5.6458 | 1.1737 | 0.090371 | 1.7335 | 0 | 0.61529 | 6.5458 | 0 | 14.0576 | 84.0325 | 2.494% | CZ 6A | 4.5458 | 0.31237 | 0.10516 | 0 | 0 | 1.7518 | 0 | 1.6542 | 0.34388 | 0.026479 | 0.5079 | 0 | 0.18028 | 0.56229 | 0 | 4.1189 | 14.1091 | 2.494% | CZ 6A | 0 | 0 | 0.017548 | 0.29497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.35879 | 2.494% | CZ 6A | 47.5904 | 3.2702 | 3.019 | 32.2404 | 0 | 18.3392 | 0 | 17.318 | 3.6001 | 0.2772 | 5.3172 | 0 | 1.8874 | 10.9436 | 0 | 43.1205 | 186.9232 | 2.494%
CZ 6B | 0.46049 | 0.031621 | 0.027956 | 0.23568 | 0 | 0.13759 | 0 | 0.15489 | 0.034801 | 0.0018186 | 0.051272 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.6749 | 0.6028% | CZ 6B | 15.5148 | 1.0653 | 2.0895 | 23.5682 | 0 | 4.6357 | 0 | 5.2186 | 1.1725 | 0.061273 | 1.7274 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 76.2723 | 0.6028% | CZ 6B | 4.5458 | 0.31215 | 0.10513 | 0 | 0 | 1.3583 | 0 | 1.529 | 0.34355 | 0.017953 | 0.50614 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 13.5796 | 0.6028% | CZ 6B | 0 | 0 | 0.017307 | 0.23568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.29926 | 0.6028% | CZ 6B | 47.5904 | 3.2679 | 2.9922 | 25.7601 | 0 | 14.2196 | 0 | 16.0075 | 3.5966 | 0.18795 | 5.2987 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 174.8732 | 0.6028%
CZ 7 | 0.46049 | 0.031598 | 0.029109 | 0.35687 | 0 | 0.14169 | 0 | 0.16724 | 0.034835 | 0.003291 | 0.051367 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.8152 | 0.3042% | CZ 7 | 15.5148 | 1.0646 | 2.2045 | 35.6873 | 0 | 4.7736 | 0 | 5.6346 | 1.1737 | 0.11088 | 1.7306 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 89.1134 | 0.3042% | CZ 7 | 4.5458 | 0.31192 | 0.10516 | 0 | 0 | 1.3987 | 0 | 1.651 | 0.34388 | 0.032488 | 0.50708 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 13.7575 | 0.3042% | CZ 7 | 0 | 0 | 0.018456 | 0.35687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.4216 | 0.3042% | CZ 7 | 47.5904 | 3.2655 | 3.1181 | 39.0062 | 0 | 14.6427 | 0 | 17.2838 | 3.6001 | 0.34012 | 5.3086 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 190.1074 | 0.3042%
CZ 8 | 0.46049 | 0.031426 | 0.030223 | 0.54657 | 0 | 0.085205 | 0 | 0.16961 | 0.034835 | 0.0051097 | 0.051188 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.9534 | 0.05063% | CZ 8 | 15.5148 | 1.0588 | 2.3155 | 54.657 | 0 | 2.8707 | 0 | 5.7144 | 1.1737 | 0.17215 | 1.7246 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 106.4204 | 0.05063% | CZ 8 | 4.5458 | 0.31023 | 0.10524 | 0 | 0 | 0.84112 | 0 | 1.6743 | 0.34388 | 0.050441 | 0.50531 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 13.2379 | 0.05063% | CZ 8 | 0 | 0 | 0.019563 | 0.54657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.6124 | 0.05063% | CZ 8 | 47.5904 | 3.2478 | 3.24 | 59.7401 | 0 | 8.8057 | 0 | 17.5284 | 3.6001 | 0.52807 | 5.2901 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 205.5224 | 0.05063%
US Weighted | 0.46049 | 0.031672 | 0.025387 | 0.12482 | 0 | 0.36377 | 0 | 0.16863 | 0.042085 | 0.00078202 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.8082 | 100% | US Weighted | 15.5148 | 1.0671 | 1.8331 | 12.4821 | 0 | 12.2559 | 0 | 5.6814 | 1.4179 | 0.026348 | 1.7455 | 0 | 0.61547 | 6.5458 | 0 | 14.0576 | 73.2431 | 100% | US Weighted | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.591 | 0 | 1.6646 | 0.41545 | 0.0077199 | 0.51144 | 0 | 0.18033 | 0.56229 | 0 | 4.1189 | 16.0152 | 100% | US Weighted | 0 | 0 | 0.014746 | 0.12482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.18584 | 100% | US Weighted | 47.5904 | 3.2732 | 2.7114 | 13.643 | 0 | 37.594 | 0 | 17.4271 | 4.3493 | 0.080819 | 5.3543 | 0 | 1.8879 | 10.9436 | 0 | 43.1205 | 187.9754 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.46049 | 0.031727 | 0.022226 | 0.013575 | 0 | 0.77176 | 0 | 0.24616 | 0.065714 | 8.7507e-05 | 0.052432 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 2.2029 | 3.243% | CZ 1A | 15.5148 | 1.0689 | 1.5177 | 1.3575 | 0 | 26.0019 | 0 | 8.2936 | 2.214 | 0.0029483 | 1.7665 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 78.9568 | 3.243% | CZ 1A | 4.5458 | 0.3132 | 0.10494 | 0 | 0 | 7.6186 | 0 | 2.43 | 0.64871 | 0.00086384 | 0.51759 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 21.0412 | 3.243% | CZ 1A | 0 | 0 | 0.011595 | 0.013575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.071438 | 3.243% | CZ 1A | 47.5904 | 3.2789 | 2.366 | 1.4838 | 0 | 79.7587 | 0 | 25.4399 | 6.7913 | 0.0090436 | 5.4187 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 228.0885 | 3.243%
CZ 1B | 0.46049 | 0.031689 | 0.022617 | 0.037831 | 0 | 0.83757 | 0 | 0.22442 | 0.013727 | 0.00014458 | 0.052356 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 2.2196 | 0% | CZ 1B | 15.5148 | 1.0677 | 1.557 | 3.7831 | 0 | 28.2191 | 0 | 7.5611 | 0.46249 | 0.004871 | 1.764 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 81.153 | 0% | CZ 1B | 4.5458 | 0.31282 | 0.1049 | 0 | 0 | 8.2682 | 0 | 2.2154 | 0.13551 | 0.0014272 | 0.51684 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 20.9624 | 0% | CZ 1B | 0 | 0 | 0.01199 | 0.037831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.096089 | 0% | CZ 1B | 47.5904 | 3.2749 | 2.4087 | 4.1349 | 0 | 86.5599 | 0 | 23.1932 | 1.4187 | 0.014942 | 5.4108 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 229.9583 | 0%
CZ 2A | 0.46049 | 0.031678 | 0.023369 | 0.054967 | 0 | 0.68393 | 0 | 0.20936 | 0.065646 | 0.00022447 | 0.052341 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 2.1208 | 19.73% | CZ 2A | 15.5148 | 1.0673 | 1.632 | 5.4967 | 0 | 23.0429 | 0 | 7.0538 | 2.2117 | 0.0075629 | 1.7634 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 79.0091 | 19.73% | CZ 2A | 4.5458 | 0.31271 | 0.10494 | 0 | 0 | 6.7516 | 0 | 2.0668 | 0.64803 | 0.0022159 | 0.51669 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 19.8103 | 19.73% | CZ 2A | 0 | 0 | 0.012739 | 0.054967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11397 | 19.73% | CZ 2A | 47.5904 | 3.2738 | 2.4909 | 6.0079 | 0 | 70.6821 | 0 | 21.6369 | 6.7842 | 0.023199 | 5.4092 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 219.8509 | 19.73%
CZ 2B | 0.46049 | 0.0317 | 0.02353 | 0.062464 | 0 | 0.48722 | 0 | 0.20526 | 0.0075637 | 0.00021306 | 0.051705 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.8689 | 3.29% | CZ 2B | 15.5148 | 1.068 | 1.6479 | 6.2464 | 0 | 16.4153 | 0 | 6.9155 | 0.25483 | 0.0071784 | 1.742 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 71.0308 | 3.29% | CZ 2B | 4.5458 | 0.31294 | 0.10498 | 0 | 0 | 4.8097 | 0 | 2.0262 | 0.074666 | 0.0021033 | 0.51042 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 17.2483 | 3.29% | CZ 2B | 0 | 0 | 0.012896 | 0.062464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12163 | 3.29% | CZ 2B | 47.5904 | 3.2761 | 2.5085 | 6.8273 | 0 | 50.3526 | 0 | 21.2127 | 0.78168 | 0.022019 | 5.3436 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 193.8667 | 3.29%
CZ 3A | 0.46049 | 0.031697 | 0.025085 | 0.11525 | 0 | 0.42385 | 0 | 0.19464 | 0.061403 | 0.00056309 | 0.051877 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.9036 | 19.28% | CZ 3A | 15.5148 | 1.0679 | 1.8031 | 11.5254 | 0 | 14.2804 | 0 | 6.5577 | 2.0688 | 0.018971 | 1.7478 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 75.8037 | 19.28% | CZ 3A | 4.5458 | 0.3129 | 0.10501 | 0 | 0 | 4.1842 | 0 | 1.9214 | 0.60615 | 0.0055586 | 0.51211 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 17.0546 | 19.28% | CZ 3A | 0 | 0 | 0.014447 | 0.11525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.17597 | 19.28% | CZ 3A | 47.5904 | 3.2757 | 2.6784 | 12.5973 | 0 | 43.8039 | 0 | 20.1152 | 6.3458 | 0.058193 | 5.3613 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 197.7781 | 19.28%
CZ 3B | 0.46049 | 0.031693 | 0.02466 | 0.09364 | 0 | 0.34326 | 0 | 0.1856 | 0.04017 | 0.00031959 | 0.051633 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.7702 | 8.936% | CZ 3B | 15.5148 | 1.0678 | 1.7607 | 9.364 | 0 | 11.5649 | 0 | 6.253 | 1.3534 | 0.010768 | 1.7396 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 69.8477 | 8.936% | CZ 3B | 4.5458 | 0.31286 | 0.10501 | 0 | 0 | 3.3885 | 0 | 1.8321 | 0.39654 | 0.0031549 | 0.5097 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 15.9552 | 8.936% | CZ 3B | 0 | 0 | 0.014023 | 0.09364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15393 | 8.936% | CZ 3B | 47.5904 | 3.2753 | 2.6321 | 10.2348 | 0 | 35.4744 | 0 | 19.1806 | 4.1514 | 0.033029 | 5.3361 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 183.8599 | 8.936%
CZ 3C | 0.46049 | 0.031689 | 0.024968 | 0.10081 | 0 | 0.27502 | 0 | 0.16367 | 0 | 0.00026633 | 0.051907 | 0 | 0.018274 | 0.10323 | 0 | 0.41724 | 1.6476 | 0.953% | CZ 3C | 15.5148 | 1.0677 | 1.7917 | 10.0806 | 0 | 9.2658 | 0 | 5.5142 | 0 | 0.008973 | 1.7488 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 66.2116 | 0.953% | CZ 3C | 4.5458 | 0.31282 | 0.10498 | 0 | 0 | 2.7149 | 0 | 1.6156 | 0 | 0.0026291 | 0.51241 | 0 | 0.18039 | 0.56229 | 0 | 4.1189 | 14.6707 | 0.953% | CZ 3C | 0 | 0 | 0.014334 | 0.10081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16141 | 0.953% | CZ 3C | 47.5904 | 3.2749 | 2.6657 | 11.0181 | 0 | 28.4219 | 0 | 16.9142 | 0 | 0.027524 | 5.3644 | 0 | 1.8885 | 10.9436 | 0 | 43.1205 | 171.2299 | 0.953%
CZ 4A | 0.46049 | 0.031647 | 0.026341 | 0.1954 | 0 | 0.2939 | 0 | 0.17918 | 0.060753 | 0.0012631 | 0.051663 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.8394 | 17.51% | CZ 4A | 15.5148 | 1.0662 | 1.9282 | 19.5401 | 0 | 9.9019 | 0 | 6.037 | 2.0469 | 0.042558 | 1.7406 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 79.0373 | 17.51% | CZ 4A | 4.5458 | 0.31241 | 0.10509 | 0 | 0 | 2.9013 | 0 | 1.7688 | 0.59973 | 0.012469 | 0.51 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 15.6172 | 17.51% | CZ 4A | 0 | 0 | 0.015695 | 0.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.25736 | 17.51% | CZ 4A | 47.5904 | 3.2706 | 2.8156 | 21.3573 | 0 | 30.3734 | 0 | 18.5181 | 6.2786 | 0.13054 | 5.3392 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 191.626 | 17.51%
CZ 4B | 0.46049 | 0.03167 | 0.025964 | 0.14904 | 0 | 0.26236 | 0 | 0.18816 | 0.027919 | 0.00092073 | 0.051481 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.7367 | 0.665% | CZ 4B | 15.5148 | 1.067 | 1.8907 | 14.9041 | 0 | 8.8393 | 0 | 6.3394 | 0.94063 | 0.031021 | 1.7345 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 72.4803 | 0.665% | CZ 4B | 4.5458 | 0.31264 | 0.10505 | 0 | 0 | 2.5899 | 0 | 1.8574 | 0.2756 | 0.0090891 | 0.5082 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 15.0653 | 0.665% | CZ 4B | 0 | 0 | 0.015322 | 0.14904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.21063 | 0.665% | CZ 4B | 47.5904 | 3.273 | 2.7745 | 16.2902 | 0 | 27.1138 | 0 | 19.4456 | 2.8853 | 0.095154 | 5.3204 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 180.7401 | 0.665%
CZ 4C | 0.46049 | 0.031609 | 0.02654 | 0.22702 | 0 | 0.15521 | 0 | 0.17868 | 0.036475 | 0.00093595 | 0.0515 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.7072 | 1.872% | CZ 4C | 15.5148 | 1.065 | 1.9479 | 22.702 | 0 | 5.2293 | 0 | 6.02 | 1.2289 | 0.031534 | 1.7351 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 76.6934 | 1.872% | CZ 4C | 4.5458 | 0.31203 | 0.10513 | 0 | 0 | 1.5322 | 0 | 1.7639 | 0.36007 | 0.0092394 | 0.50839 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 13.9982 | 1.872% | CZ 4C | 0 | 0 | 0.015891 | 0.22702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.28918 | 1.872% | CZ 4C | 47.5904 | 3.2667 | 2.8375 | 24.8133 | 0 | 16.0405 | 0 | 18.4658 | 3.7696 | 0.096727 | 5.3223 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 178.1547 | 1.872%
CZ 5A | 0.46049 | 0.031655 | 0.027377 | 0.30371 | 0 | 0.17915 | 0 | 0.18747 | 0.038545 | 0.0020659 | 0.051488 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.8207 | 16.48% | CZ 5A | 15.5148 | 1.0665 | 2.0316 | 30.3707 | 0 | 6.0359 | 0 | 6.3161 | 1.2986 | 0.069605 | 1.7347 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 85.6575 | 16.48% | CZ 5A | 4.5458 | 0.31249 | 0.10513 | 0 | 0 | 1.7685 | 0 | 1.8506 | 0.3805 | 0.020394 | 0.50828 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 14.3533 | 16.48% | CZ 5A | 0 | 0 | 0.016728 | 0.30371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.3667 | 16.48% | CZ 5A | 47.5904 | 3.2714 | 2.9289 | 33.1951 | 0 | 18.5145 | 0 | 19.3741 | 3.9835 | 0.21351 | 5.3212 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 190.3448 | 16.48%
CZ 5B | 0.46049 | 0.031659 | 0.027047 | 0.22895 | 0 | 0.20011 | 0 | 0.17975 | 0.028767 | 0.0017197 | 0.051382 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.7486 | 4.56% | CZ 5B | 15.5148 | 1.0666 | 1.9988 | 22.8949 | 0 | 6.7419 | 0 | 6.0561 | 0.96921 | 0.05794 | 1.7311 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 78.2503 | 4.56% | CZ 5B | 4.5458 | 0.31252 | 0.10509 | 0 | 0 | 1.9754 | 0 | 1.7744 | 0.28398 | 0.016976 | 0.50723 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 14.3829 | 4.56% | CZ 5B | 0 | 0 | 0.016401 | 0.22895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.29162 | 4.56% | CZ 5B | 47.5904 | 3.2718 | 2.8928 | 25.0241 | 0 | 20.6803 | 0 | 18.5767 | 2.973 | 0.17773 | 5.3101 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 182.4487 | 4.56%
CZ 5C | 0.46049 | 0.031609 | 0.027093 | 0.27126 | 0 | 0.11401 | 0 | 0.19022 | 0.035996 | 0.0011528 | 0.05142 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 1.722 | 0.02421% | CZ 5C | 15.5148 | 1.065 | 2.0031 | 27.1255 | 0 | 3.8413 | 0 | 6.4089 | 1.2128 | 0.03884 | 1.7324 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 80.1617 | 0.02421% | CZ 5C | 4.5458 | 0.31203 | 0.10513 | 0 | 0 | 1.1255 | 0 | 1.8778 | 0.35534 | 0.01138 | 0.5076 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 13.7021 | 0.02421% | CZ 5C | 0 | 0 | 0.016443 | 0.27126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.33397 | 0.02421% | CZ 5C | 47.5904 | 3.2667 | 2.8978 | 29.6482 | 0 | 11.783 | 0 | 19.6587 | 3.72 | 0.11914 | 5.3141 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 179.9503 | 0.02421%
CZ 6A | 0.46049 | 0.031643 | 0.028219 | 0.41696 | 0 | 0.18567 | 0 | 0.19285 | 0.038473 | 0.0033747 | 0.051435 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.9479 | 2.494% | CZ 6A | 15.5148 | 1.0661 | 2.1153 | 41.6958 | 0 | 6.2556 | 0 | 6.4975 | 1.2962 | 0.1137 | 1.7329 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 97.5067 | 2.494% | CZ 6A | 4.5458 | 0.31237 | 0.1052 | 0 | 0 | 1.8329 | 0 | 1.9038 | 0.37979 | 0.033314 | 0.50775 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 14.4824 | 2.494% | CZ 6A | 0 | 0 | 0.017562 | 0.41696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.48079 | 2.494% | CZ 6A | 47.5904 | 3.2702 | 3.0209 | 45.5735 | 0 | 19.1885 | 0 | 19.9304 | 3.976 | 0.34877 | 5.3156 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 204.1662 | 2.494%
CZ 6B | 0.46049 | 0.031621 | 0.027977 | 0.32356 | 0 | 0.14361 | 0 | 0.17682 | 0.038282 | 0.0021572 | 0.051256 | 0 | 0.018266 | 0.10323 | 0 | 0.41724 | 1.7945 | 0.6028% | CZ 6B | 15.5148 | 1.0653 | 2.0913 | 32.356 | 0 | 4.8384 | 0 | 5.9573 | 1.2898 | 0.072681 | 1.7269 | 0 | 0.61542 | 6.5458 | 0 | 14.0576 | 86.1314 | 0.6028% | CZ 6B | 4.5458 | 0.31215 | 0.10516 | 0 | 0 | 1.4176 | 0 | 1.7455 | 0.37791 | 0.021296 | 0.50599 | 0 | 0.18032 | 0.56229 | 0 | 4.1189 | 13.8929 | 0.6028% | CZ 6B | 0 | 0 | 0.017324 | 0.32356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.38715 | 0.6028% | CZ 6B | 47.5904 | 3.2679 | 2.9945 | 35.3651 | 0 | 14.8413 | 0 | 18.2735 | 3.9564 | 0.22294 | 5.2972 | 0 | 1.8877 | 10.9436 | 0 | 43.1205 | 187.7609 | 0.6028%
CZ 7 | 0.46049 | 0.031598 | 0.029135 | 0.50427 | 0 | 0.15255 | 0 | 0.18977 | 0.038024 | 0.0040329 | 0.05134 | 0 | 0.018274 | 0.10323 | 0 | 0.41724 | 2 | 0.3042% | CZ 7 | 15.5148 | 1.0646 | 2.2066 | 50.4266 | 0 | 5.1397 | 0 | 6.3936 | 1.2811 | 0.13588 | 1.7297 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 105.1118 | 0.3042% | CZ 7 | 4.5458 | 0.31192 | 0.10524 | 0 | 0 | 1.5059 | 0 | 1.8733 | 0.37536 | 0.039812 | 0.50681 | 0 | 0.18039 | 0.56229 | 0 | 4.1189 | 14.1258 | 0.3042% | CZ 7 | 0 | 0 | 0.018475 | 0.50427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.56901 | 0.3042% | CZ 7 | 47.5904 | 3.2655 | 3.121 | 55.1162 | 0 | 15.7657 | 0 | 19.6119 | 3.9296 | 0.41679 | 5.3058 | 0 | 1.8885 | 10.9436 | 0 | 43.1205 | 210.0757 | 0.3042%
CZ 8 | 0.46049 | 0.031426 | 0.030231 | 0.70048 | 0 | 0.091182 | 0 | 0.19886 | 0.036981 | 0.0054178 | 0.051188 | 0 | 0.01827 | 0.10323 | 0 | 0.41724 | 2.145 | 0.05063% | CZ 8 | 15.5148 | 1.0588 | 2.3162 | 70.0483 | 0 | 3.0721 | 0 | 6.7 | 1.246 | 0.18254 | 1.7246 | 0 | 0.61555 | 6.5458 | 0 | 14.0576 | 123.0823 | 0.05063% | CZ 8 | 4.5458 | 0.31023 | 0.10524 | 0 | 0 | 0.90012 | 0 | 1.9631 | 0.36507 | 0.053483 | 0.50531 | 0 | 0.18036 | 0.56229 | 0 | 4.1189 | 13.6099 | 0.05063% | CZ 8 | 0 | 0 | 0.01957 | 0.70048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.76632 | 0.05063% | CZ 8 | 47.5904 | 3.2478 | 3.2408 | 76.5628 | 0 | 9.4234 | 0 | 20.5517 | 3.8219 | 0.55991 | 5.2901 | 0 | 1.8881 | 10.9436 | 0 | 43.1205 | 226.241 | 0.05063%
US Weighted | 0.46049 | 0.031672 | 0.025395 | 0.15915 | 0 | 0.39183 | 0 | 0.19339 | 0.051266 | 0.00097001 | 0.051809 | 0 | 0.018268 | 0.10323 | 0 | 0.41724 | 1.9047 | 100% | US Weighted | 15.5148 | 1.0671 | 1.8339 | 15.9148 | 0 | 13.2015 | 0 | 6.5155 | 1.7272 | 0.032681 | 1.7455 | 0 | 0.61549 | 6.5458 | 0 | 14.0576 | 78.772 | 100% | US Weighted | 4.5458 | 0.31266 | 0.10504 | 0 | 0 | 3.8681 | 0 | 1.9091 | 0.50608 | 0.0095756 | 0.51144 | 0 | 0.18034 | 0.56229 | 0 | 4.1189 | 16.6292 | 100% | US Weighted | 0 | 0 | 0.014754 | 0.15915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22017 | 100% | US Weighted | 47.5904 | 3.2732 | 2.7123 | 17.3949 | 0 | 40.4946 | 0 | 19.9859 | 5.2982 | 0.10025 | 5.3542 | 0 | 1.888 | 10.9436 | 0 | 43.1205 | 198.156 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Primary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 73959 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 73959 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.32285 | 0.021972 | 0.00095785 | 0.0078187 | 0 | 0.42614 | 0 | 0.14302 | 0.027234 | 2.2828e-05 | 0.010744 | 0 | 0.011665 | 0 | 0 | 0.056735 | 1.0292 | 3.243% | CZ 1A | 10.8774 | 0.74027 | 0.042554 | 0.78187 | 0 | 14.3573 | 0 | 4.8186 | 0.91755 | 0.00076911 | 0.362 | 0 | 0.39302 | 0 | 0 | 1.9115 | 35.2029 | 3.243% | CZ 1A | 3.1871 | 0.2169 | 0.0079248 | 0 | 0 | 4.2067 | 0 | 1.4119 | 0.26884 | 0.00022535 | 0.10606 | 0 | 0.11515 | 0 | 0 | 0.56007 | 10.0808 | 3.243% | CZ 1A | 0 | 0 | 0.00015507 | 0.0078187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079738 | 3.243% | CZ 1A | 33.3656 | 2.2707 | 0.099914 | 0.85458 | 0 | 44.0398 | 0 | 14.7807 | 2.8145 | 0.0023592 | 1.1104 | 0 | 1.2055 | 0 | 0 | 5.8634 | 106.4075 | 3.243%
CZ 1B | 0.32475 | 0.021964 | 0.00095533 | 0.016822 | 0 | 0.41465 | 0 | 0.12944 | -0.028428 | 2.6633e-05 | 0.010699 | 0 | 0.011669 | 0 | 0 | 0.056735 | 0.95929 | 0% | CZ 1B | 10.9415 | 0.74001 | 0.042554 | 1.6822 | 0 | 13.9703 | 0 | 4.3611 | -0.9578 | 0.0008973 | 0.36046 | 0 | 0.39314 | 0 | 0 | 1.9115 | 33.4459 | 0% | CZ 1B | 3.2059 | 0.21682 | 0.0078873 | 0 | 0 | 4.0933 | 0 | 1.2778 | -0.28064 | 0.00026291 | 0.10561 | 0 | 0.11519 | 0 | 0 | 0.56007 | 9.3022 | 0% | CZ 1B | 0 | 0 | 0.00015635 | 0.016822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016978 | 0% | CZ 1B | 33.5622 | 2.2699 | 0.099661 | 1.8386 | 0 | 42.8527 | 0 | 13.3774 | -2.938 | 0.0027524 | 1.1057 | 0 | 1.2059 | 0 | 0 | 5.8634 | 99.2403 | 0%
CZ 2A | 0.32381 | 0.021941 | 0.00096041 | 0.028877 | 0 | 0.38476 | 0 | 0.11175 | 0.029829 | 5.707e-05 | 0.01068 | 0 | 0.01168 | 0 | 0 | 0.056735 | 0.98109 | 19.73% | CZ 2A | 10.9099 | 0.73925 | 0.04281 | 2.8877 | 0 | 12.9633 | 0 | 3.7651 | 1.005 | 0.0019228 | 0.35982 | 0 | 0.39353 | 0 | 0 | 1.9115 | 34.9797 | 19.73% | CZ 2A | 3.1966 | 0.2166 | 0.0079248 | 0 | 0 | 3.7982 | 0 | 1.1032 | 0.29446 | 0.00056338 | 0.10543 | 0 | 0.1153 | 0 | 0 | 0.56007 | 9.3983 | 19.73% | CZ 2A | 0 | 0 | 0.00015763 | 0.028877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029035 | 19.73% | CZ 2A | 33.4651 | 2.2676 | 0.10019 | 3.1563 | 0 | 39.7638 | 0 | 11.549 | 3.0827 | 0.005898 | 1.1037 | 0 | 1.2071 | 0 | 0 | 5.8634 | 101.5647 | 19.73%
CZ 2B | 0.32117 | 0.021961 | 0.00095397 | 0.032859 | 0 | 0.23657 | 0 | 0.10899 | -0.0289 | 6.8484e-05 | 0.010223 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.7723 | 3.29% | CZ 2B | 10.8208 | 0.73989 | 0.041913 | 3.2859 | 0 | 7.9703 | 0 | 3.672 | -0.9737 | 0.0023073 | 0.34443 | 0 | 0.3934 | 0 | 0 | 1.9115 | 28.2087 | 3.29% | CZ 2B | 3.1705 | 0.21679 | 0.0079624 | 0 | 0 | 2.3353 | 0 | 1.0759 | -0.28529 | 0.00067605 | 0.10092 | 0 | 0.11527 | 0 | 0 | 0.56007 | 7.2981 | 3.29% | CZ 2B | 0 | 0 | 0.00014738 | 0.032859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033006 | 3.29% | CZ 2B | 33.1918 | 2.2695 | 0.099466 | 3.5915 | 0 | 24.4483 | 0 | 11.2636 | -2.9867 | 0.0070776 | 1.0565 | 0 | 1.2067 | 0 | 0 | 5.8634 | 80.0111 | 3.29%
CZ 3A | 0.32017 | 0.02193 | 0.00095653 | 0.059216 | 0 | 0.23415 | 0 | 0.10494 | 0.027032 | 4.9461e-05 | 0.01033 | 0 | 0.011673 | 0 | 0 | 0.056735 | 0.84718 | 19.28% | CZ 3A | 10.7872 | 0.73886 | 0.042169 | 5.9216 | 0 | 7.8888 | 0 | 3.5355 | 0.91076 | 0.0016664 | 0.34802 | 0 | 0.39327 | 0 | 0 | 1.9115 | 32.4793 | 19.28% | CZ 3A | 3.1606 | 0.21649 | 0.0079624 | 0 | 0 | 2.3114 | 0 | 1.0359 | 0.26685 | 0.00048826 | 0.10197 | 0 | 0.11523 | 0 | 0 | 0.56007 | 7.777 | 19.28% | CZ 3A | 0 | 0 | 0.00014994 | 0.059216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059366 | 19.28% | CZ 3A | 33.0888 | 2.2664 | 0.099747 | 6.4723 | 0 | 24.1982 | 0 | 10.8448 | 2.7937 | 0.0051116 | 1.0675 | 0 | 1.2063 | 0 | 0 | 5.8634 | 87.9063 | 19.28%
CZ 3B | 0.31863 | 0.021987 | 0.00095649 | 0.034939 | 0 | 0.15515 | 0 | 0.097118 | 0.04017 | -0.00038047 | 0.010143 | 0 | 0.011669 | 0 | 0 | 0.056735 | 0.74711 | 8.936% | CZ 3B | 10.735 | 0.74078 | 0.041913 | 3.4939 | 0 | 5.2271 | 0 | 3.2721 | 1.3534 | -0.012819 | 0.34174 | 0 | 0.39314 | 0 | 0 | 1.9115 | 27.4978 | 8.936% | CZ 3B | 3.1454 | 0.21705 | 0.0079999 | 0 | 0 | 1.5316 | 0 | 0.95871 | 0.39654 | -0.0037558 | 0.10013 | 0 | 0.11519 | 0 | 0 | 0.56007 | 7.0289 | 8.936% | CZ 3B | 0 | 0 | 0.0001461 | 0.034939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035085 | 8.936% | CZ 3B | 32.9288 | 2.2723 | 0.09972 | 3.8188 | 0 | 16.0338 | 0 | 10.0368 | 4.1514 | -0.03932 | 1.0483 | 0 | 1.2059 | 0 | 0 | 5.8634 | 77.4199 | 8.936%
CZ 3C | 0.31903 | 0.021976 | 0.00094632 | 0.05148 | 0 | 0.14435 | 0 | 0.076181 | 0 | -3.0437e-05 | 0.010391 | 0 | 0.011684 | 0 | 0 | 0.056735 | 0.69274 | 0.953% | CZ 3C | 10.7487 | 0.7404 | 0.0414 | 5.148 | 0 | 4.8632 | 0 | 2.5667 | 0 | -0.0010255 | 0.35007 | 0 | 0.39366 | 0 | 0 | 1.9115 | 26.7626 | 0.953% | CZ 3C | 3.1494 | 0.21694 | 0.0079248 | 0 | 0 | 1.4249 | 0 | 0.75203 | 0 | -0.00030047 | 0.10257 | 0 | 0.11534 | 0 | 0 | 0.56007 | 6.3289 | 0.953% | CZ 3C | 0 | 0 | 0.00014353 | 0.05148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051623 | 0.953% | CZ 3C | 32.9709 | 2.2711 | 0.098653 | 5.6267 | 0 | 14.9176 | 0 | 7.873 | 0 | -0.0031456 | 1.0738 | 0 | 1.2075 | 0 | 0 | 5.8634 | 71.8995 | 0.953%
CZ 4A | 0.32372 | 0.021888 | 0.00097055 | 0.12512 | 0 | 0.15687 | 0 | 0.09138 | 0.028923 | 0.00035003 | 0.010162 | 0 | 0.01168 | 0 | 0 | 0.056735 | 0.82779 | 17.51% | CZ 4A | 10.9065 | 0.73745 | 0.043067 | 12.5118 | 0 | 5.2851 | 0 | 3.0788 | 0.97447 | 0.011793 | 0.34238 | 0 | 0.39353 | 0 | 0 | 1.9115 | 36.1964 | 17.51% | CZ 4A | 3.1956 | 0.21607 | 0.0080375 | 0 | 0 | 1.5485 | 0 | 0.90208 | 0.28552 | 0.0034554 | 0.10032 | 0 | 0.1153 | 0 | 0 | 0.56007 | 6.935 | 17.51% | CZ 4A | 0 | 0 | 0.00015635 | 0.12512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12527 | 17.51% | CZ 4A | 33.4549 | 2.2621 | 0.10123 | 13.6754 | 0 | 16.2116 | 0 | 9.4438 | 2.9891 | 0.036174 | 1.0502 | 0 | 1.2071 | 0 | 0 | 5.8634 | 86.295 | 17.51%
CZ 4B | 0.32469 | 0.021957 | 0.00097183 | 0.062547 | 0 | 0.13391 | 0 | 0.091555 | 0.027919 | -0.00015599 | 0.010014 | 0 | 0.011669 | 0 | 0 | 0.056735 | 0.74181 | 0.665% | CZ 4B | 10.9392 | 0.73976 | 0.043195 | 6.2547 | 0 | 4.5117 | 0 | 3.0847 | 0.94063 | -0.0052556 | 0.33738 | 0 | 0.39314 | 0 | 0 | 1.9115 | 29.1507 | 0.665% | CZ 4B | 3.2052 | 0.21675 | 0.0080375 | 0 | 0 | 1.3219 | 0 | 0.9038 | 0.2756 | -0.0015399 | 0.098854 | 0 | 0.11519 | 0 | 0 | 0.56007 | 6.7039 | 0.665% | CZ 4B | 0 | 0 | 0.00015763 | 0.062547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062705 | 0.665% | CZ 4B | 33.5552 | 2.2691 | 0.10137 | 6.8364 | 0 | 13.8394 | 0 | 9.4619 | 2.8853 | -0.016121 | 1.0349 | 0 | 1.2059 | 0 | 0 | 5.8634 | 77.0368 | 0.665%
CZ 4C | 0.32159 | 0.021805 | 0.00097051 | 0.096341 | 0 | 0.10177 | 0 | 0.10314 | 0.036475 | -0.00093595 | 0.010056 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.75963 | 1.872% | CZ 4C | 10.8349 | 0.73463 | 0.04281 | 9.6341 | 0 | 3.429 | 0 | 3.4751 | 1.2289 | -0.031534 | 0.33879 | 0 | 0.3934 | 0 | 0 | 1.9115 | 31.9916 | 1.872% | CZ 4C | 3.1746 | 0.21525 | 0.008075 | 0 | 0 | 1.0047 | 0 | 1.0182 | 0.36007 | -0.0092394 | 0.099267 | 0 | 0.11527 | 0 | 0 | 0.56007 | 6.5463 | 1.872% | CZ 4C | 0 | 0 | 0.0001525 | 0.096341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096494 | 1.872% | CZ 4C | 33.2351 | 2.2534 | 0.10121 | 10.5301 | 0 | 10.5181 | 0 | 10.6596 | 3.7696 | -0.096727 | 1.0392 | 0 | 1.2067 | 0 | 0 | 5.8634 | 79.0797 | 1.872%
CZ 5A | 0.32456 | 0.021896 | 0.00097691 | 0.20769 | 0 | 0.093427 | 0 | 0.10371 | 0.0082409 | 0.00061255 | 0.010037 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.83956 | 16.48% | CZ 5A | 10.935 | 0.73771 | 0.043451 | 20.769 | 0 | 3.1477 | 0 | 3.4941 | 0.27765 | 0.020638 | 0.33815 | 0 | 0.3934 | 0 | 0 | 1.9115 | 42.0683 | 16.48% | CZ 5A | 3.204 | 0.21615 | 0.008075 | 0 | 0 | 0.92228 | 0 | 1.0238 | 0.081351 | 0.0060469 | 0.099079 | 0 | 0.11527 | 0 | 0 | 0.56007 | 6.236 | 16.48% | CZ 5A | 0 | 0 | 0.00015891 | 0.20769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20785 | 16.48% | CZ 5A | 33.5422 | 2.2629 | 0.10191 | 22.7005 | 0 | 9.6554 | 0 | 10.7178 | 0.85167 | 0.063305 | 1.0373 | 0 | 1.2067 | 0 | 0 | 5.8634 | 88.0029 | 16.48%
CZ 5B | 0.32436 | 0.021911 | 0.00097055 | 0.095842 | 0 | 0.10656 | 0 | 0.090962 | 0.028767 | -0.00017501 | 0.0099378 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.74755 | 4.56% | CZ 5B | 10.9282 | 0.73822 | 0.043067 | 9.5842 | 0 | 3.5902 | 0 | 3.0647 | 0.96921 | -0.0058965 | 0.33482 | 0 | 0.3934 | 0 | 0 | 1.9115 | 31.5516 | 4.56% | CZ 5B | 3.202 | 0.2163 | 0.0080375 | 0 | 0 | 1.0519 | 0 | 0.89794 | 0.28398 | -0.0017277 | 0.098102 | 0 | 0.11527 | 0 | 0 | 0.56007 | 6.4319 | 4.56% | CZ 5B | 0 | 0 | 0.00015635 | 0.095842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095998 | 4.56% | CZ 5B | 33.5213 | 2.2644 | 0.10123 | 10.4755 | 0 | 11.0127 | 0 | 9.4006 | 2.973 | -0.018087 | 1.027 | 0 | 1.2067 | 0 | 0 | 5.8634 | 77.8278 | 4.56%
CZ 5C | 0.32272 | 0.021805 | 0.00097179 | 0.17131 | 0 | 0.071379 | 0 | 0.11292 | 0.0081191 | 0.00017121 | 0.009991 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.78781 | 0.02421% | CZ 5C | 10.8731 | 0.73463 | 0.042938 | 17.1312 | 0 | 2.4049 | 0 | 3.8045 | 0.27355 | 0.0057683 | 0.33662 | 0 | 0.3934 | 0 | 0 | 1.9115 | 37.9121 | 0.02421% | CZ 5C | 3.1858 | 0.21525 | 0.008075 | 0 | 0 | 0.70463 | 0 | 1.1147 | 0.08015 | 0.0016901 | 0.098628 | 0 | 0.11527 | 0 | 0 | 0.56007 | 6.0843 | 0.02421% | CZ 5C | 0 | 0 | 0.00015379 | 0.17131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17147 | 0.02421% | CZ 5C | 33.3523 | 2.2534 | 0.10135 | 18.7244 | 0 | 7.3768 | 0 | 11.6701 | 0.83909 | 0.017694 | 1.0325 | 0 | 1.2067 | 0 | 0 | 5.8634 | 82.4377 | 0.02421%
CZ 6A | 0.32665 | 0.021873 | 0.00098324 | 0.28227 | 0 | 0.09173 | 0 | 0.10857 | 0.0066353 | 0.0012708 | 0.009991 | 0 | 0.01168 | 0 | 0 | 0.056735 | 0.91838 | 2.494% | CZ 6A | 11.0052 | 0.73694 | 0.043579 | 28.2265 | 0 | 3.0906 | 0 | 3.658 | 0.22356 | 0.042814 | 0.33662 | 0 | 0.39353 | 0 | 0 | 1.9115 | 49.6689 | 2.494% | CZ 6A | 3.2245 | 0.21592 | 0.0081502 | 0 | 0 | 0.90553 | 0 | 1.0718 | 0.065502 | 0.012544 | 0.098628 | 0 | 0.1153 | 0 | 0 | 0.56007 | 6.278 | 2.494% | CZ 6A | 0 | 0 | 0.00015763 | 0.28227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28242 | 2.494% | CZ 6A | 33.7577 | 2.2605 | 0.10255 | 30.8516 | 0 | 9.48 | 0 | 11.2207 | 0.68574 | 0.13133 | 1.0325 | 0 | 1.2071 | 0 | 0 | 5.8634 | 96.5931 | 2.494%
CZ 6B | 0.32733 | 0.021835 | 0.00097944 | 0.21378 | 0 | 0.078068 | 0 | 0.09372 | 0.0038275 | 0.00092834 | 0.0098503 | 0 | 0.011677 | 0 | 0 | 0.056735 | 0.81874 | 0.6028% | CZ 6B | 11.0284 | 0.73566 | 0.043451 | 21.3785 | 0 | 2.6302 | 0 | 3.1576 | 0.12895 | 0.031277 | 0.33187 | 0 | 0.3934 | 0 | 0 | 1.9115 | 41.7708 | 0.6028% | CZ 6B | 3.2313 | 0.21555 | 0.0081126 | 0 | 0 | 0.77066 | 0 | 0.92517 | 0.037784 | 0.0091642 | 0.097239 | 0 | 0.11527 | 0 | 0 | 0.56007 | 5.9703 | 0.6028% | CZ 6B | 0 | 0 | 0.00015763 | 0.21378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21394 | 0.6028% | CZ 6B | 33.8288 | 2.2566 | 0.10216 | 23.3667 | 0 | 8.068 | 0 | 9.6857 | 0.39556 | 0.09594 | 1.018 | 0 | 1.2067 | 0 | 0 | 5.8634 | 85.8875 | 0.6028%
CZ 7 | 0.32811 | 0.021789 | 0.0010011 | 0.34134 | 0 | 0.076477 | 0 | 0.10601 | 0.0058211 | 0.0036525 | 0.0099378 | 0 | 0.011684 | 0 | 0 | 0.056735 | 0.96256 | 0.3042% | CZ 7 | 11.0546 | 0.73412 | 0.045117 | 34.1335 | 0 | 2.5767 | 0 | 3.5718 | 0.19612 | 0.12306 | 0.33482 | 0 | 0.39366 | 0 | 0 | 1.9115 | 55.0749 | 0.3042% | CZ 7 | 3.239 | 0.2151 | 0.0081877 | 0 | 0 | 0.75496 | 0 | 1.0465 | 0.057464 | 0.036056 | 0.098102 | 0 | 0.11534 | 0 | 0 | 0.56007 | 6.1308 | 0.3042% | CZ 7 | 0 | 0 | 0.00017173 | 0.34134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34151 | 0.3042% | CZ 7 | 33.909 | 2.2518 | 0.10449 | 37.308 | 0 | 7.9037 | 0 | 10.9561 | 0.60159 | 0.37747 | 1.027 | 0 | 1.2075 | 0 | 0 | 5.8634 | 101.5101 | 0.3042%
CZ 8 | 0.31865 | 0.021298 | 0.00097812 | 0.44125 | 0 | 0.053866 | 0 | 0.12118 | 0.0019252 | 0.0044629 | 0.0098845 | 0 | 0.01168 | 0 | 0 | 0.056735 | 1.0419 | 0.05063% | CZ 8 | 10.7358 | 0.71758 | 0.043067 | 44.1247 | 0 | 1.8148 | 0 | 4.0827 | 0.064862 | 0.15036 | 0.33303 | 0 | 0.39353 | 0 | 0 | 1.9115 | 64.372 | 0.05063% | CZ 8 | 3.1456 | 0.21025 | 0.0081502 | 0 | 0 | 0.53175 | 0 | 1.1962 | 0.019005 | 0.044056 | 0.097577 | 0 | 0.1153 | 0 | 0 | 0.56007 | 5.928 | 0.05063% | CZ 8 | 0 | 0 | 0.0001525 | 0.44125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4414 | 0.05063% | CZ 8 | 32.9311 | 2.2011 | 0.10199 | 48.2283 | 0 | 5.5669 | 0 | 12.5234 | 0.19896 | 0.46122 | 1.0215 | 0 | 1.2071 | 0 | 0 | 5.8634 | 110.305 | 0.05063%
US Weighted | 0.32268 | 0.021921 | 0.00096492 | 0.094424 | 0 | 0.21147 | 0 | 0.10338 | 0.023432 | 0.00017592 | 0.010277 | 0 | 0.011676 | 0 | 0 | 0.056735 | 0.85713 | 100% | US Weighted | 10.8717 | 0.73857 | 0.04275 | 9.4424 | 0 | 7.1248 | 0 | 3.483 | 0.78945 | 0.005927 | 0.34625 | 0 | 0.39339 | 0 | 0 | 1.9115 | 35.1496 | 100% | US Weighted | 3.1854 | 0.2164 | 0.0080009 | 0 | 0 | 2.0876 | 0 | 1.0205 | 0.23131 | 0.0017366 | 0.10145 | 0 | 0.11526 | 0 | 0 | 0.56007 | 7.5277 | 100% | US Weighted | 0 | 0 | 0.00015443 | 0.094424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094578 | 100% | US Weighted | 33.348 | 2.2655 | 0.10064 | 10.3205 | 0 | 21.8546 | 0 | 10.6837 | 2.4216 | 0.01818 | 1.0621 | 0 | 1.2067 | 0 | 0 | 5.8634 | 89.1449 | 100%
Building Type: | Primary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 73959 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 73959 | [17 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 70.11% | 69.25% | 4.31% | 57.59% | 0% | 55.22% | 0% | 58.1% | 41.44% | 26.09% | 20.49% | 0% | 63.86% | 0% | 0% | 13.6% | 46.72% | 3.243% | CZ 1A | 70.11% | 69.25% | 2.804% | 57.59% | 0% | 55.22% | 0% | 58.1% | 41.44% | 26.09% | 20.49% | 0% | 63.86% | 0% | 0% | 13.6% | 44.58% | 3.243% | CZ 1A | 70.11% | 69.25% | 7.552% | 0% | 0% | 55.22% | 0% | 58.1% | 41.44% | 26.09% | 20.49% | 0% | 63.86% | 0% | 0% | 13.6% | 47.91% | 3.243% | CZ 1A | 0% | 0% | 1.337% | 57.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.16% | 3.243% | CZ 1A | 70.11% | 69.25% | 4.223% | 57.59% | 0% | 55.22% | 0% | 58.1% | 41.44% | 26.09% | 20.49% | 0% | 63.86% | 0% | 0% | 13.6% | 46.65% | 3.243%
CZ 1B | 70.52% | 69.31% | 4.224% | 44.46% | 0% | 49.51% | 0% | 57.68% | -207.1% | 18.42% | 20.43% | 0% | 63.88% | 0% | 0% | 13.6% | 43.22% | 0% | CZ 1B | 70.52% | 69.31% | 2.733% | 44.46% | 0% | 49.51% | 0% | 57.68% | -207.1% | 18.42% | 20.43% | 0% | 63.88% | 0% | 0% | 13.6% | 41.21% | 0% | CZ 1B | 70.52% | 69.31% | 7.519% | 0% | 0% | 49.51% | 0% | 57.68% | -207.1% | 18.42% | 20.43% | 0% | 63.88% | 0% | 0% | 13.6% | 44.38% | 0% | CZ 1B | 0% | 0% | 1.304% | 44.46% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.67% | 0% | CZ 1B | 70.52% | 69.31% | 4.137% | 44.46% | 0% | 49.51% | 0% | 57.68% | -207.1% | 18.42% | 20.43% | 0% | 63.88% | 0% | 0% | 13.6% | 43.16% | 0%
CZ 2A | 70.32% | 69.26% | 4.11% | 52.54% | 0% | 56.26% | 0% | 53.38% | 45.44% | 25.42% | 20.4% | 0% | 63.93% | 0% | 0% | 13.6% | 46.26% | 19.73% | CZ 2A | 70.32% | 69.26% | 2.623% | 52.54% | 0% | 56.26% | 0% | 53.38% | 45.44% | 25.42% | 20.4% | 0% | 63.93% | 0% | 0% | 13.6% | 44.27% | 19.73% | CZ 2A | 70.32% | 69.26% | 7.552% | 0% | 0% | 56.26% | 0% | 53.38% | 45.44% | 25.42% | 20.4% | 0% | 63.93% | 0% | 0% | 13.6% | 47.44% | 19.73% | CZ 2A | 0% | 0% | 1.237% | 52.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.48% | 19.73% | CZ 2A | 70.32% | 69.26% | 4.022% | 52.54% | 0% | 56.26% | 0% | 53.38% | 45.44% | 25.42% | 20.4% | 0% | 63.93% | 0% | 0% | 13.6% | 46.2% | 19.73%
CZ 2B | 69.74% | 69.28% | 4.054% | 52.6% | 0% | 48.55% | 0% | 53.1% | -382.1% | 32.14% | 19.77% | 0% | 63.92% | 0% | 0% | 13.6% | 41.32% | 3.29% | CZ 2B | 69.74% | 69.28% | 2.543% | 52.6% | 0% | 48.55% | 0% | 53.1% | -382.1% | 32.14% | 19.77% | 0% | 63.92% | 0% | 0% | 13.6% | 39.71% | 3.29% | CZ 2B | 69.74% | 69.28% | 7.585% | 0% | 0% | 48.55% | 0% | 53.1% | -382.1% | 32.14% | 19.77% | 0% | 63.92% | 0% | 0% | 13.6% | 42.31% | 3.29% | CZ 2B | 0% | 0% | 1.143% | 52.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.14% | 3.29% | CZ 2B | 69.74% | 69.28% | 3.965% | 52.6% | 0% | 48.55% | 0% | 53.1% | -382.1% | 32.14% | 19.77% | 0% | 63.92% | 0% | 0% | 13.6% | 41.27% | 3.29%
CZ 3A | 69.53% | 69.19% | 3.813% | 51.38% | 0% | 55.24% | 0% | 53.91% | 44.02% | 8.784% | 19.91% | 0% | 63.9% | 0% | 0% | 13.6% | 44.5% | 19.28% | CZ 3A | 69.53% | 69.19% | 2.339% | 51.38% | 0% | 55.24% | 0% | 53.91% | 44.02% | 8.784% | 19.91% | 0% | 63.9% | 0% | 0% | 13.6% | 42.85% | 19.28% | CZ 3A | 69.53% | 69.19% | 7.582% | 0% | 0% | 55.24% | 0% | 53.91% | 44.02% | 8.784% | 19.91% | 0% | 63.9% | 0% | 0% | 13.6% | 45.6% | 19.28% | CZ 3A | 0% | 0% | 1.038% | 51.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.74% | 19.28% | CZ 3A | 69.53% | 69.19% | 3.724% | 51.38% | 0% | 55.24% | 0% | 53.91% | 44.02% | 8.784% | 19.91% | 0% | 63.9% | 0% | 0% | 13.6% | 44.45% | 19.28%
CZ 3B | 69.19% | 69.38% | 3.879% | 37.31% | 0% | 45.2% | 0% | 52.33% | 100% | -119% | 19.64% | 0% | 63.88% | 0% | 0% | 13.6% | 42.2% | 8.936% | CZ 3B | 69.19% | 69.38% | 2.381% | 37.31% | 0% | 45.2% | 0% | 52.33% | 100% | -119% | 19.64% | 0% | 63.88% | 0% | 0% | 13.6% | 39.37% | 8.936% | CZ 3B | 69.19% | 69.38% | 7.618% | 0% | 0% | 45.2% | 0% | 52.33% | 100% | -119% | 19.64% | 0% | 63.88% | 0% | 0% | 13.6% | 44.05% | 8.936% | CZ 3B | 0% | 0% | 1.042% | 37.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.79% | 8.936% | CZ 3B | 69.19% | 69.38% | 3.789% | 37.31% | 0% | 45.2% | 0% | 52.33% | 100% | -119% | 19.64% | 0% | 63.88% | 0% | 0% | 13.6% | 42.11% | 8.936%
CZ 3C | 69.28% | 69.35% | 3.79% | 51.07% | 0% | 52.49% | 0% | 46.55% | 0% | -11.43% | 20.02% | 0% | 63.94% | 0% | 0% | 13.6% | 42.05% | 0.953% | CZ 3C | 69.28% | 69.35% | 2.311% | 51.07% | 0% | 52.49% | 0% | 46.55% | 0% | -11.43% | 20.02% | 0% | 63.94% | 0% | 0% | 13.6% | 40.42% | 0.953% | CZ 3C | 69.28% | 69.35% | 7.549% | 0% | 0% | 52.49% | 0% | 46.55% | 0% | -11.43% | 20.02% | 0% | 63.94% | 0% | 0% | 13.6% | 43.14% | 0.953% | CZ 3C | 0% | 0% | 1.001% | 51.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.98% | 0.953% | CZ 3C | 69.28% | 69.35% | 3.701% | 51.07% | 0% | 52.49% | 0% | 46.55% | 0% | -11.43% | 20.02% | 0% | 63.94% | 0% | 0% | 13.6% | 41.99% | 0.953%
CZ 4A | 70.3% | 69.16% | 3.685% | 64.03% | 0% | 53.37% | 0% | 51% | 47.61% | 27.71% | 19.67% | 0% | 63.93% | 0% | 0% | 13.6% | 45% | 17.51% | CZ 4A | 70.3% | 69.16% | 2.234% | 64.03% | 0% | 53.37% | 0% | 51% | 47.61% | 27.71% | 19.67% | 0% | 63.93% | 0% | 0% | 13.6% | 45.8% | 17.51% | CZ 4A | 70.3% | 69.16% | 7.648% | 0% | 0% | 53.37% | 0% | 51% | 47.61% | 27.71% | 19.67% | 0% | 63.93% | 0% | 0% | 13.6% | 44.41% | 17.51% | CZ 4A | 0% | 0% | 0.9962% | 64.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 48.68% | 17.51% | CZ 4A | 70.3% | 69.16% | 3.595% | 64.03% | 0% | 53.37% | 0% | 51% | 47.61% | 27.71% | 19.67% | 0% | 63.93% | 0% | 0% | 13.6% | 45.03% | 17.51%
CZ 4B | 70.51% | 69.33% | 3.743% | 41.97% | 0% | 51.04% | 0% | 48.66% | 100% | -16.94% | 19.45% | 0% | 63.88% | 0% | 0% | 13.6% | 42.71% | 0.665% | CZ 4B | 70.51% | 69.33% | 2.285% | 41.97% | 0% | 51.04% | 0% | 48.66% | 100% | -16.94% | 19.45% | 0% | 63.88% | 0% | 0% | 13.6% | 40.22% | 0.665% | CZ 4B | 70.51% | 69.33% | 7.651% | 0% | 0% | 51.04% | 0% | 48.66% | 100% | -16.94% | 19.45% | 0% | 63.88% | 0% | 0% | 13.6% | 44.5% | 0.665% | CZ 4B | 0% | 0% | 1.029% | 41.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.77% | 0.665% | CZ 4B | 70.51% | 69.33% | 3.654% | 41.97% | 0% | 51.04% | 0% | 48.66% | 100% | -16.94% | 19.45% | 0% | 63.88% | 0% | 0% | 13.6% | 42.62% | 0.665%
CZ 4C | 69.84% | 68.98% | 3.657% | 42.44% | 0% | 65.57% | 0% | 57.73% | 100% | -100% | 19.53% | 0% | 63.92% | 0% | 0% | 13.6% | 44.5% | 1.872% | CZ 4C | 69.84% | 68.98% | 2.198% | 42.44% | 0% | 65.57% | 0% | 57.73% | 100% | -100% | 19.53% | 0% | 63.92% | 0% | 0% | 13.6% | 41.71% | 1.872% | CZ 4C | 69.84% | 68.98% | 7.681% | 0% | 0% | 65.57% | 0% | 57.73% | 100% | -100% | 19.53% | 0% | 63.92% | 0% | 0% | 13.6% | 46.77% | 1.872% | CZ 4C | 0% | 0% | 0.9597% | 42.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.37% | 1.872% | CZ 4C | 69.84% | 68.98% | 3.567% | 42.44% | 0% | 65.57% | 0% | 57.73% | 100% | -100% | 19.53% | 0% | 63.92% | 0% | 0% | 13.6% | 44.39% | 1.872%
CZ 5A | 70.48% | 69.17% | 3.568% | 68.38% | 0% | 52.15% | 0% | 55.32% | 21.38% | 29.65% | 19.49% | 0% | 63.91% | 0% | 0% | 13.6% | 46.11% | 16.48% | CZ 5A | 70.48% | 69.17% | 2.139% | 68.38% | 0% | 52.15% | 0% | 55.32% | 21.38% | 29.65% | 19.49% | 0% | 63.91% | 0% | 0% | 13.6% | 49.11% | 16.48% | CZ 5A | 70.48% | 69.17% | 7.681% | 0% | 0% | 52.15% | 0% | 55.32% | 21.38% | 29.65% | 19.49% | 0% | 63.91% | 0% | 0% | 13.6% | 43.45% | 16.48% | CZ 5A | 0% | 0% | 0.95% | 68.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 56.68% | 16.48% | CZ 5A | 70.48% | 69.17% | 3.479% | 68.38% | 0% | 52.15% | 0% | 55.32% | 21.38% | 29.65% | 19.49% | 0% | 63.91% | 0% | 0% | 13.6% | 46.23% | 16.48%
CZ 5B | 70.44% | 69.21% | 3.588% | 41.86% | 0% | 53.25% | 0% | 50.6% | 100% | -10.18% | 19.34% | 0% | 63.92% | 0% | 0% | 13.6% | 42.75% | 4.56% | CZ 5B | 70.44% | 69.21% | 2.155% | 41.86% | 0% | 53.25% | 0% | 50.6% | 100% | -10.18% | 19.34% | 0% | 63.92% | 0% | 0% | 13.6% | 40.32% | 4.56% | CZ 5B | 70.44% | 69.21% | 7.648% | 0% | 0% | 53.25% | 0% | 50.6% | 100% | -10.18% | 19.34% | 0% | 63.92% | 0% | 0% | 13.6% | 44.72% | 4.56% | CZ 5B | 0% | 0% | 0.9533% | 41.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.92% | 4.56% | CZ 5B | 70.44% | 69.21% | 3.499% | 41.86% | 0% | 53.25% | 0% | 50.6% | 100% | -10.18% | 19.34% | 0% | 63.92% | 0% | 0% | 13.6% | 42.66% | 4.56%
CZ 5C | 70.08% | 68.98% | 3.587% | 63.16% | 0% | 62.61% | 0% | 59.36% | 22.56% | 14.85% | 19.43% | 0% | 63.91% | 0% | 0% | 13.6% | 45.75% | 0.02421% | CZ 5C | 70.08% | 68.98% | 2.144% | 63.16% | 0% | 62.61% | 0% | 59.36% | 22.56% | 14.85% | 19.43% | 0% | 63.91% | 0% | 0% | 13.6% | 47.29% | 0.02421% | CZ 5C | 70.08% | 68.98% | 7.681% | 0% | 0% | 62.61% | 0% | 59.36% | 22.56% | 14.85% | 19.43% | 0% | 63.91% | 0% | 0% | 13.6% | 44.4% | 0.02421% | CZ 5C | 0% | 0% | 0.9352% | 63.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.34% | 0.02421% | CZ 5C | 70.08% | 68.98% | 3.497% | 63.16% | 0% | 62.61% | 0% | 59.36% | 22.56% | 14.85% | 19.43% | 0% | 63.91% | 0% | 0% | 13.6% | 45.81% | 0.02421%
CZ 6A | 70.93% | 69.12% | 3.484% | 67.7% | 0% | 49.4% | 0% | 56.3% | 17.25% | 37.66% | 19.42% | 0% | 63.95% | 0% | 0% | 13.6% | 47.15% | 2.494% | CZ 6A | 70.93% | 69.12% | 2.06% | 67.7% | 0% | 49.4% | 0% | 56.3% | 17.25% | 37.66% | 19.42% | 0% | 63.95% | 0% | 0% | 13.6% | 50.94% | 2.494% | CZ 6A | 70.93% | 69.12% | 7.747% | 0% | 0% | 49.4% | 0% | 56.3% | 17.25% | 37.66% | 19.42% | 0% | 63.95% | 0% | 0% | 13.6% | 43.35% | 2.494% | CZ 6A | 0% | 0% | 0.8975% | 67.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.74% | 2.494% | CZ 6A | 70.93% | 69.12% | 3.395% | 67.7% | 0% | 49.4% | 0% | 56.3% | 17.25% | 37.66% | 19.42% | 0% | 63.95% | 0% | 0% | 13.6% | 47.31% | 2.494%
CZ 6B | 71.08% | 69.05% | 3.501% | 66.07% | 0% | 54.36% | 0% | 53% | 9.998% | 43.03% | 19.22% | 0% | 63.92% | 0% | 0% | 13.6% | 45.62% | 0.6028% | CZ 6B | 71.08% | 69.05% | 2.078% | 66.07% | 0% | 54.36% | 0% | 53% | 9.998% | 43.03% | 19.22% | 0% | 63.92% | 0% | 0% | 13.6% | 48.5% | 0.6028% | CZ 6B | 71.08% | 69.05% | 7.714% | 0% | 0% | 54.36% | 0% | 53% | 9.998% | 43.03% | 19.22% | 0% | 63.92% | 0% | 0% | 13.6% | 42.97% | 0.6028% | CZ 6B | 0% | 0% | 0.9099% | 66.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.26% | 0.6028% | CZ 6B | 71.08% | 69.05% | 3.412% | 66.07% | 0% | 54.36% | 0% | 53% | 9.998% | 43.03% | 19.22% | 0% | 63.92% | 0% | 0% | 13.6% | 45.74% | 0.6028%
CZ 7 | 71.25% | 68.96% | 3.436% | 67.69% | 0% | 50.13% | 0% | 55.86% | 15.31% | 90.57% | 19.36% | 0% | 63.94% | 0% | 0% | 13.6% | 48.13% | 0.3042% | CZ 7 | 71.25% | 68.96% | 2.045% | 67.69% | 0% | 50.13% | 0% | 55.86% | 15.31% | 90.57% | 19.36% | 0% | 63.94% | 0% | 0% | 13.6% | 52.4% | 0.3042% | CZ 7 | 71.25% | 68.96% | 7.78% | 0% | 0% | 50.13% | 0% | 55.86% | 15.31% | 90.57% | 19.36% | 0% | 63.94% | 0% | 0% | 13.6% | 43.4% | 0.3042% | CZ 7 | 0% | 0% | 0.9295% | 67.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.02% | 0.3042% | CZ 7 | 71.25% | 68.96% | 3.348% | 67.69% | 0% | 50.13% | 0% | 55.86% | 15.31% | 90.57% | 19.36% | 0% | 63.94% | 0% | 0% | 13.6% | 48.32% | 0.3042%
CZ 8 | 69.2% | 67.77% | 3.235% | 62.99% | 0% | 59.08% | 0% | 60.94% | 5.206% | 82.37% | 19.31% | 0% | 63.93% | 0% | 0% | 13.6% | 48.57% | 0.05063% | CZ 8 | 69.2% | 67.77% | 1.859% | 62.99% | 0% | 59.08% | 0% | 60.94% | 5.206% | 82.37% | 19.31% | 0% | 63.93% | 0% | 0% | 13.6% | 52.3% | 0.05063% | CZ 8 | 69.2% | 67.77% | 7.744% | 0% | 0% | 59.08% | 0% | 60.94% | 5.206% | 82.37% | 19.31% | 0% | 63.93% | 0% | 0% | 13.6% | 43.56% | 0.05063% | CZ 8 | 0% | 0% | 0.7793% | 62.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.6% | 0.05063% | CZ 8 | 69.2% | 67.77% | 3.147% | 62.99% | 0% | 59.08% | 0% | 60.94% | 5.206% | 82.37% | 19.31% | 0% | 63.93% | 0% | 0% | 13.6% | 48.76% | 0.05063%
US Weighted | 70.07% | 69.21% | 3.8% | 59.33% | 0% | 53.97% | 0% | 53.46% | 45.71% | 18.14% | 19.84% | 0% | 63.92% | 0% | 0% | 13.6% | 45% | 100% | US Weighted | 70.07% | 69.21% | 2.331% | 59.33% | 0% | 53.97% | 0% | 53.46% | 45.71% | 18.14% | 19.84% | 0% | 63.92% | 0% | 0% | 13.6% | 44.62% | 100% | US Weighted | 70.07% | 69.21% | 7.617% | 0% | 0% | 53.97% | 0% | 53.46% | 45.71% | 18.14% | 19.84% | 0% | 63.92% | 0% | 0% | 13.6% | 45.27% | 100% | US Weighted | 0% | 0% | 1.047% | 59.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.96% | 100% | US Weighted | 70.07% | 69.21% | 3.711% | 59.33% | 0% | 53.97% | 0% | 53.46% | 45.71% | 18.14% | 19.84% | 0% | 63.92% | 0% | 0% | 13.6% | 44.99% | 100%

## SchSec
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Secondary School |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Secondary School | [14 empty] | Prototype Floor Area: | 210887 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.12815 | 0.0090796 | 0.04202 | 0.04409 | 0 | 0.19639 | 0 | 0.095701 | 0.024194 | 0.0042554 | 0.02377 | 0.0087798 | 0.0039621 | 0.072419 | 0 | 0.25606 | 0.90888 |  | STD2016 | 4.3177 | 0.30591 | 2.836 | 4.409 | 0 | 6.6168 | 0 | 3.2243 | 0.81514 | 0.14337 | 0.80084 | 0.29581 | 0.13349 | 4.0625 | 0 | 8.6272 | 36.588 |  | STD2016 | 1.2651 | 0.089631 | 0.20338 | 0 | 0 | 1.9387 | 0 | 0.94473 | 0.23884 | 0.042007 | 0.23465 | 0.086671 | 0.039112 | 0.47333 | 0 | 2.5278 | 8.0839 |  | STD2016 | 0 | 0 | 0.021418 | 0.04409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.089978 |  | STD2016 | 13.2442 | 0.93835 | 4.4702 | 4.819 | 0 | 20.2966 | 0 | 9.8904 | 2.5004 | 0.43978 | 2.4565 | 0.90736 | 0.40946 | 7.6299 | 0 | 26.4631 | 94.4653
STD2013 | 0.24658 | 0.015715 | 0.042024 | 0.045064 | 0 | 0.21383 | 0 | 0.10932 | 0.02766 | 0.0058638 | 0.023777 | 0.0087798 | 0.0054567 | 0.072419 | 0 | 0.25606 | 1.0725 |  | STD2013 | 8.3077 | 0.52948 | 2.8363 | 4.5064 | 0 | 7.2043 | 0 | 3.683 | 0.9319 | 0.19756 | 0.80109 | 0.29581 | 0.18385 | 4.0625 | 0 | 8.6272 | 42.1671 |  | STD2013 | 2.4342 | 0.15514 | 0.20337 | 0 | 0 | 2.1108 | 0 | 1.0791 | 0.27305 | 0.057885 | 0.23472 | 0.086671 | 0.053867 | 0.47333 | 0 | 2.5278 | 9.6899 |  | STD2013 | 0 | 0 | 0.021422 | 0.045064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090956 |  | STD2013 | 25.4833 | 1.6241 | 4.4706 | 4.9255 | 0 | 22.0985 | 0 | 11.2974 | 2.8585 | 0.606 | 2.4573 | 0.90736 | 0.56394 | 7.6299 | 0 | 26.4631 | 111.3855
STD2010 | 0.28426 | 0.015715 | 0.042057 | 0.049631 | 0 | 0.29791 | 0 | 0.13697 | 0.032326 | 0.0079145 | 0.02813 | 0.0088025 | 0.005922 | 0.072419 | 0 | 0.28192 | 1.264 |  | STD2010 | 9.5772 | 0.52948 | 2.8385 | 4.9631 | 0 | 10.0371 | 0 | 4.6147 | 1.0891 | 0.26665 | 0.94774 | 0.29657 | 0.19952 | 4.0625 | 0 | 9.4984 | 48.9207 |  | STD2010 | 2.8061 | 0.15514 | 0.20354 | 0 | 0 | 2.9409 | 0 | 1.3521 | 0.31911 | 0.078129 | 0.27769 | 0.086895 | 0.05846 | 0.47333 | 0 | 2.783 | 11.5344 |  | STD2010 | 0 | 0 | 0.021439 | 0.049631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.095541 |  | STD2010 | 29.3774 | 1.6241 | 4.4741 | 5.4247 | 0 | 30.7879 | 0 | 14.1551 | 3.3408 | 0.81793 | 2.9071 | 0.9097 | 0.61202 | 7.6299 | 0 | 29.1356 | 131.1964
STD2007 | 0.43965 | 0.028922 | 0.042081 | 0.077919 | 0 | 0.40373 | 0 | 0.18222 | 0.04763 | 0.022544 | 0.028205 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6492 |  | STD2007 | 14.8126 | 0.97442 | 2.8409 | 7.7919 | 0 | 13.6023 | 0 | 6.1394 | 1.6047 | 0.75954 | 0.95026 | 0.34054 | 0.35679 | 4.0625 | 0 | 9.5412 | 63.777 |  | STD2007 | 4.3401 | 0.28551 | 0.20354 | 0 | 0 | 3.9855 | 0 | 1.7988 | 0.47019 | 0.22254 | 0.27843 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 15.0578 |  | STD2007 | 0 | 0 | 0.021462 | 0.077919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12385 |  | STD2007 | 45.4364 | 2.989 | 4.4767 | 8.5166 | 0 | 41.7238 | 0 | 18.832 | 4.9224 | 2.3298 | 2.9148 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 171.1773
STD2004 | 0.43965 | 0.028922 | 0.042086 | 0.10791 | 0 | 0.44641 | 0 | 0.24316 | 0.073218 | 0.024298 | 0.0282 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.8102 |  | STD2004 | 14.8126 | 0.97442 | 2.8414 | 10.7907 | 0 | 15.0403 | 0 | 8.1925 | 2.4668 | 0.81864 | 0.95009 | 0.34054 | 0.3568 | 4.0625 | 0 | 9.5412 | 71.1886 |  | STD2004 | 4.3401 | 0.28551 | 0.20355 | 0 | 0 | 4.4068 | 0 | 2.4004 | 0.72279 | 0.23986 | 0.27838 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 16.3506 |  | STD2004 | 0 | 0 | 0.021467 | 0.10791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15384 |  | STD2004 | 45.4364 | 2.989 | 4.4772 | 11.7943 | 0 | 46.1348 | 0 | 25.1299 | 7.5668 | 2.5111 | 2.9143 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 187.9898
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 5.2372e-06 | 0.029988 | 0 | 0.042682 | 0 | 0.06094 | 0.025588 | 0.0017542 | -4.9775e-06 | 0 | 3.0322e-07 | 0 | 0 | 0 | 0.16095 |  | 2004-2007 | 0 | 0 | 0.00050426 | 2.9988 | 0 | 1.438 | 0 | 2.0532 | 0.8621 | 0.059102 | -0.0001677 | 0 | 1.0216e-05 | 0 | 0 | 0 | 7.4116 |  | 2004-2007 | 0 | 0 | 2.8974e-06 | 0 | 0 | 0.42134 | 0 | 0.60158 | 0.2526 | 0.017317 | -4.9136e-05 | 0 | 2.9933e-06 | 0 | 0 | 0 | 1.2928 |  | 2004-2007 | 0 | 0 | 4.9437e-06 | 0.029988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029993 |  | 2004-2007 | 0 | 0 | 0.00057068 | 3.2777 | 0 | 4.411 | 0 | 6.298 | 2.6444 | 0.18129 | -0.0005144 | 0 | 3.1337e-05 | 0 | 0 | 0 | 16.8125
2007-2010 | 0.15539 | 0.013206 | 2.3441e-05 | 0.028288 | 0 | 0.10582 | 0 | 0.045254 | 0.015304 | 0.014629 | 7.4775e-05 | 0.001305 | 0.0046678 | 0 | 0 | 0.0012716 | 0.38523 |  | 2007-2010 | 5.2354 | 0.44494 | 0.0023121 | 2.8288 | 0 | 3.5652 | 0 | 1.5247 | 0.51562 | 0.49288 | 0.0025193 | 0.043966 | 0.15727 | 0 | 0 | 0.042842 | 14.8564 |  | 2007-2010 | 1.534 | 0.13037 | 4.7648e-06 | 0 | 0 | 1.0446 | 0 | 0.44674 | 0.15108 | 0.14441 | 0.00073815 | 0.012882 | 0.046079 | 0 | 0 | 0.012553 | 3.5234 |  | 2007-2010 | 0 | 0 | 2.2959e-05 | 0.028288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028311 |  | 2007-2010 | 16.0591 | 1.3648 | 0.0025593 | 3.0918 | 0 | 10.9359 | 0 | 4.6769 | 1.5816 | 1.5119 | 0.0077277 | 0.13486 | 0.4824 | 0 | 0 | 0.13142 | 39.981
2010-2013 | 0.03768 | 0 | 3.2989e-05 | 0.0045678 | 0 | 0.084081 | 0 | 0.027651 | 0.0046665 | 0.0020507 | 0.0043528 | 2.2683e-05 | 0.00046524 | 0 | 0 | 0.025859 | 0.19143 |  | 2010-2013 | 1.2695 | 0 | 0.0021999 | 0.45678 | 0 | 2.8328 | 0 | 0.93162 | 0.15722 | 0.069091 | 0.14665 | 0.00076424 | 0.015675 | 0 | 0 | 0.87123 | 6.7536 |  | 2010-2013 | 0.37196 | 0 | 0.00016361 | 0 | 0 | 0.83002 | 0 | 0.27296 | 0.046066 | 0.020244 | 0.04297 | 0.00022392 | 0.0045927 | 0 | 0 | 0.25527 | 1.8445 |  | 2010-2013 | 0 | 0 | 1.6415e-05 | 0.0045678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045842 |  | 2010-2013 | 3.8941 | 0 | 0.003507 | 0.49926 | 0 | 8.6895 | 0 | 2.8577 | 0.48227 | 0.21193 | 0.44985 | 0.0023442 | 0.048081 | 0 | 0 | 2.6724 | 19.8109
2013-2016 | 0.11843 | 0.0066358 | 3.7003e-06 | 0.00097396 | 0 | 0.017435 | 0 | 0.013615 | 0.0034653 | 0.0016084 | 7.299e-06 | 0 | 0.0014947 | 0 | 0 | 0 | 0.16367 |  | 2013-2016 | 3.99 | 0.22357 | 0.0003884 | 0.097396 | 0 | 0.58742 | 0 | 0.45871 | 0.11675 | 0.054191 | 0.00024592 | 0 | 0.050359 | 0 | 0 | 0 | 5.5791 |  | 2013-2016 | 1.1691 | 0.065506 | -2.7345e-06 | 0 | 0 | 0.17211 | 0 | 0.1344 | 0.034209 | 0.015878 | 7.2053e-05 | 0 | 0.014755 | 0 | 0 | 0 | 1.606 |  | 2013-2016 | 0 | 0 | 3.9773e-06 | 0.00097396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00097793 |  | 2013-2016 | 12.2391 | 0.68579 | 0.00040609 | 0.10645 | 0 | 1.8019 | 0 | 1.407 | 0.35813 | 0.16623 | 0.00075433 | 0 | 0.15447 | 0 | 0 | 0 | 16.9202
2004-2016 | 0.3115 | 0.019842 | 6.5368e-05 | 0.063818 | 0 | 0.25002 | 0 | 0.14746 | 0.049024 | 0.020043 | 0.0044299 | 0.0013276 | 0.006628 | 0 | 0 | 0.027131 | 0.90128 |  | 2004-2016 | 10.4949 | 0.66851 | 0.0054047 | 6.3818 | 0 | 8.4234 | 0 | 4.9682 | 1.6517 | 0.67527 | 0.14925 | 0.04473 | 0.22331 | 0 | 0 | 0.91407 | 34.6006 |  | 2004-2016 | 3.075 | 0.19587 | 0.00016854 | 0 | 0 | 2.4681 | 0 | 1.4557 | 0.48395 | 0.19785 | 0.043731 | 0.013106 | 0.06543 | 0 | 0 | 0.26782 | 8.2667 |  | 2004-2016 | 0 | 0 | 4.8294e-05 | 0.063818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063866 |  | 2004-2016 | 32.1922 | 2.0506 | 0.007043 | 6.9753 | 0 | 25.8382 | 0 | 15.2395 | 5.0665 | 2.0713 | 0.45782 | 0.13721 | 0.68498 | 0 | 0 | 2.8038 | 93.5245
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.01244% | 27.79% |  | 9.561% |  | 25.06% | 34.95% | 7.22% | -0.01765% | 0% | 0.002863% | 0% |  | 0% | 8.892% |  | 2004-2007 | 0% | 0% | 0.01775% | 27.79% |  | 9.561% |  | 25.06% | 34.95% | 7.22% | -0.01765% | 0% | 0.002863% | 0% |  | 0% | 10.41% |  | 2004-2007 | 0% | 0% | 0.001423% |  |  | 9.561% |  | 25.06% | 34.95% | 7.22% | -0.01765% | 0% | 0.002863% | 0% |  | 0% | 7.907% |  | 2004-2007 |  |  | 0.02303% | 27.79% | [9 empty] | 0% |  |  | 19.5% |  | 2004-2007 | 0% | 0% | 0.01275% | 27.79% |  | 9.561% |  | 25.06% | 34.95% | 7.22% | -0.01765% | 0% | 0.002863% | 0% |  | 0% | 8.943%
2007-2010 | 35.34% | 45.66% | 0.05571% | 36.3% |  | 26.21% |  | 24.83% | 32.13% | 64.89% | 0.2651% | 12.91% | 44.08% | 0% |  | 0.449% | 23.36% |  | 2007-2010 | 35.34% | 45.66% | 0.08139% | 36.3% |  | 26.21% |  | 24.83% | 32.13% | 64.89% | 0.2651% | 12.91% | 44.08% | 0% |  | 0.449% | 23.29% |  | 2007-2010 | 35.34% | 45.66% | 0.002341% |  |  | 26.21% |  | 24.83% | 32.13% | 64.89% | 0.2651% | 12.91% | 44.08% | 0% |  | 0.449% | 23.4% |  | 2007-2010 |  |  | 0.107% | 36.3% | [9 empty] | 0% |  |  | 22.86% |  | 2007-2010 | 35.34% | 45.66% | 0.05717% | 36.3% |  | 26.21% |  | 24.83% | 32.13% | 64.89% | 0.2651% | 12.91% | 44.08% | 0% |  | 0.449% | 23.36%
2010-2013 | 13.26% | 0% | 0.07844% | 9.203% |  | 28.22% |  | 20.19% | 14.44% | 25.91% | 15.47% | 0.2577% | 7.856% | 0% |  | 9.172% | 15.15% |  | 2010-2013 | 13.26% | 0% | 0.0775% | 9.203% |  | 28.22% |  | 20.19% | 14.44% | 25.91% | 15.47% | 0.2577% | 7.856% | 0% |  | 9.172% | 13.81% |  | 2010-2013 | 13.26% | 0% | 0.08038% |  |  | 28.22% |  | 20.19% | 14.44% | 25.91% | 15.47% | 0.2577% | 7.856% | 0% |  | 9.172% | 15.99% |  | 2010-2013 |  |  | 0.07657% | 9.203% | [9 empty] | 0% |  |  | 4.798% |  | 2010-2013 | 13.26% | 0% | 0.07838% | 9.203% |  | 28.22% |  | 20.19% | 14.44% | 25.91% | 15.47% | 0.2577% | 7.856% | 0% |  | 9.172% | 15.1%
2013-2016 | 48.03% | 42.22% | 0.008805% | 2.161% |  | 8.154% |  | 12.45% | 12.53% | 27.43% | 0.0307% | 0% | 27.39% | 0% |  | 0% | 15.26% |  | 2013-2016 | 48.03% | 42.22% | 0.01369% | 2.161% |  | 8.154% |  | 12.45% | 12.53% | 27.43% | 0.0307% | 0% | 27.39% | 0% |  | 0% | 13.23% |  | 2013-2016 | 48.03% | 42.22% | -0.001345% |  |  | 8.154% |  | 12.45% | 12.53% | 27.43% | 0.0307% | 0% | 27.39% | 0% |  | 0% | 16.57% |  | 2013-2016 |  |  | 0.01857% | 2.161% | [9 empty] | 0% |  |  | 1.075% |  | 2013-2016 | 48.03% | 42.22% | 0.009084% | 2.161% |  | 8.154% |  | 12.45% | 12.53% | 27.43% | 0.0307% | 0% | 27.39% | 0% |  | 0% | 15.19%
2004-2016 | 70.85% | 68.61% | 0.1553% | 59.14% |  | 56.01% |  | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% |  | 9.58% | 49.79% |  | 2004-2016 | 70.85% | 68.61% | 0.1902% | 59.14% |  | 56.01% |  | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% |  | 9.58% | 48.6% |  | 2004-2016 | 70.85% | 68.61% | 0.0828% |  |  | 56.01% |  | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% |  | 9.58% | 50.56% |  | 2004-2016 |  |  | 0.225% | 59.14% | [9 empty] | 0% |  |  | 41.51% |  | 2004-2016 | 70.85% | 68.61% | 0.1573% | 59.14% |  | 56.01% |  | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% |  | 9.58% | 49.75%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.12768 | 0.0090773 | 0.03661 | 0.0074882 | 0 | 0.41568 | 0 | 0.10668 | 0.043731 | 0.0069331 | 0.023902 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 1.119 | 3.045% | CZ 1A | 4.3019 | 0.30583 | 2.2949 | 0.74882 | 0 | 14.0049 | 0 | 3.5944 | 1.4734 | 0.23359 | 0.80528 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 40.8819 | 3.045% | CZ 1A | 1.2604 | 0.089608 | 0.20337 | 0 | 0 | 4.1034 | 0 | 1.0532 | 0.4317 | 0.068441 | 0.23595 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 10.573 | 3.045% | CZ 1A | 0 | 0 | 0.016008 | 0.0074882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.047967 | 3.045% | CZ 1A | 13.1956 | 0.93811 | 3.8788 | 0.81846 | 0 | 42.9587 | 0 | 11.0255 | 4.5194 | 0.71651 | 2.4701 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 115.9312 | 3.045%
CZ 1B | 0.12606 | 0.0090613 | 0.037202 | 0.013321 | 0 | 0.51407 | 0 | 0.13006 | 0.035082 | 0.0068584 | 0.023873 | 0.0087798 | 0.0039602 | 0.072419 | 0 | 0.25606 | 1.2368 | 0% | CZ 1B | 4.2471 | 0.30529 | 2.3541 | 1.3321 | 0 | 17.3198 | 0 | 4.3818 | 1.182 | 0.23107 | 0.80434 | 0.29581 | 0.13343 | 4.0625 | 0 | 8.6272 | 45.2764 | 0% | CZ 1B | 1.2444 | 0.08945 | 0.20337 | 0 | 0 | 5.0747 | 0 | 1.2839 | 0.34632 | 0.067703 | 0.23567 | 0.086671 | 0.039094 | 0.47333 | 0 | 2.5278 | 11.6723 | 0% | CZ 1B | 0 | 0 | 0.0166 | 0.013321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.054391 | 0% | CZ 1B | 13.0278 | 0.93645 | 3.9435 | 1.4559 | 0 | 53.1269 | 0 | 13.4408 | 3.6256 | 0.70879 | 2.4672 | 0.90736 | 0.40928 | 7.6299 | 0 | 26.4631 | 128.1427 | 0%
CZ 2A | 0.12709 | 0.009056 | 0.038414 | 0.01643 | 0 | 0.35895 | 0 | 0.099809 | 0.029386 | 0.0065248 | 0.023886 | 0.0087798 | 0.0039602 | 0.072419 | 0 | 0.25606 | 1.0508 | 15.33% | CZ 2A | 4.2819 | 0.30511 | 2.4753 | 1.643 | 0 | 12.0936 | 0 | 3.3627 | 0.99005 | 0.21983 | 0.80474 | 0.29581 | 0.13343 | 4.0625 | 0 | 8.6272 | 39.2952 | 15.33% | CZ 2A | 1.2546 | 0.089398 | 0.20337 | 0 | 0 | 3.5434 | 0 | 0.98528 | 0.29008 | 0.06441 | 0.23579 | 0.086671 | 0.039094 | 0.47333 | 0 | 2.5278 | 9.7932 | 15.33% | CZ 2A | 0 | 0 | 0.017812 | 0.01643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.058713 | 15.33% | CZ 2A | 13.1344 | 0.9359 | 4.076 | 1.7958 | 0 | 37.0962 | 0 | 10.3149 | 3.0369 | 0.67431 | 2.4685 | 0.90736 | 0.40928 | 7.6299 | 0 | 26.4631 | 108.9426 | 15.33%
CZ 2B | 0.12973 | 0.0090653 | 0.038672 | 0.015626 | 0 | 0.27732 | 0 | 0.10264 | 0.024647 | 0.0050637 | 0.023731 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.96771 | 2.216% | CZ 2B | 4.3708 | 0.30543 | 2.5011 | 1.5626 | 0 | 9.3432 | 0 | 3.4581 | 0.83041 | 0.17061 | 0.79953 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 36.4608 | 2.216% | CZ 2B | 1.2806 | 0.08949 | 0.20337 | 0 | 0 | 2.7376 | 0 | 1.0132 | 0.24331 | 0.049987 | 0.23426 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 8.9787 | 2.216% | CZ 2B | 0 | 0 | 0.01807 | 0.015626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.058167 | 2.216% | CZ 2B | 13.407 | 0.93687 | 4.1042 | 1.7079 | 0 | 28.6596 | 0 | 10.6074 | 2.5472 | 0.52332 | 2.4525 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 100.356 | 2.216%
CZ 3A | 0.13023 | 0.009064 | 0.041144 | 0.035462 | 0 | 0.22008 | 0 | 0.092486 | 0.02506 | 0.0047328 | 0.023793 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.92328 | 19.18% | CZ 3A | 4.3876 | 0.30538 | 2.7484 | 3.5462 | 0 | 7.4149 | 0 | 3.116 | 0.8443 | 0.15946 | 0.80164 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 36.4429 | 19.18% | CZ 3A | 1.2856 | 0.089477 | 0.20337 | 0 | 0 | 2.1726 | 0 | 0.913 | 0.24738 | 0.046721 | 0.23488 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 8.3198 | 19.18% | CZ 3A | 0 | 0 | 0.020543 | 0.035462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.080475 | 19.18% | CZ 3A | 13.4585 | 0.93673 | 4.3744 | 3.876 | 0 | 22.7446 | 0 | 9.5582 | 2.5898 | 0.48912 | 2.459 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 95.8964 | 19.18%
CZ 3B | 0.13146 | 0.0090626 | 0.040472 | 0.03745 | 0 | 0.21092 | 0 | 0.10115 | 0 | 0.0051384 | 0.023729 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.9006 | 7.906% | CZ 3B | 4.4291 | 0.30534 | 2.6811 | 3.745 | 0 | 7.1062 | 0 | 3.4078 | 0 | 0.17312 | 0.79948 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 35.7662 | 7.906% | CZ 3B | 1.2977 | 0.089463 | 0.20337 | 0 | 0 | 2.0821 | 0 | 0.99848 | 0 | 0.050725 | 0.23425 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 8.083 | 7.906% | CZ 3B | 0 | 0 | 0.01987 | 0.03745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081791 | 7.906% | CZ 3B | 13.586 | 0.93659 | 4.3009 | 4.0933 | 0 | 21.7977 | 0 | 10.4531 | 0 | 0.53104 | 2.4523 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 93.5609 | 7.906%
CZ 3C | 0.13119 | 0.0090947 | 0.040984 | 0.02915 | 0 | 0.14207 | 0 | 0.091697 | 0 | 0.0029982 | 0.023777 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.81219 | 1.057% | CZ 3C | 4.42 | 0.30641 | 2.7323 | 2.915 | 0 | 4.7867 | 0 | 3.0894 | 0 | 0.10101 | 0.8011 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 32.271 | 1.057% | CZ 3C | 1.2951 | 0.08978 | 0.20337 | 0 | 0 | 1.4025 | 0 | 0.9052 | 0 | 0.029597 | 0.23472 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 7.2871 | 1.057% | CZ 3C | 0 | 0 | 0.020382 | 0.02915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.074003 | 1.057% | CZ 3C | 13.5581 | 0.9399 | 4.3569 | 3.1861 | 0 | 14.6828 | 0 | 9.4765 | 0 | 0.30985 | 2.4573 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 84.3775 | 1.057%
CZ 4A | 0.12746 | 0.0091107 | 0.04313 | 0.038624 | 0 | 0.15892 | 0 | 0.094142 | 0.030494 | 0.0037708 | 0.023753 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.87063 | 18.98% | CZ 4A | 4.2942 | 0.30695 | 2.9469 | 3.8624 | 0 | 5.3544 | 0 | 3.1718 | 1.0274 | 0.12704 | 0.80029 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 35.0104 | 18.98% | CZ 4A | 1.2582 | 0.089938 | 0.20337 | 0 | 0 | 1.5688 | 0 | 0.92934 | 0.30103 | 0.037224 | 0.23449 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 7.7493 | 18.98% | CZ 4A | 0 | 0 | 0.022528 | 0.038624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.085622 | 18.98% | CZ 4A | 13.1721 | 0.94156 | 4.5914 | 4.2216 | 0 | 16.4243 | 0 | 9.7293 | 3.1515 | 0.3897 | 2.4548 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 90.4862 | 18.98%
CZ 4B | 0.12657 | 0.0090626 | 0.042542 | 0.065916 | 0 | 0.14848 | 0 | 0.10791 | 0 | 0.0046207 | 0.023711 | 0.0087798 | 0.0039616 | 0.072419 | 0 | 0.25606 | 0.87004 | 0.5989% | CZ 4B | 4.2644 | 0.30534 | 2.8881 | 6.5916 | 0 | 5.0027 | 0 | 3.6357 | 0 | 0.15568 | 0.79885 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 36.7613 | 0.5989% | CZ 4B | 1.2495 | 0.089463 | 0.20337 | 0 | 0 | 1.4658 | 0 | 1.0653 | 0 | 0.045614 | 0.23406 | 0.086671 | 0.039107 | 0.47333 | 0 | 2.5278 | 7.4799 | 0.5989% | CZ 4B | 0 | 0 | 0.02194 | 0.065916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11233 | 0.5989% | CZ 4B | 13.0806 | 0.93659 | 4.5272 | 7.2046 | 0 | 15.3454 | 0 | 11.1522 | 0 | 0.47754 | 2.4504 | 0.90736 | 0.40941 | 7.6299 | 0 | 26.4631 | 90.5844 | 0.5989%
CZ 4C | 0.12981 | 0.0091173 | 0.043444 | 0.091713 | 0 | 0.06085 | 0 | 0.084515 | 0 | 0.0014864 | 0.023728 | 0.0087798 | 0.0039629 | 0.072419 | 0 | 0.25606 | 0.78589 | 2.262% | CZ 4C | 4.3735 | 0.30718 | 2.9784 | 9.1713 | 0 | 2.0501 | 0 | 2.8475 | 0 | 0.05008 | 0.79944 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 35.6965 | 2.262% | CZ 4C | 1.2814 | 0.090003 | 0.20337 | 0 | 0 | 0.60069 | 0 | 0.83431 | 0 | 0.014673 | 0.23424 | 0.086671 | 0.03912 | 0.47333 | 0 | 2.5278 | 6.3856 | 2.262% | CZ 4C | 0 | 0 | 0.022842 | 0.091713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.13903 | 2.262% | CZ 4C | 13.4154 | 0.94225 | 4.6258 | 10.0242 | 0 | 6.2886 | 0 | 8.7344 | 0 | 0.15362 | 2.4522 | 0.90736 | 0.40955 | 7.6299 | 0 | 26.4631 | 82.0464 | 2.262%
CZ 5A | 0.12675 | 0.0090787 | 0.044761 | 0.058294 | 0 | 0.099462 | 0 | 0.091719 | 0.028218 | 0.002706 | 0.023717 | 0.0087798 | 0.0039616 | 0.072419 | 0 | 0.25606 | 0.82593 | 20.76% | CZ 5A | 4.2706 | 0.30588 | 3.11 | 5.8294 | 0 | 3.3511 | 0 | 3.0902 | 0.95071 | 0.091169 | 0.79908 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 34.9169 | 20.76% | CZ 5A | 1.2513 | 0.089621 | 0.20339 | 0 | 0 | 0.98186 | 0 | 0.90542 | 0.27856 | 0.026713 | 0.23413 | 0.086671 | 0.039107 | 0.47333 | 0 | 2.5278 | 7.0978 | 20.76% | CZ 5A | 0 | 0 | 0.024158 | 0.058294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10692 | 20.76% | CZ 5A | 13.0996 | 0.93825 | 4.7697 | 6.3715 | 0 | 10.2791 | 0 | 9.4789 | 2.9162 | 0.27965 | 2.4511 | 0.90736 | 0.40941 | 7.6299 | 0 | 26.4631 | 85.9938 | 20.76%
CZ 5B | 0.12713 | 0.0090987 | 0.04425 | 0.11344 | 0 | 0.11021 | 0 | 0.10302 | 0 | 0.0026233 | 0.023691 | 0.0087798 | 0.0039616 | 0.072419 | 0 | 0.25606 | 0.87468 | 4.314% | CZ 5B | 4.2832 | 0.30655 | 3.0589 | 11.3437 | 0 | 3.713 | 0 | 3.471 | 0 | 0.088382 | 0.79818 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 40.1819 | 4.314% | CZ 5B | 1.255 | 0.089819 | 0.20337 | 0 | 0 | 1.0879 | 0 | 1.017 | 0 | 0.025896 | 0.23387 | 0.086671 | 0.039107 | 0.47333 | 0 | 2.5278 | 7.0397 | 4.314% | CZ 5B | 0 | 0 | 0.023648 | 0.11344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.16156 | 4.314% | CZ 5B | 13.1382 | 0.94032 | 4.7139 | 12.3986 | 0 | 11.3894 | 0 | 10.6471 | 0 | 0.2711 | 2.4484 | 0.90736 | 0.40941 | 7.6299 | 0 | 26.4631 | 91.3569 | 4.314%
CZ 5C | 0.12877 | 0.0091107 | 0.04432 | 0.04989 | 0 | 0.040442 | 0 | 0.083533 | 0.025002 | 0.0015558 | 0.023716 | 0.0087798 | 0.0039602 | 0.072419 | 0 | 0.25606 | 0.74756 | 0.08114% | CZ 5C | 4.3385 | 0.30695 | 3.0659 | 4.989 | 0 | 1.3625 | 0 | 2.8144 | 0.84237 | 0.052418 | 0.79903 | 0.29581 | 0.13343 | 4.0625 | 0 | 8.6272 | 31.6901 | 0.08114% | CZ 5C | 1.2712 | 0.089938 | 0.20337 | 0 | 0 | 0.39923 | 0 | 0.82461 | 0.24681 | 0.015358 | 0.23412 | 0.086671 | 0.039094 | 0.47333 | 0 | 2.5278 | 6.4115 | 0.08114% | CZ 5C | 0 | 0 | 0.023718 | 0.04989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.098079 | 0.08114% | CZ 5C | 13.308 | 0.94156 | 4.7215 | 5.453 | 0 | 4.1795 | 0 | 8.6329 | 2.5839 | 0.16079 | 2.451 | 0.90736 | 0.40928 | 7.6299 | 0 | 26.4631 | 77.8418 | 0.08114%
CZ 6A | 0.12556 | 0.0090933 | 0.046087 | 0.095806 | 0 | 0.11135 | 0 | 0.098359 | 0.031081 | 0.0031343 | 0.023697 | 0.0087798 | 0.0039602 | 0.072419 | 0 | 0.25606 | 0.88539 | 2.944% | CZ 6A | 4.2303 | 0.30637 | 3.2425 | 9.5806 | 0 | 3.7517 | 0 | 3.3139 | 1.0472 | 0.1056 | 0.7984 | 0.29581 | 0.13343 | 4.0625 | 0 | 8.6272 | 39.4954 | 2.944% | CZ 6A | 1.2395 | 0.089766 | 0.20339 | 0 | 0 | 1.0992 | 0 | 0.97096 | 0.30683 | 0.030941 | 0.23393 | 0.086671 | 0.039094 | 0.47333 | 0 | 2.5278 | 7.3014 | 2.944% | CZ 6A | 0 | 0 | 0.025484 | 0.095806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14576 | 2.944% | CZ 6A | 12.9761 | 0.93976 | 4.9146 | 10.4715 | 0 | 11.508 | 0 | 10.165 | 3.2122 | 0.32392 | 2.449 | 0.90736 | 0.40928 | 7.6299 | 0 | 26.4631 | 92.3699 | 2.944%
CZ 6B | 0.12515 | 0.009084 | 0.04571 | 0.069808 | 0 | 0.075385 | 0 | 0.097902 | 0.032551 | 0.0023377 | 0.023652 | 0.0087798 | 0.0039616 | 0.072419 | 0 | 0.25606 | 0.8228 | 0.7512% | CZ 6B | 4.2166 | 0.30606 | 3.2048 | 6.9808 | 0 | 2.5398 | 0 | 3.2985 | 1.0967 | 0.078762 | 0.79688 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 35.6379 | 0.7512% | CZ 6B | 1.2355 | 0.089674 | 0.20339 | 0 | 0 | 0.74417 | 0 | 0.96646 | 0.32133 | 0.023077 | 0.23348 | 0.086671 | 0.039107 | 0.47333 | 0 | 2.5278 | 6.9439 | 0.7512% | CZ 6B | 0 | 0 | 0.025107 | 0.069808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11939 | 0.7512% | CZ 6B | 12.934 | 0.9388 | 4.8734 | 7.6301 | 0 | 7.7907 | 0 | 10.1179 | 3.364 | 0.24159 | 2.4444 | 0.90736 | 0.40941 | 7.6299 | 0 | 26.4631 | 85.7446 | 0.7512%
CZ 7 | 0.12488 | 0.0091147 | 0.047523 | 0.11692 | 0 | 0.087163 | 0 | 0.09786 | 0.030844 | 0.0042738 | 0.023657 | 0.0087798 | 0.0039616 | 0.072419 | 0 | 0.25606 | 0.88345 | 0.4899% | CZ 7 | 4.2073 | 0.30709 | 3.3861 | 11.6921 | 0 | 2.9367 | 0 | 3.2971 | 1.0392 | 0.14399 | 0.79706 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 40.9255 | 0.4899% | CZ 7 | 1.2327 | 0.089977 | 0.20339 | 0 | 0 | 0.86044 | 0 | 0.96604 | 0.30448 | 0.04219 | 0.23354 | 0.086671 | 0.039107 | 0.47333 | 0 | 2.5278 | 7.0597 | 0.4899% | CZ 7 | 0 | 0 | 0.02692 | 0.11692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.16831 | 0.4899% | CZ 7 | 12.9054 | 0.94197 | 5.0716 | 12.7794 | 0 | 9.0079 | 0 | 10.1135 | 3.1876 | 0.44168 | 2.4449 | 0.90736 | 0.40941 | 7.6299 | 0 | 26.4631 | 92.3039 | 0.4899%
CZ 8 | 0.13407 | 0.0094629 | 0.049279 | 0.20961 | 0 | 0.037367 | 0 | 0.097672 | 0.033392 | 0.0024324 | 0.023587 | 0.0087798 | 0.0039669 | 0.072419 | 0 | 0.25606 | 0.9381 | 0.08174% | CZ 8 | 4.5172 | 0.31882 | 3.5616 | 20.9608 | 0 | 1.259 | 0 | 3.2907 | 1.125 | 0.081953 | 0.79467 | 0.29581 | 0.13365 | 4.0625 | 0 | 8.6272 | 49.029 | 0.08174% | CZ 8 | 1.3235 | 0.093415 | 0.2034 | 0 | 0 | 0.36888 | 0 | 0.96418 | 0.32964 | 0.024012 | 0.23284 | 0.086671 | 0.03916 | 0.47333 | 0 | 2.5278 | 6.6668 | 0.08174% | CZ 8 | 0 | 0 | 0.028674 | 0.20961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.26275 | 0.08174% | CZ 8 | 13.8561 | 0.97796 | 5.2635 | 22.9102 | 0 | 3.8618 | 0 | 10.094 | 3.451 | 0.25139 | 2.4376 | 0.90736 | 0.40997 | 7.6299 | 0 | 26.4631 | 98.5139 | 0.08174%
US Weighted | 0.12815 | 0.0090796 | 0.04202 | 0.04409 | 0 | 0.19639 | 0 | 0.095701 | 0.024194 | 0.0042554 | 0.02377 | 0.0087798 | 0.0039621 | 0.072419 | 0 | 0.25606 | 0.90888 | 100% | US Weighted | 4.3177 | 0.30591 | 2.836 | 4.409 | 0 | 6.6168 | 0 | 3.2243 | 0.81514 | 0.14337 | 0.80084 | 0.29581 | 0.13349 | 4.0625 | 0 | 8.6272 | 36.588 | 100% | US Weighted | 1.2651 | 0.089631 | 0.20338 | 0 | 0 | 1.9387 | 0 | 0.94473 | 0.23884 | 0.042007 | 0.23465 | 0.086671 | 0.039112 | 0.47333 | 0 | 2.5278 | 8.0839 | 100% | US Weighted | 0 | 0 | 0.021418 | 0.04409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.089978 | 100% | US Weighted | 13.2442 | 0.93835 | 4.4702 | 4.819 | 0 | 20.2966 | 0 | 9.8904 | 2.5004 | 0.43978 | 2.4565 | 0.90736 | 0.40946 | 7.6299 | 0 | 26.4631 | 94.4653 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.24261 | 0.015728 | 0.036615 | 0.0068963 | 0 | 0.44418 | 0 | 0.10489 | 0.045528 | 0.0092841 | 0.023919 | 0.0087798 | 0.005452 | 0.072419 | 0 | 0.25606 | 1.2724 | 3.045% | CZ 1A | 8.1739 | 0.52989 | 2.2954 | 0.68963 | 0 | 14.9651 | 0 | 3.5338 | 1.5339 | 0.3128 | 0.80587 | 0.29581 | 0.18369 | 4.0625 | 0 | 8.6272 | 46.0095 | 3.045% | CZ 1A | 2.395 | 0.15526 | 0.20337 | 0 | 0 | 4.3848 | 0 | 1.0354 | 0.44944 | 0.09165 | 0.23612 | 0.086671 | 0.05382 | 0.47333 | 0 | 2.5278 | 12.0926 | 3.045% | CZ 1A | 0 | 0 | 0.016013 | 0.0068963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.047379 | 3.045% | CZ 1A | 25.0727 | 1.6254 | 3.8793 | 0.75376 | 0 | 45.9043 | 0 | 10.8396 | 4.7052 | 0.95948 | 2.4719 | 0.90736 | 0.56344 | 7.6299 | 0 | 26.4631 | 131.7756 | 3.045%
CZ 1B | 0.2415 | 0.015704 | 0.037206 | 0.012743 | 0 | 0.54566 | 0 | 0.13531 | 0.036516 | 0.0088838 | 0.023886 | 0.0087798 | 0.0054547 | 0.072419 | 0 | 0.25606 | 1.4001 | 0% | CZ 1B | 8.1364 | 0.52908 | 2.3545 | 1.2743 | 0 | 18.3843 | 0 | 4.559 | 1.2303 | 0.29931 | 0.80474 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 50.7411 | 0% | CZ 1B | 2.384 | 0.15502 | 0.20337 | 0 | 0 | 5.3866 | 0 | 1.3358 | 0.36047 | 0.087698 | 0.23579 | 0.086671 | 0.053847 | 0.47333 | 0 | 2.5278 | 13.2903 | 0% | CZ 1B | 0 | 0 | 0.016604 | 0.012743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.053817 | 0% | CZ 1B | 24.9577 | 1.6229 | 3.9439 | 1.3928 | 0 | 56.3925 | 0 | 13.9842 | 3.7738 | 0.91811 | 2.4685 | 0.90736 | 0.56372 | 7.6299 | 0 | 26.4631 | 145.0185 | 0%
CZ 2A | 0.24337 | 0.015697 | 0.038417 | 0.015882 | 0 | 0.38403 | 0 | 0.10523 | 0.029978 | 0.0086623 | 0.023899 | 0.0087798 | 0.0054547 | 0.072419 | 0 | 0.25606 | 1.2079 | 15.33% | CZ 2A | 8.1996 | 0.52885 | 2.4756 | 1.5882 | 0 | 12.9387 | 0 | 3.5454 | 1.01 | 0.29185 | 0.80519 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 44.5527 | 15.33% | CZ 2A | 2.4025 | 0.15495 | 0.20337 | 0 | 0 | 3.791 | 0 | 1.0388 | 0.29593 | 0.085512 | 0.23592 | 0.086671 | 0.053847 | 0.47333 | 0 | 2.5278 | 11.3496 | 15.33% | CZ 2A | 0 | 0 | 0.017815 | 0.015882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.058167 | 15.33% | CZ 2A | 25.1516 | 1.6222 | 4.0763 | 1.7359 | 0 | 39.6884 | 0 | 10.8752 | 3.0981 | 0.89522 | 2.4699 | 0.90736 | 0.56372 | 7.6299 | 0 | 26.4631 | 125.1769 | 15.33%
CZ 2B | 0.24731 | 0.01571 | 0.038676 | 0.016479 | 0 | 0.2964 | 0 | 0.1114 | 0.024982 | 0.0066275 | 0.023737 | 0.0087798 | 0.005456 | 0.072419 | 0 | 0.25606 | 1.124 | 2.216% | CZ 2B | 8.3324 | 0.5293 | 2.5015 | 1.6479 | 0 | 9.9862 | 0 | 3.7534 | 0.8417 | 0.22329 | 0.79975 | 0.29581 | 0.18382 | 4.0625 | 0 | 8.6272 | 41.7847 | 2.216% | CZ 2B | 2.4414 | 0.15509 | 0.20337 | 0 | 0 | 2.9259 | 0 | 1.0997 | 0.24662 | 0.065425 | 0.23433 | 0.086671 | 0.05386 | 0.47333 | 0 | 2.5278 | 10.5135 | 2.216% | CZ 2B | 0 | 0 | 0.018074 | 0.016479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.059023 | 2.216% | CZ 2B | 25.5591 | 1.6236 | 4.1046 | 1.8011 | 0 | 30.6318 | 0 | 11.5131 | 2.5818 | 0.68493 | 2.4532 | 0.90736 | 0.56386 | 7.6299 | 0 | 26.4631 | 116.5175 | 2.216%
CZ 3A | 0.24659 | 0.015708 | 0.041149 | 0.035101 | 0 | 0.24921 | 0 | 0.10221 | 0.03514 | 0.0062819 | 0.023799 | 0.0087798 | 0.0054573 | 0.072419 | 0 | 0.25606 | 1.0979 | 19.18% | CZ 3A | 8.308 | 0.52921 | 2.7489 | 3.5101 | 0 | 8.3962 | 0 | 3.4435 | 1.1839 | 0.21165 | 0.80182 | 0.29581 | 0.18387 | 4.0625 | 0 | 8.6272 | 42.3027 | 19.18% | CZ 3A | 2.4343 | 0.15506 | 0.20337 | 0 | 0 | 2.4601 | 0 | 1.0089 | 0.34689 | 0.062013 | 0.23493 | 0.086671 | 0.053873 | 0.47333 | 0 | 2.5278 | 10.0472 | 19.18% | CZ 3A | 0 | 0 | 0.020548 | 0.035101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.080119 | 19.18% | CZ 3A | 25.4842 | 1.6233 | 4.375 | 3.8365 | 0 | 25.7548 | 0 | 10.5626 | 3.6316 | 0.64922 | 2.4595 | 0.90736 | 0.564 | 7.6299 | 0 | 26.4631 | 113.9412 | 19.18%
CZ 3B | 0.24586 | 0.015706 | 0.040479 | 0.037991 | 0 | 0.22321 | 0 | 0.10537 | 0 | 0.006434 | 0.023739 | 0.0087798 | 0.0054533 | 0.072419 | 0 | 0.25606 | 1.0415 | 7.906% | CZ 3B | 8.2834 | 0.52917 | 2.6819 | 3.7991 | 0 | 7.5202 | 0 | 3.5501 | 0 | 0.21677 | 0.7998 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 40.5497 | 7.906% | CZ 3B | 2.427 | 0.15505 | 0.20337 | 0 | 0 | 2.2034 | 0 | 1.0402 | 0 | 0.063515 | 0.23434 | 0.086671 | 0.053833 | 0.47333 | 0 | 2.5278 | 9.4685 | 7.906% | CZ 3B | 0 | 0 | 0.019878 | 0.037991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.082339 | 7.906% | CZ 3B | 25.4087 | 1.6232 | 4.3017 | 4.1524 | 0 | 23.0677 | 0 | 10.8897 | 0 | 0.66494 | 2.4533 | 0.90736 | 0.56358 | 7.6299 | 0 | 26.4631 | 108.1256 | 7.906%
CZ 3C | 0.24505 | 0.015733 | 0.040984 | 0.028798 | 0 | 0.15007 | 0 | 0.094085 | 0 | 0.0040857 | 0.023787 | 0.0087798 | 0.005456 | 0.072419 | 0 | 0.25606 | 0.94531 | 1.057% | CZ 3C | 8.2562 | 0.53007 | 2.7324 | 2.8798 | 0 | 5.056 | 0 | 3.1699 | 0 | 0.13765 | 0.80142 | 0.29581 | 0.18382 | 4.0625 | 0 | 8.6272 | 36.7326 | 1.057% | CZ 3C | 2.4191 | 0.15531 | 0.20337 | 0 | 0 | 1.4814 | 0 | 0.92878 | 0 | 0.040332 | 0.23482 | 0.086671 | 0.05386 | 0.47333 | 0 | 2.5278 | 8.6047 | 1.057% | CZ 3C | 0 | 0 | 0.020383 | 0.028798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.073651 | 1.057% | CZ 3C | 25.3251 | 1.6259 | 4.3569 | 3.1476 | 0 | 15.5088 | 0 | 9.7234 | 0 | 0.42224 | 2.4583 | 0.90736 | 0.56386 | 7.6299 | 0 | 26.4631 | 98.1325 | 1.057%
CZ 4A | 0.24716 | 0.015738 | 0.043129 | 0.039509 | 0 | 0.17081 | 0 | 0.1139 | 0.033018 | 0.0048689 | 0.023756 | 0.0087798 | 0.0054587 | 0.072419 | 0 | 0.25606 | 1.0346 | 18.98% | CZ 4A | 8.3271 | 0.53025 | 2.9469 | 3.9509 | 0 | 5.7549 | 0 | 3.8376 | 1.1124 | 0.16404 | 0.80038 | 0.29581 | 0.18391 | 4.0625 | 0 | 8.6272 | 40.5939 | 18.98% | CZ 4A | 2.4399 | 0.15536 | 0.20337 | 0 | 0 | 1.6862 | 0 | 1.1244 | 0.32594 | 0.048064 | 0.23451 | 0.086671 | 0.053886 | 0.47333 | 0 | 2.5278 | 9.3594 | 18.98% | CZ 4A | 0 | 0 | 0.022527 | 0.039509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.086507 | 18.98% | CZ 4A | 25.5428 | 1.6265 | 4.5914 | 4.3184 | 0 | 17.6528 | 0 | 11.7715 | 3.4122 | 0.50318 | 2.4551 | 0.90736 | 0.56413 | 7.6299 | 0 | 26.4631 | 107.4385 | 18.98%
CZ 4B | 0.24587 | 0.015701 | 0.042547 | 0.066605 | 0 | 0.15579 | 0 | 0.11178 | 0 | 0.0055374 | 0.023721 | 0.0087798 | 0.0054547 | 0.072419 | 0 | 0.25606 | 1.0103 | 0.5989% | CZ 4B | 8.2836 | 0.52899 | 2.8886 | 6.6605 | 0 | 5.249 | 0 | 3.7661 | 0 | 0.18656 | 0.79921 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 41.5318 | 0.5989% | CZ 4B | 2.4271 | 0.15499 | 0.20337 | 0 | 0 | 1.5379 | 0 | 1.1035 | 0 | 0.054663 | 0.23417 | 0.086671 | 0.053847 | 0.47333 | 0 | 2.5278 | 8.8573 | 0.5989% | CZ 4B | 0 | 0 | 0.021945 | 0.066605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11302 | 0.5989% | CZ 4B | 25.4093 | 1.6226 | 4.5277 | 7.2799 | 0 | 16.1008 | 0 | 11.5521 | 0 | 0.57227 | 2.4515 | 0.90736 | 0.56372 | 7.6299 | 0 | 26.4631 | 105.0804 | 0.5989%
CZ 4C | 0.25322 | 0.015736 | 0.043447 | 0.092434 | 0 | 0.066022 | 0 | 0.086664 | 0 | 0.0034959 | 0.023725 | 0.0087798 | 0.00546 | 0.072419 | 0 | 0.25606 | 0.92746 | 2.262% | CZ 4C | 8.5313 | 0.53016 | 2.9786 | 9.2434 | 0 | 2.2244 | 0 | 2.9198 | 0 | 0.11778 | 0.79935 | 0.29581 | 0.18396 | 4.0625 | 0 | 8.6272 | 40.5143 | 2.262% | CZ 4C | 2.4997 | 0.15534 | 0.20337 | 0 | 0 | 0.65174 | 0 | 0.85551 | 0 | 0.03451 | 0.23421 | 0.086671 | 0.053899 | 0.47333 | 0 | 2.5278 | 7.776 | 2.262% | CZ 4C | 0 | 0 | 0.022845 | 0.092434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.13975 | 2.262% | CZ 4C | 26.169 | 1.6262 | 4.6261 | 10.1031 | 0 | 6.8231 | 0 | 8.9564 | 0 | 0.36129 | 2.4519 | 0.90736 | 0.56427 | 7.6299 | 0 | 26.4631 | 96.6818 | 2.262%
CZ 5A | 0.24833 | 0.015712 | 0.044766 | 0.060229 | 0 | 0.111 | 0 | 0.11637 | 0.031552 | 0.0042671 | 0.023728 | 0.0087798 | 0.0054573 | 0.072419 | 0 | 0.25606 | 0.99867 | 20.76% | CZ 5A | 8.3665 | 0.52935 | 3.1105 | 6.0229 | 0 | 3.7399 | 0 | 3.9207 | 1.0631 | 0.14377 | 0.79944 | 0.29581 | 0.18387 | 4.0625 | 0 | 8.6272 | 40.8656 | 20.76% | CZ 5A | 2.4514 | 0.1551 | 0.20337 | 0 | 0 | 1.0958 | 0 | 1.1488 | 0.31148 | 0.042124 | 0.23424 | 0.086671 | 0.053873 | 0.47333 | 0 | 2.5278 | 8.7839 | 20.76% | CZ 5A | 0 | 0 | 0.024164 | 0.060229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10886 | 20.76% | CZ 5A | 25.6636 | 1.6237 | 4.7703 | 6.5831 | 0 | 11.4717 | 0 | 12.0265 | 3.2608 | 0.44099 | 2.4522 | 0.90736 | 0.564 | 7.6299 | 0 | 26.4631 | 103.8574 | 20.76%
CZ 5B | 0.24686 | 0.015729 | 0.044255 | 0.1146 | 0 | 0.11986 | 0 | 0.10861 | 0 | 0.0052492 | 0.0237 | 0.0087798 | 0.0054573 | 0.072419 | 0 | 0.25606 | 1.0216 | 4.314% | CZ 5B | 8.3171 | 0.52993 | 3.0594 | 11.4596 | 0 | 4.0381 | 0 | 3.6593 | 0 | 0.17685 | 0.79849 | 0.29581 | 0.18387 | 4.0625 | 0 | 8.6272 | 45.2082 | 4.314% | CZ 5B | 2.4369 | 0.15527 | 0.20337 | 0 | 0 | 1.1832 | 0 | 1.0722 | 0 | 0.051818 | 0.23396 | 0.086671 | 0.053873 | 0.47333 | 0 | 2.5278 | 8.4783 | 4.314% | CZ 5B | 0 | 0 | 0.023653 | 0.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.16272 | 4.314% | CZ 5B | 25.5119 | 1.6255 | 4.7144 | 12.5254 | 0 | 12.3867 | 0 | 11.2246 | 0 | 0.54248 | 2.4493 | 0.90736 | 0.564 | 7.6299 | 0 | 26.4631 | 106.5448 | 4.314%
CZ 5C | 0.25101 | 0.015728 | 0.044322 | 0.05292 | 0 | 0.050268 | 0 | 0.11424 | 0.031395 | 0.0020055 | 0.023711 | 0.0087798 | 0.0054587 | 0.072419 | 0 | 0.25606 | 0.92831 | 0.08114% | CZ 5C | 8.4568 | 0.52989 | 3.0661 | 5.292 | 0 | 1.6936 | 0 | 3.8488 | 1.0578 | 0.067568 | 0.79885 | 0.29581 | 0.18391 | 4.0625 | 0 | 8.6272 | 37.9808 | 0.08114% | CZ 5C | 2.4779 | 0.15526 | 0.20337 | 0 | 0 | 0.49622 | 0 | 1.1277 | 0.30992 | 0.019797 | 0.23406 | 0.086671 | 0.053886 | 0.47333 | 0 | 2.5278 | 8.1659 | 0.08114% | CZ 5C | 0 | 0 | 0.02372 | 0.05292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10111 | 0.08114% | CZ 5C | 25.9407 | 1.6254 | 4.7217 | 5.7842 | 0 | 5.195 | 0 | 11.806 | 3.2446 | 0.20726 | 2.4504 | 0.90736 | 0.56413 | 7.6299 | 0 | 26.4631 | 96.5397 | 0.08114%
CZ 6A | 0.24886 | 0.015721 | 0.046094 | 0.10524 | 0 | 0.12186 | 0 | 0.12592 | 0.035908 | 0.0046247 | 0.023687 | 0.0087798 | 0.00546 | 0.072419 | 0 | 0.25606 | 1.0706 | 2.944% | CZ 6A | 8.3844 | 0.52966 | 3.2433 | 10.524 | 0 | 4.1056 | 0 | 4.2423 | 1.2098 | 0.15581 | 0.79804 | 0.29581 | 0.18396 | 4.0625 | 0 | 8.6272 | 46.3623 | 2.944% | CZ 6A | 2.4566 | 0.15519 | 0.20339 | 0 | 0 | 1.2029 | 0 | 1.243 | 0.35447 | 0.045654 | 0.23383 | 0.086671 | 0.053899 | 0.47333 | 0 | 2.5278 | 9.0368 | 2.944% | CZ 6A | 0 | 0 | 0.025491 | 0.10524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.1552 | 2.944% | CZ 6A | 25.7184 | 1.6247 | 4.9154 | 11.5027 | 0 | 12.5935 | 0 | 13.013 | 3.7109 | 0.47795 | 2.4479 | 0.90736 | 0.56427 | 7.6299 | 0 | 26.4631 | 111.5692 | 2.944%
CZ 6B | 0.24929 | 0.015702 | 0.045716 | 0.078212 | 0 | 0.085297 | 0 | 0.12797 | 0.038455 | 0.0047421 | 0.023649 | 0.0087798 | 0.0054573 | 0.072419 | 0 | 0.25606 | 1.0118 | 0.7512% | CZ 6B | 8.3991 | 0.52903 | 3.2054 | 7.8212 | 0 | 2.8738 | 0 | 4.3116 | 1.2956 | 0.15977 | 0.79679 | 0.29581 | 0.18387 | 4.0625 | 0 | 8.6272 | 42.5616 | 0.7512% | CZ 6B | 2.4609 | 0.15501 | 0.20339 | 0 | 0 | 0.84203 | 0 | 1.2633 | 0.37961 | 0.046813 | 0.23346 | 0.086671 | 0.053873 | 0.47333 | 0 | 2.5278 | 8.7262 | 0.7512% | CZ 6B | 0 | 0 | 0.025113 | 0.078212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12779 | 0.7512% | CZ 6B | 25.7636 | 1.6228 | 4.8741 | 8.5485 | 0 | 8.8152 | 0 | 13.2254 | 3.9742 | 0.49008 | 2.4441 | 0.90736 | 0.564 | 7.6299 | 0 | 26.4631 | 105.3222 | 0.7512%
CZ 7 | 0.23557 | 0.015728 | 0.04753 | 0.13187 | 0 | 0.094112 | 0 | 0.12765 | 0.034034 | 0.0047061 | 0.023647 | 0.0087798 | 0.0054507 | 0.072419 | 0 | 0.25606 | 1.0576 | 0.4899% | CZ 7 | 7.9369 | 0.52989 | 3.3869 | 13.1869 | 0 | 3.1708 | 0 | 4.3008 | 1.1467 | 0.15856 | 0.7967 | 0.29581 | 0.18364 | 4.0625 | 0 | 8.6272 | 47.7832 | 0.4899% | CZ 7 | 2.3255 | 0.15526 | 0.20339 | 0 | 0 | 0.92904 | 0 | 1.2601 | 0.33598 | 0.046457 | 0.23343 | 0.086671 | 0.053807 | 0.47333 | 0 | 2.5278 | 8.6308 | 0.4899% | CZ 7 | 0 | 0 | 0.026927 | 0.13187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.18327 | 0.4899% | CZ 7 | 24.3457 | 1.6254 | 5.0724 | 14.4133 | 0 | 9.7261 | 0 | 13.1924 | 3.5173 | 0.48636 | 2.4438 | 0.90736 | 0.56331 | 7.6299 | 0 | 26.4631 | 110.3866 | 0.4899%
CZ 8 | 0.24898 | 0.015832 | 0.04929 | 0.24669 | 0 | 0.039203 | 0 | 0.13601 | 0.034169 | 0.0051531 | 0.02356 | 0.0087798 | 0.00546 | 0.072419 | 0 | 0.25606 | 1.1416 | 0.08174% | CZ 8 | 8.3887 | 0.53339 | 3.5627 | 24.6689 | 0 | 1.3208 | 0 | 4.5823 | 1.1512 | 0.17362 | 0.79377 | 0.29581 | 0.18396 | 4.0625 | 0 | 8.6272 | 58.3449 | 0.08174% | CZ 8 | 2.4579 | 0.15628 | 0.2034 | 0 | 0 | 0.387 | 0 | 1.3426 | 0.33731 | 0.05087 | 0.23258 | 0.086671 | 0.053899 | 0.47333 | 0 | 2.5278 | 8.3096 | 0.08174% | CZ 8 | 0 | 0 | 0.028685 | 0.24669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.29984 | 0.08174% | CZ 8 | 25.7316 | 1.6361 | 5.2647 | 26.9631 | 0 | 4.0515 | 0 | 14.0558 | 3.5313 | 0.53256 | 2.4348 | 0.90736 | 0.56427 | 7.6299 | 0 | 26.4631 | 119.7662 | 0.08174%
US Weighted | 0.24658 | 0.015715 | 0.042024 | 0.045064 | 0 | 0.21383 | 0 | 0.10932 | 0.02766 | 0.0058638 | 0.023777 | 0.0087798 | 0.0054567 | 0.072419 | 0 | 0.25606 | 1.0725 | 100% | US Weighted | 8.3077 | 0.52948 | 2.8363 | 4.5064 | 0 | 7.2043 | 0 | 3.683 | 0.9319 | 0.19756 | 0.80109 | 0.29581 | 0.18385 | 4.0625 | 0 | 8.6272 | 42.1671 | 100% | US Weighted | 2.4342 | 0.15514 | 0.20337 | 0 | 0 | 2.1108 | 0 | 1.0791 | 0.27305 | 0.057885 | 0.23472 | 0.086671 | 0.053867 | 0.47333 | 0 | 2.5278 | 9.6899 | 100% | US Weighted | 0 | 0 | 0.021422 | 0.045064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090956 | 100% | US Weighted | 25.4833 | 1.6241 | 4.4706 | 4.9255 | 0 | 22.0985 | 0 | 11.2974 | 2.8585 | 0.606 | 2.4573 | 0.90736 | 0.56394 | 7.6299 | 0 | 26.4631 | 111.3855 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.28779 | 0.015728 | 0.036657 | 0.0014171 | 0 | 0.69677 | 0 | 0.14885 | 0.064834 | 0.014978 | 0.028198 | 0.0088025 | 0.0059217 | 0.072419 | 0 | 0.28192 | 1.6643 | 3.045% | CZ 1A | 9.6962 | 0.52989 | 2.2984 | 0.14171 | 0 | 23.4753 | 0 | 5.0151 | 2.1844 | 0.50462 | 0.95004 | 0.29657 | 0.19951 | 4.0625 | 0 | 9.4984 | 58.8527 | 3.045% | CZ 1A | 2.841 | 0.15526 | 0.20356 | 0 | 0 | 6.8783 | 0 | 1.4694 | 0.64002 | 0.14785 | 0.27836 | 0.086895 | 0.058457 | 0.47333 | 0 | 2.783 | 16.0154 | 3.045% | CZ 1A | 0 | 0 | 0.016037 | 0.0014171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.041925 | 3.045% | CZ 1A | 29.7423 | 1.6254 | 3.8839 | 0.15489 | 0 | 72.0085 | 0 | 15.3834 | 6.7004 | 1.5479 | 2.9142 | 0.9097 | 0.61198 | 7.6299 | 0 | 29.1356 | 172.2481 | 3.045%
CZ 1B | 0.28712 | 0.015704 | 0.037206 | 0.017684 | 0 | 0.64114 | 0 | 0.15631 | 0.038257 | 0.010189 | 0.029196 | 0.0088025 | 0.005923 | 0.072419 | 0 | 0.28192 | 1.6019 | 0% | CZ 1B | 9.6735 | 0.52908 | 2.3545 | 1.7684 | 0 | 21.6012 | 0 | 5.2665 | 1.289 | 0.34328 | 0.98366 | 0.29657 | 0.19956 | 4.0625 | 0 | 9.4984 | 57.8661 | 0% | CZ 1B | 2.8343 | 0.15502 | 0.20337 | 0 | 0 | 6.3292 | 0 | 1.5431 | 0.37766 | 0.10058 | 0.28821 | 0.086895 | 0.05847 | 0.47333 | 0 | 2.783 | 15.2331 | 0% | CZ 1B | 0 | 0 | 0.016604 | 0.017684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.058759 | 0% | CZ 1B | 29.6725 | 1.6229 | 3.944 | 1.9329 | 0 | 66.2599 | 0 | 16.1546 | 3.9538 | 1.053 | 3.0173 | 0.9097 | 0.61212 | 7.6299 | 0 | 29.1356 | 165.8981 | 0%
CZ 2A | 0.28933 | 0.015697 | 0.038458 | 0.01511 | 0 | 0.58288 | 0 | 0.13881 | 0.033202 | 0.014029 | 0.028186 | 0.0088025 | 0.0059257 | 0.072419 | 0 | 0.28192 | 1.5248 | 15.33% | CZ 2A | 9.7481 | 0.52885 | 2.4786 | 1.511 | 0 | 19.6383 | 0 | 4.6768 | 1.1186 | 0.47266 | 0.94963 | 0.29657 | 0.19965 | 4.0625 | 0 | 9.4984 | 55.1797 | 15.33% | CZ 2A | 2.8562 | 0.15495 | 0.20355 | 0 | 0 | 5.754 | 0 | 1.3703 | 0.32776 | 0.13849 | 0.27824 | 0.086895 | 0.058496 | 0.47333 | 0 | 2.783 | 14.4853 | 15.33% | CZ 2A | 0 | 0 | 0.017839 | 0.01511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.05742 | 15.33% | CZ 2A | 29.9016 | 1.6222 | 4.0807 | 1.6516 | 0 | 60.2388 | 0 | 14.3458 | 3.4313 | 1.4498 | 2.9129 | 0.9097 | 0.6124 | 7.6299 | 0 | 29.1356 | 157.9223 | 15.33%
CZ 2B | 0.29352 | 0.01571 | 0.038677 | 0.021079 | 0 | 0.35603 | 0 | 0.1319 | 0.027013 | 0.0077657 | 0.029028 | 0.0088025 | 0.0059297 | 0.072419 | 0 | 0.28192 | 1.2898 | 2.216% | CZ 2B | 9.8892 | 0.5293 | 2.5016 | 2.1079 | 0 | 11.9952 | 0 | 4.4439 | 0.91012 | 0.26164 | 0.978 | 0.29657 | 0.19978 | 4.0625 | 0 | 9.4984 | 47.6741 | 2.216% | CZ 2B | 2.8975 | 0.15509 | 0.20337 | 0 | 0 | 3.5146 | 0 | 1.3021 | 0.26666 | 0.07666 | 0.28655 | 0.086895 | 0.058536 | 0.47333 | 0 | 2.783 | 12.1043 | 2.216% | CZ 2B | 0 | 0 | 0.018075 | 0.021079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.063625 | 2.216% | CZ 2B | 30.3343 | 1.6236 | 4.1047 | 2.3039 | 0 | 36.7942 | 0 | 13.6313 | 2.7917 | 0.80256 | 2.9999 | 0.9097 | 0.61281 | 7.6299 | 0 | 29.1356 | 133.6743 | 2.216%
CZ 3A | 0.28566 | 0.015708 | 0.041185 | 0.036048 | 0 | 0.34462 | 0 | 0.12718 | 0.032022 | 0.008609 | 0.028053 | 0.0088025 | 0.005923 | 0.072419 | 0 | 0.28192 | 1.2881 | 19.18% | CZ 3A | 9.6243 | 0.52921 | 2.7512 | 3.6048 | 0 | 11.6109 | 0 | 4.2848 | 1.0789 | 0.29005 | 0.94514 | 0.29657 | 0.19956 | 4.0625 | 0 | 9.4984 | 48.7764 | 19.18% | CZ 3A | 2.8199 | 0.15506 | 0.20356 | 0 | 0 | 3.402 | 0 | 1.2554 | 0.31611 | 0.084985 | 0.27693 | 0.086895 | 0.05847 | 0.47333 | 0 | 2.783 | 11.9157 | 19.18% | CZ 3A | 0 | 0 | 0.020565 | 0.036048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081084 | 19.18% | CZ 3A | 29.5218 | 1.6233 | 4.3788 | 3.9401 | 0 | 35.6156 | 0 | 13.1432 | 3.3094 | 0.88971 | 2.8991 | 0.9097 | 0.61212 | 7.6299 | 0 | 29.1356 | 133.6083 | 19.18%
CZ 3B | 0.28599 | 0.015706 | 0.040477 | 0.026558 | 0 | 0.24756 | 0 | 0.12829 | 0.029866 | 0.0064394 | 0.029031 | 0.0088025 | 0.005923 | 0.072419 | 0 | 0.28192 | 1.179 | 7.906% | CZ 3B | 9.6357 | 0.52917 | 2.6817 | 2.6558 | 0 | 8.3407 | 0 | 4.3224 | 1.0062 | 0.21695 | 0.97809 | 0.29657 | 0.19956 | 4.0625 | 0 | 9.4984 | 44.4237 | 7.906% | CZ 3B | 2.8232 | 0.15505 | 0.20337 | 0 | 0 | 2.4438 | 0 | 1.2664 | 0.29483 | 0.063567 | 0.28658 | 0.086895 | 0.05847 | 0.47333 | 0 | 2.783 | 10.9387 | 7.906% | CZ 3B | 0 | 0 | 0.019876 | 0.026558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.070905 | 7.906% | CZ 3B | 29.5566 | 1.6232 | 4.3015 | 2.9028 | 0 | 25.5845 | 0 | 13.2585 | 3.0865 | 0.66549 | 3.0002 | 0.9097 | 0.61212 | 7.6299 | 0 | 29.1356 | 122.2666 | 7.906%
CZ 3C | 0.28545 | 0.015733 | 0.041016 | 0.014667 | 0 | 0.20882 | 0 | 0.11551 | 0.030609 | 0.0056041 | 0.028062 | 0.0088025 | 0.0059217 | 0.072419 | 0 | 0.28192 | 1.1145 | 1.057% | CZ 3C | 9.6172 | 0.53007 | 2.7343 | 1.4667 | 0 | 7.0355 | 0 | 3.8917 | 1.0313 | 0.18881 | 0.94545 | 0.29657 | 0.19951 | 4.0625 | 0 | 9.4984 | 41.498 | 1.057% | CZ 3C | 2.8178 | 0.15531 | 0.20356 | 0 | 0 | 2.0614 | 0 | 1.1403 | 0.30216 | 0.055322 | 0.27702 | 0.086895 | 0.058457 | 0.47333 | 0 | 2.783 | 10.4146 | 1.057% | CZ 3C | 0 | 0 | 0.020395 | 0.014667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.059533 | 1.057% | CZ 3C | 29.5 | 1.6259 | 4.3603 | 1.6031 | 0 | 21.5808 | 0 | 11.9374 | 3.1633 | 0.57916 | 2.9001 | 0.9097 | 0.61198 | 7.6299 | 0 | 29.1356 | 115.5373 | 1.057%
CZ 4A | 0.28084 | 0.015738 | 0.043168 | 0.051668 | 0 | 0.23514 | 0 | 0.13895 | 0.032421 | 0.0065835 | 0.027987 | 0.0088025 | 0.005919 | 0.072419 | 0 | 0.28192 | 1.2016 | 18.98% | CZ 4A | 9.4621 | 0.53025 | 2.9495 | 5.1668 | 0 | 7.9223 | 0 | 4.6816 | 1.0923 | 0.22181 | 0.94294 | 0.29657 | 0.19942 | 4.0625 | 0 | 9.4984 | 47.0265 | 18.98% | CZ 4A | 2.7724 | 0.15536 | 0.20356 | 0 | 0 | 2.3212 | 0 | 1.3717 | 0.32005 | 0.06499 | 0.27628 | 0.086895 | 0.05843 | 0.47333 | 0 | 2.783 | 10.8873 | 18.98% | CZ 4A | 0 | 0 | 0.022548 | 0.051668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.098686 | 18.98% | CZ 4A | 29.0242 | 1.6265 | 4.5955 | 5.6473 | 0 | 24.3011 | 0 | 14.3604 | 3.3506 | 0.68038 | 2.8924 | 0.9097 | 0.61171 | 7.6299 | 0 | 29.1356 | 124.7652 | 18.98%
CZ 4B | 0.28059 | 0.015701 | 0.042585 | 0.032244 | 0 | 0.2061 | 0 | 0.1573 | 0.028411 | 0.0062939 | 0.027959 | 0.0088025 | 0.0059203 | 0.072419 | 0 | 0.28192 | 1.1663 | 0.5989% | CZ 4B | 9.4535 | 0.52899 | 2.8912 | 3.2244 | 0 | 6.944 | 0 | 5.2999 | 0.95723 | 0.21205 | 0.94199 | 0.29657 | 0.19947 | 4.0625 | 0 | 9.4984 | 44.5102 | 0.5989% | CZ 4B | 2.7699 | 0.15499 | 0.20356 | 0 | 0 | 2.0346 | 0 | 1.5529 | 0.28047 | 0.062132 | 0.276 | 0.086895 | 0.058444 | 0.47333 | 0 | 2.783 | 10.7362 | 0.5989% | CZ 4B | 0 | 0 | 0.021965 | 0.032244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.078679 | 0.5989% | CZ 4B | 28.998 | 1.6226 | 4.5318 | 3.5243 | 0 | 21.3002 | 0 | 16.2569 | 2.9362 | 0.65046 | 2.8895 | 0.9097 | 0.61185 | 7.6299 | 0 | 29.1356 | 120.9969 | 0.5989%
CZ 4C | 0.28487 | 0.015736 | 0.043477 | 0.04967 | 0 | 0.097269 | 0 | 0.13012 | 0.032732 | 0.0030035 | 0.027959 | 0.0088025 | 0.0059217 | 0.072419 | 0 | 0.28192 | 1.0539 | 2.262% | CZ 4C | 9.5979 | 0.53016 | 2.9804 | 4.967 | 0 | 3.2771 | 0 | 4.384 | 1.1028 | 0.10119 | 0.94199 | 0.29657 | 0.19951 | 4.0625 | 0 | 9.4984 | 41.9396 | 2.262% | CZ 4C | 2.8122 | 0.15534 | 0.20356 | 0 | 0 | 0.9602 | 0 | 1.2845 | 0.32312 | 0.02965 | 0.276 | 0.086895 | 0.058457 | 0.47333 | 0 | 2.783 | 9.4463 | 2.262% | CZ 4C | 0 | 0 | 0.022856 | 0.04967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.096997 | 2.262% | CZ 4C | 29.4407 | 1.6262 | 4.6293 | 5.429 | 0 | 10.0524 | 0 | 13.4477 | 3.3827 | 0.3104 | 2.8895 | 0.9097 | 0.61198 | 7.6299 | 0 | 29.1356 | 109.495 | 2.262%
CZ 5A | 0.28134 | 0.015712 | 0.044799 | 0.083975 | 0 | 0.14712 | 0 | 0.14034 | 0.02884 | 0.0051611 | 0.027954 | 0.0088025 | 0.0059203 | 0.072419 | 0 | 0.28192 | 1.1443 | 20.76% | CZ 5A | 9.479 | 0.52935 | 3.1126 | 8.3975 | 0 | 4.9569 | 0 | 4.7282 | 0.97166 | 0.17389 | 0.94181 | 0.29657 | 0.19947 | 4.0625 | 0 | 9.4984 | 47.3478 | 20.76% | CZ 5A | 2.7773 | 0.1551 | 0.20356 | 0 | 0 | 1.4524 | 0 | 1.3854 | 0.2847 | 0.050949 | 0.27595 | 0.086895 | 0.058444 | 0.47333 | 0 | 2.783 | 9.987 | 20.76% | CZ 5A | 0 | 0 | 0.024179 | 0.083975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.13262 | 20.76% | CZ 5A | 29.076 | 1.6237 | 4.7738 | 9.1785 | 0 | 15.2047 | 0 | 14.5034 | 2.9805 | 0.53338 | 2.8889 | 0.9097 | 0.61185 | 7.6299 | 0 | 29.1356 | 119.05 | 20.76%
CZ 5B | 0.28129 | 0.015729 | 0.044293 | 0.062345 | 0 | 0.15339 | 0 | 0.15262 | 0.029351 | 0.0054627 | 0.027931 | 0.0088025 | 0.0059217 | 0.072419 | 0 | 0.28192 | 1.1415 | 4.314% | CZ 5B | 9.4772 | 0.52993 | 3.062 | 6.2345 | 0 | 5.168 | 0 | 5.1422 | 0.98888 | 0.18405 | 0.94105 | 0.29657 | 0.19951 | 4.0625 | 0 | 9.4984 | 45.7847 | 4.314% | CZ 5B | 2.7768 | 0.15527 | 0.20356 | 0 | 0 | 1.5142 | 0 | 1.5067 | 0.28974 | 0.053926 | 0.27573 | 0.086895 | 0.058457 | 0.47333 | 0 | 2.783 | 10.1776 | 4.314% | CZ 5B | 0 | 0 | 0.023672 | 0.062345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11049 | 4.314% | CZ 5B | 29.0705 | 1.6255 | 4.7184 | 6.8143 | 0 | 15.8523 | 0 | 15.7731 | 3.0333 | 0.56455 | 2.8866 | 0.9097 | 0.61198 | 7.6299 | 0 | 29.1356 | 118.6258 | 4.314%
CZ 5C | 0.28352 | 0.015728 | 0.044354 | 0.058177 | 0 | 0.055551 | 0 | 0.13206 | 0.029875 | 0.0024805 | 0.027943 | 0.0088025 | 0.005923 | 0.072419 | 0 | 0.28192 | 1.0188 | 0.08114% | CZ 5C | 9.5522 | 0.52989 | 3.0681 | 5.8177 | 0 | 1.8716 | 0 | 4.4493 | 1.0065 | 0.083572 | 0.94145 | 0.29657 | 0.19956 | 4.0625 | 0 | 9.4984 | 41.3774 | 0.08114% | CZ 5C | 2.7988 | 0.15526 | 0.20356 | 0 | 0 | 0.54838 | 0 | 1.3036 | 0.29492 | 0.024487 | 0.27585 | 0.086895 | 0.05847 | 0.47333 | 0 | 2.783 | 9.0066 | 0.08114% | CZ 5C | 0 | 0 | 0.023734 | 0.058177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10638 | 0.08114% | CZ 5C | 29.3006 | 1.6254 | 4.7251 | 6.3588 | 0 | 5.741 | 0 | 13.6477 | 3.0875 | 0.25635 | 2.8878 | 0.9097 | 0.61212 | 7.6299 | 0 | 29.1356 | 105.9177 | 0.08114%
CZ 6A | 0.28199 | 0.015721 | 0.046129 | 0.14639 | 0 | 0.16494 | 0 | 0.14987 | 0.035595 | 0.0060538 | 0.027935 | 0.0088025 | 0.0059203 | 0.072419 | 0 | 0.28192 | 1.2437 | 2.944% | CZ 6A | 9.5007 | 0.52966 | 3.2455 | 14.6388 | 0 | 5.5573 | 0 | 5.0495 | 1.1993 | 0.20396 | 0.94118 | 0.29657 | 0.19947 | 4.0625 | 0 | 9.4984 | 54.9227 | 2.944% | CZ 6A | 2.7837 | 0.15519 | 0.20357 | 0 | 0 | 1.6283 | 0 | 1.4795 | 0.35139 | 0.059761 | 0.27577 | 0.086895 | 0.058444 | 0.47333 | 0 | 2.783 | 10.3389 | 2.944% | CZ 6A | 0 | 0 | 0.025507 | 0.14639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.19637 | 2.944% | CZ 6A | 29.1426 | 1.6247 | 4.9191 | 16.0002 | 0 | 17.0465 | 0 | 15.4888 | 3.6787 | 0.62564 | 2.887 | 0.9097 | 0.61185 | 7.6299 | 0 | 29.1356 | 129.7002 | 2.944%
CZ 6B | 0.28271 | 0.015702 | 0.04575 | 0.10764 | 0 | 0.1048 | 0 | 0.14699 | 0.032293 | 0.0050264 | 0.027882 | 0.0088025 | 0.0059217 | 0.072419 | 0 | 0.28192 | 1.1378 | 0.7512% | CZ 6B | 9.5251 | 0.52903 | 3.2077 | 10.7635 | 0 | 3.5307 | 0 | 4.9522 | 1.088 | 0.16935 | 0.93938 | 0.29657 | 0.19951 | 4.0625 | 0 | 9.4984 | 48.762 | 0.7512% | CZ 6B | 2.7909 | 0.15501 | 0.20356 | 0 | 0 | 1.0345 | 0 | 1.451 | 0.31879 | 0.049618 | 0.27524 | 0.086895 | 0.058457 | 0.47333 | 0 | 2.783 | 9.6803 | 0.7512% | CZ 6B | 0 | 0 | 0.025129 | 0.10764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15723 | 0.7512% | CZ 6B | 29.2175 | 1.6228 | 4.8777 | 11.7645 | 0 | 10.8302 | 0 | 15.1905 | 3.3374 | 0.51946 | 2.8815 | 0.9097 | 0.61198 | 7.6299 | 0 | 29.1356 | 118.5287 | 0.7512%
CZ 7 | 0.2749 | 0.015728 | 0.047569 | 0.19292 | 0 | 0.12262 | 0 | 0.15157 | 0.035724 | 0.0062953 | 0.02788 | 0.0088025 | 0.005919 | 0.072419 | 0 | 0.28192 | 1.2443 | 0.4899% | CZ 7 | 9.2619 | 0.52989 | 3.3895 | 19.2916 | 0 | 4.1313 | 0 | 5.1065 | 1.2036 | 0.2121 | 0.93934 | 0.29657 | 0.19942 | 4.0625 | 0 | 9.4984 | 58.1226 | 0.4899% | CZ 7 | 2.7137 | 0.15526 | 0.20357 | 0 | 0 | 1.2105 | 0 | 1.4962 | 0.35265 | 0.062145 | 0.27523 | 0.086895 | 0.05843 | 0.47333 | 0 | 2.783 | 9.8709 | 0.4899% | CZ 7 | 0 | 0 | 0.026947 | 0.19292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.24433 | 0.4899% | CZ 7 | 28.41 | 1.6254 | 5.0765 | 21.0857 | 0 | 12.6724 | 0 | 15.6638 | 3.6919 | 0.6506 | 2.8813 | 0.9097 | 0.61171 | 7.6299 | 0 | 29.1356 | 130.0446 | 0.4899%
CZ 8 | 0.29321 | 0.015832 | 0.049328 | 0.34054 | 0 | 0.051604 | 0 | 0.15665 | 0.034922 | 0.0057215 | 0.027786 | 0.0088025 | 0.005931 | 0.072419 | 0 | 0.28192 | 1.3447 | 0.08174% | CZ 8 | 9.8788 | 0.53339 | 3.5654 | 34.0542 | 0 | 1.7386 | 0 | 5.278 | 1.1766 | 0.19277 | 0.93615 | 0.29657 | 0.19983 | 4.0625 | 0 | 9.4984 | 71.4112 | 0.08174% | CZ 8 | 2.8945 | 0.15628 | 0.20357 | 0 | 0 | 0.50942 | 0 | 1.5464 | 0.34473 | 0.056481 | 0.27429 | 0.086895 | 0.058549 | 0.47333 | 0 | 2.783 | 9.3875 | 0.08174% | CZ 8 | 0 | 0 | 0.028706 | 0.34054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.39372 | 0.08174% | CZ 8 | 30.3025 | 1.6361 | 5.2687 | 37.2213 | 0 | 5.3331 | 0 | 16.1897 | 3.609 | 0.5913 | 2.8716 | 0.9097 | 0.61295 | 7.6299 | 0 | 29.1356 | 141.3115 | 0.08174%
US Weighted | 0.28426 | 0.015715 | 0.042057 | 0.049631 | 0 | 0.29791 | 0 | 0.13697 | 0.032326 | 0.0079145 | 0.02813 | 0.0088025 | 0.005922 | 0.072419 | 0 | 0.28192 | 1.264 | 100% | US Weighted | 9.5772 | 0.52948 | 2.8385 | 4.9631 | 0 | 10.0371 | 0 | 4.6147 | 1.0891 | 0.26665 | 0.94774 | 0.29657 | 0.19952 | 4.0625 | 0 | 9.4984 | 48.9207 | 100% | US Weighted | 2.8061 | 0.15514 | 0.20354 | 0 | 0 | 2.9409 | 0 | 1.3521 | 0.31911 | 0.078129 | 0.27769 | 0.086895 | 0.05846 | 0.47333 | 0 | 2.783 | 11.5344 | 100% | US Weighted | 0 | 0 | 0.021439 | 0.049631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.095541 | 100% | US Weighted | 29.3774 | 1.6241 | 4.4741 | 5.4247 | 0 | 30.7879 | 0 | 14.1551 | 3.3408 | 0.81793 | 2.9071 | 0.9097 | 0.61202 | 7.6299 | 0 | 29.1356 | 131.1964 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.43965 | 0.028976 | 0.036685 | 0.0017793 | 0 | 0.86519 | 0 | 0.20844 | 0.066293 | 0.041908 | 0.028533 | 0.010107 | 0.010588 | 0.072419 | 0 | 0.28319 | 2.0938 | 3.045% | CZ 1A | 14.8126 | 0.97625 | 2.3012 | 0.17793 | 0 | 29.1499 | 0 | 7.0227 | 2.2335 | 1.412 | 0.96132 | 0.34054 | 0.35672 | 4.0625 | 0 | 9.5412 | 73.3483 | 3.045% | CZ 1A | 4.3401 | 0.28604 | 0.20356 | 0 | 0 | 8.5409 | 0 | 2.0576 | 0.65442 | 0.4137 | 0.28167 | 0.099777 | 0.10452 | 0.47333 | 0 | 2.7956 | 20.2512 | 3.045% | CZ 1A | 0 | 0 | 0.016065 | 0.0017793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.042315 | 3.045% | CZ 1A | 45.4364 | 2.9946 | 3.8869 | 0.19448 | 0 | 89.4148 | 0 | 21.5415 | 6.8511 | 4.331 | 2.9488 | 1.0446 | 1.0942 | 7.6299 | 0 | 29.267 | 216.6353 | 3.045%
CZ 1B | 0.43965 | 0.02894 | 0.037222 | 0.024914 | 0 | 0.84499 | 0 | 0.2097 | 0.02572 | 0.029299 | 0.029558 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 2.0463 | 0% | CZ 1B | 14.8126 | 0.97503 | 2.3561 | 2.4914 | 0 | 28.4691 | 0 | 7.0651 | 0.86656 | 0.98713 | 0.99585 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 73.3199 | 0% | CZ 1B | 4.3401 | 0.28568 | 0.20337 | 0 | 0 | 8.3414 | 0 | 2.0701 | 0.2539 | 0.28923 | 0.29178 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 19.5488 | 0% | CZ 1B | 0 | 0 | 0.01662 | 0.024914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.066004 | 0% | CZ 1B | 45.4364 | 2.9908 | 3.9457 | 2.7231 | 0 | 87.3265 | 0 | 21.6715 | 2.6581 | 3.0279 | 3.0547 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 211.8707 | 0%
CZ 2A | 0.43965 | 0.028929 | 0.038483 | 0.017436 | 0 | 0.79412 | 0 | 0.191 | 0.061937 | 0.041628 | 0.028509 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 2.018 | 15.33% | CZ 2A | 14.8126 | 0.97467 | 2.481 | 1.7436 | 0 | 26.7553 | 0 | 6.4352 | 2.0868 | 1.4025 | 0.96051 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.9532 | 15.33% | CZ 2A | 4.3401 | 0.28558 | 0.20356 | 0 | 0 | 7.8393 | 0 | 1.8855 | 0.61143 | 0.41094 | 0.28143 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 19.3311 | 15.33% | CZ 2A | 0 | 0 | 0.017862 | 0.017436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.059769 | 15.33% | CZ 2A | 45.4364 | 2.9897 | 4.0834 | 1.9058 | 0 | 82.0697 | 0 | 19.7393 | 6.401 | 4.3021 | 2.9463 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 208.9096 | 15.33%
CZ 2B | 0.43965 | 0.028951 | 0.038691 | 0.028641 | 0 | 0.46049 | 0 | 0.18049 | 0.03972 | 0.021009 | 0.029107 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6431 | 2.216% | CZ 2B | 14.8126 | 0.97539 | 2.5031 | 2.8641 | 0 | 15.5148 | 0 | 6.081 | 1.3382 | 0.70782 | 0.98065 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 60.0788 | 2.216% | CZ 2B | 4.3401 | 0.28579 | 0.20337 | 0 | 0 | 4.5458 | 0 | 1.7817 | 0.3921 | 0.20739 | 0.28733 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 15.5169 | 2.216% | CZ 2B | 0 | 0 | 0.01809 | 0.028641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.071201 | 2.216% | CZ 2B | 45.4364 | 2.9919 | 4.1063 | 3.1305 | 0 | 47.5903 | 0 | 18.653 | 4.1049 | 2.1712 | 3.0081 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 170.2285 | 2.216%
CZ 3A | 0.43965 | 0.028945 | 0.041205 | 0.045954 | 0 | 0.47384 | 0 | 0.17486 | 0.056239 | 0.026289 | 0.028175 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 1.6915 | 19.18% | CZ 3A | 14.8126 | 0.97521 | 2.7532 | 4.5954 | 0 | 15.9644 | 0 | 5.8913 | 1.8948 | 0.88571 | 0.94927 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 63.023 | 19.18% | CZ 3A | 4.3401 | 0.28574 | 0.20356 | 0 | 0 | 4.6776 | 0 | 1.7261 | 0.55517 | 0.25951 | 0.27814 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 15.7992 | 19.18% | CZ 3A | 0 | 0 | 0.020585 | 0.045954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.091009 | 19.18% | CZ 3A | 45.4364 | 2.9914 | 4.381 | 5.0227 | 0 | 48.9695 | 0 | 18.071 | 5.8121 | 2.7168 | 2.9118 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 175.3489 | 19.18%
CZ 3B | 0.43965 | 0.028944 | 0.040492 | 0.035292 | 0 | 0.309 | 0 | 0.17486 | 0.024749 | 0.014571 | 0.029056 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.4729 | 7.906% | CZ 3B | 14.8126 | 0.97517 | 2.6832 | 3.5292 | 0 | 10.4107 | 0 | 5.8914 | 0.83383 | 0.49091 | 0.97894 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 54.9071 | 7.906% | CZ 3B | 4.3401 | 0.28572 | 0.20337 | 0 | 0 | 3.0503 | 0 | 1.7262 | 0.24431 | 0.14384 | 0.28683 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 13.7539 | 7.906% | CZ 3B | 0 | 0 | 0.019891 | 0.035292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.079653 | 7.906% | CZ 3B | 45.4364 | 2.9912 | 4.3032 | 3.8574 | 0 | 31.934 | 0 | 18.0715 | 2.5577 | 1.5058 | 3.0028 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 152.6961 | 7.906%
CZ 3C | 0.43965 | 0.02894 | 0.04104 | 0.023669 | 0 | 0.25854 | 0 | 0.16026 | 0 | 0.015068 | 0.028235 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.3717 | 1.057% | CZ 3C | 14.8126 | 0.97503 | 2.7367 | 2.3669 | 0 | 8.7106 | 0 | 5.3994 | 0 | 0.50768 | 0.9513 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 50.7612 | 1.057% | CZ 3C | 4.3401 | 0.28568 | 0.20356 | 0 | 0 | 2.5522 | 0 | 1.582 | 0 | 0.14875 | 0.27873 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.8643 | 1.057% | CZ 3C | 0 | 0 | 0.02042 | 0.023669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.068559 | 1.057% | CZ 3C | 45.4364 | 2.9908 | 4.3629 | 2.587 | 0 | 26.7189 | 0 | 16.5622 | 0 | 1.5573 | 2.918 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 142.1694 | 1.057%
CZ 4A | 0.43965 | 0.028901 | 0.043193 | 0.093933 | 0 | 0.32705 | 0 | 0.16767 | 0.054822 | 0.019792 | 0.028021 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.5793 | 18.98% | CZ 4A | 14.8126 | 0.97373 | 2.952 | 9.3933 | 0 | 11.0187 | 0 | 5.6492 | 1.847 | 0.66682 | 0.94406 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 62.5585 | 18.98% | CZ 4A | 4.3401 | 0.2853 | 0.20356 | 0 | 0 | 3.2285 | 0 | 1.6552 | 0.54118 | 0.19538 | 0.27661 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 14.1991 | 18.98% | CZ 4A | 0 | 0 | 0.022572 | 0.093933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14098 | 18.98% | CZ 4A | 45.4364 | 2.9868 | 4.5982 | 10.2668 | 0 | 33.7991 | 0 | 17.3285 | 5.6656 | 2.0454 | 2.8958 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 164.0586 | 18.98%
CZ 4B | 0.43965 | 0.028923 | 0.042607 | 0.045817 | 0 | 0.25305 | 0 | 0.20606 | 0.025996 | 0.014356 | 0.027918 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.4607 | 0.5989% | CZ 4B | 14.8126 | 0.97445 | 2.8934 | 4.5817 | 0 | 8.5258 | 0 | 6.9425 | 0.87586 | 0.48367 | 0.9406 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 55.3317 | 0.5989% | CZ 4B | 4.3401 | 0.28551 | 0.20356 | 0 | 0 | 2.4981 | 0 | 2.0342 | 0.25663 | 0.14172 | 0.2756 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 13.5086 | 0.5989% | CZ 4B | 0 | 0 | 0.021987 | 0.045817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.092274 | 0.5989% | CZ 4B | 45.4364 | 2.989 | 4.5342 | 5.0078 | 0 | 26.1522 | 0 | 21.2956 | 2.6866 | 1.4836 | 2.8852 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 151.5067 | 0.5989%
CZ 4C | 0.43965 | 0.028868 | 0.043497 | 0.083249 | 0 | 0.11356 | 0 | 0.16828 | 0.022175 | 0.0082367 | 0.027952 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.3118 | 2.262% | CZ 4C | 14.8126 | 0.97261 | 2.9824 | 8.3249 | 0 | 3.826 | 0 | 5.6697 | 0.74711 | 0.27751 | 0.94177 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 52.8557 | 2.262% | CZ 4C | 4.3401 | 0.28497 | 0.20356 | 0 | 0 | 1.121 | 0 | 1.6612 | 0.2189 | 0.08131 | 0.27594 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 11.6602 | 2.262% | CZ 4C | 0 | 0 | 0.022877 | 0.083249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.1306 | 2.262% | CZ 4C | 45.4364 | 2.9834 | 4.6315 | 9.0991 | 0 | 11.7358 | 0 | 17.3914 | 2.2917 | 0.85123 | 2.8888 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 136.3453 | 2.262%
CZ 5A | 0.43965 | 0.028909 | 0.044827 | 0.14238 | 0 | 0.20852 | 0 | 0.18885 | 0.038674 | 0.013932 | 0.027892 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.5099 | 20.76% | CZ 5A | 14.8126 | 0.974 | 3.1153 | 14.2376 | 0 | 7.0254 | 0 | 6.3628 | 1.303 | 0.46938 | 0.93974 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 63.5408 | 20.76% | CZ 5A | 4.3401 | 0.28538 | 0.20357 | 0 | 0 | 2.0584 | 0 | 1.8643 | 0.38177 | 0.13753 | 0.27534 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 13.0197 | 20.76% | CZ 5A | 0 | 0 | 0.024205 | 0.14238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.19105 | 20.76% | CZ 5A | 45.4364 | 2.9877 | 4.7768 | 15.5617 | 0 | 21.5499 | 0 | 19.5173 | 3.9968 | 1.4398 | 2.8826 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 157.1847 | 20.76%
CZ 5B | 0.43965 | 0.028911 | 0.044315 | 0.08596 | 0 | 0.21613 | 0 | 0.20311 | 0.039137 | 0.012473 | 0.027847 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.4738 | 4.314% | CZ 5B | 14.8126 | 0.97404 | 3.0642 | 8.596 | 0 | 7.2817 | 0 | 6.8431 | 1.3186 | 0.42024 | 0.93822 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 58.5497 | 4.314% | CZ 5B | 4.3401 | 0.2854 | 0.20356 | 0 | 0 | 2.1335 | 0 | 2.005 | 0.38634 | 0.12313 | 0.2749 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 13.2252 | 4.314% | CZ 5B | 0 | 0 | 0.023695 | 0.08596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.13413 | 4.314% | CZ 5B | 45.4364 | 2.9878 | 4.7209 | 9.3955 | 0 | 22.3359 | 0 | 20.9906 | 4.0446 | 1.2891 | 2.8779 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 153.1145 | 4.314%
CZ 5C | 0.43965 | 0.028865 | 0.044374 | 0.094087 | 0 | 0.069722 | 0 | 0.1701 | 0.023853 | 0.0054093 | 0.027904 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.2803 | 0.08114% | CZ 5C | 14.8126 | 0.97252 | 3.07 | 9.4087 | 0 | 2.349 | 0 | 5.7309 | 0.80366 | 0.18225 | 0.94015 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 52.5709 | 0.08114% | CZ 5C | 4.3401 | 0.28495 | 0.20357 | 0 | 0 | 0.68827 | 0 | 1.6792 | 0.23547 | 0.053399 | 0.27546 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 11.2336 | 0.08114% | CZ 5C | 0 | 0 | 0.023752 | 0.094087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14231 | 0.08114% | CZ 5C | 45.4364 | 2.9831 | 4.7273 | 10.2837 | 0 | 7.2055 | 0 | 17.579 | 2.4652 | 0.55903 | 2.8838 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 133.159 | 0.08114%
CZ 6A | 0.43965 | 0.028896 | 0.046159 | 0.22091 | 0 | 0.22081 | 0 | 0.20134 | 0.039815 | 0.015459 | 0.027866 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6172 | 2.944% | CZ 6A | 14.8126 | 0.97355 | 3.2485 | 22.0911 | 0 | 7.4395 | 0 | 6.7834 | 1.3414 | 0.52085 | 0.93884 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 72.451 | 2.944% | CZ 6A | 4.3401 | 0.28525 | 0.20357 | 0 | 0 | 2.1798 | 0 | 1.9875 | 0.39304 | 0.15261 | 0.27508 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 13.2902 | 2.944% | CZ 6A | 0 | 0 | 0.025537 | 0.22091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.27092 | 2.944% | CZ 6A | 45.4364 | 2.9863 | 4.9224 | 24.1456 | 0 | 22.8202 | 0 | 20.8076 | 4.1147 | 1.5977 | 2.8798 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 168.7467 | 2.944%
CZ 6B | 0.43965 | 0.028876 | 0.045772 | 0.15677 | 0 | 0.1547 | 0 | 0.19463 | 0.039055 | 0.010473 | 0.027754 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.474 | 0.7512% | CZ 6B | 14.8126 | 0.97288 | 3.2099 | 15.6772 | 0 | 5.212 | 0 | 6.5574 | 1.3158 | 0.35285 | 0.93507 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 63.3469 | 0.7512% | CZ 6B | 4.3401 | 0.28505 | 0.20356 | 0 | 0 | 1.5271 | 0 | 1.9213 | 0.38554 | 0.10339 | 0.27398 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 12.5133 | 0.7512% | CZ 6B | 0 | 0 | 0.025152 | 0.15677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.20639 | 0.7512% | CZ 6B | 45.4364 | 2.9842 | 4.8801 | 17.1352 | 0 | 15.9874 | 0 | 20.1144 | 4.0362 | 1.0823 | 2.8682 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 153.5606 | 0.7512%
CZ 7 | 0.43965 | 0.028857 | 0.047596 | 0.27116 | 0 | 0.16707 | 0 | 0.20559 | 0.039781 | 0.012568 | 0.027786 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6164 | 0.4899% | CZ 7 | 14.8126 | 0.97225 | 3.3922 | 27.1157 | 0 | 5.6288 | 0 | 6.9267 | 1.3403 | 0.42343 | 0.93615 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 75.8493 | 0.4899% | CZ 7 | 4.3401 | 0.28487 | 0.20357 | 0 | 0 | 1.6492 | 0 | 2.0295 | 0.39271 | 0.12407 | 0.27429 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 12.7716 | 0.4899% | CZ 7 | 0 | 0 | 0.026974 | 0.27116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.3226 | 0.4899% | CZ 7 | 45.4364 | 2.9823 | 5.0795 | 29.6375 | 0 | 17.2659 | 0 | 21.2472 | 4.1112 | 1.2988 | 2.8716 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 168.9664 | 0.4899%
CZ 8 | 0.43965 | 0.028698 | 0.049355 | 0.44464 | 0 | 0.082188 | 0 | 0.20136 | 0.038994 | 0.0088532 | 0.027638 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6977 | 0.08174% | CZ 8 | 14.8126 | 0.9669 | 3.5681 | 44.4636 | 0 | 2.7691 | 0 | 6.7841 | 1.3138 | 0.29828 | 0.93116 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 90.2086 | 0.08174% | CZ 8 | 4.3401 | 0.2833 | 0.20357 | 0 | 0 | 0.81133 | 0 | 1.9877 | 0.38493 | 0.087395 | 0.27283 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 11.8444 | 0.08174% | CZ 8 | 0 | 0 | 0.028733 | 0.44464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.49784 | 0.08174% | CZ 8 | 45.4364 | 2.9659 | 5.2717 | 48.5988 | 0 | 8.4939 | 0 | 20.8095 | 4.0299 | 0.91494 | 2.8562 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 178.4132 | 0.08174%
US Weighted | 0.43965 | 0.028922 | 0.042081 | 0.077919 | 0 | 0.40373 | 0 | 0.18222 | 0.04763 | 0.022544 | 0.028205 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6492 | 100% | US Weighted | 14.8126 | 0.97442 | 2.8409 | 7.7919 | 0 | 13.6023 | 0 | 6.1394 | 1.6047 | 0.75954 | 0.95026 | 0.34054 | 0.35679 | 4.0625 | 0 | 9.5412 | 63.777 | 100% | US Weighted | 4.3401 | 0.28551 | 0.20354 | 0 | 0 | 3.9855 | 0 | 1.7988 | 0.47019 | 0.22254 | 0.27843 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 15.0578 | 100% | US Weighted | 0 | 0 | 0.021462 | 0.077919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12385 | 100% | US Weighted | 45.4364 | 2.989 | 4.4767 | 8.5166 | 0 | 41.7238 | 0 | 18.832 | 4.9224 | 2.3298 | 2.9148 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 171.1773 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.43965 | 0.028976 | 0.03669 | 0.0019349 | 0 | 0.95997 | 0 | 0.27228 | 0.097788 | 0.04402 | 0.028533 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 2.2861 | 3.045% | CZ 1A | 14.8126 | 0.97625 | 2.3017 | 0.19349 | 0 | 32.3429 | 0 | 9.1735 | 3.2946 | 1.4831 | 0.96132 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 79.8405 | 3.045% | CZ 1A | 4.3401 | 0.28604 | 0.20356 | 0 | 0 | 9.4765 | 0 | 2.6878 | 0.96533 | 0.43455 | 0.28167 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 22.1488 | 3.045% | CZ 1A | 0 | 0 | 0.016069 | 0.0019349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.042475 | 3.045% | CZ 1A | 45.4364 | 2.9946 | 3.8874 | 0.21148 | 0 | 99.2091 | 0 | 28.1389 | 10.106 | 4.5493 | 2.9488 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 236.5179 | 3.045%
CZ 1B | 0.43965 | 0.02894 | 0.037222 | 0.026651 | 0 | 0.83854 | 0 | 0.22199 | 0.066291 | 0.030813 | 0.02956 | 0.010107 | 0.010588 | 0.072419 | 0 | 0.28319 | 2.096 | 0% | CZ 1B | 14.8126 | 0.97503 | 2.3561 | 2.6651 | 0 | 28.2519 | 0 | 7.4792 | 2.2335 | 1.0382 | 0.99594 | 0.34054 | 0.35672 | 4.0625 | 0 | 9.5412 | 75.1086 | 0% | CZ 1B | 4.3401 | 0.28568 | 0.20337 | 0 | 0 | 8.2778 | 0 | 2.1914 | 0.65441 | 0.30418 | 0.29181 | 0.099777 | 0.10452 | 0.47333 | 0 | 2.7956 | 20.022 | 0% | CZ 1B | 0 | 0 | 0.01662 | 0.026651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.067742 | 0% | CZ 1B | 45.4364 | 2.9908 | 3.9457 | 2.913 | 0 | 86.6604 | 0 | 22.942 | 6.851 | 3.1844 | 3.055 | 1.0446 | 1.0942 | 7.6299 | 0 | 29.267 | 217.0144 | 0%
CZ 2A | 0.43965 | 0.028929 | 0.038485 | 0.02269 | 0 | 0.8978 | 0 | 0.25386 | 0.094214 | 0.045194 | 0.028508 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 2.2256 | 15.33% | CZ 2A | 14.8126 | 0.97467 | 2.4812 | 2.269 | 0 | 30.2482 | 0 | 8.5529 | 3.1742 | 1.5227 | 0.96047 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 79.2971 | 15.33% | CZ 2A | 4.3401 | 0.28558 | 0.20356 | 0 | 0 | 8.8627 | 0 | 2.506 | 0.93005 | 0.44614 | 0.28142 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 21.3288 | 15.33% | CZ 2A | 0 | 0 | 0.017864 | 0.02269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.065025 | 15.33% | CZ 2A | 45.4364 | 2.9897 | 4.0836 | 2.48 | 0 | 92.784 | 0 | 26.2352 | 9.7367 | 4.6707 | 2.9462 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 230.3987 | 15.33%
CZ 2B | 0.43965 | 0.028951 | 0.038697 | 0.034152 | 0 | 0.51567 | 0 | 0.22498 | 0.062563 | 0.022929 | 0.029104 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.773 | 2.216% | CZ 2B | 14.8126 | 0.97539 | 2.5036 | 3.4152 | 0 | 17.3738 | 0 | 7.5799 | 2.1079 | 0.77251 | 0.98056 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 64.8226 | 2.216% | CZ 2B | 4.3401 | 0.28579 | 0.20337 | 0 | 0 | 5.0905 | 0 | 2.2209 | 0.6176 | 0.22635 | 0.2873 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 16.7452 | 2.216% | CZ 2B | 0 | 0 | 0.018095 | 0.034152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.076717 | 2.216% | CZ 2B | 45.4364 | 2.9919 | 4.1069 | 3.7328 | 0 | 53.2928 | 0 | 23.2508 | 6.4657 | 2.3696 | 3.0078 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 183.6907 | 2.216%
CZ 3A | 0.43965 | 0.028945 | 0.041209 | 0.064414 | 0 | 0.52297 | 0 | 0.23546 | 0.086034 | 0.028266 | 0.028174 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.8514 | 19.18% | CZ 3A | 14.8126 | 0.97521 | 2.7536 | 6.4414 | 0 | 17.6197 | 0 | 7.9331 | 2.8986 | 0.95233 | 0.94923 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 69.6369 | 19.18% | CZ 3A | 4.3401 | 0.28574 | 0.20356 | 0 | 0 | 5.1626 | 0 | 2.3244 | 0.8493 | 0.27903 | 0.27812 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 17.1961 | 19.18% | CZ 3A | 0 | 0 | 0.020589 | 0.064414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10947 | 19.18% | CZ 3A | 45.4364 | 2.9914 | 4.3814 | 7.0405 | 0 | 54.0471 | 0 | 24.334 | 8.8913 | 2.9212 | 2.9117 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 191.9909 | 19.18%
CZ 3B | 0.43965 | 0.028944 | 0.040496 | 0.04631 | 0 | 0.35262 | 0 | 0.22203 | 0.038411 | 0.016176 | 0.029052 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 1.59 | 7.906% | CZ 3B | 14.8126 | 0.97517 | 2.6836 | 4.631 | 0 | 11.8803 | 0 | 7.4804 | 1.2941 | 0.54499 | 0.97881 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 59.5821 | 7.906% | CZ 3B | 4.3401 | 0.28572 | 0.20337 | 0 | 0 | 3.4809 | 0 | 2.1918 | 0.37918 | 0.15968 | 0.28679 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 14.8008 | 7.906% | CZ 3B | 0 | 0 | 0.019895 | 0.04631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090675 | 7.906% | CZ 3B | 45.4364 | 2.9912 | 4.3036 | 5.0617 | 0 | 36.4417 | 0 | 22.9455 | 3.9696 | 1.6717 | 3.0024 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 164.8601 | 7.906%
CZ 3C | 0.43965 | 0.02894 | 0.04104 | 0.045454 | 0 | 0.28746 | 0 | 0.22346 | 0 | 0.016856 | 0.02823 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.4874 | 1.057% | CZ 3C | 14.8126 | 0.97503 | 2.7367 | 4.5454 | 0 | 9.6851 | 0 | 7.5287 | 0 | 0.56792 | 0.95112 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 56.1038 | 1.057% | CZ 3C | 4.3401 | 0.28568 | 0.20356 | 0 | 0 | 2.8377 | 0 | 2.2059 | 0 | 0.1664 | 0.27868 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 13.7913 | 1.057% | CZ 3C | 0 | 0 | 0.02042 | 0.045454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090345 | 1.057% | CZ 3C | 45.4364 | 2.9908 | 4.363 | 4.9682 | 0 | 29.7083 | 0 | 23.0938 | 0 | 1.742 | 2.9175 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 154.2559 | 1.057%
CZ 4A | 0.43965 | 0.028901 | 0.043201 | 0.14035 | 0 | 0.35572 | 0 | 0.23067 | 0.085337 | 0.021302 | 0.028011 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.7495 | 18.98% | CZ 4A | 14.8126 | 0.97373 | 2.9527 | 14.0349 | 0 | 11.9847 | 0 | 7.7718 | 2.8752 | 0.71771 | 0.94374 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 71.3681 | 18.98% | CZ 4A | 4.3401 | 0.2853 | 0.20357 | 0 | 0 | 3.5115 | 0 | 2.2771 | 0.84242 | 0.21029 | 0.27652 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 15.4201 | 18.98% | CZ 4A | 0 | 0 | 0.022579 | 0.14035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.1874 | 18.98% | CZ 4A | 45.4364 | 2.9868 | 4.5991 | 15.3402 | 0 | 36.7621 | 0 | 23.8393 | 8.8193 | 2.2015 | 2.8949 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 181.9155 | 18.98%
CZ 4B | 0.43965 | 0.028923 | 0.042613 | 0.076294 | 0 | 0.28049 | 0 | 0.26875 | 0.04036 | 0.015669 | 0.02791 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 1.597 | 0.5989% | CZ 4B | 14.8126 | 0.97445 | 2.894 | 7.6294 | 0 | 9.4503 | 0 | 9.0546 | 1.3598 | 0.52791 | 0.94033 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 61.9445 | 0.5989% | CZ 4B | 4.3401 | 0.28551 | 0.20356 | 0 | 0 | 2.7689 | 0 | 2.653 | 0.39842 | 0.15468 | 0.27552 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 14.5529 | 0.5989% | CZ 4B | 0 | 0 | 0.021993 | 0.076294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12276 | 0.5989% | CZ 4B | 45.4364 | 2.989 | 4.5349 | 8.3389 | 0 | 28.9879 | 0 | 27.7741 | 4.1711 | 1.6193 | 2.8844 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 165.7722 | 0.5989%
CZ 4C | 0.43965 | 0.028868 | 0.043505 | 0.11982 | 0 | 0.11895 | 0 | 0.22804 | 0.041228 | 0.0089692 | 0.027943 | 0.010107 | 0.010589 | 0.072419 | 0 | 0.28319 | 1.4333 | 2.262% | CZ 4C | 14.8126 | 0.97261 | 2.9831 | 11.9817 | 0 | 4.0078 | 0 | 7.6832 | 1.389 | 0.30219 | 0.94145 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 59.3747 | 2.262% | CZ 4C | 4.3401 | 0.28497 | 0.20357 | 0 | 0 | 1.1743 | 0 | 2.2512 | 0.40698 | 0.088541 | 0.27585 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.4987 | 2.262% | CZ 4C | 0 | 0 | 0.022883 | 0.11982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.16717 | 2.262% | CZ 4C | 45.4364 | 2.9834 | 4.6323 | 13.096 | 0 | 12.2935 | 0 | 23.5675 | 4.2607 | 0.92694 | 2.8878 | 1.0446 | 1.0943 | 7.6299 | 0 | 29.267 | 149.1204 | 2.262%
CZ 5A | 0.43965 | 0.028909 | 0.044832 | 0.18815 | 0 | 0.22132 | 0 | 0.2521 | 0.060015 | 0.014712 | 0.027886 | 0.010107 | 0.010588 | 0.072419 | 0 | 0.28319 | 1.6539 | 20.76% | CZ 5A | 14.8126 | 0.974 | 3.1158 | 18.8149 | 0 | 7.4566 | 0 | 8.4937 | 2.022 | 0.49568 | 0.93952 | 0.34054 | 0.35672 | 4.0625 | 0 | 9.5412 | 71.4259 | 20.76% | CZ 5A | 4.3401 | 0.28538 | 0.20357 | 0 | 0 | 2.1848 | 0 | 2.4887 | 0.59244 | 0.14523 | 0.27528 | 0.099777 | 0.10452 | 0.47333 | 0 | 2.7956 | 13.9887 | 20.76% | CZ 5A | 0 | 0 | 0.024211 | 0.18815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.23683 | 20.76% | CZ 5A | 45.4364 | 2.9877 | 4.7774 | 20.5646 | 0 | 22.8726 | 0 | 26.0539 | 6.2023 | 1.5204 | 2.8819 | 1.0446 | 1.0942 | 7.6299 | 0 | 29.267 | 172.333 | 20.76%
CZ 5B | 0.43965 | 0.028911 | 0.044322 | 0.13552 | 0 | 0.2275 | 0 | 0.26516 | 0.055059 | 0.013463 | 0.027839 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.6137 | 4.314% | CZ 5B | 14.8126 | 0.97404 | 3.0649 | 13.552 | 0 | 7.6648 | 0 | 8.9336 | 1.855 | 0.4536 | 0.93795 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 66.5496 | 4.314% | CZ 5B | 4.3401 | 0.2854 | 0.20356 | 0 | 0 | 2.2458 | 0 | 2.6175 | 0.54352 | 0.1329 | 0.27482 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 14.1169 | 4.314% | CZ 5B | 0 | 0 | 0.023702 | 0.13552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.18369 | 4.314% | CZ 5B | 45.4364 | 2.9878 | 4.7217 | 14.8124 | 0 | 23.5111 | 0 | 27.403 | 5.6902 | 1.3914 | 2.8771 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 167.8669 | 4.314%
CZ 5C | 0.43965 | 0.028865 | 0.04438 | 0.12885 | 0 | 0.076572 | 0 | 0.22733 | 0.04819 | 0.0064647 | 0.027896 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.4045 | 0.08114% | CZ 5C | 14.8126 | 0.97252 | 3.0706 | 12.8846 | 0 | 2.5798 | 0 | 7.6591 | 1.6236 | 0.21781 | 0.93988 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 59.0617 | 0.08114% | CZ 5C | 4.3401 | 0.28495 | 0.20357 | 0 | 0 | 0.75589 | 0 | 2.2441 | 0.47572 | 0.063818 | 0.27538 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 12.1168 | 0.08114% | CZ 5C | 0 | 0 | 0.023758 | 0.12885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.17707 | 0.08114% | CZ 5C | 45.4364 | 2.9831 | 4.728 | 14.0829 | 0 | 7.9135 | 0 | 23.4937 | 4.9803 | 0.66811 | 2.883 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 146.2049 | 0.08114%
CZ 6A | 0.43965 | 0.028896 | 0.046166 | 0.28864 | 0 | 0.23691 | 0 | 0.26626 | 0.061233 | 0.016887 | 0.027859 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.7888 | 2.944% | CZ 6A | 14.8126 | 0.97355 | 3.2492 | 28.8639 | 0 | 7.9818 | 0 | 8.9709 | 2.063 | 0.56895 | 0.93862 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 82.7236 | 2.944% | CZ 6A | 4.3401 | 0.28525 | 0.20357 | 0 | 0 | 2.3387 | 0 | 2.6285 | 0.60447 | 0.1667 | 0.27502 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 14.3155 | 2.944% | CZ 6A | 0 | 0 | 0.025545 | 0.28864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.33865 | 2.944% | CZ 6A | 45.4364 | 2.9863 | 4.9232 | 31.5482 | 0 | 24.4834 | 0 | 27.5175 | 6.3282 | 1.7452 | 2.8791 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 186.8835 | 2.944%
CZ 6B | 0.43965 | 0.028876 | 0.045784 | 0.21557 | 0 | 0.16076 | 0 | 0.26086 | 0.061833 | 0.011629 | 0.027743 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.629 | 0.7512% | CZ 6B | 14.8126 | 0.97288 | 3.211 | 21.5569 | 0 | 5.4162 | 0 | 8.7887 | 2.0833 | 0.39178 | 0.93471 | 0.34054 | 0.35681 | 4.0625 | 0 | 9.5412 | 72.4692 | 0.7512% | CZ 6B | 4.3401 | 0.28505 | 0.20357 | 0 | 0 | 1.5869 | 0 | 2.5751 | 0.6104 | 0.11479 | 0.27387 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 13.4631 | 0.7512% | CZ 6B | 0 | 0 | 0.025162 | 0.21557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.2652 | 0.7512% | CZ 6B | 45.4364 | 2.9842 | 4.8814 | 23.5617 | 0 | 16.6138 | 0 | 26.9587 | 6.3903 | 1.2018 | 2.8671 | 1.0446 | 1.0945 | 7.6299 | 0 | 29.267 | 169.9314 | 0.7512%
CZ 7 | 0.43965 | 0.028857 | 0.047604 | 0.35614 | 0 | 0.18661 | 0 | 0.2769 | 0.062835 | 0.014025 | 0.027778 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 1.8167 | 0.4899% | CZ 7 | 14.8126 | 0.97225 | 3.393 | 35.6139 | 0 | 6.2871 | 0 | 9.3293 | 2.117 | 0.47252 | 0.93588 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 88.2348 | 0.4899% | CZ 7 | 4.3401 | 0.28487 | 0.20357 | 0 | 0 | 1.8421 | 0 | 2.7335 | 0.62029 | 0.13845 | 0.27421 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 13.9104 | 0.4899% | CZ 7 | 0 | 0 | 0.026982 | 0.35614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.40759 | 0.4899% | CZ 7 | 45.4364 | 2.9823 | 5.0803 | 38.926 | 0 | 19.2852 | 0 | 28.6169 | 6.4938 | 1.4494 | 2.8707 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 190.1773 | 0.4899%
CZ 8 | 0.43965 | 0.028698 | 0.049359 | 0.53348 | 0 | 0.087004 | 0 | 0.26988 | 0.061366 | 0.0098632 | 0.027638 | 0.010107 | 0.010592 | 0.072419 | 0 | 0.28319 | 1.8833 | 0.08174% | CZ 8 | 14.8126 | 0.9669 | 3.5685 | 53.348 | 0 | 2.9313 | 0 | 9.0927 | 2.0675 | 0.33231 | 0.93116 | 0.34054 | 0.35685 | 4.0625 | 0 | 9.5412 | 102.3522 | 0.08174% | CZ 8 | 4.3401 | 0.2833 | 0.20357 | 0 | 0 | 0.85887 | 0 | 2.6642 | 0.60579 | 0.097367 | 0.27283 | 0.099777 | 0.10456 | 0.47333 | 0 | 2.7956 | 12.7992 | 0.08174% | CZ 8 | 0 | 0 | 0.028737 | 0.53348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.58669 | 0.08174% | CZ 8 | 45.4364 | 2.9659 | 5.2721 | 58.3094 | 0 | 8.9915 | 0 | 27.8912 | 6.342 | 1.0193 | 2.8562 | 1.0446 | 1.0946 | 7.6299 | 0 | 29.267 | 198.1203 | 0.08174%
US Weighted | 0.43965 | 0.028922 | 0.042086 | 0.10791 | 0 | 0.44641 | 0 | 0.24316 | 0.073218 | 0.024298 | 0.0282 | 0.010107 | 0.01059 | 0.072419 | 0 | 0.28319 | 1.8102 | 100% | US Weighted | 14.8126 | 0.97442 | 2.8414 | 10.7907 | 0 | 15.0403 | 0 | 8.1925 | 2.4668 | 0.81864 | 0.95009 | 0.34054 | 0.3568 | 4.0625 | 0 | 9.5412 | 71.1886 | 100% | US Weighted | 4.3401 | 0.28551 | 0.20355 | 0 | 0 | 4.4068 | 0 | 2.4004 | 0.72279 | 0.23986 | 0.27838 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 16.3506 | 100% | US Weighted | 0 | 0 | 0.021467 | 0.10791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15384 | 100% | US Weighted | 45.4364 | 2.989 | 4.4772 | 11.7943 | 0 | 46.1348 | 0 | 25.1299 | 7.5668 | 2.5111 | 2.9143 | 1.0446 | 1.0944 | 7.6299 | 0 | 29.267 | 187.9898 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Secondary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 210887 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 210887 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.31197 | 0.019899 | 7.9805e-05 | -0.0055533 | 0 | 0.54429 | 0 | 0.16559 | 0.054057 | 0.037087 | 0.0046314 | 0.0013276 | 0.0066262 | 0 | 0 | 0.027131 | 1.1671 | 3.045% | CZ 1A | 10.5108 | 0.67042 | 0.0067418 | -0.55533 | 0 | 18.338 | 0 | 5.5791 | 1.8213 | 1.2495 | 0.15604 | 0.04473 | 0.22325 | 0 | 0 | 0.91407 | 38.9586 | 3.045% | CZ 1A | 3.0797 | 0.19643 | 0.00018441 | 0 | 0 | 5.373 | 0 | 1.6347 | 0.53363 | 0.36611 | 0.04572 | 0.013106 | 0.065412 | 0 | 0 | 0.26782 | 11.5758 | 3.045% | CZ 1A | 0 | 0 | 6.1124e-05 | -0.0055533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0054922 | 3.045% | CZ 1A | 32.2409 | 2.0564 | 0.0086114 | -0.60698 | 0 | 56.2504 | 0 | 17.1134 | 5.5866 | 3.8328 | 0.47864 | 0.13721 | 0.68479 | 0 | 0 | 2.8038 | 120.5866 | 3.045%
CZ 1B | 0.31359 | 0.019879 | 2.0225e-05 | 0.01333 | 0 | 0.32448 | 0 | 0.091935 | 0.03121 | 0.023955 | 0.0056868 | 0.0013276 | 0.0066275 | 0 | 0 | 0.027131 | 0.85917 | 0% | CZ 1B | 10.5655 | 0.66974 | 0.0020225 | 1.333 | 0 | 10.9322 | 0 | 3.0975 | 1.0515 | 0.80708 | 0.1916 | 0.04473 | 0.22329 | 0 | 0 | 0.91407 | 29.8322 | 0% | CZ 1B | 3.0957 | 0.19623 | 0 | 0 | 0 | 3.2031 | 0 | 0.90756 | 0.30809 | 0.23647 | 0.056139 | 0.013106 | 0.065425 | 0 | 0 | 0.26782 | 8.3497 | 0% | CZ 1B | 0 | 0 | 2.0225e-05 | 0.01333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013351 | 0% | CZ 1B | 32.4087 | 2.0544 | 0.0022106 | 1.457 | 0 | 33.5335 | 0 | 9.5012 | 3.2254 | 2.4757 | 0.58771 | 0.13721 | 0.68493 | 0 | 0 | 2.8038 | 88.8718 | 0%
CZ 2A | 0.31256 | 0.019873 | 7.0816e-05 | 0.0062603 | 0 | 0.53885 | 0 | 0.15405 | 0.064829 | 0.03867 | 0.0046221 | 0.0013276 | 0.0066315 | 0 | 0 | 0.027131 | 1.1749 | 15.33% | CZ 2A | 10.5307 | 0.66956 | 0.0058429 | 0.62603 | 0 | 18.1546 | 0 | 5.1901 | 2.1842 | 1.3028 | 0.15572 | 0.04473 | 0.22343 | 0 | 0 | 0.91407 | 40.0019 | 15.33% | CZ 2A | 3.0855 | 0.19618 | 0.00018441 | 0 | 0 | 5.3193 | 0 | 1.5207 | 0.63997 | 0.38173 | 0.045627 | 0.013106 | 0.065464 | 0 | 0 | 0.26782 | 11.5356 | 15.33% | CZ 2A | 0 | 0 | 5.2135e-05 | 0.0062603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063124 | 15.33% | CZ 2A | 32.3021 | 2.0538 | 0.0076289 | 0.68425 | 0 | 55.6878 | 0 | 15.9203 | 6.6998 | 3.9964 | 0.47767 | 0.13721 | 0.68535 | 0 | 0 | 2.8038 | 121.4562 | 15.33%
CZ 2B | 0.30992 | 0.019885 | 2.4719e-05 | 0.018526 | 0 | 0.23836 | 0 | 0.12234 | 0.037916 | 0.017865 | 0.0053733 | 0.0013276 | 0.0066262 | 0 | 0 | 0.027131 | 0.80529 | 2.216% | CZ 2B | 10.4418 | 0.66997 | 0.0024719 | 1.8526 | 0 | 8.0306 | 0 | 4.1219 | 1.2774 | 0.60191 | 0.18103 | 0.04473 | 0.22325 | 0 | 0 | 0.91407 | 28.3617 | 2.216% | CZ 2B | 3.0595 | 0.1963 | 0 | 0 | 0 | 2.353 | 0 | 1.2077 | 0.37429 | 0.17636 | 0.053043 | 0.013106 | 0.065412 | 0 | 0 | 0.26782 | 7.7665 | 2.216% | CZ 2B | 0 | 0 | 2.4719e-05 | 0.018526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01855 | 2.216% | CZ 2B | 32.0295 | 2.0551 | 0.0027018 | 2.0248 | 0 | 24.6333 | 0 | 12.6434 | 3.9185 | 1.8463 | 0.55531 | 0.13721 | 0.68479 | 0 | 0 | 2.8038 | 83.3347 | 2.216%
CZ 3A | 0.30942 | 0.019881 | 6.4524e-05 | 0.028952 | 0 | 0.30289 | 0 | 0.14297 | 0.060974 | 0.023533 | 0.0043805 | 0.0013276 | 0.0066275 | 0 | 0 | 0.027131 | 0.92816 | 19.18% | CZ 3A | 10.425 | 0.66983 | 0.0052137 | 2.8952 | 0 | 10.2048 | 0 | 4.817 | 2.0543 | 0.79288 | 0.14759 | 0.04473 | 0.22329 | 0 | 0 | 0.91407 | 33.194 | 19.18% | CZ 3A | 3.0545 | 0.19626 | 0.00018441 | 0 | 0 | 2.99 | 0 | 1.4114 | 0.60192 | 0.23231 | 0.043243 | 0.013106 | 0.065425 | 0 | 0 | 0.26782 | 8.8762 | 19.18% | CZ 3A | 0 | 0 | 4.5843e-05 | 0.028952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028998 | 19.18% | CZ 3A | 31.9779 | 2.0547 | 0.0069412 | 3.1645 | 0 | 31.3025 | 0 | 14.7759 | 6.3015 | 2.4321 | 0.45271 | 0.13721 | 0.68493 | 0 | 0 | 2.8038 | 96.0946 | 19.18%
CZ 3B | 0.30819 | 0.019881 | 2.427e-05 | 0.0088603 | 0 | 0.1417 | 0 | 0.12088 | 0.038411 | 0.011037 | 0.0053226 | 0.0013276 | 0.0066289 | 0 | 0 | 0.027131 | 0.68939 | 7.906% | CZ 3B | 10.3835 | 0.66983 | 0.002427 | 0.88603 | 0 | 4.7741 | 0 | 4.0726 | 1.2941 | 0.37187 | 0.17933 | 0.04473 | 0.22334 | 0 | 0 | 0.91407 | 23.8159 | 7.906% | CZ 3B | 3.0424 | 0.19626 | 0 | 0 | 0 | 1.3988 | 0 | 1.1933 | 0.37918 | 0.10896 | 0.052543 | 0.013106 | 0.065438 | 0 | 0 | 0.26782 | 6.7177 | 7.906% | CZ 3B | 0 | 0 | 2.427e-05 | 0.0088603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088846 | 7.906% | CZ 3B | 31.8505 | 2.0547 | 0.0026527 | 0.96843 | 0 | 14.644 | 0 | 12.4924 | 3.9696 | 1.1407 | 0.55007 | 0.13721 | 0.68507 | 0 | 0 | 2.8038 | 71.2992 | 7.906%
CZ 3C | 0.30846 | 0.019845 | 5.6434e-05 | 0.016304 | 0 | 0.14539 | 0 | 0.13176 | 0 | 0.013858 | 0.0044526 | 0.0013276 | 0.0066275 | 0 | 0 | 0.027131 | 0.67522 | 1.057% | CZ 3C | 10.3926 | 0.66862 | 0.0044047 | 1.6304 | 0 | 4.8984 | 0 | 4.4393 | 0 | 0.4669 | 0.15002 | 0.04473 | 0.22329 | 0 | 0 | 0.91407 | 23.8328 | 1.057% | CZ 3C | 3.045 | 0.19591 | 0.00018441 | 0 | 0 | 1.4352 | 0 | 1.3007 | 0 | 0.1368 | 0.043955 | 0.013106 | 0.065425 | 0 | 0 | 0.26782 | 6.5042 | 1.057% | CZ 3C | 0 | 0 | 3.7753e-05 | 0.016304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016342 | 1.057% | CZ 3C | 31.8783 | 2.0509 | 0.006057 | 1.7821 | 0 | 15.0255 | 0 | 13.6173 | 0 | 1.4322 | 0.46016 | 0.13721 | 0.68493 | 0 | 0 | 2.8038 | 69.8785 | 1.057%
CZ 4A | 0.3122 | 0.019791 | 7.1251e-05 | 0.10173 | 0 | 0.19679 | 0 | 0.13653 | 0.054843 | 0.017532 | 0.0042578 | 0.0013276 | 0.0066275 | 0 | 0 | 0.027131 | 0.87882 | 18.98% | CZ 4A | 10.5184 | 0.66678 | 0.005798 | 10.1726 | 0 | 6.6303 | 0 | 4.6 | 1.8477 | 0.59067 | 0.14345 | 0.04473 | 0.22329 | 0 | 0 | 0.91407 | 36.3577 | 18.98% | CZ 4A | 3.0819 | 0.19537 | 0.00019758 | 0 | 0 | 1.9427 | 0 | 1.3478 | 0.54139 | 0.17307 | 0.042031 | 0.013106 | 0.065425 | 0 | 0 | 0.26782 | 7.6707 | 18.98% | CZ 4A | 0 | 0 | 5.1237e-05 | 0.10173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10178 | 18.98% | CZ 4A | 32.2643 | 2.0453 | 0.0076686 | 11.1186 | 0 | 20.3378 | 0 | 14.11 | 5.6678 | 1.8118 | 0.44003 | 0.13721 | 0.68493 | 0 | 0 | 2.8038 | 91.4293 | 18.98%
CZ 4B | 0.31308 | 0.01986 | 7.1715e-05 | 0.010378 | 0 | 0.13201 | 0 | 0.16084 | 0.04036 | 0.011048 | 0.0041991 | 0.0013276 | 0.0066302 | 0 | 0 | 0.027131 | 0.72693 | 0.5989% | CZ 4B | 10.5482 | 0.66911 | 0.0059328 | 1.0378 | 0 | 4.4476 | 0 | 5.4189 | 1.3598 | 0.37223 | 0.14147 | 0.04473 | 0.22338 | 0 | 0 | 0.91407 | 25.1832 | 0.5989% | CZ 4B | 3.0906 | 0.19605 | 0.00018441 | 0 | 0 | 1.3031 | 0 | 1.5877 | 0.39842 | 0.10906 | 0.041452 | 0.013106 | 0.065451 | 0 | 0 | 0.26782 | 7.073 | 0.5989% | CZ 4B | 0 | 0 | 5.3034e-05 | 0.010378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010431 | 0.5989% | CZ 4B | 32.3559 | 2.0524 | 0.0077272 | 1.1343 | 0 | 13.6425 | 0 | 16.6219 | 4.1711 | 1.1418 | 0.43396 | 0.13721 | 0.68521 | 0 | 0 | 2.8038 | 75.1878 | 0.5989%
CZ 4C | 0.30984 | 0.01975 | 6.0914e-05 | 0.028104 | 0 | 0.058104 | 0 | 0.14353 | 0.041228 | 0.0074828 | 0.0042151 | 0.0013276 | 0.0066262 | 0 | 0 | 0.027131 | 0.6474 | 2.262% | CZ 4C | 10.4391 | 0.66543 | 0.0047643 | 2.8104 | 0 | 1.9576 | 0 | 4.8357 | 1.389 | 0.25211 | 0.14201 | 0.04473 | 0.22325 | 0 | 0 | 0.91407 | 23.6782 | 2.262% | CZ 4C | 3.0587 | 0.19497 | 0.00019758 | 0 | 0 | 0.57358 | 0 | 1.4169 | 0.40698 | 0.073868 | 0.04161 | 0.013106 | 0.065412 | 0 | 0 | 0.26782 | 6.1131 | 2.262% | CZ 4C | 0 | 0 | 4.0899e-05 | 0.028104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028145 | 2.262% | CZ 4C | 32.0211 | 2.0411 | 0.0065387 | 3.0718 | 0 | 6.0048 | 0 | 14.8331 | 4.2607 | 0.77332 | 0.43561 | 0.13721 | 0.68479 | 0 | 0 | 2.8038 | 67.074 | 2.262%
CZ 5A | 0.3129 | 0.019831 | 7.1265e-05 | 0.12985 | 0 | 0.12186 | 0 | 0.16038 | 0.031797 | 0.012006 | 0.0041684 | 0.0013276 | 0.0066262 | 0 | 0 | 0.027131 | 0.82795 | 20.76% | CZ 5A | 10.542 | 0.66812 | 0.0058879 | 12.9855 | 0 | 4.1056 | 0 | 5.4036 | 1.0713 | 0.40451 | 0.14044 | 0.04473 | 0.22325 | 0 | 0 | 0.91407 | 36.509 | 20.76% | CZ 5A | 3.0888 | 0.19576 | 0.00018441 | 0 | 0 | 1.2029 | 0 | 1.5832 | 0.31389 | 0.11852 | 0.041149 | 0.013106 | 0.065412 | 0 | 0 | 0.26782 | 6.8908 | 20.76% | CZ 5A | 0 | 0 | 5.2585e-05 | 0.12985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12991 | 20.76% | CZ 5A | 32.3368 | 2.0494 | 0.0076781 | 14.1931 | 0 | 12.5935 | 0 | 16.575 | 3.2861 | 1.2408 | 0.43079 | 0.13721 | 0.68479 | 0 | 0 | 2.8038 | 86.3391 | 20.76%
CZ 5B | 0.31252 | 0.019812 | 7.2164e-05 | 0.022083 | 0 | 0.11729 | 0 | 0.16213 | 0.055059 | 0.01084 | 0.0041484 | 0.0013276 | 0.0066289 | 0 | 0 | 0.027131 | 0.73905 | 4.314% | CZ 5B | 10.5295 | 0.66749 | 0.0059777 | 2.2083 | 0 | 3.9517 | 0 | 5.4626 | 1.855 | 0.36522 | 0.13977 | 0.04473 | 0.22334 | 0 | 0 | 0.91407 | 26.3677 | 4.314% | CZ 5B | 3.0851 | 0.19558 | 0.00018441 | 0 | 0 | 1.1579 | 0 | 1.6005 | 0.54352 | 0.10701 | 0.040951 | 0.013106 | 0.065438 | 0 | 0 | 0.26782 | 7.0771 | 4.314% | CZ 5B | 0 | 0 | 5.3484e-05 | 0.022083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022137 | 4.314% | CZ 5B | 32.2982 | 2.0475 | 0.0077763 | 2.4137 | 0 | 12.1216 | 0 | 16.7559 | 5.6902 | 1.1203 | 0.42872 | 0.13721 | 0.68507 | 0 | 0 | 2.8038 | 76.51 | 4.314%
CZ 5C | 0.31088 | 0.019754 | 6.0465e-05 | 0.078955 | 0 | 0.03613 | 0 | 0.1438 | 0.023188 | 0.0049089 | 0.0041804 | 0.0013276 | 0.0066302 | 0 | 0 | 0.027131 | 0.65694 | 0.08114% | CZ 5C | 10.4741 | 0.66556 | 0.0047193 | 7.8955 | 0 | 1.2173 | 0 | 4.8447 | 0.78123 | 0.16539 | 0.14084 | 0.04473 | 0.22338 | 0 | 0 | 0.91407 | 27.3716 | 0.08114% | CZ 5C | 3.0689 | 0.19501 | 0.00019758 | 0 | 0 | 0.35667 | 0 | 1.4195 | 0.2289 | 0.048459 | 0.041267 | 0.013106 | 0.065451 | 0 | 0 | 0.26782 | 5.7053 | 0.08114% | CZ 5C | 0 | 0 | 4.045e-05 | 0.078955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078996 | 0.08114% | CZ 5C | 32.1285 | 2.0416 | 0.0064896 | 8.6298 | 0 | 3.734 | 0 | 14.8608 | 2.3964 | 0.50732 | 0.43203 | 0.13721 | 0.68521 | 0 | 0 | 2.8038 | 68.3631 | 0.08114%
CZ 6A | 0.31409 | 0.019803 | 7.9355e-05 | 0.19283 | 0 | 0.12555 | 0 | 0.16791 | 0.030151 | 0.013753 | 0.0041617 | 0.0013276 | 0.0066302 | 0 | 0 | 0.027131 | 0.90342 | 2.944% | CZ 6A | 10.5823 | 0.66718 | 0.0066969 | 19.2833 | 0 | 4.2301 | 0 | 5.657 | 1.0159 | 0.46335 | 0.14022 | 0.04473 | 0.22338 | 0 | 0 | 0.91407 | 43.2282 | 2.944% | CZ 6A | 3.1006 | 0.19548 | 0.00018441 | 0 | 0 | 1.2394 | 0 | 1.6575 | 0.29764 | 0.13576 | 0.041083 | 0.013106 | 0.065451 | 0 | 0 | 0.26782 | 7.0141 | 2.944% | CZ 6A | 0 | 0 | 6.0675e-05 | 0.19283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19289 | 2.944% | CZ 6A | 32.4604 | 2.0465 | 0.0085623 | 21.0767 | 0 | 12.9754 | 0 | 17.3525 | 3.116 | 1.4213 | 0.4301 | 0.13721 | 0.68521 | 0 | 0 | 2.8038 | 94.5137 | 2.944%
CZ 6B | 0.3145 | 0.019792 | 7.3962e-05 | 0.14576 | 0 | 0.085373 | 0 | 0.16296 | 0.029283 | 0.0092908 | 0.004091 | 0.0013276 | 0.0066289 | 0 | 0 | 0.027131 | 0.80621 | 0.7512% | CZ 6B | 10.596 | 0.66682 | 0.0061575 | 14.5761 | 0 | 2.8764 | 0 | 5.4902 | 0.98659 | 0.31302 | 0.13783 | 0.04473 | 0.22334 | 0 | 0 | 0.91407 | 36.8313 | 0.7512% | CZ 6B | 3.1046 | 0.19538 | 0.00018441 | 0 | 0 | 0.84278 | 0 | 1.6086 | 0.28907 | 0.091716 | 0.040385 | 0.013106 | 0.065438 | 0 | 0 | 0.26782 | 6.5192 | 0.7512% | CZ 6B | 0 | 0 | 5.5282e-05 | 0.14576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14582 | 0.7512% | CZ 6B | 32.5025 | 2.0454 | 0.0079728 | 15.9316 | 0 | 8.823 | 0 | 16.8409 | 3.0263 | 0.96017 | 0.42279 | 0.13721 | 0.68507 | 0 | 0 | 2.8038 | 84.1867 | 0.7512%
CZ 7 | 0.31478 | 0.019742 | 8.0704e-05 | 0.23922 | 0 | 0.099445 | 0 | 0.17904 | 0.031991 | 0.0097511 | 0.0041204 | 0.0013276 | 0.0066302 | 0 | 0 | 0.027131 | 0.93326 | 0.4899% | CZ 7 | 10.6053 | 0.66516 | 0.0068317 | 23.9218 | 0 | 3.3505 | 0 | 6.0323 | 1.0778 | 0.32853 | 0.13882 | 0.04473 | 0.22338 | 0 | 0 | 0.91407 | 47.3093 | 0.4899% | CZ 7 | 3.1074 | 0.19489 | 0.00018441 | 0 | 0 | 0.98169 | 0 | 1.7675 | 0.31581 | 0.09626 | 0.040675 | 0.013106 | 0.065451 | 0 | 0 | 0.26782 | 6.8507 | 0.4899% | CZ 7 | 0 | 0 | 6.2023e-05 | 0.23922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23928 | 0.4899% | CZ 7 | 32.531 | 2.0403 | 0.0087097 | 26.1466 | 0 | 10.2773 | 0 | 18.5035 | 3.3062 | 1.0077 | 0.42582 | 0.13721 | 0.68521 | 0 | 0 | 2.8038 | 97.8734 | 0.4899%
CZ 8 | 0.30558 | 0.019235 | 7.9819e-05 | 0.32387 | 0 | 0.049636 | 0 | 0.17221 | 0.027974 | 0.0074308 | 0.004051 | 0.0013276 | 0.0066249 | 0 | 0 | 0.027131 | 0.94515 | 0.08174% | CZ 8 | 10.2954 | 0.64807 | 0.0068317 | 32.3872 | 0 | 1.6723 | 0 | 5.802 | 0.94249 | 0.25036 | 0.13648 | 0.04473 | 0.2232 | 0 | 0 | 0.91407 | 53.3232 | 0.08174% | CZ 8 | 3.0166 | 0.18989 | 0.00017123 | 0 | 0 | 0.48999 | 0 | 1.7 | 0.27615 | 0.073354 | 0.03999 | 0.013106 | 0.065398 | 0 | 0 | 0.26782 | 6.1324 | 0.08174% | CZ 8 | 0 | 0 | 6.2473e-05 | 0.32387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32393 | 0.08174% | CZ 8 | 31.5803 | 1.9879 | 0.0086209 | 35.3992 | 0 | 5.1297 | 0 | 17.7972 | 2.891 | 0.76794 | 0.41865 | 0.13721 | 0.68466 | 0 | 0 | 2.8038 | 99.6064 | 0.08174%
US Weighted | 0.3115 | 0.019842 | 6.5368e-05 | 0.063818 | 0 | 0.25002 | 0 | 0.14746 | 0.049024 | 0.020043 | 0.0044299 | 0.0013276 | 0.006628 | 0 | 0 | 0.027131 | 0.90128 | 100% | US Weighted | 10.4949 | 0.66851 | 0.0054047 | 6.3818 | 0 | 8.4234 | 0 | 4.9682 | 1.6517 | 0.67527 | 0.14925 | 0.04473 | 0.22331 | 0 | 0 | 0.91407 | 34.6006 | 100% | US Weighted | 3.075 | 0.19587 | 0.00016854 | 0 | 0 | 2.4681 | 0 | 1.4557 | 0.48395 | 0.19785 | 0.043731 | 0.013106 | 0.06543 | 0 | 0 | 0.26782 | 8.2667 | 100% | US Weighted | 0 | 0 | 4.8294e-05 | 0.063818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063866 | 100% | US Weighted | 32.1922 | 2.0506 | 0.007043 | 6.9753 | 0 | 25.8382 | 0 | 15.2395 | 5.0665 | 2.0713 | 0.45782 | 0.13721 | 0.68498 | 0 | 0 | 2.8038 | 93.5245 | 100%
Building Type: | Secondary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 210887 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 210887 | [17 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 70.96% | 68.67% | 0.2175% | -287% | 0% | 56.7% | 0% | 60.82% | 55.28% | 84.25% | 16.23% | 13.14% | 62.58% | 0% | 0% | 9.58% | 51.05% | 3.045% | CZ 1A | 70.96% | 68.67% | 0.2929% | -287% | 0% | 56.7% | 0% | 60.82% | 55.28% | 84.25% | 16.23% | 13.14% | 62.58% | 0% | 0% | 9.58% | 48.8% | 3.045% | CZ 1A | 70.96% | 68.67% | 0.09059% | 0% | 0% | 56.7% | 0% | 60.82% | 55.28% | 84.25% | 16.23% | 13.14% | 62.58% | 0% | 0% | 9.58% | 52.26% | 3.045% | CZ 1A | 0% | 0% | 0.3804% | -287% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -12.93% | 3.045% | CZ 1A | 70.96% | 68.67% | 0.2215% | -287% | 0% | 56.7% | 0% | 60.82% | 55.28% | 84.25% | 16.23% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.98% | 3.045%
CZ 1B | 71.33% | 68.69% | 0.05434% | 50.02% | 0% | 38.7% | 0% | 41.41% | 47.08% | 77.74% | 19.24% | 13.14% | 62.6% | 0% | 0% | 9.58% | 40.99% | 0% | CZ 1B | 71.33% | 68.69% | 0.08584% | 50.02% | 0% | 38.7% | 0% | 41.41% | 47.08% | 77.74% | 19.24% | 13.14% | 62.6% | 0% | 0% | 9.58% | 39.72% | 0% | CZ 1B | 71.33% | 68.69% | 0% | 0% | 0% | 38.7% | 0% | 41.41% | 47.08% | 77.74% | 19.24% | 13.14% | 62.6% | 0% | 0% | 9.58% | 41.7% | 0% | CZ 1B | 0% | 0% | 0.1217% | 50.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.71% | 0% | CZ 1B | 71.33% | 68.69% | 0.05602% | 50.02% | 0% | 38.7% | 0% | 41.41% | 47.08% | 77.74% | 19.24% | 13.14% | 62.6% | 0% | 0% | 9.58% | 40.95% | 0%
CZ 2A | 71.09% | 68.7% | 0.184% | 27.59% | 0% | 60.02% | 0% | 60.68% | 68.81% | 85.56% | 16.21% | 13.14% | 62.61% | 0% | 0% | 9.58% | 52.79% | 15.33% | CZ 2A | 71.09% | 68.7% | 0.2355% | 27.59% | 0% | 60.02% | 0% | 60.68% | 68.81% | 85.56% | 16.21% | 13.14% | 62.61% | 0% | 0% | 9.58% | 50.45% | 15.33% | CZ 2A | 71.09% | 68.7% | 0.09059% | 0% | 0% | 60.02% | 0% | 60.68% | 68.81% | 85.56% | 16.21% | 13.14% | 62.61% | 0% | 0% | 9.58% | 54.08% | 15.33% | CZ 2A | 0% | 0% | 0.2918% | 27.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.708% | 15.33% | CZ 2A | 71.09% | 68.7% | 0.1868% | 27.59% | 0% | 60.02% | 0% | 60.68% | 68.81% | 85.56% | 16.21% | 13.14% | 62.61% | 0% | 0% | 9.58% | 52.72% | 15.33%
CZ 2B | 70.49% | 68.69% | 0.06388% | 54.24% | 0% | 46.22% | 0% | 54.38% | 60.6% | 77.92% | 18.46% | 13.14% | 62.58% | 0% | 0% | 9.58% | 45.42% | 2.216% | CZ 2B | 70.49% | 68.69% | 0.09873% | 54.24% | 0% | 46.22% | 0% | 54.38% | 60.6% | 77.92% | 18.46% | 13.14% | 62.58% | 0% | 0% | 9.58% | 43.75% | 2.216% | CZ 2B | 70.49% | 68.69% | 0% | 0% | 0% | 46.22% | 0% | 54.38% | 60.6% | 77.92% | 18.46% | 13.14% | 62.58% | 0% | 0% | 9.58% | 46.38% | 2.216% | CZ 2B | 0% | 0% | 0.1366% | 54.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.18% | 2.216% | CZ 2B | 70.49% | 68.69% | 0.06579% | 54.24% | 0% | 46.22% | 0% | 54.38% | 60.6% | 77.92% | 18.46% | 13.14% | 62.58% | 0% | 0% | 9.58% | 45.37% | 2.216%
CZ 3A | 70.38% | 68.69% | 0.1566% | 44.95% | 0% | 57.92% | 0% | 60.72% | 70.87% | 83.26% | 15.55% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.13% | 19.18% | CZ 3A | 70.38% | 68.69% | 0.1893% | 44.95% | 0% | 57.92% | 0% | 60.72% | 70.87% | 83.26% | 15.55% | 13.14% | 62.58% | 0% | 0% | 9.58% | 47.67% | 19.18% | CZ 3A | 70.38% | 68.69% | 0.09059% | 0% | 0% | 57.92% | 0% | 60.72% | 70.87% | 83.26% | 15.55% | 13.14% | 62.58% | 0% | 0% | 9.58% | 51.62% | 19.18% | CZ 3A | 0% | 0% | 0.2227% | 44.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.49% | 19.18% | CZ 3A | 70.38% | 68.69% | 0.1584% | 44.95% | 0% | 57.92% | 0% | 60.72% | 70.87% | 83.26% | 15.55% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.05% | 19.18%
CZ 3B | 70.1% | 68.69% | 0.05993% | 19.13% | 0% | 40.18% | 0% | 54.44% | 100% | 68.23% | 18.32% | 13.14% | 62.59% | 0% | 0% | 9.58% | 43.36% | 7.906% | CZ 3B | 70.1% | 68.69% | 0.09044% | 19.13% | 0% | 40.18% | 0% | 54.44% | 100% | 68.23% | 18.32% | 13.14% | 62.59% | 0% | 0% | 9.58% | 39.97% | 7.906% | CZ 3B | 70.1% | 68.69% | 0% | 0% | 0% | 40.18% | 0% | 54.44% | 100% | 68.23% | 18.32% | 13.14% | 62.59% | 0% | 0% | 9.58% | 45.39% | 7.906% | CZ 3B | 0% | 0% | 0.122% | 19.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.798% | 7.906% | CZ 3B | 70.1% | 68.69% | 0.06164% | 19.13% | 0% | 40.18% | 0% | 54.44% | 100% | 68.23% | 18.32% | 13.14% | 62.59% | 0% | 0% | 9.58% | 43.25% | 7.906%
CZ 3C | 70.16% | 68.57% | 0.1375% | 35.87% | 0% | 50.58% | 0% | 58.97% | 0% | 82.21% | 15.77% | 13.14% | 62.58% | 0% | 0% | 9.58% | 45.4% | 1.057% | CZ 3C | 70.16% | 68.57% | 0.1609% | 35.87% | 0% | 50.58% | 0% | 58.97% | 0% | 82.21% | 15.77% | 13.14% | 62.58% | 0% | 0% | 9.58% | 42.48% | 1.057% | CZ 3C | 70.16% | 68.57% | 0.09059% | 0% | 0% | 50.58% | 0% | 58.97% | 0% | 82.21% | 15.77% | 13.14% | 62.58% | 0% | 0% | 9.58% | 47.16% | 1.057% | CZ 3C | 0% | 0% | 0.1849% | 35.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.09% | 1.057% | CZ 3C | 70.16% | 68.57% | 0.1388% | 35.87% | 0% | 50.58% | 0% | 58.97% | 0% | 82.21% | 15.77% | 13.14% | 62.58% | 0% | 0% | 9.58% | 45.3% | 1.057%
CZ 4A | 71.01% | 68.48% | 0.1649% | 72.48% | 0% | 55.32% | 0% | 59.19% | 64.27% | 82.3% | 15.2% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.23% | 18.98% | CZ 4A | 71.01% | 68.48% | 0.1964% | 72.48% | 0% | 55.32% | 0% | 59.19% | 64.27% | 82.3% | 15.2% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.94% | 18.98% | CZ 4A | 71.01% | 68.48% | 0.09706% | 0% | 0% | 55.32% | 0% | 59.19% | 64.27% | 82.3% | 15.2% | 13.14% | 62.58% | 0% | 0% | 9.58% | 49.75% | 18.98% | CZ 4A | 0% | 0% | 0.2269% | 72.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.31% | 18.98% | CZ 4A | 71.01% | 68.48% | 0.1667% | 72.48% | 0% | 55.32% | 0% | 59.19% | 64.27% | 82.3% | 15.2% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.26% | 18.98%
CZ 4B | 71.21% | 68.67% | 0.1683% | 13.6% | 0% | 47.06% | 0% | 59.85% | 100% | 70.51% | 15.05% | 13.14% | 62.6% | 0% | 0% | 9.58% | 45.52% | 0.5989% | CZ 4B | 71.21% | 68.67% | 0.205% | 13.6% | 0% | 47.06% | 0% | 59.85% | 100% | 70.51% | 15.05% | 13.14% | 62.6% | 0% | 0% | 9.58% | 40.65% | 0.5989% | CZ 4B | 71.21% | 68.67% | 0.09059% | 0% | 0% | 47.06% | 0% | 59.85% | 100% | 70.51% | 15.05% | 13.14% | 62.6% | 0% | 0% | 9.58% | 48.6% | 0.5989% | CZ 4B | 0% | 0% | 0.2411% | 13.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.497% | 0.5989% | CZ 4B | 71.21% | 68.67% | 0.1704% | 13.6% | 0% | 47.06% | 0% | 59.85% | 100% | 70.51% | 15.05% | 13.14% | 62.6% | 0% | 0% | 9.58% | 45.36% | 0.5989%
CZ 4C | 70.47% | 68.42% | 0.14% | 23.46% | 0% | 48.85% | 0% | 62.94% | 100% | 83.43% | 15.08% | 13.14% | 62.58% | 0% | 0% | 9.58% | 45.17% | 2.262% | CZ 4C | 70.47% | 68.42% | 0.1597% | 23.46% | 0% | 48.85% | 0% | 62.94% | 100% | 83.43% | 15.08% | 13.14% | 62.58% | 0% | 0% | 9.58% | 39.88% | 2.262% | CZ 4C | 70.47% | 68.42% | 0.09706% | 0% | 0% | 48.85% | 0% | 62.94% | 100% | 83.43% | 15.08% | 13.14% | 62.58% | 0% | 0% | 9.58% | 48.91% | 2.262% | CZ 4C | 0% | 0% | 0.1787% | 23.46% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 16.84% | 2.262% | CZ 4C | 70.47% | 68.42% | 0.1412% | 23.46% | 0% | 48.85% | 0% | 62.94% | 100% | 83.43% | 15.08% | 13.14% | 62.58% | 0% | 0% | 9.58% | 44.98% | 2.262%
CZ 5A | 71.17% | 68.6% | 0.159% | 69.02% | 0% | 55.06% | 0% | 63.62% | 52.98% | 81.61% | 14.95% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.06% | 20.76% | CZ 5A | 71.17% | 68.6% | 0.189% | 69.02% | 0% | 55.06% | 0% | 63.62% | 52.98% | 81.61% | 14.95% | 13.14% | 62.58% | 0% | 0% | 9.58% | 51.11% | 20.76% | CZ 5A | 71.17% | 68.6% | 0.09059% | 0% | 0% | 55.06% | 0% | 63.62% | 52.98% | 81.61% | 14.95% | 13.14% | 62.58% | 0% | 0% | 9.58% | 49.26% | 20.76% | CZ 5A | 0% | 0% | 0.2172% | 69.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.85% | 20.76% | CZ 5A | 71.17% | 68.6% | 0.1607% | 69.02% | 0% | 55.06% | 0% | 63.62% | 52.98% | 81.61% | 14.95% | 13.14% | 62.58% | 0% | 0% | 9.58% | 50.1% | 20.76%
CZ 5B | 71.08% | 68.53% | 0.1628% | 16.3% | 0% | 51.56% | 0% | 61.15% | 100% | 80.52% | 14.9% | 13.14% | 62.59% | 0% | 0% | 9.58% | 45.8% | 4.314% | CZ 5B | 71.08% | 68.53% | 0.195% | 16.3% | 0% | 51.56% | 0% | 61.15% | 100% | 80.52% | 14.9% | 13.14% | 62.59% | 0% | 0% | 9.58% | 39.62% | 4.314% | CZ 5B | 71.08% | 68.53% | 0.09059% | 0% | 0% | 51.56% | 0% | 61.15% | 100% | 80.52% | 14.9% | 13.14% | 62.59% | 0% | 0% | 9.58% | 50.13% | 4.314% | CZ 5B | 0% | 0% | 0.2257% | 16.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.05% | 4.314% | CZ 5B | 71.08% | 68.53% | 0.1647% | 16.3% | 0% | 51.56% | 0% | 61.15% | 100% | 80.52% | 14.9% | 13.14% | 62.59% | 0% | 0% | 9.58% | 45.58% | 4.314%
CZ 5C | 70.71% | 68.44% | 0.1362% | 61.28% | 0% | 47.18% | 0% | 63.25% | 48.12% | 75.93% | 14.99% | 13.14% | 62.61% | 0% | 0% | 9.58% | 46.77% | 0.08114% | CZ 5C | 70.71% | 68.44% | 0.1537% | 61.28% | 0% | 47.18% | 0% | 63.25% | 48.12% | 75.93% | 14.99% | 13.14% | 62.61% | 0% | 0% | 9.58% | 46.34% | 0.08114% | CZ 5C | 70.71% | 68.44% | 0.09706% | 0% | 0% | 47.18% | 0% | 63.25% | 48.12% | 75.93% | 14.99% | 13.14% | 62.61% | 0% | 0% | 9.58% | 47.09% | 0.08114% | CZ 5C | 0% | 0% | 0.1703% | 61.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.61% | 0.08114% | CZ 5C | 70.71% | 68.44% | 0.1373% | 61.28% | 0% | 47.18% | 0% | 63.25% | 48.12% | 75.93% | 14.99% | 13.14% | 62.61% | 0% | 0% | 9.58% | 46.76% | 0.08114%
CZ 6A | 71.44% | 68.53% | 0.1719% | 66.81% | 0% | 53% | 0% | 63.06% | 49.24% | 81.44% | 14.94% | 13.14% | 62.61% | 0% | 0% | 9.58% | 50.5% | 2.944% | CZ 6A | 71.44% | 68.53% | 0.2061% | 66.81% | 0% | 53% | 0% | 63.06% | 49.24% | 81.44% | 14.94% | 13.14% | 62.61% | 0% | 0% | 9.58% | 52.26% | 2.944% | CZ 6A | 71.44% | 68.53% | 0.09059% | 0% | 0% | 53% | 0% | 63.06% | 49.24% | 81.44% | 14.94% | 13.14% | 62.61% | 0% | 0% | 9.58% | 49% | 2.944% | CZ 6A | 0% | 0% | 0.2375% | 66.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 56.96% | 2.944% | CZ 6A | 71.44% | 68.53% | 0.1739% | 66.81% | 0% | 53% | 0% | 63.06% | 49.24% | 81.44% | 14.94% | 13.14% | 62.61% | 0% | 0% | 9.58% | 50.57% | 2.944%
CZ 6B | 71.53% | 68.54% | 0.1615% | 67.62% | 0% | 53.11% | 0% | 62.47% | 47.36% | 79.9% | 14.75% | 13.14% | 62.59% | 0% | 0% | 9.58% | 49.49% | 0.7512% | CZ 6B | 71.53% | 68.54% | 0.1918% | 67.62% | 0% | 53.11% | 0% | 62.47% | 47.36% | 79.9% | 14.75% | 13.14% | 62.59% | 0% | 0% | 9.58% | 50.82% | 0.7512% | CZ 6B | 71.53% | 68.54% | 0.09059% | 0% | 0% | 53.11% | 0% | 62.47% | 47.36% | 79.9% | 14.75% | 13.14% | 62.59% | 0% | 0% | 9.58% | 48.42% | 0.7512% | CZ 6B | 0% | 0% | 0.2197% | 67.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.98% | 0.7512% | CZ 6B | 71.53% | 68.54% | 0.1633% | 67.62% | 0% | 53.11% | 0% | 62.47% | 47.36% | 79.9% | 14.75% | 13.14% | 62.59% | 0% | 0% | 9.58% | 49.54% | 0.7512%
CZ 7 | 71.6% | 68.41% | 0.1695% | 67.17% | 0% | 53.29% | 0% | 64.66% | 50.91% | 69.53% | 14.83% | 13.14% | 62.6% | 0% | 0% | 9.58% | 51.37% | 0.4899% | CZ 7 | 71.6% | 68.41% | 0.2013% | 67.17% | 0% | 53.29% | 0% | 64.66% | 50.91% | 69.53% | 14.83% | 13.14% | 62.6% | 0% | 0% | 9.58% | 53.62% | 0.4899% | CZ 7 | 71.6% | 68.41% | 0.09059% | 0% | 0% | 53.29% | 0% | 64.66% | 50.91% | 69.53% | 14.83% | 13.14% | 62.6% | 0% | 0% | 9.58% | 49.25% | 0.4899% | CZ 7 | 0% | 0% | 0.2299% | 67.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.71% | 0.4899% | CZ 7 | 71.6% | 68.41% | 0.1714% | 67.17% | 0% | 53.29% | 0% | 64.66% | 50.91% | 69.53% | 14.83% | 13.14% | 62.6% | 0% | 0% | 9.58% | 51.46% | 0.4899%
CZ 8 | 69.5% | 67.03% | 0.1617% | 60.71% | 0% | 57.05% | 0% | 63.81% | 45.59% | 75.34% | 14.66% | 13.14% | 62.55% | 0% | 0% | 9.58% | 50.19% | 0.08174% | CZ 8 | 69.5% | 67.03% | 0.1914% | 60.71% | 0% | 57.05% | 0% | 63.81% | 45.59% | 75.34% | 14.66% | 13.14% | 62.55% | 0% | 0% | 9.58% | 52.1% | 0.08174% | CZ 8 | 69.5% | 67.03% | 0.08412% | 0% | 0% | 57.05% | 0% | 63.81% | 45.59% | 75.34% | 14.66% | 13.14% | 62.55% | 0% | 0% | 9.58% | 47.91% | 0.08174% | CZ 8 | 0% | 0% | 0.2174% | 60.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.21% | 0.08174% | CZ 8 | 69.5% | 67.03% | 0.1635% | 60.71% | 0% | 57.05% | 0% | 63.81% | 45.59% | 75.34% | 14.66% | 13.14% | 62.55% | 0% | 0% | 9.58% | 50.28% | 0.08174%
US Weighted | 70.85% | 68.61% | 0.1553% | 59.14% | 0% | 56.01% | 0% | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% | 0% | 9.58% | 49.79% | 100% | US Weighted | 70.85% | 68.61% | 0.1902% | 59.14% | 0% | 56.01% | 0% | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% | 0% | 9.58% | 48.6% | 100% | US Weighted | 70.85% | 68.61% | 0.0828% | 0% | 0% | 56.01% | 0% | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% | 0% | 9.58% | 50.56% | 100% | US Weighted | 0% | 0% | 0.225% | 59.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.51% | 100% | US Weighted | 70.85% | 68.61% | 0.1573% | 59.14% | 0% | 56.01% | 0% | 60.64% | 66.96% | 82.49% | 15.71% | 13.14% | 62.59% | 0% | 0% | 9.58% | 49.75% | 100%

## MedOP
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Outpatient Healthcare | [14 empty] | Prototype Floor Area: | 40946 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.3173 | 0.037575 | 0.050432 | 0.30504 | 0.1145 | 0.50061 | 0 | 0.24582 | 0 | 0.0016858 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8738 |  | STD2016 | 10.6905 | 1.266 | 5.0432 | 19.3407 | 3.8577 | 16.8663 | 0 | 8.282 | 0 | 0.056797 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.1209 |  | STD2016 | 3.1323 | 0.37093 | 0 | 1.662 | 1.1303 | 4.9418 | 0 | 2.4266 | 0 | 0.016642 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.0913 |  | STD2016 | 0 | 0 | 0.050432 | 0.13668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23072 |  | STD2016 | 32.7921 | 3.8833 | 5.5123 | 32.339 | 11.833 | 51.736 | 0 | 25.4042 | 0 | 0.17422 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 298.3679
STD2013 | 0.34511 | 0.077156 | 0.056464 | 0.33484 | 0.070894 | 0.56647 | 0 | 0.26354 | 0.012571 | 0.0018147 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.0297 |  | STD2013 | 11.6272 | 2.5995 | 5.6464 | 21.3854 | 2.3885 | 19.0852 | 0 | 8.8792 | 0.42353 | 0.06114 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 118.8139 |  | STD2013 | 3.4068 | 0.76166 | 0 | 1.8012 | 0.69984 | 5.592 | 0 | 2.6016 | 0.1241 | 0.017914 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.4158 |  | STD2013 | 0 | 0 | 0.056464 | 0.15238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25245 |  | STD2013 | 35.6655 | 7.9738 | 6.1715 | 35.5117 | 7.3267 | 58.5423 | 0 | 27.2362 | 1.2992 | 0.18754 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 314.6081
STD2010 | 0.37216 | 0.077156 | 0.056466 | 0.38331 | 0.096876 | 0.5829 | 0 | 0.28688 | 0.0029554 | 0.0018838 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.1644 |  | STD2010 | 12.5387 | 2.5995 | 5.6466 | 23.146 | 3.2639 | 19.6387 | 0 | 9.6653 | 0.099572 | 0.063468 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 123.4801 |  | STD2010 | 3.6738 | 0.76166 | 0 | 2.2607 | 0.95633 | 5.7541 | 0 | 2.8319 | 0.029175 | 0.018596 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 28.7265 |  | STD2010 | 0 | 0 | 0.056466 | 0.1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25437 |  | STD2010 | 38.4613 | 7.9738 | 6.1718 | 40.5323 | 10.0118 | 60.2402 | 0 | 29.6476 | 0.30543 | 0.19468 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 328.5409
STD2007 | 0.42008 | 0.15592 | 0.05724 | 0.6701 | 0.1241 | 0.7853 | 0 | 0.37453 | 0 | 0.0021423 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9069 |  | STD2007 | 14.1533 | 5.2532 | 5.724 | 35.2107 | 4.1813 | 26.4581 | 0 | 12.6187 | 0 | 0.072177 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.9499 |  | STD2007 | 4.1469 | 1.5392 | 0 | 4.7341 | 1.2251 | 7.7522 | 0 | 3.6973 | 0 | 0.021148 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.691 |  | STD2007 | 0 | 0 | 0.05724 | 0.19053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29138 |  | STD2007 | 43.4142 | 16.1138 | 6.2564 | 70.3869 | 12.8257 | 81.158 | 0 | 38.7068 | 0 | 0.2214 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 405.4964
STD2004 | 0.42008 | 0.15592 | 0.057242 | 0.79271 | 0.15057 | 0.82063 | 0 | 0.41446 | 0 | 0.0023374 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1314 |  | STD2004 | 14.1533 | 5.2532 | 5.7242 | 40.8476 | 5.0728 | 27.6483 | 0 | 13.9638 | 0 | 0.078751 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 160.0203 |  | STD2004 | 4.1469 | 1.5392 | 0 | 5.7203 | 1.4863 | 8.101 | 0 | 4.0914 | 0 | 0.023074 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.6831 |  | STD2004 | 0 | 0 | 0.057242 | 0.21325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.31409 |  | STD2004 | 43.4142 | 16.1138 | 6.2565 | 83.1931 | 15.5604 | 84.8089 | 0 | 42.8327 | 0 | 0.24156 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 428.8344
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.074e-06 | 0.12261 | 0.026462 | 0.035326 | 0 | 0.039924 | 0 | 0.00019513 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22451 |  | 2004-2007 | 0 | 0 | 0.0001074 | 5.6369 | 0.89154 | 1.1902 | 0 | 1.3451 | 0 | 0.0065742 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0704 |  | 2004-2007 | 0 | 0 | 0 | 0.98611 | 0.26122 | 0.34873 | 0 | 0.39411 | 0 | 0.0019262 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9921 |  | 2004-2007 | 0 | 0 | 1.074e-06 | 0.022714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022715 |  | 2004-2007 | 0 | 0 | 0.00011739 | 12.8062 | 2.7347 | 3.6508 | 0 | 4.126 | 0 | 0.020166 | 0 | 0 | 0 | 0 | 0 | 0 | 23.338
2007-2010 | 0.047925 | 0.078765 | 0.00077431 | 0.28679 | 0.027228 | 0.20241 | 0 | 0.087659 | -0.0029554 | 0.00025848 | 0 | 0.0075457 | 0 | 0 | 0 | 0.0061094 | 0.7425 |  | 2007-2010 | 1.6147 | 2.6537 | 0.077431 | 12.0647 | 0.91735 | 6.8194 | 0 | 2.9534 | -0.099572 | 0.0087085 | 0 | 0.25423 | 0 | 0 | 0 | 0.20584 | 27.4698 |  | 2007-2010 | 0.4731 | 0.77754 | 0 | 2.4735 | 0.26878 | 1.9981 | 0 | 0.86534 | -0.029175 | 0.0025516 | 0 | 0.074488 | 0 | 0 | 0 | 0.06031 | 6.9645 |  | 2007-2010 | 0 | 0 | 0.00077431 | 0.036229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037003 |  | 2007-2010 | 4.9528 | 8.1401 | 0.084632 | 29.8545 | 2.8139 | 20.9179 | 0 | 9.0592 | -0.30543 | 0.026713 | 0 | 0.77982 | 0 | 0 | 0 | 0.63138 | 76.9556
2010-2013 | 0.027052 | 0 | 2.2919e-06 | 0.04847 | 0.025982 | 0.016429 | 0 | 0.023333 | -0.0096155 | 6.9115e-05 | 0 | 0.0012164 | 0 | 0 | 0 | 0.0017662 | 0.1347 |  | 2010-2013 | 0.91144 | 0 | 0.00022919 | 1.7606 | 0.87538 | 0.55351 | 0 | 0.78613 | -0.32396 | 0.0023286 | 0 | 0.040982 | 0 | 0 | 0 | 0.059505 | 4.6661 |  | 2010-2013 | 0.26705 | 0 | 0 | 0.4595 | 0.25649 | 0.16218 | 0 | 0.23034 | -0.094921 | 0.00068228 | 0 | 0.012008 | 0 | 0 | 0 | 0.017435 | 1.3108 |  | 2010-2013 | 0 | 0 | 2.2919e-06 | 0.0019232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019255 |  | 2010-2013 | 2.7958 | 0 | 0.0002505 | 5.0207 | 2.6851 | 1.6979 | 0 | 2.4114 | -0.99373 | 0.0071428 | 0 | 0.12571 | 0 | 0 | 0 | 0.18253 | 13.9327
2013-2016 | 0.027804 | 0.039581 | 0.0060315 | 0.029795 | -0.043604 | 0.065859 | 0 | 0.017726 | 0.012571 | 0.0001289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15589 |  | 2013-2016 | 0.93676 | 1.3335 | 0.60315 | 2.0447 | -1.4691 | 2.2189 | 0 | 0.59722 | 0.42353 | 0.0043427 | 0 | 0 | 0 | 0 | 0 | 0 | 6.693 |  | 2013-2016 | 0.27447 | 0.39073 | 0 | 0.13916 | -0.43045 | 0.65014 | 0 | 0.17499 | 0.1241 | 0.0012724 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3244 |  | 2013-2016 | 0 | 0 | 0.0060315 | 0.015697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021729 |  | 2013-2016 | 2.8734 | 4.0905 | 0.65924 | 3.1726 | -4.5064 | 6.8063 | 0 | 1.8319 | 1.2992 | 0.013321 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2402
2004-2016 | 0.10278 | 0.11835 | 0.0068091 | 0.48766 | 0.036067 | 0.32002 | 0 | 0.16864 | 0 | 0.00065162 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2576 |  | 2004-2016 | 3.4629 | 3.9872 | 0.68091 | 21.5069 | 1.2152 | 10.782 | 0 | 5.6818 | 0 | 0.021954 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.8994 |  | 2004-2016 | 1.0146 | 1.1683 | 0 | 4.0582 | 0.35604 | 3.1591 | 0 | 1.6648 | 0 | 0.0064325 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.5917 |  | 2004-2016 | 0 | 0 | 0.0068091 | 0.076563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083372 |  | 2004-2016 | 10.6221 | 12.2306 | 0.74424 | 50.854 | 3.7274 | 33.0729 | 0 | 17.4285 | 0 | 0.067342 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 130.4665
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.001876% | 15.47% | 17.57% | 4.305% |  | 9.633% |  | 8.348% |  | 0% |  |  |  | 0% | 5.434% |  | 2004-2007 | 0% | 0% | 0.001876% | 13.8% | 17.57% | 4.305% |  | 9.633% |  | 8.348% |  | 0% |  |  |  | 0% | 5.668% |  | 2004-2007 | 0% | 0% |  | 17.24% | 17.57% | 4.305% |  | 9.633% |  | 8.348% |  | 0% |  |  |  | 0% | 5.286% |  | 2004-2007 |  |  | 0.001876% | 10.65% | [11 empty] | 0% | 7.232% |  | 2004-2007 | 0% | 0% | 0.001876% | 15.39% | 17.57% | 4.305% |  | 9.633% |  | 8.348% |  | 0% |  |  |  | 0% | 5.442%
2007-2010 | 11.41% | 50.52% | 1.353% | 42.8% | 21.94% | 25.77% |  | 23.4% |  | 12.07% |  | 1.684% |  |  |  | 0.7027% | 19.01% |  | 2007-2010 | 11.41% | 50.52% | 1.353% | 34.26% | 21.94% | 25.77% |  | 23.4% |  | 12.07% |  | 1.684% |  |  |  | 0.6396% | 18.2% |  | 2007-2010 | 11.41% | 50.52% |  | 52.25% | 21.94% | 25.77% |  | 23.4% |  | 12.07% |  | 1.684% |  |  |  | 0.7398% | 19.51% |  | 2007-2010 |  |  | 1.353% | 19.01% | [11 empty] | 0% | 12.7% |  | 2007-2010 | 11.41% | 50.52% | 1.353% | 42.41% | 21.94% | 25.77% |  | 23.4% |  | 12.07% |  | 1.684% |  |  |  | 0.7007% | 18.98%
2010-2013 | 7.269% | 0% | 0.004059% | 12.65% | 26.82% | 2.818% |  | 8.134% | -325.4% | 3.669% |  | 0.2761% |  |  |  | 0.2046% | 4.257% |  | 2010-2013 | 7.269% | 0% | 0.004059% | 7.606% | 26.82% | 2.818% |  | 8.134% | -325.4% | 3.669% |  | 0.2761% |  |  |  | 0.1861% | 3.779% |  | 2010-2013 | 7.269% | 0% |  | 20.33% | 26.82% | 2.818% |  | 8.134% | -325.4% | 3.669% |  | 0.2761% |  |  |  | 0.2155% | 4.563% |  | 2010-2013 |  |  | 0.004059% | 1.246% | [11 empty] | 0% | 0.757% |  | 2010-2013 | 7.269% | 0% | 0.004059% | 12.39% | 26.82% | 2.818% |  | 8.134% | -325.4% | 3.669% |  | 0.2761% |  |  |  | 0.204% | 4.241%
2013-2016 | 8.057% | 51.3% | 10.68% | 8.898% | -61.51% | 11.63% |  | 6.726% | 100% | 7.103% |  | 0% |  |  |  | 0% | 5.145% |  | 2013-2016 | 8.057% | 51.3% | 10.68% | 9.561% | -61.51% | 11.63% |  | 6.726% | 100% | 7.103% |  | 0% |  |  |  | 0% | 5.633% |  | 2013-2016 | 8.057% | 51.3% |  | 7.726% | -61.51% | 11.63% |  | 6.726% | 100% | 7.103% |  | 0% |  |  |  | 0% | 4.831% |  | 2013-2016 |  |  | 10.68% | 10.3% | [11 empty] | 0% | 8.607% |  | 2013-2016 | 8.057% | 51.3% | 10.68% | 8.934% | -61.51% | 11.63% |  | 6.726% | 100% | 7.103% |  | 0% |  |  |  | 0% | 5.162%
2004-2016 | 24.47% | 75.9% | 11.9% | 61.52% | 23.95% | 39% |  | 40.69% |  | 27.88% |  | 1.955% |  |  |  | 0.9059% | 30.44% |  | 2004-2016 | 24.47% | 75.9% | 11.9% | 52.65% | 23.95% | 39% |  | 40.69% |  | 27.88% |  | 1.955% |  |  |  | 0.8245% | 29.93% |  | 2004-2016 | 24.47% | 75.9% |  | 70.95% | 23.95% | 39% |  | 40.69% |  | 27.88% |  | 1.955% |  |  |  | 0.9537% | 30.76% |  | 2004-2016 |  |  | 11.9% | 35.9% | [11 empty] | 0% | 26.54% |  | 2004-2016 | 24.47% | 75.9% | 11.9% | 61.13% | 23.95% | 39% |  | 40.69% |  | 27.88% |  | 1.955% |  |  |  | 0.9033% | 30.42%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.31739 | 0.037453 | 0.047423 | 0.18334 | 0 | 1.0528 | 0 | 0.25125 | 0 | 0.00096211 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.1915 | 1.751% | CZ 1A | 10.6933 | 1.2619 | 4.7423 | 12.33 | 0 | 35.4718 | 0 | 8.4652 | 0 | 0.032415 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 119.7147 | 1.751% | CZ 1A | 3.1331 | 0.36973 | 0 | 0.89386 | 0 | 10.3932 | 0 | 2.4803 | 0 | 0.0094976 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 29.6905 | 1.751% | CZ 1A | 0 | 0 | 0.047423 | 0.092793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18382 | 1.751% | CZ 1A | 32.8007 | 3.8707 | 5.1834 | 19.5001 | 0 | 108.8067 | 0 | 25.9663 | 0 | 0.09943 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 330.921 | 1.751%
CZ 1B | 0.31725 | 0.03733 | 0.04756 | 0.17787 | 0.0015325 | 1.0744 | 0 | 0.25549 | 0 | 0.00095524 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.2132 | 0% | CZ 1B | 10.6889 | 1.2577 | 4.756 | 11.7 | 0.051633 | 36.1995 | 0 | 8.6078 | 0 | 0.032183 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 120.0114 | 0% | CZ 1B | 3.1318 | 0.36851 | 0 | 0.90614 | 0.015128 | 10.6064 | 0 | 2.5221 | 0 | 0.0094298 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 29.9703 | 0% | CZ 1B | 0 | 0 | 0.04756 | 0.086073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17724 | 0% | CZ 1B | 32.7872 | 3.8579 | 5.1983 | 18.8942 | 0.15838 | 111.0389 | 0 | 26.4037 | 0 | 0.09872 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 333.1311 | 0%
CZ 2A | 0.31738 | 0.03746 | 0.047648 | 0.2344 | 0.019098 | 0.93074 | 0 | 0.23849 | 0 | 0.0010171 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.127 | 14.08% | CZ 2A | 10.693 | 1.2621 | 4.7648 | 13.8168 | 0.64344 | 31.3581 | 0 | 8.035 | 0 | 0.034267 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.3253 | 14.08% | CZ 2A | 3.1331 | 0.3698 | 0 | 1.4327 | 0.18853 | 9.1879 | 0 | 2.3543 | 0 | 0.01004 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 29.087 | 14.08% | CZ 2A | 0 | 0 | 0.047648 | 0.08927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18052 | 14.08% | CZ 2A | 32.8 | 3.8714 | 5.2079 | 24.7563 | 1.9737 | 96.1883 | 0 | 24.6467 | 0 | 0.10511 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 324.2431 | 14.08%
CZ 2B | 0.31784 | 0.037474 | 0.0479 | 0.20475 | 0.1483 | 0.67119 | 0 | 0.25479 | 0 | 0.00081092 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9839 | 3.07% | CZ 2B | 10.7085 | 1.2626 | 4.79 | 11.2504 | 4.9963 | 22.6134 | 0 | 8.5844 | 0 | 0.027321 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 110.9507 | 3.07% | CZ 2B | 3.1376 | 0.36993 | 0 | 1.3734 | 1.4639 | 6.6257 | 0 | 2.5152 | 0 | 0.0080051 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.9045 | 3.07% | CZ 2B | 0 | 0 | 0.0479 | 0.065631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15714 | 3.07% | CZ 2B | 32.8475 | 3.8728 | 5.2355 | 21.5512 | 15.3258 | 69.3648 | 0 | 26.332 | 0 | 0.083806 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 309.3071 | 3.07%
CZ 3A | 0.31828 | 0.037763 | 0.049113 | 0.32217 | 0.080453 | 0.60081 | 0 | 0.23742 | 0 | 0.0012645 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9481 | 14.41% | CZ 3A | 10.7234 | 1.2723 | 4.9113 | 17.6306 | 2.7106 | 20.2423 | 0 | 7.9991 | 0 | 0.042603 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.2499 | 14.41% | CZ 3A | 3.1419 | 0.37278 | 0 | 2.1716 | 0.7942 | 5.931 | 0 | 2.3437 | 0 | 0.012483 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.1784 | 14.41% | CZ 3A | 0 | 0 | 0.049113 | 0.10219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19491 | 14.41% | CZ 3A | 32.893 | 3.9026 | 5.3681 | 33.9036 | 8.3145 | 62.0915 | 0 | 24.5366 | 0 | 0.13068 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 305.8343 | 14.41%
CZ 3B | 0.31807 | 0.037165 | 0.048713 | 0.20362 | 0.14305 | 0.52806 | 0 | 0.25166 | 0 | 0.00088651 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.832 | 6.297% | CZ 3B | 10.7164 | 1.2521 | 4.8713 | 11.483 | 4.8197 | 17.7912 | 0 | 8.4788 | 0 | 0.029868 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 106.1601 | 6.297% | CZ 3B | 3.1399 | 0.36688 | 0 | 1.3219 | 1.4122 | 5.2128 | 0 | 2.4843 | 0 | 0.0087514 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.3574 | 6.297% | CZ 3B | 0 | 0 | 0.048713 | 0.069715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16203 | 6.297% | CZ 3B | 32.8717 | 3.8409 | 5.3243 | 21.4584 | 14.7839 | 54.5731 | 0 | 26.0082 | 0 | 0.091618 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 293.6458 | 6.297%
CZ 3C | 0.31795 | 0.037055 | 0.048979 | 0.18725 | 0.032162 | 0.46497 | 0 | 0.23208 | 0 | 0.0010446 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.6223 | 1.4% | CZ 3C | 10.7122 | 1.2484 | 4.8979 | 12.362 | 1.0836 | 15.6657 | 0 | 7.8192 | 0 | 0.035193 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 100.5421 | 1.4% | CZ 3C | 3.1387 | 0.36579 | 0 | 0.94732 | 0.31749 | 4.5901 | 0 | 2.291 | 0 | 0.010312 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 24.0714 | 1.4% | CZ 3C | 0 | 0 | 0.048979 | 0.091289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18387 | 1.4% | CZ 3C | 32.8589 | 3.8295 | 5.3534 | 19.8953 | 3.3238 | 48.0533 | 0 | 23.9847 | 0 | 0.10795 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 272.1007 | 1.4%
CZ 4A | 0.31694 | 0.037453 | 0.050692 | 0.29693 | 0.12801 | 0.43902 | 0 | 0.24853 | 0 | 0.0017455 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8201 | 18.54% | CZ 4A | 10.6782 | 1.2619 | 5.0692 | 19.3352 | 4.3128 | 14.7912 | 0 | 8.3733 | 0 | 0.05881 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 110.5983 | 18.54% | CZ 4A | 3.1287 | 0.36973 | 0 | 1.542 | 1.2637 | 4.3338 | 0 | 2.4534 | 0 | 0.017231 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.5192 | 18.54% | CZ 4A | 0 | 0 | 0.050692 | 0.14072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23502 | 18.54% | CZ 4A | 32.7545 | 3.8707 | 5.5406 | 31.5243 | 13.2292 | 45.3708 | 0 | 25.6843 | 0 | 0.1804 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 292.8486 | 18.54%
CZ 4B | 0.31666 | 0.03724 | 0.050104 | 0.22821 | 0.19767 | 0.41314 | 0 | 0.28038 | 0 | 0.0010652 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8253 | 0.5369% | CZ 4B | 10.6689 | 1.2547 | 5.0104 | 12.949 | 6.6599 | 13.9192 | 0 | 9.4464 | 0 | 0.035888 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 106.6623 | 0.5369% | CZ 4B | 3.126 | 0.36763 | 0 | 1.4697 | 1.9514 | 4.0783 | 0 | 2.7678 | 0 | 0.010515 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.182 | 0.5369% | CZ 4B | 0 | 0 | 0.050104 | 0.07933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17304 | 0.5369% | CZ 4B | 32.7261 | 3.8487 | 5.4763 | 24.057 | 20.4287 | 42.6961 | 0 | 28.9762 | 0 | 0.11008 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 293.0129 | 0.5369%
CZ 4C | 0.31759 | 0.037941 | 0.051229 | 0.24287 | 0.051858 | 0.25919 | 0 | 0.24474 | 0 | 0.0013744 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.5076 | 3.995% | CZ 4C | 10.7002 | 1.2783 | 5.1229 | 15.8039 | 1.7472 | 8.7326 | 0 | 8.2457 | 0 | 0.046307 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 98.3949 | 3.995% | CZ 4C | 3.1352 | 0.37454 | 0 | 1.263 | 0.51192 | 2.5587 | 0 | 2.416 | 0 | 0.013568 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 22.6835 | 3.995% | CZ 4C | 0 | 0 | 0.051229 | 0.11493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20977 | 3.995% | CZ 4C | 32.822 | 3.9211 | 5.5993 | 25.7844 | 5.3593 | 26.7866 | 0 | 25.293 | 0 | 0.14204 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 260.4015 | 3.995%
CZ 5A | 0.31697 | 0.037701 | 0.052354 | 0.36909 | 0.15226 | 0.30638 | 0 | 0.24172 | 0 | 0.0023915 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.7797 | 24.16% | CZ 5A | 10.6794 | 1.2702 | 5.2354 | 25.1906 | 5.1299 | 10.3226 | 0 | 8.144 | 0 | 0.080574 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.7704 | 24.16% | CZ 5A | 3.1291 | 0.37217 | 0 | 1.7445 | 1.5031 | 3.0245 | 0 | 2.3862 | 0 | 0.023608 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 24.5938 | 24.16% | CZ 5A | 0 | 0 | 0.052354 | 0.19237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28832 | 24.16% | CZ 5A | 32.7581 | 3.8963 | 5.7223 | 39.2889 | 15.7356 | 31.6636 | 0 | 24.9812 | 0 | 0.24716 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 288.9868 | 24.16%
CZ 5B | 0.31671 | 0.037419 | 0.0519 | 0.29042 | 0.18314 | 0.32476 | 0 | 0.27997 | 0 | 0.0015394 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.7867 | 5.042% | CZ 5B | 10.6703 | 1.2607 | 5.19 | 17.2395 | 6.1702 | 10.9417 | 0 | 9.4325 | 0 | 0.051864 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.6747 | 5.042% | CZ 5B | 3.1264 | 0.36939 | 0 | 1.7571 | 1.8079 | 3.2059 | 0 | 2.7637 | 0 | 0.015196 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.4563 | 5.042% | CZ 5B | 0 | 0 | 0.0519 | 0.11243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20793 | 5.042% | CZ 5B | 32.7304 | 3.8671 | 5.6727 | 30.6829 | 18.9266 | 33.5627 | 0 | 28.9335 | 0 | 0.15909 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 289.2288 | 5.042%
CZ 5C | 0.31743 | 0.03801 | 0.052226 | 0.2529 | 0.056579 | 0.19361 | 0 | 0.24871 | 0 | 0.0014638 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.4617 | 0.1564% | CZ 5C | 10.6949 | 1.2806 | 5.2226 | 16.6047 | 1.9062 | 6.5231 | 0 | 8.3795 | 0 | 0.049317 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 97.3787 | 0.1564% | CZ 5C | 3.1336 | 0.37522 | 0 | 1.2931 | 0.55853 | 1.9113 | 0 | 2.4552 | 0 | 0.01445 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 22.1521 | 0.1564% | CZ 5C | 0 | 0 | 0.052226 | 0.12191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21774 | 0.1564% | CZ 5C | 32.8056 | 3.9282 | 5.7084 | 26.8626 | 5.8472 | 20.009 | 0 | 25.7035 | 0 | 0.15128 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 255.7095 | 0.1564%
CZ 6A | 0.31642 | 0.037715 | 0.05368 | 0.46469 | 0.1907 | 0.3109 | 0 | 0.24846 | 0 | 0.0031406 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9265 | 5.203% | CZ 6A | 10.6608 | 1.2707 | 5.368 | 32.5503 | 6.4249 | 10.4749 | 0 | 8.3712 | 0 | 0.10581 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 121.9444 | 5.203% | CZ 6A | 3.1236 | 0.37231 | 0 | 2.0721 | 1.8825 | 3.0692 | 0 | 2.4528 | 0 | 0.031003 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.4142 | 5.203% | CZ 6A | 0 | 0 | 0.05368 | 0.25478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.35207 | 5.203% | CZ 6A | 32.7012 | 3.8977 | 5.8672 | 49.5406 | 19.7078 | 32.1309 | 0 | 25.6779 | 0 | 0.32457 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 304.5418 | 5.203%
CZ 6B | 0.31651 | 0.038031 | 0.053354 | 0.38359 | 0.22831 | 0.24708 | 0 | 0.26509 | 0 | 0.002206 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.835 | 0.6872% | CZ 6B | 10.6636 | 1.2813 | 5.3354 | 24.4168 | 7.6923 | 8.3244 | 0 | 8.9315 | 0 | 0.074323 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.4375 | 0.6872% | CZ 6B | 3.1244 | 0.37543 | 0 | 2.0757 | 2.2538 | 2.4391 | 0 | 2.6169 | 0 | 0.021777 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.3179 | 0.6872% | CZ 6B | 0 | 0 | 0.053354 | 0.17333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27028 | 0.6872% | CZ 6B | 32.7098 | 3.9303 | 5.8316 | 40.675 | 23.5955 | 25.5344 | 0 | 27.3966 | 0 | 0.22798 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 294.595 | 0.6872%
CZ 7 | 0.3162 | 0.038031 | 0.055224 | 0.53766 | 0.25335 | 0.25187 | 0 | 0.25187 | 0 | 0.0040271 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.009 | 0.6411% | CZ 7 | 10.6532 | 1.2813 | 5.5224 | 39.2841 | 8.5358 | 8.4858 | 0 | 8.486 | 0 | 0.13568 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 129.1022 | 0.6411% | CZ 7 | 3.1214 | 0.37543 | 0 | 2.156 | 2.501 | 2.4863 | 0 | 2.4864 | 0 | 0.039754 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.577 | 0.6411% | CZ 7 | 0 | 0 | 0.055224 | 0.31926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.41809 | 0.6411% | CZ 7 | 32.6778 | 3.9303 | 6.036 | 57.4657 | 26.1829 | 26.0295 | 0 | 26.0302 | 0 | 0.41619 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 313.4623 | 0.6411%
CZ 8 | 0.31826 | 0.040615 | 0.057382 | 0.72255 | 0.35817 | 0.14849 | 0 | 0.25674 | 0 | 0.0057726 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.2088 | 0.03247% | CZ 8 | 10.7227 | 1.3684 | 5.7382 | 53.9771 | 12.0672 | 5.0028 | 0 | 8.65 | 0 | 0.19449 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 144.4385 | 0.03247% | CZ 8 | 3.1417 | 0.40093 | 0 | 2.7212 | 3.5357 | 1.4658 | 0 | 2.5344 | 0 | 0.056986 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.2675 | 0.03247% | CZ 8 | 0 | 0 | 0.057382 | 0.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.54788 | 0.03247% | CZ 8 | 32.8909 | 4.1974 | 6.2718 | 77.3341 | 37.0151 | 15.3457 | 0 | 26.533 | 0 | 0.59658 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 334.8783 | 0.03247%
US Weighted | 0.3173 | 0.037575 | 0.050432 | 0.30504 | 0.1145 | 0.50061 | 0 | 0.24582 | 0 | 0.0016858 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8738 | 100% | US Weighted | 10.6905 | 1.266 | 5.0432 | 19.3407 | 3.8577 | 16.8663 | 0 | 8.282 | 0 | 0.056797 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.1209 | 100% | US Weighted | 3.1323 | 0.37093 | 0 | 1.662 | 1.1303 | 4.9418 | 0 | 2.4266 | 0 | 0.016642 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.0913 | 100% | US Weighted | 0 | 0 | 0.050432 | 0.13668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23072 | 100% | US Weighted | 32.7921 | 3.8833 | 5.5123 | 32.339 | 11.833 | 51.736 | 0 | 25.4042 | 0 | 0.17422 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 298.3679 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.34559 | 0.077216 | 0.054856 | 0.21746 | 0 | 1.1211 | 0 | 0.27006 | 0.020761 | 0.0012301 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.4091 | 1.751% | CZ 1A | 11.6435 | 2.6015 | 5.4856 | 15.3528 | 0 | 37.773 | 0 | 9.0989 | 0.69947 | 0.041445 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 129.414 | 1.751% | CZ 1A | 3.4115 | 0.76225 | 0 | 0.95186 | 0 | 11.0675 | 0 | 2.666 | 0.20494 | 0.012143 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 31.4869 | 1.751% | CZ 1A | 0 | 0 | 0.054856 | 0.12104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2195 | 1.751% | CZ 1A | 35.7154 | 7.98 | 5.9958 | 23.1948 | 0 | 115.8656 | 0 | 27.9101 | 2.1456 | 0.12713 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 353.6281 | 1.751%
CZ 1B | 0.34538 | 0.077099 | 0.054856 | 0.21218 | 0.00028176 | 1.1684 | 0 | 0.27689 | 0 | 0.0011889 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.4371 | 0% | CZ 1B | 11.6363 | 2.5976 | 5.4856 | 14.5021 | 0.009493 | 39.3657 | 0 | 9.3288 | 0 | 0.040056 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 129.6835 | 0% | CZ 1B | 3.4094 | 0.7611 | 0 | 0.99989 | 0.0027814 | 11.5342 | 0 | 2.7333 | 0 | 0.011736 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 31.8632 | 0% | CZ 1B | 0 | 0 | 0.054856 | 0.1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20935 | 0% | CZ 1B | 35.6934 | 7.9679 | 5.9958 | 22.5887 | 0.029119 | 120.7511 | 0 | 28.6154 | 0 | 0.12287 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 356.458 | 0%
CZ 2A | 0.34555 | 0.077072 | 0.054856 | 0.28084 | 0.0087895 | 1.0027 | 0 | 0.25763 | 0.017373 | 0.0013057 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.3469 | 14.08% | CZ 2A | 11.6421 | 2.5967 | 5.4856 | 17.4535 | 0.29613 | 33.7811 | 0 | 8.68 | 0.58532 | 0.043992 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 127.2823 | 14.08% | CZ 2A | 3.4111 | 0.76083 | 0 | 1.5826 | 0.086767 | 9.8979 | 0 | 2.5433 | 0.1715 | 0.01289 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 30.8775 | 14.08% | CZ 2A | 0 | 0 | 0.054856 | 0.12052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21898 | 14.08% | CZ 2A | 35.7111 | 7.9651 | 5.9958 | 29.741 | 0.90837 | 103.6207 | 0 | 26.6253 | 1.7954 | 0.13494 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 347.1916 | 14.08%
CZ 2B | 0.3461 | 0.077134 | 0.054856 | 0.21959 | 0.090328 | 0.73234 | 0 | 0.27176 | 0 | 0.0010858 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.094 | 3.07% | CZ 2B | 11.6608 | 2.5988 | 5.4856 | 13.5343 | 3.0433 | 24.6739 | 0 | 9.1561 | 0 | 0.036583 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 116.9071 | 3.07% | CZ 2B | 3.4166 | 0.76144 | 0 | 1.2542 | 0.89169 | 7.2294 | 0 | 2.6827 | 0 | 0.010719 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 28.6576 | 3.07% | CZ 2B | 0 | 0 | 0.054856 | 0.092536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.191 | 3.07% | CZ 2B | 35.7687 | 7.9715 | 5.9958 | 23.2447 | 9.3351 | 75.685 | 0 | 28.0855 | 0 | 0.11221 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 320.8923 | 3.07%
CZ 3A | 0.34602 | 0.07712 | 0.055474 | 0.37265 | 0.048126 | 0.6812 | 0 | 0.25772 | 0.014473 | 0.001505 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.1551 | 14.41% | CZ 3A | 11.6578 | 2.5983 | 5.5474 | 21.0062 | 1.6214 | 22.9508 | 0 | 8.6831 | 0.48761 | 0.050706 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 121.3212 | 14.41% | CZ 3A | 3.4157 | 0.7613 | 0 | 2.4205 | 0.47508 | 6.7246 | 0 | 2.5441 | 0.14287 | 0.014857 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 28.9098 | 14.41% | CZ 3A | 0 | 0 | 0.055474 | 0.12745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22653 | 14.41% | CZ 3A | 35.7594 | 7.9701 | 6.0633 | 39.2709 | 4.9737 | 70.3996 | 0 | 26.6346 | 1.4957 | 0.15554 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 327.4165 | 14.41%
CZ 3B | 0.34583 | 0.077113 | 0.055229 | 0.22687 | 0.092995 | 0.57643 | 0 | 0.2696 | 0 | 0.0011064 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.946 | 6.297% | CZ 3B | 11.6516 | 2.5981 | 5.5229 | 13.7524 | 3.1331 | 19.421 | 0 | 9.0834 | 0 | 0.037277 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 111.9175 | 6.297% | CZ 3B | 3.4139 | 0.76123 | 0 | 1.3302 | 0.91801 | 5.6904 | 0 | 2.6614 | 0 | 0.010922 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.1968 | 6.297% | CZ 3B | 0 | 0 | 0.055229 | 0.092124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19096 | 6.297% | CZ 3B | 35.7403 | 7.9693 | 6.0365 | 23.9951 | 9.6107 | 59.5723 | 0 | 27.8625 | 0 | 0.11434 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 305.5948 | 6.297%
CZ 3C | 0.34569 | 0.077237 | 0.054986 | 0.22463 | 0.018926 | 0.52642 | 0 | 0.25098 | 0 | 0.0013401 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.801 | 1.4% | CZ 3C | 11.6467 | 2.6022 | 5.4986 | 15.4225 | 0.63765 | 17.7361 | 0 | 8.4559 | 0 | 0.04515 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 108.7627 | 1.4% | CZ 3C | 3.4125 | 0.76245 | 0 | 1.0482 | 0.18683 | 5.1967 | 0 | 2.4776 | 0 | 0.013229 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.5082 | 1.4% | CZ 3C | 0 | 0 | 0.054986 | 0.11845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21704 | 1.4% | CZ 3C | 35.7253 | 7.9821 | 6.0099 | 23.9202 | 1.9559 | 54.4041 | 0 | 25.9378 | 0 | 0.13849 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 290.7677 | 1.4%
CZ 4A | 0.3445 | 0.07725 | 0.056507 | 0.32397 | 0.078762 | 0.508 | 0 | 0.26576 | 0.01595 | 0.0018555 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9734 | 18.54% | CZ 4A | 11.6069 | 2.6027 | 5.6507 | 21.2135 | 2.6536 | 17.1154 | 0 | 8.954 | 0.53739 | 0.062515 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.1144 | 18.54% | CZ 4A | 3.4008 | 0.76259 | 0 | 1.6649 | 0.77751 | 5.0148 | 0 | 2.6235 | 0.15746 | 0.018317 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.8307 | 18.54% | CZ 4A | 0 | 0 | 0.056507 | 0.15531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25542 | 18.54% | CZ 4A | 35.6032 | 7.9836 | 6.1762 | 34.4057 | 8.1398 | 52.5 | 0 | 27.4655 | 1.6484 | 0.19176 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 308.8078 | 18.54%
CZ 4B | 0.34425 | 0.077085 | 0.056148 | 0.25227 | 0.13145 | 0.43843 | 0 | 0.2843 | 0 | 0.0012233 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.886 | 0.5369% | CZ 4B | 11.5983 | 2.5971 | 5.6148 | 14.8836 | 4.4288 | 14.7713 | 0 | 9.5784 | 0 | 0.041213 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 110.2313 | 0.5369% | CZ 4B | 3.3983 | 0.76096 | 0 | 1.5398 | 1.2976 | 4.328 | 0 | 2.8065 | 0 | 0.012076 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.554 | 0.5369% | CZ 4B | 0 | 0 | 0.056148 | 0.096282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19603 | 0.5369% | CZ 4B | 35.5769 | 7.9665 | 6.1369 | 26.6441 | 13.585 | 45.3097 | 0 | 29.381 | 0 | 0.12642 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 299.4204 | 0.5369%
CZ 4C | 0.34533 | 0.07723 | 0.056669 | 0.27141 | 0.02052 | 0.29654 | 0 | 0.25759 | 0 | 0.0017043 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.6278 | 3.995% | CZ 4C | 11.6347 | 2.602 | 5.6669 | 18.9467 | 0.69137 | 9.991 | 0 | 8.6787 | 0 | 0.057421 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.9865 | 3.995% | CZ 4C | 3.409 | 0.76239 | 0 | 1.22 | 0.20257 | 2.9274 | 0 | 2.5428 | 0 | 0.016824 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 23.4916 | 3.995% | CZ 4C | 0 | 0 | 0.056669 | 0.14783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2481 | 3.995% | CZ 4C | 35.6884 | 7.9814 | 6.1939 | 28.9296 | 2.1207 | 30.6466 | 0 | 26.6211 | 0 | 0.17613 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 273.0516 | 3.995%
CZ 5A | 0.34465 | 0.077134 | 0.05775 | 0.38395 | 0.09551 | 0.37883 | 0 | 0.25985 | 0.015655 | 0.0023297 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9165 | 24.16% | CZ 5A | 11.612 | 2.5988 | 5.775 | 25.6245 | 3.2179 | 12.7634 | 0 | 8.7548 | 0.52744 | 0.078491 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.6701 | 24.16% | CZ 5A | 3.4023 | 0.76144 | 0 | 1.9012 | 0.94284 | 3.7397 | 0 | 2.5652 | 0.15454 | 0.022998 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.9009 | 24.16% | CZ 5A | 0 | 0 | 0.05775 | 0.19136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29271 | 24.16% | CZ 5A | 35.6188 | 7.9715 | 6.312 | 40.8192 | 9.8706 | 39.1507 | 0 | 26.8547 | 1.6179 | 0.24076 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 303.15 | 24.16%
CZ 5B | 0.3444 | 0.077209 | 0.057298 | 0.31488 | 0.11122 | 0.3497 | 0 | 0.29532 | 0 | 0.0017318 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.8526 | 5.042% | CZ 5B | 11.6034 | 2.6013 | 5.7298 | 19.4993 | 3.7472 | 11.7819 | 0 | 9.9498 | 0 | 0.058347 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 111.6888 | 5.042% | CZ 5B | 3.3998 | 0.76218 | 0 | 1.7848 | 1.0979 | 3.4521 | 0 | 2.9153 | 0 | 0.017096 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.8399 | 5.042% | CZ 5B | 0 | 0 | 0.057298 | 0.13408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23498 | 5.042% | CZ 5B | 35.5925 | 7.9793 | 6.2627 | 33.3398 | 11.4942 | 36.1401 | 0 | 30.5202 | 0 | 0.17897 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 296.2015 | 5.042%
CZ 5C | 0.34514 | 0.077195 | 0.057594 | 0.26508 | 0.01738 | 0.22586 | 0 | 0.26726 | 0 | 0.0018211 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.5581 | 0.1564% | CZ 5C | 11.6282 | 2.6008 | 5.7594 | 19.4345 | 0.58555 | 7.6097 | 0 | 9.0044 | 0 | 0.061357 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 103.4018 | 0.1564% | CZ 5C | 3.4071 | 0.76205 | 0 | 1.0531 | 0.17157 | 2.2296 | 0 | 2.6383 | 0 | 0.017978 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 22.6904 | 0.1564% | CZ 5C | 0 | 0 | 0.057594 | 0.1584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2596 | 0.1564% | CZ 5C | 35.6685 | 7.9779 | 6.2951 | 28.3383 | 1.7961 | 23.342 | 0 | 27.6203 | 0 | 0.18821 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 265.9202 | 0.1564%
CZ 6A | 0.34468 | 0.077175 | 0.059011 | 0.49269 | 0.12879 | 0.37491 | 0 | 0.26277 | 0.015923 | 0.0029963 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.0598 | 5.203% | CZ 6A | 11.6129 | 2.6001 | 5.9011 | 32.837 | 4.3392 | 12.6314 | 0 | 8.853 | 0.53647 | 0.10095 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 126.13 | 5.203% | CZ 6A | 3.4026 | 0.76184 | 0 | 2.4463 | 1.2714 | 3.701 | 0 | 2.5939 | 0.15719 | 0.029578 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.7746 | 5.203% | CZ 6A | 0 | 0 | 0.059011 | 0.24488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.34749 | 5.203% | CZ 6A | 35.6217 | 7.9757 | 6.4499 | 52.3756 | 13.3102 | 38.7459 | 0 | 27.1559 | 1.6456 | 0.30965 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 318.2838 | 5.203%
CZ 6B | 0.34479 | 0.077079 | 0.058694 | 0.42821 | 0.15166 | 0.26591 | 0 | 0.27656 | 0 | 0.0025084 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 2.9062 | 0.6872% | CZ 6B | 11.6166 | 2.5969 | 5.8694 | 27.8449 | 5.1095 | 8.9591 | 0 | 9.3177 | 0 | 0.084511 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 118.1164 | 0.6872% | CZ 6B | 3.4037 | 0.76089 | 0 | 2.2296 | 1.4971 | 2.625 | 0 | 2.7301 | 0 | 0.024762 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 25.6819 | 0.6872% | CZ 6B | 0 | 0 | 0.058694 | 0.20235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.30465 | 0.6872% | CZ 6B | 35.633 | 7.9658 | 6.4153 | 45.4591 | 15.6731 | 27.4811 | 0 | 28.5813 | 0 | 0.25923 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 302.1617 | 0.6872%
CZ 7 | 0.34366 | 0.077195 | 0.060553 | 0.54572 | 0.18099 | 0.32407 | 0 | 0.27042 | 0.016095 | 0.003766 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.1233 | 0.6411% | CZ 7 | 11.5784 | 2.6008 | 6.0553 | 38.0948 | 6.0977 | 10.9183 | 0 | 9.1109 | 0.54226 | 0.12688 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 131.8433 | 0.6411% | CZ 7 | 3.3925 | 0.76205 | 0 | 2.4531 | 1.7866 | 3.1991 | 0 | 2.6695 | 0.15888 | 0.037176 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 26.8696 | 0.6411% | CZ 7 | 0 | 0 | 0.060553 | 0.29722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.40138 | 0.6411% | CZ 7 | 35.5158 | 7.9779 | 6.6184 | 58.1681 | 18.7043 | 33.491 | 0 | 27.947 | 1.6633 | 0.3892 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 325.1689 | 0.6411%
CZ 8 | 0.34591 | 0.077642 | 0.062634 | 0.72724 | 0.26573 | 0.21014 | 0 | 0.27575 | 0.015456 | 0.0053397 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.2866 | 0.03247% | CZ 8 | 11.6541 | 2.6159 | 6.2634 | 51.7672 | 8.953 | 7.0799 | 0 | 9.2904 | 0.52072 | 0.1799 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 145.0424 | 0.03247% | CZ 8 | 3.4147 | 0.76646 | 0 | 3.1199 | 2.6232 | 2.0744 | 0 | 2.7221 | 0.15257 | 0.052712 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.3367 | 0.03247% | CZ 8 | 0 | 0 | 0.062634 | 0.41119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.51743 | 0.03247% | CZ 8 | 35.7481 | 8.024 | 6.8459 | 77.6054 | 27.4627 | 21.717 | 0 | 28.4975 | 1.5973 | 0.55184 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 342.7434 | 0.03247%
US Weighted | 0.34511 | 0.077156 | 0.056464 | 0.33484 | 0.070894 | 0.56647 | 0 | 0.26354 | 0.012571 | 0.0018147 | 0 | 0.43932 | 0 | 0 | 0 | 0.86149 | 3.0297 | 100% | US Weighted | 11.6272 | 2.5995 | 5.6464 | 21.3854 | 2.3885 | 19.0852 | 0 | 8.8792 | 0.42353 | 0.06114 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 118.8139 | 100% | US Weighted | 3.4068 | 0.76166 | 0 | 1.8012 | 0.69984 | 5.592 | 0 | 2.6016 | 0.1241 | 0.017914 | 0 | 4.3368 | 0 | 0 | 0 | 8.0739 | 27.4158 | 100% | US Weighted | 0 | 0 | 0.056464 | 0.15238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25245 | 100% | US Weighted | 35.6655 | 7.9738 | 6.1715 | 35.5117 | 7.3267 | 58.5423 | 0 | 27.2362 | 1.2992 | 0.18754 | 0 | 45.4021 | 0 | 0 | 0 | 89.2917 | 314.6081 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.37247 | 0.077216 | 0.054856 | 0.21938 | 0 | 1.2044 | 0 | 0.30483 | 0 | 0.0012576 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.5382 | 1.751% | CZ 1A | 12.549 | 2.6015 | 5.4856 | 15.6807 | 0 | 40.5792 | 0 | 10.2702 | 0 | 0.042371 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 134.027 | 1.751% | CZ 1A | 3.6769 | 0.76225 | 0 | 0.93151 | 0 | 11.8897 | 0 | 3.0092 | 0 | 0.012415 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 32.7221 | 1.751% | CZ 1A | 0 | 0 | 0.054856 | 0.12502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22348 | 1.751% | CZ 1A | 38.4931 | 7.98 | 5.9958 | 23.4162 | 0 | 124.4734 | 0 | 31.5031 | 0 | 0.12997 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 366.9935 | 1.751%
CZ 1B | 0.37237 | 0.077099 | 0.054856 | 0.2202 | 0.00060475 | 1.214 | 0 | 0.30799 | 0 | 0.0012164 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.5522 | 0% | CZ 1B | 12.5458 | 2.5976 | 5.4856 | 15.0308 | 0.020375 | 40.9024 | 0 | 10.3767 | 0 | 0.040982 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 133.8187 | 0% | CZ 1B | 3.6759 | 0.7611 | 0 | 1.0405 | 0.0059699 | 11.9844 | 0 | 3.0404 | 0 | 0.012008 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 32.9605 | 0% | CZ 1B | 0 | 0 | 0.054856 | 0.1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21326 | 0% | CZ 1B | 38.4831 | 7.9679 | 5.9958 | 23.4405 | 0.062499 | 125.4648 | 0 | 31.8298 | 0 | 0.12571 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 368.3721 | 0%
CZ 2A | 0.37247 | 0.077072 | 0.054856 | 0.30259 | 0.0089064 | 1.073 | 0 | 0.29056 | 0 | 0.0013744 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.4846 | 14.08% | CZ 2A | 12.549 | 2.5967 | 5.4856 | 18.5983 | 0.30007 | 36.1511 | 0 | 9.7893 | 0 | 0.046307 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 132.3347 | 14.08% | CZ 2A | 3.6769 | 0.76083 | 0 | 1.736 | 0.087921 | 10.5923 | 0 | 2.8683 | 0 | 0.013568 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 32.1759 | 14.08% | CZ 2A | 0 | 0 | 0.054856 | 0.12673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22519 | 14.08% | CZ 2A | 38.4931 | 7.9651 | 5.9958 | 32.0264 | 0.92044 | 110.8905 | 0 | 30.028 | 0 | 0.14204 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 361.4632 | 14.08%
CZ 2B | 0.3726 | 0.077134 | 0.054856 | 0.30401 | 0.15588 | 0.78812 | 0 | 0.31153 | 0 | 0.0010721 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.369 | 3.07% | CZ 2B | 12.5534 | 2.5988 | 5.4856 | 15.5415 | 5.2519 | 26.553 | 0 | 10.496 | 0 | 0.03612 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 125.3346 | 3.07% | CZ 2B | 3.6782 | 0.76144 | 0 | 2.2123 | 1.5388 | 7.78 | 0 | 3.0753 | 0 | 0.010583 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 31.4968 | 3.07% | CZ 2B | 0 | 0 | 0.054856 | 0.079911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17837 | 3.07% | CZ 2B | 38.5066 | 7.9715 | 5.9958 | 31.8945 | 16.1099 | 81.4491 | 0 | 32.1956 | 0 | 0.11079 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 349.2357 | 3.07%
CZ 3A | 0.37221 | 0.07712 | 0.055474 | 0.39957 | 0.057376 | 0.6896 | 0 | 0.27489 | 0 | 0.0015119 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.2316 | 14.41% | CZ 3A | 12.5404 | 2.5983 | 5.5474 | 21.8886 | 1.9331 | 23.2339 | 0 | 9.2614 | 0 | 0.050938 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 123.8725 | 14.41% | CZ 3A | 3.6744 | 0.7613 | 0 | 2.69 | 0.5664 | 6.8075 | 0 | 2.7136 | 0 | 0.014925 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 29.6683 | 14.41% | CZ 3A | 0 | 0 | 0.055474 | 0.12708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22616 | 14.41% | CZ 3A | 38.4668 | 7.9701 | 6.0633 | 42.0511 | 5.9296 | 71.2682 | 0 | 28.4087 | 0 | 0.15625 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 335.316 | 14.41%
CZ 3B | 0.37218 | 0.077113 | 0.055229 | 0.28861 | 0.1882 | 0.60742 | 0 | 0.30492 | 0 | 0.0010377 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.1985 | 6.297% | CZ 3B | 12.5395 | 2.5981 | 5.5229 | 14.8016 | 6.3406 | 20.465 | 0 | 10.2732 | 0 | 0.034962 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 119.3942 | 6.297% | CZ 3B | 3.6741 | 0.76123 | 0 | 2.0931 | 1.8578 | 5.9962 | 0 | 3.0101 | 0 | 0.010244 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 29.843 | 6.297% | CZ 3B | 0 | 0 | 0.055229 | 0.076578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17541 | 6.297% | CZ 3B | 38.4639 | 7.9693 | 6.0365 | 30.283 | 19.4493 | 62.7747 | 0 | 31.5123 | 0 | 0.10724 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 331.5984 | 6.297%
CZ 3C | 0.37216 | 0.077237 | 0.054988 | 0.23187 | 0.022225 | 0.5454 | 0 | 0.28544 | 0 | 0.0013676 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 2.8945 | 1.4% | CZ 3C | 12.5386 | 2.6022 | 5.4988 | 15.8357 | 0.74879 | 18.3754 | 0 | 9.6171 | 0 | 0.046076 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 112.081 | 1.4% | CZ 3C | 3.6738 | 0.76245 | 0 | 1.0945 | 0.21939 | 5.384 | 0 | 2.8178 | 0 | 0.0135 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 26.4056 | 1.4% | CZ 3C | 0 | 0 | 0.054988 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2196 | 1.4% | CZ 3C | 38.4611 | 7.9821 | 6.0102 | 24.6836 | 2.2968 | 56.365 | 0 | 29.4996 | 0 | 0.14133 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 300.4418 | 1.4%
CZ 4A | 0.37202 | 0.07725 | 0.056509 | 0.35737 | 0.081662 | 0.52567 | 0 | 0.28127 | 0.015937 | 0.0018417 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.0733 | 18.54% | CZ 4A | 12.534 | 2.6027 | 5.6509 | 22.0823 | 2.7513 | 17.7106 | 0 | 9.4765 | 0.53693 | 0.062052 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 120.2256 | 18.54% | CZ 4A | 3.6725 | 0.76259 | 0 | 2.0328 | 0.80614 | 5.1892 | 0 | 2.7766 | 0.15732 | 0.018181 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 27.8555 | 18.54% | CZ 4A | 0 | 0 | 0.056509 | 0.15144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25156 | 18.54% | CZ 4A | 38.4469 | 7.9836 | 6.1764 | 37.8344 | 8.4395 | 54.3259 | 0 | 29.0685 | 1.647 | 0.19034 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 319.1145 | 18.54%
CZ 4B | 0.37199 | 0.077085 | 0.056148 | 0.3312 | 0.29492 | 0.47558 | 0 | 0.33071 | 0 | 0.0011133 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.2426 | 0.5369% | CZ 4B | 12.533 | 2.5971 | 5.6148 | 16.1672 | 9.9364 | 16.0232 | 0 | 11.1422 | 0 | 0.037509 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 120.8698 | 0.5369% | CZ 4B | 3.6722 | 0.76096 | 0 | 2.5239 | 2.9114 | 4.6948 | 0 | 3.2647 | 0 | 0.01099 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 30.279 | 0.5369% | CZ 4B | 0 | 0 | 0.056148 | 0.075532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17528 | 0.5369% | CZ 4B | 38.4441 | 7.9665 | 6.1369 | 34.6786 | 30.479 | 49.1499 | 0 | 34.1778 | 0 | 0.11506 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 336.1497 | 0.5369%
CZ 4C | 0.37213 | 0.07723 | 0.056669 | 0.2924 | 0.025145 | 0.30726 | 0 | 0.28112 | 0 | 0.0017249 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 2.7175 | 3.995% | CZ 4C | 12.5377 | 2.602 | 5.6669 | 19.7691 | 0.84719 | 10.352 | 0 | 9.4714 | 0 | 0.058116 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 108.1226 | 3.995% | CZ 4C | 3.6735 | 0.76239 | 0 | 1.4099 | 0.24823 | 3.0331 | 0 | 2.7751 | 0 | 0.017028 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 24.3595 | 3.995% | CZ 4C | 0 | 0 | 0.056669 | 0.14957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24984 | 3.995% | CZ 4C | 38.4583 | 7.9814 | 6.1939 | 31.1085 | 2.5987 | 31.7538 | 0 | 29.0529 | 0 | 0.17826 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 282.3277 | 3.995%
CZ 5A | 0.37205 | 0.077134 | 0.057757 | 0.44601 | 0.10519 | 0.35739 | 0 | 0.27788 | 0 | 0.0025427 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 2.9997 | 24.16% | CZ 5A | 12.5349 | 2.5988 | 5.7757 | 28.5738 | 3.5441 | 12.041 | 0 | 9.3622 | 0 | 0.085668 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 121.3343 | 24.16% | CZ 5A | 3.6727 | 0.76144 | 0 | 2.386 | 1.0384 | 3.528 | 0 | 2.7431 | 0 | 0.025101 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 26.595 | 24.16% | CZ 5A | 0 | 0 | 0.057757 | 0.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.30566 | 24.16% | CZ 5A | 38.4497 | 7.9715 | 6.3128 | 47.3095 | 10.8713 | 36.9348 | 0 | 28.7176 | 0 | 0.26278 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 311.832 | 24.16%
CZ 5B | 0.37199 | 0.077209 | 0.057301 | 0.42237 | 0.29362 | 0.38351 | 0 | 0.32683 | 0 | 0.00156 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.2382 | 5.042% | CZ 5B | 12.533 | 2.6013 | 5.7301 | 21.1929 | 9.8926 | 12.9211 | 0 | 11.0116 | 0 | 0.052559 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 122.7535 | 5.042% | CZ 5B | 3.6722 | 0.76218 | 0 | 3.1329 | 2.8985 | 3.7859 | 0 | 3.2264 | 0 | 0.0154 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 29.9337 | 5.042% | CZ 5B | 0 | 0 | 0.057301 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20591 | 5.042% | CZ 5B | 38.4441 | 7.9793 | 6.2629 | 44.2755 | 30.3447 | 39.6344 | 0 | 33.7772 | 0 | 0.16122 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 335.8813 | 5.042%
CZ 5C | 0.37212 | 0.077195 | 0.057594 | 0.30071 | 0.022747 | 0.23402 | 0 | 0.28581 | 0 | 0.0018417 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 2.6558 | 0.1564% | CZ 5C | 12.5374 | 2.6008 | 5.7594 | 20.6603 | 0.76638 | 7.8845 | 0 | 9.6296 | 0 | 0.062052 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 106.7188 | 0.1564% | CZ 5C | 3.6735 | 0.76205 | 0 | 1.401 | 0.22455 | 2.3102 | 0 | 2.8215 | 0 | 0.018181 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 23.651 | 0.1564% | CZ 5C | 0 | 0 | 0.057594 | 0.15879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25999 | 0.1564% | CZ 5C | 38.4576 | 7.9779 | 6.2951 | 32.0222 | 2.3508 | 24.185 | 0 | 29.5379 | 0 | 0.19034 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 276.0189 | 0.1564%
CZ 6A | 0.37203 | 0.077175 | 0.059013 | 0.5927 | 0.16941 | 0.36451 | 0 | 0.28797 | 0 | 0.0033742 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.23 | 5.203% | CZ 6A | 12.5344 | 2.6001 | 5.9013 | 37.9595 | 5.7078 | 12.2809 | 0 | 9.702 | 0 | 0.11368 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 133.6182 | 5.203% | CZ 6A | 3.6726 | 0.76184 | 0 | 3.1726 | 1.6724 | 3.5983 | 0 | 2.8427 | 0 | 0.033309 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 28.1939 | 5.203% | CZ 6A | 0 | 0 | 0.059013 | 0.27132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.37393 | 5.203% | CZ 6A | 38.4483 | 7.9757 | 6.4502 | 62.8688 | 17.5083 | 37.6706 | 0 | 29.7602 | 0 | 0.34872 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 336.0328 | 5.203%
CZ 6B | 0.37206 | 0.077079 | 0.058689 | 0.53949 | 0.30341 | 0.29793 | 0 | 0.30873 | 0 | 0.0023778 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.2636 | 0.6872% | CZ 6B | 12.5354 | 2.5969 | 5.8689 | 30.2106 | 10.2223 | 10.0378 | 0 | 10.4018 | 0 | 0.080111 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 128.772 | 0.6872% | CZ 6B | 3.6729 | 0.76089 | 0 | 3.5341 | 2.9951 | 2.9411 | 0 | 3.0477 | 0 | 0.023473 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 29.4154 | 0.6872% | CZ 6B | 0 | 0 | 0.058689 | 0.18149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28378 | 0.6872% | CZ 6B | 38.4512 | 7.9658 | 6.4147 | 56.8349 | 31.3561 | 30.79 | 0 | 31.9065 | 0 | 0.24574 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 338.9669 | 0.6872%
CZ 7 | 0.37206 | 0.077195 | 0.060546 | 0.69479 | 0.22246 | 0.29557 | 0 | 0.2881 | 0 | 0.0042195 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.3187 | 0.6411% | CZ 7 | 12.5354 | 2.6008 | 6.0546 | 45.3776 | 7.495 | 9.9584 | 0 | 9.7067 | 0 | 0.14216 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 140.689 | 0.6411% | CZ 7 | 3.6729 | 0.76205 | 0 | 3.5881 | 2.196 | 2.9178 | 0 | 2.8441 | 0 | 0.041654 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 28.4627 | 0.6411% | CZ 7 | 0 | 0 | 0.060546 | 0.33132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.43547 | 0.6411% | CZ 7 | 38.4512 | 7.9779 | 6.6177 | 73.7763 | 22.9904 | 30.5464 | 0 | 29.7744 | 0 | 0.43607 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 345.5724 | 0.6411%
CZ 8 | 0.3724 | 0.077642 | 0.062608 | 0.93572 | 0.30561 | 0.17786 | 0 | 0.28999 | 0 | 0.0057589 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.5314 | 0.03247% | CZ 8 | 12.5467 | 2.6159 | 6.2608 | 60.7853 | 10.2964 | 5.9924 | 0 | 9.7704 | 0 | 0.19403 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 155.2802 | 0.03247% | CZ 8 | 3.6762 | 0.76646 | 0 | 4.8811 | 3.0168 | 1.7558 | 0 | 2.8627 | 0 | 0.05685 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 29.4561 | 0.03247% | CZ 8 | 0 | 0 | 0.062608 | 0.44126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.54748 | 0.03247% | CZ 8 | 38.486 | 8.024 | 6.8431 | 99.3302 | 31.5834 | 18.3811 | 0 | 29.9697 | 0 | 0.59516 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 368.2147 | 0.03247%
US Weighted | 0.37216 | 0.077156 | 0.056466 | 0.38331 | 0.096876 | 0.5829 | 0 | 0.28688 | 0.0029554 | 0.0018838 | 0 | 0.44054 | 0 | 0 | 0 | 0.86326 | 3.1644 | 100% | US Weighted | 12.5387 | 2.5995 | 5.6466 | 23.146 | 3.2639 | 19.6387 | 0 | 9.6653 | 0.099572 | 0.063468 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 123.4801 | 100% | US Weighted | 3.6738 | 0.76166 | 0 | 2.2607 | 0.95633 | 5.7541 | 0 | 2.8319 | 0.029175 | 0.018596 | 0 | 4.3488 | 0 | 0 | 0 | 8.0913 | 28.7265 | 100% | US Weighted | 0 | 0 | 0.056466 | 0.1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25437 | 100% | US Weighted | 38.4613 | 7.9738 | 6.1718 | 40.5323 | 10.0118 | 60.2402 | 0 | 29.6476 | 0.30543 | 0.19468 | 0 | 45.5278 | 0 | 0 | 0 | 89.4742 | 328.5409 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.42008 | 0.15623 | 0.055768 | 0.37649 | 0 | 1.4263 | 0 | 0.39861 | 0 | 0.0018692 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1528 | 1.751% | CZ 1A | 14.1533 | 5.2637 | 5.5768 | 25.7821 | 0 | 48.0534 | 0 | 13.43 | 0 | 0.062978 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 159.6007 | 1.751% | CZ 1A | 4.1469 | 1.5423 | 0 | 1.7666 | 0 | 14.0797 | 0 | 3.935 | 0 | 0.018452 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.0639 | 1.751% | CZ 1A | 0 | 0 | 0.055768 | 0.19753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2969 | 1.751% | CZ 1A | 43.4142 | 16.1461 | 6.0955 | 40.0844 | 0 | 147.3999 | 0 | 41.1954 | 0 | 0.19318 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 430.9418 | 1.751%
CZ 1B | 0.42008 | 0.15603 | 0.055768 | 0.44477 | 0.0025427 | 1.4592 | 0 | 0.40841 | 0 | 0.0018005 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.2661 | 0% | CZ 1B | 14.1533 | 5.257 | 5.5768 | 27.0107 | 0.085668 | 49.1643 | 0 | 13.7599 | 0 | 0.060662 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 162.3469 | 0% | CZ 1B | 4.1469 | 1.5403 | 0 | 2.6003 | 0.025101 | 14.4052 | 0 | 4.0317 | 0 | 0.017774 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 39.3422 | 0% | CZ 1B | 0 | 0 | 0.055768 | 0.18136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28073 | 0% | CZ 1B | 43.4142 | 16.1255 | 6.0955 | 47.0453 | 0.26278 | 150.8075 | 0 | 42.2075 | 0 | 0.18608 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 442.5574 | 0%
CZ 2A | 0.42008 | 0.15599 | 0.055768 | 0.4822 | 0.014074 | 1.3337 | 0 | 0.39011 | 0 | 0.0019173 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1713 | 14.08% | CZ 2A | 14.1533 | 5.2554 | 5.5768 | 28.6399 | 0.47419 | 44.9363 | 0 | 13.1436 | 0 | 0.064599 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 159.5225 | 14.08% | CZ 2A | 4.1469 | 1.5398 | 0 | 2.915 | 0.13894 | 13.1663 | 0 | 3.8511 | 0 | 0.018927 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.352 | 14.08% | CZ 2A | 0 | 0 | 0.055768 | 0.18691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28628 | 14.08% | CZ 2A | 43.4142 | 16.1205 | 6.0955 | 50.9467 | 1.4545 | 137.8383 | 0 | 40.3169 | 0 | 0.19815 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 432.7978 | 14.08%
CZ 2B | 0.42008 | 0.1561 | 0.055768 | 0.58342 | 0.18594 | 1.0082 | 0 | 0.4141 | 0 | 0.0015737 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1427 | 3.07% | CZ 2B | 14.1533 | 5.2591 | 5.5768 | 27.9635 | 6.2647 | 33.9689 | 0 | 13.9517 | 0 | 0.053022 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 154.4693 | 3.07% | CZ 2B | 4.1469 | 1.5409 | 0 | 4.5226 | 1.8355 | 9.9529 | 0 | 4.0878 | 0 | 0.015535 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.6772 | 3.07% | CZ 2B | 0 | 0 | 0.055768 | 0.12528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22465 | 3.07% | CZ 2B | 43.4142 | 16.1319 | 6.0955 | 61.0404 | 19.2163 | 104.1967 | 0 | 42.7956 | 0 | 0.16264 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 429.4663 | 3.07%
CZ 3A | 0.42008 | 0.15607 | 0.056314 | 0.57209 | 0.074756 | 0.94945 | 0 | 0.36893 | 0 | 0.0019242 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9171 | 14.41% | CZ 3A | 14.1533 | 5.2582 | 5.6314 | 30.5137 | 2.5186 | 31.9885 | 0 | 12.4298 | 0 | 0.06483 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 149.8368 | 14.41% | CZ 3A | 4.1469 | 1.5406 | 0 | 3.9743 | 0.73796 | 9.3726 | 0 | 3.6419 | 0 | 0.018995 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 36.0084 | 14.41% | CZ 3A | 0 | 0 | 0.056314 | 0.16949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26941 | 14.41% | CZ 3A | 43.4142 | 16.129 | 6.1552 | 60.1331 | 7.7257 | 98.1222 | 0 | 38.1273 | 0 | 0.19886 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 406.4187 | 14.41%
CZ 3B | 0.42008 | 0.15606 | 0.056067 | 0.54321 | 0.2417 | 0.79341 | 0 | 0.39505 | 0 | 0.0014775 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9245 | 6.297% | CZ 3B | 14.1533 | 5.2579 | 5.6067 | 25.9429 | 8.1431 | 26.7313 | 0 | 13.3101 | 0 | 0.04978 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 146.4734 | 6.297% | CZ 3B | 4.1469 | 1.5406 | 0 | 4.2248 | 2.3859 | 7.8323 | 0 | 3.8999 | 0 | 0.014586 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 36.6199 | 6.297% | CZ 3B | 0 | 0 | 0.056067 | 0.11524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21491 | 6.297% | CZ 3B | 43.4142 | 16.1283 | 6.1281 | 56.825 | 24.9783 | 81.996 | 0 | 40.8275 | 0 | 0.1527 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 406.8633 | 6.297%
CZ 3C | 0.42008 | 0.15603 | 0.055819 | 0.48837 | 0.028712 | 0.76492 | 0 | 0.36577 | 0 | 0.0019173 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.5991 | 1.4% | CZ 3C | 14.1533 | 5.257 | 5.5819 | 28.1334 | 0.96736 | 25.7713 | 0 | 12.3233 | 0 | 0.064599 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 139.5305 | 1.4% | CZ 3C | 4.1469 | 1.5403 | 0 | 3.0822 | 0.28344 | 7.551 | 0 | 3.6107 | 0 | 0.018927 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 32.8085 | 1.4% | CZ 3C | 0 | 0 | 0.055819 | 0.17614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27556 | 1.4% | CZ 3C | 43.4142 | 16.1255 | 6.101 | 51.5199 | 2.9673 | 79.0514 | 0 | 37.8006 | 0 | 0.19815 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 373.5912 | 1.4%
CZ 4A | 0.42008 | 0.15583 | 0.057257 | 0.70259 | 0.10723 | 0.78127 | 0 | 0.36177 | 0 | 0.0021854 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9057 | 18.54% | CZ 4A | 14.1533 | 5.2501 | 5.7257 | 36.8136 | 3.6129 | 26.3222 | 0 | 12.1887 | 0 | 0.073628 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 151.4184 | 18.54% | CZ 4A | 4.1469 | 1.5383 | 0 | 4.9793 | 1.0586 | 7.7124 | 0 | 3.5713 | 0 | 0.021573 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.6033 | 18.54% | CZ 4A | 0 | 0 | 0.057257 | 0.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29906 | 18.54% | CZ 4A | 43.4142 | 16.1042 | 6.2581 | 73.7906 | 11.0822 | 80.741 | 0 | 37.388 | 0 | 0.22585 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 405.4173 | 18.54%
CZ 4B | 0.42008 | 0.15594 | 0.056912 | 0.59333 | 0.347 | 0.63311 | 0 | 0.41705 | 0 | 0.0014432 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9423 | 0.5369% | CZ 4B | 14.1533 | 5.254 | 5.6912 | 26.9735 | 11.6912 | 21.3307 | 0 | 14.0512 | 0 | 0.048623 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 146.472 | 0.5369% | CZ 4B | 4.1469 | 1.5394 | 0 | 4.8175 | 3.4255 | 6.2499 | 0 | 4.117 | 0 | 0.014246 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 36.8855 | 0.5369% | CZ 4B | 0 | 0 | 0.056912 | 0.10531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20583 | 0.5369% | CZ 4B | 43.4142 | 16.1162 | 6.2204 | 61.9455 | 35.8617 | 65.4302 | 0 | 43.101 | 0 | 0.14915 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 408.6515 | 0.5369%
CZ 4C | 0.42008 | 0.15565 | 0.057349 | 0.67759 | 0.05517 | 0.48573 | 0 | 0.3624 | 0 | 0.002151 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.5336 | 3.995% | CZ 4C | 14.1533 | 5.2441 | 5.7349 | 35.0355 | 1.8588 | 16.365 | 0 | 12.2098 | 0 | 0.072471 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 137.9521 | 3.995% | CZ 4C | 4.1469 | 1.5365 | 0 | 4.8717 | 0.54462 | 4.7949 | 0 | 3.5775 | 0 | 0.021234 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 32.0684 | 3.995% | CZ 4C | 0 | 0 | 0.057349 | 0.18408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28504 | 3.995% | CZ 4C | 43.4142 | 16.0857 | 6.2683 | 71.1225 | 5.7016 | 50.1982 | 0 | 37.4526 | 0 | 0.2223 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 366.8785 | 3.995%
CZ 5A | 0.42008 | 0.15588 | 0.058442 | 0.79962 | 0.13983 | 0.49085 | 0 | 0.35916 | 0 | 0.0024809 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.7438 | 24.16% | CZ 5A | 14.1533 | 5.2517 | 5.8442 | 41.5151 | 4.7111 | 16.5377 | 0 | 12.1008 | 0 | 0.083584 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 147.4757 | 24.16% | CZ 5A | 4.1469 | 1.5387 | 0 | 5.7238 | 1.3803 | 4.8455 | 0 | 3.5455 | 0 | 0.02449 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 33.7803 | 24.16% | CZ 5A | 0 | 0 | 0.058442 | 0.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32184 | 24.16% | CZ 5A | 43.4142 | 16.1091 | 6.3877 | 83.9465 | 14.4508 | 50.728 | 0 | 37.1181 | 0 | 0.25639 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 388.8239 | 24.16%
CZ 5B | 0.42008 | 0.15588 | 0.058009 | 0.72847 | 0.35711 | 0.52134 | 0 | 0.41632 | 0 | 0.0016906 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9763 | 5.042% | CZ 5B | 14.1533 | 5.2519 | 5.8009 | 32.8278 | 12.0315 | 17.5648 | 0 | 14.0264 | 0 | 0.056958 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 148.992 | 5.042% | CZ 5B | 4.1469 | 1.5388 | 0 | 5.9579 | 3.5252 | 5.1465 | 0 | 4.1097 | 0 | 0.016689 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.0168 | 5.042% | CZ 5B | 0 | 0 | 0.058009 | 0.12494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22655 | 5.042% | CZ 5B | 43.4142 | 16.1099 | 6.3404 | 76.029 | 36.9057 | 53.8785 | 0 | 43.025 | 0 | 0.17471 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 412.2905 | 5.042%
CZ 5C | 0.42008 | 0.15563 | 0.058298 | 0.70609 | 0.061382 | 0.38707 | 0 | 0.36199 | 0 | 0.0021441 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.4701 | 0.1564% | CZ 5C | 14.1533 | 5.2436 | 5.8298 | 35.5418 | 2.0681 | 13.041 | 0 | 12.1959 | 0 | 0.072239 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 135.4241 | 0.1564% | CZ 5C | 4.1469 | 1.5364 | 0 | 5.2206 | 0.60595 | 3.821 | 0 | 3.5734 | 0 | 0.021166 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 31.5004 | 0.1564% | CZ 5C | 0 | 0 | 0.058298 | 0.17724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27914 | 0.1564% | CZ 5C | 43.4142 | 16.0843 | 6.372 | 74.027 | 6.3437 | 40.0023 | 0 | 37.41 | 0 | 0.22159 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 360.2882 | 0.1564%
CZ 6A | 0.42008 | 0.15581 | 0.059689 | 0.94619 | 0.19316 | 0.48815 | 0 | 0.3728 | 0 | 0.0031681 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9565 | 5.203% | CZ 6A | 14.1533 | 5.2494 | 5.9689 | 50.6331 | 6.508 | 16.4467 | 0 | 12.5604 | 0 | 0.10674 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 158.9048 | 5.203% | CZ 6A | 4.1469 | 1.5381 | 0 | 6.5484 | 1.9068 | 4.8189 | 0 | 3.6802 | 0 | 0.031274 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.2455 | 5.203% | CZ 6A | 0 | 0 | 0.059689 | 0.28284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.38613 | 5.203% | CZ 6A | 43.4142 | 16.102 | 6.524 | 99.4691 | 19.9628 | 50.4489 | 0 | 38.5279 | 0 | 0.32741 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 411.1895 | 5.203%
CZ 6B | 0.42008 | 0.15569 | 0.059351 | 0.90345 | 0.35574 | 0.42535 | 0 | 0.3976 | 0 | 0.0024121 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.0371 | 0.6872% | CZ 6B | 14.1533 | 5.2454 | 5.9351 | 43.7959 | 11.9855 | 14.3307 | 0 | 13.3957 | 0 | 0.081269 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 156.2013 | 0.6872% | CZ 6B | 4.1469 | 1.5369 | 0 | 6.93 | 3.5117 | 4.1989 | 0 | 3.925 | 0 | 0.023812 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 36.8482 | 0.6872% | CZ 6B | 0 | 0 | 0.059351 | 0.20144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.3044 | 0.6872% | CZ 6B | 43.4142 | 16.09 | 6.4871 | 94.5676 | 36.7644 | 43.9582 | 0 | 41.0903 | 0 | 0.24929 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 419.0342 | 0.6872%
CZ 7 | 0.42008 | 0.15559 | 0.061215 | 1.0623 | 0.24676 | 0.40282 | 0 | 0.37284 | 0 | 0.0037935 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.0429 | 0.6411% | CZ 7 | 14.1533 | 5.2422 | 6.1215 | 58.3235 | 8.3138 | 13.5717 | 0 | 12.5615 | 0 | 0.12781 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 165.6937 | 0.6411% | CZ 7 | 4.1469 | 1.536 | 0 | 7.1325 | 2.4359 | 3.9765 | 0 | 3.6805 | 0 | 0.037448 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.5208 | 0.6411% | CZ 7 | 0 | 0 | 0.061215 | 0.33981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.44462 | 0.6411% | CZ 7 | 43.4142 | 16.08 | 6.6908 | 111.8108 | 25.5018 | 41.6301 | 0 | 38.5314 | 0 | 0.39204 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 420.4643 | 0.6411%
CZ 8 | 0.42008 | 0.15474 | 0.063194 | 1.3602 | 0.34553 | 0.27168 | 0 | 0.37759 | 0 | 0.0049342 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.3154 | 0.03247% | CZ 8 | 14.1533 | 5.2135 | 6.3194 | 75.1009 | 11.6414 | 9.1533 | 0 | 12.7215 | 0 | 0.16624 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 181.748 | 0.03247% | CZ 8 | 4.1469 | 1.5276 | 0 | 9.0693 | 3.4109 | 2.6819 | 0 | 3.7274 | 0 | 0.048709 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.1877 | 0.03247% | CZ 8 | 0 | 0 | 0.063194 | 0.44148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.54828 | 0.03247% | CZ 8 | 43.4142 | 15.992 | 6.9071 | 143.1997 | 35.709 | 28.077 | 0 | 39.0222 | 0 | 0.50994 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 449.2442 | 0.03247%
US Weighted | 0.42008 | 0.15592 | 0.05724 | 0.6701 | 0.1241 | 0.7853 | 0 | 0.37453 | 0 | 0.0021423 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9069 | 100% | US Weighted | 14.1533 | 5.2532 | 5.724 | 35.2107 | 4.1813 | 26.4581 | 0 | 12.6187 | 0 | 0.072177 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.9499 | 100% | US Weighted | 4.1469 | 1.5392 | 0 | 4.7341 | 1.2251 | 7.7522 | 0 | 3.6973 | 0 | 0.021148 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.691 | 100% | US Weighted | 0 | 0 | 0.05724 | 0.19053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29138 | 100% | US Weighted | 43.4142 | 16.1138 | 6.2564 | 70.3869 | 12.8257 | 81.158 | 0 | 38.7068 | 0 | 0.2214 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 405.4964 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.42008 | 0.15623 | 0.055768 | 0.3997 | 0 | 1.516 | 0 | 0.43327 | 0 | 0.0018761 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.3004 | 1.751% | CZ 1A | 14.1533 | 5.2637 | 5.5768 | 26.726 | 0 | 51.0773 | 0 | 14.5976 | 0 | 0.063209 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 164.7363 | 1.751% | CZ 1A | 4.1469 | 1.5423 | 0 | 1.9716 | 0 | 14.9656 | 0 | 4.2771 | 0 | 0.01852 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 39.4971 | 1.751% | CZ 1A | 0 | 0 | 0.055768 | 0.19997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29934 | 1.751% | CZ 1A | 43.4142 | 16.1461 | 6.0955 | 42.4976 | 0 | 156.6753 | 0 | 44.7771 | 0 | 0.19389 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 446.2128 | 1.751%
CZ 1B | 0.42008 | 0.15603 | 0.055768 | 0.46995 | 0.0034361 | 1.5392 | 0 | 0.44497 | 0 | 0.001828 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.4087 | 0% | CZ 1B | 14.1533 | 5.257 | 5.5768 | 27.8869 | 0.11577 | 51.8587 | 0 | 14.9917 | 0 | 0.061589 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 167.1802 | 0% | CZ 1B | 4.1469 | 1.5403 | 0 | 2.8447 | 0.03392 | 15.1946 | 0 | 4.3926 | 0 | 0.018045 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 40.7461 | 0% | CZ 1B | 0 | 0 | 0.055768 | 0.18178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28115 | 0% | CZ 1B | 43.4142 | 16.1255 | 6.0955 | 49.65 | 0.35511 | 159.0723 | 0 | 45.9859 | 0 | 0.18892 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 457.3005 | 0%
CZ 2A | 0.42008 | 0.15599 | 0.055768 | 0.53117 | 0.019098 | 1.4224 | 0 | 0.42874 | 0 | 0.0018967 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.3526 | 14.08% | CZ 2A | 14.1533 | 5.2554 | 5.5768 | 30.2533 | 0.64344 | 47.9245 | 0 | 14.4451 | 0 | 0.063904 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 165.594 | 14.08% | CZ 2A | 4.1469 | 1.5398 | 0 | 3.4039 | 0.18853 | 14.0419 | 0 | 4.2324 | 0 | 0.018724 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 40.1471 | 14.08% | CZ 2A | 0 | 0 | 0.055768 | 0.18636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28573 | 14.08% | CZ 2A | 43.4142 | 16.1205 | 6.0955 | 56.0043 | 1.9737 | 147.0043 | 0 | 44.309 | 0 | 0.19602 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 451.5307 | 14.08%
CZ 2B | 0.42008 | 0.1561 | 0.055768 | 0.64986 | 0.21709 | 1.0572 | 0 | 0.45405 | 0 | 0.0015806 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.3292 | 3.07% | CZ 2B | 14.1533 | 5.2591 | 5.5768 | 30.2867 | 7.314 | 35.6204 | 0 | 15.2976 | 0 | 0.053253 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 160.8395 | 3.07% | CZ 2B | 4.1469 | 1.5409 | 0 | 5.1659 | 2.143 | 10.4368 | 0 | 4.4822 | 0 | 0.015603 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 40.5063 | 3.07% | CZ 2B | 0 | 0 | 0.055768 | 0.12656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22593 | 3.07% | CZ 2B | 43.4142 | 16.1319 | 6.0955 | 67.9143 | 22.4351 | 109.2627 | 0 | 46.9241 | 0 | 0.16335 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 448.7541 | 3.07%
CZ 3A | 0.42008 | 0.15607 | 0.056317 | 0.67382 | 0.095544 | 1.0013 | 0 | 0.40813 | 0 | 0.0020204 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1308 | 14.41% | CZ 3A | 14.1533 | 5.2582 | 5.6317 | 35.4359 | 3.219 | 33.7362 | 0 | 13.7507 | 0 | 0.068072 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 158.5313 | 14.41% | CZ 3A | 4.1469 | 1.5406 | 0 | 4.7561 | 0.94318 | 9.8847 | 0 | 4.029 | 0 | 0.019945 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.8954 | 14.41% | CZ 3A | 0 | 0 | 0.056317 | 0.19204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29196 | 14.41% | CZ 3A | 43.4142 | 16.129 | 6.1554 | 70.7807 | 9.8742 | 103.4829 | 0 | 42.1791 | 0 | 0.2088 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 428.6375 | 14.41%
CZ 3B | 0.42008 | 0.15606 | 0.056067 | 0.62807 | 0.27164 | 0.84206 | 0 | 0.43747 | 0 | 0.001505 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1304 | 6.297% | CZ 3B | 14.1533 | 5.2579 | 5.6067 | 29.0586 | 9.1519 | 28.3706 | 0 | 14.7391 | 0 | 0.050706 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 153.6672 | 6.297% | CZ 3B | 4.1469 | 1.5406 | 0 | 5.0244 | 2.6815 | 8.3126 | 0 | 4.3186 | 0 | 0.014857 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.6143 | 6.297% | CZ 3B | 0 | 0 | 0.056067 | 0.11911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21878 | 6.297% | CZ 3B | 43.4142 | 16.1283 | 6.1281 | 65.6184 | 28.0728 | 87.0243 | 0 | 45.211 | 0 | 0.15554 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 428.1658 | 6.297%
CZ 3C | 0.42008 | 0.15603 | 0.055819 | 0.599 | 0.037948 | 0.84378 | 0 | 0.4154 | 0 | 0.0020136 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.8475 | 1.4% | CZ 3C | 14.1533 | 5.257 | 5.5819 | 32.6709 | 1.2785 | 28.4284 | 0 | 13.9954 | 0 | 0.06784 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 148.7118 | 1.4% | CZ 3C | 4.1469 | 1.5403 | 0 | 4.0537 | 0.37461 | 8.3295 | 0 | 4.1007 | 0 | 0.019877 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.1406 | 1.4% | CZ 3C | 0 | 0 | 0.055819 | 0.18836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28778 | 1.4% | CZ 3C | 43.4142 | 16.1255 | 6.101 | 63.0258 | 3.9218 | 87.2019 | 0 | 42.9298 | 0 | 0.20809 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 399.3412 | 1.4%
CZ 4A | 0.42008 | 0.15583 | 0.057259 | 0.85775 | 0.13813 | 0.81236 | 0 | 0.40149 | 0 | 0.002419 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1628 | 18.54% | CZ 4A | 14.1533 | 5.2501 | 5.7259 | 43.5972 | 4.6539 | 27.3699 | 0 | 13.527 | 0 | 0.081501 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 161.6371 | 18.54% | CZ 4A | 4.1469 | 1.5383 | 0 | 6.2793 | 1.3636 | 8.0194 | 0 | 3.9634 | 0 | 0.02388 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.9097 | 18.54% | CZ 4A | 0 | 0 | 0.057259 | 0.22166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32253 | 18.54% | CZ 4A | 43.4142 | 16.1042 | 6.2584 | 89.9654 | 14.2754 | 83.9548 | 0 | 41.493 | 0 | 0.25 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 432.1285 | 18.54%
CZ 4B | 0.42008 | 0.15594 | 0.056912 | 0.72172 | 0.38396 | 0.6628 | 0 | 0.46099 | 0 | 0.0015394 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1814 | 0.5369% | CZ 4B | 14.1533 | 5.254 | 5.6912 | 31.9175 | 12.9364 | 22.3307 | 0 | 15.5317 | 0 | 0.051864 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 155.1449 | 0.5369% | CZ 4B | 4.1469 | 1.5394 | 0 | 5.9929 | 3.7904 | 6.5429 | 0 | 4.5508 | 0 | 0.015196 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 39.1534 | 0.5369% | CZ 4B | 0 | 0 | 0.056912 | 0.11464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21516 | 0.5369% | CZ 4B | 43.4142 | 16.1162 | 6.2204 | 75.2694 | 39.6813 | 68.4976 | 0 | 47.6421 | 0 | 0.15909 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 433.4135 | 0.5369%
CZ 4C | 0.42008 | 0.15565 | 0.057349 | 0.84262 | 0.068303 | 0.48725 | 0 | 0.40383 | 0 | 0.0023091 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.7548 | 3.995% | CZ 4C | 14.1533 | 5.2441 | 5.7349 | 42.3417 | 2.3012 | 16.4161 | 0 | 13.6057 | 0 | 0.077796 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 147.1532 | 3.995% | CZ 4C | 4.1469 | 1.5365 | 0 | 6.2409 | 0.67426 | 4.8099 | 0 | 3.9865 | 0 | 0.022794 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 33.9927 | 3.995% | CZ 4C | 0 | 0 | 0.057349 | 0.21042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.31137 | 3.995% | CZ 4C | 43.4142 | 16.0857 | 6.2683 | 88.3344 | 7.0588 | 50.3551 | 0 | 41.7345 | 0 | 0.23863 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 389.9028 | 3.995%
CZ 5A | 0.42008 | 0.15588 | 0.058442 | 0.95192 | 0.17575 | 0.49581 | 0 | 0.39822 | 0 | 0.0028382 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.9764 | 24.16% | CZ 5A | 14.1533 | 5.2517 | 5.8442 | 49.1028 | 5.9213 | 16.7046 | 0 | 13.4166 | 0 | 0.095624 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 157.7684 | 24.16% | CZ 5A | 4.1469 | 1.5387 | 0 | 6.8615 | 1.7349 | 4.8945 | 0 | 3.9311 | 0 | 0.028018 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 35.7106 | 24.16% | CZ 5A | 0 | 0 | 0.058442 | 0.25685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.35889 | 24.16% | CZ 5A | 43.4142 | 16.1091 | 6.3877 | 99.9062 | 18.1631 | 51.24 | 0 | 41.1542 | 0 | 0.29332 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 413.0811 | 24.16%
CZ 5B | 0.42008 | 0.15588 | 0.058009 | 0.84824 | 0.38998 | 0.53104 | 0 | 0.45845 | 0 | 0.0018417 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.181 | 5.042% | CZ 5B | 14.1533 | 5.2519 | 5.8009 | 38.0782 | 13.139 | 17.8917 | 0 | 15.446 | 0 | 0.062052 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 157.1014 | 5.042% | CZ 5B | 4.1469 | 1.5388 | 0 | 6.9592 | 3.8497 | 5.2423 | 0 | 4.5257 | 0 | 0.018181 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.8558 | 5.042% | CZ 5B | 0 | 0 | 0.058009 | 0.14327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24488 | 5.042% | CZ 5B | 43.4142 | 16.1099 | 6.3404 | 88.5151 | 40.3027 | 54.8813 | 0 | 47.3793 | 0 | 0.19034 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 433.5463 | 5.042%
CZ 5C | 0.42008 | 0.15563 | 0.0583 | 0.83093 | 0.072062 | 0.38005 | 0 | 0.40151 | 0 | 0.0022266 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 3.6383 | 0.1564% | CZ 5C | 14.1533 | 5.2436 | 5.83 | 40.9986 | 2.4279 | 12.8046 | 0 | 13.5277 | 0 | 0.075018 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 142.3392 | 0.1564% | CZ 5C | 4.1469 | 1.5364 | 0 | 6.2669 | 0.71137 | 3.7518 | 0 | 3.9636 | 0 | 0.02198 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 32.9738 | 0.1564% | CZ 5C | 0 | 0 | 0.0583 | 0.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.298 | 0.1564% | CZ 5C | 43.4142 | 16.0843 | 6.3722 | 87.0415 | 7.4473 | 39.2771 | 0 | 41.4952 | 0 | 0.23011 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 377.7751 | 0.1564%
CZ 6A | 0.42008 | 0.15581 | 0.059694 | 1.1396 | 0.23689 | 0.49609 | 0 | 0.41382 | 0 | 0.0037247 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.2431 | 5.203% | CZ 6A | 14.1533 | 5.2494 | 5.9694 | 60.9098 | 7.9813 | 16.7141 | 0 | 13.9424 | 0 | 0.12549 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 172.3235 | 5.203% | CZ 6A | 4.1469 | 1.5381 | 0 | 7.8975 | 2.3385 | 4.8972 | 0 | 4.0851 | 0 | 0.036769 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.5151 | 5.203% | CZ 6A | 0 | 0 | 0.059694 | 0.33956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.44286 | 5.203% | CZ 6A | 43.4142 | 16.102 | 6.5246 | 119.7924 | 24.4819 | 51.2692 | 0 | 42.7672 | 0 | 0.38494 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 441.1495 | 5.203%
CZ 6B | 0.42008 | 0.15569 | 0.059356 | 1.066 | 0.39969 | 0.42131 | 0 | 0.44016 | 0 | 0.0027489 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.2825 | 0.6872% | CZ 6B | 14.1533 | 5.2454 | 5.9356 | 51.5319 | 13.4664 | 14.1945 | 0 | 14.8299 | 0 | 0.092614 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 166.728 | 0.6872% | CZ 6B | 4.1469 | 1.5369 | 0 | 8.1983 | 3.9456 | 4.159 | 0 | 4.3452 | 0 | 0.027136 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.934 | 0.6872% | CZ 6B | 0 | 0 | 0.059356 | 0.23551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.33847 | 0.6872% | CZ 6B | 43.4142 | 16.09 | 6.4876 | 111.5694 | 41.3069 | 43.5406 | 0 | 45.4894 | 0 | 0.28409 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 444.5953 | 0.6872%
CZ 7 | 0.42008 | 0.15559 | 0.061219 | 1.2795 | 0.30629 | 0.41459 | 0 | 0.42204 | 0 | 0.0045563 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.3813 | 0.6411% | CZ 7 | 14.1533 | 5.2422 | 6.1219 | 70.5005 | 10.3196 | 13.9681 | 0 | 14.2191 | 0 | 0.15351 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 181.9566 | 0.6411% | CZ 7 | 4.1469 | 1.536 | 0 | 8.5523 | 3.0236 | 4.0927 | 0 | 4.1662 | 0 | 0.044978 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 38.1376 | 0.6411% | CZ 7 | 0 | 0 | 0.061219 | 0.41312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.51794 | 0.6411% | CZ 7 | 43.4142 | 16.08 | 6.6913 | 134.688 | 31.6544 | 42.846 | 0 | 43.6159 | 0 | 0.47087 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 455.8737 | 0.6411%
CZ 8 | 0.42008 | 0.15474 | 0.06321 | 1.5607 | 0.42243 | 0.27101 | 0 | 0.43095 | 0 | 0.0060132 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.6466 | 0.03247% | CZ 8 | 14.1533 | 5.2135 | 6.321 | 88.7157 | 14.2325 | 9.1306 | 0 | 14.5194 | 0 | 0.20259 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 199.767 | 0.03247% | CZ 8 | 4.1469 | 1.5276 | 0 | 10.0272 | 4.1701 | 2.6753 | 0 | 4.2542 | 0 | 0.05936 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 39.4356 | 0.03247% | CZ 8 | 0 | 0 | 0.06321 | 0.54493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.65175 | 0.03247% | CZ 8 | 43.4142 | 15.992 | 6.9089 | 164.5361 | 43.6571 | 28.0074 | 0 | 44.537 | 0 | 0.62144 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 484.0872 | 0.03247%
US Weighted | 0.42008 | 0.15592 | 0.057242 | 0.79271 | 0.15057 | 0.82063 | 0 | 0.41446 | 0 | 0.0023374 | 0 | 0.44808 | 0 | 0 | 0 | 0.86937 | 4.1314 | 100% | US Weighted | 14.1533 | 5.2532 | 5.7242 | 40.8476 | 5.0728 | 27.6483 | 0 | 13.9638 | 0 | 0.078751 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 160.0203 | 100% | US Weighted | 4.1469 | 1.5392 | 0 | 5.7203 | 1.4863 | 8.101 | 0 | 4.0914 | 0 | 0.023074 | 0 | 4.4233 | 0 | 0 | 0 | 8.1517 | 37.6831 | 100% | US Weighted | 0 | 0 | 0.057242 | 0.21325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.31409 | 100% | US Weighted | 43.4142 | 16.1138 | 6.2565 | 83.1931 | 15.5604 | 84.8089 | 0 | 42.8327 | 0 | 0.24156 | 0 | 46.3076 | 0 | 0 | 0 | 90.1056 | 428.8344 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 40946 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 40946 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1027 | 0.11878 | 0.0083448 | 0.21635 | 0 | 0.46319 | 0 | 0.18202 | 0 | 0.000914 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.1089 | 1.751% | CZ 1A | 3.4601 | 4.0019 | 0.83448 | 14.3959 | 0 | 15.6055 | 0 | 6.1325 | 0 | 0.030794 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.0217 | 1.751% | CZ 1A | 1.0138 | 1.1725 | 0 | 1.0778 | 0 | 4.5724 | 0 | 1.7968 | 0 | 0.0090227 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 9.8066 | 1.751% | CZ 1A | 0 | 0 | 0.0083448 | 0.10718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11552 | 1.751% | CZ 1A | 10.6135 | 12.2754 | 0.91209 | 22.9975 | 0 | 47.8686 | 0 | 18.8108 | 0 | 0.094459 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 115.2918 | 1.751%
CZ 1B | 0.10283 | 0.1187 | 0.0082083 | 0.29209 | 0.0019036 | 0.46478 | 0 | 0.18948 | 0 | 0.00087277 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.1955 | 0% | CZ 1B | 3.4645 | 3.9993 | 0.82083 | 16.1869 | 0.064135 | 15.6592 | 0 | 6.3839 | 0 | 0.029405 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.1688 | 0% | CZ 1B | 1.0151 | 1.1718 | 0 | 1.9386 | 0.018792 | 4.5882 | 0 | 1.8705 | 0 | 0.0086157 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 10.7758 | 0% | CZ 1B | 0 | 0 | 0.0082083 | 0.095705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10391 | 0% | CZ 1B | 10.627 | 12.2676 | 0.89716 | 30.7558 | 0.19673 | 48.0334 | 0 | 19.5821 | 0 | 0.090198 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 124.1694 | 0%
CZ 2A | 0.1027 | 0.11852 | 0.0081203 | 0.29677 | 0 | 0.49171 | 0 | 0.19026 | 0 | 0.00087964 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2256 | 14.08% | CZ 2A | 3.4603 | 3.9933 | 0.81203 | 16.4365 | 0 | 16.5664 | 0 | 6.4101 | 0 | 0.029637 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 48.2688 | 14.08% | CZ 2A | 1.0139 | 1.17 | 0 | 1.9712 | 0 | 4.854 | 0 | 1.8782 | 0 | 0.0086835 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.0601 | 14.08% | CZ 2A | 0 | 0 | 0.0081203 | 0.09709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10521 | 14.08% | CZ 2A | 10.6142 | 12.2491 | 0.88755 | 31.248 | 0 | 50.816 | 0 | 19.6624 | 0 | 0.090908 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 127.2876 | 14.08%
CZ 2B | 0.10224 | 0.11862 | 0.007868 | 0.44511 | 0.068791 | 0.38606 | 0 | 0.19925 | 0 | 0.00076969 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3454 | 3.07% | CZ 2B | 3.4448 | 3.9965 | 0.7868 | 19.0363 | 2.3177 | 13.007 | 0 | 6.7132 | 0 | 0.025932 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 49.8888 | 3.07% | CZ 2B | 1.0093 | 1.171 | 0 | 3.7925 | 0.67908 | 3.811 | 0 | 1.967 | 0 | 0.0075981 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.6018 | 3.07% | CZ 2B | 0 | 0 | 0.007868 | 0.060925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068793 | 3.07% | CZ 2B | 10.5666 | 12.2591 | 0.85997 | 46.3631 | 7.1093 | 39.8979 | 0 | 20.592 | 0 | 0.079544 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 139.447 | 3.07%
CZ 3A | 0.1018 | 0.1183 | 0.0072037 | 0.35165 | 0.015091 | 0.40051 | 0 | 0.17071 | 0 | 0.00075594 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.1827 | 14.41% | CZ 3A | 3.43 | 3.9859 | 0.72037 | 17.8052 | 0.50845 | 13.4939 | 0 | 5.7516 | 0 | 0.025469 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 46.2814 | 14.41% | CZ 3A | 1.005 | 1.1679 | 0 | 2.5845 | 0.14898 | 3.9537 | 0 | 1.6852 | 0 | 0.0074624 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 10.717 | 14.41% | CZ 3A | 0 | 0 | 0.0072037 | 0.089844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097048 | 14.41% | CZ 3A | 10.5212 | 12.2264 | 0.78736 | 36.8771 | 1.5596 | 41.3915 | 0 | 17.6425 | 0 | 0.078124 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 122.8032 | 14.41%
CZ 3B | 0.10201 | 0.1189 | 0.0073541 | 0.42445 | 0.12859 | 0.314 | 0 | 0.18581 | 0 | 0.0006185 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2984 | 6.297% | CZ 3B | 3.4369 | 4.0058 | 0.73541 | 17.5756 | 4.3323 | 10.5793 | 0 | 6.2603 | 0 | 0.020838 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.507 | 6.297% | CZ 3B | 1.007 | 1.1737 | 0 | 3.7025 | 1.2694 | 3.0997 | 0 | 1.8343 | 0 | 0.0061056 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.2569 | 6.297% | CZ 3B | 0 | 0 | 0.0073541 | 0.049391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056745 | 6.297% | CZ 3B | 10.5425 | 12.2875 | 0.8038 | 44.1599 | 13.2889 | 32.4512 | 0 | 19.2029 | 0 | 0.06392 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 134.52 | 6.297%
CZ 3C | 0.10213 | 0.11898 | 0.0068402 | 0.41175 | 0.0057864 | 0.37881 | 0 | 0.18332 | 0 | 0.00096898 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2252 | 1.4% | CZ 3C | 3.4411 | 4.0086 | 0.68402 | 20.3089 | 0.19495 | 12.7627 | 0 | 6.1762 | 0 | 0.032647 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 48.1697 | 1.4% | CZ 3C | 1.0082 | 1.1745 | 0 | 3.1064 | 0.057121 | 3.7395 | 0 | 1.8096 | 0 | 0.0095654 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.0692 | 1.4% | CZ 3C | 0 | 0 | 0.0068402 | 0.097069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10391 | 1.4% | CZ 3C | 10.5552 | 12.296 | 0.74764 | 43.1305 | 0.598 | 39.1486 | 0 | 18.945 | 0 | 0.10014 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 127.2406 | 1.4%
CZ 4A | 0.10314 | 0.11837 | 0.0065671 | 0.56082 | 0.010123 | 0.37335 | 0 | 0.15297 | 0 | 0.00067348 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3427 | 18.54% | CZ 4A | 3.4751 | 3.9882 | 0.65671 | 24.2621 | 0.34105 | 12.5787 | 0 | 5.1538 | 0 | 0.022691 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 51.0388 | 18.54% | CZ 4A | 1.0182 | 1.1685 | 0 | 4.7373 | 0.099928 | 3.6855 | 0 | 1.5101 | 0 | 0.0066483 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.3904 | 18.54% | CZ 4A | 0 | 0 | 0.0065671 | 0.080939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087506 | 18.54% | CZ 4A | 10.6597 | 12.2335 | 0.71778 | 58.4411 | 1.0462 | 38.584 | 0 | 15.8087 | 0 | 0.069601 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 139.2799 | 18.54%
CZ 4B | 0.10342 | 0.1187 | 0.0068078 | 0.49351 | 0.18629 | 0.24966 | 0 | 0.18062 | 0 | 0.00047418 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3561 | 0.5369% | CZ 4B | 3.4844 | 3.9993 | 0.68078 | 18.9684 | 6.2765 | 8.4115 | 0 | 6.0852 | 0 | 0.015976 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 48.4826 | 0.5369% | CZ 4B | 1.0209 | 1.1718 | 0 | 4.5232 | 1.839 | 2.4646 | 0 | 1.783 | 0 | 0.004681 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.9714 | 0.5369% | CZ 4B | 0 | 0 | 0.0068078 | 0.03531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042118 | 0.5369% | CZ 4B | 10.6881 | 12.2676 | 0.74409 | 51.2124 | 19.2526 | 25.8015 | 0 | 18.6659 | 0 | 0.049005 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 140.4006 | 0.5369%
CZ 4C | 0.10249 | 0.11771 | 0.0061203 | 0.59974 | 0.016445 | 0.22805 | 0 | 0.15909 | 0 | 0.00093462 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2472 | 3.995% | CZ 4C | 3.4531 | 3.9657 | 0.61203 | 26.5377 | 0.55407 | 7.6835 | 0 | 5.3601 | 0 | 0.031489 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 48.7583 | 3.995% | CZ 4C | 1.0118 | 1.162 | 0 | 4.9779 | 0.16234 | 2.2513 | 0 | 1.5705 | 0 | 0.0092262 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.3092 | 3.995% | CZ 4C | 0 | 0 | 0.0061203 | 0.095483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1016 | 3.995% | CZ 4C | 10.5922 | 12.1646 | 0.66895 | 62.5499 | 1.6995 | 23.5686 | 0 | 16.4415 | 0 | 0.09659 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 129.5013 | 3.995%
CZ 5A | 0.10311 | 0.11817 | 0.0060879 | 0.58283 | 0.023489 | 0.18943 | 0 | 0.15649 | 0 | 0.00044669 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.1967 | 24.16% | CZ 5A | 3.474 | 3.9815 | 0.60879 | 23.9122 | 0.79139 | 6.3821 | 0 | 5.2725 | 0 | 0.01505 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.998 | 24.16% | CZ 5A | 1.0179 | 1.1666 | 0 | 5.117 | 0.23188 | 1.8699 | 0 | 1.5449 | 0 | 0.0044096 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.1167 | 24.16% | CZ 5A | 0 | 0 | 0.0060879 | 0.064481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070569 | 24.16% | CZ 5A | 10.6561 | 12.2129 | 0.66541 | 60.6173 | 2.4275 | 19.5764 | 0 | 16.1731 | 0 | 0.046164 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 124.0944 | 24.16%
CZ 5B | 0.10338 | 0.11846 | 0.0061088 | 0.55782 | 0.20684 | 0.20628 | 0 | 0.17848 | 0 | 0.00030238 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3943 | 5.042% | CZ 5B | 3.483 | 3.9912 | 0.61088 | 20.8386 | 6.9688 | 6.95 | 0 | 6.0135 | 0 | 0.010188 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 49.4267 | 5.042% | CZ 5B | 1.0205 | 1.1694 | 0 | 5.2022 | 2.0418 | 2.0364 | 0 | 1.7619 | 0 | 0.002985 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 13.3995 | 5.042% | CZ 5B | 0 | 0 | 0.0061088 | 0.030838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036946 | 5.042% | CZ 5B | 10.6838 | 12.2427 | 0.66769 | 57.8322 | 21.3761 | 21.3186 | 0 | 18.4458 | 0 | 0.03125 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 144.3175 | 5.042%
CZ 5C | 0.10265 | 0.11762 | 0.006074 | 0.57803 | 0.015483 | 0.18644 | 0 | 0.1528 | 0 | 0.00076281 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.1765 | 0.1564% | CZ 5C | 3.4585 | 3.963 | 0.6074 | 24.394 | 0.52165 | 6.2816 | 0 | 5.1482 | 0 | 0.0257 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.9605 | 0.1564% | CZ 5C | 1.0133 | 1.1611 | 0 | 4.9738 | 0.15284 | 1.8405 | 0 | 1.5084 | 0 | 0.0075302 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 10.8218 | 0.1564% | CZ 5C | 0 | 0 | 0.006074 | 0.074187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080261 | 0.1564% | CZ 5C | 10.6085 | 12.1561 | 0.66389 | 60.1789 | 1.6001 | 19.2682 | 0 | 15.7917 | 0 | 0.078834 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 122.0657 | 0.1564%
CZ 6A | 0.10366 | 0.11809 | 0.0060138 | 0.67489 | 0.046195 | 0.18519 | 0 | 0.16536 | 0 | 0.00058414 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3166 | 5.203% | CZ 6A | 3.4925 | 3.9787 | 0.60138 | 28.3595 | 1.5564 | 6.2392 | 0 | 5.5712 | 0 | 0.019681 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 50.3791 | 5.203% | CZ 6A | 1.0233 | 1.1658 | 0 | 5.8254 | 0.45602 | 1.8281 | 0 | 1.6324 | 0 | 0.0057664 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.1009 | 5.203% | CZ 6A | 0 | 0 | 0.0060138 | 0.084777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090791 | 5.203% | CZ 6A | 10.7129 | 12.2044 | 0.65731 | 70.2518 | 4.7741 | 19.1382 | 0 | 17.0892 | 0 | 0.060368 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 136.6077 | 5.203%
CZ 6B | 0.10358 | 0.11766 | 0.0060023 | 0.6824 | 0.17138 | 0.17423 | 0 | 0.17507 | 0 | 0.0005429 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.4475 | 0.6872% | CZ 6B | 3.4897 | 3.9641 | 0.60023 | 27.1151 | 5.774 | 5.8701 | 0 | 5.8984 | 0 | 0.018291 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 53.2905 | 0.6872% | CZ 6B | 1.0225 | 1.1615 | 0 | 6.1226 | 1.6918 | 1.7199 | 0 | 1.7282 | 0 | 0.0053594 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 13.6161 | 0.6872% | CZ 6B | 0 | 0 | 0.0060023 | 0.062189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068192 | 0.6872% | CZ 6B | 10.7044 | 12.1596 | 0.65605 | 70.8944 | 17.7114 | 18.0061 | 0 | 18.0928 | 0 | 0.056107 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 150.0003 | 0.6872%
CZ 7 | 0.10389 | 0.11756 | 0.0059953 | 0.74181 | 0.052943 | 0.16272 | 0 | 0.17016 | 0 | 0.00052916 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.3722 | 0.6411% | CZ 7 | 3.5001 | 3.9609 | 0.59953 | 31.2164 | 1.7838 | 5.4823 | 0 | 5.7331 | 0 | 0.017828 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 52.8544 | 0.6411% | CZ 7 | 1.0255 | 1.1605 | 0 | 6.3964 | 0.52264 | 1.6063 | 0 | 1.6798 | 0 | 0.0052237 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 12.5606 | 0.6411% | CZ 7 | 0 | 0 | 0.0059953 | 0.093858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099853 | 0.6411% | CZ 7 | 10.7364 | 12.1497 | 0.65529 | 77.2222 | 5.4715 | 16.8165 | 0 | 17.5857 | 0 | 0.054687 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 142.4114 | 0.6411%
CZ 8 | 0.10183 | 0.11413 | 0.0058287 | 0.83814 | 0.064269 | 0.12252 | 0 | 0.17421 | 0 | 0.00024053 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.4378 | 0.03247% | CZ 8 | 3.4307 | 3.8451 | 0.58287 | 34.7387 | 2.1653 | 4.1278 | 0 | 5.8694 | 0 | 0.0081038 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 55.3285 | 0.03247% | CZ 8 | 1.0052 | 1.1266 | 0 | 7.306 | 0.63444 | 1.2095 | 0 | 1.7197 | 0 | 0.0023744 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 13.1681 | 0.03247% | CZ 8 | 0 | 0 | 0.0058287 | 0.098034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10386 | 0.03247% | CZ 8 | 10.5233 | 11.7946 | 0.63707 | 87.202 | 6.642 | 12.6618 | 0 | 18.004 | 0 | 0.024858 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 149.2089 | 0.03247%
US Weighted | 0.10278 | 0.11835 | 0.0068091 | 0.48766 | 0.036067 | 0.32002 | 0 | 0.16864 | 0 | 0.00065162 | 0 | 0.008762 | 0 | 0 | 0 | 0.0078755 | 1.2576 | 100% | US Weighted | 3.4629 | 3.9872 | 0.68091 | 21.5069 | 1.2152 | 10.782 | 0 | 5.6818 | 0 | 0.021954 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.8994 | 100% | US Weighted | 1.0146 | 1.1683 | 0 | 4.0582 | 0.35604 | 3.1591 | 0 | 1.6648 | 0 | 0.0064325 | 0 | 0.086496 | 0 | 0 | 0 | 0.077745 | 11.5917 | 100% | US Weighted | 0 | 0 | 0.0068091 | 0.076563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083372 | 100% | US Weighted | 10.6221 | 12.2306 | 0.74424 | 50.854 | 3.7274 | 33.0729 | 0 | 17.4285 | 0 | 0.067342 | 0 | 0.90553 | 0 | 0 | 0 | 0.81391 | 130.4665 | 100%
Building Type: | Outpatient Healthcare |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 40946 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 40946 | [17 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 24.45% | 76.03% | 14.96% | 54.13% | 0% | 30.55% | 0% | 42.01% | 0% | 48.72% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 25.79% | 1.751% | CZ 1A | 24.45% | 76.03% | 14.96% | 53.86% | 0% | 30.55% | 0% | 42.01% | 0% | 48.72% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 27.33% | 1.751% | CZ 1A | 24.45% | 76.03% | 0% | 54.66% | 0% | 30.55% | 0% | 42.01% | 0% | 48.72% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 24.83% | 1.751% | CZ 1A | 0% | 0% | 14.96% | 53.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.59% | 1.751% | CZ 1A | 24.45% | 76.03% | 14.96% | 54.11% | 0% | 30.55% | 0% | 42.01% | 0% | 48.72% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 25.84% | 1.751%
CZ 1B | 24.48% | 76.08% | 14.72% | 62.15% | 55.4% | 30.2% | 0% | 42.58% | 0% | 47.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 27.12% | 0% | CZ 1B | 24.48% | 76.08% | 14.72% | 58.04% | 55.4% | 30.2% | 0% | 42.58% | 0% | 47.74% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.21% | 0% | CZ 1B | 24.48% | 76.08% | 0% | 68.15% | 55.4% | 30.2% | 0% | 42.58% | 0% | 47.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 26.45% | 0% | CZ 1B | 0% | 0% | 14.72% | 52.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.96% | 0% | CZ 1B | 24.48% | 76.08% | 14.72% | 61.95% | 55.4% | 30.2% | 0% | 42.58% | 0% | 47.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 27.15% | 0%
CZ 2A | 24.45% | 75.98% | 14.56% | 55.87% | 0% | 34.57% | 0% | 44.38% | 0% | 46.38% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 28.16% | 14.08% | CZ 2A | 24.45% | 75.98% | 14.56% | 54.33% | 0% | 34.57% | 0% | 44.38% | 0% | 46.38% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.15% | 14.08% | CZ 2A | 24.45% | 75.98% | 0% | 57.91% | 0% | 34.57% | 0% | 44.38% | 0% | 46.38% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 27.55% | 14.08% | CZ 2A | 0% | 0% | 14.56% | 52.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.82% | 14.08% | CZ 2A | 24.45% | 75.98% | 14.56% | 55.8% | 0% | 34.57% | 0% | 44.38% | 0% | 46.38% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.19% | 14.08%
CZ 2B | 24.34% | 75.99% | 14.11% | 68.49% | 31.69% | 36.52% | 0% | 43.88% | 0% | 48.7% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 31.08% | 3.07% | CZ 2B | 24.34% | 75.99% | 14.11% | 62.85% | 31.69% | 36.52% | 0% | 43.88% | 0% | 48.7% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.02% | 3.07% | CZ 2B | 24.34% | 75.99% | 0% | 73.41% | 31.69% | 36.52% | 0% | 43.88% | 0% | 48.7% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 31.11% | 3.07% | CZ 2B | 0% | 0% | 14.11% | 48.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.45% | 3.07% | CZ 2B | 24.34% | 75.99% | 14.11% | 68.27% | 31.69% | 36.52% | 0% | 43.88% | 0% | 48.7% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.07% | 3.07%
CZ 3A | 24.23% | 75.8% | 12.79% | 52.19% | 15.8% | 40% | 0% | 41.83% | 0% | 37.41% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 28.63% | 14.41% | CZ 3A | 24.23% | 75.8% | 12.79% | 50.25% | 15.8% | 40% | 0% | 41.83% | 0% | 37.41% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.19% | 14.41% | CZ 3A | 24.23% | 75.8% | 0% | 54.34% | 15.8% | 40% | 0% | 41.83% | 0% | 37.41% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 28.28% | 14.41% | CZ 3A | 0% | 0% | 12.79% | 46.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.24% | 14.41% | CZ 3A | 24.23% | 75.8% | 12.79% | 52.1% | 15.8% | 40% | 0% | 41.83% | 0% | 37.41% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.65% | 14.41%
CZ 3B | 24.28% | 76.19% | 13.12% | 67.58% | 47.34% | 37.29% | 0% | 42.47% | 0% | 41.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 31.43% | 6.297% | CZ 3B | 24.28% | 76.19% | 13.12% | 60.48% | 47.34% | 37.29% | 0% | 42.47% | 0% | 41.1% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 30.92% | 6.297% | CZ 3B | 24.28% | 76.19% | 0% | 73.69% | 47.34% | 37.29% | 0% | 42.47% | 0% | 41.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 31.74% | 6.297% | CZ 3B | 0% | 0% | 13.12% | 41.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.94% | 6.297% | CZ 3B | 24.28% | 76.19% | 13.12% | 67.3% | 47.34% | 37.29% | 0% | 42.47% | 0% | 41.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.42% | 6.297%
CZ 3C | 24.31% | 76.25% | 12.25% | 68.74% | 15.25% | 44.89% | 0% | 44.13% | 0% | 48.12% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 31.84% | 1.4% | CZ 3C | 24.31% | 76.25% | 12.25% | 62.16% | 15.25% | 44.89% | 0% | 44.13% | 0% | 48.12% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 32.39% | 1.4% | CZ 3C | 24.31% | 76.25% | 0% | 76.63% | 15.25% | 44.89% | 0% | 44.13% | 0% | 48.12% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 31.5% | 1.4% | CZ 3C | 0% | 0% | 12.25% | 51.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.11% | 1.4% | CZ 3C | 24.31% | 76.25% | 12.25% | 68.43% | 15.25% | 44.89% | 0% | 44.13% | 0% | 48.12% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.86% | 1.4%
CZ 4A | 24.55% | 75.96% | 11.47% | 65.38% | 7.328% | 45.96% | 0% | 38.1% | 0% | 27.84% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 32.25% | 18.54% | CZ 4A | 24.55% | 75.96% | 11.47% | 55.65% | 7.328% | 45.96% | 0% | 38.1% | 0% | 27.84% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.58% | 18.54% | CZ 4A | 24.55% | 75.96% | 0% | 75.44% | 7.328% | 45.96% | 0% | 38.1% | 0% | 27.84% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 32.68% | 18.54% | CZ 4A | 0% | 0% | 11.47% | 36.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.13% | 18.54% | CZ 4A | 24.55% | 75.96% | 11.47% | 64.96% | 7.328% | 45.96% | 0% | 38.1% | 0% | 27.84% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 32.23% | 18.54%
CZ 4B | 24.62% | 76.12% | 11.96% | 68.38% | 48.52% | 37.67% | 0% | 39.18% | 0% | 30.8% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 32.43% | 0.5369% | CZ 4B | 24.62% | 76.12% | 11.96% | 59.43% | 48.52% | 37.67% | 0% | 39.18% | 0% | 30.8% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.25% | 0.5369% | CZ 4B | 24.62% | 76.12% | 0% | 75.48% | 48.52% | 37.67% | 0% | 39.18% | 0% | 30.8% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 33.13% | 0.5369% | CZ 4B | 0% | 0% | 11.96% | 30.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.58% | 0.5369% | CZ 4B | 24.62% | 76.12% | 11.96% | 68.04% | 48.52% | 37.67% | 0% | 39.18% | 0% | 30.8% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 32.39% | 0.5369%
CZ 4C | 24.4% | 75.62% | 10.67% | 71.18% | 24.08% | 46.8% | 0% | 39.4% | 0% | 40.48% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 33.22% | 3.995% | CZ 4C | 24.4% | 75.62% | 10.67% | 62.68% | 24.08% | 46.8% | 0% | 39.4% | 0% | 40.48% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 33.13% | 3.995% | CZ 4C | 24.4% | 75.62% | 0% | 79.76% | 24.08% | 46.8% | 0% | 39.4% | 0% | 40.48% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 33.27% | 3.995% | CZ 4C | 0% | 0% | 10.67% | 45.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.63% | 3.995% | CZ 4C | 24.4% | 75.62% | 10.67% | 70.81% | 24.08% | 46.8% | 0% | 39.4% | 0% | 40.48% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 33.21% | 3.995%
CZ 5A | 24.55% | 75.81% | 10.42% | 61.23% | 13.37% | 38.21% | 0% | 39.3% | 0% | 15.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 30.1% | 24.16% | CZ 5A | 24.55% | 75.81% | 10.42% | 48.7% | 13.37% | 38.21% | 0% | 39.3% | 0% | 15.74% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.52% | 24.16% | CZ 5A | 24.55% | 75.81% | 0% | 74.58% | 13.37% | 38.21% | 0% | 39.3% | 0% | 15.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 31.13% | 24.16% | CZ 5A | 0% | 0% | 10.42% | 25.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.66% | 24.16% | CZ 5A | 24.55% | 75.81% | 10.42% | 60.67% | 13.37% | 38.21% | 0% | 39.3% | 0% | 15.74% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 30.04% | 24.16%
CZ 5B | 24.61% | 76% | 10.53% | 65.76% | 53.04% | 38.84% | 0% | 38.93% | 0% | 16.42% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 33.35% | 5.042% | CZ 5B | 24.61% | 76% | 10.53% | 54.73% | 53.04% | 38.84% | 0% | 38.93% | 0% | 16.42% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.46% | 5.042% | CZ 5B | 24.61% | 76% | 0% | 74.75% | 53.04% | 38.84% | 0% | 38.93% | 0% | 16.42% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 34.49% | 5.042% | CZ 5B | 0% | 0% | 10.53% | 21.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.09% | 5.042% | CZ 5B | 24.61% | 76% | 10.53% | 65.34% | 53.04% | 38.84% | 0% | 38.93% | 0% | 16.42% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 33.29% | 5.042%
CZ 5C | 24.44% | 75.58% | 10.42% | 69.56% | 21.49% | 49.06% | 0% | 38.06% | 0% | 34.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 32.34% | 0.1564% | CZ 5C | 24.44% | 75.58% | 10.42% | 59.5% | 21.49% | 49.06% | 0% | 38.06% | 0% | 34.26% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.59% | 0.1564% | CZ 5C | 24.44% | 75.58% | 0% | 79.37% | 21.49% | 49.06% | 0% | 38.06% | 0% | 34.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 32.82% | 0.1564% | CZ 5C | 0% | 0% | 10.42% | 37.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.93% | 0.1564% | CZ 5C | 24.44% | 75.58% | 10.42% | 69.14% | 21.49% | 49.06% | 0% | 38.06% | 0% | 34.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 32.31% | 0.1564%
CZ 6A | 24.68% | 75.79% | 10.07% | 59.22% | 19.5% | 37.33% | 0% | 39.96% | 0% | 15.68% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 31.03% | 5.203% | CZ 6A | 24.68% | 75.79% | 10.07% | 46.56% | 19.5% | 37.33% | 0% | 39.96% | 0% | 15.68% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.24% | 5.203% | CZ 6A | 24.68% | 75.79% | 0% | 73.76% | 19.5% | 37.33% | 0% | 39.96% | 0% | 15.68% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 32.26% | 5.203% | CZ 6A | 0% | 0% | 10.07% | 24.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.5% | 5.203% | CZ 6A | 24.68% | 75.79% | 10.07% | 58.64% | 19.5% | 37.33% | 0% | 39.96% | 0% | 15.68% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 30.97% | 5.203%
CZ 6B | 24.66% | 75.57% | 10.11% | 64.02% | 42.88% | 41.35% | 0% | 39.77% | 0% | 19.75% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 33.8% | 0.6872% | CZ 6B | 24.66% | 75.57% | 10.11% | 52.62% | 42.88% | 41.35% | 0% | 39.77% | 0% | 19.75% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 31.96% | 0.6872% | CZ 6B | 24.66% | 75.57% | 0% | 74.68% | 42.88% | 41.35% | 0% | 39.77% | 0% | 19.75% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 34.97% | 0.6872% | CZ 6B | 0% | 0% | 10.11% | 26.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.15% | 0.6872% | CZ 6B | 24.66% | 75.57% | 10.11% | 63.54% | 42.88% | 41.35% | 0% | 39.77% | 0% | 19.75% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 33.74% | 0.6872%
CZ 7 | 24.73% | 75.56% | 9.793% | 57.98% | 17.29% | 39.25% | 0% | 40.32% | 0% | 11.61% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 31.32% | 0.6411% | CZ 7 | 24.73% | 75.56% | 9.793% | 44.28% | 17.29% | 39.25% | 0% | 40.32% | 0% | 11.61% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.05% | 0.6411% | CZ 7 | 24.73% | 75.56% | 0% | 74.79% | 17.29% | 39.25% | 0% | 40.32% | 0% | 11.61% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 32.94% | 0.6411% | CZ 7 | 0% | 0% | 9.793% | 22.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.28% | 0.6411% | CZ 7 | 24.73% | 75.56% | 9.793% | 57.33% | 17.29% | 39.25% | 0% | 40.32% | 0% | 11.61% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.24% | 0.6411%
CZ 8 | 24.24% | 73.75% | 9.221% | 53.7% | 15.21% | 45.21% | 0% | 40.42% | 0% | 4% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 30.94% | 0.03247% | CZ 8 | 24.24% | 73.75% | 9.221% | 39.16% | 15.21% | 45.21% | 0% | 40.42% | 0% | 4% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 27.7% | 0.03247% | CZ 8 | 24.24% | 73.75% | 0% | 72.86% | 15.21% | 45.21% | 0% | 40.42% | 0% | 4% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 33.39% | 0.03247% | CZ 8 | 0% | 0% | 9.221% | 17.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.94% | 0.03247% | CZ 8 | 24.24% | 73.75% | 9.221% | 53% | 15.21% | 45.21% | 0% | 40.42% | 0% | 4% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 30.82% | 0.03247%
US Weighted | 24.47% | 75.9% | 11.9% | 61.52% | 23.95% | 39% | 0% | 40.69% | 0% | 27.88% | 0% | 1.955% | 0% | 0% | 0% | 0.9059% | 30.44% | 100% | US Weighted | 24.47% | 75.9% | 11.9% | 52.65% | 23.95% | 39% | 0% | 40.69% | 0% | 27.88% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.93% | 100% | US Weighted | 24.47% | 75.9% | 0% | 70.95% | 23.95% | 39% | 0% | 40.69% | 0% | 27.88% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 30.76% | 100% | US Weighted | 0% | 0% | 11.9% | 35.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.54% | 100% | US Weighted | 24.47% | 75.9% | 11.9% | 61.13% | 23.95% | 39% | 0% | 40.69% | 0% | 27.88% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 30.42% | 100%

## MedHos
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Hospital |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Hospital | [14 empty] | Prototype Floor Area: | 241501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.39609 | 0.018054 | 0.050157 | 0.29008 | 0.077457 | 0.28568 | 0.028979 | 0.33976 | 0.021383 | 0.056989 | 0.024318 | 0.29215 | 0.0082805 | 0.27223 | 0 | 0.63669 | 2.7983 |  | STD2016 | 13.3448 | 0.60826 | 4.8112 | 25.1823 | 2.6096 | 9.6251 | 0.97634 | 11.4471 | 0.72045 | 1.9201 | 0.81931 | 9.843 | 0.27898 | 16.4378 | 0 | 21.4513 | 120.0757 |  | STD2016 | 3.91 | 0.17822 | 0.030447 | 0.56951 | 0.76463 | 2.8202 | 0.28607 | 3.354 | 0.21109 | 0.56258 | 0.24006 | 2.884 | 0.081742 | 1.6057 | 0 | 6.2852 | 23.7834 |  | STD2016 | 0 | 0 | 0.047073 | 0.23239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38904 |  | STD2016 | 40.9341 | 1.8658 | 5.4638 | 31.362 | 8.0049 | 29.5242 | 2.9948 | 35.1131 | 2.2099 | 5.8896 | 2.5132 | 30.1926 | 0.85576 | 28.7866 | 0 | 65.8001 | 291.5104
STD2013 | 0.40432 | 0.024723 | 0.051803 | 0.29584 | 0.078325 | 0.29192 | 0.028853 | 0.34038 | 0.027866 | 0.063272 | 0.024315 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.8447 |  | STD2013 | 13.6223 | 0.83296 | 4.9758 | 25.7233 | 2.6389 | 9.8352 | 0.97209 | 11.4681 | 0.93887 | 2.1317 | 0.81923 | 9.843 | 0.40475 | 16.4378 | 0 | 21.4513 | 122.0953 |  | STD2013 | 3.9913 | 0.24406 | 0.030447 | 0.57472 | 0.77319 | 2.8817 | 0.28482 | 3.3602 | 0.27509 | 0.6246 | 0.24003 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 24.1737 |  | STD2013 | 0 | 0 | 0.048719 | 0.23762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.39591 |  | STD2013 | 41.7854 | 2.555 | 5.6437 | 31.9885 | 8.0946 | 30.1685 | 2.9818 | 35.1775 | 2.8799 | 6.5389 | 2.5129 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 296.3475
STD2010 | 0.41794 | 0.024723 | 0.051802 | 0.37364 | 0.15295 | 0.30912 | 0.035546 | 0.34835 | 0.02223 | 0.069945 | 0.031067 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.0532 |  | STD2010 | 14.081 | 0.83296 | 4.9757 | 28.7195 | 5.1533 | 10.4148 | 1.1976 | 11.7366 | 0.74897 | 2.3566 | 1.0467 | 9.8645 | 0.40737 | 16.4378 | 0 | 21.5211 | 129.4944 |  | STD2010 | 4.1257 | 0.24406 | 0.030453 | 1.2869 | 1.5099 | 3.0516 | 0.35089 | 3.4388 | 0.21945 | 0.69048 | 0.30669 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 26.176 |  | STD2010 | 0 | 0 | 0.048717 | 0.24327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40157 |  | STD2010 | 43.1922 | 2.555 | 5.6436 | 40.0627 | 15.8074 | 31.9467 | 3.6735 | 36.001 | 2.2974 | 7.2286 | 3.2107 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 317.9276
STD2007 | 0.48738 | 0.030451 | 0.052276 | 0.59829 | 0.20717 | 0.47027 | 0.077453 | 0.5042 | 0 | 0.13213 | 0.031174 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.8362 |  | STD2007 | 16.4205 | 1.026 | 5.0054 | 52.7178 | 6.9798 | 15.8442 | 2.6095 | 16.9872 | 0 | 4.4516 | 1.0503 | 9.9723 | 0.68134 | 16.4378 | 0 | 22.1353 | 172.3191 |  | STD2007 | 4.8112 | 0.3006 | 0.033081 | 1.0587 | 2.0451 | 4.6424 | 0.76459 | 4.9773 | 0 | 1.3043 | 0.30774 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.4578 |  | STD2007 | 0 | 0 | 0.048925 | 0.49105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64955 |  | STD2007 | 50.3685 | 3.147 | 5.6938 | 64.7548 | 21.4099 | 48.6008 | 8.0045 | 52.1069 | 0 | 13.6549 | 3.2217 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 400.3269
STD2004 | 0.48738 | 0.030451 | 0.052268 | 0.55914 | 0.20787 | 0.47749 | 0.074972 | 0.51945 | 0 | 0.12772 | 0.03114 | 0.29599 | 0.020222 | 0.27223 | 0 | 0.657 | 3.8133 |  | STD2004 | 16.4205 | 1.026 | 5.0046 | 48.7892 | 7.0036 | 16.0876 | 2.526 | 17.5013 | 0 | 4.303 | 1.0492 | 9.9723 | 0.68131 | 16.4378 | 0 | 22.1353 | 168.9374 |  | STD2004 | 4.8112 | 0.3006 | 0.033092 | 1.0607 | 2.0521 | 4.7137 | 0.7401 | 5.1279 | 0 | 1.2608 | 0.3074 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.6203 |  | STD2004 | 0 | 0 | 0.048916 | 0.45169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61018 |  | STD2004 | 50.3685 | 3.147 | 5.693 | 60.4739 | 21.4831 | 49.3473 | 7.7481 | 53.6837 | 0 | 13.199 | 3.2182 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 397.7258
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -7.8788e-06 | -0.039155 | 0.00070826 | 0.0072232 | -0.0024802 | 0.015258 | 0 | -0.004412 | -3.4281e-05 | 0 | -8.1764e-07 | 0 | 0 | 0 | -0.022901 |  | 2004-2007 | 0 | 0 | -0.00086172 | -3.9287 | 0.023862 | 0.24336 | -0.083561 | 0.51406 | 0 | -0.14865 | -0.001155 | 0 | -2.7548e-05 | 0 | 0 | 0 | -3.3816 |  | 2004-2007 | 0 | 0 | 1.0993e-05 | 0.0019537 | 0.0069917 | 0.071305 | -0.024483 | 0.15062 | 0 | -0.043554 | -0.00033841 | 0 | -8.0714e-06 | 0 | 0 | 0 | 0.1625 |  | 2004-2007 | 0 | 0 | -8.9924e-06 | -0.039353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.039362 |  | 2004-2007 | 0 | 0 | -0.00086778 | -4.2809 | 0.073196 | 0.74649 | -0.25632 | 1.5768 | 0 | -0.45597 | -0.0035428 | 0 | -8.45e-05 | 0 | 0 | 0 | -2.6011
2007-2010 | 0.069439 | 0.0057283 | 0.00047412 | 0.22465 | 0.054211 | 0.16115 | 0.041907 | 0.15584 | -0.02223 | 0.062182 | 0.00010688 | 0.0032007 | 0.0081317 | 0 | 0 | 0.01823 | 0.78303 |  | 2007-2010 | 2.3395 | 0.193 | 0.029757 | 23.9983 | 1.8265 | 5.4294 | 1.4119 | 5.2506 | -0.74897 | 2.095 | 0.003601 | 0.10784 | 0.27397 | 0 | 0 | 0.61421 | 42.8246 |  | 2007-2010 | 0.68548 | 0.056548 | 0.0026285 | -0.22824 | 0.53515 | 1.5908 | 0.41369 | 1.5384 | -0.21945 | 0.61384 | 0.0010551 | 0.031596 | 0.080273 | 0 | 0 | 0.17996 | 5.2818 |  | 2007-2010 | 0 | 0 | 0.00020786 | 0.24777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24798 |  | 2007-2010 | 7.1763 | 0.592 | 0.050236 | 24.6921 | 5.6025 | 16.6541 | 4.3309 | 16.1058 | -2.2974 | 6.4263 | 0.011046 | 0.33078 | 0.84038 | 0 | 0 | 1.884 | 82.3993
2010-2013 | 0.013613 | 0 | -1.0327e-06 | 0.077802 | 0.07463 | 0.017206 | 0.006693 | 0.0079689 | -0.0056363 | 0.0066734 | 0.0067519 | 0.00063735 | 7.7717e-05 | 0 | 0 | 0.0020717 | 0.20849 |  | 2010-2013 | 0.45864 | 0 | -0.00014363 | 2.9962 | 2.5144 | 0.57969 | 0.2255 | 0.26849 | -0.1899 | 0.22484 | 0.22748 | 0.021473 | 0.0026184 | 0 | 0 | 0.069798 | 7.3991 |  | 2010-2013 | 0.13438 | 0 | 6.0086e-06 | 0.71222 | 0.73673 | 0.16985 | 0.066072 | 0.078667 | -0.055639 | 0.065877 | 0.066652 | 0.0062917 | 0.0007672 | 0 | 0 | 0.020451 | 2.0023 |  | 2010-2013 | 0 | 0 | -1.6414e-06 | 0.0056538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056522 |  | 2010-2013 | 1.4068 | 0 | -0.0001165 | 8.0742 | 7.7128 | 1.7782 | 0.6917 | 0.82356 | -0.58249 | 0.68967 | 0.69778 | 0.065867 | 0.0080318 | 0 | 0 | 0.2141 | 21.5801
2013-2016 | 0.0082368 | 0.0066693 | 0.0016459 | 0.0057603 | 0.00086805 | 0.0062349 | -0.00012605 | 0.00062327 | 0.0064829 | 0.0062831 | -2.3729e-06 | 0 | 0.0037328 | 0 | 0 | 0 | 0.046409 |  | 2013-2016 | 0.27751 | 0.2247 | 0.16459 | 0.541 | 0.029246 | 0.21006 | -0.0042467 | 0.020999 | 0.21842 | 0.21169 | -7.9948e-05 | 0 | 0.12576 | 0 | 0 | 0 | 2.0197 |  | 2013-2016 | 0.081311 | 0.065837 | -8.7976e-08 | 0.0052156 | 0.0085691 | 0.061549 | -0.0012443 | 0.0061527 | 0.063997 | 0.062024 | -2.3425e-05 | 0 | 0.036849 | 0 | 0 | 0 | 0.39024 |  | 2013-2016 | 0 | 0 | 0.0016459 | 0.005232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0068779 |  | 2013-2016 | 0.85124 | 0.68925 | 0.1799 | 0.62646 | 0.08971 | 0.64435 | -0.013027 | 0.064413 | 0.66999 | 0.64933 | -0.00024523 | 0 | 0.38577 | 0 | 0 | 0 | 4.8371
2004-2016 | 0.091289 | 0.012398 | 0.0021111 | 0.26906 | 0.13042 | 0.19181 | 0.045994 | 0.17969 | -0.021383 | 0.070727 | 0.0068221 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 1.015 |  | 2004-2016 | 3.0757 | 0.41769 | 0.19334 | 23.6068 | 4.394 | 6.4625 | 1.5496 | 6.0542 | -0.72045 | 2.3829 | 0.22985 | 0.12931 | 0.40232 | 0 | 0 | 0.684 | 48.8618 |  | 2004-2016 | 0.90117 | 0.12238 | 0.0026454 | 0.49115 | 1.2874 | 1.8935 | 0.45404 | 1.7739 | -0.21109 | 0.69819 | 0.067346 | 0.037888 | 0.11788 | 0 | 0 | 0.20041 | 7.8368 |  | 2004-2016 | 0 | 0 | 0.0018431 | 0.21931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22115 |  | 2004-2016 | 9.4344 | 1.2812 | 0.22915 | 29.1119 | 13.4782 | 19.8231 | 4.7533 | 18.5707 | -2.2099 | 7.3094 | 0.70504 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 106.2154
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.01507% | -7.003% | 0.3407% | 1.513% | -3.308% | 2.937% |  | -3.455% | -0.1101% | 0% | -0.004043% | 0% |  | 0% | -0.6006% |  | 2004-2007 | 0% | 0% | -0.01722% | -8.052% | 0.3407% | 1.513% | -3.308% | 2.937% |  | -3.455% | -0.1101% | 0% | -0.004043% | 0% |  | 0% | -2.002% |  | 2004-2007 | 0% | 0% | 0.03322% | 0.1842% | 0.3407% | 1.513% | -3.308% | 2.937% |  | -3.455% | -0.1101% | 0% | -0.004043% | 0% |  | 0% | 0.5139% |  | 2004-2007 |  |  | -0.01838% | -8.712% | [9 empty] | 0% |  |  | -6.451% |  | 2004-2007 | 0% | 0% | -0.01524% | -7.079% | 0.3407% | 1.513% | -3.308% | 2.937% |  | -3.455% | -0.1101% | 0% | -0.004043% | 0% |  | 0% | -0.654%
2007-2010 | 14.25% | 18.81% | 0.907% | 37.55% | 26.17% | 34.27% | 54.11% | 30.91% |  | 47.06% | 0.3429% | 1.081% | 40.21% | 0% |  | 2.775% | 20.41% |  | 2007-2010 | 14.25% | 18.81% | 0.5945% | 45.52% | 26.17% | 34.27% | 54.11% | 30.91% |  | 47.06% | 0.3429% | 1.081% | 40.21% | 0% |  | 2.775% | 24.85% |  | 2007-2010 | 14.25% | 18.81% | 7.946% | -21.56% | 26.17% | 34.27% | 54.11% | 30.91% |  | 47.06% | 0.3429% | 1.081% | 40.21% | 0% |  | 2.775% | 16.79% |  | 2007-2010 |  |  | 0.4248% | 50.46% | [9 empty] | 0% |  |  | 38.18% |  | 2007-2010 | 14.25% | 18.81% | 0.8823% | 38.13% | 26.17% | 34.27% | 54.11% | 30.91% |  | 47.06% | 0.3429% | 1.081% | 40.21% | 0% |  | 2.775% | 20.58%
2010-2013 | 3.257% | 0% | -0.001994% | 20.82% | 48.79% | 5.566% | 18.83% | 2.288% | -25.35% | 9.541% | 21.73% | 0.2177% | 0.6428% | 0% |  | 0.3243% | 6.829% |  | 2010-2013 | 3.257% | 0% | -0.002887% | 10.43% | 48.79% | 5.566% | 18.83% | 2.288% | -25.35% | 9.541% | 21.73% | 0.2177% | 0.6428% | 0% |  | 0.3243% | 5.714% |  | 2010-2013 | 3.257% | 0% | 0.01973% | 55.34% | 48.79% | 5.566% | 18.83% | 2.288% | -25.35% | 9.541% | 21.73% | 0.2177% | 0.6428% | 0% |  | 0.3243% | 7.649% |  | 2010-2013 |  |  | -0.003369% | 2.324% | [9 empty] | 0% |  |  | 1.408% |  | 2010-2013 | 3.257% | 0% | -0.002064% | 20.15% | 48.79% | 5.566% | 18.83% | 2.288% | -25.35% | 9.541% | 21.73% | 0.2177% | 0.6428% | 0% |  | 0.3243% | 6.788%
2013-2016 | 2.037% | 26.98% | 3.177% | 1.947% | 1.108% | 2.136% | -0.4369% | 0.1831% | 23.26% | 9.93% | -0.009759% | 0% | 31.07% | 0% |  | 0% | 1.631% |  | 2013-2016 | 2.037% | 26.98% | 3.308% | 2.103% | 1.108% | 2.136% | -0.4369% | 0.1831% | 23.26% | 9.93% | -0.009759% | 0% | 31.07% | 0% |  | 0% | 1.654% |  | 2013-2016 | 2.037% | 26.98% | -0.000289% | 0.9075% | 1.108% | 2.136% | -0.4369% | 0.1831% | 23.26% | 9.93% | -0.009759% | 0% | 31.07% | 0% |  | 0% | 1.614% |  | 2013-2016 |  |  | 3.378% | 2.202% | [9 empty] | 0% |  |  | 1.737% |  | 2013-2016 | 2.037% | 26.98% | 3.188% | 1.958% | 1.108% | 2.136% | -0.4369% | 0.1831% | 23.26% | 9.93% | -0.009759% | 0% | 31.07% | 0% |  | 0% | 1.632%
2004-2016 | 18.73% | 40.71% | 4.039% | 48.12% | 62.74% | 40.17% | 61.35% | 34.59% |  | 55.38% | 21.91% | 1.297% | 59.05% | 0% |  | 3.09% | 26.62% |  | 2004-2016 | 18.73% | 40.71% | 3.863% | 48.39% | 62.74% | 40.17% | 61.35% | 34.59% |  | 55.38% | 21.91% | 1.297% | 59.05% | 0% |  | 3.09% | 28.92% |  | 2004-2016 | 18.73% | 40.71% | 7.994% | 46.31% | 62.74% | 40.17% | 61.35% | 34.59% |  | 55.38% | 21.91% | 1.297% | 59.05% | 0% |  | 3.09% | 24.78% |  | 2004-2016 |  |  | 3.768% | 48.55% | [9 empty] | 0% |  |  | 36.24% |  | 2004-2016 | 18.73% | 40.71% | 4.025% | 48.14% | 62.74% | 40.17% | 61.35% | 34.59% |  | 55.38% | 21.91% | 1.297% | 59.05% | 0% |  | 3.09% | 26.71%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.39622 | 0.018089 | 0.042974 | 0.15223 | 0 | 0.53715 | 0.085175 | 0.3284 | 0.023679 | 0.089855 | 0.026156 | 0.29215 | 0.0082785 | 0.27223 | 0 | 0.63669 | 2.9093 | 1.766% | CZ 1A | 13.3493 | 0.60946 | 4.0929 | 15.2227 | 0 | 18.0974 | 2.8697 | 11.0645 | 0.79777 | 3.0274 | 0.88123 | 9.843 | 0.27892 | 16.4378 | 0 | 21.4513 | 118.0232 | 1.766% | CZ 1A | 3.9113 | 0.17857 | 0.030446 | 0 | 0 | 5.3025 | 0.84082 | 3.2419 | 0.23375 | 0.88702 | 0.2582 | 2.884 | 0.081723 | 1.6057 | 0 | 6.2852 | 25.7412 | 1.766% | CZ 1A | 0 | 0 | 0.039889 | 0.15223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30169 | 1.766% | CZ 1A | 40.9479 | 1.8695 | 4.6787 | 16.6384 | 0 | 55.5122 | 8.8025 | 33.9395 | 2.4471 | 9.2862 | 2.7031 | 30.1926 | 0.85555 | 28.7866 | 0 | 65.8001 | 302.4598 | 1.766%
CZ 1B | 0.39606 | 0.018068 | 0.043392 | 0.16446 | 0.00061521 | 0.55964 | 0.058207 | 0.33693 | 0.023679 | 0.082645 | 0.02587 | 0.29215 | 0.0082762 | 0.27223 | 0 | 0.63669 | 2.9189 | 0% | CZ 1B | 13.3439 | 0.60875 | 4.1346 | 16.4164 | 0.020727 | 18.8553 | 1.9611 | 11.3517 | 0.79777 | 2.7845 | 0.87161 | 9.843 | 0.27884 | 16.4378 | 0 | 21.4513 | 119.1572 | 0% | CZ 1B | 3.9098 | 0.17836 | 0.030458 | 0.0043708 | 0.0060731 | 5.5246 | 0.5746 | 3.326 | 0.23375 | 0.81585 | 0.25538 | 2.884 | 0.0817 | 1.6057 | 0 | 6.2852 | 25.7158 | 0% | CZ 1B | 0 | 0 | 0.040307 | 0.16401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.3139 | 0% | CZ 1B | 40.9313 | 1.8673 | 4.7244 | 17.9725 | 0.06358 | 57.837 | 6.0155 | 34.8203 | 2.4471 | 8.5411 | 2.6736 | 30.1926 | 0.85531 | 28.7866 | 0 | 65.8001 | 303.5282 | 0%
CZ 2A | 0.39616 | 0.018053 | 0.044589 | 0.19783 | 0.012646 | 0.49606 | 0.06913 | 0.32367 | 0.022384 | 0.08253 | 0.025626 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.898 | 14.8% | CZ 2A | 13.3474 | 0.60824 | 4.2544 | 19.1473 | 0.42605 | 16.713 | 2.3291 | 10.9049 | 0.75416 | 2.7806 | 0.86337 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 120.1395 | 14.8% | CZ 2A | 3.9108 | 0.17821 | 0.030446 | 0.094582 | 0.12483 | 4.8969 | 0.68243 | 3.1951 | 0.22097 | 0.81471 | 0.25297 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 25.2586 | 14.8% | CZ 2A | 0 | 0 | 0.041505 | 0.18825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.33933 | 14.8% | CZ 2A | 40.942 | 1.8657 | 4.8552 | 21.5654 | 1.3069 | 51.2656 | 7.1444 | 33.4498 | 2.3133 | 8.5292 | 2.6483 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 301.5209 | 14.8%
CZ 2B | 0.39639 | 0.018065 | 0.044874 | 0.19744 | 0.10459 | 0.31911 | 0.020309 | 0.34343 | 0.021199 | 0.060042 | 0.025145 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 2.76 | 2.777% | CZ 2B | 13.3551 | 0.60863 | 4.2829 | 17.97 | 3.5238 | 10.7513 | 0.68424 | 11.5706 | 0.71423 | 2.0229 | 0.84719 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 114.342 | 2.777% | CZ 2B | 3.9131 | 0.17833 | 0.030446 | 0.26416 | 1.0325 | 3.1501 | 0.20048 | 3.3902 | 0.20927 | 0.59272 | 0.24823 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 24.0661 | 2.777% | CZ 2B | 0 | 0 | 0.04179 | 0.17068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32205 | 2.777% | CZ 2B | 40.9657 | 1.8669 | 4.8864 | 21.4212 | 10.809 | 32.9788 | 2.0988 | 35.492 | 2.1908 | 6.2052 | 2.5987 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 287.1485 | 2.777%
CZ 3A | 0.39649 | 0.018082 | 0.047975 | 0.27036 | 0.05681 | 0.32751 | 0.036866 | 0.33079 | 0.021546 | 0.065573 | 0.024642 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 2.806 | 14.21% | CZ 3A | 13.3585 | 0.60922 | 4.593 | 24.2683 | 1.914 | 11.0345 | 1.2421 | 11.1448 | 0.72593 | 2.2093 | 0.83023 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 119.9408 | 14.21% | CZ 3A | 3.914 | 0.1785 | 0.030446 | 0.41204 | 0.56081 | 3.2331 | 0.36393 | 3.2654 | 0.2127 | 0.64732 | 0.24326 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 23.9182 | 14.21% | CZ 3A | 0 | 0 | 0.044891 | 0.22862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38309 | 14.21% | CZ 3A | 40.976 | 1.8687 | 5.2253 | 29.3018 | 5.8711 | 33.8473 | 3.81 | 34.1857 | 2.2267 | 6.7768 | 2.5467 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 292.2711 | 14.21%
CZ 3B | 0.39642 | 0.018071 | 0.047036 | 0.1975 | 0.10277 | 0.25292 | 0.018506 | 0.3578 | 0.020901 | 0.048215 | 0.024647 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.6941 | 7.904% | CZ 3B | 13.356 | 0.60883 | 4.4991 | 16.8773 | 3.4624 | 8.5212 | 0.62351 | 12.0549 | 0.70418 | 1.6244 | 0.83039 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 111.1733 | 7.904% | CZ 3B | 3.9133 | 0.17839 | 0.030446 | 0.42764 | 1.0145 | 2.4967 | 0.18269 | 3.5321 | 0.20633 | 0.47596 | 0.2433 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 23.558 | 7.904% | CZ 3B | 0 | 0 | 0.043951 | 0.15418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30771 | 7.904% | CZ 3B | 40.9685 | 1.8675 | 5.1226 | 21.3286 | 10.6207 | 26.1381 | 1.9126 | 36.9773 | 2.16 | 4.9828 | 2.5472 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 280.2609 | 7.904%
CZ 3C | 0.39629 | 0.018069 | 0.048169 | 0.21838 | 0.030695 | 0.23339 | 0.030485 | 0.32807 | 0 | 0.044117 | 0.024613 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 2.5816 | 1.133% | CZ 3C | 13.3517 | 0.60879 | 4.6124 | 21.0473 | 1.0342 | 7.8631 | 1.0271 | 11.0532 | 0 | 1.4864 | 0.82925 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 110.9244 | 1.133% | CZ 3C | 3.912 | 0.17838 | 0.030446 | 0.11764 | 0.30301 | 2.3039 | 0.30094 | 3.2386 | 0 | 0.43551 | 0.24297 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 21.9201 | 1.133% | CZ 3C | 0 | 0 | 0.045085 | 0.20646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36112 | 1.133% | CZ 3C | 40.9552 | 1.8674 | 5.2465 | 23.7975 | 3.1722 | 24.1195 | 3.1506 | 33.9048 | 0 | 4.5593 | 2.5437 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 268.9516 | 1.133%
CZ 4A | 0.3959 | 0.01805 | 0.05117 | 0.32965 | 0.091249 | 0.26519 | 0.025256 | 0.3356 | 0.02193 | 0.056366 | 0.024028 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.8237 | 19.08% | CZ 4A | 13.3386 | 0.60812 | 4.9125 | 27.9214 | 3.0743 | 8.9346 | 0.85092 | 11.3068 | 0.73885 | 1.8991 | 0.80955 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 122.4058 | 19.08% | CZ 4A | 3.9082 | 0.17818 | 0.030446 | 0.75087 | 0.90078 | 2.6178 | 0.24932 | 3.3129 | 0.21648 | 0.55643 | 0.2372 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 23.8153 | 19.08% | CZ 4A | 0 | 0 | 0.048086 | 0.25359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41125 | 19.08% | CZ 4A | 40.915 | 1.8654 | 5.5745 | 35.578 | 9.4302 | 27.4062 | 2.6101 | 34.6827 | 2.2663 | 5.8252 | 2.4832 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 294.272 | 19.08%
CZ 4B | 0.39581 | 0.018057 | 0.050211 | 0.19848 | 0.12631 | 0.1961 | 0.016378 | 0.376 | 0.020987 | 0.040136 | 0.024012 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 2.6718 | 0.906% | CZ 4B | 13.3354 | 0.60836 | 4.8166 | 17.5701 | 4.2558 | 6.6068 | 0.55179 | 12.6679 | 0.70709 | 1.3523 | 0.809 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 111.292 | 0.906% | CZ 4B | 3.9073 | 0.17825 | 0.030446 | 0.3392 | 1.2469 | 1.9358 | 0.16167 | 3.7117 | 0.20718 | 0.39621 | 0.23704 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 23.2083 | 0.906% | CZ 4B | 0 | 0 | 0.047127 | 0.16412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32083 | 0.906% | CZ 4B | 40.9052 | 1.8661 | 5.4697 | 21.4898 | 13.0542 | 20.2658 | 1.6926 | 38.8578 | 2.1689 | 4.148 | 2.4815 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 278.0345 | 0.906%
CZ 4C | 0.39619 | 0.018034 | 0.052055 | 0.28411 | 0.029413 | 0.15302 | 0.009206 | 0.33771 | 0.020721 | 0.035189 | 0.023739 | 0.29215 | 0.008282 | 0.27223 | 0 | 0.63669 | 2.5687 | 2.972% | CZ 4C | 13.3484 | 0.60761 | 5.001 | 25.746 | 0.99099 | 5.1555 | 0.31017 | 11.378 | 0.69814 | 1.1856 | 0.79981 | 9.843 | 0.27903 | 16.4378 | 0 | 21.4513 | 113.2324 | 2.972% | CZ 4C | 3.9111 | 0.17803 | 0.030446 | 0.39672 | 0.29036 | 1.5106 | 0.090878 | 3.3338 | 0.20455 | 0.34738 | 0.23434 | 2.884 | 0.081757 | 1.6057 | 0 | 6.2852 | 21.3848 | 2.972% | CZ 4C | 0 | 0 | 0.048971 | 0.24392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40247 | 2.972% | CZ 4C | 40.9451 | 1.8638 | 5.6713 | 30.8137 | 3.0398 | 15.8141 | 0.95141 | 34.9012 | 2.1415 | 3.6367 | 2.4534 | 30.1926 | 0.85592 | 28.7866 | 0 | 65.8001 | 267.8671 | 2.972%
CZ 5A | 0.39592 | 0.018034 | 0.054053 | 0.37422 | 0.10009 | 0.20657 | 0.014018 | 0.34086 | 0.021345 | 0.047915 | 0.023626 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.806 | 23.15% | CZ 5A | 13.3392 | 0.60761 | 5.2008 | 31.1642 | 3.3722 | 6.9598 | 0.47229 | 11.484 | 0.71914 | 1.6143 | 0.796 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 123.7408 | 23.15% | CZ 5A | 3.9084 | 0.17803 | 0.030446 | 0.93166 | 0.98805 | 2.0392 | 0.13838 | 3.3648 | 0.21071 | 0.473 | 0.23323 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 23.3526 | 23.15% | CZ 5A | 0 | 0 | 0.050969 | 0.27985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.44039 | 23.15% | CZ 5A | 40.917 | 1.8638 | 5.8897 | 40.3406 | 10.3438 | 21.3487 | 1.4487 | 35.2263 | 2.2059 | 4.9519 | 2.4417 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 292.6131 | 23.15%
CZ 5B | 0.3958 | 0.018051 | 0.053197 | 0.23298 | 0.11485 | 0.16292 | 0.0073475 | 0.37777 | 0.021234 | 0.035825 | 0.023603 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.6529 | 6.131% | CZ 5B | 13.335 | 0.60816 | 5.1152 | 20.8114 | 3.8695 | 5.489 | 0.24755 | 12.7278 | 0.71541 | 1.207 | 0.79522 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 112.9323 | 6.131% | CZ 5B | 3.9072 | 0.17819 | 0.030446 | 0.37024 | 1.1338 | 1.6083 | 0.072532 | 3.7293 | 0.20961 | 0.35366 | 0.233 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 22.6828 | 6.131% | CZ 5B | 0 | 0 | 0.050112 | 0.19548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.35517 | 6.131% | CZ 5B | 40.9041 | 1.8655 | 5.796 | 25.2418 | 11.8694 | 16.8369 | 0.75934 | 39.0416 | 2.1945 | 3.7024 | 2.4393 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 276.2858 | 6.131%
CZ 5C | 0.39615 | 0.01803 | 0.053787 | 0.29767 | 0.027526 | 0.12806 | 0.0043379 | 0.34009 | 0.021046 | 0.030554 | 0.023443 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 2.55 | 0.1013% | CZ 5C | 13.347 | 0.60745 | 5.1742 | 26.3976 | 0.92739 | 4.3144 | 0.14615 | 11.4582 | 0.70909 | 1.0294 | 0.78984 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 112.9118 | 0.1013% | CZ 5C | 3.9107 | 0.17798 | 0.030446 | 0.50161 | 0.27173 | 1.2641 | 0.042822 | 3.3573 | 0.20776 | 0.30162 | 0.23142 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 21.1541 | 0.1013% | CZ 5C | 0 | 0 | 0.050703 | 0.24686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40714 | 0.1013% | CZ 5C | 40.9408 | 1.8633 | 5.8606 | 32.2327 | 2.8447 | 13.2341 | 0.44831 | 35.1471 | 2.1751 | 3.1577 | 2.4228 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 265.962 | 0.1013%
CZ 6A | 0.39576 | 0.018048 | 0.056352 | 0.43416 | 0.11994 | 0.20998 | 0.015997 | 0.34492 | 0.021645 | 0.051192 | 0.023514 | 0.29215 | 0.0082785 | 0.27223 | 0 | 0.63669 | 2.9009 | 3.602% | CZ 6A | 13.334 | 0.60808 | 5.4307 | 35.6341 | 4.0409 | 7.0746 | 0.53895 | 11.621 | 0.72927 | 1.7247 | 0.79223 | 9.843 | 0.27892 | 16.4378 | 0 | 21.4513 | 129.5394 | 3.602% | CZ 6A | 3.9069 | 0.17817 | 0.030458 | 1.1585 | 1.184 | 2.0728 | 0.15791 | 3.405 | 0.21368 | 0.50535 | 0.23212 | 2.884 | 0.081723 | 1.6057 | 0 | 6.2852 | 23.9015 | 3.602% | CZ 6A | 0 | 0 | 0.053267 | 0.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47964 | 3.602% | CZ 6A | 40.9008 | 1.8652 | 6.141 | 46.7547 | 12.395 | 21.7006 | 1.6532 | 35.6466 | 2.237 | 5.2905 | 2.4301 | 30.1926 | 0.85555 | 28.7866 | 0 | 65.8001 | 302.6495 | 3.602%
CZ 6B | 0.39576 | 0.018033 | 0.055757 | 0.30677 | 0.12592 | 0.14165 | 0.005707 | 0.36453 | 0.021408 | 0.033821 | 0.023299 | 0.29215 | 0.0082808 | 0.27223 | 0 | 0.63669 | 2.702 | 0.6285% | CZ 6B | 13.3338 | 0.60757 | 5.3712 | 27.1137 | 4.2423 | 4.7725 | 0.19228 | 12.2816 | 0.72126 | 1.1395 | 0.78497 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 118.5717 | 0.6285% | CZ 6B | 3.9068 | 0.17802 | 0.030458 | 0.53051 | 1.243 | 1.3983 | 0.056337 | 3.5985 | 0.21133 | 0.33387 | 0.23 | 2.884 | 0.081746 | 1.6057 | 0 | 6.2852 | 22.5738 | 0.6285% | CZ 6B | 0 | 0 | 0.052672 | 0.25303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41528 | 0.6285% | CZ 6B | 40.9002 | 1.8637 | 6.0759 | 33.2103 | 13.013 | 14.6392 | 0.5898 | 37.6728 | 2.2124 | 3.4953 | 2.4078 | 30.1926 | 0.8558 | 28.7866 | 0 | 65.8001 | 281.7155 | 0.6285%
CZ 7 | 0.3956 | 0.018043 | 0.059093 | 0.4956 | 0.15892 | 0.17367 | 0.0098748 | 0.34735 | 0.021575 | 0.042546 | 0.023277 | 0.29215 | 0.0082785 | 0.27223 | 0 | 0.63669 | 2.9549 | 0.8031% | CZ 7 | 13.3284 | 0.60789 | 5.7047 | 39.77 | 5.3544 | 5.8514 | 0.3327 | 11.7027 | 0.72691 | 1.4334 | 0.78423 | 9.843 | 0.27892 | 16.4378 | 0 | 21.4513 | 133.6078 | 0.8031% | CZ 7 | 3.9052 | 0.17811 | 0.030458 | 1.4576 | 1.5688 | 1.7145 | 0.097481 | 3.4289 | 0.21299 | 0.42 | 0.22978 | 2.884 | 0.081723 | 1.6057 | 0 | 6.2852 | 24.1004 | 0.8031% | CZ 7 | 0 | 0 | 0.056008 | 0.34795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51354 | 0.8031% | CZ 7 | 40.8837 | 1.8646 | 6.4405 | 53.2905 | 16.4242 | 17.9486 | 1.0205 | 35.8972 | 2.2297 | 4.397 | 2.4055 | 30.1926 | 0.85555 | 28.7866 | 0 | 65.8001 | 308.437 | 0.8031%
CZ 8 | 0.3965 | 0.017917 | 0.0628 | 0.5933 | 0.21162 | 0.10622 | 0.0030924 | 0.34504 | 0.021841 | 0.028984 | 0.022893 | 0.29215 | 0.0082797 | 0.27223 | 0 | 0.63669 | 3.0196 | 0.03822% | CZ 8 | 13.3586 | 0.60365 | 6.0755 | 46.8552 | 7.1298 | 3.5787 | 0.10419 | 11.625 | 0.73586 | 0.9765 | 0.77131 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 139.8254 | 0.03822% | CZ 8 | 3.9141 | 0.17687 | 0.030446 | 1.8572 | 2.089 | 1.0486 | 0.030527 | 3.4061 | 0.21561 | 0.28612 | 0.22599 | 2.884 | 0.081734 | 1.6057 | 0 | 6.2852 | 24.1372 | 0.03822% | CZ 8 | 0 | 0 | 0.059716 | 0.40517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.57446 | 0.03822% | CZ 8 | 40.9764 | 1.8516 | 6.8457 | 63.7276 | 21.8701 | 10.9775 | 0.31958 | 35.6588 | 2.2572 | 2.9953 | 2.3659 | 30.1926 | 0.85568 | 28.7866 | 0 | 65.8001 | 315.4806 | 0.03822%
US Weighted | 0.39609 | 0.018054 | 0.050157 | 0.29008 | 0.077457 | 0.28568 | 0.028979 | 0.33976 | 0.021383 | 0.056989 | 0.024318 | 0.29215 | 0.0082805 | 0.27223 | 0 | 0.63669 | 2.7983 | 100% | US Weighted | 13.3448 | 0.60826 | 4.8112 | 25.1823 | 2.6096 | 9.6251 | 0.97634 | 11.4471 | 0.72045 | 1.9201 | 0.81931 | 9.843 | 0.27898 | 16.4378 | 0 | 21.4513 | 120.0757 | 100% | US Weighted | 3.91 | 0.17822 | 0.030447 | 0.56951 | 0.76463 | 2.8202 | 0.28607 | 3.354 | 0.21109 | 0.56258 | 0.24006 | 2.884 | 0.081742 | 1.6057 | 0 | 6.2852 | 23.7834 | 100% | US Weighted | 0 | 0 | 0.047073 | 0.23239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38904 | 100% | US Weighted | 40.9341 | 1.8658 | 5.4638 | 31.362 | 8.0049 | 29.5242 | 2.9948 | 35.1131 | 2.2099 | 5.8896 | 2.5132 | 30.1926 | 0.85576 | 28.7866 | 0 | 65.8001 | 291.5104 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.4046 | 0.024773 | 0.046545 | 0.15038 | 0 | 0.55802 | 0.085997 | 0.32982 | 0.032126 | 0.096215 | 0.026153 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.9677 | 1.766% | CZ 1A | 13.6317 | 0.83463 | 4.45 | 15.0375 | 0 | 18.8006 | 2.8974 | 11.1121 | 1.0824 | 3.2416 | 0.88115 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 120.106 | 1.766% | CZ 1A | 3.9941 | 0.24455 | 0.030446 | 0 | 0 | 5.5086 | 0.84894 | 3.2558 | 0.31714 | 0.9498 | 0.25818 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 26.3011 | 1.766% | CZ 1A | 0 | 0 | 0.043461 | 0.15038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30341 | 1.766% | CZ 1A | 41.8142 | 2.5602 | 5.0691 | 16.436 | 0 | 57.6692 | 8.8875 | 34.0854 | 3.3201 | 9.9435 | 2.7029 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 308.5087 | 1.766%
CZ 1B | 0.40439 | 0.024742 | 0.046591 | 0.16423 | 0.00062569 | 0.58012 | 0.057348 | 0.33866 | 0.032126 | 0.086919 | 0.025869 | 0.29215 | 0.012011 | 0.27223 | 0 | 0.63669 | 2.9747 | 0% | CZ 1B | 13.6246 | 0.83361 | 4.4545 | 16.3935 | 0.021081 | 19.5451 | 1.9322 | 11.4099 | 1.0824 | 2.9285 | 0.87157 | 9.843 | 0.40466 | 16.4378 | 0 | 21.4513 | 121.2336 | 0% | CZ 1B | 3.992 | 0.24425 | 0.030458 | 0.0044053 | 0.0061766 | 5.7267 | 0.56612 | 3.3431 | 0.31714 | 0.85804 | 0.25537 | 2.884 | 0.11856 | 1.6057 | 0 | 6.2852 | 26.2373 | 0% | CZ 1B | 0 | 0 | 0.043506 | 0.16378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.31687 | 0% | CZ 1B | 41.7923 | 2.557 | 5.074 | 17.9478 | 0.064663 | 59.9529 | 5.9267 | 34.999 | 3.3201 | 8.9828 | 2.6735 | 30.1926 | 1.2412 | 28.7866 | 0 | 65.8001 | 309.3113 | 0%
CZ 2A | 0.40451 | 0.024723 | 0.047615 | 0.19694 | 0.012802 | 0.5157 | 0.068511 | 0.3249 | 0.029323 | 0.089938 | 0.025617 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.9537 | 14.8% | CZ 2A | 13.6286 | 0.83294 | 4.557 | 19.0563 | 0.43131 | 17.3749 | 2.3082 | 10.9465 | 0.98793 | 3.0302 | 0.86309 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 122.1538 | 14.8% | CZ 2A | 3.9932 | 0.24405 | 0.030446 | 0.094881 | 0.12637 | 5.0909 | 0.67631 | 3.2073 | 0.28946 | 0.88784 | 0.25289 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 25.7871 | 14.8% | CZ 2A | 0 | 0 | 0.044531 | 0.18733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.34143 | 14.8% | CZ 2A | 41.8047 | 2.555 | 5.186 | 21.468 | 1.323 | 53.2962 | 7.0803 | 33.5774 | 3.0304 | 9.2948 | 2.6475 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 307.2838 | 14.8%
CZ 2B | 0.40476 | 0.024738 | 0.047798 | 0.1974 | 0.10615 | 0.32273 | 0.020445 | 0.34501 | 0.026949 | 0.063006 | 0.025145 | 0.29215 | 0.012015 | 0.27223 | 0 | 0.63669 | 2.7972 | 2.777% | CZ 2B | 13.6371 | 0.83345 | 4.5753 | 17.9564 | 3.5764 | 10.8732 | 0.68883 | 11.624 | 0.90796 | 2.1228 | 0.84719 | 9.843 | 0.40481 | 16.4378 | 0 | 21.4513 | 115.7795 | 2.777% | CZ 2B | 3.9957 | 0.2442 | 0.030446 | 0.26557 | 1.0479 | 3.1859 | 0.20183 | 3.4058 | 0.26603 | 0.62198 | 0.24823 | 2.884 | 0.11861 | 1.6057 | 0 | 6.2852 | 24.4071 | 2.777% | CZ 2B | 0 | 0 | 0.044714 | 0.1705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32479 | 2.777% | CZ 2B | 41.8306 | 2.5565 | 5.206 | 21.4159 | 10.9704 | 33.3527 | 2.1129 | 35.6557 | 2.7851 | 6.5115 | 2.5987 | 30.1926 | 1.2417 | 28.7866 | 0 | 65.8001 | 291.017 | 2.777%
CZ 3A | 0.40469 | 0.024762 | 0.050126 | 0.2702 | 0.057415 | 0.33471 | 0.03671 | 0.33199 | 0.028065 | 0.07031 | 0.024641 | 0.29215 | 0.012014 | 0.27223 | 0 | 0.63669 | 2.8467 | 14.21% | CZ 3A | 13.6345 | 0.83428 | 4.808 | 24.2461 | 1.9344 | 11.277 | 1.2368 | 11.1851 | 0.94557 | 2.3689 | 0.8302 | 9.843 | 0.40477 | 16.4378 | 0 | 21.4513 | 121.4378 | 14.21% | CZ 3A | 3.9949 | 0.24444 | 0.030446 | 0.41298 | 0.56678 | 3.3042 | 0.36239 | 3.2772 | 0.27705 | 0.69407 | 0.24325 | 2.884 | 0.1186 | 1.6057 | 0 | 6.2852 | 24.3013 | 14.21% | CZ 3A | 0 | 0 | 0.047041 | 0.22837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38498 | 14.21% | CZ 3A | 41.8228 | 2.5591 | 5.4604 | 29.2839 | 5.9336 | 34.5914 | 3.7938 | 34.3095 | 2.9005 | 7.2663 | 2.5466 | 30.1926 | 1.2416 | 28.7866 | 0 | 65.8001 | 296.4887 | 14.21%
CZ 3B | 0.40461 | 0.024747 | 0.049436 | 0.21569 | 0.1043 | 0.27035 | 0.018636 | 0.35913 | 0.026548 | 0.056741 | 0.024639 | 0.29215 | 0.012012 | 0.27223 | 0 | 0.63669 | 2.7679 | 7.904% | CZ 3B | 13.6321 | 0.83377 | 4.7391 | 18.6894 | 3.5142 | 9.1086 | 0.62787 | 12.0997 | 0.89446 | 1.9117 | 0.83012 | 9.843 | 0.40469 | 16.4378 | 0 | 21.4513 | 115.0177 | 7.904% | CZ 3B | 3.9942 | 0.24429 | 0.030446 | 0.42872 | 1.0297 | 2.6688 | 0.18397 | 3.5452 | 0.26208 | 0.56013 | 0.24322 | 2.884 | 0.11858 | 1.6057 | 0 | 6.2852 | 24.0842 | 7.904% | CZ 3B | 0 | 0 | 0.046351 | 0.17226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32819 | 7.904% | CZ 3B | 41.8153 | 2.5575 | 5.3849 | 23.3165 | 10.7795 | 27.9399 | 1.9259 | 37.1148 | 2.7437 | 5.864 | 2.5463 | 30.1926 | 1.2414 | 28.7866 | 0 | 65.8001 | 288.009 | 7.904%
CZ 3C | 0.40449 | 0.024745 | 0.050108 | 0.21654 | 0.030983 | 0.23724 | 0.030687 | 0.32901 | 0 | 0.049642 | 0.024612 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.6111 | 1.133% | CZ 3C | 13.6279 | 0.83369 | 4.8062 | 20.8602 | 1.0439 | 7.9932 | 1.0339 | 11.0848 | 0 | 1.6725 | 0.82921 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 111.9223 | 1.133% | CZ 3C | 3.993 | 0.24427 | 0.030446 | 0.11817 | 0.30585 | 2.342 | 0.30293 | 3.2479 | 0 | 0.49005 | 0.24296 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 22.211 | 1.133% | CZ 3C | 0 | 0 | 0.047023 | 0.20457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36117 | 1.133% | CZ 3C | 41.8024 | 2.5573 | 5.4584 | 23.5966 | 3.202 | 24.5184 | 3.1714 | 34.0018 | 0 | 5.1303 | 2.5435 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 272.0028 | 1.133%
CZ 4A | 0.40409 | 0.024717 | 0.052425 | 0.3349 | 0.092082 | 0.26847 | 0.024988 | 0.33598 | 0.029248 | 0.062898 | 0.024027 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.8669 | 19.08% | CZ 4A | 13.6144 | 0.83275 | 5.038 | 28.4383 | 3.1024 | 9.0452 | 0.84189 | 11.3197 | 0.98542 | 2.1191 | 0.80951 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 124.2835 | 19.08% | CZ 4A | 3.989 | 0.24399 | 0.030446 | 0.75201 | 0.909 | 2.6503 | 0.24667 | 3.3167 | 0.28873 | 0.62091 | 0.23719 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 24.1784 | 19.08% | CZ 4A | 0 | 0 | 0.049341 | 0.25872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41763 | 19.08% | CZ 4A | 41.761 | 2.5544 | 5.7117 | 36.1506 | 9.5163 | 27.7455 | 2.5824 | 34.7222 | 3.0227 | 6.5003 | 2.4831 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 298.7709 | 19.08%
CZ 4B | 0.40399 | 0.024727 | 0.051701 | 0.20397 | 0.12828 | 0.19781 | 0.016424 | 0.37423 | 0.026676 | 0.045582 | 0.024007 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.7105 | 0.906% | CZ 4B | 13.6111 | 0.8331 | 4.9655 | 18.1098 | 4.3219 | 6.6644 | 0.55336 | 12.6083 | 0.89878 | 1.5358 | 0.80884 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 113.0477 | 0.906% | CZ 4B | 3.988 | 0.2441 | 0.030446 | 0.34049 | 1.2663 | 1.9527 | 0.16213 | 3.6942 | 0.26334 | 0.44998 | 0.23699 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 23.5222 | 0.906% | CZ 4B | 0 | 0 | 0.048616 | 0.16948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32767 | 0.906% | CZ 4B | 41.7508 | 2.5555 | 5.6325 | 22.0884 | 13.2571 | 20.4425 | 1.6974 | 38.6749 | 2.7569 | 4.7108 | 2.481 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 282.0686 | 0.906%
CZ 4C | 0.4044 | 0.024697 | 0.053115 | 0.28859 | 0.029718 | 0.15028 | 0.0093097 | 0.33825 | 0.027318 | 0.039645 | 0.02374 | 0.29215 | 0.012015 | 0.27223 | 0 | 0.63669 | 2.6022 | 2.972% | CZ 4C | 13.625 | 0.83208 | 5.107 | 26.1866 | 1.0012 | 5.0633 | 0.31366 | 11.3961 | 0.92041 | 1.3357 | 0.79985 | 9.843 | 0.40481 | 16.4378 | 0 | 21.4513 | 114.7178 | 2.972% | CZ 4C | 3.9921 | 0.2438 | 0.030446 | 0.3978 | 0.29336 | 1.4836 | 0.091902 | 3.3391 | 0.26968 | 0.39136 | 0.23436 | 2.884 | 0.11861 | 1.6057 | 0 | 6.2852 | 21.661 | 2.972% | CZ 4C | 0 | 0 | 0.050031 | 0.24829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.4079 | 2.972% | CZ 4C | 41.7935 | 2.5523 | 5.7872 | 31.3026 | 3.0712 | 15.5314 | 0.96212 | 34.9566 | 2.8233 | 4.0972 | 2.4535 | 30.1926 | 1.2417 | 28.7866 | 0 | 65.8001 | 271.3517 | 2.972%
CZ 5A | 0.40413 | 0.024697 | 0.05481 | 0.38061 | 0.10071 | 0.20565 | 0.013879 | 0.34129 | 0.027434 | 0.054007 | 0.023626 | 0.29215 | 0.012014 | 0.27223 | 0 | 0.63669 | 2.8439 | 23.15% | CZ 5A | 13.6158 | 0.83208 | 5.2765 | 31.7927 | 3.3932 | 6.9288 | 0.46762 | 11.4986 | 0.92429 | 1.8196 | 0.796 | 9.843 | 0.40477 | 16.4378 | 0 | 21.4513 | 125.482 | 23.15% | CZ 5A | 3.9894 | 0.2438 | 0.030446 | 0.93315 | 0.99421 | 2.0301 | 0.13701 | 3.3691 | 0.27082 | 0.53314 | 0.23323 | 2.884 | 0.1186 | 1.6057 | 0 | 6.2852 | 23.658 | 23.15% | CZ 5A | 0 | 0 | 0.051725 | 0.28608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.44738 | 23.15% | CZ 5A | 41.7654 | 2.5523 | 5.9723 | 41.0376 | 10.4084 | 21.2535 | 1.4344 | 35.2709 | 2.8352 | 5.5814 | 2.4417 | 30.1926 | 1.2416 | 28.7866 | 0 | 65.8001 | 296.574 | 23.15%
CZ 5B | 0.40401 | 0.024718 | 0.054077 | 0.24136 | 0.11629 | 0.16566 | 0.008141 | 0.37666 | 0.027466 | 0.041824 | 0.023602 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.6969 | 6.131% | CZ 5B | 13.6117 | 0.83279 | 5.2032 | 21.644 | 3.9181 | 5.5812 | 0.27428 | 12.6905 | 0.92539 | 1.4091 | 0.79518 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 115.0223 | 6.131% | CZ 5B | 3.9882 | 0.24401 | 0.030446 | 0.37098 | 1.148 | 1.6353 | 0.080365 | 3.7183 | 0.27114 | 0.41287 | 0.23299 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 23.0261 | 6.131% | CZ 5B | 0 | 0 | 0.050993 | 0.20378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36435 | 6.131% | CZ 5B | 41.7529 | 2.5545 | 5.8922 | 26.1568 | 12.0185 | 17.1199 | 0.84135 | 38.927 | 2.8386 | 4.3223 | 2.4391 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 280.8839 | 6.131%
CZ 5C | 0.40436 | 0.02469 | 0.054423 | 0.3027 | 0.027782 | 0.12344 | 0.004374 | 0.34034 | 0.028704 | 0.034924 | 0.023444 | 0.29215 | 0.012016 | 0.27223 | 0 | 0.63669 | 2.5823 | 0.1013% | CZ 5C | 13.6234 | 0.83184 | 5.2378 | 26.8902 | 0.93603 | 4.1588 | 0.14737 | 11.4665 | 0.96708 | 1.1766 | 0.78988 | 9.843 | 0.40485 | 16.4378 | 0 | 21.4513 | 114.3624 | 0.1013% | CZ 5C | 3.9917 | 0.24373 | 0.030446 | 0.50318 | 0.27426 | 1.2185 | 0.043179 | 3.3597 | 0.28336 | 0.34475 | 0.23143 | 2.884 | 0.11862 | 1.6057 | 0 | 6.2852 | 21.4178 | 0.1013% | CZ 5C | 0 | 0 | 0.051339 | 0.25173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41264 | 0.1013% | CZ 5C | 41.7888 | 2.5516 | 5.93 | 32.7817 | 2.8712 | 12.7567 | 0.45204 | 35.1725 | 2.9664 | 3.6092 | 2.4229 | 30.1926 | 1.2418 | 28.7866 | 0 | 65.8001 | 269.3243 | 0.1013%
CZ 6A | 0.40414 | 0.024716 | 0.056836 | 0.45106 | 0.1203 | 0.20797 | 0.015631 | 0.34462 | 0.028051 | 0.058441 | 0.023514 | 0.29215 | 0.012012 | 0.27223 | 0 | 0.63669 | 2.9484 | 3.602% | CZ 6A | 13.6162 | 0.83271 | 5.479 | 37.2923 | 4.053 | 7.0069 | 0.52663 | 11.6108 | 0.9451 | 1.969 | 0.79223 | 9.843 | 0.40469 | 16.4378 | 0 | 21.4513 | 132.2605 | 3.602% | CZ 6A | 3.9895 | 0.24398 | 0.030458 | 1.1632 | 1.1875 | 2.053 | 0.1543 | 3.402 | 0.27691 | 0.57691 | 0.23212 | 2.884 | 0.11858 | 1.6057 | 0 | 6.2852 | 24.2035 | 3.602% | CZ 6A | 0 | 0 | 0.05375 | 0.33322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49655 | 3.602% | CZ 6A | 41.7665 | 2.5543 | 6.1938 | 48.599 | 12.4323 | 21.4932 | 1.6154 | 35.615 | 2.899 | 6.0397 | 2.4301 | 30.1926 | 1.2414 | 28.7866 | 0 | 65.8001 | 307.6589 | 3.602%
CZ 6B | 0.40412 | 0.024696 | 0.056271 | 0.39265 | 0.14994 | 0.14182 | 0.0061882 | 0.36314 | 0.028294 | 0.040668 | 0.023298 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.8442 | 0.6285% | CZ 6B | 13.6154 | 0.83204 | 5.4225 | 31.58 | 5.0516 | 4.7781 | 0.20849 | 12.2349 | 0.95326 | 1.3702 | 0.78493 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 124.9683 | 0.6285% | CZ 6B | 3.9893 | 0.24379 | 0.030458 | 1.144 | 1.4801 | 1.4 | 0.061088 | 3.5848 | 0.27931 | 0.40146 | 0.22999 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 23.7379 | 0.6285% | CZ 6B | 0 | 0 | 0.053186 | 0.27675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.43952 | 0.6285% | CZ 6B | 41.7642 | 2.5522 | 6.1321 | 42.2263 | 15.4954 | 14.6565 | 0.63953 | 37.5295 | 2.9241 | 4.2029 | 2.4077 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 296.5512 | 0.6285%
CZ 7 | 0.40389 | 0.024707 | 0.059303 | 0.51783 | 0.15984 | 0.1702 | 0.0096406 | 0.34742 | 0.028332 | 0.05048 | 0.023278 | 0.29215 | 0.012011 | 0.27223 | 0 | 0.63669 | 3.008 | 0.8031% | CZ 7 | 13.6076 | 0.83243 | 5.7258 | 41.8412 | 5.3854 | 5.7342 | 0.32481 | 11.7052 | 0.95456 | 1.7007 | 0.78427 | 9.843 | 0.40466 | 16.4378 | 0 | 21.4513 | 136.7329 | 0.8031% | CZ 7 | 3.987 | 0.2439 | 0.030446 | 1.48 | 1.5779 | 1.6801 | 0.095169 | 3.4296 | 0.27969 | 0.49832 | 0.22979 | 2.884 | 0.11856 | 1.6057 | 0 | 6.2852 | 24.4255 | 0.8031% | CZ 7 | 0 | 0 | 0.056219 | 0.3679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.53369 | 0.8031% | CZ 7 | 41.7401 | 2.5534 | 6.4635 | 55.7059 | 16.5193 | 17.5891 | 0.99632 | 35.9048 | 2.928 | 5.2169 | 2.4057 | 30.1926 | 1.2412 | 28.7866 | 0 | 65.8001 | 314.0435 | 0.8031%
CZ 8 | 0.40465 | 0.024536 | 0.06286 | 0.65565 | 0.21296 | 0.11077 | 0.0034605 | 0.34502 | 0.02901 | 0.040036 | 0.022885 | 0.29215 | 0.012012 | 0.27223 | 0 | 0.63669 | 3.1249 | 0.03822% | CZ 8 | 13.6335 | 0.82666 | 6.0814 | 52.2429 | 7.1749 | 3.7319 | 0.11659 | 11.6245 | 0.97741 | 1.3489 | 0.77104 | 9.843 | 0.40469 | 16.4378 | 0 | 21.4513 | 146.6664 | 0.03822% | CZ 8 | 3.9946 | 0.24221 | 0.030458 | 1.9833 | 2.1023 | 1.0934 | 0.034161 | 3.406 | 0.28638 | 0.39522 | 0.22591 | 2.884 | 0.11858 | 1.6057 | 0 | 6.2852 | 24.6874 | 0.03822% | CZ 8 | 0 | 0 | 0.059775 | 0.45474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.62409 | 0.03822% | CZ 8 | 41.8196 | 2.5357 | 6.8522 | 70.4662 | 22.0085 | 11.4472 | 0.35764 | 35.6571 | 2.9981 | 4.1376 | 2.3651 | 30.1926 | 1.2414 | 28.7866 | 0 | 65.8001 | 326.6657 | 0.03822%
US Weighted | 0.40432 | 0.024723 | 0.051803 | 0.29584 | 0.078325 | 0.29192 | 0.028853 | 0.34038 | 0.027866 | 0.063272 | 0.024315 | 0.29215 | 0.012013 | 0.27223 | 0 | 0.63669 | 2.8447 | 100% | US Weighted | 13.6223 | 0.83296 | 4.9758 | 25.7233 | 2.6389 | 9.8352 | 0.97209 | 11.4681 | 0.93887 | 2.1317 | 0.81923 | 9.843 | 0.40475 | 16.4378 | 0 | 21.4513 | 122.0953 | 100% | US Weighted | 3.9913 | 0.24406 | 0.030447 | 0.57472 | 0.77319 | 2.8817 | 0.28482 | 3.3602 | 0.27509 | 0.6246 | 0.24003 | 2.884 | 0.11859 | 1.6057 | 0 | 6.2852 | 24.1737 | 100% | US Weighted | 0 | 0 | 0.048719 | 0.23762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.39591 | 100% | US Weighted | 41.7854 | 2.555 | 5.6437 | 31.9885 | 8.0946 | 30.1685 | 2.9818 | 35.1775 | 2.8799 | 6.5389 | 2.5129 | 30.1926 | 1.2415 | 28.7866 | 0 | 65.8001 | 296.3475 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.41804 | 0.024773 | 0.046545 | 0.14976 | 0 | 0.5852 | 0.094411 | 0.3451 | 0.032126 | 0.097524 | 0.033049 | 0.29279 | 0.01209 | 0.27223 | 0 | 0.63877 | 3.0424 | 1.766% | CZ 1A | 14.0846 | 0.83463 | 4.45 | 14.9756 | 0 | 19.7164 | 3.1809 | 11.6269 | 1.0824 | 3.2858 | 1.1135 | 9.8645 | 0.40732 | 16.4378 | 0 | 21.5211 | 122.5813 | 1.766% | CZ 1A | 4.1268 | 0.24455 | 0.030446 | 0 | 0 | 5.7769 | 0.932 | 3.4067 | 0.31714 | 0.96273 | 0.32625 | 2.8903 | 0.11935 | 1.6057 | 0 | 6.3057 | 27.0445 | 1.766% | CZ 1A | 0 | 0 | 0.04346 | 0.14976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30279 | 1.766% | CZ 1A | 43.2034 | 2.5602 | 5.069 | 16.3683 | 0 | 60.4785 | 9.7571 | 35.6645 | 3.3201 | 10.0788 | 3.4155 | 30.2585 | 1.2494 | 28.7866 | 0 | 66.0142 | 316.224 | 1.766%
CZ 1B | 0.41799 | 0.024742 | 0.046589 | 0.17363 | 0.0098993 | 0.65425 | 0.069643 | 0.36179 | 0 | 0.092639 | 0.032775 | 0.29279 | 0.01209 | 0.27223 | 0 | 0.63877 | 3.0998 | 0% | CZ 1B | 14.0829 | 0.83361 | 4.4544 | 16.3117 | 0.33352 | 22.0428 | 2.3464 | 12.1893 | 0 | 3.1212 | 1.1042 | 9.8645 | 0.40732 | 16.4378 | 0 | 21.5211 | 125.0508 | 0% | CZ 1B | 4.1263 | 0.24425 | 0.030446 | 0.15652 | 0.097722 | 6.4585 | 0.68749 | 3.5715 | 0 | 0.9145 | 0.32354 | 2.8903 | 0.11935 | 1.6057 | 0 | 6.3057 | 27.5318 | 0% | CZ 1B | 0 | 0 | 0.043505 | 0.15778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.31086 | 0% | CZ 1B | 43.1982 | 2.557 | 5.0738 | 18.8835 | 1.0231 | 67.6145 | 7.1974 | 37.3897 | 0 | 9.5739 | 3.3872 | 30.2585 | 1.2494 | 28.7866 | 0 | 66.0142 | 322.207 | 0%
CZ 2A | 0.41804 | 0.024723 | 0.047615 | 0.21794 | 0.024489 | 0.539 | 0.076536 | 0.33808 | 0.029323 | 0.094913 | 0.032462 | 0.29279 | 0.012092 | 0.27223 | 0 | 0.63877 | 3.059 | 14.8% | CZ 2A | 14.0844 | 0.83294 | 4.557 | 19.9113 | 0.82509 | 18.16 | 2.5786 | 11.3906 | 0.98793 | 3.1978 | 1.0937 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 125.8502 | 14.8% | CZ 2A | 4.1267 | 0.24405 | 0.030446 | 0.28027 | 0.24175 | 5.3209 | 0.75554 | 3.3375 | 0.28946 | 0.93695 | 0.32045 | 2.8903 | 0.11937 | 1.6057 | 0 | 6.3057 | 26.805 | 14.8% | CZ 2A | 0 | 0 | 0.044531 | 0.18955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.34366 | 14.8% | CZ 2A | 43.2028 | 2.555 | 5.186 | 23.6517 | 2.5309 | 55.7041 | 7.9098 | 34.9399 | 3.0304 | 9.809 | 3.3548 | 30.2585 | 1.2497 | 28.7866 | 0 | 66.0142 | 318.1832 | 14.8%
CZ 2B | 0.41814 | 0.024738 | 0.047798 | 0.28765 | 0.30637 | 0.36433 | 0.031662 | 0.36192 | 0 | 0.069091 | 0.031983 | 0.29279 | 0.012092 | 0.27223 | 0 | 0.63877 | 3.1595 | 2.777% | CZ 2B | 14.0877 | 0.83345 | 4.5753 | 21.0255 | 10.3221 | 12.2748 | 1.0668 | 12.1936 | 0 | 2.3278 | 1.0776 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 128.0153 | 2.777% | CZ 2B | 4.1277 | 0.2442 | 0.030446 | 1.1522 | 3.0244 | 3.5965 | 0.31256 | 3.5727 | 0 | 0.68204 | 0.31572 | 2.8903 | 0.11937 | 1.6057 | 0 | 6.3057 | 27.9795 | 2.777% | CZ 2B | 0 | 0 | 0.044714 | 0.17093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32522 | 2.777% | CZ 2B | 43.2129 | 2.5565 | 5.2059 | 30.7449 | 31.6623 | 37.652 | 3.2722 | 37.4027 | 0 | 7.1403 | 3.3053 | 30.2585 | 1.2497 | 28.7866 | 0 | 66.0142 | 328.464 | 2.777%
CZ 3A | 0.41796 | 0.024762 | 0.050125 | 0.32007 | 0.098118 | 0.35012 | 0.04385 | 0.33895 | 0.028027 | 0.076148 | 0.031422 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 2.9954 | 14.21% | CZ 3A | 14.0818 | 0.83428 | 4.808 | 26.0136 | 3.3057 | 11.7962 | 1.4774 | 11.4198 | 0.94427 | 2.5656 | 1.0587 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 126.5359 | 14.21% | CZ 3A | 4.126 | 0.24444 | 0.030446 | 0.89226 | 0.96858 | 3.4563 | 0.43287 | 3.346 | 0.27667 | 0.75171 | 0.31019 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 25.7564 | 14.21% | CZ 3A | 0 | 0 | 0.047041 | 0.22968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.3863 | 14.21% | CZ 3A | 43.1947 | 2.5591 | 5.4603 | 34.4454 | 10.1401 | 36.1838 | 4.5317 | 35.0292 | 2.8965 | 7.8697 | 3.2474 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 311.8666 | 14.21%
CZ 3B | 0.41791 | 0.024747 | 0.049434 | 0.30446 | 0.29784 | 0.29591 | 0.02716 | 0.36984 | 0 | 0.064275 | 0.03143 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.0989 | 7.904% | CZ 3B | 14.0801 | 0.83377 | 4.7389 | 21.0888 | 10.0347 | 9.9696 | 0.91507 | 12.4604 | 0 | 2.1655 | 1.0589 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 125.5766 | 7.904% | CZ 3B | 4.1255 | 0.24429 | 0.030446 | 1.3931 | 2.9402 | 2.9211 | 0.26811 | 3.6509 | 0 | 0.6345 | 0.31027 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 27.4394 | 7.904% | CZ 3B | 0 | 0 | 0.046349 | 0.16334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.31927 | 7.904% | CZ 3B | 43.1897 | 2.5575 | 5.3847 | 32.4377 | 30.7806 | 30.5809 | 2.8069 | 38.2212 | 0 | 6.6426 | 3.2482 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 322.1589 | 7.904%
CZ 3C | 0.41789 | 0.024745 | 0.050106 | 0.24272 | 0.055866 | 0.24807 | 0.04437 | 0.34294 | 0 | 0.056004 | 0.031365 | 0.29279 | 0.012092 | 0.27223 | 0 | 0.63877 | 2.73 | 1.133% | CZ 3C | 14.0795 | 0.83369 | 4.806 | 21.6821 | 1.8822 | 8.358 | 1.4949 | 11.5541 | 0 | 1.8869 | 1.0567 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 115.865 | 1.133% | CZ 3C | 4.1253 | 0.24427 | 0.030446 | 0.38557 | 0.55149 | 2.4489 | 0.438 | 3.3854 | 0 | 0.55285 | 0.30963 | 2.8903 | 0.11937 | 1.6057 | 0 | 6.3057 | 23.3928 | 1.133% | CZ 3C | 0 | 0 | 0.047021 | 0.20366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36026 | 1.133% | CZ 3C | 43.1878 | 2.5573 | 5.4582 | 26.2968 | 5.7736 | 25.6375 | 4.5854 | 35.4413 | 0 | 5.7878 | 3.2415 | 30.2585 | 1.2497 | 28.7866 | 0 | 66.0142 | 284.276 | 1.133%
CZ 4A | 0.41789 | 0.024717 | 0.052425 | 0.41219 | 0.14025 | 0.2827 | 0.030446 | 0.34201 | 0.029199 | 0.069952 | 0.030751 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.0484 | 19.08% | CZ 4A | 14.0794 | 0.83275 | 5.0379 | 31.5634 | 4.7251 | 9.5247 | 1.0258 | 11.5228 | 0.98377 | 2.3568 | 1.0361 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 130.9191 | 19.08% | CZ 4A | 4.1253 | 0.24399 | 0.030458 | 1.4375 | 1.3845 | 2.7907 | 0.30055 | 3.3762 | 0.28824 | 0.69054 | 0.30356 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 25.8926 | 19.08% | CZ 4A | 0 | 0 | 0.04934 | 0.26657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.42549 | 19.08% | CZ 4A | 43.1873 | 2.5544 | 5.7117 | 44.1859 | 14.4939 | 29.2163 | 3.1465 | 35.3453 | 3.0176 | 7.2293 | 3.178 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 317.5748 | 19.08%
CZ 4B | 0.41786 | 0.024727 | 0.0517 | 0.34638 | 0.37798 | 0.21611 | 0.02805 | 0.38706 | 0 | 0.054335 | 0.030741 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.1508 | 0.906% | CZ 4B | 14.0784 | 0.8331 | 4.9655 | 22.4312 | 12.7346 | 7.2812 | 0.94506 | 13.0406 | 0 | 1.8306 | 1.0357 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 127.4067 | 0.906% | CZ 4B | 4.125 | 0.2441 | 0.030446 | 1.8173 | 3.7312 | 2.1334 | 0.2769 | 3.8209 | 0 | 0.53638 | 0.30346 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 27.9401 | 0.906% | CZ 4B | 0 | 0 | 0.048616 | 0.16229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32048 | 0.906% | CZ 4B | 43.1844 | 2.5555 | 5.6324 | 36.7633 | 39.0624 | 22.3345 | 2.8989 | 40.0008 | 0 | 5.6154 | 3.1769 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 327.5333 | 0.906%
CZ 4C | 0.41795 | 0.024697 | 0.053114 | 0.407 | 0.096828 | 0.14965 | 0.01529 | 0.34524 | 0 | 0.04721 | 0.030429 | 0.29279 | 0.01209 | 0.27223 | 0 | 0.63877 | 2.8033 | 2.972% | CZ 4C | 14.0813 | 0.83208 | 5.1068 | 30.9426 | 3.2623 | 5.042 | 0.51516 | 11.6316 | 0 | 1.5906 | 1.0252 | 9.8645 | 0.40732 | 16.4378 | 0 | 21.5211 | 122.2603 | 2.972% | CZ 4C | 4.1258 | 0.2438 | 0.030458 | 1.4527 | 0.95585 | 1.4773 | 0.15094 | 3.4081 | 0 | 0.46604 | 0.30039 | 2.8903 | 0.11935 | 1.6057 | 0 | 6.3057 | 23.5324 | 2.972% | CZ 4C | 0 | 0 | 0.050028 | 0.25985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41945 | 2.972% | CZ 4C | 43.1933 | 2.5523 | 5.787 | 43.6093 | 10.0068 | 15.4659 | 1.5802 | 35.6791 | 0 | 4.879 | 3.1448 | 30.2585 | 1.2494 | 28.7866 | 0 | 66.0142 | 292.2064 | 2.972%
CZ 5A | 0.4179 | 0.024697 | 0.054808 | 0.4693 | 0.15978 | 0.21841 | 0.018425 | 0.34576 | 0.027416 | 0.061354 | 0.030323 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.044 | 23.15% | CZ 5A | 14.0798 | 0.83208 | 5.2763 | 35.3444 | 5.3831 | 7.3587 | 0.62076 | 11.6491 | 0.9237 | 2.0671 | 1.0216 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 132.7874 | 23.15% | CZ 5A | 4.1254 | 0.2438 | 0.030458 | 1.7248 | 1.5773 | 2.1561 | 0.18188 | 3.4132 | 0.27065 | 0.60567 | 0.29934 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 25.5496 | 23.15% | CZ 5A | 0 | 0 | 0.051723 | 0.29458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.45587 | 23.15% | CZ 5A | 43.1885 | 2.5523 | 5.9722 | 50.2546 | 16.5123 | 22.5721 | 1.9041 | 35.7327 | 2.8334 | 6.3407 | 3.1338 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 317.3055 | 23.15%
CZ 5B | 0.41787 | 0.024718 | 0.054073 | 0.42924 | 0.366 | 0.1774 | 0.017521 | 0.38616 | 0 | 0.049374 | 0.030311 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.1685 | 6.131% | CZ 5B | 14.0787 | 0.83279 | 5.2027 | 27.8879 | 12.3311 | 5.9768 | 0.5903 | 13.0103 | 0 | 1.6635 | 1.0212 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 130.8259 | 6.131% | CZ 5B | 4.125 | 0.24401 | 0.030458 | 2.2384 | 3.613 | 1.7512 | 0.17296 | 3.812 | 0 | 0.4874 | 0.29922 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 27.6948 | 6.131% | CZ 5B | 0 | 0 | 0.050988 | 0.20248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36305 | 6.131% | CZ 5B | 43.1851 | 2.5545 | 5.8918 | 45.5655 | 37.8246 | 18.3332 | 1.8107 | 39.908 | 0 | 5.1026 | 3.1325 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 329.6173 | 6.131%
CZ 5C | 0.41795 | 0.02469 | 0.054422 | 0.44195 | 0.099416 | 0.12046 | 0.0080793 | 0.34724 | 0 | 0.042015 | 0.030113 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 2.8022 | 0.1013% | CZ 5C | 14.0816 | 0.83184 | 5.2376 | 32.9439 | 3.3495 | 4.0586 | 0.2722 | 11.699 | 0 | 1.4155 | 1.0145 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 123.1351 | 0.1013% | CZ 5C | 4.1259 | 0.24373 | 0.030458 | 1.6751 | 0.9814 | 1.1892 | 0.079756 | 3.4278 | 0 | 0.41476 | 0.29726 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 23.3863 | 0.1013% | CZ 5C | 0 | 0 | 0.051336 | 0.27227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.43318 | 0.1013% | CZ 5C | 43.1941 | 2.5516 | 5.9299 | 47.2952 | 10.2742 | 12.4496 | 0.83496 | 35.8859 | 0 | 4.3421 | 3.112 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 292.1784 | 0.1013%
CZ 6A | 0.4179 | 0.024716 | 0.056833 | 0.57199 | 0.18565 | 0.23091 | 0.020473 | 0.34876 | 0.027954 | 0.066674 | 0.030208 | 0.29279 | 0.012089 | 0.27223 | 0 | 0.63877 | 3.1979 | 3.602% | CZ 6A | 14.0796 | 0.83271 | 5.4787 | 44.0871 | 6.255 | 7.7798 | 0.68977 | 11.7504 | 0.9418 | 2.2464 | 1.0178 | 9.8645 | 0.40729 | 16.4378 | 0 | 21.5211 | 143.3896 | 3.602% | CZ 6A | 4.1253 | 0.24398 | 0.030458 | 1.952 | 1.8327 | 2.2795 | 0.2021 | 3.4429 | 0.27595 | 0.65819 | 0.2982 | 2.8903 | 0.11933 | 1.6057 | 0 | 6.3057 | 26.2622 | 3.602% | CZ 6A | 0 | 0 | 0.053747 | 0.37425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.53757 | 3.602% | CZ 6A | 43.1881 | 2.5543 | 6.1935 | 61.3409 | 19.1866 | 23.8638 | 2.1158 | 36.0435 | 2.8889 | 6.8906 | 3.1219 | 30.2585 | 1.2493 | 28.7866 | 0 | 66.0142 | 333.6963 | 3.602%
CZ 6B | 0.41791 | 0.024696 | 0.056268 | 0.4573 | 0.23623 | 0.17356 | 0.0127 | 0.3687 | 0.028234 | 0.049721 | 0.029983 | 0.29279 | 0.01209 | 0.27223 | 0 | 0.63877 | 3.0712 | 0.6285% | CZ 6B | 14.08 | 0.83204 | 5.4222 | 35.3747 | 7.9591 | 5.8474 | 0.4279 | 12.4221 | 0.95126 | 1.6752 | 1.0102 | 9.8645 | 0.40732 | 16.4378 | 0 | 21.5211 | 134.2327 | 0.6285% | CZ 6B | 4.1254 | 0.24379 | 0.030458 | 1.5416 | 2.332 | 1.7133 | 0.12537 | 3.6397 | 0.27872 | 0.49083 | 0.29598 | 2.8903 | 0.11935 | 1.6057 | 0 | 6.3057 | 25.7382 | 0.6285% | CZ 6B | 0 | 0 | 0.053182 | 0.30113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.46389 | 0.6285% | CZ 6B | 43.1891 | 2.5522 | 6.1317 | 49.0528 | 24.414 | 17.9365 | 1.3125 | 38.1037 | 2.9179 | 5.1385 | 3.0987 | 30.2585 | 1.2494 | 28.7866 | 0 | 66.0142 | 320.1562 | 0.6285%
CZ 7 | 0.41791 | 0.024707 | 0.059303 | 0.66862 | 0.22849 | 0.19768 | 0.013298 | 0.34783 | 0.028346 | 0.059201 | 0.029942 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.2912 | 0.8031% | CZ 7 | 14.0802 | 0.83243 | 5.7257 | 51.0594 | 7.6981 | 6.6601 | 0.44803 | 11.7191 | 0.95503 | 1.9946 | 1.0088 | 9.8645 | 0.40736 | 16.4378 | 0 | 21.5211 | 150.4122 | 0.8031% | CZ 7 | 4.1255 | 0.2439 | 0.030458 | 2.3527 | 2.2556 | 1.9514 | 0.13127 | 3.4337 | 0.27982 | 0.58441 | 0.29558 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 26.6053 | 0.8031% | CZ 7 | 0 | 0 | 0.056217 | 0.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.59609 | 0.8031% | CZ 7 | 43.1899 | 2.5534 | 6.4634 | 71.6617 | 23.6134 | 20.4292 | 1.3743 | 35.9474 | 2.9295 | 6.1182 | 3.0944 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 343.6836 | 0.8031%
CZ 8 | 0.41818 | 0.024536 | 0.062859 | 0.85083 | 0.28688 | 0.13976 | 0.0080175 | 0.34385 | 0.029049 | 0.048414 | 0.029517 | 0.29279 | 0.012089 | 0.27223 | 0 | 0.63877 | 3.4578 | 0.03822% | CZ 8 | 14.0893 | 0.82666 | 6.0813 | 64.8598 | 9.6655 | 4.7088 | 0.27012 | 11.5847 | 0.9787 | 1.6311 | 0.99448 | 9.8645 | 0.40729 | 16.4378 | 0 | 21.5211 | 163.9212 | 0.03822% | CZ 8 | 4.1282 | 0.24221 | 0.030458 | 3.0108 | 2.832 | 1.3797 | 0.079146 | 3.3943 | 0.28676 | 0.47793 | 0.29138 | 2.8903 | 0.11933 | 1.6057 | 0 | 6.3057 | 27.0738 | 0.03822% | CZ 8 | 0 | 0 | 0.059774 | 0.54584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.71519 | 0.03822% | CZ 8 | 43.2177 | 2.5357 | 6.8521 | 91.1802 | 29.6481 | 14.4438 | 0.82858 | 35.5352 | 3.0021 | 5.0034 | 3.0505 | 30.2585 | 1.2493 | 28.7866 | 0 | 66.0142 | 361.6059 | 0.03822%
US Weighted | 0.41794 | 0.024723 | 0.051802 | 0.37364 | 0.15295 | 0.30912 | 0.035546 | 0.34835 | 0.02223 | 0.069945 | 0.031067 | 0.29279 | 0.012091 | 0.27223 | 0 | 0.63877 | 3.0532 | 100% | US Weighted | 14.081 | 0.83296 | 4.9757 | 28.7195 | 5.1533 | 10.4148 | 1.1976 | 11.7366 | 0.74897 | 2.3566 | 1.0467 | 9.8645 | 0.40737 | 16.4378 | 0 | 21.5211 | 129.4944 | 100% | US Weighted | 4.1257 | 0.24406 | 0.030453 | 1.2869 | 1.5099 | 3.0516 | 0.35089 | 3.4388 | 0.21945 | 0.69048 | 0.30669 | 2.8903 | 0.11936 | 1.6057 | 0 | 6.3057 | 26.176 | 100% | US Weighted | 0 | 0 | 0.048717 | 0.24327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40157 | 100% | US Weighted | 43.1922 | 2.555 | 5.6436 | 40.0627 | 15.8074 | 31.9467 | 3.6735 | 36.001 | 2.2974 | 7.2286 | 3.2107 | 30.2585 | 1.2496 | 28.7866 | 0 | 66.0142 | 317.9276 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.48738 | 0.030512 | 0.047124 | 0.3428 | 0 | 0.94991 | 0.19815 | 0.50661 | 0 | 0.17215 | 0.033266 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 4.0133 | 1.766% | CZ 1A | 16.4205 | 1.028 | 4.4903 | 34.2804 | 0 | 32.004 | 6.6761 | 17.0685 | 0 | 5.7999 | 1.1208 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 168.1152 | 1.766% | CZ 1A | 4.8112 | 0.30121 | 0.033069 | 0 | 0 | 9.3772 | 1.9561 | 5.0011 | 0 | 1.6994 | 0.32839 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 34.7204 | 1.766% | CZ 1A | 0 | 0 | 0.043774 | 0.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49615 | 1.766% | CZ 1A | 50.3685 | 3.1533 | 5.1307 | 37.4685 | 0 | 98.1696 | 20.4785 | 52.3562 | 0 | 17.7907 | 3.4379 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 417.718 | 1.766%
CZ 1B | 0.48738 | 0.030475 | 0.047147 | 0.33239 | 0.0095124 | 0.89145 | 0.14649 | 0.54243 | 0 | 0.16297 | 0.033121 | 0.29599 | 0.020225 | 0.27223 | 0 | 0.657 | 3.9288 | 0% | CZ 1B | 16.4205 | 1.0268 | 4.4927 | 32.0396 | 0.32049 | 30.0345 | 4.9355 | 18.2753 | 0 | 5.4906 | 1.1159 | 9.9723 | 0.68141 | 16.4378 | 0 | 22.1353 | 163.3786 | 0% | CZ 1B | 4.8112 | 0.30084 | 0.033057 | 0.17863 | 0.093903 | 8.8001 | 1.4461 | 5.3547 | 0 | 1.6087 | 0.32696 | 2.9219 | 0.19965 | 1.6057 | 0 | 6.4856 | 34.1671 | 0% | CZ 1B | 0 | 0 | 0.043799 | 0.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.46767 | 0% | CZ 1B | 50.3685 | 3.1495 | 5.1333 | 36.223 | 0.98308 | 92.1284 | 15.1392 | 56.0579 | 0 | 16.842 | 3.4229 | 30.5892 | 2.0902 | 28.7866 | 0 | 67.8982 | 408.8119 | 0%
CZ 2A | 0.48738 | 0.03045 | 0.048186 | 0.4225 | 0.038252 | 0.8028 | 0.16436 | 0.50131 | 0 | 0.17416 | 0.03262 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.9475 | 14.8% | CZ 2A | 16.4205 | 1.0259 | 4.5964 | 40.1379 | 1.2888 | 27.0478 | 5.5376 | 16.89 | 0 | 5.8677 | 1.099 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 169.1384 | 14.8% | CZ 2A | 4.8112 | 0.3006 | 0.033069 | 0.31451 | 0.37762 | 7.925 | 1.6225 | 4.9488 | 0 | 1.7192 | 0.32201 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 33.5874 | 14.8% | CZ 2A | 0 | 0 | 0.044836 | 0.39064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.54506 | 14.8% | CZ 2A | 50.3685 | 3.1469 | 5.2467 | 45.9901 | 3.9533 | 82.967 | 16.986 | 51.8087 | 0 | 17.9988 | 3.3712 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 411.2011 | 14.8%
CZ 2B | 0.48738 | 0.03047 | 0.048356 | 0.49331 | 0.32376 | 0.53298 | 0.073888 | 0.52338 | 0 | 0.12938 | 0.032096 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.9204 | 2.777% | CZ 2B | 16.4205 | 1.0266 | 4.6135 | 39.5123 | 10.9081 | 17.957 | 2.4894 | 17.6336 | 0 | 4.3591 | 1.0814 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 165.2281 | 2.777% | CZ 2B | 4.8112 | 0.30079 | 0.033069 | 1.4618 | 3.1961 | 5.2614 | 0.7294 | 5.1667 | 0 | 1.2772 | 0.31684 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 33.7673 | 2.777% | CZ 2B | 0 | 0 | 0.045006 | 0.34523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49982 | 2.777% | CZ 2B | 50.3685 | 3.149 | 5.2654 | 53.0372 | 33.4596 | 55.0816 | 7.6361 | 54.0897 | 0 | 13.3712 | 3.317 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 408.1392 | 2.777%
CZ 3A | 0.48738 | 0.030499 | 0.050635 | 0.53698 | 0.14661 | 0.57456 | 0.098297 | 0.50236 | 0 | 0.14681 | 0.031584 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.8511 | 14.21% | CZ 3A | 16.4205 | 1.0276 | 4.8413 | 48.2628 | 4.9394 | 19.3579 | 3.3118 | 16.9253 | 0 | 4.9464 | 1.0641 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 170.3238 | 14.21% | CZ 3A | 4.8112 | 0.30108 | 0.03308 | 0.80914 | 1.4472 | 5.6719 | 0.97035 | 4.9591 | 0 | 1.4493 | 0.31179 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.977 | 14.21% | CZ 3A | 0 | 0 | 0.047284 | 0.45501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61187 | 14.21% | CZ 3A | 50.3685 | 3.152 | 5.5144 | 58.2038 | 15.1512 | 59.3786 | 10.1586 | 51.9171 | 0 | 15.1726 | 3.2641 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 401.6449 | 14.21%
CZ 3B | 0.48738 | 0.030481 | 0.049977 | 0.44207 | 0.31746 | 0.40191 | 0.06053 | 0.52904 | 0 | 0.11472 | 0.031526 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.7105 | 7.904% | CZ 3B | 16.4205 | 1.0269 | 4.7755 | 35.3063 | 10.6958 | 13.5412 | 2.0394 | 17.8242 | 0 | 3.8653 | 1.0622 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 155.7839 | 7.904% | CZ 3B | 4.8112 | 0.3009 | 0.03308 | 1.3251 | 3.1339 | 3.9676 | 0.59754 | 5.2225 | 0 | 1.1325 | 0.31121 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 32.0483 | 7.904% | CZ 3B | 0 | 0 | 0.046626 | 0.30784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.46404 | 7.904% | CZ 3B | 50.3685 | 3.1501 | 5.4425 | 47.519 | 32.8086 | 41.5364 | 6.2556 | 54.6742 | 0 | 11.8564 | 3.2581 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 386.2333 | 7.904%
CZ 3C | 0.48738 | 0.030478 | 0.050613 | 0.44887 | 0.062044 | 0.36881 | 0.059283 | 0.49879 | 0 | 0.10847 | 0.031418 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.3916 | 1.133% | CZ 3C | 16.4205 | 1.0269 | 4.8391 | 42.1798 | 2.0904 | 12.4259 | 1.9973 | 16.8049 | 0 | 3.6545 | 1.0585 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 151.7246 | 1.133% | CZ 3C | 4.8112 | 0.30087 | 0.03308 | 0.403 | 0.61248 | 3.6408 | 0.58522 | 4.9238 | 0 | 1.0708 | 0.31014 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 27.9043 | 1.133% | CZ 3C | 0 | 0 | 0.047262 | 0.40804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.56488 | 1.133% | CZ 3C | 50.3685 | 3.1498 | 5.512 | 48.8182 | 6.412 | 38.1155 | 6.1266 | 51.5478 | 0 | 11.21 | 3.2469 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 353.8713 | 1.133%
CZ 4A | 0.48738 | 0.030443 | 0.052885 | 0.65873 | 0.20749 | 0.45945 | 0.069856 | 0.49464 | 0 | 0.13581 | 0.030889 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.873 | 19.08% | CZ 4A | 16.4205 | 1.0257 | 5.0663 | 58.1349 | 6.9907 | 15.4798 | 2.3536 | 16.6652 | 0 | 4.5758 | 1.0407 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 176.9798 | 19.08% | CZ 4A | 4.8112 | 0.30053 | 0.03308 | 1.1521 | 2.0483 | 4.5356 | 0.6896 | 4.8829 | 0 | 1.3407 | 0.30492 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.3117 | 19.08% | CZ 4A | 0 | 0 | 0.049534 | 0.54203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.70114 | 19.08% | CZ 4A | 50.3685 | 3.1462 | 5.7604 | 71.3047 | 21.4433 | 47.483 | 7.2194 | 51.1191 | 0 | 14.0359 | 3.1922 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 404.4367 | 19.08%
CZ 4B | 0.48738 | 0.030456 | 0.052186 | 0.47434 | 0.40976 | 0.29199 | 0.034831 | 0.54333 | 0 | 0.099587 | 0.030802 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.7001 | 0.906% | CZ 4B | 16.4205 | 1.0261 | 4.9964 | 37.5581 | 13.8054 | 9.8377 | 1.1735 | 18.3059 | 0 | 3.3552 | 1.0378 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 156.7433 | 0.906% | CZ 4B | 4.8112 | 0.30065 | 0.03308 | 1.4702 | 4.045 | 2.8825 | 0.34384 | 5.3636 | 0 | 0.98309 | 0.30407 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.7501 | 0.906% | CZ 4B | 0 | 0 | 0.048835 | 0.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.48381 | 0.906% | CZ 4B | 50.3685 | 3.1476 | 5.6839 | 50.9584 | 42.3469 | 30.1765 | 3.5997 | 56.1517 | 0 | 10.2919 | 3.1833 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 385.2724 | 0.906%
CZ 4C | 0.48738 | 0.030419 | 0.05355 | 0.60829 | 0.11049 | 0.23517 | 0.023519 | 0.49351 | 0 | 0.094385 | 0.030487 | 0.29599 | 0.020225 | 0.27223 | 0 | 0.657 | 3.4126 | 2.972% | CZ 4C | 16.4205 | 1.0249 | 5.1328 | 53.5244 | 3.7226 | 7.9234 | 0.79239 | 16.6272 | 0 | 3.18 | 1.0271 | 9.9723 | 0.68141 | 16.4378 | 0 | 22.1353 | 158.6022 | 2.972% | CZ 4C | 4.8112 | 0.30029 | 0.03308 | 1.0875 | 1.0907 | 2.3216 | 0.23217 | 4.8718 | 0 | 0.93174 | 0.30095 | 2.9219 | 0.19965 | 1.6057 | 0 | 6.4856 | 27.1939 | 2.972% | CZ 4C | 0 | 0 | 0.050199 | 0.49813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.6579 | 2.972% | CZ 4C | 50.3685 | 3.1437 | 5.833 | 65.8307 | 11.4189 | 24.3044 | 2.4306 | 51.0026 | 0 | 9.7544 | 3.1507 | 30.5892 | 2.0902 | 28.7866 | 0 | 67.8982 | 356.6018 | 2.972%
CZ 5A | 0.48738 | 0.030419 | 0.05521 | 0.74064 | 0.24778 | 0.31636 | 0.043947 | 0.49526 | 0 | 0.11681 | 0.030377 | 0.29599 | 0.020224 | 0.27223 | 0 | 0.657 | 3.8096 | 23.15% | CZ 5A | 16.4205 | 1.0249 | 5.2988 | 65.2013 | 8.348 | 10.6586 | 1.4806 | 16.6862 | 0 | 3.9355 | 1.0235 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 179.3046 | 23.15% | CZ 5A | 4.8112 | 0.30029 | 0.033092 | 1.3194 | 2.446 | 3.123 | 0.43383 | 4.8891 | 0 | 1.1531 | 0.29987 | 2.9219 | 0.19964 | 1.6057 | 0 | 6.4856 | 30.0216 | 23.15% | CZ 5A | 0 | 0 | 0.051858 | 0.60698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.76842 | 23.15% | CZ 5A | 50.3685 | 3.1437 | 6.0145 | 80.1559 | 25.6068 | 32.6944 | 4.5417 | 51.1836 | 0 | 12.0719 | 3.1394 | 30.5892 | 2.0901 | 28.7866 | 0 | 67.8982 | 398.2845 | 23.15%
CZ 5B | 0.48738 | 0.030446 | 0.054489 | 0.56277 | 0.41315 | 0.26012 | 0.024225 | 0.54065 | 0 | 0.094137 | 0.030354 | 0.29599 | 0.020225 | 0.27223 | 0 | 0.657 | 3.7431 | 6.131% | CZ 5B | 16.4205 | 1.0258 | 5.2267 | 45.0725 | 13.9196 | 8.7638 | 0.81618 | 18.2153 | 0 | 3.1716 | 1.0227 | 9.9723 | 0.68141 | 16.4378 | 0 | 22.1353 | 162.8814 | 6.131% | CZ 5B | 4.8112 | 0.30055 | 0.03308 | 1.6681 | 4.0784 | 2.5678 | 0.23914 | 5.3371 | 0 | 0.92929 | 0.29964 | 2.9219 | 0.19965 | 1.6057 | 0 | 6.4856 | 31.4771 | 6.131% | CZ 5B | 0 | 0 | 0.051138 | 0.39379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.55451 | 6.131% | CZ 5B | 50.3685 | 3.1465 | 5.9357 | 60.5047 | 42.6972 | 26.8821 | 2.5036 | 55.8738 | 0 | 9.7288 | 3.137 | 30.5892 | 2.0902 | 28.7866 | 0 | 67.8982 | 390.142 | 6.131%
CZ 5C | 0.48738 | 0.030411 | 0.054854 | 0.64066 | 0.11569 | 0.19652 | 0.014488 | 0.49206 | 0 | 0.084859 | 0.03017 | 0.29599 | 0.020224 | 0.27223 | 0 | 0.657 | 3.3925 | 0.1013% | CZ 5C | 16.4205 | 1.0246 | 5.2632 | 55.7743 | 3.8978 | 6.6211 | 0.48811 | 16.5782 | 0 | 2.859 | 1.0165 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 159.17 | 0.1013% | CZ 5C | 4.8112 | 0.30021 | 0.03308 | 1.2345 | 1.142 | 1.94 | 0.14302 | 4.8574 | 0 | 0.8377 | 0.29782 | 2.9219 | 0.19964 | 1.6057 | 0 | 6.4856 | 26.8098 | 0.1013% | CZ 5C | 0 | 0 | 0.051503 | 0.51561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.67669 | 0.1013% | CZ 5C | 50.3685 | 3.1429 | 5.9756 | 69.28 | 11.9561 | 20.3097 | 1.4973 | 50.8522 | 0 | 8.7699 | 3.1179 | 30.5892 | 2.0901 | 28.7866 | 0 | 67.8982 | 354.6341 | 0.1013%
CZ 6A | 0.48738 | 0.030442 | 0.057208 | 0.88061 | 0.29652 | 0.32698 | 0.048738 | 0.49906 | 0 | 0.12528 | 0.030243 | 0.29599 | 0.020224 | 0.27223 | 0 | 0.657 | 4.0279 | 3.602% | CZ 6A | 16.4205 | 1.0257 | 5.4985 | 79.0525 | 9.9903 | 11.0164 | 1.6421 | 16.8143 | 0 | 4.2207 | 1.0189 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 195.9266 | 3.602% | CZ 6A | 4.8112 | 0.30052 | 0.033092 | 1.3411 | 2.9272 | 3.2278 | 0.48112 | 4.9266 | 0 | 1.2367 | 0.29855 | 2.9219 | 0.19964 | 1.6057 | 0 | 6.4856 | 30.7967 | 3.602% | CZ 6A | 0 | 0 | 0.053856 | 0.74475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.90818 | 3.602% | CZ 6A | 50.3685 | 3.1461 | 6.2329 | 95.4418 | 30.6444 | 33.7919 | 5.0369 | 51.5764 | 0 | 12.9468 | 3.1255 | 30.5892 | 2.0901 | 28.7866 | 0 | 67.8982 | 421.6753 | 3.602%
CZ 6B | 0.48738 | 0.030418 | 0.056655 | 0.76097 | 0.42506 | 0.2419 | 0.017864 | 0.51908 | 0 | 0.095081 | 0.030011 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.9099 | 0.6285% | CZ 6B | 16.4205 | 1.0248 | 5.4432 | 63.7419 | 14.321 | 8.1501 | 0.60188 | 17.4887 | 0 | 3.2034 | 1.0111 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 180.6334 | 0.6285% | CZ 6B | 4.8112 | 0.30027 | 0.033092 | 1.8394 | 4.1961 | 2.388 | 0.17635 | 5.1242 | 0 | 0.93861 | 0.29626 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.3162 | 0.6285% | CZ 6B | 0 | 0 | 0.053303 | 0.57464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.73752 | 0.6285% | CZ 6B | 50.3685 | 3.1436 | 6.1724 | 82.0646 | 43.9286 | 24.9997 | 1.8462 | 53.645 | 0 | 9.8263 | 3.1016 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 408.4605 | 0.6285%
CZ 7 | 0.48738 | 0.030432 | 0.059626 | 1.0009 | 0.3688 | 0.27927 | 0.033021 | 0.49665 | 0 | 0.11172 | 0.029975 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 4.1432 | 0.8031% | CZ 7 | 16.4205 | 1.0253 | 5.7404 | 89.813 | 12.4256 | 9.4091 | 1.1125 | 16.733 | 0 | 3.7642 | 1.0099 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 206.6801 | 0.8031% | CZ 7 | 4.8112 | 0.30041 | 0.033092 | 1.5297 | 3.6407 | 2.7569 | 0.32597 | 4.9028 | 0 | 1.1029 | 0.2959 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 30.9124 | 0.8031% | CZ 7 | 0 | 0 | 0.056274 | 0.84592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 1.0118 | 0.8031% | CZ 7 | 50.3685 | 3.145 | 6.4972 | 108.4739 | 38.1144 | 28.8616 | 3.4126 | 51.327 | 0 | 11.5463 | 3.0978 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 434.2084 | 0.8031%
CZ 8 | 0.48738 | 0.030221 | 0.063147 | 1.2413 | 0.47174 | 0.20625 | 0.013651 | 0.49023 | 0 | 0.094288 | 0.029544 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 4.3732 | 0.03822% | CZ 8 | 16.4205 | 1.0182 | 6.0924 | 111.4302 | 15.8938 | 6.9488 | 0.45993 | 16.5167 | 0 | 3.1767 | 0.99539 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 228.1793 | 0.03822% | CZ 8 | 4.8112 | 0.29833 | 0.033092 | 1.8908 | 4.6569 | 2.036 | 0.13476 | 4.8394 | 0 | 0.93078 | 0.29165 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.1357 | 0.03822% | CZ 8 | 0 | 0 | 0.059795 | 1.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 1.2191 | 0.03822% | CZ 8 | 50.3685 | 3.1232 | 6.882 | 134.5343 | 48.7528 | 21.3148 | 1.4108 | 50.6637 | 0 | 9.7443 | 3.0533 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 459.2116 | 0.03822%
US Weighted | 0.48738 | 0.030451 | 0.052276 | 0.59829 | 0.20717 | 0.47027 | 0.077453 | 0.5042 | 0 | 0.13213 | 0.031174 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.8362 | 100% | US Weighted | 16.4205 | 1.026 | 5.0054 | 52.7178 | 6.9798 | 15.8442 | 2.6095 | 16.9872 | 0 | 4.4516 | 1.0503 | 9.9723 | 0.68134 | 16.4378 | 0 | 22.1353 | 172.3191 | 100% | US Weighted | 4.8112 | 0.3006 | 0.033081 | 1.0587 | 2.0451 | 4.6424 | 0.76459 | 4.9773 | 0 | 1.3043 | 0.30774 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.4578 | 100% | US Weighted | 0 | 0 | 0.048925 | 0.49105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64955 | 100% | US Weighted | 50.3685 | 3.147 | 5.6938 | 64.7548 | 21.4099 | 48.6008 | 8.0045 | 52.1069 | 0 | 13.6549 | 3.2217 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 400.3269 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.48738 | 0.030512 | 0.047117 | 0.33632 | 0 | 0.90654 | 0.18801 | 0.52199 | 0 | 0.16333 | 0.033256 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.9599 | 1.766% | CZ 1A | 16.4205 | 1.028 | 4.4896 | 33.6321 | 0 | 30.5428 | 6.3343 | 17.5866 | 0 | 5.5029 | 1.1205 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 165.884 | 1.766% | CZ 1A | 4.8112 | 0.30121 | 0.033069 | 0 | 0 | 8.9491 | 1.856 | 5.1529 | 0 | 1.6124 | 0.32829 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 34.2569 | 1.766% | CZ 1A | 0 | 0 | 0.043767 | 0.33632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.48966 | 1.766% | CZ 1A | 50.3685 | 3.1533 | 5.13 | 36.7598 | 0 | 93.6876 | 19.4301 | 53.9454 | 0 | 16.8798 | 3.4369 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 412.1553 | 1.766%
CZ 1B | 0.48738 | 0.030475 | 0.047141 | 0.32996 | 0.0097559 | 0.8622 | 0.14055 | 0.55815 | 0 | 0.15649 | 0.033112 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.9007 | 0% | CZ 1B | 16.4205 | 1.0268 | 4.492 | 31.791 | 0.32869 | 29.0489 | 4.7355 | 18.805 | 0 | 5.2725 | 1.1156 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 162.2631 | 0% | CZ 1B | 4.8112 | 0.30084 | 0.033069 | 0.17944 | 0.096307 | 8.5113 | 1.3875 | 5.5099 | 0 | 1.5448 | 0.32687 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 33.9141 | 0% | CZ 1B | 0 | 0 | 0.043791 | 0.31179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.46515 | 0% | CZ 1B | 50.3685 | 3.1495 | 5.1326 | 35.9568 | 1.0082 | 89.1051 | 14.5258 | 57.6827 | 0 | 16.1728 | 3.422 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 405.888 | 0%
CZ 2A | 0.48738 | 0.03045 | 0.048181 | 0.40833 | 0.038533 | 0.86949 | 0.15694 | 0.51933 | 0 | 0.16802 | 0.03258 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 4.0047 | 14.8% | CZ 2A | 16.4205 | 1.0259 | 4.5959 | 38.709 | 1.2982 | 29.2945 | 5.2874 | 17.497 | 0 | 5.6609 | 1.0977 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 170.1137 | 14.8% | CZ 2A | 4.8112 | 0.3006 | 0.03308 | 0.31615 | 0.38039 | 8.5833 | 1.5492 | 5.1266 | 0 | 1.6586 | 0.32162 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 34.2937 | 14.8% | CZ 2A | 0 | 0 | 0.04483 | 0.3763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.53071 | 14.8% | CZ 2A | 50.3685 | 3.1469 | 5.2462 | 44.4393 | 3.9823 | 89.8584 | 16.2188 | 53.6707 | 0 | 17.3642 | 3.3671 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 417.0264 | 14.8%
CZ 2B | 0.48738 | 0.03047 | 0.048351 | 0.48651 | 0.33115 | 0.53972 | 0.073911 | 0.54841 | 0 | 0.12812 | 0.032041 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.9515 | 2.777% | CZ 2B | 16.4205 | 1.0266 | 4.6128 | 38.7088 | 11.157 | 18.1841 | 2.4902 | 18.4769 | 0 | 4.3166 | 1.0795 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 165.6997 | 2.777% | CZ 2B | 4.8112 | 0.30079 | 0.033092 | 1.4801 | 3.269 | 5.328 | 0.72963 | 5.4137 | 0 | 1.2648 | 0.3163 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 34.1594 | 2.777% | CZ 2B | 0 | 0 | 0.044999 | 0.33657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49115 | 2.777% | CZ 2B | 50.3685 | 3.149 | 5.2648 | 52.2826 | 34.223 | 55.7783 | 7.6385 | 56.6763 | 0 | 13.2409 | 3.3113 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 411.2972 | 2.777%
CZ 3A | 0.48738 | 0.030499 | 0.050628 | 0.51145 | 0.14683 | 0.56536 | 0.094408 | 0.51665 | 0 | 0.14174 | 0.03156 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.8219 | 14.21% | CZ 3A | 16.4205 | 1.0276 | 4.8405 | 45.7072 | 4.9471 | 19.0478 | 3.1808 | 17.4067 | 0 | 4.7754 | 1.0633 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 167.6434 | 14.21% | CZ 3A | 4.8112 | 0.30108 | 0.033092 | 0.80951 | 1.4495 | 5.581 | 0.93196 | 5.1002 | 0 | 1.3992 | 0.31155 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.9411 | 14.21% | CZ 3A | 0 | 0 | 0.047276 | 0.42944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.5863 | 14.21% | CZ 3A | 50.3685 | 3.152 | 5.5137 | 55.4129 | 15.1747 | 58.4275 | 9.7567 | 53.3936 | 0 | 14.6481 | 3.2616 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 398.4732 | 14.21%
CZ 3B | 0.48738 | 0.030481 | 0.04997 | 0.42708 | 0.31962 | 0.39869 | 0.059423 | 0.54549 | 0 | 0.11187 | 0.031501 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.7069 | 7.904% | CZ 3B | 16.4205 | 1.0269 | 4.7748 | 33.7914 | 10.7685 | 13.4326 | 2.0021 | 18.3785 | 0 | 3.769 | 1.0613 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 154.6524 | 7.904% | CZ 3B | 4.8112 | 0.3009 | 0.03308 | 1.3275 | 3.1552 | 3.9358 | 0.58661 | 5.3849 | 0 | 1.1043 | 0.31097 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 32.1633 | 7.904% | CZ 3B | 0 | 0 | 0.046619 | 0.29261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.4488 | 7.904% | CZ 3B | 50.3685 | 3.1501 | 5.4418 | 45.8796 | 33.0315 | 41.2034 | 6.1412 | 56.3744 | 0 | 11.5611 | 3.2556 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 385.7712 | 7.904%
CZ 3C | 0.48738 | 0.030478 | 0.050605 | 0.44011 | 0.062218 | 0.37 | 0.059187 | 0.51415 | 0 | 0.10822 | 0.031397 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.3992 | 1.133% | CZ 3C | 16.4205 | 1.0269 | 4.8383 | 41.2939 | 2.0962 | 12.466 | 1.9941 | 17.3227 | 0 | 3.646 | 1.0578 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 151.389 | 1.133% | CZ 3C | 4.8112 | 0.30087 | 0.03308 | 0.40448 | 0.61419 | 3.6525 | 0.58427 | 5.0755 | 0 | 1.0683 | 0.30994 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 28.0672 | 1.133% | CZ 3C | 0 | 0 | 0.047254 | 0.39913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.55596 | 1.133% | CZ 3C | 50.3685 | 3.1498 | 5.5111 | 47.8599 | 6.43 | 38.2383 | 6.1168 | 53.1359 | 0 | 11.1839 | 3.2447 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 354.6028 | 1.133%
CZ 4A | 0.48738 | 0.030443 | 0.052877 | 0.61501 | 0.20763 | 0.45613 | 0.067806 | 0.50842 | 0 | 0.13147 | 0.030854 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.8334 | 19.08% | CZ 4A | 16.4205 | 1.0257 | 5.0654 | 53.7553 | 6.9954 | 15.3678 | 2.2845 | 17.1294 | 0 | 4.4295 | 1.0395 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 172.7396 | 19.08% | CZ 4A | 4.8112 | 0.30053 | 0.033092 | 1.1531 | 2.0497 | 4.5028 | 0.66936 | 5.0189 | 0 | 1.2978 | 0.30458 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.3539 | 19.08% | CZ 4A | 0 | 0 | 0.049525 | 0.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.6573 | 19.08% | CZ 4A | 50.3685 | 3.1462 | 5.7595 | 66.5249 | 21.4579 | 47.1393 | 7.0075 | 52.543 | 0 | 13.5871 | 3.1886 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 400.0864 | 19.08%
CZ 4B | 0.48738 | 0.030456 | 0.052177 | 0.44968 | 0.41286 | 0.29153 | 0.034574 | 0.56135 | 0 | 0.097304 | 0.030767 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.6935 | 0.906% | CZ 4B | 16.4205 | 1.0261 | 4.9954 | 35.0457 | 13.9099 | 9.8222 | 1.1649 | 18.9128 | 0 | 3.2783 | 1.0366 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 154.8391 | 0.906% | CZ 4B | 4.8112 | 0.30065 | 0.033092 | 1.4772 | 4.0756 | 2.8779 | 0.3413 | 5.5415 | 0 | 0.96056 | 0.30373 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.9355 | 0.906% | CZ 4B | 0 | 0 | 0.048825 | 0.30004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.45844 | 0.906% | CZ 4B | 50.3685 | 3.1476 | 5.683 | 48.2593 | 42.6673 | 30.1287 | 3.5731 | 58.0135 | 0 | 10.0561 | 3.1797 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 384.4405 | 0.906%
CZ 4C | 0.48738 | 0.030419 | 0.053544 | 0.58462 | 0.11058 | 0.23542 | 0.02351 | 0.50607 | 0 | 0.093268 | 0.030454 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.4007 | 2.972% | CZ 4C | 16.4205 | 1.0249 | 5.1322 | 51.1533 | 3.7255 | 7.9316 | 0.79208 | 17.0504 | 0 | 3.1424 | 1.026 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 156.6256 | 2.972% | CZ 4C | 4.8112 | 0.30029 | 0.033092 | 1.0881 | 1.0916 | 2.324 | 0.23208 | 4.9958 | 0 | 0.92071 | 0.30063 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 27.3103 | 2.972% | CZ 4C | 0 | 0 | 0.050192 | 0.4744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.63416 | 2.972% | CZ 4C | 50.3685 | 3.1437 | 5.8324 | 63.2432 | 11.4276 | 24.3297 | 2.4296 | 52.3006 | 0 | 9.6389 | 3.1473 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 355.2256 | 2.972%
CZ 5A | 0.48738 | 0.030419 | 0.055198 | 0.67365 | 0.24783 | 0.31622 | 0.043312 | 0.50887 | 0 | 0.11211 | 0.03034 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.7508 | 23.15% | CZ 5A | 16.4205 | 1.0249 | 5.2974 | 58.497 | 8.3497 | 10.6539 | 1.4592 | 17.1447 | 0 | 3.7772 | 1.0222 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 172.8735 | 23.15% | CZ 5A | 4.8112 | 0.30029 | 0.033103 | 1.3202 | 2.4465 | 3.1216 | 0.42756 | 5.0234 | 0 | 1.1067 | 0.2995 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 30.1029 | 23.15% | CZ 5A | 0 | 0 | 0.051844 | 0.53991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.70133 | 23.15% | CZ 5A | 50.3685 | 3.1437 | 6.0131 | 72.8338 | 25.612 | 32.68 | 4.4761 | 52.59 | 0 | 11.5863 | 3.1355 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 391.8029 | 23.15%
CZ 5B | 0.48738 | 0.030446 | 0.054485 | 0.51852 | 0.41575 | 0.26265 | 0.024552 | 0.55769 | 0 | 0.092264 | 0.030316 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.7195 | 6.131% | CZ 5B | 16.4205 | 1.0258 | 5.2262 | 40.6141 | 14.0072 | 8.8491 | 0.82721 | 18.7894 | 0 | 3.1085 | 1.0214 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 159.1161 | 6.131% | CZ 5B | 4.8112 | 0.30055 | 0.033092 | 1.6731 | 4.1041 | 2.5928 | 0.24237 | 5.5053 | 0 | 0.9108 | 0.29927 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.6854 | 6.131% | CZ 5B | 0 | 0 | 0.051132 | 0.34904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.50975 | 6.131% | CZ 5B | 50.3685 | 3.1465 | 5.9352 | 55.6654 | 42.9658 | 27.144 | 2.5374 | 57.6349 | 0 | 9.5351 | 3.1331 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 387.4299 | 6.131%
CZ 5C | 0.48738 | 0.030411 | 0.054846 | 0.60448 | 0.11577 | 0.19717 | 0.014489 | 0.50436 | 0 | 0.084253 | 0.030138 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 3.3687 | 0.1013% | CZ 5C | 16.4205 | 1.0246 | 5.2623 | 52.1515 | 3.9006 | 6.6431 | 0.48815 | 16.9927 | 0 | 2.8386 | 1.0154 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 155.964 | 0.1013% | CZ 5C | 4.8112 | 0.30021 | 0.033092 | 1.2351 | 1.1429 | 1.9464 | 0.14303 | 4.9788 | 0 | 0.83172 | 0.29751 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 26.9328 | 0.1013% | CZ 5C | 0 | 0 | 0.051494 | 0.47936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64043 | 0.1013% | CZ 5C | 50.3685 | 3.1429 | 5.9747 | 65.3244 | 11.9646 | 20.3771 | 1.4974 | 52.1236 | 0 | 8.7073 | 3.1147 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 351.959 | 0.1013%
CZ 6A | 0.48738 | 0.030442 | 0.057202 | 0.79655 | 0.2966 | 0.32529 | 0.047514 | 0.51297 | 0 | 0.11903 | 0.0302 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.9486 | 3.602% | CZ 6A | 16.4205 | 1.0257 | 5.4978 | 70.6437 | 9.993 | 10.9597 | 1.6008 | 17.2828 | 0 | 4.0102 | 1.0175 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 187.6784 | 3.602% | CZ 6A | 4.8112 | 0.30052 | 0.033115 | 1.3416 | 2.9279 | 3.2112 | 0.46905 | 5.0639 | 0 | 1.175 | 0.29812 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 30.8445 | 3.602% | CZ 6A | 0 | 0 | 0.053848 | 0.66065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.82407 | 3.602% | CZ 6A | 50.3685 | 3.1461 | 6.2322 | 86.2543 | 30.6527 | 33.6179 | 4.9104 | 53.0136 | 0 | 12.3011 | 3.1211 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 412.9819 | 3.602%
CZ 6B | 0.48738 | 0.030418 | 0.056649 | 0.69989 | 0.42651 | 0.24503 | 0.018217 | 0.53515 | 0 | 0.092757 | 0.029967 | 0.29599 | 0.020223 | 0.27223 | 0 | 0.657 | 3.8674 | 0.6285% | CZ 6B | 16.4205 | 1.0248 | 5.4425 | 57.6052 | 14.3699 | 8.2555 | 0.61377 | 18.03 | 0 | 3.1251 | 1.0096 | 9.9723 | 0.68133 | 16.4378 | 0 | 22.1353 | 175.1237 | 0.6285% | CZ 6B | 4.8112 | 0.30027 | 0.033103 | 1.8436 | 4.2104 | 2.4189 | 0.17984 | 5.2828 | 0 | 0.91566 | 0.29582 | 2.9219 | 0.19963 | 1.6057 | 0 | 6.4856 | 31.5044 | 0.6285% | CZ 6B | 0 | 0 | 0.053295 | 0.51313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.676 | 0.6285% | CZ 6B | 50.3685 | 3.1436 | 6.1717 | 75.3857 | 44.0786 | 25.3231 | 1.8827 | 55.3054 | 0 | 9.5861 | 3.097 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 403.7064 | 0.6285%
CZ 7 | 0.48738 | 0.030432 | 0.059619 | 0.89574 | 0.37079 | 0.28272 | 0.033085 | 0.51407 | 0 | 0.10731 | 0.029932 | 0.29599 | 0.020224 | 0.27223 | 0 | 0.657 | 4.0565 | 0.8031% | CZ 7 | 16.4205 | 1.0253 | 5.7396 | 79.2103 | 12.4924 | 9.5252 | 1.1147 | 17.3201 | 0 | 3.6155 | 1.0085 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 196.6987 | 0.8031% | CZ 7 | 4.8112 | 0.30041 | 0.033103 | 1.5429 | 3.6603 | 2.7909 | 0.3266 | 5.0748 | 0 | 1.0593 | 0.29548 | 2.9219 | 0.19964 | 1.6057 | 0 | 6.4856 | 31.1078 | 0.8031% | CZ 7 | 0 | 0 | 0.056266 | 0.73945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.90529 | 0.8031% | CZ 7 | 50.3685 | 3.145 | 6.4964 | 96.9736 | 38.3193 | 29.2177 | 3.4192 | 53.1278 | 0 | 11.0902 | 3.0934 | 30.5892 | 2.0901 | 28.7866 | 0 | 67.8982 | 424.6153 | 0.8031%
CZ 8 | 0.48738 | 0.030221 | 0.063136 | 1.0842 | 0.47257 | 0.21225 | 0.014319 | 0.50527 | 0 | 0.089206 | 0.029539 | 0.29599 | 0.020221 | 0.27223 | 0 | 0.657 | 4.2335 | 0.03822% | CZ 8 | 16.4205 | 1.0182 | 6.0912 | 95.6563 | 15.9215 | 7.1512 | 0.48242 | 17.0234 | 0 | 3.0055 | 0.99523 | 9.9723 | 0.6813 | 16.4378 | 0 | 22.1353 | 212.9922 | 0.03822% | CZ 8 | 4.8112 | 0.29833 | 0.033103 | 1.8995 | 4.665 | 2.0953 | 0.14135 | 4.9879 | 0 | 0.88062 | 0.2916 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.3167 | 0.03822% | CZ 8 | 0 | 0 | 0.059782 | 0.89173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 1.0611 | 0.03822% | CZ 8 | 50.3685 | 3.1232 | 6.8808 | 117.3525 | 48.838 | 21.9358 | 1.4798 | 52.2179 | 0 | 9.2192 | 3.0528 | 30.5892 | 2.0898 | 28.7866 | 0 | 67.8982 | 443.8323 | 0.03822%
US Weighted | 0.48738 | 0.030451 | 0.052268 | 0.55914 | 0.20787 | 0.47749 | 0.074972 | 0.51945 | 0 | 0.12772 | 0.03114 | 0.29599 | 0.020222 | 0.27223 | 0 | 0.657 | 3.8133 | 100% | US Weighted | 16.4205 | 1.026 | 5.0046 | 48.7892 | 7.0036 | 16.0876 | 2.526 | 17.5013 | 0 | 4.303 | 1.0492 | 9.9723 | 0.68131 | 16.4378 | 0 | 22.1353 | 168.9374 | 100% | US Weighted | 4.8112 | 0.3006 | 0.033092 | 1.0607 | 2.0521 | 4.7137 | 0.7401 | 5.1279 | 0 | 1.2608 | 0.3074 | 2.9219 | 0.19962 | 1.6057 | 0 | 6.4856 | 31.6203 | 100% | US Weighted | 0 | 0 | 0.048916 | 0.45169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61018 | 100% | US Weighted | 50.3685 | 3.147 | 5.693 | 60.4739 | 21.4831 | 49.3473 | 7.7481 | 53.6837 | 0 | 13.199 | 3.2182 | 30.5892 | 2.0899 | 28.7866 | 0 | 67.8982 | 397.7258 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Hospital |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 241501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 241501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.091156 | 0.012423 | 0.0041436 | 0.18409 | 0 | 0.36939 | 0.10283 | 0.19358 | -0.023679 | 0.073477 | 0.0071005 | 0.0038381 | 0.011943 | 0 | 0 | 0.020302 | 1.0506 | 1.766% | CZ 1A | 3.0712 | 0.41855 | 0.39675 | 18.4094 | 0 | 12.4455 | 3.4647 | 6.5221 | -0.79777 | 2.4756 | 0.23923 | 0.12931 | 0.40238 | 0 | 0 | 0.684 | 47.8608 | 1.766% | CZ 1A | 0.89986 | 0.12264 | 0.0026225 | 0 | 0 | 3.6465 | 1.0151 | 1.911 | -0.23375 | 0.72534 | 0.070094 | 0.037888 | 0.1179 | 0 | 0 | 0.20041 | 8.5156 | 1.766% | CZ 1A | 0 | 0 | 0.003878 | 0.18409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18797 | 1.766% | CZ 1A | 9.4206 | 1.2839 | 0.45132 | 20.1215 | 0 | 38.1754 | 10.6275 | 20.0059 | -2.4471 | 7.5935 | 0.73381 | 0.39665 | 1.2343 | 0 | 0 | 2.0981 | 109.6955 | 1.766%
CZ 1B | 0.091316 | 0.012407 | 0.0037488 | 0.16551 | 0.0091407 | 0.30256 | 0.082347 | 0.22122 | -0.023679 | 0.073846 | 0.0072415 | 0.0038381 | 0.011946 | 0 | 0 | 0.020302 | 0.98174 | 0% | CZ 1B | 3.0766 | 0.418 | 0.35735 | 15.3747 | 0.30797 | 10.1936 | 2.7744 | 7.4533 | -0.79777 | 2.488 | 0.24398 | 0.12931 | 0.4025 | 0 | 0 | 0.684 | 43.1059 | 0% | CZ 1B | 0.90145 | 0.12247 | 0.002611 | 0.17507 | 0.090234 | 2.9867 | 0.8129 | 2.1838 | -0.23375 | 0.72898 | 0.071486 | 0.037888 | 0.11793 | 0 | 0 | 0.20041 | 8.1983 | 0% | CZ 1B | 0 | 0 | 0.0034843 | 0.14777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15126 | 0% | CZ 1B | 9.4372 | 1.2822 | 0.40817 | 17.9843 | 0.94466 | 31.2682 | 8.5103 | 22.8624 | -2.4471 | 7.6317 | 0.74838 | 0.39665 | 1.2346 | 0 | 0 | 2.0981 | 102.3597 | 0%
CZ 2A | 0.091213 | 0.012397 | 0.0035918 | 0.2105 | 0.025888 | 0.37343 | 0.087806 | 0.19566 | -0.022384 | 0.085489 | 0.0069549 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.1066 | 14.8% | CZ 2A | 3.0731 | 0.41769 | 0.34149 | 19.5616 | 0.8722 | 12.5815 | 2.9583 | 6.5921 | -0.75416 | 2.8803 | 0.23432 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 49.9742 | 14.8% | CZ 2A | 0.90042 | 0.12238 | 0.002634 | 0.22157 | 0.25555 | 3.6864 | 0.86679 | 1.9315 | -0.22097 | 0.84392 | 0.068656 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 9.035 | 14.8% | CZ 2A | 0 | 0 | 0.003325 | 0.18805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19138 | 14.8% | CZ 2A | 9.4265 | 1.2812 | 0.391 | 22.8739 | 2.6754 | 38.5928 | 9.0744 | 20.2208 | -2.3133 | 8.835 | 0.71876 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 115.5055 | 14.8%
CZ 2B | 0.090983 | 0.012406 | 0.0034768 | 0.28906 | 0.22656 | 0.22061 | 0.053602 | 0.20498 | -0.021199 | 0.06808 | 0.0068955 | 0.0038381 | 0.011943 | 0 | 0 | 0.020302 | 1.1915 | 2.777% | CZ 2B | 3.0654 | 0.41796 | 0.32991 | 20.7388 | 7.6331 | 7.4328 | 1.806 | 6.9062 | -0.71423 | 2.2937 | 0.23232 | 0.12931 | 0.40238 | 0 | 0 | 0.684 | 51.3577 | 2.777% | CZ 2B | 0.89816 | 0.12246 | 0.0026455 | 1.2159 | 2.2365 | 2.1778 | 0.52914 | 2.0235 | -0.20927 | 0.67206 | 0.06807 | 0.037888 | 0.1179 | 0 | 0 | 0.20041 | 10.0933 | 2.777% | CZ 2B | 0 | 0 | 0.0032088 | 0.16589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1691 | 2.777% | CZ 2B | 9.4028 | 1.2821 | 0.37842 | 30.8613 | 23.414 | 22.7995 | 5.5396 | 21.1843 | -2.1908 | 7.0358 | 0.71262 | 0.39665 | 1.2343 | 0 | 0 | 2.0981 | 124.1487 | 2.777%
CZ 3A | 0.090884 | 0.012417 | 0.002653 | 0.24109 | 0.090023 | 0.23784 | 0.057542 | 0.18586 | -0.021546 | 0.076165 | 0.0069176 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.0159 | 14.21% | CZ 3A | 3.062 | 0.41836 | 0.24753 | 21.4389 | 3.033 | 8.0133 | 1.9387 | 6.2619 | -0.72593 | 2.5661 | 0.23307 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 47.7026 | 14.21% | CZ 3A | 0.89718 | 0.12258 | 0.0026455 | 0.39747 | 0.88868 | 2.3479 | 0.56803 | 1.8347 | -0.2127 | 0.75187 | 0.068288 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 8.0229 | 14.21% | CZ 3A | 0 | 0 | 0.002385 | 0.20082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20321 | 14.21% | CZ 3A | 9.3926 | 1.2833 | 0.28838 | 26.1111 | 9.3036 | 24.5801 | 5.9467 | 19.2079 | -2.2267 | 7.8713 | 0.71491 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 106.2021 | 14.21%
CZ 3B | 0.090956 | 0.01241 | 0.0029344 | 0.22959 | 0.21685 | 0.14578 | 0.040917 | 0.18769 | -0.020901 | 0.063653 | 0.0068547 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.0128 | 7.904% | CZ 3B | 3.0645 | 0.41812 | 0.27575 | 16.9141 | 7.3061 | 4.9114 | 1.3786 | 6.3236 | -0.70418 | 2.1446 | 0.23095 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 43.4791 | 7.904% | CZ 3B | 0.89789 | 0.12251 | 0.002634 | 0.89987 | 2.1407 | 1.439 | 0.40392 | 1.8528 | -0.20633 | 0.62836 | 0.067667 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 8.6053 | 7.904% | CZ 3B | 0 | 0 | 0.0026676 | 0.13843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1411 | 7.904% | CZ 3B | 9.4 | 1.2825 | 0.31915 | 24.551 | 22.4108 | 15.0654 | 4.2286 | 19.3971 | -2.16 | 6.5783 | 0.70841 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 105.5102 | 7.904%
CZ 3C | 0.091085 | 0.012409 | 0.002436 | 0.22173 | 0.031522 | 0.13662 | 0.028702 | 0.18608 | 0 | 0.0641 | 0.0067836 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 0.81755 | 1.133% | CZ 3C | 3.0688 | 0.41808 | 0.22591 | 20.2466 | 1.062 | 4.6028 | 0.967 | 6.2695 | 0 | 2.1597 | 0.22855 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 40.4646 | 1.133% | CZ 3C | 0.89916 | 0.1225 | 0.002634 | 0.28684 | 0.31118 | 1.3486 | 0.28333 | 1.837 | 0 | 0.63278 | 0.066965 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 6.1472 | 1.133% | CZ 3C | 0 | 0 | 0.0021692 | 0.19268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19485 | 1.133% | CZ 3C | 9.4133 | 1.2824 | 0.26467 | 24.0624 | 3.2577 | 14.1188 | 2.9662 | 19.2311 | 0 | 6.6246 | 0.70106 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 85.6512 | 1.133%
CZ 4A | 0.091474 | 0.012394 | 0.0017072 | 0.28536 | 0.11638 | 0.19094 | 0.04255 | 0.17282 | -0.02193 | 0.075105 | 0.0068255 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 1.0097 | 19.08% | CZ 4A | 3.0819 | 0.41757 | 0.15295 | 25.8338 | 3.9211 | 6.4331 | 1.4336 | 5.8226 | -0.73885 | 2.5304 | 0.22996 | 0.12931 | 0.4023 | 0 | 0 | 0.684 | 50.3338 | 19.08% | CZ 4A | 0.903 | 0.12235 | 0.0026455 | 0.40224 | 1.1489 | 1.8849 | 0.42004 | 1.706 | -0.21648 | 0.74142 | 0.06738 | 0.037888 | 0.11787 | 0 | 0 | 0.20041 | 7.5386 | 19.08% | CZ 4A | 0 | 0 | 0.0014392 | 0.24461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24605 | 19.08% | CZ 4A | 9.4535 | 1.2809 | 0.185 | 30.9469 | 12.0276 | 19.7332 | 4.3973 | 17.8603 | -2.2663 | 7.7619 | 0.7054 | 0.39665 | 1.234 | 0 | 0 | 2.0981 | 105.8145 | 19.08%
CZ 4B | 0.091569 | 0.0124 | 0.0019658 | 0.2512 | 0.28654 | 0.095435 | 0.018196 | 0.18535 | -0.020987 | 0.057168 | 0.0067556 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.0217 | 0.906% | CZ 4B | 3.0851 | 0.41777 | 0.17881 | 17.4756 | 9.6541 | 3.2154 | 0.61307 | 6.2449 | -0.70709 | 1.9261 | 0.22761 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 43.547 | 0.906% | CZ 4B | 0.90394 | 0.12241 | 0.0026455 | 1.138 | 2.8287 | 0.94211 | 0.17963 | 1.8297 | -0.20718 | 0.56434 | 0.066689 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 8.7272 | 0.906% | CZ 4B | 0 | 0 | 0.0016978 | 0.13592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13761 | 0.906% | CZ 4B | 9.4634 | 1.2815 | 0.21327 | 26.7695 | 29.6132 | 9.8629 | 1.8805 | 19.1556 | -2.1689 | 5.9081 | 0.69817 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 106.4061 | 0.906%
CZ 4C | 0.091182 | 0.012385 | 0.001489 | 0.30052 | 0.081162 | 0.082398 | 0.014304 | 0.16836 | -0.020721 | 0.058079 | 0.0067149 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 0.83195 | 2.972% | CZ 4C | 3.0721 | 0.41726 | 0.13113 | 25.4073 | 2.7345 | 2.7761 | 0.48191 | 5.6723 | -0.69814 | 1.9568 | 0.22623 | 0.12931 | 0.4023 | 0 | 0 | 0.684 | 43.3932 | 2.972% | CZ 4C | 0.90012 | 0.12226 | 0.0026455 | 0.69143 | 0.8012 | 0.81341 | 0.1412 | 1.662 | -0.20455 | 0.57334 | 0.066287 | 0.037888 | 0.11787 | 0 | 0 | 0.20041 | 5.9255 | 2.972% | CZ 4C | 0 | 0 | 0.001221 | 0.23048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2317 | 2.972% | CZ 4C | 9.4234 | 1.2799 | 0.16115 | 32.4295 | 8.3878 | 8.5156 | 1.4782 | 17.3994 | -2.1415 | 6.0023 | 0.69396 | 0.39665 | 1.234 | 0 | 0 | 2.0981 | 87.3584 | 2.972%
CZ 5A | 0.091455 | 0.012385 | 0.0011444 | 0.29943 | 0.14774 | 0.10964 | 0.029293 | 0.16801 | -0.021345 | 0.064196 | 0.0067137 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 0.94475 | 23.15% | CZ 5A | 3.0813 | 0.41726 | 0.096589 | 27.3328 | 4.9775 | 3.6941 | 0.98695 | 5.6607 | -0.71914 | 2.1629 | 0.2262 | 0.12931 | 0.4023 | 0 | 0 | 0.684 | 49.1327 | 23.15% | CZ 5A | 0.90281 | 0.12226 | 0.002657 | 0.38858 | 1.4584 | 1.0824 | 0.28918 | 1.6586 | -0.21071 | 0.63372 | 0.066275 | 0.037888 | 0.11787 | 0 | 0 | 0.20041 | 6.7503 | 23.15% | CZ 5A | 0 | 0 | 0.00087521 | 0.26007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26094 | 23.15% | CZ 5A | 9.4516 | 1.2799 | 0.12348 | 32.4932 | 15.2681 | 11.3314 | 3.0274 | 17.3636 | -2.2059 | 6.6344 | 0.69384 | 0.39665 | 1.234 | 0 | 0 | 2.0981 | 99.1898 | 23.15%
CZ 5B | 0.09158 | 0.012395 | 0.001288 | 0.28554 | 0.30089 | 0.099734 | 0.017205 | 0.17991 | -0.021234 | 0.056438 | 0.0067137 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 1.0665 | 6.131% | CZ 5B | 3.0855 | 0.41761 | 0.11103 | 19.8027 | 10.1377 | 3.3602 | 0.57966 | 6.0615 | -0.71541 | 1.9015 | 0.2262 | 0.12931 | 0.4023 | 0 | 0 | 0.684 | 46.1838 | 6.131% | CZ 5B | 0.90405 | 0.12236 | 0.0026455 | 1.3028 | 2.9703 | 0.98454 | 0.16984 | 1.776 | -0.20961 | 0.55714 | 0.066275 | 0.037888 | 0.11787 | 0 | 0 | 0.20041 | 9.0026 | 6.131% | CZ 5B | 0 | 0 | 0.00102 | 0.15356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15458 | 6.131% | CZ 5B | 9.4644 | 1.281 | 0.13918 | 30.4237 | 31.0964 | 10.3071 | 1.7781 | 18.5933 | -2.1945 | 5.8327 | 0.69384 | 0.39665 | 1.234 | 0 | 0 | 2.0981 | 111.1441 | 6.131%
CZ 5C | 0.091224 | 0.012381 | 0.0010584 | 0.30681 | 0.088246 | 0.069118 | 0.010151 | 0.16427 | -0.021046 | 0.053699 | 0.006695 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 0.81868 | 0.1013% | CZ 5C | 3.0735 | 0.41714 | 0.088072 | 25.7539 | 2.9732 | 2.3287 | 0.342 | 5.5345 | -0.70909 | 1.8092 | 0.22557 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 43.0523 | 0.1013% | CZ 5C | 0.90054 | 0.12222 | 0.0026455 | 0.73349 | 0.87114 | 0.68231 | 0.10021 | 1.6216 | -0.20776 | 0.5301 | 0.066091 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 5.7788 | 0.1013% | CZ 5C | 0 | 0 | 0.00079043 | 0.23251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2333 | 0.1013% | CZ 5C | 9.4277 | 1.2795 | 0.11409 | 33.0917 | 9.1199 | 7.1431 | 1.0491 | 16.9765 | -2.1751 | 5.5496 | 0.69191 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 85.997 | 0.1013%
CZ 6A | 0.091611 | 0.012394 | 0.00084962 | 0.3624 | 0.17666 | 0.11531 | 0.031518 | 0.16805 | -0.021645 | 0.067836 | 0.0066857 | 0.0038381 | 0.011944 | 0 | 0 | 0.020302 | 1.0478 | 3.602% | CZ 6A | 3.0865 | 0.41757 | 0.067114 | 35.0097 | 5.9521 | 3.8851 | 1.0619 | 5.6618 | -0.72927 | 2.2855 | 0.22525 | 0.12931 | 0.40242 | 0 | 0 | 0.684 | 58.139 | 3.602% | CZ 6A | 0.90436 | 0.12235 | 0.002657 | 0.18313 | 1.744 | 1.1383 | 0.31113 | 1.6589 | -0.21368 | 0.66965 | 0.065999 | 0.037888 | 0.11791 | 0 | 0 | 0.20041 | 6.943 | 3.602% | CZ 6A | 0 | 0 | 0.00058046 | 0.34385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34443 | 3.602% | CZ 6A | 9.4677 | 1.2809 | 0.091261 | 39.4996 | 18.2577 | 11.9173 | 3.2572 | 17.367 | -2.237 | 7.0106 | 0.69095 | 0.39665 | 1.2344 | 0 | 0 | 2.0981 | 110.3324 | 3.602%
CZ 6B | 0.091617 | 0.012385 | 0.00089123 | 0.39311 | 0.3006 | 0.10338 | 0.01251 | 0.17062 | -0.021408 | 0.058935 | 0.0066682 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.1654 | 0.6285% | CZ 6B | 3.0867 | 0.41726 | 0.071353 | 30.4914 | 10.1276 | 3.483 | 0.4215 | 5.7484 | -0.72126 | 1.9856 | 0.22466 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 56.552 | 0.6285% | CZ 6B | 0.90441 | 0.12226 | 0.0026455 | 1.3131 | 2.9674 | 1.0205 | 0.1235 | 1.6843 | -0.21133 | 0.58179 | 0.065827 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 8.9305 | 0.6285% | CZ 6B | 0 | 0 | 0.00062324 | 0.2601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26072 | 0.6285% | CZ 6B | 9.4683 | 1.2799 | 0.095816 | 42.1754 | 31.0656 | 10.6839 | 1.2929 | 17.6326 | -2.2124 | 6.0908 | 0.68914 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 121.9909 | 0.6285%
CZ 7 | 0.091777 | 0.012389 | 0.00052623 | 0.40013 | 0.21186 | 0.10904 | 0.02321 | 0.16673 | -0.021575 | 0.064765 | 0.0066554 | 0.0038381 | 0.011945 | 0 | 0 | 0.020302 | 1.1016 | 0.8031% | CZ 7 | 3.0921 | 0.41741 | 0.034853 | 39.4404 | 7.138 | 3.6738 | 0.78199 | 5.6173 | -0.72691 | 2.182 | 0.22423 | 0.12931 | 0.40246 | 0 | 0 | 0.684 | 63.0909 | 0.8031% | CZ 7 | 0.90599 | 0.1223 | 0.0026455 | 0.085288 | 2.0914 | 1.0764 | 0.22912 | 1.6459 | -0.21299 | 0.63933 | 0.0657 | 0.037888 | 0.11792 | 0 | 0 | 0.20041 | 7.0073 | 0.8031% | CZ 7 | 0 | 0 | 0.00025824 | 0.39149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39175 | 0.8031% | CZ 7 | 9.4848 | 1.2804 | 0.055922 | 43.683 | 21.8951 | 11.2691 | 2.3987 | 17.2307 | -2.2297 | 6.6932 | 0.68782 | 0.39665 | 1.2345 | 0 | 0 | 2.0981 | 116.1783 | 0.8031%
CZ 8 | 0.090879 | 0.012304 | 0.00033587 | 0.49086 | 0.26095 | 0.10603 | 0.011226 | 0.16023 | -0.021841 | 0.060223 | 0.0066461 | 0.0038381 | 0.011942 | 0 | 0 | 0.020302 | 1.2139 | 0.03822% | CZ 8 | 3.0619 | 0.41455 | 0.01574 | 48.8011 | 8.7918 | 3.5725 | 0.37824 | 5.3984 | -0.73586 | 2.029 | 0.22392 | 0.12931 | 0.40234 | 0 | 0 | 0.684 | 73.1669 | 0.03822% | CZ 8 | 0.89713 | 0.12146 | 0.002657 | 0.042339 | 2.576 | 1.0467 | 0.11082 | 1.5817 | -0.21561 | 0.5945 | 0.065608 | 0.037888 | 0.11789 | 0 | 0 | 0.20041 | 7.1796 | 0.03822% | CZ 8 | 0 | 0 | 6.672e-05 | 0.48657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48663 | 0.03822% | CZ 8 | 9.3921 | 1.2716 | 0.035109 | 53.6249 | 26.968 | 10.9583 | 1.1602 | 16.5591 | -2.2572 | 6.2238 | 0.68685 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 128.3517 | 0.03822%
US Weighted | 0.091289 | 0.012398 | 0.0021111 | 0.26906 | 0.13042 | 0.19181 | 0.045994 | 0.17969 | -0.021383 | 0.070727 | 0.0068221 | 0.0038381 | 0.011941 | 0 | 0 | 0.020302 | 1.015 | 100% | US Weighted | 3.0757 | 0.41769 | 0.19334 | 23.6068 | 4.394 | 6.4625 | 1.5496 | 6.0542 | -0.72045 | 2.3829 | 0.22985 | 0.12931 | 0.40232 | 0 | 0 | 0.684 | 48.8618 | 100% | US Weighted | 0.90117 | 0.12238 | 0.0026454 | 0.49115 | 1.2874 | 1.8935 | 0.45404 | 1.7739 | -0.21109 | 0.69819 | 0.067346 | 0.037888 | 0.11788 | 0 | 0 | 0.20041 | 7.8368 | 100% | US Weighted | 0 | 0 | 0.0018431 | 0.21931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22115 | 100% | US Weighted | 9.4344 | 1.2812 | 0.22915 | 29.1119 | 13.4782 | 19.8231 | 4.7533 | 18.5707 | -2.2099 | 7.3094 | 0.70504 | 0.39665 | 1.2341 | 0 | 0 | 2.0981 | 106.2154 | 100%
Building Type: | Hospital |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 241501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 241501 | [17 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 18.7% | 40.71% | 8.794% | 54.74% | 0% | 40.75% | 54.7% | 37.09% | 0% | 44.99% | 21.35% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.53% | 1.766% | CZ 1A | 18.7% | 40.71% | 8.837% | 54.74% | 0% | 40.75% | 54.7% | 37.09% | 0% | 44.99% | 21.35% | 1.297% | 59.06% | 0% | 0% | 3.09% | 28.85% | 1.766% | CZ 1A | 18.7% | 40.71% | 7.93% | 0% | 0% | 40.75% | 54.7% | 37.09% | 0% | 44.99% | 21.35% | 1.297% | 59.06% | 0% | 0% | 3.09% | 24.86% | 1.766% | CZ 1A | 0% | 0% | 8.86% | 54.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.39% | 1.766% | CZ 1A | 18.7% | 40.71% | 8.798% | 54.74% | 0% | 40.75% | 54.7% | 37.09% | 0% | 44.99% | 21.35% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.62% | 1.766%
CZ 1B | 18.74% | 40.71% | 7.952% | 50.16% | 93.69% | 35.09% | 58.59% | 39.63% | 0% | 47.19% | 21.87% | 1.297% | 59.07% | 0% | 0% | 3.09% | 25.17% | 0% | CZ 1B | 18.74% | 40.71% | 7.955% | 48.36% | 93.69% | 35.09% | 58.59% | 39.63% | 0% | 47.19% | 21.87% | 1.297% | 59.07% | 0% | 0% | 3.09% | 26.57% | 0% | CZ 1B | 18.74% | 40.71% | 7.896% | 97.56% | 93.69% | 35.09% | 58.59% | 39.63% | 0% | 47.19% | 21.87% | 1.297% | 59.07% | 0% | 0% | 3.09% | 24.17% | 0% | CZ 1B | 0% | 0% | 7.957% | 47.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.52% | 0% | CZ 1B | 18.74% | 40.71% | 7.953% | 50.02% | 93.69% | 35.09% | 58.59% | 39.63% | 0% | 47.19% | 21.87% | 1.297% | 59.07% | 0% | 0% | 3.09% | 25.22% | 0%
CZ 2A | 18.72% | 40.71% | 7.455% | 51.55% | 67.18% | 42.95% | 55.95% | 37.68% | 0% | 50.88% | 21.35% | 1.297% | 59.05% | 0% | 0% | 3.09% | 27.63% | 14.8% | CZ 2A | 18.72% | 40.71% | 7.43% | 50.54% | 67.18% | 42.95% | 55.95% | 37.68% | 0% | 50.88% | 21.35% | 1.297% | 59.05% | 0% | 0% | 3.09% | 29.38% | 14.8% | CZ 2A | 18.72% | 40.71% | 7.962% | 70.08% | 67.18% | 42.95% | 55.95% | 37.68% | 0% | 50.88% | 21.35% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.35% | 14.8% | CZ 2A | 0% | 0% | 7.417% | 49.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.06% | 14.8% | CZ 2A | 18.72% | 40.71% | 7.453% | 51.47% | 67.18% | 42.95% | 55.95% | 37.68% | 0% | 50.88% | 21.35% | 1.297% | 59.05% | 0% | 0% | 3.09% | 27.7% | 14.8%
CZ 2B | 18.67% | 40.71% | 7.191% | 59.42% | 68.42% | 40.88% | 72.52% | 37.38% | 0% | 53.14% | 21.52% | 1.297% | 59.06% | 0% | 0% | 3.09% | 30.15% | 2.777% | CZ 2B | 18.67% | 40.71% | 7.152% | 53.58% | 68.42% | 40.88% | 72.52% | 37.38% | 0% | 53.14% | 21.52% | 1.297% | 59.06% | 0% | 0% | 3.09% | 30.99% | 2.777% | CZ 2B | 18.67% | 40.71% | 7.994% | 82.15% | 68.42% | 40.88% | 72.52% | 37.38% | 0% | 53.14% | 21.52% | 1.297% | 59.06% | 0% | 0% | 3.09% | 29.55% | 2.777% | CZ 2B | 0% | 0% | 7.131% | 49.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.43% | 2.777% | CZ 2B | 18.67% | 40.71% | 7.188% | 59.03% | 68.42% | 40.88% | 72.52% | 37.38% | 0% | 53.14% | 21.52% | 1.297% | 59.06% | 0% | 0% | 3.09% | 30.18% | 2.777%
CZ 3A | 18.65% | 40.71% | 5.24% | 47.14% | 61.31% | 42.07% | 60.95% | 35.97% | 0% | 53.74% | 21.92% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.58% | 14.21% | CZ 3A | 18.65% | 40.71% | 5.114% | 46.9% | 61.31% | 42.07% | 60.95% | 35.97% | 0% | 53.74% | 21.92% | 1.297% | 59.06% | 0% | 0% | 3.09% | 28.45% | 14.21% | CZ 3A | 18.65% | 40.71% | 7.994% | 49.1% | 61.31% | 42.07% | 60.95% | 35.97% | 0% | 53.74% | 21.92% | 1.297% | 59.06% | 0% | 0% | 3.09% | 25.12% | 14.21% | CZ 3A | 0% | 0% | 5.045% | 46.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.66% | 14.21% | CZ 3A | 18.65% | 40.71% | 5.23% | 47.12% | 61.31% | 42.07% | 60.95% | 35.97% | 0% | 53.74% | 21.92% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.65% | 14.21%
CZ 3B | 18.66% | 40.71% | 5.872% | 53.76% | 67.85% | 36.56% | 68.86% | 34.41% | 0% | 56.9% | 21.76% | 1.297% | 59.05% | 0% | 0% | 3.09% | 27.32% | 7.904% | CZ 3B | 18.66% | 40.71% | 5.775% | 50.05% | 67.85% | 36.56% | 68.86% | 34.41% | 0% | 56.9% | 21.76% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.11% | 7.904% | CZ 3B | 18.66% | 40.71% | 7.962% | 67.79% | 67.85% | 36.56% | 68.86% | 34.41% | 0% | 56.9% | 21.76% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.75% | 7.904% | CZ 3B | 0% | 0% | 5.722% | 47.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.44% | 7.904% | CZ 3B | 18.66% | 40.71% | 5.865% | 53.51% | 67.85% | 36.56% | 68.86% | 34.41% | 0% | 56.9% | 21.76% | 1.297% | 59.05% | 0% | 0% | 3.09% | 27.35% | 7.904%
CZ 3C | 18.69% | 40.71% | 4.814% | 50.38% | 50.66% | 36.92% | 48.49% | 36.19% | 0% | 59.23% | 21.61% | 1.297% | 59.06% | 0% | 0% | 3.09% | 24.05% | 1.133% | CZ 3C | 18.69% | 40.71% | 4.669% | 49.03% | 50.66% | 36.92% | 48.49% | 36.19% | 0% | 59.23% | 21.61% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.73% | 1.133% | CZ 3C | 18.69% | 40.71% | 7.962% | 70.92% | 50.66% | 36.92% | 48.49% | 36.19% | 0% | 59.23% | 21.61% | 1.297% | 59.06% | 0% | 0% | 3.09% | 21.9% | 1.133% | CZ 3C | 0% | 0% | 4.59% | 48.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.05% | 1.133% | CZ 3C | 18.69% | 40.71% | 4.802% | 50.28% | 50.66% | 36.92% | 48.49% | 36.19% | 0% | 59.23% | 21.61% | 1.297% | 59.06% | 0% | 0% | 3.09% | 24.15% | 1.133%
CZ 4A | 18.77% | 40.71% | 3.229% | 46.4% | 56.05% | 41.86% | 62.75% | 33.99% | 0% | 57.13% | 22.12% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.34% | 19.08% | CZ 4A | 18.77% | 40.71% | 3.019% | 48.06% | 56.05% | 41.86% | 62.75% | 33.99% | 0% | 57.13% | 22.12% | 1.297% | 59.05% | 0% | 0% | 3.09% | 29.14% | 19.08% | CZ 4A | 18.77% | 40.71% | 7.994% | 34.88% | 56.05% | 41.86% | 62.75% | 33.99% | 0% | 57.13% | 22.12% | 1.297% | 59.05% | 0% | 0% | 3.09% | 24.04% | 19.08% | CZ 4A | 0% | 0% | 2.906% | 49.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.43% | 19.08% | CZ 4A | 18.77% | 40.71% | 3.212% | 46.52% | 56.05% | 41.86% | 62.75% | 33.99% | 0% | 57.13% | 22.12% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.45% | 19.08%
CZ 4B | 18.79% | 40.71% | 3.768% | 55.86% | 69.4% | 32.74% | 52.63% | 33.02% | 0% | 58.75% | 21.96% | 1.297% | 59.06% | 0% | 0% | 3.09% | 27.66% | 0.906% | CZ 4B | 18.79% | 40.71% | 3.58% | 49.87% | 69.4% | 32.74% | 52.63% | 33.02% | 0% | 58.75% | 21.96% | 1.297% | 59.06% | 0% | 0% | 3.09% | 28.12% | 0.906% | CZ 4B | 18.79% | 40.71% | 7.994% | 77.04% | 69.4% | 32.74% | 52.63% | 33.02% | 0% | 58.75% | 21.96% | 1.297% | 59.06% | 0% | 0% | 3.09% | 27.33% | 0.906% | CZ 4B | 0% | 0% | 3.477% | 45.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.02% | 0.906% | CZ 4B | 18.79% | 40.71% | 3.753% | 55.47% | 69.4% | 32.74% | 52.63% | 33.02% | 0% | 58.75% | 21.96% | 1.297% | 59.06% | 0% | 0% | 3.09% | 27.68% | 0.906%
CZ 4C | 18.71% | 40.71% | 2.781% | 51.4% | 73.4% | 35% | 60.84% | 33.27% | 0% | 62.27% | 22.05% | 1.297% | 59.05% | 0% | 0% | 3.09% | 24.46% | 2.972% | CZ 4C | 18.71% | 40.71% | 2.555% | 49.67% | 73.4% | 35% | 60.84% | 33.27% | 0% | 62.27% | 22.05% | 1.297% | 59.05% | 0% | 0% | 3.09% | 27.71% | 2.972% | CZ 4C | 18.71% | 40.71% | 7.994% | 63.54% | 73.4% | 35% | 60.84% | 33.27% | 0% | 62.27% | 22.05% | 1.297% | 59.05% | 0% | 0% | 3.09% | 21.7% | 2.972% | CZ 4C | 0% | 0% | 2.433% | 48.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.54% | 2.972% | CZ 4C | 18.71% | 40.71% | 2.763% | 51.28% | 73.4% | 35% | 60.84% | 33.27% | 0% | 62.27% | 22.05% | 1.297% | 59.05% | 0% | 0% | 3.09% | 24.59% | 2.972%
CZ 5A | 18.76% | 40.71% | 2.073% | 44.45% | 59.61% | 34.67% | 67.63% | 33.02% | 0% | 57.26% | 22.13% | 1.297% | 59.05% | 0% | 0% | 3.09% | 25.19% | 23.15% | CZ 5A | 18.76% | 40.71% | 1.823% | 46.73% | 59.61% | 34.67% | 67.63% | 33.02% | 0% | 57.26% | 22.13% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.42% | 23.15% | CZ 5A | 18.76% | 40.71% | 8.026% | 29.43% | 59.61% | 34.67% | 67.63% | 33.02% | 0% | 57.26% | 22.13% | 1.297% | 59.05% | 0% | 0% | 3.09% | 22.42% | 23.15% | CZ 5A | 0% | 0% | 1.688% | 48.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.21% | 23.15% | CZ 5A | 18.76% | 40.71% | 2.053% | 44.61% | 59.61% | 34.67% | 67.63% | 33.02% | 0% | 57.26% | 22.13% | 1.297% | 59.05% | 0% | 0% | 3.09% | 25.32% | 23.15%
CZ 5B | 18.79% | 40.71% | 2.364% | 55.07% | 72.37% | 37.97% | 70.07% | 32.26% | 0% | 61.17% | 22.15% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.67% | 6.131% | CZ 5B | 18.79% | 40.71% | 2.125% | 48.76% | 72.37% | 37.97% | 70.07% | 32.26% | 0% | 61.17% | 22.15% | 1.297% | 59.05% | 0% | 0% | 3.09% | 29.03% | 6.131% | CZ 5B | 18.79% | 40.71% | 7.994% | 77.87% | 72.37% | 37.97% | 70.07% | 32.26% | 0% | 61.17% | 22.15% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.41% | 6.131% | CZ 5B | 0% | 0% | 1.995% | 44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.33% | 6.131% | CZ 5B | 18.79% | 40.71% | 2.345% | 54.65% | 72.37% | 37.97% | 70.07% | 32.26% | 0% | 61.17% | 22.15% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.69% | 6.131%
CZ 5C | 18.72% | 40.71% | 1.93% | 50.76% | 76.22% | 35.05% | 70.06% | 32.57% | 0% | 63.74% | 22.21% | 1.297% | 59.06% | 0% | 0% | 3.09% | 24.3% | 0.1013% | CZ 5C | 18.72% | 40.71% | 1.674% | 49.38% | 76.22% | 35.05% | 70.06% | 32.57% | 0% | 63.74% | 22.21% | 1.297% | 59.06% | 0% | 0% | 3.09% | 27.6% | 0.1013% | CZ 5C | 18.72% | 40.71% | 7.994% | 59.39% | 76.22% | 35.05% | 70.06% | 32.57% | 0% | 63.74% | 22.21% | 1.297% | 59.06% | 0% | 0% | 3.09% | 21.46% | 0.1013% | CZ 5C | 0% | 0% | 1.535% | 48.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.43% | 0.1013% | CZ 5C | 18.72% | 40.71% | 1.91% | 50.66% | 76.22% | 35.05% | 70.06% | 32.57% | 0% | 63.74% | 22.21% | 1.297% | 59.06% | 0% | 0% | 3.09% | 24.43% | 0.1013%
CZ 6A | 18.8% | 40.71% | 1.485% | 45.5% | 59.56% | 35.45% | 66.33% | 32.76% | 0% | 56.99% | 22.14% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.53% | 3.602% | CZ 6A | 18.8% | 40.71% | 1.221% | 49.56% | 59.56% | 35.45% | 66.33% | 32.76% | 0% | 56.99% | 22.14% | 1.297% | 59.06% | 0% | 0% | 3.09% | 30.98% | 3.602% | CZ 6A | 18.8% | 40.71% | 8.024% | 13.65% | 59.56% | 35.45% | 66.33% | 32.76% | 0% | 56.99% | 22.14% | 1.297% | 59.06% | 0% | 0% | 3.09% | 22.51% | 3.602% | CZ 6A | 0% | 0% | 1.078% | 52.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.8% | 3.602% | CZ 6A | 18.8% | 40.71% | 1.464% | 45.79% | 59.56% | 35.45% | 66.33% | 32.76% | 0% | 56.99% | 22.14% | 1.297% | 59.06% | 0% | 0% | 3.09% | 26.72% | 3.602%
CZ 6B | 18.8% | 40.71% | 1.573% | 56.17% | 70.48% | 42.19% | 68.67% | 31.88% | 0% | 63.54% | 22.25% | 1.297% | 59.05% | 0% | 0% | 3.09% | 30.13% | 0.6285% | CZ 6B | 18.8% | 40.71% | 1.311% | 52.93% | 70.48% | 42.19% | 68.67% | 31.88% | 0% | 63.54% | 22.25% | 1.297% | 59.05% | 0% | 0% | 3.09% | 32.29% | 0.6285% | CZ 6B | 18.8% | 40.71% | 7.992% | 71.22% | 70.48% | 42.19% | 68.67% | 31.88% | 0% | 63.54% | 22.25% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.35% | 0.6285% | CZ 6B | 0% | 0% | 1.169% | 50.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.57% | 0.6285% | CZ 6B | 18.8% | 40.71% | 1.552% | 55.95% | 70.48% | 42.19% | 68.67% | 31.88% | 0% | 63.54% | 22.25% | 1.297% | 59.05% | 0% | 0% | 3.09% | 30.22% | 0.6285%
CZ 7 | 18.83% | 40.71% | 0.8827% | 44.67% | 57.14% | 38.57% | 70.15% | 32.43% | 0% | 60.35% | 22.24% | 1.297% | 59.07% | 0% | 0% | 3.09% | 27.16% | 0.8031% | CZ 7 | 18.83% | 40.71% | 0.6072% | 49.79% | 57.14% | 38.57% | 70.15% | 32.43% | 0% | 60.35% | 22.24% | 1.297% | 59.07% | 0% | 0% | 3.09% | 32.07% | 0.8031% | CZ 7 | 18.83% | 40.71% | 7.992% | 5.528% | 57.14% | 38.57% | 70.15% | 32.43% | 0% | 60.35% | 22.24% | 1.297% | 59.07% | 0% | 0% | 3.09% | 22.53% | 0.8031% | CZ 7 | 0% | 0% | 0.459% | 52.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.27% | 0.8031% | CZ 7 | 18.83% | 40.71% | 0.8608% | 45.05% | 57.14% | 38.57% | 70.15% | 32.43% | 0% | 60.35% | 22.24% | 1.297% | 59.07% | 0% | 0% | 3.09% | 27.36% | 0.8031%
CZ 8 | 18.65% | 40.71% | 0.532% | 45.28% | 55.22% | 49.96% | 78.4% | 31.71% | 0% | 67.51% | 22.5% | 1.297% | 59.06% | 0% | 0% | 3.09% | 28.67% | 0.03822% | CZ 8 | 18.65% | 40.71% | 0.2584% | 51.02% | 55.22% | 49.96% | 78.4% | 31.71% | 0% | 67.51% | 22.5% | 1.297% | 59.06% | 0% | 0% | 3.09% | 34.35% | 0.03822% | CZ 8 | 18.65% | 40.71% | 8.026% | 2.229% | 55.22% | 49.96% | 78.4% | 31.71% | 0% | 67.51% | 22.5% | 1.297% | 59.06% | 0% | 0% | 3.09% | 22.93% | 0.03822% | CZ 8 | 0% | 0% | 0.1116% | 54.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 45.86% | 0.03822% | CZ 8 | 18.65% | 40.71% | 0.5102% | 45.7% | 55.22% | 49.96% | 78.4% | 31.71% | 0% | 67.51% | 22.5% | 1.297% | 59.06% | 0% | 0% | 3.09% | 28.92% | 0.03822%
US Weighted | 18.73% | 40.71% | 4.039% | 48.12% | 62.74% | 40.17% | 61.35% | 34.59% | 0% | 55.38% | 21.91% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.62% | 100% | US Weighted | 18.73% | 40.71% | 3.863% | 48.39% | 62.74% | 40.17% | 61.35% | 34.59% | 0% | 55.38% | 21.91% | 1.297% | 59.05% | 0% | 0% | 3.09% | 28.92% | 100% | US Weighted | 18.73% | 40.71% | 7.994% | 46.31% | 62.74% | 40.17% | 61.35% | 34.59% | 0% | 55.38% | 21.91% | 1.297% | 59.05% | 0% | 0% | 3.09% | 24.78% | 100% | US Weighted | 0% | 0% | 3.768% | 48.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.24% | 100% | US Weighted | 18.73% | 40.71% | 4.025% | 48.14% | 62.74% | 40.17% | 61.35% | 34.59% | 0% | 55.38% | 21.91% | 1.297% | 59.05% | 0% | 0% | 3.09% | 26.71% | 100%

## HotSml
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Hotel |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Small Hotel | [14 empty] | Prototype Floor Area: | 43202 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.18905 | 0.028854 | 0.12811 | 0.074891 | 0 | 0.17781 | 0 | 0.11817 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1728 |  | STD2016 | 6.3694 | 0.97213 | 12.8112 | 3.425 | 0 | 5.9909 | 0 | 3.9815 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 55.0409 |  | STD2016 | 1.8662 | 0.28483 | 0 | 0.60505 | 0 | 1.7553 | 0 | 1.1666 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.2654 |  | STD2016 | 0 | 0 | 0.12811 | 0.013599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23418 |  | STD2016 | 19.5377 | 2.9819 | 14.0027 | 7.8207 | 0 | 18.3765 | 0 | 12.2128 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 122.5961
STD2013 | 0.2115 | 0.042854 | 0.12971 | 0.11499 | 0 | 0.19522 | 0 | 0.18128 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3314 |  | STD2013 | 7.1259 | 1.4438 | 12.9709 | 4.802 | 0 | 6.5772 | 0 | 6.1076 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 60.5182 |  | STD2013 | 2.0879 | 0.42304 | 0 | 0.99699 | 0 | 1.9271 | 0 | 1.7895 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.812 |  | STD2013 | 0 | 0 | 0.12971 | 0.013993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23617 |  | STD2013 | 21.8581 | 4.4288 | 14.1772 | 11.9669 | 0 | 20.1749 | 0 | 18.7346 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 139.0042
STD2010 | 0.27062 | 0.042854 | 0.12969 | 0.11059 | 0 | 0.21914 | 0 | 0.18327 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4338 |  | STD2010 | 9.1178 | 1.4438 | 12.9694 | 4.62 | 0 | 7.3833 | 0 | 6.1748 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.9316 |  | STD2010 | 2.6715 | 0.42304 | 0 | 0.95857 | 0 | 2.1633 | 0 | 1.8092 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.8274 |  | STD2010 | 0 | 0 | 0.12969 | 0.013484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23565 |  | STD2010 | 27.968 | 4.4288 | 14.1756 | 11.509 | 0 | 22.6477 | 0 | 18.9408 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 149.5778
STD2007 | 0.32434 | 0.06204 | 0.13 | 0.12099 | 0 | 0.25144 | 0 | 0.19289 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5664 |  | STD2007 | 10.9277 | 2.0902 | 12.9996 | 4.9113 | 0 | 8.4713 | 0 | 6.4987 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.3612 |  | STD2007 | 3.2018 | 0.61244 | 0 | 1.0701 | 0 | 2.4821 | 0 | 1.9041 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.1426 |  | STD2007 | 0 | 0 | 0.13 | 0.012592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23506 |  | STD2007 | 33.5198 | 6.4116 | 14.2086 | 12.5787 | 0 | 25.985 | 0 | 19.9344 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 163.2818
STD2004 | 0.32434 | 0.06204 | 0.13005 | 0.20947 | 0 | 0.27029 | 0 | 0.19398 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6749 |  | STD2004 | 10.9277 | 2.0902 | 13.0049 | 9.3443 | 0 | 9.1065 | 0 | 6.5356 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.4716 |  | STD2004 | 3.2018 | 0.61244 | 0 | 1.7273 | 0 | 2.6682 | 0 | 1.9149 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.9968 |  | STD2004 | 0 | 0 | 0.13005 | 0.034491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25701 |  | STD2004 | 33.5198 | 6.4116 | 14.2143 | 21.853 | 0 | 27.9335 | 0 | 20.0476 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 174.6234
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 5.2519e-05 | 0.088478 | 0 | 0.018853 | 0 | 0.0010954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10848 |  | 2004-2007 | 0 | 0 | 0.0052519 | 4.4331 | 0 | 0.6352 | 0 | 0.036906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1104 |  | 2004-2007 | 0 | 0 | 0 | 0.65725 | 0 | 0.18611 | 0 | 0.010813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85417 |  | 2004-2007 | 0 | 0 | 5.2519e-05 | 0.021899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021952 |  | 2004-2007 | 0 | 0 | 0.0057403 | 9.2743 | 0 | 1.9484 | 0 | 0.11321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3416
2007-2010 | 0.053721 | 0.019186 | 0.00030178 | 0.010402 | 0 | 0.032293 | 0 | 0.0096136 | 0 | 0 | 0 | 0.0055819 | 0 | 0 | 0 | 0.0015371 | 0.13264 |  | 2007-2010 | 1.81 | 0.64641 | 0.030178 | 0.29132 | 0 | 1.088 | 0 | 0.3239 | 0 | 0 | 0 | 0.18806 | 0 | 0 | 0 | 0.051789 | 4.4296 |  | 2007-2010 | 0.53032 | 0.1894 | 0 | 0.11148 | 0 | 0.31878 | 0 | 0.094903 | 0 | 0 | 0 | 0.055103 | 0 | 0 | 0 | 0.015174 | 1.3152 |  | 2007-2010 | 0 | 0 | 0.00030178 | -0.00089176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00058998 |  | 2007-2010 | 5.5519 | 1.9828 | 0.032984 | 1.0697 | 0 | 3.3373 | 0 | 0.99354 | 0 | 0 | 0 | 0.57687 | 0 | 0 | 0 | 0.15886 | 13.7039
2010-2013 | 0.059121 | 0 | -1.4911e-05 | -0.0044011 | 0 | 0.023927 | 0 | 0.0019955 | 0 | 0 | 0 | 0.00043639 | 0 | 0 | 0 | 0.021279 | 0.10234 |  | 2010-2013 | 1.9919 | 0 | -0.0014911 | -0.18202 | 0 | 0.80615 | 0 | 0.06723 | 0 | 0 | 0 | 0.014703 | 0 | 0 | 0 | 0.71693 | 3.4134 |  | 2010-2013 | 0.58362 | 0 | 0 | -0.038424 | 0 | 0.2362 | 0 | 0.019699 | 0 | 0 | 0 | 0.0043079 | 0 | 0 | 0 | 0.21006 | 1.0155 |  | 2010-2013 | 0 | 0 | -1.4911e-05 | -0.00050877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00052368 |  | 2010-2013 | 6.1099 | 0 | -0.0016298 | -0.45787 | 0 | 2.4728 | 0 | 0.20622 | 0 | 0 | 0 | 0.0451 | 0 | 0 | 0 | 2.1991 | 10.5737
2013-2016 | 0.022453 | 0.014 | 0.001597 | 0.040097 | 0 | 0.017401 | 0 | 0.063106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15865 |  | 2013-2016 | 0.75647 | 0.47169 | 0.1597 | 1.377 | 0 | 0.58628 | 0 | 2.1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4773 |  | 2013-2016 | 0.22164 | 0.1382 | 0 | 0.39194 | 0 | 0.17178 | 0 | 0.62296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5465 |  | 2013-2016 | 0 | 0 | 0.001597 | 0.00039339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019904 |  | 2013-2016 | 2.3204 | 1.4469 | 0.17456 | 4.1462 | 0 | 1.7984 | 0 | 6.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4081
2004-2016 | 0.13529 | 0.033186 | 0.0019364 | 0.13458 | 0 | 0.092475 | 0 | 0.07581 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50211 |  | 2004-2016 | 4.5583 | 1.1181 | 0.19364 | 5.9194 | 0 | 3.1156 | 0 | 2.5542 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 18.4307 |  | 2004-2016 | 1.3356 | 0.3276 | 0 | 1.1222 | 0 | 0.91288 | 0 | 0.74837 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.7313 |  | 2004-2016 | 0 | 0 | 0.0019364 | 0.020892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022828 |  | 2004-2016 | 13.9822 | 3.4297 | 0.21165 | 14.0323 | 0 | 9.5569 | 0 | 7.8347 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.0274
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.04038% | 42.24% |  | 6.975% |  | 0.5647% |  | 0% |  | 0% |  | 0% |  | 0% | 6.477% |  | 2004-2007 | 0% | 0% | 0.04038% | 47.44% |  | 6.975% |  | 0.5647% |  | 0% |  | 0% |  | 0% |  | 0% | 6.956% |  | 2004-2007 | 0% | 0% |  | 38.05% |  | 6.975% |  | 0.5647% |  | 0% |  | 0% |  | 0% |  | 0% | 6.103% |  | 2004-2007 |  |  | 0.04038% | 63.49% | [9 empty] | 0% |  |  | 8.541% |  | 2004-2007 | 0% | 0% | 0.04038% | 42.44% |  | 6.975% |  | 0.5647% |  | 0% |  | 0% |  | 0% |  | 0% | 6.495%
2007-2010 | 16.56% | 30.93% | 0.2321% | 8.597% |  | 12.84% |  | 4.984% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 8.468% |  | 2007-2010 | 16.56% | 30.93% | 0.2321% | 5.932% |  | 12.84% |  | 4.984% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 6.48% |  | 2007-2010 | 16.56% | 30.93% |  | 10.42% |  | 12.84% |  | 4.984% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 10.01% |  | 2007-2010 |  |  | 0.2321% | -7.082% | [9 empty] | 0% |  |  | -0.251% |  | 2007-2010 | 16.56% | 30.93% | 0.2321% | 8.504% |  | 12.84% |  | 4.984% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 8.393%
2010-2013 | 21.85% | 0% | -0.0115% | -3.98% |  | 10.92% |  | 1.089% |  | 0% |  | 0.2674% |  | 0% |  | 10.47% | 7.138% |  | 2010-2013 | 21.85% | 0% | -0.0115% | -3.94% |  | 10.92% |  | 1.089% |  | 0% |  | 0.2674% |  | 0% |  | 10.47% | 5.339% |  | 2010-2013 | 21.85% | 0% |  | -4.008% |  | 10.92% |  | 1.089% |  | 0% |  | 0.2674% |  | 0% |  | 10.47% | 8.586% |  | 2010-2013 |  |  | -0.0115% | -3.773% | [9 empty] | 0% |  |  | -0.2222% |  | 2010-2013 | 21.85% | 0% | -0.0115% | -3.978% |  | 10.92% |  | 1.089% |  | 0% |  | 0.2674% |  | 0% |  | 10.47% | 7.069%
2013-2016 | 10.62% | 32.67% | 1.231% | 34.87% |  | 8.914% |  | 34.81% |  | 0% |  | 0% |  | 0% |  | 0% | 11.92% |  | 2013-2016 | 10.62% | 32.67% | 1.231% | 28.68% |  | 8.914% |  | 34.81% |  | 0% |  | 0% |  | 0% |  | 0% | 9.051% |  | 2013-2016 | 10.62% | 32.67% |  | 39.31% |  | 8.914% |  | 34.81% |  | 0% |  | 0% |  | 0% |  | 0% | 14.3% |  | 2013-2016 |  |  | 1.231% | 2.811% | [9 empty] | 0% |  |  | 0.8428% |  | 2013-2016 | 10.62% | 32.67% | 1.231% | 34.65% |  | 8.914% |  | 34.81% |  | 0% |  | 0% |  | 0% |  | 0% | 11.8%
2004-2016 | 41.71% | 53.49% | 1.489% | 64.25% |  | 34.21% |  | 39.08% |  | 0% |  | 3.566% |  | 0% |  | 11.14% | 29.98% |  | 2004-2016 | 41.71% | 53.49% | 1.489% | 63.35% |  | 34.21% |  | 39.08% |  | 0% |  | 3.566% |  | 0% |  | 11.14% | 25.09% |  | 2004-2016 | 41.71% | 53.49% |  | 64.97% |  | 34.21% |  | 39.08% |  | 0% |  | 3.566% |  | 0% |  | 11.14% | 33.8% |  | 2004-2016 |  |  | 1.489% | 60.57% | [9 empty] | 0% |  |  | 8.882% |  | 2004-2016 | 41.71% | 53.49% | 1.489% | 64.21% |  | 34.21% |  | 39.08% |  | 0% |  | 3.566% |  | 0% |  | 11.14% | 29.79%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.19054 | 0.028906 | 0.09822 | 2.6053e-05 | 0 | 0.34769 | 0 | 0.11998 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2412 | 1.516% | CZ 1A | 6.4196 | 0.9739 | 9.822 | 0.00087778 | 0 | 11.7142 | 0 | 4.0422 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 54.4636 | 1.516% | CZ 1A | 1.881 | 0.28535 | 0 | 0.00025719 | 0 | 3.4323 | 0 | 1.1844 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.3706 | 1.516% | CZ 1A | 0 | 0 | 0.09822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19069 | 1.516% | CZ 1A | 19.6917 | 2.9874 | 10.7354 | 0.0026925 | 0 | 35.9323 | 0 | 12.3991 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 129.4123 | 1.516%
CZ 1B | 0.18982 | 0.028874 | 0.10054 | 0.0038078 | 0 | 0.36647 | 0 | 0.12527 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2707 | 0% | CZ 1B | 6.3955 | 0.9728 | 10.0539 | 0.16786 | 0 | 12.3471 | 0 | 4.2206 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 55.6486 | 0% | CZ 1B | 1.8739 | 0.28503 | 0 | 0.031699 | 0 | 3.6177 | 0 | 1.2366 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.6324 | 0% | CZ 1B | 0 | 0 | 0.10054 | 0.00059675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19361 | 0% | CZ 1B | 19.6177 | 2.984 | 10.9889 | 0.39708 | 0 | 37.8737 | 0 | 12.9463 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 132.4713 | 0%
CZ 2A | 0.18949 | 0.028854 | 0.10619 | 0.0066798 | 0 | 0.29705 | 0 | 0.11817 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2023 | 17.53% | CZ 2A | 6.3843 | 0.97214 | 10.6188 | 0.31728 | 0 | 10.0082 | 0 | 3.9814 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 53.773 | 17.53% | CZ 2A | 1.8706 | 0.28484 | 0 | 0.05221 | 0 | 2.9324 | 0 | 1.1665 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.894 | 17.53% | CZ 2A | 0 | 0 | 0.10619 | 0.0013909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20005 | 17.53% | CZ 2A | 19.5834 | 2.982 | 11.6063 | 0.69861 | 0 | 30.6994 | 0 | 12.2126 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 125.4461 | 17.53%
CZ 2B | 0.19113 | 0.028867 | 0.10736 | 0.0074191 | 0 | 0.24143 | 0 | 0.12509 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1572 | 1.732% | CZ 2B | 6.4396 | 0.97258 | 10.7362 | 0.33594 | 0 | 8.1342 | 0 | 4.2144 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 52.3238 | 1.732% | CZ 2B | 1.8868 | 0.28497 | 0 | 0.06044 | 0 | 2.3833 | 0 | 1.2348 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.4378 | 1.732% | CZ 2B | 0 | 0 | 0.10736 | 0.0012966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20113 | 1.732% | CZ 2B | 19.753 | 2.9833 | 11.7346 | 0.77446 | 0 | 24.9509 | 0 | 12.9275 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 120.7875 | 1.732%
CZ 3A | 0.19036 | 0.0289 | 0.12058 | 0.040089 | 0 | 0.19634 | 0 | 0.11816 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1503 | 15.93% | CZ 3A | 6.4135 | 0.97368 | 12.0576 | 1.8447 | 0 | 6.6152 | 0 | 3.9812 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 53.3767 | 15.93% | CZ 3A | 1.8792 | 0.28529 | 0 | 0.32219 | 0 | 1.9382 | 0 | 1.1665 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.1788 | 15.93% | CZ 3A | 0 | 0 | 0.12058 | 0.0074506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2205 | 15.93% | CZ 3A | 19.6729 | 2.9867 | 13.1789 | 4.1874 | 0 | 20.2915 | 0 | 12.2119 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 120.193 | 15.93%
CZ 3B | 0.19058 | 0.02888 | 0.11672 | 0.016888 | 0 | 0.1962 | 0 | 0.12427 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1294 | 6.609% | CZ 3B | 6.421 | 0.97302 | 11.6719 | 0.78575 | 0 | 6.6103 | 0 | 4.187 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 52.1398 | 6.609% | CZ 3B | 1.8813 | 0.28509 | 0 | 0.13445 | 0 | 1.9368 | 0 | 1.2268 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.0519 | 6.609% | CZ 3B | 0 | 0 | 0.11672 | 0.0032689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21246 | 6.609% | CZ 3B | 19.6958 | 2.9847 | 12.7574 | 1.7648 | 0 | 20.2767 | 0 | 12.8433 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 117.9864 | 6.609%
CZ 3C | 0.19013 | 0.02888 | 0.12225 | 0.0053014 | 0 | 0.16494 | 0 | 0.11609 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.0835 | 1.264% | CZ 3C | 6.4058 | 0.97302 | 12.2254 | 0.28656 | 0 | 5.5572 | 0 | 3.9112 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 50.8501 | 1.264% | CZ 3C | 1.8769 | 0.28509 | 0 | 0.036264 | 0 | 1.6283 | 0 | 1.146 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 8.5599 | 1.264% | CZ 3C | 0 | 0 | 0.12225 | 0.0016279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21635 | 1.264% | CZ 3C | 19.6493 | 2.9847 | 13.3624 | 0.55757 | 0 | 17.0463 | 0 | 11.9972 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 113.2612 | 1.264%
CZ 4A | 0.18796 | 0.028848 | 0.13289 | 0.083556 | 0 | 0.1502 | 0 | 0.11587 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1552 | 18.74% | CZ 4A | 6.3325 | 0.97192 | 13.2888 | 3.8877 | 0 | 5.0604 | 0 | 3.9039 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 54.9362 | 18.74% | CZ 4A | 1.8554 | 0.28477 | 0 | 0.66516 | 0 | 1.4827 | 0 | 1.1439 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.0193 | 18.74% | CZ 4A | 0 | 0 | 0.13289 | 0.016176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24154 | 18.74% | CZ 4A | 19.4245 | 2.9813 | 14.5246 | 8.7315 | 0 | 15.5224 | 0 | 11.975 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 120.8231 | 18.74%
CZ 4B | 0.18839 | 0.028854 | 0.12934 | 0.032788 | 0 | 0.16111 | 0 | 0.12532 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1217 | 1.192% | CZ 4B | 6.3472 | 0.97214 | 12.9343 | 1.5349 | 0 | 5.4282 | 0 | 4.2221 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 52.9297 | 1.192% | CZ 4B | 1.8597 | 0.28484 | 0 | 0.25963 | 0 | 1.5905 | 0 | 1.2371 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 8.8192 | 1.192% | CZ 4B | 0 | 0 | 0.12934 | 0.0064874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2283 | 1.192% | CZ 4B | 19.4696 | 2.982 | 14.1371 | 3.4272 | 0 | 16.6505 | 0 | 12.951 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 117.2812 | 1.192%
CZ 4C | 0.18941 | 0.028821 | 0.1366 | 0.042669 | 0 | 0.10795 | 0 | 0.1162 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.0775 | 2.105% | CZ 4C | 6.3815 | 0.97104 | 13.6598 | 2.0781 | 0 | 3.6369 | 0 | 3.9151 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 52.1333 | 2.105% | CZ 4C | 1.8698 | 0.28452 | 0 | 0.32586 | 0 | 1.0656 | 0 | 1.1471 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 8.2803 | 2.105% | CZ 4C | 0 | 0 | 0.1366 | 0.0096598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23873 | 2.105% | CZ 4C | 19.5746 | 2.9786 | 14.9301 | 4.4672 | 0 | 11.1558 | 0 | 12.0093 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 112.7794 | 2.105%
CZ 5A | 0.18825 | 0.028821 | 0.14336 | 0.14074 | 0 | 0.11142 | 0 | 0.11576 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1842 | 20.28% | CZ 5A | 6.3424 | 0.97104 | 14.3357 | 6.4105 | 0 | 3.754 | 0 | 3.9002 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 57.2048 | 20.28% | CZ 5A | 1.8583 | 0.28452 | 0 | 1.141 | 0 | 1.0999 | 0 | 1.1428 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.1139 | 20.28% | CZ 5A | 0 | 0 | 0.14336 | 0.025164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26099 | 20.28% | CZ 5A | 19.4548 | 2.9786 | 15.669 | 14.6951 | 0 | 11.5152 | 0 | 11.9635 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 123.94 | 20.28%
CZ 5B | 0.18829 | 0.028848 | 0.14035 | 0.0762 | 0 | 0.12931 | 0 | 0.12496 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1438 | 5.437% | CZ 5B | 6.3439 | 0.97192 | 14.0354 | 3.4963 | 0 | 4.3566 | 0 | 4.2101 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 54.9051 | 5.437% | CZ 5B | 1.8588 | 0.28477 | 0 | 0.61391 | 0 | 1.2765 | 0 | 1.2335 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 8.8549 | 5.437% | CZ 5B | 0 | 0 | 0.14035 | 0.01401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24684 | 5.437% | CZ 5B | 19.4595 | 2.9813 | 15.3407 | 7.9584 | 0 | 13.3636 | 0 | 12.914 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 119.6812 | 5.437%
CZ 5C | 0.18883 | 0.028815 | 0.14252 | 0.046317 | 0 | 0.092633 | 0 | 0.11458 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.0696 | 0.1861% | CZ 5C | 6.3622 | 0.97083 | 14.2524 | 2.3932 | 0 | 3.1209 | 0 | 3.8603 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 52.4506 | 0.1861% | CZ 5C | 1.8641 | 0.28445 | 0 | 0.33325 | 0 | 0.91444 | 0 | 1.1311 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 8.1147 | 0.1861% | CZ 5C | 0 | 0 | 0.14252 | 0.012558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24755 | 0.1861% | CZ 5C | 19.5154 | 2.9779 | 15.5778 | 4.8614 | 0 | 9.5733 | 0 | 11.841 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 112.0106 | 0.1861%
CZ 6A | 0.18836 | 0.028841 | 0.15113 | 0.22837 | 0 | 0.10966 | 0 | 0.11747 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2797 | 4.86% | CZ 6A | 6.3461 | 0.9717 | 15.1126 | 10.1397 | 0 | 3.6948 | 0 | 3.9579 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 61.7137 | 4.86% | CZ 6A | 1.8594 | 0.28471 | 0 | 1.8903 | 0 | 1.0826 | 0 | 1.1597 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.8641 | 4.86% | CZ 6A | 0 | 0 | 0.15113 | 0.03688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28048 | 4.86% | CZ 6A | 19.4662 | 2.9806 | 16.5181 | 23.821 | 0 | 11.3335 | 0 | 12.1406 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 133.9237 | 4.86%
CZ 6B | 0.18865 | 0.028821 | 0.14913 | 0.14351 | 0 | 0.09813 | 0 | 0.1213 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1854 | 1.535% | CZ 6B | 6.3558 | 0.97104 | 14.9125 | 6.4575 | 0 | 3.3062 | 0 | 4.0867 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 57.5806 | 1.535% | CZ 6B | 1.8622 | 0.28452 | 0 | 1.1752 | 0 | 0.96871 | 0 | 1.1974 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.0755 | 1.535% | CZ 6B | 0 | 0 | 0.14913 | 0.024467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26606 | 1.535% | CZ 6B | 19.4959 | 2.9786 | 16.2994 | 14.977 | 0 | 10.1414 | 0 | 12.5357 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 124.0916 | 1.535%
CZ 7 | 0.18786 | 0.028835 | 0.16036 | 0.26228 | 0 | 0.094313 | 0 | 0.11645 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.306 | 0.8923% | CZ 7 | 6.3292 | 0.97148 | 16.0358 | 11.9505 | 0 | 3.1776 | 0 | 3.9232 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 63.8787 | 0.8923% | CZ 7 | 1.8545 | 0.28464 | 0 | 2.1255 | 0 | 0.93103 | 0 | 1.1495 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.9326 | 0.8923% | CZ 7 | 0 | 0 | 0.16036 | 0.046961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29979 | 0.8923% | CZ 7 | 19.4144 | 2.9799 | 17.5271 | 27.3851 | 0 | 9.7469 | 0 | 12.0342 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 136.7515 | 0.8923%
CZ 8 | 0.18934 | 0.028633 | 0.17281 | 0.35384 | 0 | 0.068918 | 0 | 0.11499 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3844 | 0.1875% | CZ 8 | 6.3791 | 0.96468 | 17.2806 | 16.26 | 0 | 2.3219 | 0 | 3.8743 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 68.5714 | 0.1875% | CZ 8 | 1.8691 | 0.28265 | 0 | 2.847 | 0 | 0.68033 | 0 | 1.1352 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.4017 | 0.1875% | CZ 8 | 0 | 0 | 0.17281 | 0.065431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.33071 | 0.1875% | CZ 8 | 19.5672 | 2.9591 | 18.8877 | 36.9572 | 0 | 7.1224 | 0 | 11.8841 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 145.0414 | 0.1875%
US Weighted | 0.18905 | 0.028854 | 0.12811 | 0.074891 | 0 | 0.17781 | 0 | 0.11817 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1728 | 100% | US Weighted | 6.3694 | 0.97213 | 12.8112 | 3.425 | 0 | 5.9909 | 0 | 3.9815 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 55.0409 | 100% | US Weighted | 1.8662 | 0.28483 | 0 | 0.60505 | 0 | 1.7553 | 0 | 1.1666 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.2654 | 100% | US Weighted | 0 | 0 | 0.12811 | 0.013599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23418 | 100% | US Weighted | 19.5377 | 2.9819 | 14.0027 | 7.8207 | 0 | 18.3765 | 0 | 12.2128 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 122.5961 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.21306 | 0.042936 | 0.10559 | 3.2567e-05 | 0 | 0.40545 | 0 | 0.18112 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.4041 | 1.516% | CZ 1A | 7.1785 | 1.4466 | 10.5593 | 0.0010972 | 0 | 13.6602 | 0 | 6.1023 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 60.439 | 1.516% | CZ 1A | 2.1033 | 0.42385 | 0 | 0.00032149 | 0 | 4.0025 | 0 | 1.788 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 11.9053 | 1.516% | CZ 1A | 0 | 0 | 0.10559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19806 | 1.516% | CZ 1A | 22.0194 | 4.4373 | 11.5414 | 0.0033656 | 0 | 41.9017 | 0 | 18.7184 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 146.2852 | 1.516%
CZ 1B | 0.21221 | 0.042884 | 0.10578 | 0.004863 | 0 | 0.42716 | 0 | 0.18571 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.4345 | 0% | CZ 1B | 7.1497 | 1.4448 | 10.5775 | 0.20385 | 0 | 14.3917 | 0 | 6.257 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 61.5155 | 0% | CZ 1B | 2.0949 | 0.42333 | 0 | 0.042051 | 0 | 4.2168 | 0 | 1.8333 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 12.1977 | 0% | CZ 1B | 0 | 0 | 0.10578 | 0.00060333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19885 | 0% | CZ 1B | 21.9312 | 4.4319 | 11.5613 | 0.50617 | 0 | 44.1452 | 0 | 19.193 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 149.4325 | 0%
CZ 2A | 0.21289 | 0.042851 | 0.11059 | 0.0094612 | 0 | 0.34407 | 0 | 0.18046 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3562 | 17.53% | CZ 2A | 7.1728 | 1.4437 | 11.0593 | 0.41274 | 0 | 11.5924 | 0 | 6.0802 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 59.252 | 17.53% | CZ 2A | 2.1016 | 0.42301 | 0 | 0.079407 | 0 | 3.3966 | 0 | 1.7815 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 11.3695 | 17.53% | CZ 2A | 0 | 0 | 0.11059 | 0.0014173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20448 | 17.53% | CZ 2A | 22.0019 | 4.4285 | 12.0878 | 0.98622 | 0 | 35.5588 | 0 | 18.6504 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 141.3774 | 17.53%
CZ 2B | 0.21477 | 0.042877 | 0.11151 | 0.0097121 | 0 | 0.27214 | 0 | 0.18738 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2943 | 1.732% | CZ 2B | 7.236 | 1.4446 | 11.151 | 0.41494 | 0 | 9.1689 | 0 | 6.3132 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 57.2195 | 1.732% | CZ 2B | 2.1201 | 0.42327 | 0 | 0.082815 | 0 | 2.6865 | 0 | 1.8498 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.7499 | 1.732% | CZ 2B | 0 | 0 | 0.11151 | 0.0013229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2053 | 1.732% | CZ 2B | 22.1958 | 4.4312 | 12.1881 | 1.0116 | 0 | 28.1247 | 0 | 19.3653 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 134.9804 | 1.732%
CZ 3A | 0.21379 | 0.042923 | 0.12267 | 0.060178 | 0 | 0.21912 | 0 | 0.18134 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2959 | 15.93% | CZ 3A | 7.2028 | 1.4461 | 12.2669 | 2.5217 | 0 | 7.3826 | 0 | 6.1098 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 58.4208 | 15.93% | CZ 3A | 2.1104 | 0.42372 | 0 | 0.52049 | 0 | 2.1631 | 0 | 1.7902 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.5953 | 15.93% | CZ 3A | 0 | 0 | 0.12267 | 0.0074527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22259 | 15.93% | CZ 3A | 22.0941 | 4.4359 | 13.4077 | 6.2636 | 0 | 22.6454 | 0 | 18.7413 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 135.2518 | 15.93%
CZ 3B | 0.21414 | 0.042897 | 0.11945 | 0.026526 | 0 | 0.21642 | 0 | 0.18719 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2625 | 6.609% | CZ 3B | 7.2147 | 1.4453 | 11.9452 | 1.1134 | 0 | 7.2917 | 0 | 6.3066 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 56.8078 | 6.609% | CZ 3B | 2.1139 | 0.42346 | 0 | 0.22916 | 0 | 2.1365 | 0 | 1.8478 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.3383 | 6.609% | CZ 3B | 0 | 0 | 0.11945 | 0.0033128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21524 | 6.609% | CZ 3B | 22.1305 | 4.4332 | 13.0561 | 2.7611 | 0 | 22.3668 | 0 | 19.3451 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 131.7566 | 6.609%
CZ 3C | 0.21365 | 0.04289 | 0.1225 | 0.0072494 | 0 | 0.1721 | 0 | 0.17953 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1938 | 1.264% | CZ 3C | 7.1982 | 1.445 | 12.2497 | 0.35568 | 0 | 5.7982 | 0 | 6.0488 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 54.5866 | 1.264% | CZ 3C | 2.1091 | 0.4234 | 0 | 0.054974 | 0 | 1.6989 | 0 | 1.7723 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.646 | 1.264% | CZ 3C | 0 | 0 | 0.1225 | 0.0016805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21665 | 1.264% | CZ 3C | 22.08 | 4.4326 | 13.389 | 0.75921 | 0 | 17.7854 | 0 | 18.5542 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 124.6641 | 1.264%
CZ 4A | 0.20965 | 0.042845 | 0.13317 | 0.13296 | 0 | 0.16021 | 0 | 0.17919 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3139 | 18.74% | CZ 4A | 7.0635 | 1.4435 | 13.3167 | 5.5924 | 0 | 5.3977 | 0 | 6.0374 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 60.342 | 18.74% | CZ 4A | 2.0696 | 0.42295 | 0 | 1.1469 | 0 | 1.5815 | 0 | 1.769 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.5774 | 18.74% | CZ 4A | 0 | 0 | 0.13317 | 0.016779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24242 | 18.74% | CZ 4A | 21.6667 | 4.4278 | 14.5551 | 13.8412 | 0 | 16.557 | 0 | 18.5191 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 137.2308 | 18.74%
CZ 4B | 0.21006 | 0.042858 | 0.12991 | 0.057197 | 0 | 0.16663 | 0 | 0.18816 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2507 | 1.192% | CZ 4B | 7.0773 | 1.4439 | 12.9906 | 2.3933 | 0 | 5.6141 | 0 | 6.3396 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 57.3497 | 1.192% | CZ 4B | 2.0737 | 0.42308 | 0 | 0.49522 | 0 | 1.6449 | 0 | 1.8575 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.0818 | 1.192% | CZ 4B | 0 | 0 | 0.12991 | 0.0070315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22941 | 1.192% | CZ 4B | 21.7091 | 4.4292 | 14.1988 | 5.953 | 0 | 17.2207 | 0 | 19.446 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 130.6205 | 1.192%
CZ 4C | 0.21123 | 0.042806 | 0.13673 | 0.072608 | 0 | 0.10376 | 0 | 0.18 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.203 | 2.105% | CZ 4C | 7.1168 | 1.4422 | 13.6732 | 3.1247 | 0 | 3.4958 | 0 | 6.0646 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 56.4081 | 2.105% | CZ 4C | 2.0852 | 0.42256 | 0 | 0.61578 | 0 | 1.0243 | 0 | 1.7769 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.5122 | 2.105% | CZ 4C | 0 | 0 | 0.13673 | 0.01023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23943 | 2.105% | CZ 4C | 21.8303 | 4.4238 | 14.9448 | 7.5647 | 0 | 10.723 | 0 | 18.6026 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 125.7529 | 2.105%
CZ 5A | 0.20996 | 0.042806 | 0.14354 | 0.21554 | 0 | 0.11402 | 0 | 0.17943 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3612 | 20.28% | CZ 5A | 7.0738 | 1.4422 | 14.3542 | 8.9799 | 0 | 3.8416 | 0 | 6.0453 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 63.2279 | 20.28% | CZ 5A | 2.0726 | 0.42256 | 0 | 1.872 | 0 | 1.1256 | 0 | 1.7713 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.8514 | 20.28% | CZ 5A | 0 | 0 | 0.14354 | 0.02591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26192 | 20.28% | CZ 5A | 21.6983 | 4.4238 | 15.6891 | 22.4295 | 0 | 11.7838 | 0 | 18.5434 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 142.2317 | 20.28%
CZ 5B | 0.20997 | 0.042845 | 0.14051 | 0.12387 | 0 | 0.13191 | 0 | 0.18813 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.2931 | 5.437% | CZ 5B | 7.0743 | 1.4435 | 14.0514 | 5.1443 | 0 | 4.4444 | 0 | 6.3385 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 59.9872 | 5.437% | CZ 5B | 2.0728 | 0.42295 | 0 | 1.0782 | 0 | 1.3022 | 0 | 1.8572 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.3207 | 5.437% | CZ 5B | 0 | 0 | 0.14051 | 0.014644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24763 | 5.437% | CZ 5B | 21.6997 | 4.4278 | 15.3582 | 12.8883 | 0 | 13.6329 | 0 | 19.4427 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 135.1134 | 5.437%
CZ 5C | 0.2106 | 0.042793 | 0.14265 | 0.081841 | 0 | 0.083885 | 0 | 0.17821 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.1959 | 0.1861% | CZ 5C | 7.0955 | 1.4418 | 14.2653 | 3.6501 | 0 | 2.8262 | 0 | 6.0042 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 56.7741 | 0.1861% | CZ 5C | 2.079 | 0.42243 | 0 | 0.67499 | 0 | 0.82809 | 0 | 1.7592 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 9.3512 | 0.1861% | CZ 5C | 0 | 0 | 0.14265 | 0.013464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24859 | 0.1861% | CZ 5C | 21.765 | 4.4225 | 15.592 | 8.5381 | 0 | 8.6692 | 0 | 18.4175 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 125.0681 | 0.1861%
CZ 6A | 0.21006 | 0.042838 | 0.15133 | 0.3333 | 0 | 0.11365 | 0 | 0.18062 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.4877 | 4.86% | CZ 6A | 7.0773 | 1.4433 | 15.1334 | 13.7322 | 0 | 3.8291 | 0 | 6.0854 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 68.7916 | 4.86% | CZ 6A | 2.0737 | 0.42288 | 0 | 2.9176 | 0 | 1.1219 | 0 | 1.783 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 11.9065 | 4.86% | CZ 6A | 0 | 0 | 0.15133 | 0.037746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28155 | 4.86% | CZ 6A | 21.7091 | 4.4272 | 16.5408 | 34.6696 | 0 | 11.7454 | 0 | 18.6666 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 155.4225 | 4.86%
CZ 6B | 0.21033 | 0.042806 | 0.14932 | 0.21983 | 0 | 0.097348 | 0 | 0.18478 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3603 | 1.535% | CZ 6B | 7.0863 | 1.4422 | 14.9323 | 9.0851 | 0 | 3.2798 | 0 | 6.2257 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 63.5422 | 1.535% | CZ 6B | 2.0763 | 0.42256 | 0 | 1.9202 | 0 | 0.96099 | 0 | 1.8241 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.7916 | 1.535% | CZ 6B | 0 | 0 | 0.14932 | 0.025316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26711 | 1.535% | CZ 6B | 21.7367 | 4.4238 | 16.321 | 22.8693 | 0 | 10.0606 | 0 | 19.0967 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 142.1719 | 1.535%
CZ 7 | 0.20779 | 0.042825 | 0.16058 | 0.38391 | 0 | 0.09587 | 0 | 0.17985 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.5267 | 0.8923% | CZ 7 | 7.001 | 1.4429 | 16.0584 | 16.1002 | 0 | 3.23 | 0 | 6.0593 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 71.3826 | 0.8923% | CZ 7 | 2.0513 | 0.42276 | 0 | 3.3186 | 0 | 0.94639 | 0 | 1.7754 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 12.1018 | 0.8923% | CZ 7 | 0 | 0 | 0.16058 | 0.04774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.3008 | 0.8923% | CZ 7 | 21.4749 | 4.4258 | 17.5518 | 39.9602 | 0 | 9.9078 | 0 | 18.5865 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 159.5707 | 0.8923%
CZ 8 | 0.21134 | 0.042526 | 0.1731 | 0.53865 | 0 | 0.064658 | 0 | 0.17895 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.6651 | 0.1875% | CZ 8 | 7.1203 | 1.4328 | 17.3098 | 22.6045 | 0 | 2.1784 | 0 | 6.0293 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 78.166 | 0.1875% | CZ 8 | 2.0863 | 0.4198 | 0 | 4.654 | 0 | 0.63828 | 0 | 1.7666 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 13.1523 | 0.1875% | CZ 8 | 0 | 0 | 0.1731 | 0.067206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.33278 | 0.1875% | CZ 8 | 21.841 | 4.3949 | 18.9196 | 56.0681 | 0 | 6.6822 | 0 | 18.4942 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 174.0638 | 0.1875%
US Weighted | 0.2115 | 0.042854 | 0.12971 | 0.11499 | 0 | 0.19522 | 0 | 0.18128 | 0 | 0.00016935 | 0 | 0.16277 | 0 | 0.11102 | 0 | 0.18191 | 1.3314 | 100% | US Weighted | 7.1259 | 1.4438 | 12.9709 | 4.802 | 0 | 6.5772 | 0 | 6.1076 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1289 | 60.5182 | 100% | US Weighted | 2.0879 | 0.42304 | 0 | 0.99699 | 0 | 1.9271 | 0 | 1.7895 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0.18312 | 0 | 1.7958 | 10.812 | 100% | US Weighted | 0 | 0 | 0.12971 | 0.013993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23617 | 100% | US Weighted | 21.8581 | 4.4288 | 14.1772 | 11.9669 | 0 | 20.1749 | 0 | 18.7346 | 0 | 0.017501 | 0 | 16.8222 | 0 | 12.0242 | 0 | 18.7998 | 139.0042 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.27241 | 0.042936 | 0.10559 | 6.5133e-06 | 0 | 0.44765 | 0 | 0.18252 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.5287 | 1.516% | CZ 1A | 9.1781 | 1.4466 | 10.5591 | 0.00021945 | 0 | 15.082 | 0 | 6.1493 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 64.6378 | 1.516% | CZ 1A | 2.6892 | 0.42385 | 0 | 6.4297e-05 | 0 | 4.419 | 0 | 1.8017 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 13.1356 | 1.516% | CZ 1A | 0 | 0 | 0.10559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19806 | 1.516% | CZ 1A | 28.153 | 4.4373 | 11.5411 | 0.00067313 | 0 | 46.2629 | 0 | 18.8624 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 159.1653 | 1.516%
CZ 1B | 0.27241 | 0.042884 | 0.10577 | 0.0048432 | 0 | 0.46833 | 0 | 0.18885 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.5607 | 0% | CZ 1B | 9.1781 | 1.4448 | 10.5771 | 0.20144 | 0 | 15.7788 | 0 | 6.3626 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 65.7653 | 0% | CZ 1B | 2.6892 | 0.42333 | 0 | 0.042115 | 0 | 4.6232 | 0 | 1.8642 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 13.4438 | 0% | CZ 1B | 0 | 0 | 0.10577 | 0.000577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19882 | 0% | CZ 1B | 28.153 | 4.4319 | 11.5608 | 0.50397 | 0 | 48.4001 | 0 | 19.5167 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 162.4744 | 0%
CZ 2A | 0.27241 | 0.042851 | 0.1106 | 0.0089255 | 0 | 0.38236 | 0 | 0.18345 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4782 | 17.53% | CZ 2A | 9.1781 | 1.4437 | 11.0602 | 0.39804 | 0 | 12.8823 | 0 | 6.1809 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.3658 | 17.53% | CZ 2A | 2.6892 | 0.42301 | 0 | 0.073621 | 0 | 3.7745 | 0 | 1.811 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 12.5731 | 17.53% | CZ 2A | 0 | 0 | 0.1106 | 0.0014677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20454 | 17.53% | CZ 2A | 28.153 | 4.4285 | 12.0888 | 0.93116 | 0 | 39.5154 | 0 | 18.9594 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 153.9842 | 17.53%
CZ 2B | 0.27241 | 0.042877 | 0.11152 | 0.0093739 | 0 | 0.30566 | 0 | 0.19145 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4109 | 1.732% | CZ 2B | 9.1781 | 1.4446 | 11.1519 | 0.4066 | 0 | 10.2981 | 0 | 6.4504 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 61.1522 | 1.732% | CZ 2B | 2.6892 | 0.42327 | 0 | 0.079022 | 0 | 3.0174 | 0 | 1.89 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.9006 | 1.732% | CZ 2B | 0 | 0 | 0.11152 | 0.001369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20536 | 1.732% | CZ 2B | 28.153 | 4.4312 | 12.189 | 0.97691 | 0 | 31.5886 | 0 | 19.786 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 147.0327 | 1.732%
CZ 3A | 0.27058 | 0.042923 | 0.12264 | 0.051444 | 0 | 0.24628 | 0 | 0.18287 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.3943 | 15.93% | CZ 3A | 9.1164 | 1.4461 | 12.264 | 2.1851 | 0 | 8.2977 | 0 | 6.1614 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 61.6932 | 15.93% | CZ 3A | 2.6711 | 0.42372 | 0 | 0.44057 | 0 | 2.4312 | 0 | 1.8053 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.5737 | 15.93% | CZ 3A | 0 | 0 | 0.12264 | 0.0068143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22193 | 15.93% | CZ 3A | 27.9638 | 4.4359 | 13.4046 | 5.3571 | 0 | 25.4524 | 0 | 18.8995 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 145.4212 | 15.93%
CZ 3B | 0.2708 | 0.042897 | 0.11942 | 0.021948 | 0 | 0.24386 | 0 | 0.18904 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.3656 | 6.609% | CZ 3B | 9.1239 | 1.4453 | 11.9424 | 0.93455 | 0 | 8.216 | 0 | 6.3692 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 60.2538 | 6.609% | CZ 3B | 2.6733 | 0.42346 | 0 | 0.18762 | 0 | 2.4073 | 0 | 1.8662 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.3596 | 6.609% | CZ 3B | 0 | 0 | 0.11942 | 0.002942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21484 | 6.609% | CZ 3B | 27.9867 | 4.4332 | 13.053 | 2.2858 | 0 | 25.202 | 0 | 19.5369 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 142.4056 | 6.609%
CZ 3C | 0.27241 | 0.04289 | 0.12246 | 0.005297 | 0 | 0.19976 | 0 | 0.18106 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.3015 | 1.264% | CZ 3C | 9.1781 | 1.445 | 12.246 | 0.27186 | 0 | 6.7304 | 0 | 6.1004 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 58.1942 | 1.264% | CZ 3C | 2.6892 | 0.4234 | 0 | 0.038386 | 0 | 1.972 | 0 | 1.7874 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 10.7121 | 1.264% | CZ 3C | 0 | 0 | 0.12246 | 0.0014085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21634 | 1.264% | CZ 3C | 28.153 | 4.4326 | 13.3849 | 0.55581 | 0 | 20.6449 | 0 | 18.7123 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 135.7914 | 1.264%
CZ 4A | 0.26983 | 0.042845 | 0.13314 | 0.12293 | 0 | 0.18012 | 0 | 0.18093 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4074 | 18.74% | CZ 4A | 9.0912 | 1.4435 | 13.3142 | 5.191 | 0 | 6.0685 | 0 | 6.0957 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.4267 | 18.74% | CZ 4A | 2.6637 | 0.42295 | 0 | 1.0572 | 0 | 1.7781 | 0 | 1.7861 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.5098 | 18.74% | CZ 4A | 0 | 0 | 0.13314 | 0.015827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24144 | 18.74% | CZ 4A | 27.8864 | 4.4278 | 14.5525 | 12.7982 | 0 | 18.6147 | 0 | 18.6982 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 146.8858 | 18.74%
CZ 4B | 0.27008 | 0.042858 | 0.12988 | 0.053246 | 0 | 0.18915 | 0 | 0.19001 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.3528 | 1.192% | CZ 4B | 9.0995 | 1.4439 | 12.988 | 2.2228 | 0 | 6.3729 | 0 | 6.4019 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 60.7516 | 1.192% | CZ 4B | 2.6662 | 0.42308 | 0 | 0.46178 | 0 | 1.8673 | 0 | 1.8757 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.0958 | 1.192% | CZ 4B | 0 | 0 | 0.12988 | 0.0064677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22882 | 1.192% | CZ 4B | 27.912 | 4.4292 | 14.1959 | 5.5413 | 0 | 19.5484 | 0 | 19.6372 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 141.172 | 1.192%
CZ 4C | 0.27018 | 0.042806 | 0.13672 | 0.064993 | 0 | 0.12018 | 0 | 0.1811 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.2936 | 2.105% | CZ 4C | 9.1028 | 1.4422 | 13.6716 | 2.821 | 0 | 4.049 | 0 | 6.1015 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 59.4105 | 2.105% | CZ 4C | 2.6671 | 0.42256 | 0 | 0.54762 | 0 | 1.1864 | 0 | 1.7877 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 10.4132 | 2.105% | CZ 4C | 0 | 0 | 0.13672 | 0.0095194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23871 | 2.105% | CZ 4C | 27.9221 | 4.4238 | 14.9431 | 6.7735 | 0 | 12.4199 | 0 | 18.7157 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 135.1061 | 2.105%
CZ 5A | 0.26986 | 0.042806 | 0.14353 | 0.21121 | 0 | 0.1292 | 0 | 0.18123 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4554 | 20.28% | CZ 5A | 9.0921 | 1.4422 | 14.3526 | 8.7943 | 0 | 4.3531 | 0 | 6.1061 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 66.3629 | 20.28% | CZ 5A | 2.664 | 0.42256 | 0 | 1.8351 | 0 | 1.2755 | 0 | 1.7891 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.788 | 20.28% | CZ 5A | 0 | 0 | 0.14353 | 0.025311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26131 | 20.28% | CZ 5A | 27.8891 | 4.4238 | 15.6874 | 21.9783 | 0 | 13.3529 | 0 | 18.7298 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 151.9693 | 20.28%
CZ 5B | 0.27004 | 0.042845 | 0.1405 | 0.12292 | 0 | 0.15022 | 0 | 0.19013 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.3943 | 5.437% | CZ 5B | 9.098 | 1.4435 | 14.0503 | 5.0789 | 0 | 5.0613 | 0 | 6.4058 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.3603 | 5.437% | CZ 5B | 2.6657 | 0.42295 | 0 | 1.0739 | 0 | 1.483 | 0 | 1.8769 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.3242 | 5.437% | CZ 5B | 0 | 0 | 0.1405 | 0.014138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24711 | 5.437% | CZ 5B | 27.9073 | 4.4278 | 15.357 | 12.7879 | 0 | 15.5251 | 0 | 19.6493 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 145.5623 | 5.437%
CZ 5C | 0.27001 | 0.042793 | 0.14264 | 0.078314 | 0 | 0.097361 | 0 | 0.17999 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.2887 | 0.1861% | CZ 5C | 9.0971 | 1.4418 | 14.2642 | 3.4814 | 0 | 3.2803 | 0 | 6.0641 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 59.8514 | 0.1861% | CZ 5C | 2.6655 | 0.42243 | 0 | 0.6476 | 0 | 0.96112 | 0 | 1.7768 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 10.2752 | 0.1861% | CZ 5C | 0 | 0 | 0.14264 | 0.012712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24783 | 0.1861% | CZ 5C | 27.9046 | 4.4225 | 15.5908 | 8.1691 | 0 | 10.0619 | 0 | 18.6013 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 134.6582 | 0.1861%
CZ 6A | 0.26993 | 0.042838 | 0.15132 | 0.33704 | 0 | 0.1286 | 0 | 0.18241 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.5897 | 4.86% | CZ 6A | 9.0945 | 1.4433 | 15.1319 | 13.813 | 0 | 4.3327 | 0 | 6.1458 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 72.1836 | 4.86% | CZ 6A | 2.6647 | 0.42288 | 0 | 2.9613 | 0 | 1.2695 | 0 | 1.8007 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 12.9208 | 4.86% | CZ 6A | 0 | 0 | 0.15132 | 0.037062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28085 | 4.86% | CZ 6A | 27.8965 | 4.4272 | 16.5392 | 35.0525 | 0 | 13.2903 | 0 | 18.8517 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 165.9653 | 4.86%
CZ 6B | 0.27013 | 0.042806 | 0.14931 | 0.22305 | 0 | 0.1115 | 0 | 0.18697 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4614 | 1.535% | CZ 6B | 9.101 | 1.4422 | 14.9312 | 9.1448 | 0 | 3.7567 | 0 | 6.2994 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 66.8978 | 1.535% | CZ 6B | 2.6666 | 0.42256 | 0 | 1.9593 | 0 | 1.1007 | 0 | 1.8457 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.7967 | 1.535% | CZ 6B | 0 | 0 | 0.14931 | 0.024578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26636 | 1.535% | CZ 6B | 27.9167 | 4.4238 | 16.3198 | 23.198 | 0 | 11.5233 | 0 | 19.3229 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 152.6125 | 1.535%
CZ 7 | 0.26981 | 0.042825 | 0.16059 | 0.39992 | 0 | 0.10716 | 0 | 0.18214 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.64 | 0.8923% | CZ 7 | 9.0905 | 1.4429 | 16.0588 | 16.6468 | 0 | 3.6103 | 0 | 6.1366 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 75.2084 | 0.8923% | CZ 7 | 2.6635 | 0.42276 | 0 | 3.4755 | 0 | 1.0578 | 0 | 1.798 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 13.2194 | 0.8923% | CZ 7 | 0 | 0 | 0.16059 | 0.047849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.30091 | 0.8923% | CZ 7 | 27.8844 | 4.4258 | 17.5523 | 41.6153 | 0 | 11.0743 | 0 | 18.8234 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 171.2835 | 0.8923%
CZ 8 | 0.27044 | 0.042526 | 0.17315 | 0.57519 | 0 | 0.072519 | 0 | 0.18162 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.793 | 0.1875% | CZ 8 | 9.1116 | 1.4328 | 17.3151 | 24.0262 | 0 | 2.4433 | 0 | 6.119 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 82.6705 | 0.1875% | CZ 8 | 2.6697 | 0.4198 | 0 | 4.9863 | 0 | 0.71589 | 0 | 1.7929 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 14.3863 | 0.1875% | CZ 8 | 0 | 0 | 0.17315 | 0.070083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.3357 | 0.1875% | CZ 8 | 27.949 | 4.3949 | 18.9254 | 59.8612 | 0 | 7.4946 | 0 | 18.7696 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 187.3026 | 0.1875%
US Weighted | 0.27062 | 0.042854 | 0.12969 | 0.11059 | 0 | 0.21914 | 0 | 0.18327 | 0 | 0.00016935 | 0 | 0.16321 | 0 | 0.11102 | 0 | 0.20319 | 1.4338 | 100% | US Weighted | 9.1178 | 1.4438 | 12.9694 | 4.62 | 0 | 7.3833 | 0 | 6.1748 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.9316 | 100% | US Weighted | 2.6715 | 0.42304 | 0 | 0.95857 | 0 | 2.1633 | 0 | 1.8092 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0.18312 | 0 | 2.0058 | 11.8274 | 100% | US Weighted | 0 | 0 | 0.12969 | 0.013484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23565 | 100% | US Weighted | 27.968 | 4.4288 | 14.1756 | 11.509 | 0 | 22.6477 | 0 | 18.9408 | 0 | 0.017501 | 0 | 16.8673 | 0 | 12.0242 | 0 | 20.999 | 149.5778 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.32434 | 0.062163 | 0.10653 | 6.5133e-06 | 0 | 0.51304 | 0 | 0.19466 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6855 | 1.516% | CZ 1A | 10.9277 | 2.0944 | 10.653 | 0.00021945 | 0 | 17.2853 | 0 | 6.5583 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.9813 | 1.516% | CZ 1A | 3.2018 | 0.61365 | 0 | 6.4297e-05 | 0 | 5.0646 | 0 | 1.9216 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.6738 | 1.516% | CZ 1A | 0 | 0 | 0.10653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.199 | 1.516% | CZ 1A | 33.5198 | 6.4244 | 11.6437 | 0.00067313 | 0 | 53.0211 | 0 | 20.1172 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 175.3706 | 1.516%
CZ 1B | 0.32434 | 0.062085 | 0.10663 | 0.0043789 | 0 | 0.52439 | 0 | 0.19724 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7038 | 0% | CZ 1B | 10.9277 | 2.0918 | 10.6631 | 0.17401 | 0 | 17.6675 | 0 | 6.6455 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.6319 | 0% | CZ 1B | 3.2018 | 0.61288 | 0 | 0.039286 | 0 | 5.1766 | 0 | 1.9471 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.8497 | 0% | CZ 1B | 0 | 0 | 0.10663 | 0.00039929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.1995 | 0% | CZ 1B | 33.5198 | 6.4163 | 11.6548 | 0.45493 | 0 | 54.1937 | 0 | 20.3844 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 177.2676 | 0%
CZ 2A | 0.32434 | 0.062039 | 0.11138 | 0.0086022 | 0 | 0.4352 | 0 | 0.19431 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6206 | 17.53% | CZ 2A | 10.9277 | 2.0902 | 11.1379 | 0.36052 | 0 | 14.6627 | 0 | 6.5465 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.1878 | 17.53% | CZ 2A | 3.2018 | 0.61243 | 0 | 0.074392 | 0 | 4.2962 | 0 | 1.9181 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.975 | 17.53% | CZ 2A | 0 | 0 | 0.11138 | 0.0010662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20492 | 17.53% | CZ 2A | 33.5198 | 6.4116 | 12.1737 | 0.89535 | 0 | 44.9765 | 0 | 20.0808 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 168.7015 | 17.53%
CZ 2B | 0.32434 | 0.062079 | 0.11218 | 0.0088649 | 0 | 0.3566 | 0 | 0.20373 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5525 | 1.732% | CZ 2B | 10.9277 | 2.0915 | 11.2182 | 0.3557 | 0 | 12.0146 | 0 | 6.864 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 65.9341 | 1.732% | CZ 2B | 3.2018 | 0.61282 | 0 | 0.079022 | 0 | 3.5203 | 0 | 2.0112 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.2972 | 1.732% | CZ 2B | 0 | 0 | 0.11218 | 0.00086002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20551 | 1.732% | CZ 2B | 33.5198 | 6.4156 | 12.2615 | 0.92128 | 0 | 36.8539 | 0 | 21.0548 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 161.6706 | 1.732%
CZ 3A | 0.32434 | 0.062137 | 0.12305 | 0.054423 | 0 | 0.28416 | 0 | 0.19162 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5244 | 15.93% | CZ 3A | 10.9277 | 2.0935 | 12.305 | 2.2364 | 0 | 9.5737 | 0 | 6.4561 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 66.0549 | 15.93% | CZ 3A | 3.2018 | 0.6134 | 0 | 0.47728 | 0 | 2.8051 | 0 | 1.8916 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.8613 | 15.93% | CZ 3A | 0 | 0 | 0.12305 | 0.006075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2216 | 15.93% | CZ 3A | 33.5198 | 6.4217 | 13.4494 | 5.6606 | 0 | 29.3666 | 0 | 19.8035 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 158.8654 | 15.93%
CZ 3B | 0.32434 | 0.062098 | 0.11989 | 0.020914 | 0 | 0.28366 | 0 | 0.19885 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4945 | 6.609% | CZ 3B | 10.9277 | 2.0922 | 11.9893 | 0.85754 | 0 | 9.5568 | 0 | 6.6997 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 64.5856 | 6.609% | CZ 3B | 3.2018 | 0.61301 | 0 | 0.1837 | 0 | 2.8002 | 0 | 1.963 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.6337 | 6.609% | CZ 3B | 0 | 0 | 0.11989 | 0.0023058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21467 | 6.609% | CZ 3B | 33.5198 | 6.4176 | 13.1043 | 2.1752 | 0 | 29.3148 | 0 | 20.5507 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 155.7261 | 6.609%
CZ 3C | 0.32434 | 0.062092 | 0.12258 | 0.0049164 | 0 | 0.23434 | 0 | 0.18959 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4226 | 1.264% | CZ 3C | 10.9277 | 2.092 | 12.2579 | 0.22776 | 0 | 7.8952 | 0 | 6.3876 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 62.2505 | 1.264% | CZ 3C | 3.2018 | 0.61295 | 0 | 0.039286 | 0 | 2.3133 | 0 | 1.8716 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 11.911 | 1.264% | CZ 3C | 0 | 0 | 0.12258 | 0.0009368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21599 | 1.264% | CZ 3C | 33.5198 | 6.4169 | 13.3978 | 0.51367 | 0 | 24.2179 | 0 | 19.5935 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 148.3033 | 1.264%
CZ 4A | 0.32434 | 0.06202 | 0.13333 | 0.13609 | 0 | 0.20517 | 0 | 0.18982 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5355 | 18.74% | CZ 4A | 10.9277 | 2.0896 | 13.3331 | 5.5569 | 0 | 6.9125 | 0 | 6.3953 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.6774 | 18.74% | CZ 4A | 3.2018 | 0.61224 | 0 | 1.1988 | 0 | 2.0254 | 0 | 1.8738 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.7841 | 18.74% | CZ 4A | 0 | 0 | 0.13333 | 0.014655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24046 | 18.74% | CZ 4A | 33.5198 | 6.4095 | 14.5731 | 14.1517 | 0 | 21.2036 | 0 | 19.617 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 160.1184 | 18.74%
CZ 4B | 0.32434 | 0.062046 | 0.13012 | 0.052314 | 0 | 0.21806 | 0 | 0.20201 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4736 | 1.192% | CZ 4B | 10.9277 | 2.0904 | 13.0117 | 2.1006 | 0 | 7.3468 | 0 | 6.8061 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 64.7457 | 1.192% | CZ 4B | 3.2018 | 0.6125 | 0 | 0.46609 | 0 | 2.1526 | 0 | 1.9942 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.2993 | 1.192% | CZ 4B | 0 | 0 | 0.13012 | 0.0050987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22769 | 1.192% | CZ 4B | 33.5198 | 6.4122 | 14.2218 | 5.4368 | 0 | 22.5357 | 0 | 20.8771 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 153.6472 | 1.192%
CZ 4C | 0.32434 | 0.061974 | 0.13672 | 0.068682 | 0 | 0.13659 | 0 | 0.18903 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4021 | 2.105% | CZ 4C | 10.9277 | 2.088 | 13.6723 | 2.8482 | 0 | 4.602 | 0 | 6.3687 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 62.9693 | 2.105% | CZ 4C | 3.2018 | 0.61179 | 0 | 0.59848 | 0 | 1.3484 | 0 | 1.866 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 11.4986 | 2.105% | CZ 4C | 0 | 0 | 0.13672 | 0.0080561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23725 | 2.105% | CZ 4C | 33.5198 | 6.4048 | 14.9438 | 7.146 | 0 | 14.1162 | 0 | 19.5356 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 146.31 | 2.105%
CZ 5A | 0.32434 | 0.061974 | 0.14354 | 0.23482 | 0 | 0.14975 | 0 | 0.19009 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5892 | 20.28% | CZ 5A | 10.9277 | 2.088 | 14.3539 | 9.5227 | 0 | 5.0455 | 0 | 6.4043 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.8045 | 20.28% | CZ 5A | 3.2018 | 0.61179 | 0 | 2.0782 | 0 | 1.4783 | 0 | 1.8765 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.1186 | 20.28% | CZ 5A | 0 | 0 | 0.14354 | 0.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26031 | 20.28% | CZ 5A | 33.5198 | 6.4048 | 15.6889 | 24.4122 | 0 | 15.4766 | 0 | 19.6446 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 165.7906 | 20.28%
CZ 5B | 0.32434 | 0.062026 | 0.14049 | 0.12637 | 0 | 0.16942 | 0 | 0.20185 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5092 | 5.437% | CZ 5B | 10.9277 | 2.0898 | 14.0494 | 5.0733 | 0 | 5.708 | 0 | 6.8006 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.1111 | 5.437% | CZ 5B | 3.2018 | 0.6123 | 0 | 1.126 | 0 | 1.6724 | 0 | 1.9926 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.4772 | 5.437% | CZ 5B | 0 | 0 | 0.14049 | 0.012301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24527 | 5.437% | CZ 5B | 33.5198 | 6.4102 | 15.356 | 13.1331 | 0 | 17.5088 | 0 | 20.8603 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 157.4319 | 5.437%
CZ 5C | 0.32434 | 0.061955 | 0.14264 | 0.075243 | 0 | 0.11451 | 0 | 0.18773 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.3911 | 0.1861% | CZ 5C | 10.9277 | 2.0874 | 14.2644 | 3.221 | 0 | 3.8581 | 0 | 6.3248 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 63.1458 | 0.1861% | CZ 5C | 3.2018 | 0.6116 | 0 | 0.64066 | 0 | 1.1304 | 0 | 1.8532 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 11.3097 | 0.1861% | CZ 5C | 0 | 0 | 0.14264 | 0.010344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24546 | 0.1861% | CZ 5C | 33.5198 | 6.4028 | 15.591 | 7.8377 | 0 | 11.8343 | 0 | 19.4009 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 145.2303 | 0.1861%
CZ 6A | 0.32434 | 0.06202 | 0.15135 | 0.37852 | 0 | 0.14925 | 0 | 0.19229 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7425 | 4.86% | CZ 6A | 10.9277 | 2.0896 | 15.1345 | 15.1733 | 0 | 5.0286 | 0 | 6.4787 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 77.2947 | 4.86% | CZ 6A | 3.2018 | 0.61224 | 0 | 3.3763 | 0 | 1.4734 | 0 | 1.8983 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.4341 | 4.86% | CZ 6A | 0 | 0 | 0.15135 | 0.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28032 | 4.86% | CZ 6A | 33.5198 | 6.4095 | 16.542 | 39.3362 | 0 | 15.4248 | 0 | 19.8728 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 181.7489 | 4.86%
CZ 6B | 0.32434 | 0.061968 | 0.14932 | 0.24141 | 0 | 0.12688 | 0 | 0.19718 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5858 | 1.535% | CZ 6B | 10.9277 | 2.0878 | 14.9316 | 9.6594 | 0 | 4.2748 | 0 | 6.6435 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.9872 | 1.535% | CZ 6B | 3.2018 | 0.61173 | 0 | 2.156 | 0 | 1.2525 | 0 | 1.9465 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.0407 | 1.535% | CZ 6B | 0 | 0 | 0.14932 | 0.02301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2648 | 1.535% | CZ 6B | 33.5198 | 6.4042 | 16.3202 | 25.0864 | 0 | 13.1126 | 0 | 20.3783 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 165.4652 | 1.535%
CZ 7 | 0.32434 | 0.062 | 0.1606 | 0.42791 | 0 | 0.12573 | 0 | 0.19222 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7775 | 0.8923% | CZ 7 | 10.9277 | 2.0889 | 16.0601 | 17.4799 | 0 | 4.2359 | 0 | 6.4763 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 79.7312 | 0.8923% | CZ 7 | 3.2018 | 0.61205 | 0 | 3.7682 | 0 | 1.2411 | 0 | 1.8975 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.5928 | 0.8923% | CZ 7 | 0 | 0 | 0.1606 | 0.046191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29926 | 0.8923% | CZ 7 | 33.5198 | 6.4075 | 17.5537 | 44.4981 | 0 | 12.9934 | 0 | 19.8654 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 185.4817 | 0.8923%
CZ 8 | 0.32434 | 0.061571 | 0.17316 | 0.58356 | 0 | 0.083019 | 0 | 0.18969 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.9001 | 0.1875% | CZ 8 | 10.9277 | 2.0744 | 17.3162 | 24.1476 | 0 | 2.797 | 0 | 6.3909 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 86.1162 | 0.1875% | CZ 8 | 3.2018 | 0.6078 | 0 | 5.0928 | 0 | 0.81954 | 0 | 1.8725 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 15.4666 | 0.1875% | CZ 8 | 0 | 0 | 0.17316 | 0.06766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.33329 | 0.1875% | CZ 8 | 33.5198 | 6.3631 | 18.9266 | 60.7119 | 0 | 8.5797 | 0 | 19.6036 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 198.3484 | 0.1875%
US Weighted | 0.32434 | 0.06204 | 0.13 | 0.12099 | 0 | 0.25144 | 0 | 0.19289 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5664 | 100% | US Weighted | 10.9277 | 2.0902 | 12.9996 | 4.9113 | 0 | 8.4713 | 0 | 6.4987 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.3612 | 100% | US Weighted | 3.2018 | 0.61244 | 0 | 1.0701 | 0 | 2.4821 | 0 | 1.9041 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.1426 | 100% | US Weighted | 0 | 0 | 0.13 | 0.012592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23506 | 100% | US Weighted | 33.5198 | 6.4116 | 14.2086 | 12.5787 | 0 | 25.985 | 0 | 19.9344 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 163.2818 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.32434 | 0.062163 | 0.10653 | 6.5133e-06 | 0 | 0.57204 | 0 | 0.19466 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7445 | 1.516% | CZ 1A | 10.9277 | 2.0944 | 10.6535 | 0.00021945 | 0 | 19.273 | 0 | 6.5586 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 71.9697 | 1.516% | CZ 1A | 3.2018 | 0.61365 | 0 | 6.4297e-05 | 0 | 5.647 | 0 | 1.9217 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 15.2562 | 1.516% | CZ 1A | 0 | 0 | 0.10653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19901 | 1.516% | CZ 1A | 33.5198 | 6.4244 | 11.6442 | 0.00067313 | 0 | 59.1183 | 0 | 20.1178 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 181.4689 | 1.516%
CZ 1B | 0.32434 | 0.062085 | 0.10664 | 0.01043 | 0 | 0.59207 | 0 | 0.19746 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7777 | 0% | CZ 1B | 10.9277 | 2.0918 | 10.6635 | 0.50401 | 0 | 19.948 | 0 | 6.6527 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.2501 | 0% | CZ 1B | 3.2018 | 0.61288 | 0 | 0.080243 | 0 | 5.8448 | 0 | 1.9492 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 15.561 | 0% | CZ 1B | 0 | 0 | 0.10664 | 0.0023014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20141 | 0% | CZ 1B | 33.5198 | 6.4163 | 11.6553 | 1.0916 | 0 | 61.1888 | 0 | 20.4066 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 184.9221 | 0%
CZ 2A | 0.32434 | 0.062039 | 0.1114 | 0.023281 | 0 | 0.49075 | 0 | 0.19382 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6904 | 17.53% | CZ 2A | 10.9277 | 2.0902 | 11.1398 | 1.1015 | 0 | 16.5343 | 0 | 6.5302 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.7862 | 17.53% | CZ 2A | 3.2018 | 0.61243 | 0 | 0.1826 | 0 | 4.8446 | 0 | 1.9134 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.6268 | 17.53% | CZ 2A | 0 | 0 | 0.1114 | 0.0047827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20865 | 17.53% | CZ 2A | 33.5198 | 6.4116 | 12.1759 | 2.4344 | 0 | 50.7176 | 0 | 20.031 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 175.934 | 17.53%
CZ 2B | 0.32434 | 0.062079 | 0.11221 | 0.025756 | 0 | 0.3925 | 0 | 0.2035 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6051 | 1.732% | CZ 2B | 10.9277 | 2.0915 | 11.2208 | 1.1875 | 0 | 13.224 | 0 | 6.8561 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.97 | 1.732% | CZ 2B | 3.2018 | 0.61282 | 0 | 0.20665 | 0 | 3.8746 | 0 | 2.0088 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.7768 | 1.732% | CZ 2B | 0 | 0 | 0.11221 | 0.0048222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2095 | 1.732% | CZ 2B | 33.5198 | 6.4156 | 12.2643 | 2.6905 | 0 | 40.5635 | 0 | 21.0306 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 167.1281 | 1.732%
CZ 3A | 0.32434 | 0.062137 | 0.1231 | 0.10806 | 0 | 0.31118 | 0 | 0.19335 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6069 | 15.93% | CZ 3A | 10.9277 | 2.0935 | 12.3096 | 4.9482 | 0 | 10.4842 | 0 | 6.5144 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.7401 | 15.93% | CZ 3A | 3.2018 | 0.6134 | 0 | 0.87207 | 0 | 3.0719 | 0 | 1.9087 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.5399 | 15.93% | CZ 3A | 0 | 0 | 0.1231 | 0.019719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23529 | 15.93% | CZ 3A | 33.5198 | 6.4217 | 13.4544 | 11.2849 | 0 | 32.1595 | 0 | 19.9825 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 167.4666 | 15.93%
CZ 3B | 0.32434 | 0.062098 | 0.11994 | 0.053273 | 0 | 0.30988 | 0 | 0.20093 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5552 | 6.609% | CZ 3B | 10.9277 | 2.0922 | 11.9937 | 2.5321 | 0 | 10.4405 | 0 | 6.7697 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.2183 | 6.609% | CZ 3B | 3.2018 | 0.61301 | 0 | 0.41613 | 0 | 3.0591 | 0 | 1.9835 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.1456 | 6.609% | CZ 3B | 0 | 0 | 0.11994 | 0.011119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22353 | 6.609% | CZ 3B | 33.5198 | 6.4176 | 13.1091 | 5.5718 | 0 | 32.0255 | 0 | 20.7654 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 162.053 | 6.609%
CZ 3C | 0.32434 | 0.062092 | 0.12264 | 0.02071 | 0 | 0.24798 | 0 | 0.19462 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4571 | 1.264% | CZ 3C | 10.9277 | 2.092 | 12.264 | 1.0975 | 0 | 8.3547 | 0 | 6.5572 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 63.7555 | 1.264% | CZ 3C | 3.2018 | 0.61295 | 0 | 0.14493 | 0 | 2.4479 | 0 | 1.9213 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.201 | 1.264% | CZ 3C | 0 | 0 | 0.12264 | 0.0060289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22114 | 1.264% | CZ 3C | 33.5198 | 6.4169 | 13.4046 | 2.1762 | 0 | 25.6274 | 0 | 20.1138 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 151.9024 | 1.264%
CZ 4A | 0.32434 | 0.06202 | 0.13342 | 0.24724 | 0 | 0.21327 | 0 | 0.19191 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6569 | 18.74% | CZ 4A | 10.9277 | 2.0896 | 13.3419 | 11.1582 | 0 | 7.1853 | 0 | 6.4657 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.6307 | 18.74% | CZ 4A | 3.2018 | 0.61224 | 0 | 2.0196 | 0 | 2.1053 | 0 | 1.8945 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.7055 | 18.74% | CZ 4A | 0 | 0 | 0.13342 | 0.042652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26854 | 18.74% | CZ 4A | 33.5198 | 6.4095 | 14.5827 | 25.8055 | 0 | 22.0403 | 0 | 19.8331 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 172.8347 | 18.74%
CZ 4B | 0.32434 | 0.062046 | 0.1302 | 0.11749 | 0 | 0.22281 | 0 | 0.20482 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.5464 | 1.192% | CZ 4B | 10.9277 | 2.0904 | 13.0198 | 5.4786 | 0 | 7.5068 | 0 | 6.9009 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.3865 | 1.192% | CZ 4B | 3.2018 | 0.6125 | 0 | 0.93353 | 0 | 2.1995 | 0 | 2.022 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.8414 | 1.192% | CZ 4B | 0 | 0 | 0.1302 | 0.022924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24559 | 1.192% | CZ 4B | 33.5198 | 6.4122 | 14.2307 | 12.2788 | 0 | 23.0264 | 0 | 21.1679 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 161.2796 | 1.192%
CZ 4C | 0.32434 | 0.061974 | 0.13682 | 0.15426 | 0 | 0.12593 | 0 | 0.19083 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4789 | 2.105% | CZ 4C | 10.9277 | 2.088 | 13.6819 | 7.3041 | 0 | 4.2428 | 0 | 6.4293 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.1362 | 2.105% | CZ 4C | 3.2018 | 0.61179 | 0 | 1.2092 | 0 | 1.2431 | 0 | 1.8838 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 12.0218 | 2.105% | CZ 4C | 0 | 0 | 0.13682 | 0.031772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26106 | 2.105% | CZ 4C | 33.5198 | 6.4048 | 14.9544 | 16.1316 | 0 | 13.0143 | 0 | 19.7214 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 154.39 | 2.105%
CZ 5A | 0.32434 | 0.061974 | 0.14359 | 0.38443 | 0 | 0.14982 | 0 | 0.19075 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7396 | 20.28% | CZ 5A | 10.9277 | 2.088 | 14.359 | 16.9513 | 0 | 5.0477 | 0 | 6.4267 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 78.2628 | 20.28% | CZ 5A | 3.2018 | 0.61179 | 0 | 3.1995 | 0 | 1.479 | 0 | 1.883 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.2472 | 20.28% | CZ 5A | 0 | 0 | 0.14359 | 0.060315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29638 | 20.28% | CZ 5A | 33.5198 | 6.4048 | 15.6944 | 40.0881 | 0 | 15.4833 | 0 | 19.7133 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 181.5474 | 20.28%
CZ 5B | 0.32434 | 0.062026 | 0.14055 | 0.23375 | 0 | 0.16952 | 0 | 0.20279 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6177 | 5.437% | CZ 5B | 10.9277 | 2.0898 | 14.0551 | 10.4969 | 0 | 5.7115 | 0 | 6.8324 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 72.5758 | 5.437% | CZ 5B | 3.2018 | 0.6123 | 0 | 1.9173 | 0 | 1.6735 | 0 | 2.0019 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.2788 | 5.437% | CZ 5B | 0 | 0 | 0.14055 | 0.039532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27256 | 5.437% | CZ 5B | 33.5198 | 6.4102 | 15.3623 | 24.3929 | 0 | 17.5196 | 0 | 20.9579 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 168.8064 | 5.437%
CZ 5C | 0.32434 | 0.061955 | 0.14271 | 0.17384 | 0 | 0.10032 | 0 | 0.18829 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.4762 | 0.1861% | CZ 5C | 10.9277 | 2.0874 | 14.2708 | 8.3968 | 0 | 3.3801 | 0 | 6.3439 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.8691 | 0.1861% | CZ 5C | 3.2018 | 0.6116 | 0 | 1.338 | 0 | 0.99037 | 0 | 1.8588 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 11.8727 | 0.1861% | CZ 5C | 0 | 0 | 0.14271 | 0.038301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27348 | 0.1861% | CZ 5C | 33.5198 | 6.4028 | 15.598 | 18.1942 | 0 | 10.3682 | 0 | 19.4595 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 154.1862 | 0.1861%
CZ 6A | 0.32434 | 0.06202 | 0.15141 | 0.57657 | 0 | 0.15153 | 0 | 0.19306 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.9436 | 4.86% | CZ 6A | 10.9277 | 2.0896 | 15.1407 | 24.9967 | 0 | 5.1054 | 0 | 6.5046 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 87.227 | 4.86% | CZ 6A | 3.2018 | 0.61224 | 0 | 4.8622 | 0 | 1.4959 | 0 | 1.9058 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 15.9501 | 4.86% | CZ 6A | 0 | 0 | 0.15141 | 0.084021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.3279 | 4.86% | CZ 6A | 33.5198 | 6.4095 | 16.5488 | 60.0862 | 0 | 15.6604 | 0 | 19.9522 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 202.8206 | 4.86%
CZ 6B | 0.32434 | 0.061968 | 0.14939 | 0.40201 | 0 | 0.12382 | 0 | 0.19812 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.7444 | 1.535% | CZ 6B | 10.9277 | 2.0878 | 14.9391 | 17.7005 | 0 | 4.1719 | 0 | 6.6749 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 78.9641 | 1.535% | CZ 6B | 3.2018 | 0.61173 | 0 | 3.3498 | 0 | 1.2224 | 0 | 1.9557 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 14.2135 | 1.535% | CZ 6B | 0 | 0 | 0.14939 | 0.062676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.30454 | 1.535% | CZ 6B | 33.5198 | 6.4042 | 16.3284 | 41.9199 | 0 | 12.7969 | 0 | 20.4746 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 182.0874 | 1.535%
CZ 7 | 0.32434 | 0.062 | 0.16065 | 0.68835 | 0 | 0.12455 | 0 | 0.19279 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 2.0374 | 0.8923% | CZ 7 | 10.9277 | 2.0889 | 16.065 | 30.0387 | 0 | 4.1964 | 0 | 6.4954 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 92.2744 | 0.8923% | CZ 7 | 3.2018 | 0.61205 | 0 | 5.7758 | 0 | 1.2296 | 0 | 1.9031 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 16.5944 | 0.8923% | CZ 7 | 0 | 0 | 0.16065 | 0.10326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.35638 | 0.8923% | CZ 7 | 33.5198 | 6.4075 | 17.559 | 71.753 | 0 | 12.8723 | 0 | 19.924 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 212.6793 | 0.8923%
CZ 8 | 0.32434 | 0.061571 | 0.17319 | 0.87536 | 0 | 0.077893 | 0 | 0.18957 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 2.1866 | 0.1875% | CZ 8 | 10.9277 | 2.0744 | 17.3192 | 38.8114 | 0 | 2.6243 | 0 | 6.387 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 100.6064 | 0.1875% | CZ 8 | 3.2018 | 0.6078 | 0 | 7.2539 | 0 | 0.76893 | 0 | 1.8714 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 17.5759 | 0.1875% | CZ 8 | 0 | 0 | 0.17319 | 0.14054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.4062 | 0.1875% | CZ 8 | 33.5198 | 6.3631 | 18.9299 | 91.3022 | 0 | 8.05 | 0 | 19.5914 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 228.4002 | 0.1875%
US Weighted | 0.32434 | 0.06204 | 0.13005 | 0.20947 | 0 | 0.27029 | 0 | 0.19398 | 0 | 0.00016935 | 0 | 0.16879 | 0 | 0.11102 | 0 | 0.20473 | 1.6749 | 100% | US Weighted | 10.9277 | 2.0902 | 13.0049 | 9.3443 | 0 | 9.1065 | 0 | 6.5356 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.4716 | 100% | US Weighted | 3.2018 | 0.61244 | 0 | 1.7273 | 0 | 2.6682 | 0 | 1.9149 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0.18312 | 0 | 2.021 | 13.9968 | 100% | US Weighted | 0 | 0 | 0.13005 | 0.034491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25701 | 100% | US Weighted | 33.5198 | 6.4116 | 14.2143 | 21.853 | 0 | 27.9335 | 0 | 20.0476 | 0 | 0.017501 | 0 | 17.4442 | 0 | 12.0242 | 0 | 21.1578 | 174.6234 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 43202 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 43202 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1338 | 0.033257 | 0.008315 | -1.954e-05 | 0 | 0.22435 | 0 | 0.074688 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50323 | 1.516% | CZ 1A | 4.5081 | 1.1205 | 0.8315 | -0.00065834 | 0 | 7.5588 | 0 | 2.5164 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 17.506 | 1.516% | CZ 1A | 1.3209 | 0.3283 | 0 | -0.00019289 | 0 | 2.2147 | 0 | 0.7373 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.8856 | 1.516% | CZ 1A | 0 | 0 | 0.008315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008315 | 1.516% | CZ 1A | 13.8281 | 3.437 | 0.90882 | -0.0020194 | 0 | 23.186 | 0 | 7.7188 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.0566 | 1.516%
CZ 1B | 0.13452 | 0.033211 | 0.0060969 | 0.0066222 | 0 | 0.2256 | 0 | 0.072187 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50707 | 0% | CZ 1B | 4.5322 | 1.119 | 0.60969 | 0.33615 | 0 | 7.6009 | 0 | 2.4321 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 17.6015 | 0% | CZ 1B | 1.3279 | 0.32785 | 0 | 0.048545 | 0 | 2.2271 | 0 | 0.71261 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.9287 | 0% | CZ 1B | 0 | 0 | 0.0060969 | 0.0017047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078016 | 0% | CZ 1B | 13.9022 | 3.4323 | 0.66639 | 0.69453 | 0 | 23.3152 | 0 | 7.4603 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.4508 | 0%
CZ 2A | 0.13485 | 0.033185 | 0.0052106 | 0.016601 | 0 | 0.1937 | 0 | 0.075652 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.48804 | 17.53% | CZ 2A | 4.5434 | 1.1181 | 0.52106 | 0.78421 | 0 | 6.5261 | 0 | 2.5489 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 17.0132 | 17.53% | CZ 2A | 1.3312 | 0.3276 | 0 | 0.1304 | 0 | 1.9121 | 0 | 0.74681 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.7328 | 17.53% | CZ 2A | 0 | 0 | 0.0052106 | 0.0033918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086024 | 17.53% | CZ 2A | 13.9365 | 3.4296 | 0.56951 | 1.7358 | 0 | 20.0182 | 0 | 7.8184 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 50.488 | 17.53%
CZ 2B | 0.13321 | 0.033211 | 0.0048464 | 0.018337 | 0 | 0.15107 | 0 | 0.078407 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.44792 | 1.732% | CZ 2B | 4.4881 | 1.119 | 0.48464 | 0.85158 | 0 | 5.0898 | 0 | 2.6417 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 15.6462 | 1.732% | CZ 2B | 1.315 | 0.32785 | 0 | 0.14621 | 0 | 1.4913 | 0 | 0.77401 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.339 | 1.732% | CZ 2B | 0 | 0 | 0.0048464 | 0.0035256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008372 | 1.732% | CZ 2B | 13.7669 | 3.4323 | 0.52971 | 1.916 | 0 | 15.6126 | 0 | 8.1031 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 46.3406 | 1.732%
CZ 3A | 0.13399 | 0.033238 | 0.0025208 | 0.06797 | 0 | 0.11484 | 0 | 0.07519 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.45658 | 15.93% | CZ 3A | 4.5142 | 1.1198 | 0.25208 | 3.1035 | 0 | 3.869 | 0 | 2.5333 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 16.3634 | 15.93% | CZ 3A | 1.3227 | 0.32811 | 0 | 0.54987 | 0 | 1.1336 | 0 | 0.74225 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.3612 | 15.93% | CZ 3A | 0 | 0 | 0.0025208 | 0.012268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014789 | 15.93% | CZ 3A | 13.847 | 3.435 | 0.27552 | 7.0975 | 0 | 11.868 | 0 | 7.7706 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 47.2735 | 15.93%
CZ 3B | 0.13376 | 0.033218 | 0.0032185 | 0.036385 | 0 | 0.11368 | 0 | 0.076655 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.42576 | 6.609% | CZ 3B | 4.5067 | 1.1192 | 0.32185 | 1.7464 | 0 | 3.8302 | 0 | 2.5827 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 15.0785 | 6.609% | CZ 3B | 1.3205 | 0.32792 | 0 | 0.28169 | 0 | 1.1222 | 0 | 0.75672 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.0937 | 6.609% | CZ 3B | 0 | 0 | 0.0032185 | 0.0078498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011068 | 6.609% | CZ 3B | 13.8241 | 3.433 | 0.35178 | 3.807 | 0 | 11.7488 | 0 | 7.9221 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 44.0666 | 6.609%
CZ 3C | 0.13421 | 0.033211 | 0.00038613 | 0.015409 | 0 | 0.083032 | 0 | 0.078538 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.37362 | 1.264% | CZ 3C | 4.5219 | 1.119 | 0.038613 | 0.81096 | 0 | 2.7975 | 0 | 2.6461 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 12.9055 | 1.264% | CZ 3C | 1.3249 | 0.32785 | 0 | 0.10866 | 0 | 0.81966 | 0 | 0.7753 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 3.641 | 1.264% | CZ 3C | 0 | 0 | 0.00038613 | 0.004401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047871 | 1.264% | CZ 3C | 13.8705 | 3.4323 | 0.042204 | 1.6186 | 0 | 8.5811 | 0 | 8.1166 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 38.6412 | 1.264%
CZ 4A | 0.13639 | 0.033172 | 0.00053093 | 0.16369 | 0 | 0.063069 | 0 | 0.076037 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50172 | 18.74% | CZ 4A | 4.5952 | 1.1176 | 0.053093 | 7.2705 | 0 | 2.1249 | 0 | 2.5618 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 18.6945 | 18.74% | CZ 4A | 1.3464 | 0.32747 | 0 | 1.3545 | 0 | 0.62259 | 0 | 0.75061 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.6862 | 18.74% | CZ 4A | 0 | 0 | 0.00053093 | 0.026476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027007 | 18.74% | CZ 4A | 14.0953 | 3.4283 | 0.05803 | 17.074 | 0 | 6.5179 | 0 | 7.8581 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.0116 | 18.74%
CZ 4B | 0.13595 | 0.033192 | 0.00085563 | 0.084703 | 0 | 0.061694 | 0 | 0.079508 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.42474 | 1.192% | CZ 4B | 4.5805 | 1.1183 | 0.085563 | 3.9437 | 0 | 2.0786 | 0 | 2.6788 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 15.4569 | 1.192% | CZ 4B | 1.3421 | 0.32766 | 0 | 0.6739 | 0 | 0.60903 | 0 | 0.78488 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.0222 | 1.192% | CZ 4B | 0 | 0 | 0.00085563 | 0.016437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017292 | 1.192% | CZ 4B | 14.0502 | 3.4303 | 0.09352 | 8.8516 | 0 | 6.3759 | 0 | 8.2169 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 43.9984 | 1.192%
CZ 4C | 0.13494 | 0.033153 | 0.00022159 | 0.11159 | 0 | 0.017983 | 0 | 0.074623 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.40134 | 2.105% | CZ 4C | 4.5462 | 1.117 | 0.022159 | 5.226 | 0 | 0.60589 | 0 | 2.5142 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 15.0029 | 2.105% | CZ 4C | 1.332 | 0.32727 | 0 | 0.88332 | 0 | 0.17753 | 0 | 0.73666 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 3.7415 | 2.105% | CZ 4C | 0 | 0 | 0.00022159 | 0.022113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022334 | 2.105% | CZ 4C | 13.9452 | 3.4262 | 0.024219 | 11.6644 | 0 | 1.8585 | 0 | 7.712 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 41.6105 | 2.105%
CZ 5A | 0.1361 | 0.033153 | 0.00023256 | 0.24368 | 0 | 0.038396 | 0 | 0.074988 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.55538 | 20.28% | CZ 5A | 4.5853 | 1.117 | 0.023256 | 10.5409 | 0 | 1.2936 | 0 | 2.5265 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 21.058 | 20.28% | CZ 5A | 1.3435 | 0.32727 | 0 | 2.0585 | 0 | 0.37903 | 0 | 0.74026 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 5.1333 | 20.28% | CZ 5A | 0 | 0 | 0.00023256 | 0.035151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035384 | 20.28% | CZ 5A | 14.065 | 3.4262 | 0.025418 | 25.3929 | 0 | 3.9681 | 0 | 7.7497 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 57.6074 | 20.28%
CZ 5B | 0.13605 | 0.033179 | 0.00019745 | 0.15755 | 0 | 0.040213 | 0 | 0.077834 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.47386 | 5.437% | CZ 5B | 4.5838 | 1.1179 | 0.019745 | 7.0006 | 0 | 1.3549 | 0 | 2.6224 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 17.6706 | 5.437% | CZ 5B | 1.343 | 0.32753 | 0 | 1.3034 | 0 | 0.39697 | 0 | 0.76835 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.4239 | 5.437% | CZ 5B | 0 | 0 | 0.00019745 | 0.025522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025719 | 5.437% | CZ 5B | 14.0603 | 3.4289 | 0.021582 | 16.4346 | 0 | 4.1559 | 0 | 8.0439 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 49.1251 | 5.437%
CZ 5C | 0.13551 | 0.03314 | 0.00018429 | 0.12753 | 0 | 0.0076922 | 0 | 0.073718 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.40661 | 0.1861% | CZ 5C | 4.5656 | 1.1165 | 0.018429 | 6.0036 | 0 | 0.25916 | 0 | 2.4837 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 15.4185 | 0.1861% | CZ 5C | 1.3377 | 0.32715 | 0 | 1.0048 | 0 | 0.075935 | 0 | 0.72772 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 3.7579 | 0.1861% | CZ 5C | 0 | 0 | 0.00018429 | 0.025743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025928 | 0.1861% | CZ 5C | 14.0045 | 3.4249 | 0.020143 | 13.3328 | 0 | 0.79497 | 0 | 7.6185 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 42.1756 | 0.1861%
CZ 6A | 0.13599 | 0.033179 | 0.00028082 | 0.34819 | 0 | 0.041868 | 0 | 0.075587 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.66393 | 4.86% | CZ 6A | 4.5816 | 1.1179 | 0.028082 | 14.857 | 0 | 1.4106 | 0 | 2.5467 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 25.5133 | 4.86% | CZ 6A | 1.3424 | 0.32753 | 0 | 2.9719 | 0 | 0.4133 | 0 | 0.74617 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 6.0859 | 4.86% | CZ 6A | 0 | 0 | 0.00028082 | 0.047141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047422 | 4.86% | CZ 6A | 14.0536 | 3.4289 | 0.030694 | 36.2652 | 0 | 4.3269 | 0 | 7.8117 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 68.8969 | 4.86%
CZ 6B | 0.1357 | 0.033146 | 0.00026546 | 0.2585 | 0 | 0.025695 | 0 | 0.076818 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.55896 | 1.535% | CZ 6B | 4.5719 | 1.1168 | 0.026546 | 11.243 | 0 | 0.86571 | 0 | 2.5881 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 21.3836 | 1.535% | CZ 6B | 1.3396 | 0.32721 | 0 | 2.1747 | 0 | 0.25365 | 0 | 0.75832 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 5.1381 | 1.535% | CZ 6B | 0 | 0 | 0.00026546 | 0.038209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038475 | 1.535% | CZ 6B | 14.024 | 3.4256 | 0.029015 | 26.9429 | 0 | 2.6555 | 0 | 7.9389 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 57.9958 | 1.535%
CZ 7 | 0.13649 | 0.033166 | 0.00029179 | 0.42607 | 0 | 0.030241 | 0 | 0.076343 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.73143 | 0.8923% | CZ 7 | 4.5985 | 1.1174 | 0.029179 | 18.0882 | 0 | 1.0189 | 0 | 2.5721 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 28.3957 | 0.8923% | CZ 7 | 1.3474 | 0.3274 | 0 | 3.6502 | 0 | 0.29853 | 0 | 0.75363 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 6.6618 | 0.8923% | CZ 7 | 0 | 0 | 0.00029179 | 0.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056592 | 0.8923% | CZ 7 | 14.1054 | 3.4276 | 0.031893 | 44.3679 | 0 | 3.1253 | 0 | 7.8898 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 75.9278 | 0.8923%
CZ 8 | 0.13501 | 0.032938 | 0.00038613 | 0.52153 | 0 | 0.0089754 | 0 | 0.074578 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.80225 | 0.1875% | CZ 8 | 4.5487 | 1.1097 | 0.038613 | 22.5514 | 0 | 0.3024 | 0 | 2.5126 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 32.035 | 0.1875% | CZ 8 | 1.3328 | 0.32515 | 0 | 4.4069 | 0 | 0.088602 | 0 | 0.73621 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 7.1742 | 0.1875% | CZ 8 | 0 | 0 | 0.00038613 | 0.075109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075495 | 0.1875% | CZ 8 | 13.9526 | 3.404 | 0.042204 | 54.345 | 0 | 0.92757 | 0 | 7.7073 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 83.3588 | 0.1875%
US Weighted | 0.13529 | 0.033186 | 0.0019364 | 0.13458 | 0 | 0.092475 | 0 | 0.07581 | 0 | 0 | 0 | 0.0060183 | 0 | 0 | 0 | 0.022816 | 0.50211 | 100% | US Weighted | 4.5583 | 1.1181 | 0.19364 | 5.9194 | 0 | 3.1156 | 0 | 2.5542 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76872 | 18.4307 | 100% | US Weighted | 1.3356 | 0.3276 | 0 | 1.1222 | 0 | 0.91288 | 0 | 0.74837 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.22523 | 4.7313 | 100% | US Weighted | 0 | 0 | 0.0019364 | 0.020892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022828 | 100% | US Weighted | 13.9822 | 3.4297 | 0.21165 | 14.0323 | 0 | 9.5569 | 0 | 7.8347 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.358 | 52.0274 | 100%
Building Type: | Small Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 43202 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 43202 | [17 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 41.25% | 53.5% | 7.805% | -300% | 0% | 39.22% | 0% | 38.37% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.85% | 1.516% | CZ 1A | 41.25% | 53.5% | 7.805% | -300% | 0% | 39.22% | 0% | 38.37% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 24.32% | 1.516% | CZ 1A | 41.25% | 53.5% | 0% | -300% | 0% | 39.22% | 0% | 38.37% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 32.02% | 1.516% | CZ 1A | 0% | 0% | 7.805% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.178% | 1.516% | CZ 1A | 41.25% | 53.5% | 7.805% | -300% | 0% | 39.22% | 0% | 38.37% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.69% | 1.516%
CZ 1B | 41.47% | 53.49% | 5.718% | 63.49% | 0% | 38.1% | 0% | 36.56% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.52% | 0% | CZ 1B | 41.47% | 53.49% | 5.718% | 66.69% | 0% | 38.1% | 0% | 36.56% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 24.03% | 0% | CZ 1B | 41.47% | 53.49% | 0% | 60.5% | 0% | 38.1% | 0% | 36.56% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.67% | 0% | CZ 1B | 0% | 0% | 5.718% | 74.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.874% | 0% | CZ 1B | 41.47% | 53.49% | 5.718% | 63.62% | 0% | 38.1% | 0% | 36.56% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.36% | 0%
CZ 2A | 41.58% | 53.49% | 4.677% | 71.31% | 0% | 39.47% | 0% | 39.03% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.87% | 17.53% | CZ 2A | 41.58% | 53.49% | 4.677% | 71.2% | 0% | 39.47% | 0% | 39.03% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 24.03% | 17.53% | CZ 2A | 41.58% | 53.49% | 0% | 71.41% | 0% | 39.47% | 0% | 39.03% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 32.36% | 17.53% | CZ 2A | 0% | 0% | 4.677% | 70.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.123% | 17.53% | CZ 2A | 41.58% | 53.49% | 4.677% | 71.3% | 0% | 39.47% | 0% | 39.03% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.7% | 17.53%
CZ 2B | 41.07% | 53.5% | 4.319% | 71.19% | 0% | 38.49% | 0% | 38.53% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.91% | 1.732% | CZ 2B | 41.07% | 53.5% | 4.319% | 71.71% | 0% | 38.49% | 0% | 38.53% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 23.02% | 1.732% | CZ 2B | 41.07% | 53.5% | 0% | 70.75% | 0% | 38.49% | 0% | 38.53% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.5% | 1.732% | CZ 2B | 0% | 0% | 4.319% | 73.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.996% | 1.732% | CZ 2B | 41.07% | 53.5% | 4.319% | 71.22% | 0% | 38.49% | 0% | 38.53% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.73% | 1.732%
CZ 3A | 41.31% | 53.49% | 2.048% | 62.9% | 0% | 36.9% | 0% | 38.89% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.41% | 15.93% | CZ 3A | 41.31% | 53.49% | 2.048% | 62.72% | 0% | 36.9% | 0% | 38.89% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 23.46% | 15.93% | CZ 3A | 41.31% | 53.49% | 0% | 63.05% | 0% | 36.9% | 0% | 38.89% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 32.21% | 15.93% | CZ 3A | 0% | 0% | 2.048% | 62.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.286% | 15.93% | CZ 3A | 41.31% | 53.49% | 2.048% | 62.89% | 0% | 36.9% | 0% | 38.89% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 28.23% | 15.93%
CZ 3B | 41.24% | 53.49% | 2.683% | 68.3% | 0% | 36.69% | 0% | 38.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.38% | 6.609% | CZ 3B | 41.24% | 53.49% | 2.683% | 68.97% | 0% | 36.69% | 0% | 38.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 22.43% | 6.609% | CZ 3B | 41.24% | 53.49% | 0% | 67.69% | 0% | 36.69% | 0% | 38.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.14% | 6.609% | CZ 3B | 0% | 0% | 2.683% | 70.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.952% | 6.609% | CZ 3B | 41.24% | 53.49% | 2.683% | 68.33% | 0% | 36.69% | 0% | 38.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.19% | 6.609%
CZ 3C | 41.38% | 53.49% | 0.3148% | 74.4% | 0% | 33.48% | 0% | 40.35% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 25.64% | 1.264% | CZ 3C | 41.38% | 53.49% | 0.3148% | 73.89% | 0% | 33.48% | 0% | 40.35% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 20.24% | 1.264% | CZ 3C | 41.38% | 53.49% | 0% | 74.98% | 0% | 33.48% | 0% | 40.35% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.84% | 1.264% | CZ 3C | 0% | 0% | 0.3148% | 73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.165% | 1.264% | CZ 3C | 41.38% | 53.49% | 0.3148% | 74.38% | 0% | 33.48% | 0% | 40.35% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 25.44% | 1.264%
CZ 4A | 42.05% | 53.49% | 0.3979% | 66.2% | 0% | 29.57% | 0% | 39.62% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 30.28% | 18.74% | CZ 4A | 42.05% | 53.49% | 0.3979% | 65.16% | 0% | 29.57% | 0% | 39.62% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 25.39% | 18.74% | CZ 4A | 42.05% | 53.49% | 0% | 67.07% | 0% | 29.57% | 0% | 39.62% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 34.19% | 18.74% | CZ 4A | 0% | 0% | 0.3979% | 62.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.06% | 18.74% | CZ 4A | 42.05% | 53.49% | 0.3979% | 66.16% | 0% | 29.57% | 0% | 39.62% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 30.09% | 18.74%
CZ 4B | 41.92% | 53.5% | 0.6572% | 72.09% | 0% | 27.69% | 0% | 38.82% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.47% | 1.192% | CZ 4B | 41.92% | 53.5% | 0.6572% | 71.98% | 0% | 27.69% | 0% | 38.82% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 22.6% | 1.192% | CZ 4B | 41.92% | 53.5% | 0% | 72.19% | 0% | 27.69% | 0% | 38.82% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.32% | 1.192% | CZ 4B | 0% | 0% | 0.6572% | 71.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.041% | 1.192% | CZ 4B | 41.92% | 53.5% | 0.6572% | 72.09% | 0% | 27.69% | 0% | 38.82% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.28% | 1.192%
CZ 4C | 41.6% | 53.49% | 0.162% | 72.34% | 0% | 14.28% | 0% | 39.11% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.14% | 2.105% | CZ 4C | 41.6% | 53.49% | 0.162% | 71.55% | 0% | 14.28% | 0% | 39.11% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 22.35% | 2.105% | CZ 4C | 41.6% | 53.49% | 0% | 73.05% | 0% | 14.28% | 0% | 39.11% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.12% | 2.105% | CZ 4C | 0% | 0% | 0.162% | 69.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.555% | 2.105% | CZ 4C | 41.6% | 53.49% | 0.162% | 72.31% | 0% | 14.28% | 0% | 39.11% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 26.95% | 2.105%
CZ 5A | 41.96% | 53.49% | 0.162% | 63.39% | 0% | 25.63% | 0% | 39.31% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.93% | 20.28% | CZ 5A | 41.96% | 53.49% | 0.162% | 62.18% | 0% | 25.63% | 0% | 39.31% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 26.91% | 20.28% | CZ 5A | 41.96% | 53.49% | 0% | 64.34% | 0% | 25.63% | 0% | 39.31% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 36.03% | 20.28% | CZ 5A | 0% | 0% | 0.162% | 58.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.94% | 20.28% | CZ 5A | 41.96% | 53.49% | 0.162% | 63.34% | 0% | 25.63% | 0% | 39.31% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.73% | 20.28%
CZ 5B | 41.95% | 53.49% | 0.1405% | 67.4% | 0% | 23.72% | 0% | 38.38% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.29% | 5.437% | CZ 5B | 41.95% | 53.49% | 0.1405% | 66.69% | 0% | 23.72% | 0% | 38.38% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 24.35% | 5.437% | CZ 5B | 41.95% | 53.49% | 0% | 67.98% | 0% | 23.72% | 0% | 38.38% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 33.32% | 5.437% | CZ 5B | 0% | 0% | 0.1405% | 64.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.436% | 5.437% | CZ 5B | 41.95% | 53.49% | 0.1405% | 67.37% | 0% | 23.72% | 0% | 38.38% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.1% | 5.437%
CZ 5C | 41.78% | 53.49% | 0.1291% | 73.36% | 0% | 7.667% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.54% | 0.1861% | CZ 5C | 41.78% | 53.49% | 0.1291% | 71.5% | 0% | 7.667% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 22.72% | 0.1861% | CZ 5C | 41.78% | 53.49% | 0% | 75.09% | 0% | 7.667% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.65% | 0.1861% | CZ 5C | 0% | 0% | 0.1291% | 67.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.481% | 0.1861% | CZ 5C | 41.78% | 53.49% | 0.1291% | 73.28% | 0% | 7.667% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.35% | 0.1861%
CZ 6A | 41.93% | 53.5% | 0.1855% | 60.39% | 0% | 27.63% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 34.16% | 4.86% | CZ 6A | 41.93% | 53.5% | 0.1855% | 59.44% | 0% | 27.63% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.25% | 4.86% | CZ 6A | 41.93% | 53.5% | 0% | 61.12% | 0% | 27.63% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 38.16% | 4.86% | CZ 6A | 0% | 0% | 0.1855% | 56.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.46% | 4.86% | CZ 6A | 41.93% | 53.5% | 0.1855% | 60.36% | 0% | 27.63% | 0% | 39.15% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 33.97% | 4.86%
CZ 6B | 41.84% | 53.49% | 0.1777% | 64.3% | 0% | 20.75% | 0% | 38.77% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 32.04% | 1.535% | CZ 6B | 41.84% | 53.49% | 0.1777% | 63.52% | 0% | 20.75% | 0% | 38.77% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 27.08% | 1.535% | CZ 6B | 41.84% | 53.49% | 0% | 64.92% | 0% | 20.75% | 0% | 38.77% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 36.15% | 1.535% | CZ 6B | 0% | 0% | 0.1777% | 60.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.63% | 1.535% | CZ 6B | 41.84% | 53.49% | 0.1777% | 64.27% | 0% | 20.75% | 0% | 38.77% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.85% | 1.535%
CZ 7 | 42.08% | 53.49% | 0.1816% | 61.9% | 0% | 24.28% | 0% | 39.6% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 35.9% | 0.8923% | CZ 7 | 42.08% | 53.49% | 0.1816% | 60.22% | 0% | 24.28% | 0% | 39.6% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 30.77% | 0.8923% | CZ 7 | 42.08% | 53.49% | 0% | 63.2% | 0% | 24.28% | 0% | 39.6% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 40.14% | 0.8923% | CZ 7 | 0% | 0% | 0.1816% | 54.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.88% | 0.8923% | CZ 7 | 42.08% | 53.49% | 0.1816% | 61.83% | 0% | 24.28% | 0% | 39.6% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 35.7% | 0.8923%
CZ 8 | 41.62% | 53.5% | 0.2229% | 59.58% | 0% | 11.52% | 0% | 39.34% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 36.69% | 0.1875% | CZ 8 | 41.62% | 53.5% | 0.2229% | 58.11% | 0% | 11.52% | 0% | 39.34% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 31.84% | 0.1875% | CZ 8 | 41.62% | 53.5% | 0% | 60.75% | 0% | 11.52% | 0% | 39.34% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 40.82% | 0.1875% | CZ 8 | 0% | 0% | 0.2229% | 53.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.59% | 0.1875% | CZ 8 | 41.62% | 53.5% | 0.2229% | 59.52% | 0% | 11.52% | 0% | 39.34% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 36.5% | 0.1875%
US Weighted | 41.71% | 53.49% | 1.489% | 64.25% | 0% | 34.21% | 0% | 39.08% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.98% | 100% | US Weighted | 41.71% | 53.49% | 1.489% | 63.35% | 0% | 34.21% | 0% | 39.08% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 25.09% | 100% | US Weighted | 41.71% | 53.49% | 0% | 64.97% | 0% | 34.21% | 0% | 39.08% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 33.8% | 100% | US Weighted | 0% | 0% | 1.489% | 60.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.882% | 100% | US Weighted | 41.71% | 53.49% | 1.489% | 64.21% | 0% | 34.21% | 0% | 39.08% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.14% | 29.79% | 100%

## HotLrg
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Hotel |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Large Hotel | [14 empty] | Prototype Floor Area: | 122120 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.19079 | 0.042116 | 0.18143 | 0.069016 | 0 | 0.35556 | 0 | 0.14446 | 0.047113 | 0.014285 | 0.019529 | 0.219 | 0.0050268 | 0.27391 | 0 | 0.24162 | 1.8038 |  | STD2016 | 6.4279 | 1.4189 | 16.7562 | 6.9016 | 0 | 11.9794 | 0 | 4.8671 | 1.5873 | 0.48129 | 0.65798 | 7.3786 | 0.16936 | 18.4346 | 0 | 8.1405 | 85.2008 |  | STD2016 | 1.8834 | 0.41575 | 0.2064 | 0 | 0 | 3.51 | 0 | 1.4261 | 0.46509 | 0.14102 | 0.19279 | 2.1619 | 0.049623 | 1.3333 | 0 | 2.3852 | 14.1705 |  | STD2016 | 0 | 0 | 0.16052 | 0.069016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36837 |  | STD2016 | 19.717 | 4.3525 | 19.7054 | 7.5435 | 0 | 36.7459 | 0 | 14.9295 | 4.869 | 1.4763 | 2.0183 | 22.6332 | 0.5195 | 29.1339 | 0 | 24.9702 | 188.6141
STD2013 | 0.21046 | 0.056718 | 0.18151 | 0.091197 | 0 | 0.36437 | 0 | 0.15241 | 0.049054 | 0.01898 | 0.019526 | 0.219 | 0.0071744 | 0.27391 | 0 | 0.24162 | 1.8859 |  | STD2013 | 7.0906 | 1.9109 | 16.7642 | 9.1197 | 0 | 12.2762 | 0 | 5.1349 | 1.6527 | 0.63946 | 0.65787 | 7.3786 | 0.24172 | 18.4346 | 0 | 8.1405 | 89.4419 |  | STD2013 | 2.0776 | 0.5599 | 0.2064 | 0 | 0 | 3.5969 | 0 | 1.5045 | 0.48424 | 0.18736 | 0.19276 | 2.1619 | 0.070823 | 1.3333 | 0 | 2.3852 | 14.7609 |  | STD2013 | 0 | 0 | 0.1606 | 0.091197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39063 |  | STD2013 | 21.7499 | 5.8616 | 19.7141 | 9.9679 | 0 | 37.6563 | 0 | 15.7508 | 5.0695 | 1.9615 | 2.018 | 22.6332 | 0.74145 | 29.1339 | 0 | 24.9702 | 197.2282
STD2010 | 0.29253 | 0.056718 | 0.18151 | 0.11568 | 0 | 0.43676 | 0 | 0.18975 | 0.037212 | 0.021037 | 0.024189 | 0.21947 | 0.0075745 | 0.27391 | 0 | 0.26025 | 2.1166 |  | STD2010 | 9.8557 | 1.9109 | 16.7642 | 11.5675 | 0 | 14.7153 | 0 | 6.3931 | 1.2537 | 0.70878 | 0.81497 | 7.3943 | 0.2552 | 18.4346 | 0 | 8.7683 | 98.8365 |  | STD2010 | 2.8877 | 0.5599 | 0.2064 | 0 | 0 | 4.3116 | 0 | 1.8732 | 0.36734 | 0.20767 | 0.23879 | 2.1665 | 0.074773 | 1.3333 | 0 | 2.5691 | 16.7963 |  | STD2010 | 0 | 0 | 0.1606 | 0.11568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41511 |  | STD2010 | 30.2314 | 5.8616 | 19.7141 | 12.6433 | 0 | 45.138 | 0 | 19.6103 | 3.8457 | 2.1741 | 2.4999 | 22.6813 | 0.7828 | 29.1339 | 0 | 26.8962 | 221.2125
STD2007 | 0.33467 | 0.07052 | 0.18202 | 0.24177 | 0 | 0.53511 | 0 | 0.19548 | 0 | 0.046941 | 0.024314 | 0.22539 | 0.013193 | 0.27391 | 0 | 0.26162 | 2.4049 |  | STD2007 | 11.2757 | 2.3759 | 16.7819 | 24.1765 | 0 | 18.0288 | 0 | 6.586 | 0 | 1.5815 | 0.81918 | 7.5938 | 0.44451 | 18.4346 | 0 | 8.8145 | 116.9129 |  | STD2007 | 3.3038 | 0.69615 | 0.21137 | 0 | 0 | 5.2824 | 0 | 1.9297 | 0 | 0.46339 | 0.24002 | 2.225 | 0.13024 | 1.3333 | 0 | 2.5827 | 18.3981 |  | STD2007 | 0 | 0 | 0.1606 | 0.24177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.54121 |  | STD2007 | 34.5873 | 7.288 | 19.7669 | 26.4249 | 0 | 55.3019 | 0 | 20.202 | 0 | 4.8512 | 2.5128 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 251.7635
STD2004 | 0.33467 | 0.07052 | 0.18204 | 0.23248 | 0 | 0.54367 | 0 | 0.23284 | 0.076267 | 0.053122 | 0.024224 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.524 |  | STD2004 | 11.2757 | 2.3759 | 16.784 | 23.248 | 0 | 18.3173 | 0 | 7.8447 | 2.5696 | 1.7898 | 0.81615 | 7.5938 | 0.44453 | 18.4346 | 0 | 8.8145 | 120.3085 |  | STD2004 | 3.3038 | 0.69615 | 0.21142 | 0 | 0 | 5.367 | 0 | 2.2985 | 0.75288 | 0.5244 | 0.23913 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 19.6644 |  | STD2004 | 0 | 0 | 0.16062 | 0.23248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.53194 |  | STD2004 | 34.5873 | 7.288 | 19.7695 | 25.4101 | 0 | 56.1867 | 0 | 24.0629 | 7.8819 | 5.49 | 2.5035 | 23.2933 | 1.3636 | 29.1339 | 0 | 27.0379 | 264.0085
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 2.3852e-05 | -0.009285 | 0 | 0.0085619 | 0 | 0.037359 | 0.076267 | 0.0061811 | -9.0028e-05 | 0 | 7.7395e-07 | 0 | 0 | 0 | 0.11902 |  | 2004-2007 | 0 | 0 | 0.0020788 | -0.9285 | 0 | 0.28847 | 0 | 1.2587 | 2.5696 | 0.20825 | -0.0030332 | 0 | 2.6076e-05 | 0 | 0 | 0 | 3.3955 |  | 2004-2007 | 0 | 0 | 4.5612e-05 | 0 | 0 | 0.08452 | 0 | 0.36879 | 0.75288 | 0.061018 | -0.00088873 | 0 | 7.6402e-06 | 0 | 0 | 0 | 1.2664 |  | 2004-2007 | 0 | 0 | 1.9232e-05 | -0.009285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0092658 |  | 2004-2007 | 0 | 0 | 0.0025795 | -1.0149 | 0 | 0.88484 | 0 | 3.8609 | 7.8819 | 0.6388 | -0.0093041 | 0 | 7.9985e-05 | 0 | 0 | 0 | 12.245
2007-2010 | 0.042148 | 0.013803 | 0.00051071 | 0.12609 | 0 | 0.098347 | 0 | 0.0057258 | -0.037212 | 0.025904 | 0.00012497 | 0.0059218 | 0.0056189 | 0 | 0 | 0.001371 | 0.28835 |  | 2007-2010 | 1.4201 | 0.46503 | 0.017695 | 12.609 | 0 | 3.3135 | 0 | 0.19291 | -1.2537 | 0.87274 | 0.0042105 | 0.19952 | 0.18931 | 0 | 0 | 0.046191 | 18.0764 |  | 2007-2010 | 0.41607 | 0.13625 | 0.004969 | 0 | 0 | 0.97085 | 0 | 0.056523 | -0.36734 | 0.25571 | 0.0012337 | 0.058458 | 0.055468 | 0 | 0 | 0.013534 | 1.6017 |  | 2007-2010 | 0 | 0 | 7.3572e-06 | 0.12609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1261 |  | 2007-2010 | 4.3559 | 1.4265 | 0.052824 | 13.7816 | 0 | 10.1639 | 0 | 0.59174 | -3.8457 | 2.6771 | 0.012915 | 0.612 | 0.58069 | 0 | 0 | 0.14169 | 30.551
2010-2013 | 0.082069 | 0 | -2.7681e-07 | 0.024478 | 0 | 0.072394 | 0 | 0.037345 | -0.011841 | 0.0020574 | 0.004663 | 0.00046545 | 0.0004001 | 0 | 0 | 0.018636 | 0.23067 |  | 2010-2013 | 2.765 | 0 | -3.3979e-05 | 2.4478 | 0 | 2.4391 | 0 | 1.2582 | -0.39896 | 0.069317 | 0.15711 | 0.015682 | 0.01348 | 0 | 0 | 0.62789 | 9.3946 |  | 2010-2013 | 0.81016 | 0 | 9.3762e-07 | 0 | 0 | 0.71465 | 0 | 0.36866 | -0.1169 | 0.02031 | 0.046032 | 0.0045948 | 0.0039496 | 0 | 0 | 0.18397 | 2.0354 |  | 2010-2013 | 0 | 0 | -3.7179e-07 | 0.024478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024478 |  | 2010-2013 | 8.4815 | 0 | -3.0821e-05 | 2.6754 | 0 | 7.4817 | 0 | 3.8595 | -1.2238 | 0.21262 | 0.48191 | 0.048102 | 0.041349 | 0 | 0 | 1.926 | 23.9843
2013-2016 | 0.019671 | 0.014602 | 7.9842e-05 | 0.022181 | 0 | 0.008809 | 0 | 0.0079471 | 0.0019404 | 0.0046945 | -3.2668e-06 | 0 | 0.0021476 | 0 | 0 | 0 | 0.082069 |  | 2013-2016 | 0.66275 | 0.49196 | 0.0079842 | 2.2181 | 0 | 0.29679 | 0 | 0.26775 | 0.065375 | 0.15817 | -0.00011007 | 0 | 0.072356 | 0 | 0 | 0 | 4.2411 |  | 2013-2016 | 0.19418 | 0.14415 | 0 | 0 | 0 | 0.086959 | 0 | 0.078451 | 0.019155 | 0.046343 | -3.2249e-05 | 0 | 0.0212 | 0 | 0 | 0 | 0.59041 |  | 2013-2016 | 0 | 0 | 7.9842e-05 | 0.022181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022261 |  | 2013-2016 | 2.0329 | 1.5091 | 0.0087268 | 2.4244 | 0 | 0.91038 | 0 | 0.8213 | 0.20053 | 0.48516 | -0.00033762 | 0 | 0.22194 | 0 | 0 | 0 | 8.6141
2004-2016 | 0.14389 | 0.028405 | 0.00061413 | 0.16346 | 0 | 0.18811 | 0 | 0.088376 | 0.029154 | 0.038837 | 0.0046947 | 0.0063872 | 0.0081673 | 0 | 0 | 0.020007 | 0.72011 |  | 2004-2016 | 4.8478 | 0.957 | 0.027724 | 16.3464 | 0 | 6.3378 | 0 | 2.9776 | 0.98224 | 1.3085 | 0.15817 | 0.2152 | 0.27517 | 0 | 0 | 0.67408 | 35.1077 |  | 2004-2016 | 1.4204 | 0.2804 | 0.0050155 | 0 | 0 | 1.857 | 0 | 0.87242 | 0.2878 | 0.38338 | 0.046344 | 0.063053 | 0.080625 | 0 | 0 | 0.19751 | 5.4939 |  | 2004-2016 | 0 | 0 | 0.00010606 | 0.16346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16357 |  | 2004-2016 | 14.8703 | 2.9355 | 0.0641 | 17.8666 | 0 | 19.4408 | 0 | 9.1334 | 3.013 | 4.0137 | 0.48518 | 0.6601 | 0.84407 | 0 | 0 | 2.0677 | 75.3944
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.0131% | -3.994% |  | 1.575% |  | 16.04% | 100% | 11.64% | -0.3716% | 0% | 0.005866% | 0% |  | 0% | 4.716% |  | 2004-2007 | 0% | 0% | 0.01239% | -3.994% |  | 1.575% |  | 16.04% | 100% | 11.64% | -0.3716% | 0% | 0.005866% | 0% |  | 0% | 2.822% |  | 2004-2007 | 0% | 0% | 0.02157% |  |  | 1.575% |  | 16.04% | 100% | 11.64% | -0.3716% | 0% | 0.005866% | 0% |  | 0% | 6.44% |  | 2004-2007 |  |  | 0.01197% | -3.994% | [9 empty] | 0% |  |  | -1.742% |  | 2004-2007 | 0% | 0% | 0.01305% | -3.994% |  | 1.575% |  | 16.04% | 100% | 11.64% | -0.3716% | 0% | 0.005866% | 0% |  | 0% | 4.638%
2007-2010 | 12.59% | 19.57% | 0.2806% | 52.15% |  | 18.38% |  | 2.929% |  | 55.18% | 0.514% | 2.627% | 42.59% | 0% |  | 0.524% | 11.99% |  | 2007-2010 | 12.59% | 19.57% | 0.1054% | 52.15% |  | 18.38% |  | 2.929% |  | 55.18% | 0.514% | 2.627% | 42.59% | 0% |  | 0.524% | 15.46% |  | 2007-2010 | 12.59% | 19.57% | 2.351% |  |  | 18.38% |  | 2.929% |  | 55.18% | 0.514% | 2.627% | 42.59% | 0% |  | 0.524% | 8.706% |  | 2007-2010 |  |  | 0.004581% | 52.15% | [9 empty] | 0% |  |  | 23.3% |  | 2007-2010 | 12.59% | 19.57% | 0.2672% | 52.15% |  | 18.38% |  | 2.929% |  | 55.18% | 0.514% | 2.627% | 42.59% | 0% |  | 0.524% | 12.13%
2010-2013 | 28.06% | 0% | -0.0001525% | 21.16% |  | 16.58% |  | 19.68% | -31.82% | 9.78% | 19.28% | 0.2121% | 5.282% | 0% |  | 7.161% | 10.9% |  | 2010-2013 | 28.06% | 0% | -0.0002027% | 21.16% |  | 16.58% |  | 19.68% | -31.82% | 9.78% | 19.28% | 0.2121% | 5.282% | 0% |  | 7.161% | 9.505% |  | 2010-2013 | 28.06% | 0% | 0.0004543% |  |  | 16.58% |  | 19.68% | -31.82% | 9.78% | 19.28% | 0.2121% | 5.282% | 0% |  | 7.161% | 12.12% |  | 2010-2013 |  |  | -0.0002315% | 21.16% | [9 empty] | 0% |  |  | 5.897% |  | 2010-2013 | 28.06% | 0% | -0.0001563% | 21.16% |  | 16.58% |  | 19.68% | -31.82% | 9.78% | 19.28% | 0.2121% | 5.282% | 0% |  | 7.161% | 10.84%
2013-2016 | 9.347% | 25.75% | 0.04399% | 24.32% |  | 2.418% |  | 5.214% | 3.956% | 24.73% | -0.01673% | 0% | 29.93% | 0% |  | 0% | 4.352% |  | 2013-2016 | 9.347% | 25.75% | 0.04763% | 24.32% |  | 2.418% |  | 5.214% | 3.956% | 24.73% | -0.01673% | 0% | 29.93% | 0% |  | 0% | 4.742% |  | 2013-2016 | 9.347% | 25.75% | 0% |  |  | 2.418% |  | 5.214% | 3.956% | 24.73% | -0.01673% | 0% | 29.93% | 0% |  | 0% | 4% |  | 2013-2016 |  |  | 0.04972% | 24.32% | [9 empty] | 0% |  |  | 5.699% |  | 2013-2016 | 9.347% | 25.75% | 0.04427% | 24.32% |  | 2.418% |  | 5.214% | 3.956% | 24.73% | -0.01673% | 0% | 29.93% | 0% |  | 0% | 4.368%
2004-2016 | 42.99% | 40.28% | 0.3374% | 70.31% |  | 34.6% |  | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% |  | 7.647% | 28.53% |  | 2004-2016 | 42.99% | 40.28% | 0.1652% | 70.31% |  | 34.6% |  | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% |  | 7.647% | 29.18% |  | 2004-2016 | 42.99% | 40.28% | 2.372% |  |  | 34.6% |  | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% |  | 7.647% | 27.94% |  | 2004-2016 |  |  | 0.06603% | 70.31% | [9 empty] | 0% |  |  | 30.75% |  | 2004-2016 | 42.99% | 40.28% | 0.3242% | 70.31% |  | 34.6% |  | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% |  | 7.647% | 28.56%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.19113 | 0.042192 | 0.16179 | 0.0067012 | 0 | 0.77551 | 0 | 0.13093 | 0.068497 | 0.017927 | 0.019613 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 2.1538 | 2.703% | CZ 1A | 6.4394 | 1.4215 | 14.7924 | 0.67012 | 0 | 26.1284 | 0 | 4.4112 | 2.3078 | 0.60398 | 0.66081 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 91.5585 | 2.703% | CZ 1A | 1.8867 | 0.41651 | 0.2064 | 0 | 0 | 7.6556 | 0 | 1.2925 | 0.67618 | 0.17697 | 0.19362 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 18.4346 | 2.703% | CZ 1A | 0 | 0 | 0.14088 | 0.0067012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28642 | 2.703% | CZ 1A | 19.7523 | 4.3604 | 17.5589 | 0.73244 | 0 | 80.1466 | 0 | 13.5311 | 7.0789 | 1.8527 | 2.027 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 224.297 | 2.703%
CZ 1B | 0.19108 | 0.042139 | 0.16208 | 0.02788 | 0 | 0.84038 | 0 | 0.14605 | 0.0672 | 0.020885 | 0.01959 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 2.2568 | 0% | CZ 1B | 6.4379 | 1.4197 | 14.8213 | 2.788 | 0 | 28.3137 | 0 | 4.9207 | 2.2641 | 0.70366 | 0.66003 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 96.4521 | 0% | CZ 1B | 1.8863 | 0.41598 | 0.2064 | 0 | 0 | 8.2959 | 0 | 1.4418 | 0.66337 | 0.20617 | 0.19339 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 19.2393 | 0% | CZ 1B | 0 | 0 | 0.14117 | 0.02788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.30789 | 0% | CZ 1B | 19.7477 | 4.3549 | 17.5906 | 3.0473 | 0 | 86.8499 | 0 | 15.0937 | 6.9449 | 2.1584 | 2.0246 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 235.0689 | 0%
CZ 2A | 0.19085 | 0.042125 | 0.16773 | 0.034666 | 0 | 0.68289 | 0 | 0.13248 | 0.054773 | 0.018837 | 0.019586 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 2.0835 | 13.88% | CZ 2A | 6.4299 | 1.4193 | 15.3861 | 3.4666 | 0 | 23.0078 | 0 | 4.4633 | 1.8454 | 0.63464 | 0.65988 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 91.4359 | 13.88% | CZ 2A | 1.884 | 0.41585 | 0.2064 | 0 | 0 | 6.7413 | 0 | 1.3078 | 0.5407 | 0.18595 | 0.19334 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 17.4053 | 13.88% | CZ 2A | 0 | 0 | 0.14682 | 0.034666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32032 | 13.88% | CZ 2A | 19.7232 | 4.3535 | 18.2079 | 3.789 | 0 | 70.5744 | 0 | 13.6909 | 5.6606 | 1.9467 | 2.0241 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 217.2271 | 13.88%
CZ 2B | 0.19093 | 0.042155 | 0.16812 | 0.024892 | 0 | 0.47322 | 0 | 0.16109 | 0.045425 | 0.013924 | 0.019487 | 0.219 | 0.0050301 | 0.27391 | 0 | 0.24162 | 1.8788 | 2.523% | CZ 2B | 6.4329 | 1.4203 | 15.4259 | 2.4892 | 0 | 15.9434 | 0 | 5.4273 | 1.5304 | 0.46913 | 0.65654 | 7.3786 | 0.16947 | 18.4346 | 0 | 8.1405 | 83.9181 | 2.523% | CZ 2B | 1.8848 | 0.41614 | 0.2064 | 0 | 0 | 4.6714 | 0 | 1.5902 | 0.44842 | 0.13746 | 0.19237 | 2.1619 | 0.049655 | 1.3333 | 0 | 2.3852 | 15.4773 | 2.523% | CZ 2B | 0 | 0 | 0.14721 | 0.024892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31095 | 2.523% | CZ 2B | 19.7322 | 4.3566 | 18.2513 | 2.7207 | 0 | 48.9052 | 0 | 16.6477 | 4.6945 | 1.439 | 2.0139 | 22.6332 | 0.51984 | 29.1339 | 0 | 24.9702 | 196.0183 | 2.523%
CZ 3A | 0.19094 | 0.042148 | 0.17791 | 0.077451 | 0 | 0.40513 | 0 | 0.13004 | 0.04716 | 0.015982 | 0.01954 | 0.219 | 0.0050301 | 0.27391 | 0 | 0.24162 | 1.8459 | 14.22% | CZ 3A | 6.4331 | 1.4201 | 16.4043 | 7.7451 | 0 | 13.6496 | 0 | 4.3811 | 1.5889 | 0.53846 | 0.65832 | 7.3786 | 0.16947 | 18.4346 | 0 | 8.1405 | 86.942 | 14.22% | CZ 3A | 1.8849 | 0.41608 | 0.2064 | 0 | 0 | 3.9993 | 0 | 1.2837 | 0.46555 | 0.15777 | 0.19289 | 2.1619 | 0.049655 | 1.3333 | 0 | 2.3852 | 14.5366 | 14.22% | CZ 3A | 0 | 0 | 0.157 | 0.077451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37329 | 14.22% | CZ 3A | 19.733 | 4.3559 | 19.3208 | 8.4654 | 0 | 41.8689 | 0 | 13.4387 | 4.8738 | 1.6517 | 2.0194 | 22.6332 | 0.51984 | 29.1339 | 0 | 24.9702 | 192.9846 | 14.22%
CZ 3B | 0.19091 | 0.042146 | 0.17529 | 0.034656 | 0 | 0.35276 | 0 | 0.15968 | 0.044268 | 0.012929 | 0.019498 | 0.219 | 0.0050255 | 0.27391 | 0 | 0.24162 | 1.7717 | 16.01% | CZ 3B | 6.432 | 1.42 | 16.1424 | 3.4656 | 0 | 11.885 | 0 | 5.38 | 1.4915 | 0.4356 | 0.65693 | 7.3786 | 0.16932 | 18.4346 | 0 | 8.1405 | 81.4319 | 16.01% | CZ 3B | 1.8846 | 0.41605 | 0.2064 | 0 | 0 | 3.4823 | 0 | 1.5763 | 0.437 | 0.12763 | 0.19248 | 2.1619 | 0.04961 | 1.3333 | 0 | 2.3852 | 14.2528 | 16.01% | CZ 3B | 0 | 0 | 0.15438 | 0.034656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32787 | 16.01% | CZ 3B | 19.7296 | 4.3557 | 19.0345 | 3.7879 | 0 | 36.4562 | 0 | 16.5027 | 4.575 | 1.3362 | 2.0151 | 22.6332 | 0.51936 | 29.1339 | 0 | 24.9702 | 185.0493 | 16.01%
CZ 3C | 0.19091 | 0.042139 | 0.17907 | 0.07193 | 0 | 0.24507 | 0 | 0.13196 | 0 | 0.012203 | 0.019572 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 1.6324 | 2.133% | CZ 3C | 6.4319 | 1.4197 | 16.521 | 7.193 | 0 | 8.2567 | 0 | 4.4459 | 0 | 0.41114 | 0.65941 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 79.4617 | 2.133% | CZ 3C | 1.8846 | 0.41598 | 0.2064 | 0 | 0 | 2.4192 | 0 | 1.3026 | 0 | 0.12046 | 0.19321 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 12.4725 | 2.133% | CZ 3C | 0 | 0 | 0.15817 | 0.07193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36893 | 2.133% | CZ 3C | 19.7294 | 4.3549 | 19.4483 | 7.8619 | 0 | 25.3267 | 0 | 13.6373 | 0 | 1.2611 | 2.0227 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 170.8992 | 2.133%
CZ 4A | 0.19067 | 0.042084 | 0.18595 | 0.070713 | 0 | 0.28654 | 0 | 0.14132 | 0.051589 | 0.015922 | 0.019535 | 0.219 | 0.0050232 | 0.27391 | 0 | 0.24162 | 1.7439 | 18.1% | CZ 4A | 6.4238 | 1.4179 | 17.2087 | 7.0713 | 0 | 9.6539 | 0 | 4.7614 | 1.7381 | 0.53644 | 0.65817 | 7.3786 | 0.16924 | 18.4346 | 0 | 8.1405 | 83.5926 | 18.1% | CZ 4A | 1.8822 | 0.41544 | 0.2064 | 0 | 0 | 2.8286 | 0 | 1.3951 | 0.50927 | 0.15718 | 0.19284 | 2.1619 | 0.049587 | 1.3333 | 0 | 2.3852 | 13.517 | 18.1% | CZ 4A | 0 | 0 | 0.16504 | 0.070713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37459 | 18.1% | CZ 4A | 19.7046 | 4.3492 | 20.2 | 7.7289 | 0 | 29.6125 | 0 | 14.6053 | 5.3315 | 1.6455 | 2.0189 | 22.6332 | 0.51913 | 29.1339 | 0 | 24.9702 | 182.4528 | 18.1%
CZ 4B | 0.1906 | 0.042116 | 0.18366 | 0.036716 | 0 | 0.26394 | 0 | 0.17476 | 0.041533 | 0.012039 | 0.019484 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 1.7044 | 0.7301% | CZ 4B | 6.4217 | 1.419 | 16.98 | 3.6716 | 0 | 8.8926 | 0 | 5.8879 | 1.3993 | 0.40563 | 0.65646 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 79.8571 | 0.7301% | CZ 4B | 1.8816 | 0.41576 | 0.2064 | 0 | 0 | 2.6055 | 0 | 1.7251 | 0.41 | 0.11885 | 0.19234 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 13.4856 | 0.7301% | CZ 4B | 0 | 0 | 0.16276 | 0.036716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33831 | 0.7301% | CZ 4B | 19.698 | 4.3526 | 19.95 | 4.013 | 0 | 27.2774 | 0 | 18.0606 | 4.2923 | 1.2442 | 2.0136 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 178.1585 | 0.7301%
CZ 4C | 0.19084 | 0.042036 | 0.18839 | 0.065556 | 0 | 0.12402 | 0 | 0.14496 | 0.040669 | 0.011304 | 0.019535 | 0.219 | 0.0050255 | 0.27391 | 0 | 0.24162 | 1.5669 | 2.455% | CZ 4C | 6.4296 | 1.4162 | 17.4521 | 6.5556 | 0 | 4.1784 | 0 | 4.884 | 1.3702 | 0.38086 | 0.65817 | 7.3786 | 0.16932 | 18.4346 | 0 | 8.1405 | 77.4482 | 2.455% | CZ 4C | 1.8839 | 0.41496 | 0.2064 | 0 | 0 | 1.2243 | 0 | 1.431 | 0.40147 | 0.11159 | 0.19284 | 2.1619 | 0.04961 | 1.3333 | 0 | 2.3852 | 11.7965 | 2.455% | CZ 4C | 0 | 0 | 0.16748 | 0.065556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37187 | 2.455% | CZ 4C | 19.7222 | 4.3442 | 20.466 | 7.1653 | 0 | 12.8169 | 0 | 14.9813 | 4.203 | 1.1683 | 2.0189 | 22.6332 | 0.51936 | 29.1339 | 0 | 24.9702 | 164.1428 | 2.455%
CZ 5A | 0.19064 | 0.042098 | 0.19278 | 0.10549 | 0 | 0.18996 | 0 | 0.14471 | 0.043996 | 0.010348 | 0.019517 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 1.6791 | 18.12% | CZ 5A | 6.4228 | 1.4183 | 17.8914 | 10.5485 | 0 | 6.3999 | 0 | 4.8755 | 1.4823 | 0.34865 | 0.65755 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 84.168 | 18.12% | CZ 5A | 1.8819 | 0.41557 | 0.2064 | 0 | 0 | 1.8752 | 0 | 1.4285 | 0.43432 | 0.10215 | 0.19266 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 12.4667 | 18.12% | CZ 5A | 0 | 0 | 0.17187 | 0.10549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41619 | 18.12% | CZ 5A | 19.7015 | 4.3507 | 20.9462 | 11.5296 | 0 | 19.6313 | 0 | 14.9551 | 4.5469 | 1.0694 | 2.017 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 176.0044 | 18.12%
CZ 5B | 0.19062 | 0.042098 | 0.19084 | 0.066083 | 0 | 0.20148 | 0 | 0.17643 | 0.043513 | 0.012415 | 0.019473 | 0.219 | 0.0050255 | 0.27391 | 0 | 0.24162 | 1.6825 | 4.122% | CZ 5B | 6.4223 | 1.4183 | 17.6979 | 6.6083 | 0 | 6.7881 | 0 | 5.9443 | 1.466 | 0.41828 | 0.65607 | 7.3786 | 0.16932 | 18.4346 | 0 | 8.1405 | 81.5426 | 4.122% | CZ 5B | 1.8817 | 0.41557 | 0.2064 | 0 | 0 | 1.9889 | 0 | 1.7417 | 0.42954 | 0.12256 | 0.19223 | 2.1619 | 0.04961 | 1.3333 | 0 | 2.3852 | 12.9087 | 4.122% | CZ 5B | 0 | 0 | 0.16993 | 0.066083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37486 | 4.122% | CZ 5B | 19.6999 | 4.3507 | 20.7347 | 7.2229 | 0 | 20.8219 | 0 | 18.2337 | 4.4969 | 1.283 | 2.0124 | 22.6332 | 0.51936 | 29.1339 | 0 | 24.9702 | 176.1127 | 4.122%
CZ 5C | 0.19068 | 0.042033 | 0.19225 | 0.071138 | 0 | 0.081506 | 0 | 0.14673 | 0.046165 | 0.0072029 | 0.019537 | 0.219 | 0.0050255 | 0.27391 | 0 | 0.24162 | 1.5368 | 0.01984% | CZ 5C | 6.4245 | 1.4162 | 17.8384 | 7.1138 | 0 | 2.7461 | 0 | 4.9437 | 1.5554 | 0.24268 | 0.65825 | 7.3786 | 0.16932 | 18.4346 | 0 | 8.1405 | 77.0619 | 0.01984% | CZ 5C | 1.8824 | 0.41494 | 0.2064 | 0 | 0 | 0.8046 | 0 | 1.4485 | 0.45572 | 0.071105 | 0.19287 | 2.1619 | 0.04961 | 1.3333 | 0 | 2.3852 | 11.4065 | 0.01984% | CZ 5C | 0 | 0 | 0.17134 | 0.071138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.38132 | 0.01984% | CZ 5C | 19.7065 | 4.344 | 20.8882 | 7.7754 | 0 | 8.4234 | 0 | 15.1644 | 4.771 | 0.7444 | 2.0191 | 22.6332 | 0.51936 | 29.1339 | 0 | 24.9702 | 161.093 | 0.01984%
CZ 6A | 0.19062 | 0.042077 | 0.19784 | 0.1743 | 0 | 0.19777 | 0 | 0.14933 | 0.046019 | 0.011701 | 0.019494 | 0.219 | 0.0050278 | 0.27391 | 0 | 0.24162 | 1.7687 | 3.21% | CZ 6A | 6.4224 | 1.4176 | 18.3981 | 17.4296 | 0 | 6.6633 | 0 | 5.031 | 1.5505 | 0.39422 | 0.65677 | 7.3786 | 0.16939 | 18.4346 | 0 | 8.1405 | 92.0865 | 3.21% | CZ 6A | 1.8818 | 0.41537 | 0.2064 | 0 | 0 | 1.9523 | 0 | 1.4741 | 0.45429 | 0.11551 | 0.19243 | 2.1619 | 0.049632 | 1.3333 | 0 | 2.3852 | 12.6222 | 3.21% | CZ 6A | 0 | 0 | 0.17694 | 0.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.49007 | 3.21% | CZ 6A | 19.7001 | 4.3485 | 21.5 | 19.0506 | 0 | 20.439 | 0 | 15.4323 | 4.756 | 1.2092 | 2.0146 | 22.6332 | 0.5196 | 29.1339 | 0 | 24.9702 | 185.707 | 3.21%
CZ 6B | 0.19057 | 0.042047 | 0.19656 | 0.13528 | 0 | 0.14291 | 0 | 0.16701 | 0.046524 | 0.0092306 | 0.01945 | 0.219 | 0.0050301 | 0.27391 | 0 | 0.24162 | 1.6891 | 1.094% | CZ 6B | 6.4205 | 1.4166 | 18.2692 | 13.5284 | 0 | 4.8148 | 0 | 5.627 | 1.5675 | 0.311 | 0.6553 | 7.3786 | 0.16947 | 18.4346 | 0 | 8.1405 | 86.7334 | 1.094% | CZ 6B | 1.8812 | 0.41507 | 0.2064 | 0 | 0 | 1.4107 | 0 | 1.6487 | 0.45927 | 0.091122 | 0.192 | 2.1619 | 0.049655 | 1.3333 | 0 | 2.3852 | 12.2346 | 1.094% | CZ 6B | 0 | 0 | 0.17565 | 0.13528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44977 | 1.094% | CZ 6B | 19.6944 | 4.3454 | 21.3591 | 14.7865 | 0 | 14.7691 | 0 | 17.2602 | 4.8081 | 0.95395 | 2.0101 | 22.6332 | 0.51984 | 29.1339 | 0 | 24.9702 | 177.2439 | 1.094%
CZ 7 | 0.19048 | 0.042022 | 0.20388 | 0.23859 | 0 | 0.15953 | 0 | 0.15257 | 0.046639 | 0.01783 | 0.019461 | 0.219 | 0.0050255 | 0.27391 | 0 | 0.24162 | 1.8106 | 0.5976% | CZ 7 | 6.4176 | 1.4158 | 19.0018 | 23.859 | 0 | 5.3748 | 0 | 5.1402 | 1.5714 | 0.60072 | 0.65568 | 7.3786 | 0.16932 | 18.4346 | 0 | 8.1405 | 98.1598 | 0.5976% | CZ 7 | 1.8804 | 0.41482 | 0.20642 | 0 | 0 | 1.5748 | 0 | 1.5061 | 0.46041 | 0.17601 | 0.19212 | 2.1619 | 0.04961 | 1.3333 | 0 | 2.3852 | 12.3411 | 0.5976% | CZ 7 | 0 | 0 | 0.18297 | 0.23859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5604 | 0.5976% | CZ 7 | 19.6856 | 4.3428 | 22.1599 | 26.0778 | 0 | 16.4868 | 0 | 15.7671 | 4.82 | 1.8427 | 2.0113 | 22.6332 | 0.51936 | 29.1339 | 0 | 24.9702 | 190.4505 | 0.5976%
CZ 8 | 0.19045 | 0.041789 | 0.21202 | 0.36689 | 0 | 0.093435 | 0 | 0.15907 | 0.048768 | 0.016111 | 0.019415 | 0.219 | 0.0050232 | 0.27391 | 0 | 0.24162 | 1.8875 | 0.07229% | CZ 8 | 6.4166 | 1.4079 | 19.8156 | 36.6893 | 0 | 3.148 | 0 | 5.3594 | 1.6431 | 0.54281 | 0.65413 | 7.3786 | 0.16924 | 18.4346 | 0 | 8.1405 | 109.7997 | 0.07229% | CZ 8 | 1.8801 | 0.41253 | 0.20642 | 0 | 0 | 0.92236 | 0 | 1.5703 | 0.48143 | 0.15904 | 0.19166 | 2.1619 | 0.049587 | 1.3333 | 0 | 2.3852 | 11.7538 | 0.07229% | CZ 8 | 0 | 0 | 0.19111 | 0.36689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.69684 | 0.07229% | CZ 8 | 19.6825 | 4.3187 | 23.0495 | 40.1014 | 0 | 9.6562 | 0 | 16.4394 | 5.04 | 1.665 | 2.0065 | 22.6332 | 0.51913 | 29.1339 | 0 | 24.9702 | 199.2155 | 0.07229%
US Weighted | 0.19079 | 0.042116 | 0.18143 | 0.069016 | 0 | 0.35556 | 0 | 0.14446 | 0.047113 | 0.014285 | 0.019529 | 0.219 | 0.0050268 | 0.27391 | 0 | 0.24162 | 1.8038 | 100% | US Weighted | 6.4279 | 1.4189 | 16.7562 | 6.9016 | 0 | 11.9794 | 0 | 4.8671 | 1.5873 | 0.48129 | 0.65798 | 7.3786 | 0.16936 | 18.4346 | 0 | 8.1405 | 85.2008 | 100% | US Weighted | 1.8834 | 0.41575 | 0.2064 | 0 | 0 | 3.51 | 0 | 1.4261 | 0.46509 | 0.14102 | 0.19279 | 2.1619 | 0.049623 | 1.3333 | 0 | 2.3852 | 14.1705 | 100% | US Weighted | 0 | 0 | 0.16052 | 0.069016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36837 | 100% | US Weighted | 19.717 | 4.3525 | 19.7054 | 7.5435 | 0 | 36.7459 | 0 | 14.9295 | 4.869 | 1.4763 | 2.0183 | 22.6332 | 0.5195 | 29.1339 | 0 | 24.9702 | 188.6141 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.21076 | 0.056822 | 0.16197 | 0.0071536 | 0 | 0.8324 | 0 | 0.14377 | 0.07208 | 0.024109 | 0.019609 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 2.2704 | 2.703% | CZ 1A | 7.101 | 1.9144 | 14.8102 | 0.71536 | 0 | 28.0449 | 0 | 4.844 | 2.4285 | 0.81227 | 0.66065 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 95.5266 | 2.703% | CZ 1A | 2.0806 | 0.56092 | 0.2064 | 0 | 0 | 8.2172 | 0 | 1.4193 | 0.71155 | 0.23799 | 0.19357 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 19.5787 | 2.703% | CZ 1A | 0 | 0 | 0.14106 | 0.0071536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28705 | 2.703% | CZ 1A | 21.7816 | 5.8723 | 17.5784 | 0.78189 | 0 | 86.0255 | 0 | 14.8584 | 7.4492 | 2.4916 | 2.0265 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 236.3442 | 2.703%
CZ 1B | 0.21072 | 0.05675 | 0.16262 | 0.029641 | 0 | 0.88486 | 0 | 0.15909 | 0.070227 | 0.028312 | 0.019588 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 2.3635 | 0% | CZ 1B | 7.0994 | 1.912 | 14.8757 | 2.9641 | 0 | 29.8124 | 0 | 5.36 | 2.3661 | 0.95387 | 0.65995 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 100.1988 | 0% | CZ 1B | 2.0801 | 0.56022 | 0.2064 | 0 | 0 | 8.735 | 0 | 1.5705 | 0.69326 | 0.27948 | 0.19337 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 20.2696 | 0% | CZ 1B | 0 | 0 | 0.14171 | 0.029641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31019 | 0% | CZ 1B | 21.7768 | 5.8649 | 17.65 | 3.2398 | 0 | 91.4471 | 0 | 16.4413 | 7.2578 | 2.9259 | 2.0244 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 246.1066 | 0%
CZ 2A | 0.21062 | 0.056732 | 0.16779 | 0.038521 | 0 | 0.71989 | 0 | 0.14254 | 0.057271 | 0.024372 | 0.019579 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 2.179 | 13.88% | CZ 2A | 7.0963 | 1.9114 | 15.393 | 3.8521 | 0 | 24.2543 | 0 | 4.8025 | 1.9296 | 0.82112 | 0.65964 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 94.9153 | 13.88% | CZ 2A | 2.0792 | 0.56004 | 0.2064 | 0 | 0 | 7.1065 | 0 | 1.4071 | 0.56536 | 0.24059 | 0.19328 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 18.3098 | 13.88% | CZ 2A | 0 | 0 | 0.14689 | 0.038521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32425 | 13.88% | CZ 2A | 21.7673 | 5.863 | 18.2154 | 4.2104 | 0 | 74.3981 | 0 | 14.7313 | 5.9187 | 2.5187 | 2.0234 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 227.1251 | 13.88%
CZ 2B | 0.21076 | 0.056771 | 0.1682 | 0.028748 | 0 | 0.48314 | 0 | 0.15944 | 0.047579 | 0.016846 | 0.019487 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 1.9327 | 2.523% | CZ 2B | 7.1008 | 1.9127 | 15.4341 | 2.8748 | 0 | 16.2778 | 0 | 5.3719 | 1.603 | 0.56757 | 0.65654 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 85.9946 | 2.523% | CZ 2B | 2.0805 | 0.56042 | 0.2064 | 0 | 0 | 4.7694 | 0 | 1.574 | 0.46969 | 0.1663 | 0.19237 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 15.9703 | 2.523% | CZ 2B | 0 | 0 | 0.1473 | 0.028748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31488 | 2.523% | CZ 2B | 21.7811 | 5.8671 | 18.2603 | 3.1422 | 0 | 49.9308 | 0 | 16.4779 | 4.9172 | 1.741 | 2.0139 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 201.6102 | 2.523%
CZ 3A | 0.21074 | 0.056762 | 0.17795 | 0.088736 | 0 | 0.42206 | 0 | 0.14009 | 0.049068 | 0.019998 | 0.019535 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 1.9266 | 14.22% | CZ 3A | 7.1003 | 1.9124 | 16.4085 | 8.8736 | 0 | 14.2199 | 0 | 4.7197 | 1.6532 | 0.67377 | 0.65817 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 90.415 | 14.22% | CZ 3A | 2.0804 | 0.56033 | 0.2064 | 0 | 0 | 4.1664 | 0 | 1.3829 | 0.48438 | 0.19742 | 0.19284 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 15.2223 | 14.22% | CZ 3A | 0 | 0 | 0.15704 | 0.088736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.38462 | 14.22% | CZ 3A | 21.7795 | 5.8661 | 19.3254 | 9.6989 | 0 | 43.6185 | 0 | 14.4774 | 5.071 | 2.0667 | 2.0189 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 201.4011 | 14.22%
CZ 3B | 0.21073 | 0.056759 | 0.17533 | 0.041592 | 0 | 0.35674 | 0 | 0.15999 | 0.045913 | 0.015473 | 0.019496 | 0.219 | 0.007173 | 0.27391 | 0 | 0.24162 | 1.8237 | 16.01% | CZ 3B | 7.0997 | 1.9123 | 16.1467 | 4.1592 | 0 | 12.0192 | 0 | 5.3904 | 1.5469 | 0.5213 | 0.65685 | 7.3786 | 0.24167 | 18.4346 | 0 | 8.1405 | 83.6479 | 16.01% | CZ 3B | 2.0802 | 0.56031 | 0.2064 | 0 | 0 | 3.5216 | 0 | 1.5794 | 0.45324 | 0.15274 | 0.19246 | 2.1619 | 0.070809 | 1.3333 | 0 | 2.3852 | 14.6976 | 16.01% | CZ 3B | 0 | 0 | 0.15442 | 0.041592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33485 | 16.01% | CZ 3B | 21.7778 | 5.8659 | 19.0392 | 4.546 | 0 | 36.8679 | 0 | 16.5346 | 4.745 | 1.599 | 2.0148 | 22.6332 | 0.7413 | 29.1339 | 0 | 24.9702 | 190.4688 | 16.01%
CZ 3C | 0.2107 | 0.05675 | 0.17906 | 0.078398 | 0 | 0.24795 | 0 | 0.1404 | 0 | 0.014945 | 0.01957 | 0.219 | 0.007173 | 0.27391 | 0 | 0.24162 | 1.6895 | 2.133% | CZ 3C | 7.0989 | 1.912 | 16.5195 | 7.8398 | 0 | 8.3538 | 0 | 4.7305 | 0 | 0.50352 | 0.65933 | 7.3786 | 0.24167 | 18.4346 | 0 | 8.1405 | 81.8126 | 2.133% | CZ 3C | 2.08 | 0.56022 | 0.2064 | 0 | 0 | 2.4477 | 0 | 1.386 | 0 | 0.14753 | 0.19318 | 2.1619 | 0.070809 | 1.3333 | 0 | 2.3852 | 12.9722 | 2.133% | CZ 3C | 0 | 0 | 0.15815 | 0.078398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37539 | 2.133% | CZ 3C | 21.7752 | 5.8649 | 19.4467 | 8.5689 | 0 | 25.6246 | 0 | 14.5103 | 0 | 1.5445 | 2.0224 | 22.6332 | 0.7413 | 29.1339 | 0 | 24.9702 | 176.836 | 2.133%
CZ 4A | 0.21021 | 0.056674 | 0.18601 | 0.10226 | 0 | 0.28999 | 0 | 0.15107 | 0.053351 | 0.019383 | 0.01953 | 0.219 | 0.0071776 | 0.27391 | 0 | 0.24162 | 1.8302 | 18.1% | CZ 4A | 7.0824 | 1.9094 | 17.2149 | 10.2261 | 0 | 9.7702 | 0 | 5.0898 | 1.7975 | 0.65304 | 0.65801 | 7.3786 | 0.24182 | 18.4346 | 0 | 8.1405 | 88.5968 | 18.1% | CZ 4A | 2.0751 | 0.55947 | 0.2064 | 0 | 0 | 2.8627 | 0 | 1.4913 | 0.52667 | 0.19134 | 0.1928 | 2.1619 | 0.070855 | 1.3333 | 0 | 2.3852 | 14.0571 | 18.1% | CZ 4A | 0 | 0 | 0.16511 | 0.10226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.4062 | 18.1% | CZ 4A | 21.7247 | 5.8571 | 20.2068 | 11.1771 | 0 | 29.9693 | 0 | 15.6126 | 5.5137 | 2.0032 | 2.0184 | 22.6332 | 0.74178 | 29.1339 | 0 | 24.9702 | 191.5617 | 18.1%
CZ 4B | 0.21015 | 0.056718 | 0.18371 | 0.054333 | 0 | 0.25234 | 0 | 0.17131 | 0.044204 | 0.014086 | 0.019482 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 1.748 | 0.7301% | CZ 4B | 7.0802 | 1.9109 | 16.9846 | 5.4333 | 0 | 8.5018 | 0 | 5.7717 | 1.4893 | 0.47457 | 0.65638 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 82.498 | 0.7301% | CZ 4B | 2.0745 | 0.5599 | 0.2064 | 0 | 0 | 2.491 | 0 | 1.6911 | 0.43636 | 0.13905 | 0.19232 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 13.7419 | 0.7301% | CZ 4B | 0 | 0 | 0.1628 | 0.054333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35597 | 0.7301% | CZ 4B | 21.7178 | 5.8616 | 19.955 | 5.9386 | 0 | 26.0784 | 0 | 17.7043 | 4.5683 | 1.4557 | 2.0134 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 182.7718 | 0.7301%
CZ 4C | 0.21041 | 0.05661 | 0.18847 | 0.089835 | 0 | 0.11119 | 0 | 0.15321 | 0.042803 | 0.013484 | 0.019533 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 1.6272 | 2.455% | CZ 4C | 7.089 | 1.9073 | 17.461 | 8.9835 | 0 | 3.7461 | 0 | 5.1618 | 1.4421 | 0.4543 | 0.65809 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 81.0985 | 2.455% | CZ 4C | 2.0771 | 0.55883 | 0.2064 | 0 | 0 | 1.0976 | 0 | 1.5124 | 0.42254 | 0.13311 | 0.19282 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 12.152 | 2.455% | CZ 4C | 0 | 0 | 0.16757 | 0.089835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39624 | 2.455% | CZ 4C | 21.7449 | 5.8504 | 20.4757 | 9.819 | 0 | 11.4908 | 0 | 15.8333 | 4.4235 | 1.3935 | 2.0186 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 170.5286 | 2.455%
CZ 5A | 0.21018 | 0.056693 | 0.19291 | 0.15043 | 0 | 0.18606 | 0 | 0.15619 | 0.045766 | 0.018441 | 0.019517 | 0.219 | 0.0071707 | 0.27391 | 0 | 0.24162 | 1.7779 | 18.12% | CZ 5A | 7.0812 | 1.9101 | 17.9045 | 15.0427 | 0 | 6.2688 | 0 | 5.2625 | 1.5419 | 0.62129 | 0.65755 | 7.3786 | 0.24159 | 18.4346 | 0 | 8.1405 | 90.4858 | 18.12% | CZ 5A | 2.0748 | 0.55965 | 0.2064 | 0 | 0 | 1.8368 | 0 | 1.5419 | 0.45179 | 0.18204 | 0.19266 | 2.1619 | 0.070786 | 1.3333 | 0 | 2.3852 | 12.9972 | 18.12% | CZ 5A | 0 | 0 | 0.172 | 0.15043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.46127 | 18.12% | CZ 5A | 21.7211 | 5.859 | 20.9605 | 16.4416 | 0 | 19.2291 | 0 | 16.1422 | 4.7298 | 1.9058 | 2.017 | 22.6332 | 0.74106 | 29.1339 | 0 | 24.9702 | 186.4843 | 18.12%
CZ 5B | 0.21017 | 0.056695 | 0.19095 | 0.09712 | 0 | 0.18966 | 0 | 0.17615 | 0.045879 | 0.014544 | 0.01947 | 0.219 | 0.007173 | 0.27391 | 0 | 0.24162 | 1.7423 | 4.122% | CZ 5B | 7.0809 | 1.9101 | 17.709 | 9.712 | 0 | 6.3901 | 0 | 5.9347 | 1.5457 | 0.49002 | 0.65599 | 7.3786 | 0.24167 | 18.4346 | 0 | 8.1405 | 85.6237 | 4.122% | CZ 5B | 2.0747 | 0.55967 | 0.2064 | 0 | 0 | 1.8723 | 0 | 1.7389 | 0.4529 | 0.14357 | 0.19221 | 2.1619 | 0.070809 | 1.3333 | 0 | 2.3852 | 13.1918 | 4.122% | CZ 5B | 0 | 0 | 0.17005 | 0.09712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.406 | 4.122% | CZ 5B | 21.7199 | 5.8592 | 20.7467 | 10.6152 | 0 | 19.601 | 0 | 18.2042 | 4.7414 | 1.5031 | 2.0122 | 22.6332 | 0.7413 | 29.1339 | 0 | 24.9702 | 182.4815 | 4.122%
CZ 5C | 0.21024 | 0.056605 | 0.19238 | 0.097969 | 0 | 0.067359 | 0 | 0.15497 | 0.048213 | 0.012309 | 0.019537 | 0.219 | 0.0071776 | 0.27391 | 0 | 0.24162 | 1.6013 | 0.01984% | CZ 5C | 7.0833 | 1.9071 | 17.8517 | 9.7969 | 0 | 2.2694 | 0 | 5.2212 | 1.6244 | 0.41471 | 0.65825 | 7.3786 | 0.24182 | 18.4346 | 0 | 8.1405 | 81.0223 | 0.01984% | CZ 5C | 2.0754 | 0.55879 | 0.2064 | 0 | 0 | 0.66494 | 0 | 1.5298 | 0.47594 | 0.12151 | 0.19287 | 2.1619 | 0.070855 | 1.3333 | 0 | 2.3852 | 11.7769 | 0.01984% | CZ 5C | 0 | 0 | 0.17147 | 0.097969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40828 | 0.01984% | CZ 5C | 21.7273 | 5.8499 | 20.9027 | 10.708 | 0 | 6.9613 | 0 | 16.0155 | 4.9827 | 1.2721 | 2.0191 | 22.6332 | 0.74178 | 29.1339 | 0 | 24.9702 | 167.9176 | 0.01984%
CZ 6A | 0.21016 | 0.056665 | 0.19802 | 0.23405 | 0 | 0.19431 | 0 | 0.16225 | 0.048054 | 0.0208 | 0.019491 | 0.219 | 0.0071776 | 0.27391 | 0 | 0.24162 | 1.8855 | 3.21% | CZ 6A | 7.0808 | 1.9091 | 18.4154 | 23.405 | 0 | 6.5467 | 0 | 5.4665 | 1.619 | 0.70079 | 0.65669 | 7.3786 | 0.24182 | 18.4346 | 0 | 8.1405 | 99.9954 | 3.21% | CZ 6A | 2.0747 | 0.55938 | 0.2064 | 0 | 0 | 1.9182 | 0 | 1.6017 | 0.47437 | 0.20533 | 0.19241 | 2.1619 | 0.070855 | 1.3333 | 0 | 2.3852 | 13.1837 | 3.21% | CZ 6A | 0 | 0 | 0.17711 | 0.23405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.55 | 3.21% | CZ 6A | 21.7197 | 5.8561 | 21.5189 | 25.5817 | 0 | 20.0813 | 0 | 16.768 | 4.9662 | 2.1496 | 2.0143 | 22.6332 | 0.74178 | 29.1339 | 0 | 24.9702 | 198.1349 | 3.21%
CZ 6B | 0.2101 | 0.056626 | 0.19672 | 0.18218 | 0 | 0.13121 | 0 | 0.17186 | 0.04854 | 0.016558 | 0.01945 | 0.219 | 0.007173 | 0.27391 | 0 | 0.24162 | 1.7749 | 1.094% | CZ 6B | 7.0787 | 1.9078 | 18.2852 | 18.2178 | 0 | 4.4206 | 0 | 5.7903 | 1.6354 | 0.55787 | 0.6553 | 7.3786 | 0.24167 | 18.4346 | 0 | 8.1405 | 92.7443 | 1.094% | CZ 6B | 2.0741 | 0.55899 | 0.2064 | 0 | 0 | 1.2952 | 0 | 1.6966 | 0.47917 | 0.16345 | 0.192 | 2.1619 | 0.070809 | 1.3333 | 0 | 2.3852 | 12.6171 | 1.094% | CZ 6B | 0 | 0 | 0.17581 | 0.18218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.49683 | 1.094% | CZ 6B | 21.7133 | 5.8521 | 21.3766 | 19.9121 | 0 | 13.5599 | 0 | 17.7612 | 5.0165 | 1.7112 | 2.0101 | 22.6332 | 0.7413 | 29.1339 | 0 | 24.9702 | 186.3914 | 1.094%
CZ 7 | 0.20969 | 0.056591 | 0.2041 | 0.293 | 0 | 0.15796 | 0 | 0.16769 | 0.048208 | 0.021335 | 0.019457 | 0.219 | 0.007173 | 0.27391 | 0 | 0.24162 | 1.9197 | 0.5976% | CZ 7 | 7.0647 | 1.9067 | 19.0233 | 29.3003 | 0 | 5.3218 | 0 | 5.6496 | 1.6242 | 0.7188 | 0.65553 | 7.3786 | 0.24167 | 18.4346 | 0 | 8.1405 | 105.4601 | 0.5976% | CZ 7 | 2.07 | 0.55865 | 0.20642 | 0 | 0 | 1.5593 | 0 | 1.6553 | 0.4759 | 0.21061 | 0.19207 | 2.1619 | 0.070809 | 1.3333 | 0 | 2.3852 | 12.8795 | 0.5976% | CZ 7 | 0 | 0 | 0.18319 | 0.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.61503 | 0.5976% | CZ 7 | 21.6704 | 5.8485 | 22.1834 | 32.0252 | 0 | 16.3241 | 0 | 17.3297 | 4.9822 | 2.2049 | 2.0108 | 22.6332 | 0.7413 | 29.1339 | 0 | 24.9702 | 202.0577 | 0.5976%
CZ 8 | 0.20992 | 0.056278 | 0.21229 | 0.4544 | 0 | 0.086732 | 0 | 0.17793 | 0.050547 | 0.022973 | 0.019408 | 0.219 | 0.0071753 | 0.27391 | 0 | 0.24162 | 2.0322 | 0.07229% | CZ 8 | 7.0725 | 1.8961 | 19.8426 | 45.4397 | 0 | 2.9222 | 0 | 5.9949 | 1.703 | 0.774 | 0.6539 | 7.3786 | 0.24175 | 18.4346 | 0 | 8.1405 | 120.4943 | 0.07229% | CZ 8 | 2.0723 | 0.55556 | 0.20642 | 0 | 0 | 0.85619 | 0 | 1.7565 | 0.49899 | 0.22678 | 0.19159 | 2.1619 | 0.070832 | 1.3333 | 0 | 2.3852 | 12.3156 | 0.07229% | CZ 8 | 0 | 0 | 0.19138 | 0.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.78462 | 0.07229% | CZ 8 | 21.6944 | 5.8161 | 23.079 | 49.6655 | 0 | 8.9635 | 0 | 18.389 | 5.2239 | 2.3742 | 2.0058 | 22.6332 | 0.74154 | 29.1339 | 0 | 24.9702 | 214.6901 | 0.07229%
US Weighted | 0.21046 | 0.056718 | 0.18151 | 0.091197 | 0 | 0.36437 | 0 | 0.15241 | 0.049054 | 0.01898 | 0.019526 | 0.219 | 0.0071744 | 0.27391 | 0 | 0.24162 | 1.8859 | 100% | US Weighted | 7.0906 | 1.9109 | 16.7642 | 9.1197 | 0 | 12.2762 | 0 | 5.1349 | 1.6527 | 0.63946 | 0.65787 | 7.3786 | 0.24172 | 18.4346 | 0 | 8.1405 | 89.4419 | 100% | US Weighted | 2.0776 | 0.5599 | 0.2064 | 0 | 0 | 3.5969 | 0 | 1.5045 | 0.48424 | 0.18736 | 0.19276 | 2.1619 | 0.070823 | 1.3333 | 0 | 2.3852 | 14.7609 | 100% | US Weighted | 0 | 0 | 0.1606 | 0.091197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39063 | 100% | US Weighted | 21.7499 | 5.8616 | 19.7141 | 9.9679 | 0 | 37.6563 | 0 | 15.7508 | 5.0695 | 1.9615 | 2.018 | 22.6332 | 0.74145 | 29.1339 | 0 | 24.9702 | 197.2282 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.29293 | 0.056822 | 0.16196 | 0.010559 | 0 | 0.95323 | 0 | 0.21721 | 0.072121 | 0.026203 | 0.024275 | 0.21947 | 0.0075762 | 0.27391 | 0 | 0.26025 | 2.5765 | 2.703% | CZ 1A | 9.8692 | 1.9144 | 14.8099 | 1.0559 | 0 | 32.1158 | 0 | 7.3181 | 2.4299 | 0.88284 | 0.81786 | 7.3943 | 0.25526 | 18.4346 | 0 | 8.7683 | 106.0663 | 2.703% | CZ 1A | 2.8917 | 0.56092 | 0.2064 | 0 | 0 | 9.4099 | 0 | 2.1442 | 0.71196 | 0.25867 | 0.23963 | 2.1665 | 0.07479 | 1.3333 | 0 | 2.5691 | 22.5672 | 2.703% | CZ 1A | 0 | 0 | 0.14105 | 0.010559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.29045 | 2.703% | CZ 1A | 30.2729 | 5.8723 | 17.578 | 1.1541 | 0 | 98.5126 | 0 | 22.4477 | 7.4535 | 2.708 | 2.5087 | 22.6813 | 0.78297 | 29.1339 | 0 | 26.8962 | 268.0022 | 2.703%
CZ 1B | 0.29289 | 0.05675 | 0.16261 | 0.057688 | 0 | 1.2915 | 0 | 0.3085 | 0.0070048 | 0.039238 | 0.024505 | 0.21947 | 0.0075716 | 0.27391 | 0 | 0.26025 | 3.0019 | 0% | CZ 1B | 9.8679 | 1.912 | 14.8751 | 5.7688 | 0 | 43.5141 | 0 | 10.3937 | 0.236 | 1.322 | 0.82562 | 7.3943 | 0.2551 | 18.4346 | 0 | 8.7683 | 123.5676 | 0% | CZ 1B | 2.8913 | 0.56022 | 0.20635 | 0 | 0 | 12.7496 | 0 | 3.0454 | 0.069149 | 0.38735 | 0.24191 | 2.1665 | 0.074744 | 1.3333 | 0 | 2.5691 | 26.295 | 0% | CZ 1B | 0 | 0 | 0.14171 | 0.057688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33824 | 0% | CZ 1B | 30.2691 | 5.8649 | 17.6491 | 6.3053 | 0 | 133.476 | 0 | 31.8819 | 0.72392 | 4.0551 | 2.5325 | 22.6813 | 0.7825 | 29.1339 | 0 | 26.8962 | 312.2516 | 0%
CZ 2A | 0.29295 | 0.056732 | 0.16779 | 0.042393 | 0 | 0.82234 | 0 | 0.19151 | 0.057024 | 0.026266 | 0.024249 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 2.4425 | 13.88% | CZ 2A | 9.87 | 1.9114 | 15.393 | 4.2393 | 0 | 27.7061 | 0 | 6.4523 | 1.9212 | 0.88493 | 0.817 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 104.0476 | 13.88% | CZ 2A | 2.8919 | 0.56004 | 0.2064 | 0 | 0 | 8.1179 | 0 | 1.8905 | 0.56293 | 0.25929 | 0.23938 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 20.8721 | 13.88% | CZ 2A | 0 | 0 | 0.14689 | 0.042393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32812 | 13.88% | CZ 2A | 30.2753 | 5.863 | 18.2154 | 4.6336 | 0 | 84.9861 | 0 | 19.792 | 5.8933 | 2.7145 | 2.5061 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 254.3732 | 13.88%
CZ 2B | 0.29317 | 0.056771 | 0.1682 | 0.081981 | 0 | 0.665 | 0 | 0.21056 | 0.0053112 | 0.021247 | 0.024146 | 0.21947 | 0.0075762 | 0.27391 | 0 | 0.26025 | 2.2876 | 2.523% | CZ 2B | 9.8774 | 1.9127 | 15.4339 | 8.1981 | 0 | 22.405 | 0 | 7.0943 | 0.17894 | 0.71585 | 0.81351 | 7.3943 | 0.25526 | 18.4346 | 0 | 8.7683 | 101.4821 | 2.523% | CZ 2B | 2.8941 | 0.56042 | 0.2064 | 0 | 0 | 6.5647 | 0 | 2.0786 | 0.05243 | 0.20974 | 0.23836 | 2.1665 | 0.07479 | 1.3333 | 0 | 2.5691 | 18.9485 | 2.523% | CZ 2B | 0 | 0 | 0.14729 | 0.081981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36811 | 2.523% | CZ 2B | 30.2981 | 5.8671 | 18.2601 | 8.9605 | 0 | 68.7256 | 0 | 21.7611 | 0.54889 | 2.1958 | 2.4954 | 22.6813 | 0.78297 | 29.1339 | 0 | 26.8962 | 238.6068 | 2.523%
CZ 3A | 0.29259 | 0.056762 | 0.17795 | 0.081206 | 0 | 0.48543 | 0 | 0.17524 | 0.048838 | 0.021157 | 0.024206 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 2.1246 | 14.22% | CZ 3A | 9.858 | 1.9124 | 16.4085 | 8.1206 | 0 | 16.3549 | 0 | 5.9041 | 1.6454 | 0.71282 | 0.81553 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 96.5846 | 14.22% | CZ 3A | 2.8884 | 0.56033 | 0.2064 | 0 | 0 | 4.792 | 0 | 1.7299 | 0.48211 | 0.20886 | 0.23895 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 17.2507 | 14.22% | CZ 3A | 0 | 0 | 0.15704 | 0.081206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37709 | 14.22% | CZ 3A | 30.2386 | 5.8661 | 19.3253 | 8.8759 | 0 | 50.1673 | 0 | 18.1103 | 5.0472 | 2.1865 | 2.5016 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 221.8128 | 14.22%
CZ 3B | 0.29261 | 0.056759 | 0.17534 | 0.13057 | 0 | 0.47705 | 0 | 0.19728 | 0 | 0.020095 | 0.02415 | 0.21947 | 0.0075762 | 0.27391 | 0 | 0.26025 | 2.1351 | 16.01% | CZ 3B | 9.8584 | 1.9123 | 16.1474 | 13.0574 | 0 | 16.0725 | 0 | 6.6467 | 0 | 0.67703 | 0.81367 | 7.3943 | 0.25526 | 18.4346 | 0 | 8.7683 | 100.0378 | 16.01% | CZ 3B | 2.8885 | 0.56031 | 0.2064 | 0 | 0 | 4.7092 | 0 | 1.9475 | 0 | 0.19837 | 0.2384 | 2.1665 | 0.07479 | 1.3333 | 0 | 2.5691 | 16.8925 | 16.01% | CZ 3B | 0 | 0 | 0.15443 | 0.13057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.42384 | 16.01% | CZ 3B | 30.2398 | 5.8659 | 19.0399 | 14.2717 | 0 | 49.301 | 0 | 20.3883 | 0 | 2.0767 | 2.4959 | 22.6813 | 0.78297 | 29.1339 | 0 | 26.8962 | 223.1735 | 16.01%
CZ 3C | 0.29255 | 0.05675 | 0.17905 | 0.075925 | 0 | 0.30536 | 0 | 0.17372 | 0 | 0.016351 | 0.024236 | 0.21947 | 0.0075762 | 0.27391 | 0 | 0.26025 | 1.8851 | 2.133% | CZ 3C | 9.8566 | 1.912 | 16.5189 | 7.5925 | 0 | 10.2881 | 0 | 5.8528 | 0 | 0.55088 | 0.81654 | 7.3943 | 0.25526 | 18.4346 | 0 | 8.7683 | 88.2408 | 2.133% | CZ 3C | 2.888 | 0.56022 | 0.2064 | 0 | 0 | 3.0144 | 0 | 1.7149 | 0 | 0.16141 | 0.23925 | 2.1665 | 0.07479 | 1.3333 | 0 | 2.5691 | 14.9283 | 2.133% | CZ 3C | 0 | 0 | 0.15814 | 0.075925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37291 | 2.133% | CZ 3C | 30.2343 | 5.8649 | 19.446 | 8.2987 | 0 | 31.5578 | 0 | 17.9529 | 0 | 1.6898 | 2.5047 | 22.6813 | 0.78297 | 29.1339 | 0 | 26.8962 | 197.0434 | 2.133%
CZ 4A | 0.2923 | 0.056674 | 0.18601 | 0.086964 | 0 | 0.33854 | 0 | 0.18414 | 0.053241 | 0.020164 | 0.024196 | 0.21947 | 0.0075762 | 0.27391 | 0 | 0.26025 | 2.0034 | 18.1% | CZ 4A | 9.848 | 1.9094 | 17.2144 | 8.6964 | 0 | 11.4058 | 0 | 6.2041 | 1.7938 | 0.67936 | 0.81522 | 7.3943 | 0.25526 | 18.4346 | 0 | 8.7683 | 93.4189 | 18.1% | CZ 4A | 2.8855 | 0.55947 | 0.2064 | 0 | 0 | 3.3419 | 0 | 1.8178 | 0.52558 | 0.19905 | 0.23886 | 2.1665 | 0.07479 | 1.3333 | 0 | 2.5691 | 15.9183 | 18.1% | CZ 4A | 0 | 0 | 0.1651 | 0.086964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3909 | 18.1% | CZ 4A | 30.2079 | 5.8571 | 20.2062 | 9.5051 | 0 | 34.9864 | 0 | 19.0305 | 5.5023 | 2.0839 | 2.5006 | 22.6813 | 0.78297 | 29.1339 | 0 | 26.8962 | 209.3742 | 18.1%
CZ 4B | 0.29233 | 0.056718 | 0.18371 | 0.21406 | 0 | 0.3239 | 0 | 0.20194 | 0 | 0.019049 | 0.024123 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 2.077 | 0.7301% | CZ 4B | 9.8492 | 1.9109 | 16.9847 | 21.4061 | 0 | 10.9129 | 0 | 6.8035 | 0 | 0.64179 | 0.81273 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 104.1742 | 0.7301% | CZ 4B | 2.8858 | 0.5599 | 0.2064 | 0 | 0 | 3.1975 | 0 | 1.9934 | 0 | 0.18804 | 0.23813 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 15.413 | 0.7301% | CZ 4B | 0 | 0 | 0.1628 | 0.21406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5157 | 0.7301% | CZ 4B | 30.2117 | 5.8616 | 19.9552 | 23.3968 | 0 | 33.4743 | 0 | 20.8693 | 0 | 1.9686 | 2.493 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 217.7246 | 0.7301%
CZ 4C | 0.29241 | 0.05661 | 0.18848 | 0.28361 | 0 | 0.14366 | 0 | 0.17406 | 0 | 0.019028 | 0.02418 | 0.21947 | 0.0075716 | 0.27391 | 0 | 0.26025 | 1.9432 | 2.455% | CZ 4C | 9.8519 | 1.9073 | 17.462 | 28.3606 | 0 | 4.8401 | 0 | 5.8645 | 0 | 0.64109 | 0.81467 | 7.3943 | 0.2551 | 18.4346 | 0 | 8.7683 | 104.5945 | 2.455% | CZ 4C | 2.8866 | 0.55883 | 0.2064 | 0 | 0 | 1.4182 | 0 | 1.7183 | 0 | 0.18784 | 0.2387 | 2.1665 | 0.074744 | 1.3333 | 0 | 2.5691 | 13.3586 | 2.455% | CZ 4C | 0 | 0 | 0.16758 | 0.28361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.59002 | 2.455% | CZ 4C | 30.22 | 5.8504 | 20.4768 | 30.9982 | 0 | 14.8468 | 0 | 17.9889 | 0 | 1.9665 | 2.4989 | 22.6813 | 0.7825 | 29.1339 | 0 | 26.8962 | 204.3403 | 2.455%
CZ 5A | 0.29229 | 0.056693 | 0.1929 | 0.13078 | 0 | 0.22322 | 0 | 0.18874 | 0.045439 | 0.018998 | 0.024183 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 1.9345 | 18.12% | CZ 5A | 9.8477 | 1.9101 | 17.9041 | 13.0784 | 0 | 7.5206 | 0 | 6.359 | 1.5309 | 0.64008 | 0.81475 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 94.4579 | 18.12% | CZ 5A | 2.8854 | 0.55965 | 0.2064 | 0 | 0 | 2.2035 | 0 | 1.8632 | 0.44856 | 0.18754 | 0.23872 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 14.7367 | 18.12% | CZ 5A | 0 | 0 | 0.172 | 0.13078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44162 | 18.12% | CZ 5A | 30.2069 | 5.859 | 20.96 | 14.2946 | 0 | 23.0689 | 0 | 19.5058 | 4.6959 | 1.9634 | 2.4992 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 202.5478 | 18.12%
CZ 5B | 0.29232 | 0.056695 | 0.19098 | 0.35336 | 0 | 0.24219 | 0 | 0.20272 | 0 | 0.020708 | 0.024095 | 0.21947 | 0.007567 | 0.27391 | 0 | 0.26025 | 2.1443 | 4.122% | CZ 5B | 9.8487 | 1.9101 | 17.711 | 35.3363 | 0 | 8.1596 | 0 | 6.8301 | 0 | 0.69768 | 0.8118 | 7.3943 | 0.25494 | 18.4346 | 0 | 8.7683 | 116.1575 | 4.122% | CZ 5B | 2.8857 | 0.55967 | 0.20642 | 0 | 0 | 2.3908 | 0 | 2.0012 | 0 | 0.20442 | 0.23786 | 2.1665 | 0.074699 | 1.3333 | 0 | 2.5691 | 14.6297 | 4.122% | CZ 5B | 0 | 0 | 0.17007 | 0.35336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.66227 | 4.122% | CZ 5B | 30.21 | 5.8592 | 20.7492 | 38.6226 | 0 | 25.029 | 0 | 20.9508 | 0 | 2.1401 | 2.4901 | 22.6813 | 0.78202 | 29.1339 | 0 | 26.8962 | 225.5443 | 4.122%
CZ 5C | 0.2923 | 0.056605 | 0.19238 | 0.083922 | 0 | 0.096343 | 0 | 0.18147 | 0.047681 | 0.012855 | 0.024206 | 0.21947 | 0.0075693 | 0.27391 | 0 | 0.26025 | 1.749 | 0.01984% | CZ 5C | 9.8482 | 1.9071 | 17.8515 | 8.3922 | 0 | 3.246 | 0 | 6.1142 | 1.6064 | 0.43311 | 0.81553 | 7.3943 | 0.25502 | 18.4346 | 0 | 8.7683 | 85.0664 | 0.01984% | CZ 5C | 2.8855 | 0.55879 | 0.2064 | 0 | 0 | 0.95107 | 0 | 1.7915 | 0.47069 | 0.1269 | 0.23895 | 2.1665 | 0.074722 | 1.3333 | 0 | 2.5691 | 13.3735 | 0.01984% | CZ 5C | 0 | 0 | 0.17147 | 0.083922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39423 | 0.01984% | CZ 5C | 30.2086 | 5.8499 | 20.9025 | 9.1727 | 0 | 9.9567 | 0 | 18.7547 | 4.9276 | 1.3285 | 2.5016 | 22.6813 | 0.78226 | 29.1339 | 0 | 26.8962 | 183.0964 | 0.01984%
CZ 6A | 0.29229 | 0.056665 | 0.19801 | 0.21288 | 0 | 0.23232 | 0 | 0.19941 | 0.047736 | 0.021242 | 0.02416 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 2.0459 | 3.21% | CZ 6A | 9.8477 | 1.9091 | 18.4149 | 21.2882 | 0 | 7.8273 | 0 | 6.7185 | 1.6083 | 0.71569 | 0.81398 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 103.9961 | 3.21% | CZ 6A | 2.8854 | 0.55938 | 0.2064 | 0 | 0 | 2.2934 | 0 | 1.9685 | 0.47124 | 0.2097 | 0.23849 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 14.9763 | 3.21% | CZ 6A | 0 | 0 | 0.1771 | 0.21288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52883 | 3.21% | CZ 6A | 30.2072 | 5.8561 | 21.5184 | 23.268 | 0 | 24.0096 | 0 | 20.6086 | 4.9334 | 2.1953 | 2.4968 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 214.5873 | 3.21%
CZ 6B | 0.29228 | 0.056626 | 0.19671 | 0.16504 | 0 | 0.16841 | 0 | 0.20765 | 0.048328 | 0.016814 | 0.024116 | 0.21947 | 0.0075716 | 0.27391 | 0 | 0.26025 | 1.9372 | 1.094% | CZ 6B | 9.8473 | 1.9078 | 18.2843 | 16.5035 | 0 | 5.6739 | 0 | 6.996 | 1.6283 | 0.56648 | 0.8125 | 7.3943 | 0.2551 | 18.4346 | 0 | 8.7683 | 97.0724 | 1.094% | CZ 6B | 2.8853 | 0.55899 | 0.2064 | 0 | 0 | 1.6625 | 0 | 2.0498 | 0.47708 | 0.16598 | 0.23806 | 2.1665 | 0.074744 | 1.3333 | 0 | 2.5691 | 14.3878 | 1.094% | CZ 6B | 0 | 0 | 0.1758 | 0.16504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.47967 | 1.094% | CZ 6B | 30.2057 | 5.8521 | 21.3756 | 18.0383 | 0 | 17.4043 | 0 | 21.4596 | 4.9946 | 1.7376 | 2.4923 | 22.6813 | 0.7825 | 29.1339 | 0 | 26.8962 | 203.054 | 1.094%
CZ 7 | 0.29221 | 0.056591 | 0.2041 | 0.3043 | 0 | 0.18504 | 0 | 0.20923 | 0.048167 | 0.02215 | 0.024125 | 0.21947 | 0.0075716 | 0.27391 | 0 | 0.26025 | 2.1071 | 0.5976% | CZ 7 | 9.845 | 1.9067 | 19.0234 | 30.4296 | 0 | 6.2344 | 0 | 7.0492 | 1.6228 | 0.74628 | 0.81281 | 7.3943 | 0.2551 | 18.4346 | 0 | 8.7683 | 112.5225 | 0.5976% | CZ 7 | 2.8846 | 0.55865 | 0.20642 | 0 | 0 | 1.8267 | 0 | 2.0654 | 0.47549 | 0.21866 | 0.23815 | 2.1665 | 0.074744 | 1.3333 | 0 | 2.5691 | 14.6178 | 0.5976% | CZ 7 | 0 | 0 | 0.18319 | 0.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.62632 | 0.5976% | CZ 7 | 30.1988 | 5.8485 | 22.1836 | 33.2595 | 0 | 19.1236 | 0 | 21.6228 | 4.9779 | 2.2892 | 2.4932 | 22.6813 | 0.7825 | 29.1339 | 0 | 26.8962 | 221.4909 | 0.5976%
CZ 8 | 0.29237 | 0.056278 | 0.2123 | 0.48883 | 0 | 0.10627 | 0 | 0.22923 | 0.050462 | 0.024295 | 0.024072 | 0.21947 | 0.0075739 | 0.27391 | 0 | 0.26025 | 2.2453 | 0.07229% | CZ 8 | 9.8503 | 1.8961 | 19.843 | 48.8826 | 0 | 3.5806 | 0 | 7.7231 | 1.7001 | 0.81856 | 0.81103 | 7.3943 | 0.25518 | 18.4346 | 0 | 8.7683 | 129.9577 | 0.07229% | CZ 8 | 2.8861 | 0.55556 | 0.20642 | 0 | 0 | 1.0491 | 0 | 2.2629 | 0.49814 | 0.23984 | 0.23763 | 2.1665 | 0.074767 | 1.3333 | 0 | 2.5691 | 14.0795 | 0.07229% | CZ 8 | 0 | 0 | 0.19139 | 0.48883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.81905 | 0.07229% | CZ 8 | 30.215 | 5.8161 | 23.0794 | 53.4287 | 0 | 10.9831 | 0 | 23.69 | 5.2151 | 2.5109 | 2.4878 | 22.6813 | 0.78274 | 29.1339 | 0 | 26.8962 | 236.92 | 0.07229%
US Weighted | 0.29253 | 0.056718 | 0.18151 | 0.11568 | 0 | 0.43676 | 0 | 0.18975 | 0.037212 | 0.021037 | 0.024189 | 0.21947 | 0.0075745 | 0.27391 | 0 | 0.26025 | 2.1166 | 100% | US Weighted | 9.8557 | 1.9109 | 16.7642 | 11.5675 | 0 | 14.7153 | 0 | 6.3931 | 1.2537 | 0.70878 | 0.81497 | 7.3943 | 0.2552 | 18.4346 | 0 | 8.7683 | 98.8365 | 100% | US Weighted | 2.8877 | 0.5599 | 0.2064 | 0 | 0 | 4.3116 | 0 | 1.8732 | 0.36734 | 0.20767 | 0.23879 | 2.1665 | 0.074773 | 1.3333 | 0 | 2.5691 | 16.7963 | 100% | US Weighted | 0 | 0 | 0.1606 | 0.11568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41511 | 100% | US Weighted | 30.2314 | 5.8616 | 19.7141 | 12.6433 | 0 | 45.138 | 0 | 19.6103 | 3.8457 | 2.1741 | 2.4999 | 22.6813 | 0.7828 | 29.1339 | 0 | 26.8962 | 221.2125 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.33467 | 0.070649 | 0.16246 | 0.016366 | 0 | 1.2135 | 0 | 0.23039 | 0 | 0.072039 | 0.024531 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.8988 | 2.703% | CZ 1A | 11.2757 | 2.3803 | 14.8265 | 1.6366 | 0 | 40.886 | 0 | 7.7622 | 0 | 2.4271 | 0.82647 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 117.3081 | 2.703% | CZ 1A | 3.3038 | 0.69742 | 0.21136 | 0 | 0 | 11.9796 | 0 | 2.2743 | 0 | 0.71114 | 0.24216 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 25.691 | 2.703% | CZ 1A | 0 | 0 | 0.14105 | 0.016366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.29626 | 2.703% | CZ 1A | 34.5873 | 7.3013 | 17.6296 | 1.7888 | 0 | 125.4143 | 0 | 23.8098 | 0 | 7.4449 | 2.5351 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 301.3397 | 2.703%
CZ 1B | 0.33467 | 0.070562 | 0.16323 | 0.073055 | 0 | 1.3448 | 0 | 0.28082 | 0 | 0.071843 | 0.024542 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 3.1376 | 0% | CZ 1B | 11.2757 | 2.3773 | 14.9031 | 7.3055 | 0 | 45.3074 | 0 | 9.4611 | 0 | 2.4205 | 0.82686 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 129.165 | 0% | CZ 1B | 3.3038 | 0.69656 | 0.21134 | 0 | 0 | 13.2751 | 0 | 2.7721 | 0 | 0.70921 | 0.24227 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 27.4816 | 0% | CZ 1B | 0 | 0 | 0.14182 | 0.073055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35371 | 0% | CZ 1B | 34.5873 | 7.2923 | 17.7133 | 7.9849 | 0 | 138.9768 | 0 | 29.0213 | 0 | 7.4247 | 2.5363 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 326.3652 | 0%
CZ 2A | 0.33467 | 0.070536 | 0.16829 | 0.072025 | 0 | 1.1007 | 0 | 0.20516 | 0 | 0.071405 | 0.02448 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.8214 | 13.88% | CZ 2A | 11.2757 | 2.3765 | 15.4097 | 7.2025 | 0 | 37.0848 | 0 | 6.9123 | 0 | 2.4058 | 0.82477 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 118.7795 | 13.88% | CZ 2A | 3.3038 | 0.69631 | 0.21136 | 0 | 0 | 10.8659 | 0 | 2.0253 | 0 | 0.70489 | 0.24166 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 24.3204 | 13.88% | CZ 2A | 0 | 0 | 0.14688 | 0.072025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35775 | 13.88% | CZ 2A | 34.5873 | 7.2897 | 18.267 | 7.8724 | 0 | 113.7547 | 0 | 21.2029 | 0 | 7.3794 | 2.5299 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 293.7119 | 13.88%
CZ 2B | 0.33467 | 0.070589 | 0.1687 | 0.081338 | 0 | 0.71277 | 0 | 0.22202 | 0 | 0.048918 | 0.024275 | 0.22539 | 0.013189 | 0.27391 | 0 | 0.26162 | 2.4374 | 2.523% | CZ 2B | 11.2757 | 2.3783 | 15.4506 | 8.1338 | 0 | 24.0145 | 0 | 7.4801 | 0 | 1.6481 | 0.81786 | 7.5938 | 0.44437 | 18.4346 | 0 | 8.8145 | 106.4862 | 2.523% | CZ 2B | 3.3038 | 0.69683 | 0.21136 | 0 | 0 | 7.0362 | 0 | 2.1917 | 0 | 0.4829 | 0.23963 | 2.225 | 0.1302 | 1.3333 | 0 | 2.5827 | 20.4336 | 2.523% | CZ 2B | 0 | 0 | 0.14729 | 0.081338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36747 | 2.523% | CZ 2B | 34.5873 | 7.2951 | 18.3117 | 8.8903 | 0 | 73.6625 | 0 | 22.9446 | 0 | 5.0555 | 2.5087 | 23.2933 | 1.3631 | 29.1339 | 0 | 27.0379 | 254.0839 | 2.523%
CZ 3A | 0.33467 | 0.070575 | 0.17845 | 0.18242 | 0 | 0.61591 | 0 | 0.18784 | 0 | 0.051718 | 0.024369 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.4201 | 14.22% | CZ 3A | 11.2757 | 2.3778 | 16.4252 | 18.2418 | 0 | 20.7511 | 0 | 6.3285 | 0 | 1.7425 | 0.82104 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 113.2511 | 14.22% | CZ 3A | 3.3038 | 0.6967 | 0.21136 | 0 | 0 | 6.0801 | 0 | 1.8543 | 0 | 0.51054 | 0.24056 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 19.1685 | 14.22% | CZ 3A | 0 | 0 | 0.15704 | 0.18242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.4783 | 14.22% | CZ 3A | 34.5873 | 7.2937 | 19.377 | 19.9383 | 0 | 63.6522 | 0 | 19.4122 | 0 | 5.3448 | 2.5185 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 252.9526 | 14.22%
CZ 3B | 0.33467 | 0.070573 | 0.17585 | 0.12289 | 0 | 0.49978 | 0 | 0.20735 | 0 | 0.04057 | 0.024277 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.2501 | 16.01% | CZ 3B | 11.2757 | 2.3777 | 16.1651 | 12.2886 | 0 | 16.8384 | 0 | 6.986 | 0 | 1.3669 | 0.81794 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 103.4036 | 16.01% | CZ 3B | 3.3038 | 0.69667 | 0.21136 | 0 | 0 | 4.9336 | 0 | 2.0469 | 0 | 0.40049 | 0.23965 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 18.1037 | 16.01% | CZ 3B | 0 | 0 | 0.15444 | 0.12289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41616 | 16.01% | CZ 3B | 34.5873 | 7.2935 | 19.0927 | 13.4315 | 0 | 51.6504 | 0 | 21.4289 | 0 | 4.1928 | 2.5089 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 235.0143 | 16.01%
CZ 3C | 0.33467 | 0.070562 | 0.17954 | 0.086446 | 0 | 0.35291 | 0 | 0.17826 | 0 | 0.037876 | 0.024438 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.0388 | 2.133% | CZ 3C | 11.2757 | 2.3773 | 16.5347 | 8.6446 | 0 | 11.89 | 0 | 6.006 | 0 | 1.2761 | 0.82337 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 94.1152 | 2.133% | CZ 3C | 3.3038 | 0.69656 | 0.21136 | 0 | 0 | 3.4838 | 0 | 1.7597 | 0 | 0.3739 | 0.24125 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 16.3416 | 2.133% | CZ 3C | 0 | 0 | 0.15813 | 0.086446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.38342 | 2.133% | CZ 3C | 34.5873 | 7.2923 | 19.4967 | 9.4485 | 0 | 36.4717 | 0 | 18.4228 | 0 | 3.9144 | 2.5256 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 212.9877 | 2.133%
CZ 4A | 0.33467 | 0.070467 | 0.18652 | 0.30726 | 0 | 0.4314 | 0 | 0.18385 | 0 | 0.044609 | 0.024293 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.3572 | 18.1% | CZ 4A | 11.2757 | 2.3742 | 17.2326 | 30.7255 | 0 | 14.5346 | 0 | 6.1941 | 0 | 1.503 | 0.81848 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 119.9455 | 18.1% | CZ 4A | 3.3038 | 0.69563 | 0.21138 | 0 | 0 | 4.2586 | 0 | 1.8149 | 0 | 0.44037 | 0.23981 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 17.2357 | 18.1% | CZ 4A | 0 | 0 | 0.16511 | 0.30726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.61121 | 18.1% | CZ 4A | 34.5873 | 7.2825 | 20.2597 | 33.583 | 0 | 44.5836 | 0 | 18.9998 | 0 | 4.6102 | 2.5106 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 247.2453 | 18.1%
CZ 4B | 0.33467 | 0.07052 | 0.18422 | 0.19433 | 0 | 0.34003 | 0 | 0.20952 | 0 | 0.034386 | 0.024208 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.166 | 0.7301% | CZ 4B | 11.2757 | 2.3759 | 17.0024 | 19.4331 | 0 | 11.4562 | 0 | 7.059 | 0 | 1.1585 | 0.81561 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 105.8639 | 0.7301% | CZ 4B | 3.3038 | 0.69615 | 0.21136 | 0 | 0 | 3.3567 | 0 | 2.0683 | 0 | 0.33944 | 0.23897 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 16.4859 | 0.7301% | CZ 4B | 0 | 0 | 0.16281 | 0.19433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.49598 | 0.7301% | CZ 4B | 34.5873 | 7.288 | 20.0079 | 21.2404 | 0 | 35.141 | 0 | 21.6528 | 0 | 3.5536 | 2.5018 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 226.8014 | 0.7301%
CZ 4C | 0.33467 | 0.070386 | 0.18899 | 0.26925 | 0 | 0.16633 | 0 | 0.17848 | 0 | 0.0293 | 0.02433 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.0359 | 2.455% | CZ 4C | 11.2757 | 2.3714 | 17.4789 | 26.9252 | 0 | 5.6039 | 0 | 6.0133 | 0 | 0.98717 | 0.81972 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 106.7628 | 2.455% | CZ 4C | 3.3038 | 0.69483 | 0.21136 | 0 | 0 | 1.6419 | 0 | 1.7619 | 0 | 0.28924 | 0.24018 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 14.4145 | 2.455% | CZ 4C | 0 | 0 | 0.16758 | 0.26925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.57567 | 2.455% | CZ 4C | 34.5873 | 7.2742 | 20.5287 | 29.4293 | 0 | 17.1895 | 0 | 18.4451 | 0 | 3.0281 | 2.5144 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 213.8254 | 2.455%
CZ 5A | 0.33467 | 0.070488 | 0.19343 | 0.42917 | 0 | 0.26594 | 0 | 0.18532 | 0 | 0.037846 | 0.024233 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.3152 | 18.12% | CZ 5A | 11.2757 | 2.3749 | 17.9232 | 42.9165 | 0 | 8.96 | 0 | 6.2438 | 0 | 1.2751 | 0.81646 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 127.0731 | 18.12% | CZ 5A | 3.3038 | 0.69583 | 0.21138 | 0 | 0 | 2.6253 | 0 | 1.8294 | 0 | 0.37361 | 0.23922 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 15.5498 | 18.12% | CZ 5A | 0 | 0 | 0.17202 | 0.42917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.74002 | 18.12% | CZ 5A | 34.5873 | 7.2847 | 21.0144 | 46.9077 | 0 | 27.4841 | 0 | 19.1524 | 0 | 3.9113 | 2.5044 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 243.675 | 18.12%
CZ 5B | 0.33467 | 0.070492 | 0.19148 | 0.29864 | 0 | 0.26699 | 0 | 0.20974 | 0 | 0.032054 | 0.024176 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.2024 | 4.122% | CZ 5B | 11.2757 | 2.375 | 17.7278 | 29.8643 | 0 | 8.9954 | 0 | 7.0666 | 0 | 1.0799 | 0.81452 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 114.4867 | 4.122% | CZ 5B | 3.3038 | 0.69588 | 0.21138 | 0 | 0 | 2.6357 | 0 | 2.0705 | 0 | 0.31642 | 0.23865 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 15.7435 | 4.122% | CZ 5B | 0 | 0 | 0.17006 | 0.29864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.60755 | 4.122% | CZ 5B | 34.5873 | 7.2851 | 20.8009 | 32.6417 | 0 | 27.5927 | 0 | 21.6763 | 0 | 3.3126 | 2.4985 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 231.2236 | 4.122%
CZ 5C | 0.33467 | 0.070382 | 0.1929 | 0.32588 | 0 | 0.10626 | 0 | 0.1757 | 0 | 0.025316 | 0.024309 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.0295 | 0.01984% | CZ 5C | 11.2757 | 2.3713 | 17.8702 | 32.5878 | 0 | 3.5799 | 0 | 5.9197 | 0 | 0.85295 | 0.81902 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 110.564 | 0.01984% | CZ 5C | 3.3038 | 0.69479 | 0.21136 | 0 | 0 | 1.0489 | 0 | 1.7345 | 0 | 0.24991 | 0.23997 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 13.7544 | 0.01984% | CZ 5C | 0 | 0 | 0.17149 | 0.32588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.63621 | 0.01984% | CZ 5C | 34.5873 | 7.2737 | 20.9564 | 35.6184 | 0 | 10.9812 | 0 | 18.1582 | 0 | 2.6163 | 2.5123 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 213.5325 | 0.01984%
CZ 6A | 0.33467 | 0.070456 | 0.19854 | 0.56533 | 0 | 0.27928 | 0 | 0.19754 | 0 | 0.041722 | 0.024176 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.4858 | 3.21% | CZ 6A | 11.2757 | 2.3738 | 18.4336 | 56.5326 | 0 | 9.4093 | 0 | 6.6554 | 0 | 1.4057 | 0.81452 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 142.1881 | 3.21% | CZ 6A | 3.3038 | 0.69551 | 0.2114 | 0 | 0 | 2.7569 | 0 | 1.95 | 0 | 0.41187 | 0.23865 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 15.8394 | 3.21% | CZ 6A | 0 | 0 | 0.17712 | 0.56533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.88129 | 3.21% | CZ 6A | 34.5873 | 7.2813 | 21.5725 | 61.7902 | 0 | 28.8622 | 0 | 20.415 | 0 | 4.3118 | 2.4985 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 262.1475 | 3.21%
CZ 6B | 0.33467 | 0.070405 | 0.19724 | 0.44726 | 0 | 0.19305 | 0 | 0.20504 | 0 | 0.031973 | 0.024139 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.2779 | 1.094% | CZ 6B | 11.2757 | 2.3721 | 18.3041 | 44.7255 | 0 | 6.5042 | 0 | 6.9081 | 0 | 1.0772 | 0.81328 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 127.2677 | 1.094% | CZ 6B | 3.3038 | 0.69501 | 0.21138 | 0 | 0 | 1.9057 | 0 | 2.0241 | 0 | 0.31563 | 0.23829 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 14.9652 | 1.094% | CZ 6B | 0 | 0 | 0.17583 | 0.44726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.76192 | 1.094% | CZ 6B | 34.5873 | 7.2761 | 21.4308 | 48.885 | 0 | 19.9511 | 0 | 21.1901 | 0 | 3.3043 | 2.4947 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 239.9481 | 1.094%
CZ 7 | 0.33467 | 0.070361 | 0.20464 | 0.7125 | 0 | 0.21983 | 0 | 0.20839 | 0 | 0.040109 | 0.024104 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.5887 | 0.5976% | CZ 7 | 11.2757 | 2.3706 | 19.0434 | 71.2504 | 0 | 7.4064 | 0 | 7.021 | 0 | 1.3513 | 0.81211 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 155.8183 | 0.5976% | CZ 7 | 3.3038 | 0.69458 | 0.21143 | 0 | 0 | 2.1701 | 0 | 2.0572 | 0 | 0.39594 | 0.23795 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 15.3421 | 0.5976% | CZ 7 | 0 | 0 | 0.18322 | 0.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.0346 | 0.5976% | CZ 7 | 34.5873 | 7.2716 | 22.2391 | 77.8767 | 0 | 22.7184 | 0 | 21.5363 | 0 | 4.1451 | 2.4911 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 273.6943 | 0.5976%
CZ 8 | 0.33467 | 0.069974 | 0.21283 | 0.999 | 0 | 0.12085 | 0 | 0.22817 | 0 | 0.038519 | 0.02398 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.8021 | 0.07229% | CZ 8 | 11.2757 | 2.3575 | 19.8623 | 99.8996 | 0 | 4.0717 | 0 | 7.6874 | 0 | 1.2978 | 0.80792 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 182.5474 | 0.07229% | CZ 8 | 3.3038 | 0.69076 | 0.21145 | 0 | 0 | 1.193 | 0 | 2.2524 | 0 | 0.38025 | 0.23672 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 14.5396 | 0.07229% | CZ 8 | 0 | 0 | 0.19141 | 0.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.3292 | 0.07229% | CZ 8 | 34.5873 | 7.2316 | 23.1344 | 109.1903 | 0 | 12.4895 | 0 | 23.5804 | 0 | 3.9808 | 2.4782 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 297.5012 | 0.07229%
US Weighted | 0.33467 | 0.07052 | 0.18202 | 0.24177 | 0 | 0.53511 | 0 | 0.19548 | 0 | 0.046941 | 0.024314 | 0.22539 | 0.013193 | 0.27391 | 0 | 0.26162 | 2.4049 | 100% | US Weighted | 11.2757 | 2.3759 | 16.7819 | 24.1765 | 0 | 18.0288 | 0 | 6.586 | 0 | 1.5815 | 0.81918 | 7.5938 | 0.44451 | 18.4346 | 0 | 8.8145 | 116.9129 | 100% | US Weighted | 3.3038 | 0.69615 | 0.21137 | 0 | 0 | 5.2824 | 0 | 1.9297 | 0 | 0.46339 | 0.24002 | 2.225 | 0.13024 | 1.3333 | 0 | 2.5827 | 18.3981 | 100% | US Weighted | 0 | 0 | 0.1606 | 0.24177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.54121 | 100% | US Weighted | 34.5873 | 7.288 | 19.7669 | 26.4249 | 0 | 55.3019 | 0 | 20.202 | 0 | 4.8512 | 2.5128 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 251.7635 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.33467 | 0.070649 | 0.16246 | 0.038402 | 0 | 1.1239 | 0 | 0.24136 | 0.11174 | 0.082301 | 0.024528 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.9641 | 2.703% | CZ 1A | 11.2757 | 2.3803 | 14.8265 | 3.8402 | 0 | 37.8656 | 0 | 8.1319 | 3.7646 | 2.7729 | 0.8264 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 120.9714 | 2.703% | CZ 1A | 3.3038 | 0.69742 | 0.21136 | 0 | 0 | 11.0946 | 0 | 2.3827 | 1.103 | 0.81245 | 0.24213 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 26.1186 | 2.703% | CZ 1A | 0 | 0 | 0.14105 | 0.038402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31829 | 2.703% | CZ 1A | 34.5873 | 7.3013 | 17.6297 | 4.1974 | 0 | 116.1496 | 0 | 24.944 | 11.5474 | 8.5056 | 2.5349 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 308.2255 | 2.703%
CZ 1B | 0.33467 | 0.070562 | 0.16322 | 0.10321 | 0 | 1.53 | 0 | 0.29792 | 0.010811 | 0.081281 | 0.02457 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 3.3904 | 0% | CZ 1B | 11.2757 | 2.3773 | 14.9029 | 10.3207 | 0 | 51.5485 | 0 | 10.0376 | 0.36425 | 2.7385 | 0.82779 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 139.6807 | 0% | CZ 1B | 3.3038 | 0.69656 | 0.21131 | 0 | 0 | 15.1037 | 0 | 2.941 | 0.10673 | 0.80238 | 0.24254 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 29.6793 | 0% | CZ 1B | 0 | 0 | 0.14182 | 0.10321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.38386 | 0% | CZ 1B | 34.5873 | 7.2923 | 17.7128 | 11.2806 | 0 | 158.1209 | 0 | 30.7894 | 1.1173 | 8.4001 | 2.5392 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 352.6684 | 0%
CZ 2A | 0.33467 | 0.070536 | 0.16829 | 0.1077 | 0 | 1.0646 | 0 | 0.23319 | 0.10785 | 0.085193 | 0.024466 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.9706 | 13.88% | CZ 2A | 11.2757 | 2.3765 | 15.4096 | 10.7699 | 0 | 35.8691 | 0 | 7.8567 | 3.6335 | 2.8703 | 0.8243 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 126.1729 | 13.88% | CZ 2A | 3.3038 | 0.69631 | 0.21136 | 0 | 0 | 10.5097 | 0 | 2.302 | 1.0646 | 0.841 | 0.24152 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 25.4415 | 13.88% | CZ 2A | 0 | 0 | 0.14688 | 0.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39342 | 13.88% | CZ 2A | 34.5873 | 7.2897 | 18.2669 | 11.7715 | 0 | 110.0256 | 0 | 24.0998 | 11.1455 | 8.8044 | 2.5285 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 309.3475 | 13.88%
CZ 2B | 0.33467 | 0.070589 | 0.1687 | 0.16055 | 0 | 0.84309 | 0 | 0.25942 | 0.008408 | 0.058764 | 0.024238 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.7025 | 2.523% | CZ 2B | 11.2757 | 2.3783 | 15.4506 | 16.055 | 0 | 28.4052 | 0 | 8.7402 | 0.28328 | 1.9799 | 0.81662 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 120.6721 | 2.523% | CZ 2B | 3.3038 | 0.69683 | 0.21136 | 0 | 0 | 8.3227 | 0 | 2.5609 | 0.083001 | 0.5801 | 0.23927 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 22.2691 | 2.523% | CZ 2B | 0 | 0 | 0.14729 | 0.16055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44668 | 2.523% | CZ 2B | 34.5873 | 7.2951 | 18.3118 | 17.5481 | 0 | 87.1305 | 0 | 26.8097 | 0.86894 | 6.0731 | 2.5049 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 281.958 | 2.523%
CZ 3A | 0.33467 | 0.070575 | 0.17845 | 0.1446 | 0 | 0.61266 | 0 | 0.20794 | 0.10347 | 0.058633 | 0.024385 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.5095 | 14.22% | CZ 3A | 11.2757 | 2.3778 | 16.4253 | 14.4604 | 0 | 20.6414 | 0 | 7.0059 | 3.4861 | 1.9754 | 0.82158 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 113.7572 | 14.22% | CZ 3A | 3.3038 | 0.6967 | 0.21136 | 0 | 0 | 6.0479 | 0 | 2.0527 | 1.0214 | 0.5788 | 0.24072 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 20.4247 | 14.22% | CZ 3A | 0 | 0 | 0.15704 | 0.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44048 | 14.22% | CZ 3A | 34.5873 | 7.2937 | 19.3771 | 15.8052 | 0 | 63.3159 | 0 | 21.4901 | 10.6933 | 6.0595 | 2.5201 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 261.9711 | 14.22%
CZ 3B | 0.33467 | 0.070573 | 0.17585 | 0.2095 | 0 | 0.55093 | 0 | 0.22336 | 0.0062651 | 0.04669 | 0.024245 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.4162 | 16.01% | CZ 3B | 11.2757 | 2.3777 | 16.1655 | 20.9495 | 0 | 18.5618 | 0 | 7.5254 | 0.21108 | 1.5731 | 0.81685 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 114.7441 | 16.01% | CZ 3B | 3.3038 | 0.69667 | 0.21136 | 0 | 0 | 5.4386 | 0 | 2.2049 | 0.061847 | 0.46091 | 0.23934 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 18.8887 | 16.01% | CZ 3B | 0 | 0 | 0.15444 | 0.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.50278 | 16.01% | CZ 3B | 34.5873 | 7.2935 | 19.0932 | 22.8978 | 0 | 56.9369 | 0 | 23.0835 | 0.64748 | 4.8252 | 2.5056 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 252.6991 | 16.01%
CZ 3C | 0.33467 | 0.070562 | 0.17954 | 0.14242 | 0 | 0.38741 | 0 | 0.2022 | 0 | 0.041957 | 0.024425 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.1573 | 2.133% | CZ 3C | 11.2757 | 2.3773 | 16.5344 | 14.242 | 0 | 13.0526 | 0 | 6.8125 | 0 | 1.4136 | 0.8229 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 101.8185 | 2.133% | CZ 3C | 3.3038 | 0.69656 | 0.21136 | 0 | 0 | 3.8244 | 0 | 1.9961 | 0 | 0.41419 | 0.24111 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 16.9587 | 2.133% | CZ 3C | 0 | 0 | 0.15813 | 0.14242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.43939 | 2.133% | CZ 3C | 34.5873 | 7.2923 | 19.4964 | 15.5665 | 0 | 40.0377 | 0 | 20.8967 | 0 | 4.3361 | 2.5242 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 225.566 | 2.133%
CZ 4A | 0.33467 | 0.070467 | 0.18652 | 0.22686 | 0 | 0.43335 | 0 | 0.21105 | 0.10163 | 0.048075 | 0.024307 | 0.22539 | 0.013196 | 0.27391 | 0 | 0.26162 | 2.4111 | 18.1% | CZ 4A | 11.2757 | 2.3742 | 17.2323 | 22.6859 | 0 | 14.6003 | 0 | 7.1106 | 3.4241 | 1.6197 | 0.81894 | 7.5938 | 0.4446 | 18.4346 | 0 | 8.8145 | 116.4293 | 18.1% | CZ 4A | 3.3038 | 0.69563 | 0.21138 | 0 | 0 | 4.2779 | 0 | 2.0834 | 1.0033 | 0.47458 | 0.23995 | 2.225 | 0.13027 | 1.3333 | 0 | 2.5827 | 18.5611 | 18.1% | CZ 4A | 0 | 0 | 0.16511 | 0.22686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.53081 | 18.1% | CZ 4A | 34.5873 | 7.2825 | 20.2594 | 24.7957 | 0 | 44.7853 | 0 | 21.8111 | 10.5032 | 4.9684 | 2.512 | 23.2933 | 1.3638 | 29.1339 | 0 | 27.0379 | 252.3338 | 18.1%
CZ 4B | 0.33467 | 0.07052 | 0.18422 | 0.32168 | 0 | 0.36449 | 0 | 0.2278 | 0.0037812 | 0.041591 | 0.024143 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.347 | 0.7301% | CZ 4B | 11.2757 | 2.3759 | 17.0021 | 32.1676 | 0 | 12.2803 | 0 | 7.6749 | 0.12739 | 1.4013 | 0.81343 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 120.4059 | 0.7301% | CZ 4B | 3.3038 | 0.69615 | 0.21138 | 0 | 0 | 3.5981 | 0 | 2.2487 | 0.037327 | 0.41057 | 0.23834 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 17.0156 | 0.7301% | CZ 4B | 0 | 0 | 0.16281 | 0.32168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.62332 | 0.7301% | CZ 4B | 34.5873 | 7.288 | 20.0077 | 35.1592 | 0 | 37.6687 | 0 | 23.5421 | 0.39077 | 4.2983 | 2.4951 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 246.2657 | 0.7301%
CZ 4C | 0.33467 | 0.070386 | 0.18908 | 0.27819 | 0 | 0.1582 | 0 | 0.24581 | 0.059365 | 0.02904 | 0.024003 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.1628 | 2.455% | CZ 4C | 11.2757 | 2.3714 | 17.487 | 27.8186 | 0 | 5.3299 | 0 | 8.2816 | 2.0001 | 0.9784 | 0.8087 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 111.6388 | 2.455% | CZ 4C | 3.3038 | 0.69483 | 0.21154 | 0 | 0 | 1.5617 | 0 | 2.4265 | 0.58604 | 0.28667 | 0.23695 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 15.5792 | 2.455% | CZ 4C | 0 | 0 | 0.16765 | 0.27819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.58467 | 2.455% | CZ 4C | 34.5873 | 7.2742 | 20.5388 | 30.4057 | 0 | 16.3491 | 0 | 25.4031 | 6.1352 | 3.0012 | 2.4806 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 227.0037 | 2.455%
CZ 5A | 0.33467 | 0.070488 | 0.19352 | 0.33705 | 0 | 0.28266 | 0 | 0.26749 | 0.096746 | 0.040932 | 0.023895 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.4216 | 18.12% | CZ 5A | 11.2757 | 2.3749 | 17.931 | 33.705 | 0 | 9.5232 | 0 | 9.0123 | 3.2596 | 1.3791 | 0.80505 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 124.5532 | 18.12% | CZ 5A | 3.3038 | 0.69583 | 0.21156 | 0 | 0 | 2.7903 | 0 | 2.6406 | 0.95505 | 0.40407 | 0.23588 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 17.5083 | 18.12% | CZ 5A | 0 | 0 | 0.17209 | 0.33705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.64798 | 18.12% | CZ 5A | 34.5873 | 7.2847 | 21.0242 | 36.8396 | 0 | 29.2118 | 0 | 27.6444 | 9.9984 | 4.2302 | 2.4694 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 254.1185 | 18.12%
CZ 5B | 0.33467 | 0.070492 | 0.19148 | 0.50882 | 0 | 0.27265 | 0 | 0.23222 | 0.0026337 | 0.039068 | 0.02409 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.4502 | 4.122% | CZ 5B | 11.2757 | 2.375 | 17.7276 | 50.8822 | 0 | 9.186 | 0 | 7.8238 | 0.088734 | 1.3163 | 0.81165 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 136.7743 | 4.122% | CZ 5B | 3.3038 | 0.69588 | 0.2114 | 0 | 0 | 2.6915 | 0 | 2.2924 | 0.025999 | 0.38566 | 0.23781 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 16.1156 | 4.122% | CZ 5B | 0 | 0 | 0.17006 | 0.50882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.81772 | 4.122% | CZ 5B | 34.5873 | 7.2851 | 20.8008 | 55.6143 | 0 | 28.1773 | 0 | 23.9988 | 0.27218 | 4.0375 | 2.4897 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 258.0914 | 4.122%
CZ 5C | 0.33467 | 0.070382 | 0.19302 | 0.30962 | 0 | 0.097412 | 0 | 0.26064 | 0.068437 | 0.023929 | 0.023897 | 0.22539 | 0.013189 | 0.27391 | 0 | 0.26162 | 2.1561 | 0.01984% | CZ 5C | 11.2757 | 2.3713 | 17.881 | 30.962 | 0 | 3.282 | 0 | 8.7815 | 2.3058 | 0.80621 | 0.80513 | 7.5938 | 0.44437 | 18.4346 | 0 | 8.8145 | 113.7579 | 0.01984% | CZ 5C | 3.3038 | 0.69479 | 0.21159 | 0 | 0 | 0.96162 | 0 | 2.573 | 0.67559 | 0.23622 | 0.2359 | 2.225 | 0.1302 | 1.3333 | 0 | 2.5827 | 15.1637 | 0.01984% | CZ 5C | 0 | 0 | 0.17159 | 0.30962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.62005 | 0.01984% | CZ 5C | 34.5873 | 7.2737 | 20.9698 | 33.8415 | 0 | 10.0672 | 0 | 26.9367 | 7.0727 | 2.473 | 2.4697 | 23.2933 | 1.3631 | 29.1339 | 0 | 27.0379 | 226.5196 | 0.01984%
CZ 6A | 0.33467 | 0.070456 | 0.19864 | 0.45463 | 0 | 0.29348 | 0 | 0.27849 | 0.096783 | 0.045847 | 0.023892 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.571 | 3.21% | CZ 6A | 11.2757 | 2.3738 | 18.4426 | 45.4635 | 0 | 9.888 | 0 | 9.3827 | 3.2608 | 1.5447 | 0.80497 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 137.724 | 3.21% | CZ 6A | 3.3038 | 0.69551 | 0.21156 | 0 | 0 | 2.8972 | 0 | 2.7491 | 0.95541 | 0.45258 | 0.23586 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 17.7722 | 3.21% | CZ 6A | 0 | 0 | 0.17721 | 0.45463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.77068 | 3.21% | CZ 6A | 34.5873 | 7.2813 | 21.5834 | 49.6916 | 0 | 30.3305 | 0 | 28.7805 | 10.0022 | 4.7381 | 2.4692 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 270.2927 | 3.21%
CZ 6B | 0.33467 | 0.070405 | 0.19734 | 0.38227 | 0 | 0.20225 | 0 | 0.25902 | 0.096251 | 0.033614 | 0.023945 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.3739 | 1.094% | CZ 6B | 11.2757 | 2.3721 | 18.3133 | 38.2273 | 0 | 6.814 | 0 | 8.727 | 3.2429 | 1.1325 | 0.80676 | 7.5938 | 0.44452 | 18.4346 | 0 | 8.8145 | 126.1988 | 1.094% | CZ 6B | 3.3038 | 0.69501 | 0.21147 | 0 | 0 | 1.9965 | 0 | 2.557 | 0.95016 | 0.33182 | 0.23638 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 16.5534 | 1.094% | CZ 6B | 0 | 0 | 0.17592 | 0.38227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.69703 | 1.094% | CZ 6B | 34.5873 | 7.2761 | 21.4414 | 41.7824 | 0 | 20.9015 | 0 | 26.7693 | 9.9472 | 3.4739 | 2.4747 | 23.2933 | 1.3635 | 29.1339 | 0 | 27.0379 | 249.4822 | 1.094%
CZ 7 | 0.33467 | 0.070361 | 0.20474 | 0.59492 | 0 | 0.23436 | 0 | 0.29118 | 0.097014 | 0.043183 | 0.023842 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.6684 | 0.5976% | CZ 7 | 11.2757 | 2.3706 | 19.0525 | 59.4916 | 0 | 7.8961 | 0 | 9.8105 | 3.2686 | 1.4549 | 0.80326 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 150.7111 | 0.5976% | CZ 7 | 3.3038 | 0.69458 | 0.21156 | 0 | 0 | 2.3136 | 0 | 2.8745 | 0.95769 | 0.42629 | 0.23536 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 17.2885 | 0.5976% | CZ 7 | 0 | 0 | 0.1833 | 0.59492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.91706 | 0.5976% | CZ 7 | 34.5873 | 7.2716 | 22.2501 | 65.0243 | 0 | 24.2208 | 0 | 30.0929 | 10.026 | 4.4628 | 2.4639 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 281.228 | 0.5976%
CZ 8 | 0.33467 | 0.069974 | 0.21295 | 0.83806 | 0 | 0.13016 | 0 | 0.31892 | 0.09538 | 0.038913 | 0.023722 | 0.22539 | 0.013192 | 0.27391 | 0 | 0.26162 | 2.8369 | 0.07229% | CZ 8 | 11.2757 | 2.3575 | 19.8733 | 83.8064 | 0 | 4.3853 | 0 | 10.7449 | 3.2135 | 1.3111 | 0.79923 | 7.5938 | 0.44445 | 18.4346 | 0 | 8.8145 | 173.0542 | 0.07229% | CZ 8 | 3.3038 | 0.69076 | 0.21159 | 0 | 0 | 1.2849 | 0 | 3.1482 | 0.94156 | 0.38414 | 0.23417 | 2.225 | 0.13022 | 1.3333 | 0 | 2.5827 | 16.4703 | 0.07229% | CZ 8 | 0 | 0 | 0.19151 | 0.83806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.1684 | 0.07229% | CZ 8 | 34.5873 | 7.2316 | 23.1473 | 91.6004 | 0 | 13.4515 | 0 | 32.959 | 9.8572 | 4.0216 | 2.4516 | 23.2933 | 1.3633 | 29.1339 | 0 | 27.0379 | 300.1357 | 0.07229%
US Weighted | 0.33467 | 0.07052 | 0.18204 | 0.23248 | 0 | 0.54367 | 0 | 0.23284 | 0.076267 | 0.053122 | 0.024224 | 0.22539 | 0.013194 | 0.27391 | 0 | 0.26162 | 2.524 | 100% | US Weighted | 11.2757 | 2.3759 | 16.784 | 23.248 | 0 | 18.3173 | 0 | 7.8447 | 2.5696 | 1.7898 | 0.81615 | 7.5938 | 0.44453 | 18.4346 | 0 | 8.8145 | 120.3085 | 100% | US Weighted | 3.3038 | 0.69615 | 0.21142 | 0 | 0 | 5.367 | 0 | 2.2985 | 0.75288 | 0.5244 | 0.23913 | 2.225 | 0.13025 | 1.3333 | 0 | 2.5827 | 19.6644 | 100% | US Weighted | 0 | 0 | 0.16062 | 0.23248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.53194 | 100% | US Weighted | 34.5873 | 7.288 | 19.7695 | 25.4101 | 0 | 56.1867 | 0 | 24.0629 | 7.8819 | 5.49 | 2.5035 | 23.2933 | 1.3636 | 29.1339 | 0 | 27.0379 | 264.0085 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 122120 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 122120 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.14355 | 0.028457 | 0.00067462 | 0.031701 | 0 | 0.34837 | 0 | 0.11043 | 0.043238 | 0.064375 | 0.0049149 | 0.0063872 | 0.0081638 | 0 | 0 | 0.020007 | 0.81027 | 2.703% | CZ 1A | 4.8363 | 0.95876 | 0.034154 | 3.1701 | 0 | 11.7372 | 0 | 3.7207 | 1.4568 | 2.1689 | 0.16559 | 0.2152 | 0.27505 | 0 | 0 | 0.67408 | 29.4129 | 2.703% | CZ 1A | 1.417 | 0.28092 | 0.0049587 | 0 | 0 | 3.439 | 0 | 1.0902 | 0.42683 | 0.63549 | 0.048518 | 0.063053 | 0.08059 | 0 | 0 | 0.19751 | 7.6841 | 2.703% | CZ 1A | 0 | 0 | 0.0001723 | 0.031701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031874 | 2.703% | CZ 1A | 14.8351 | 2.9409 | 0.070745 | 3.4649 | 0 | 36.003 | 0 | 11.4129 | 4.4685 | 6.6529 | 0.50793 | 0.6601 | 0.8437 | 0 | 0 | 2.0677 | 83.9285 | 2.703%
CZ 1B | 0.14359 | 0.028422 | 0.0011458 | 0.075327 | 0 | 0.68963 | 0 | 0.15187 | -0.056388 | 0.060395 | 0.0049794 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 1.1335 | 0% | CZ 1B | 4.8378 | 0.9576 | 0.081576 | 7.5327 | 0 | 23.2348 | 0 | 5.1169 | -1.8998 | 2.0348 | 0.16776 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 43.2286 | 0% | CZ 1B | 1.4175 | 0.28058 | 0.0049132 | 0 | 0 | 6.8078 | 0 | 1.4993 | -0.55665 | 0.5962 | 0.049155 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 10.4399 | 0% | CZ 1B | 0 | 0 | 0.00064807 | 0.075327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075975 | 0% | CZ 1B | 14.8396 | 2.9373 | 0.12227 | 8.2333 | 0 | 71.2709 | 0 | 15.6957 | -5.8275 | 6.2417 | 0.5146 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 117.5995 | 0%
CZ 2A | 0.14383 | 0.028411 | 0.00056751 | 0.073033 | 0 | 0.38174 | 0 | 0.10072 | 0.053073 | 0.066356 | 0.0048803 | 0.0063872 | 0.0081638 | 0 | 0 | 0.020007 | 0.88716 | 13.88% | CZ 2A | 4.8458 | 0.95721 | 0.023443 | 7.3033 | 0 | 12.8614 | 0 | 3.3934 | 1.7881 | 2.2357 | 0.16443 | 0.2152 | 0.27505 | 0 | 0 | 0.67408 | 34.737 | 13.88% | CZ 2A | 1.4198 | 0.28046 | 0.0049587 | 0 | 0 | 3.7684 | 0 | 0.99426 | 0.52392 | 0.65505 | 0.048177 | 0.063053 | 0.08059 | 0 | 0 | 0.19751 | 8.0362 | 13.88% | CZ 2A | 0 | 0 | 6.5195e-05 | 0.073033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073098 | 13.88% | CZ 2A | 14.8641 | 2.9362 | 0.059038 | 7.9825 | 0 | 39.4512 | 0 | 10.4089 | 5.4849 | 6.8577 | 0.50436 | 0.6601 | 0.8437 | 0 | 0 | 2.0677 | 92.1203 | 13.88%
CZ 2B | 0.14374 | 0.028434 | 0.00058071 | 0.13566 | 0 | 0.36987 | 0 | 0.098329 | -0.037017 | 0.04484 | 0.0047513 | 0.0063872 | 0.0081638 | 0 | 0 | 0.020007 | 0.82375 | 2.523% | CZ 2B | 4.8429 | 0.95798 | 0.024763 | 13.5658 | 0 | 12.4617 | 0 | 3.3129 | -1.2472 | 1.5107 | 0.16008 | 0.2152 | 0.27505 | 0 | 0 | 0.67408 | 36.7539 | 2.523% | CZ 2B | 1.419 | 0.28069 | 0.0049587 | 0 | 0 | 3.6513 | 0 | 0.97068 | -0.36542 | 0.44264 | 0.046903 | 0.063053 | 0.08059 | 0 | 0 | 0.19751 | 6.7918 | 2.523% | CZ 2B | 0 | 0 | 7.839e-05 | 0.13566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13574 | 2.523% | CZ 2B | 14.8551 | 2.9385 | 0.060481 | 14.8274 | 0 | 38.2253 | 0 | 10.162 | -3.8256 | 4.634 | 0.49103 | 0.6601 | 0.8437 | 0 | 0 | 2.0677 | 85.9397 | 2.523%
CZ 3A | 0.14373 | 0.028427 | 0.00054267 | 0.067153 | 0 | 0.20753 | 0 | 0.077907 | 0.05631 | 0.042651 | 0.0048457 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.66366 | 14.22% | CZ 3A | 4.8426 | 0.95775 | 0.02096 | 6.7153 | 0 | 6.9919 | 0 | 2.6248 | 1.8972 | 1.437 | 0.16326 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 26.8152 | 14.22% | CZ 3A | 1.4189 | 0.28062 | 0.0049587 | 0 | 0 | 2.0486 | 0 | 0.76908 | 0.55587 | 0.42103 | 0.047835 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 5.8881 | 14.22% | CZ 3A | 0 | 0 | 4.0359e-05 | 0.067153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067193 | 14.22% | CZ 3A | 14.8544 | 2.9378 | 0.056324 | 7.3398 | 0 | 21.447 | 0 | 8.0514 | 5.8194 | 4.4078 | 0.50079 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 68.9866 | 14.22%
CZ 3B | 0.14377 | 0.028427 | 0.00056441 | 0.17484 | 0 | 0.19818 | 0 | 0.063677 | -0.038003 | 0.033761 | 0.0047467 | 0.0063872 | 0.0081684 | 0 | 0 | 0.020007 | 0.64452 | 16.01% | CZ 3B | 4.8437 | 0.95775 | 0.023133 | 17.4839 | 0 | 6.6769 | 0 | 2.1454 | -1.2804 | 1.1375 | 0.15992 | 0.2152 | 0.27521 | 0 | 0 | 0.67408 | 33.3122 | 16.01% | CZ 3B | 1.4192 | 0.28062 | 0.0049587 | 0 | 0 | 1.9563 | 0 | 0.62859 | -0.37515 | 0.33328 | 0.046857 | 0.063053 | 0.080636 | 0 | 0 | 0.19751 | 4.6359 | 16.01% | CZ 3B | 0 | 0 | 6.2091e-05 | 0.17484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1749 | 16.01% | CZ 3B | 14.8577 | 2.9378 | 0.058699 | 19.1099 | 0 | 20.4807 | 0 | 6.5807 | -3.9275 | 3.4891 | 0.49055 | 0.6601 | 0.84417 | 0 | 0 | 2.0677 | 67.6497 | 16.01%
CZ 3C | 0.14377 | 0.028422 | 0.00046739 | 0.07049 | 0 | 0.14235 | 0 | 0.070244 | 0 | 0.029754 | 0.0048526 | 0.0063872 | 0.0081684 | 0 | 0 | 0.020007 | 0.52491 | 2.133% | CZ 3C | 4.8438 | 0.9576 | 0.013431 | 7.049 | 0 | 4.7959 | 0 | 2.3666 | 0 | 1.0025 | 0.16349 | 0.2152 | 0.27521 | 0 | 0 | 0.67408 | 22.3568 | 2.133% | CZ 3C | 1.4192 | 0.28058 | 0.0049587 | 0 | 0 | 1.4052 | 0 | 0.69342 | 0 | 0.29372 | 0.047904 | 0.063053 | 0.080636 | 0 | 0 | 0.19751 | 4.4862 | 2.133% | CZ 3C | 0 | 0 | -3.4926e-05 | 0.07049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070455 | 2.133% | CZ 3C | 14.8579 | 2.9373 | 0.048095 | 7.7046 | 0 | 14.711 | 0 | 7.2594 | 0 | 3.075 | 0.5015 | 0.6601 | 0.84417 | 0 | 0 | 2.0677 | 54.6669 | 2.133%
CZ 4A | 0.14401 | 0.028383 | 0.00057059 | 0.15615 | 0 | 0.14681 | 0 | 0.069725 | 0.050043 | 0.032153 | 0.004772 | 0.0063872 | 0.008173 | 0 | 0 | 0.020007 | 0.66718 | 18.1% | CZ 4A | 4.8519 | 0.95628 | 0.023599 | 15.6146 | 0 | 4.9464 | 0 | 2.3492 | 1.686 | 1.0833 | 0.16078 | 0.2152 | 0.27536 | 0 | 0 | 0.67408 | 32.8367 | 18.1% | CZ 4A | 1.4216 | 0.28019 | 0.0049814 | 0 | 0 | 1.4493 | 0 | 0.6883 | 0.494 | 0.3174 | 0.047108 | 0.063053 | 0.080681 | 0 | 0 | 0.19751 | 5.0441 | 18.1% | CZ 4A | 0 | 0 | 6.5972e-05 | 0.15615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15621 | 18.1% | CZ 4A | 14.8827 | 2.9333 | 0.059361 | 17.0668 | 0 | 15.1728 | 0 | 7.2058 | 5.1717 | 3.3229 | 0.49317 | 0.6601 | 0.84465 | 0 | 0 | 2.0677 | 69.881 | 18.1%
CZ 4B | 0.14407 | 0.028404 | 0.00055507 | 0.28496 | 0 | 0.10055 | 0 | 0.05304 | -0.037752 | 0.029551 | 0.0046591 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.6426 | 0.7301% | CZ 4B | 4.854 | 0.95697 | 0.022046 | 28.496 | 0 | 3.3876 | 0 | 1.787 | -1.2719 | 0.99564 | 0.15697 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 40.5488 | 0.7301% | CZ 4B | 1.4222 | 0.28039 | 0.0049814 | 0 | 0 | 0.99258 | 0 | 0.5236 | -0.37268 | 0.29172 | 0.045993 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 3.53 | 0.7301% | CZ 4B | 0 | 0 | 5.0449e-05 | 0.28496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28501 | 0.7301% | CZ 4B | 14.8894 | 2.9354 | 0.057665 | 31.1461 | 0 | 10.3913 | 0 | 5.4815 | -3.9015 | 3.054 | 0.4815 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 68.1072 | 0.7301%
CZ 4C | 0.14384 | 0.028351 | 0.00069383 | 0.21263 | 0 | 0.034178 | 0 | 0.10084 | 0.018696 | 0.017735 | 0.0044678 | 0.0063872 | 0.0081684 | 0 | 0 | 0.020007 | 0.596 | 2.455% | CZ 4C | 4.8461 | 0.95519 | 0.034853 | 21.2629 | 0 | 1.1515 | 0 | 3.3976 | 0.62991 | 0.59754 | 0.15053 | 0.2152 | 0.27521 | 0 | 0 | 0.67408 | 34.1907 | 2.455% | CZ 4C | 1.4199 | 0.27987 | 0.0051407 | 0 | 0 | 0.3374 | 0 | 0.99549 | 0.18456 | 0.17508 | 0.044105 | 0.063053 | 0.080636 | 0 | 0 | 0.19751 | 3.7828 | 2.455% | CZ 4C | 0 | 0 | 0.00017308 | 0.21263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2128 | 2.455% | CZ 4C | 14.8651 | 2.93 | 0.072735 | 23.2404 | 0 | 3.5322 | 0 | 10.4218 | 1.9322 | 1.8329 | 0.46174 | 0.6601 | 0.84417 | 0 | 0 | 2.0677 | 62.861 | 2.455%
CZ 5A | 0.14404 | 0.02839 | 0.0007427 | 0.23156 | 0 | 0.092703 | 0 | 0.12278 | 0.05275 | 0.030584 | 0.004378 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.74249 | 18.12% | CZ 5A | 4.8529 | 0.95651 | 0.039587 | 23.1565 | 0 | 3.1233 | 0 | 4.1368 | 1.7772 | 1.0304 | 0.1475 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 40.3851 | 18.12% | CZ 5A | 1.4219 | 0.28026 | 0.0051634 | 0 | 0 | 0.91513 | 0 | 1.2121 | 0.52073 | 0.30191 | 0.043218 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 5.0416 | 18.12% | CZ 5A | 0 | 0 | 0.00021965 | 0.23156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23178 | 18.12% | CZ 5A | 14.8858 | 2.934 | 0.078063 | 25.31 | 0 | 9.5805 | 0 | 12.6893 | 5.4515 | 3.1607 | 0.45245 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 78.1141 | 18.12%
CZ 5B | 0.14405 | 0.028395 | 0.00063266 | 0.44274 | 0 | 0.071172 | 0 | 0.055785 | -0.040879 | 0.026653 | 0.0046176 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.76773 | 4.122% | CZ 5B | 4.8534 | 0.95666 | 0.029653 | 44.2739 | 0 | 2.3979 | 0 | 1.8795 | -1.3773 | 0.89797 | 0.15558 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 55.2317 | 4.122% | CZ 5B | 1.4221 | 0.2803 | 0.0050042 | 0 | 0 | 0.70259 | 0 | 0.55069 | -0.40354 | 0.26311 | 0.045584 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 3.207 | 4.122% | CZ 5B | 0 | 0 | 0.00012573 | 0.44274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44286 | 4.122% | CZ 5B | 14.8875 | 2.9345 | 0.066132 | 48.3914 | 0 | 7.3554 | 0 | 5.7652 | -4.2247 | 2.7545 | 0.47721 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 81.9787 | 4.122%
CZ 5C | 0.14399 | 0.028349 | 0.0007745 | 0.23848 | 0 | 0.015906 | 0 | 0.11391 | 0.022272 | 0.016726 | 0.0043595 | 0.0063872 | 0.0081638 | 0 | 0 | 0.020007 | 0.61933 | 0.01984% | CZ 5C | 4.8512 | 0.95511 | 0.042614 | 23.8482 | 0 | 0.5359 | 0 | 3.8378 | 0.75039 | 0.56353 | 0.14688 | 0.2152 | 0.27505 | 0 | 0 | 0.67408 | 36.696 | 0.01984% | CZ 5C | 1.4214 | 0.27985 | 0.0051862 | 0 | 0 | 0.15702 | 0 | 1.1245 | 0.21987 | 0.16512 | 0.043036 | 0.063053 | 0.08059 | 0 | 0 | 0.19751 | 3.7571 | 0.01984% | CZ 5C | 0 | 0 | 0.00024914 | 0.23848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23873 | 0.01984% | CZ 5C | 14.8808 | 2.9297 | 0.081525 | 26.0661 | 0 | 1.6438 | 0 | 11.7722 | 2.3018 | 1.7286 | 0.45054 | 0.6601 | 0.8437 | 0 | 0 | 2.0677 | 65.4266 | 0.01984%
CZ 6A | 0.14405 | 0.028379 | 0.00079237 | 0.28034 | 0 | 0.095712 | 0 | 0.12916 | 0.050764 | 0.034146 | 0.0043987 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.8023 | 3.21% | CZ 6A | 4.8533 | 0.95612 | 0.044554 | 28.0339 | 0 | 3.2247 | 0 | 4.3516 | 1.7103 | 1.1504 | 0.1482 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 45.6376 | 3.21% | CZ 6A | 1.422 | 0.28014 | 0.0051634 | 0 | 0 | 0.94484 | 0 | 1.275 | 0.50112 | 0.33708 | 0.043423 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 5.15 | 3.21% | CZ 6A | 0 | 0 | 0.00026932 | 0.28034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28061 | 3.21% | CZ 6A | 14.8872 | 2.9328 | 0.083492 | 30.641 | 0 | 9.8915 | 0 | 13.3482 | 5.2463 | 3.5289 | 0.45459 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 84.5857 | 3.21%
CZ 6B | 0.14411 | 0.028358 | 0.00078083 | 0.24699 | 0 | 0.059338 | 0 | 0.092011 | 0.049727 | 0.024383 | 0.0044955 | 0.0063872 | 0.0081638 | 0 | 0 | 0.020007 | 0.68475 | 1.094% | CZ 6B | 4.8552 | 0.95542 | 0.044011 | 24.6989 | 0 | 1.9992 | 0 | 3.1 | 1.6754 | 0.82151 | 0.15146 | 0.2152 | 0.27505 | 0 | 0 | 0.67408 | 39.4654 | 1.094% | CZ 6B | 1.4226 | 0.27994 | 0.0050724 | 0 | 0 | 0.58576 | 0 | 0.90831 | 0.49089 | 0.2407 | 0.044378 | 0.063053 | 0.08059 | 0 | 0 | 0.19751 | 4.3188 | 1.094% | CZ 6B | 0 | 0 | 0.00026699 | 0.24699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24726 | 1.094% | CZ 6B | 14.8929 | 2.9307 | 0.082285 | 26.9959 | 0 | 6.1323 | 0 | 9.509 | 5.1391 | 2.5199 | 0.46459 | 0.6601 | 0.8437 | 0 | 0 | 2.0677 | 72.2383 | 1.094%
CZ 7 | 0.14419 | 0.028339 | 0.00085294 | 0.35633 | 0 | 0.074836 | 0 | 0.13862 | 0.050374 | 0.025353 | 0.0043803 | 0.0063872 | 0.0081661 | 0 | 0 | 0.020007 | 0.85783 | 0.5976% | CZ 7 | 4.8581 | 0.9548 | 0.050764 | 35.6326 | 0 | 2.5213 | 0 | 4.6703 | 1.6972 | 0.85419 | 0.14758 | 0.2152 | 0.27513 | 0 | 0 | 0.67408 | 52.5513 | 0.5976% | CZ 7 | 1.4234 | 0.27976 | 0.0051407 | 0 | 0 | 0.73875 | 0 | 1.3684 | 0.49728 | 0.25028 | 0.043241 | 0.063053 | 0.080613 | 0 | 0 | 0.19751 | 4.9474 | 0.5976% | CZ 7 | 0 | 0 | 0.00033219 | 0.35633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35666 | 0.5976% | CZ 7 | 14.9018 | 2.9288 | 0.090126 | 38.9465 | 0 | 7.734 | 0 | 14.3257 | 5.206 | 2.6202 | 0.45269 | 0.6601 | 0.84394 | 0 | 0 | 2.0677 | 90.7775 | 0.5976%
CZ 8 | 0.14422 | 0.028185 | 0.00092354 | 0.47117 | 0 | 0.036724 | 0 | 0.15985 | 0.046612 | 0.022802 | 0.0043065 | 0.0063872 | 0.0081684 | 0 | 0 | 0.020007 | 0.94936 | 0.07229% | CZ 8 | 4.8591 | 0.9496 | 0.057671 | 47.1171 | 0 | 1.2373 | 0 | 5.3855 | 1.5704 | 0.76825 | 0.14509 | 0.2152 | 0.27521 | 0 | 0 | 0.67408 | 63.2546 | 0.07229% | CZ 8 | 1.4237 | 0.27823 | 0.0051634 | 0 | 0 | 0.36253 | 0 | 1.578 | 0.46013 | 0.2251 | 0.042513 | 0.063053 | 0.080636 | 0 | 0 | 0.19751 | 4.7165 | 0.07229% | CZ 8 | 0 | 0 | 0.00040049 | 0.47117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47157 | 0.07229% | CZ 8 | 14.9049 | 2.9128 | 0.097829 | 51.499 | 0 | 3.7953 | 0 | 16.5196 | 4.8172 | 2.3565 | 0.44507 | 0.6601 | 0.84417 | 0 | 0 | 2.0677 | 100.9202 | 0.07229%
US Weighted | 0.14389 | 0.028405 | 0.00061413 | 0.16346 | 0 | 0.18811 | 0 | 0.088376 | 0.029154 | 0.038837 | 0.0046947 | 0.0063872 | 0.0081673 | 0 | 0 | 0.020007 | 0.72011 | 100% | US Weighted | 4.8478 | 0.957 | 0.027724 | 16.3464 | 0 | 6.3378 | 0 | 2.9776 | 0.98224 | 1.3085 | 0.15817 | 0.2152 | 0.27517 | 0 | 0 | 0.67408 | 35.1077 | 100% | US Weighted | 1.4204 | 0.2804 | 0.0050155 | 0 | 0 | 1.857 | 0 | 0.87242 | 0.2878 | 0.38338 | 0.046344 | 0.063053 | 0.080625 | 0 | 0 | 0.19751 | 5.4939 | 100% | US Weighted | 0 | 0 | 0.00010606 | 0.16346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16357 | 100% | US Weighted | 14.8703 | 2.9355 | 0.0641 | 17.8666 | 0 | 19.4408 | 0 | 9.1334 | 3.013 | 4.0137 | 0.48518 | 0.6601 | 0.84407 | 0 | 0 | 2.0677 | 75.3944 | 100%
Building Type: | Large Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 122120 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 122120 | [17 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 42.89% | 40.28% | 0.4152% | 82.55% | 0% | 31% | 0% | 45.75% | 38.7% | 78.22% | 20.04% | 2.834% | 61.89% | 0% | 0% | 7.647% | 27.34% | 2.703% | CZ 1A | 42.89% | 40.28% | 0.2304% | 82.55% | 0% | 31% | 0% | 45.75% | 38.7% | 78.22% | 20.04% | 2.834% | 61.89% | 0% | 0% | 7.647% | 24.31% | 2.703% | CZ 1A | 42.89% | 40.28% | 2.346% | 0% | 0% | 31% | 0% | 45.75% | 38.7% | 78.22% | 20.04% | 2.834% | 61.89% | 0% | 0% | 7.647% | 29.42% | 2.703% | CZ 1A | 0% | 0% | 0.1222% | 82.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.01% | 2.703% | CZ 1A | 42.89% | 40.28% | 0.4013% | 82.55% | 0% | 31% | 0% | 45.75% | 38.7% | 78.22% | 20.04% | 2.834% | 61.89% | 0% | 0% | 7.647% | 27.23% | 2.703%
CZ 1B | 42.9% | 40.28% | 0.702% | 72.99% | 0% | 45.07% | 0% | 50.98% | -521.6% | 74.3% | 20.27% | 2.834% | 61.89% | 0% | 0% | 7.647% | 33.43% | 0% | CZ 1B | 42.9% | 40.28% | 0.5474% | 72.99% | 0% | 45.07% | 0% | 50.98% | -521.6% | 74.3% | 20.27% | 2.834% | 61.89% | 0% | 0% | 7.647% | 30.95% | 0% | CZ 1B | 42.9% | 40.28% | 2.325% | 0% | 0% | 45.07% | 0% | 50.98% | -521.6% | 74.3% | 20.27% | 2.834% | 61.89% | 0% | 0% | 7.647% | 35.18% | 0% | CZ 1B | 0% | 0% | 0.457% | 72.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.79% | 0% | CZ 1B | 42.9% | 40.28% | 0.6903% | 72.99% | 0% | 45.07% | 0% | 50.98% | -521.6% | 74.3% | 20.27% | 2.834% | 61.89% | 0% | 0% | 7.647% | 33.35% | 0%
CZ 2A | 42.98% | 40.28% | 0.3372% | 67.81% | 0% | 35.86% | 0% | 43.19% | 49.21% | 77.89% | 19.95% | 2.834% | 61.89% | 0% | 0% | 7.647% | 29.86% | 13.88% | CZ 2A | 42.98% | 40.28% | 0.1521% | 67.81% | 0% | 35.86% | 0% | 43.19% | 49.21% | 77.89% | 19.95% | 2.834% | 61.89% | 0% | 0% | 7.647% | 27.53% | 13.88% | CZ 2A | 42.98% | 40.28% | 2.346% | 0% | 0% | 35.86% | 0% | 43.19% | 49.21% | 77.89% | 19.95% | 2.834% | 61.89% | 0% | 0% | 7.647% | 31.59% | 13.88% | CZ 2A | 0% | 0% | 0.04439% | 67.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.58% | 13.88% | CZ 2A | 42.98% | 40.28% | 0.3232% | 67.81% | 0% | 35.86% | 0% | 43.19% | 49.21% | 77.89% | 19.95% | 2.834% | 61.89% | 0% | 0% | 7.647% | 29.78% | 13.88%
CZ 2B | 42.95% | 40.28% | 0.3442% | 84.5% | 0% | 43.87% | 0% | 37.9% | -440.3% | 76.3% | 19.6% | 2.834% | 61.88% | 0% | 0% | 7.647% | 30.48% | 2.523% | CZ 2B | 42.95% | 40.28% | 0.1603% | 84.5% | 0% | 43.87% | 0% | 37.9% | -440.3% | 76.3% | 19.6% | 2.834% | 61.88% | 0% | 0% | 7.647% | 30.46% | 2.523% | CZ 2B | 42.95% | 40.28% | 2.346% | 0% | 0% | 43.87% | 0% | 37.9% | -440.3% | 76.3% | 19.6% | 2.834% | 61.88% | 0% | 0% | 7.647% | 30.5% | 2.523% | CZ 2B | 0% | 0% | 0.05322% | 84.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.39% | 2.523% | CZ 2B | 42.95% | 40.28% | 0.3303% | 84.5% | 0% | 43.87% | 0% | 37.9% | -440.3% | 76.3% | 19.6% | 2.834% | 61.88% | 0% | 0% | 7.647% | 30.48% | 2.523%
CZ 3A | 42.95% | 40.28% | 0.3041% | 46.44% | 0% | 33.87% | 0% | 37.47% | 54.42% | 72.74% | 19.87% | 2.834% | 61.88% | 0% | 0% | 7.647% | 26.45% | 14.22% | CZ 3A | 42.95% | 40.28% | 0.1276% | 46.44% | 0% | 33.87% | 0% | 37.47% | 54.42% | 72.74% | 19.87% | 2.834% | 61.88% | 0% | 0% | 7.647% | 23.57% | 14.22% | CZ 3A | 42.95% | 40.28% | 2.346% | 0% | 0% | 33.87% | 0% | 37.47% | 54.42% | 72.74% | 19.87% | 2.834% | 61.88% | 0% | 0% | 7.647% | 28.83% | 14.22% | CZ 3A | 0% | 0% | 0.0257% | 46.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.25% | 14.22% | CZ 3A | 42.95% | 40.28% | 0.2907% | 46.44% | 0% | 33.87% | 0% | 37.47% | 54.42% | 72.74% | 19.87% | 2.834% | 61.88% | 0% | 0% | 7.647% | 26.33% | 14.22%
CZ 3B | 42.96% | 40.28% | 0.321% | 83.46% | 0% | 35.97% | 0% | 28.51% | -606.6% | 72.31% | 19.58% | 2.834% | 61.91% | 0% | 0% | 7.647% | 26.67% | 16.01% | CZ 3B | 42.96% | 40.28% | 0.1431% | 83.46% | 0% | 35.97% | 0% | 28.51% | -606.6% | 72.31% | 19.58% | 2.834% | 61.91% | 0% | 0% | 7.647% | 29.03% | 16.01% | CZ 3B | 42.96% | 40.28% | 2.346% | 0% | 0% | 35.97% | 0% | 28.51% | -606.6% | 72.31% | 19.58% | 2.834% | 61.91% | 0% | 0% | 7.647% | 24.54% | 16.01% | CZ 3B | 0% | 0% | 0.0402% | 83.46% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.79% | 16.01% | CZ 3B | 42.96% | 40.28% | 0.3074% | 83.46% | 0% | 35.97% | 0% | 28.51% | -606.6% | 72.31% | 19.58% | 2.834% | 61.91% | 0% | 0% | 7.647% | 26.77% | 16.01%
CZ 3C | 42.96% | 40.28% | 0.2603% | 49.49% | 0% | 36.74% | 0% | 34.74% | 0% | 70.92% | 19.87% | 2.834% | 61.9% | 0% | 0% | 7.647% | 24.33% | 2.133% | CZ 3C | 42.96% | 40.28% | 0.08123% | 49.49% | 0% | 36.74% | 0% | 34.74% | 0% | 70.92% | 19.87% | 2.834% | 61.9% | 0% | 0% | 7.647% | 21.96% | 2.133% | CZ 3C | 42.96% | 40.28% | 2.346% | 0% | 0% | 36.74% | 0% | 34.74% | 0% | 70.92% | 19.87% | 2.834% | 61.9% | 0% | 0% | 7.647% | 26.45% | 2.133% | CZ 3C | 0% | 0% | -0.02209% | 49.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 16.03% | 2.133% | CZ 3C | 42.96% | 40.28% | 0.2467% | 49.49% | 0% | 36.74% | 0% | 34.74% | 0% | 70.92% | 19.87% | 2.834% | 61.9% | 0% | 0% | 7.647% | 24.24% | 2.133%
CZ 4A | 43.03% | 40.28% | 0.3059% | 68.83% | 0% | 33.88% | 0% | 33.04% | 49.24% | 66.88% | 19.63% | 2.834% | 61.93% | 0% | 0% | 7.647% | 27.67% | 18.1% | CZ 4A | 43.03% | 40.28% | 0.1369% | 68.83% | 0% | 33.88% | 0% | 33.04% | 49.24% | 66.88% | 19.63% | 2.834% | 61.93% | 0% | 0% | 7.647% | 28.2% | 18.1% | CZ 4A | 43.03% | 40.28% | 2.357% | 0% | 0% | 33.88% | 0% | 33.04% | 49.24% | 66.88% | 19.63% | 2.834% | 61.93% | 0% | 0% | 7.647% | 27.18% | 18.1% | CZ 4A | 0% | 0% | 0.03996% | 68.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.43% | 18.1% | CZ 4A | 43.03% | 40.28% | 0.293% | 68.83% | 0% | 33.88% | 0% | 33.04% | 49.24% | 66.88% | 19.63% | 2.834% | 61.93% | 0% | 0% | 7.647% | 27.69% | 18.1%
CZ 4B | 43.05% | 40.28% | 0.3013% | 88.59% | 0% | 27.59% | 0% | 23.28% | -998.4% | 71.05% | 19.3% | 2.834% | 61.89% | 0% | 0% | 7.647% | 27.38% | 0.7301% | CZ 4B | 43.05% | 40.28% | 0.1297% | 88.59% | 0% | 27.59% | 0% | 23.28% | -998.4% | 71.05% | 19.3% | 2.834% | 61.89% | 0% | 0% | 7.647% | 33.68% | 0.7301% | CZ 4B | 43.05% | 40.28% | 2.357% | 0% | 0% | 27.59% | 0% | 23.28% | -998.4% | 71.05% | 19.3% | 2.834% | 61.89% | 0% | 0% | 7.647% | 20.75% | 0.7301% | CZ 4B | 0% | 0% | 0.03099% | 88.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 45.72% | 0.7301% | CZ 4B | 43.05% | 40.28% | 0.2882% | 88.59% | 0% | 27.59% | 0% | 23.28% | -998.4% | 71.05% | 19.3% | 2.834% | 61.89% | 0% | 0% | 7.647% | 27.66% | 0.7301%
CZ 4C | 42.98% | 40.28% | 0.367% | 76.43% | 0% | 21.6% | 0% | 41.03% | 31.49% | 61.07% | 18.61% | 2.834% | 61.91% | 0% | 0% | 7.647% | 27.56% | 2.455% | CZ 4C | 42.98% | 40.28% | 0.1993% | 76.43% | 0% | 21.6% | 0% | 41.03% | 31.49% | 61.07% | 18.61% | 2.834% | 61.91% | 0% | 0% | 7.647% | 30.63% | 2.455% | CZ 4C | 42.98% | 40.28% | 2.43% | 0% | 0% | 21.6% | 0% | 41.03% | 31.49% | 61.07% | 18.61% | 2.834% | 61.91% | 0% | 0% | 7.647% | 24.28% | 2.455% | CZ 4C | 0% | 0% | 0.1032% | 76.43% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.4% | 2.455% | CZ 4C | 42.98% | 40.28% | 0.3541% | 76.43% | 0% | 21.6% | 0% | 41.03% | 31.49% | 61.07% | 18.61% | 2.834% | 61.91% | 0% | 0% | 7.647% | 27.69% | 2.455%
CZ 5A | 43.04% | 40.28% | 0.3838% | 68.7% | 0% | 32.8% | 0% | 45.9% | 54.52% | 74.72% | 18.32% | 2.834% | 61.89% | 0% | 0% | 7.647% | 30.66% | 18.12% | CZ 5A | 43.04% | 40.28% | 0.2208% | 68.7% | 0% | 32.8% | 0% | 45.9% | 54.52% | 74.72% | 18.32% | 2.834% | 61.89% | 0% | 0% | 7.647% | 32.42% | 18.12% | CZ 5A | 43.04% | 40.28% | 2.441% | 0% | 0% | 32.8% | 0% | 45.9% | 54.52% | 74.72% | 18.32% | 2.834% | 61.89% | 0% | 0% | 7.647% | 28.8% | 18.12% | CZ 5A | 0% | 0% | 0.1276% | 68.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.77% | 18.12% | CZ 5A | 43.04% | 40.28% | 0.3713% | 68.7% | 0% | 32.8% | 0% | 45.9% | 54.52% | 74.72% | 18.32% | 2.834% | 61.89% | 0% | 0% | 7.647% | 30.74% | 18.12%
CZ 5B | 43.04% | 40.28% | 0.3304% | 87.01% | 0% | 26.1% | 0% | 24.02% | -1552% | 68.22% | 19.17% | 2.834% | 61.9% | 0% | 0% | 7.647% | 31.33% | 4.122% | CZ 5B | 43.04% | 40.28% | 0.1673% | 87.01% | 0% | 26.1% | 0% | 24.02% | -1552% | 68.22% | 19.17% | 2.834% | 61.9% | 0% | 0% | 7.647% | 40.38% | 4.122% | CZ 5B | 43.04% | 40.28% | 2.367% | 0% | 0% | 26.1% | 0% | 24.02% | -1552% | 68.22% | 19.17% | 2.834% | 61.9% | 0% | 0% | 7.647% | 19.9% | 4.122% | CZ 5B | 0% | 0% | 0.07393% | 87.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.16% | 4.122% | CZ 5B | 43.04% | 40.28% | 0.3179% | 87.01% | 0% | 26.1% | 0% | 24.02% | -1552% | 68.22% | 19.17% | 2.834% | 61.9% | 0% | 0% | 7.647% | 31.76% | 4.122%
CZ 5C | 43.02% | 40.28% | 0.4012% | 77.02% | 0% | 16.33% | 0% | 43.7% | 32.54% | 69.9% | 18.24% | 2.834% | 61.9% | 0% | 0% | 7.647% | 28.72% | 0.01984% | CZ 5C | 43.02% | 40.28% | 0.2383% | 77.02% | 0% | 16.33% | 0% | 43.7% | 32.54% | 69.9% | 18.24% | 2.834% | 61.9% | 0% | 0% | 7.647% | 32.26% | 0.01984% | CZ 5C | 43.02% | 40.28% | 2.451% | 0% | 0% | 16.33% | 0% | 43.7% | 32.54% | 69.9% | 18.24% | 2.834% | 61.9% | 0% | 0% | 7.647% | 24.78% | 0.01984% | CZ 5C | 0% | 0% | 0.1452% | 77.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.5% | 0.01984% | CZ 5C | 43.02% | 40.28% | 0.3888% | 77.02% | 0% | 16.33% | 0% | 43.7% | 32.54% | 69.9% | 18.24% | 2.834% | 61.9% | 0% | 0% | 7.647% | 28.88% | 0.01984%
CZ 6A | 43.04% | 40.28% | 0.3989% | 61.66% | 0% | 32.61% | 0% | 46.38% | 52.45% | 74.48% | 18.41% | 2.834% | 61.89% | 0% | 0% | 7.647% | 31.21% | 3.21% | CZ 6A | 43.04% | 40.28% | 0.2416% | 61.66% | 0% | 32.61% | 0% | 46.38% | 52.45% | 74.48% | 18.41% | 2.834% | 61.89% | 0% | 0% | 7.647% | 33.14% | 3.21% | CZ 6A | 43.04% | 40.28% | 2.441% | 0% | 0% | 32.61% | 0% | 46.38% | 52.45% | 74.48% | 18.41% | 2.834% | 61.89% | 0% | 0% | 7.647% | 28.98% | 3.21% | CZ 6A | 0% | 0% | 0.152% | 61.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.41% | 3.21% | CZ 6A | 43.04% | 40.28% | 0.3868% | 61.66% | 0% | 32.61% | 0% | 46.38% | 52.45% | 74.48% | 18.41% | 2.834% | 61.89% | 0% | 0% | 7.647% | 31.29% | 3.21%
CZ 6B | 43.06% | 40.28% | 0.3957% | 64.61% | 0% | 29.34% | 0% | 35.52% | 51.66% | 72.54% | 18.77% | 2.834% | 61.88% | 0% | 0% | 7.647% | 28.85% | 1.094% | CZ 6B | 43.06% | 40.28% | 0.2403% | 64.61% | 0% | 29.34% | 0% | 35.52% | 51.66% | 72.54% | 18.77% | 2.834% | 61.88% | 0% | 0% | 7.647% | 31.27% | 1.094% | CZ 6B | 43.06% | 40.28% | 2.399% | 0% | 0% | 29.34% | 0% | 35.52% | 51.66% | 72.54% | 18.77% | 2.834% | 61.88% | 0% | 0% | 7.647% | 26.09% | 1.094% | CZ 6B | 0% | 0% | 0.1518% | 64.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.47% | 1.094% | CZ 6B | 43.06% | 40.28% | 0.3838% | 64.61% | 0% | 29.34% | 0% | 35.52% | 51.66% | 72.54% | 18.77% | 2.834% | 61.88% | 0% | 0% | 7.647% | 28.96% | 1.094%
CZ 7 | 43.08% | 40.28% | 0.4166% | 59.9% | 0% | 31.93% | 0% | 47.61% | 51.93% | 58.71% | 18.37% | 2.834% | 61.9% | 0% | 0% | 7.647% | 32.15% | 0.5976% | CZ 7 | 43.08% | 40.28% | 0.2664% | 59.9% | 0% | 31.93% | 0% | 47.61% | 51.93% | 58.71% | 18.37% | 2.834% | 61.9% | 0% | 0% | 7.647% | 34.87% | 0.5976% | CZ 7 | 43.08% | 40.28% | 2.43% | 0% | 0% | 31.93% | 0% | 47.61% | 51.93% | 58.71% | 18.37% | 2.834% | 61.9% | 0% | 0% | 7.647% | 28.62% | 0.5976% | CZ 7 | 0% | 0% | 0.1812% | 59.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.89% | 0.5976% | CZ 7 | 43.08% | 40.28% | 0.4051% | 59.9% | 0% | 31.93% | 0% | 47.61% | 51.93% | 58.71% | 18.37% | 2.834% | 61.9% | 0% | 0% | 7.647% | 32.28% | 0.5976%
CZ 8 | 43.09% | 40.28% | 0.4337% | 56.22% | 0% | 28.21% | 0% | 50.12% | 48.87% | 58.6% | 18.15% | 2.834% | 61.92% | 0% | 0% | 7.647% | 33.47% | 0.07229% | CZ 8 | 43.09% | 40.28% | 0.2902% | 56.22% | 0% | 28.21% | 0% | 50.12% | 48.87% | 58.6% | 18.15% | 2.834% | 61.92% | 0% | 0% | 7.647% | 36.55% | 0.07229% | CZ 8 | 43.09% | 40.28% | 2.44% | 0% | 0% | 28.21% | 0% | 50.12% | 48.87% | 58.6% | 18.15% | 2.834% | 61.92% | 0% | 0% | 7.647% | 28.64% | 0.07229% | CZ 8 | 0% | 0% | 0.2091% | 56.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.36% | 0.07229% | CZ 8 | 43.09% | 40.28% | 0.4226% | 56.22% | 0% | 28.21% | 0% | 50.12% | 48.87% | 58.6% | 18.15% | 2.834% | 61.92% | 0% | 0% | 7.647% | 33.62% | 0.07229%
US Weighted | 42.99% | 40.28% | 0.3374% | 70.31% | 0% | 34.6% | 0% | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% | 0% | 7.647% | 28.53% | 100% | US Weighted | 42.99% | 40.28% | 0.1652% | 70.31% | 0% | 34.6% | 0% | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% | 0% | 7.647% | 29.18% | 100% | US Weighted | 42.99% | 40.28% | 2.372% | 0% | 0% | 34.6% | 0% | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% | 0% | 7.647% | 27.94% | 100% | US Weighted | 0% | 0% | 0.06603% | 70.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.75% | 100% | US Weighted | 42.99% | 40.28% | 0.3242% | 70.31% | 0% | 34.6% | 0% | 37.96% | 38.23% | 73.11% | 19.38% | 2.834% | 61.9% | 0% | 0% | 7.647% | 28.56% | 100%

## Whse
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Warehouse |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Warehouse | [14 empty] | Prototype Floor Area: | 52045 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.1 | 0.03073 | 0.013415 | 0.065002 | 0 | 0.010542 | 0 | 0.016801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.31029 |  | STD2016 | 3.3693 | 1.0353 | 0.45196 | 6.5002 | 0 | 0.35519 | 0 | 0.56606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.7645 |  | STD2016 | 0.98721 | 0.30335 | 0.13243 | 0 | 0 | 0.10407 | 0 | 0.16586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.4215 |  | STD2016 | 0 | 0 | 0 | 0.065002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065002 |  | STD2016 | 10.3351 | 3.1758 | 1.3864 | 7.1047 | 0 | 1.0895 | 0 | 1.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 32.4548
STD2013 | 0.16972 | 0.045269 | 0.013414 | 0.065791 | 0 | 0.011554 | 0 | 0.017433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.39698 |  | STD2013 | 5.718 | 1.5252 | 0.45196 | 6.5791 | 0 | 0.38927 | 0 | 0.58734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.7374 |  | STD2013 | 1.6754 | 0.44688 | 0.13242 | 0 | 0 | 0.11406 | 0 | 0.17209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2694 |  | STD2013 | 0 | 0 | 0 | 0.065791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065791 |  | STD2013 | 17.5396 | 4.6784 | 1.3863 | 7.191 | 0 | 1.194 | 0 | 1.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 41.418
STD2010 | 0.17373 | 0.045269 | 0.013416 | 0.068505 | 0 | 0.014427 | 0 | 0.021008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.41046 |  | STD2010 | 5.8533 | 1.5252 | 0.45199 | 6.8505 | 0 | 0.48607 | 0 | 0.70779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 18.3715 |  | STD2010 | 1.715 | 0.44688 | 0.13243 | 0 | 0 | 0.14242 | 0 | 0.20738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.3757 |  | STD2010 | 0 | 0 | 0 | 0.068505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068505 |  | STD2010 | 17.9546 | 4.6784 | 1.3864 | 7.4876 | 0 | 1.491 | 0 | 2.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 42.8274
STD2007 | 0.26058 | 0.066751 | 0.013857 | 0.084382 | 0 | 0.021034 | 0 | 0.036092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.558 |  | STD2007 | 8.7793 | 2.2489 | 0.46686 | 8.4382 | 0 | 0.70868 | 0 | 1.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 24.3951 |  | STD2007 | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.20764 | 0 | 0.35629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6754 |  | STD2007 | 0 | 0 | 0 | 0.084382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084382 |  | STD2007 | 26.9299 | 6.8984 | 1.4321 | 9.223 | 0 | 2.1738 | 0 | 3.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 58.1695
STD2004 | 0.26058 | 0.066751 | 0.013857 | 0.10565 | 0 | 0.021594 | 0 | 0.036386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.58013 |  | STD2004 | 8.7793 | 2.2489 | 0.46687 | 10.5655 | 0 | 0.72755 | 0 | 1.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 26.5512 |  | STD2004 | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.21317 | 0 | 0.35919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6838 |  | STD2004 | 0 | 0 | 0 | 0.10565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10565 |  | STD2004 | 26.9299 | 6.8984 | 1.4321 | 11.5481 | 0 | 2.2317 | 0 | 3.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 60.5829
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 9.4581e-08 | 0.021273 | 0 | 0.00056007 | 0 | 0.00029402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022127 |  | 2004-2007 | 0 | 0 | 3.1866e-06 | 2.1273 | 0 | 0.01887 | 0 | 0.009906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.156 |  | 2004-2007 | 0 | 0 | 9.3368e-07 | 0 | 0 | 0.0055289 | 0 | 0.0029025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084323 |  | 2004-2007 | 0 | 0 | 0 | 0.021273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021273 |  | 2004-2007 | 0 | 0 | 9.7747e-06 | 2.3251 | 0 | 0.057882 | 0 | 0.030386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4134
2007-2010 | 0.086847 | 0.021482 | 0.00044138 | 0.015877 | 0 | 0.0066074 | 0 | 0.015084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012003 | 0.14754 |  | 2007-2010 | 2.926 | 0.72376 | 0.014871 | 1.5877 | 0 | 0.22261 | 0 | 0.5082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040439 | 6.0236 |  | 2007-2010 | 0.85732 | 0.21206 | 0.0043572 | 0 | 0 | 0.065226 | 0 | 0.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011849 | 1.2997 |  | 2007-2010 | 0 | 0 | 0 | 0.015877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015877 |  | 2007-2010 | 8.9753 | 2.2201 | 0.045615 | 1.7354 | 0 | 0.68285 | 0 | 1.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12404 | 15.3422
2010-2013 | 0.0040154 | 0 | 1.0827e-06 | 0.0027136 | 0 | 0.0028731 | 0 | 0.003575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030277 | 0.013481 |  | 2010-2013 | 0.13528 | 0 | 3.6478e-05 | 0.27136 | 0 | 0.096798 | 0 | 0.12045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010201 | 0.63412 |  | 2010-2013 | 0.039638 | 0 | 1.0688e-05 | 0 | 0 | 0.028362 | 0 | 0.035291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029889 | 0.10629 |  | 2010-2013 | 0 | 0 | 0 | 0.0027136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027136 |  | 2010-2013 | 0.41497 | 0 | 0.00011189 | 0.29659 | 0 | 0.29692 | 0 | 0.36947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03129 | 1.4094
2013-2016 | 0.069712 | 0.014539 | -2.2587e-07 | 0.0007898 | 0 | 0.0010115 | 0 | 0.00063157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086684 |  | 2013-2016 | 2.3487 | 0.48984 | -7.6098e-06 | 0.07898 | 0 | 0.034078 | 0 | 0.021279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9729 |  | 2013-2016 | 0.68817 | 0.14352 | -2.2297e-06 | 0 | 0 | 0.009985 | 0 | 0.0062347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84792 |  | 2013-2016 | 0 | 0 | 0 | 0.0007898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007898 |  | 2013-2016 | 7.2045 | 1.5026 | -2.3343e-05 | 0.086325 | 0 | 0.10453 | 0 | 0.065271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9632
2004-2016 | 0.16057 | 0.036021 | 0.00044234 | 0.040653 | 0 | 0.011052 | 0 | 0.019584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.26983 |  | 2004-2016 | 5.41 | 1.2136 | 0.014903 | 4.0653 | 0 | 0.37236 | 0 | 0.65983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.7867 |  | 2004-2016 | 1.5851 | 0.35559 | 0.0043666 | 0 | 0 | 0.1091 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2624 |  | 2004-2016 | 0 | 0 | 0 | 0.040653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040653 |  | 2004-2016 | 16.5948 | 3.7226 | 0.045714 | 4.4434 | 0 | 1.1422 | 0 | 2.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 28.1281
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.0006826% | 20.13% |  | 2.594% |  | 0.8081% | [7 empty] | 0% | 3.814% |  | 2004-2007 | 0% | 0% | 0.0006826% | 20.13% |  | 2.594% |  | 0.8081% | [7 empty] | 0% | 8.12% |  | 2004-2007 | 0% | 0% | 0.0006826% |  |  | 2.594% |  | 0.8081% | [7 empty] | 0% | 0.18% |  | 2004-2007 |  |  |  | 20.13% | [12 empty] | 20.13% |  | 2004-2007 | 0% | 0% | 0.0006826% | 20.13% |  | 2.594% |  | 0.8081% | [7 empty] | 0% | 3.984%
2007-2010 | 33.33% | 32.18% | 3.185% | 18.82% |  | 31.41% |  | 41.79% | [7 empty] | 1.594% | 26.44% |  | 2007-2010 | 33.33% | 32.18% | 3.185% | 18.82% |  | 31.41% |  | 41.79% | [7 empty] | 1.594% | 24.69% |  | 2007-2010 | 33.33% | 32.18% | 3.185% |  |  | 31.41% |  | 41.79% | [7 empty] | 1.594% | 27.8% |  | 2007-2010 |  |  |  | 18.82% | [12 empty] | 18.82% |  | 2007-2010 | 33.33% | 32.18% | 3.185% | 18.82% |  | 31.41% |  | 41.79% | [7 empty] | 1.594% | 26.37%
2010-2013 | 2.311% | 0% | 0.008071% | 3.961% |  | 19.91% |  | 17.02% | [7 empty] | 0.4086% | 3.284% |  | 2010-2013 | 2.311% | 0% | 0.008071% | 3.961% |  | 19.91% |  | 17.02% | [7 empty] | 0.4086% | 3.452% |  | 2010-2013 | 2.311% | 0% | 0.008071% |  |  | 19.91% |  | 17.02% | [7 empty] | 0.4086% | 3.149% |  | 2010-2013 |  |  |  | 3.961% | [12 empty] | 3.961% |  | 2010-2013 | 2.311% | 0% | 0.008071% | 3.961% |  | 19.91% |  | 17.02% | [7 empty] | 0.4086% | 3.291%
2013-2016 | 41.08% | 32.12% | -0.001684% | 1.2% |  | 8.754% |  | 3.623% | [7 empty] | 0% | 21.84% |  | 2013-2016 | 41.08% | 32.12% | -0.001684% | 1.2% |  | 8.754% |  | 3.623% | [7 empty] | 0% | 16.76% |  | 2013-2016 | 41.08% | 32.12% | -0.001684% |  |  | 8.754% |  | 3.623% | [7 empty] | 0% | 25.94% |  | 2013-2016 |  |  |  | 1.2% | [12 empty] | 1.2% |  | 2013-2016 | 41.08% | 32.12% | -0.001684% | 1.2% |  | 8.754% |  | 3.623% | [7 empty] | 0% | 21.64%
2004-2016 | 61.62% | 53.96% | 3.192% | 38.48% |  | 51.18% |  | 53.82% | [7 empty] | 1.996% | 46.51% |  | 2004-2016 | 61.62% | 53.96% | 3.192% | 38.48% |  | 51.18% |  | 53.82% | [7 empty] | 1.996% | 44.39% |  | 2004-2016 | 61.62% | 53.96% | 3.192% |  |  | 51.18% |  | 53.82% | [7 empty] | 1.996% | 48.3% |  | 2004-2016 |  |  |  | 38.48% | [12 empty] | 38.48% |  | 2004-2016 | 61.62% | 53.96% | 3.192% | 38.48% |  | 51.18% |  | 53.82% | [7 empty] | 1.996% | 46.43%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.09659 | 0.030699 | 0.012251 | 6.0098e-05 | 0 | 0.027417 | 0 | 0.016106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.25692 | 3.023% | CZ 1A | 3.2543 | 1.0343 | 0.41277 | 0.0060098 | 0 | 0.92373 | 0 | 0.54265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 8.6602 | 3.023% | CZ 1A | 0.9535 | 0.30305 | 0.12094 | 0 | 0 | 0.27065 | 0 | 0.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.5357 | 3.023% | CZ 1A | 0 | 0 | 0 | 6.0098e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0098e-05 | 3.023% | CZ 1A | 9.9822 | 3.1726 | 1.2661 | 0.0065687 | 0 | 2.8335 | 0 | 1.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 26.5526 | 3.023%
CZ 1B | 0.094746 | 0.030656 | 0.012268 | 0.0047587 | 0 | 0.089599 | 0 | 0.053082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.35891 | 0% | CZ 1B | 3.1922 | 1.0328 | 0.41332 | 0.47587 | 0 | 3.0187 | 0 | 1.7884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.4078 | 0% | CZ 1B | 0.9353 | 0.30262 | 0.1211 | 0 | 0 | 0.88449 | 0 | 0.52401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.4961 | 0% | CZ 1B | 0 | 0 | 0 | 0.0047587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047587 | 0% | CZ 1B | 9.7917 | 3.1682 | 1.2678 | 0.52012 | 0 | 9.2597 | 0 | 5.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 37.1204 | 0%
CZ 2A | 0.097812 | 0.030629 | 0.012635 | 0.0049244 | 0 | 0.024092 | 0 | 0.018372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.26226 | 18.37% | CZ 2A | 3.2954 | 1.0319 | 0.42571 | 0.49244 | 0 | 0.8117 | 0 | 0.61898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.1627 | 18.37% | CZ 2A | 0.96556 | 0.30236 | 0.12473 | 0 | 0 | 0.23783 | 0 | 0.18136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.5404 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.0049244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049244 | 18.37% | CZ 2A | 10.1085 | 3.1654 | 1.3058 | 0.53824 | 0 | 2.4898 | 0 | 1.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 27.1334 | 18.37%
CZ 2B | 0.10446 | 0.030656 | 0.012662 | 0.01169 | 0 | 0.037425 | 0 | 0.034565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.30525 | 3.472% | CZ 2B | 3.5193 | 1.0328 | 0.42662 | 1.169 | 0 | 1.2609 | 0 | 1.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.0597 | 3.472% | CZ 2B | 1.0312 | 0.30262 | 0.125 | 0 | 0 | 0.36945 | 0 | 0.34121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.898 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.01169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01169 | 3.472% | CZ 2B | 10.7952 | 3.1682 | 1.3086 | 1.2777 | 0 | 3.8677 | 0 | 3.5721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 31.6166 | 3.472%
CZ 3A | 0.10002 | 0.030731 | 0.013279 | 0.043407 | 0 | 0.0088669 | 0 | 0.014409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.28452 | 16.13% | CZ 3A | 3.3699 | 1.0354 | 0.44738 | 4.3407 | 0 | 0.29874 | 0 | 0.48545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.4641 | 16.13% | CZ 3A | 0.98739 | 0.30337 | 0.13108 | 0 | 0 | 0.087531 | 0 | 0.14224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.3802 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.043407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043407 | 16.13% | CZ 3A | 10.337 | 3.176 | 1.3723 | 4.7444 | 0 | 0.91636 | 0 | 1.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 29.6622 | 16.13%
CZ 3B | 0.1022 | 0.03065 | 0.013111 | 0.026676 | 0 | 0.012965 | 0 | 0.022751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.28216 | 13.75% | CZ 3B | 3.4434 | 1.0327 | 0.44174 | 2.6676 | 0 | 0.43682 | 0 | 0.76653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.2752 | 13.75% | CZ 3B | 1.0089 | 0.30257 | 0.12943 | 0 | 0 | 0.12799 | 0 | 0.22459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.522 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.026676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026676 | 13.75% | CZ 3B | 10.5622 | 3.1676 | 1.355 | 2.9157 | 0 | 1.3399 | 0 | 2.3513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 29.3187 | 13.75%
CZ 3C | 0.10061 | 0.030769 | 0.013371 | 0.023384 | 0 | 0.000492 | 0 | 0.0074882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.24991 | 0.9199% | CZ 3C | 3.3896 | 1.0367 | 0.45048 | 2.3384 | 0 | 0.016576 | 0 | 0.25229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.9705 | 0.9199% | CZ 3C | 0.99316 | 0.30374 | 0.13199 | 0 | 0 | 0.0048569 | 0 | 0.073921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.2362 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.023384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023384 | 0.9199% | CZ 3C | 10.3974 | 3.1799 | 1.3818 | 2.5558 | 0 | 0.050847 | 0 | 0.77388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 25.9667 | 0.9199%
CZ 4A | 0.093394 | 0.030845 | 0.013776 | 0.091717 | 0 | 0.0033792 | 0 | 0.013479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.32039 | 16.99% | CZ 4A | 3.1466 | 1.0392 | 0.46414 | 9.1717 | 0 | 0.11385 | 0 | 0.45412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 16.8761 | 16.99% | CZ 4A | 0.92196 | 0.30449 | 0.13599 | 0 | 0 | 0.033358 | 0 | 0.13306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.2574 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.091717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091717 | 16.99% | CZ 4A | 9.652 | 3.1877 | 1.4237 | 10.0246 | 0 | 0.34922 | 0 | 1.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 33.6573 | 16.99%
CZ 4B | 0.094195 | 0.030672 | 0.013636 | 0.046529 | 0 | 0.0038712 | 0 | 0.019399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.2821 | 0.4596% | CZ 4B | 3.1736 | 1.0334 | 0.45941 | 4.6529 | 0 | 0.13043 | 0 | 0.65359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.5897 | 0.4596% | CZ 4B | 0.92986 | 0.30278 | 0.13461 | 0 | 0 | 0.038215 | 0 | 0.1915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.3255 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.046529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046529 | 0.4596% | CZ 4B | 9.7347 | 3.1698 | 1.4092 | 5.0856 | 0 | 0.40007 | 0 | 2.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 29.4312 | 0.4596%
CZ 4C | 0.096719 | 0.030921 | 0.013944 | 0.064421 | 0 | 0.00012976 | 0 | 0.013933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.29387 | 2.588% | CZ 4C | 3.2586 | 1.0418 | 0.46979 | 6.4421 | 0 | 0.0043718 | 0 | 0.46942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.1726 | 2.588% | CZ 4C | 0.95478 | 0.30524 | 0.13765 | 0 | 0 | 0.0012809 | 0 | 0.13754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.265 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.064421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064421 | 2.588% | CZ 4C | 9.9956 | 3.1955 | 1.441 | 7.0413 | 0 | 0.01341 | 0 | 1.4399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 30.7538 | 2.588%
CZ 5A | 0.10288 | 0.030748 | 0.014198 | 0.15033 | 0 | 0.00061095 | 0 | 0.012911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.38548 | 17.98% | CZ 5A | 3.4661 | 1.0359 | 0.47835 | 15.0332 | 0 | 0.020584 | 0 | 0.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 22.9557 | 17.98% | CZ 5A | 1.0156 | 0.30353 | 0.14016 | 0 | 0 | 0.0060311 | 0 | 0.12745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.3213 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.15033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15033 | 17.98% | CZ 5A | 10.632 | 3.1777 | 1.4673 | 16.4313 | 0 | 0.06314 | 0 | 1.3343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.7328 | 17.98%
CZ 5B | 0.10488 | 0.030791 | 0.014079 | 0.086035 | 0 | 0.0012976 | 0 | 0.01941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.3303 | 4.178% | CZ 5B | 3.5337 | 1.0374 | 0.47434 | 8.6035 | 0 | 0.043718 | 0 | 0.65395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 16.8331 | 4.178% | CZ 5B | 1.0354 | 0.30396 | 0.13898 | 0 | 0 | 0.012809 | 0 | 0.19161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.4113 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.086035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086035 | 4.178% | CZ 5B | 10.8393 | 3.1821 | 1.455 | 9.4036 | 0 | 0.1341 | 0 | 2.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 34.6472 | 4.178%
CZ 5C | 0.10568 | 0.030904 | 0.014182 | 0.073826 | 0 | 0.00011895 | 0 | 0.012516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.31103 | 0.01929% | CZ 5C | 3.5605 | 1.0412 | 0.4778 | 7.3826 | 0 | 0.0040075 | 0 | 0.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.3743 | 0.01929% | CZ 5C | 1.0432 | 0.30508 | 0.14 | 0 | 0 | 0.0011742 | 0 | 0.12356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.3416 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.073826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073826 | 0.01929% | CZ 5C | 10.9215 | 3.1939 | 1.4656 | 8.0692 | 0 | 0.012293 | 0 | 1.2935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 32.583 | 0.01929%
CZ 6A | 0.12607 | 0.030823 | 0.014501 | 0.22891 | 0 | 0.00060014 | 0 | 0.016625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.49133 | 1.74% | CZ 6A | 4.2474 | 1.0385 | 0.48855 | 22.8915 | 0 | 0.02022 | 0 | 0.56014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 31.7328 | 1.74% | CZ 6A | 1.2445 | 0.30428 | 0.14315 | 0 | 0 | 0.0059244 | 0 | 0.16412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.5905 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.22891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22891 | 1.74% | CZ 6A | 13.0286 | 3.1855 | 1.4986 | 25.0204 | 0 | 0.062022 | 0 | 1.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 52.1403 | 1.74%
CZ 6B | 0.12648 | 0.030818 | 0.01443 | 0.1434 | 0 | 0.00031359 | 0 | 0.013895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.40315 | 0.1795% | CZ 6B | 4.2614 | 1.0383 | 0.48618 | 14.3405 | 0 | 0.010565 | 0 | 0.46815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 23.0916 | 0.1795% | CZ 6B | 1.2486 | 0.30422 | 0.14245 | 0 | 0 | 0.0030956 | 0 | 0.13717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.5641 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1434 | 0.1795% | CZ 6B | 13.0716 | 3.1849 | 1.4913 | 15.6741 | 0 | 0.032408 | 0 | 1.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 42.5174 | 0.1795%
CZ 7 | 0.12635 | 0.030948 | 0.014868 | 0.23007 | 0 | 0.00020545 | 0 | 0.014501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.49074 | 0.1907% | CZ 7 | 4.2569 | 1.0427 | 0.50094 | 23.0071 | 0 | 0.006922 | 0 | 0.48855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 31.7896 | 0.1907% | CZ 7 | 1.2473 | 0.3055 | 0.14677 | 0 | 0 | 0.0020282 | 0 | 0.14315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.5733 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.23007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23007 | 0.1907% | CZ 7 | 13.0576 | 3.1983 | 1.5366 | 25.1468 | 0 | 0.021233 | 0 | 1.4986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 52.0862 | 0.1907%
CZ 8 | 0.12828 | 0.031715 | 0.01536 | 0.22695 | 0 | 0.00011895 | 0 | 0.017404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.49363 | 0.009711% | CZ 8 | 4.3219 | 1.0685 | 0.51751 | 22.695 | 0 | 0.0040075 | 0 | 0.58637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 31.6798 | 0.009711% | CZ 8 | 1.2663 | 0.31308 | 0.15163 | 0 | 0 | 0.0011742 | 0 | 0.17181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.6326 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.22695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22695 | 0.009711% | CZ 8 | 13.2571 | 3.2777 | 1.5874 | 24.8056 | 0 | 0.012293 | 0 | 1.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 52.3658 | 0.009711%
US Weighted | 0.1 | 0.03073 | 0.013415 | 0.065002 | 0 | 0.010542 | 0 | 0.016801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.31029 | 100% | US Weighted | 3.3693 | 1.0353 | 0.45196 | 6.5002 | 0 | 0.35519 | 0 | 0.56606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.7645 | 100% | US Weighted | 0.98721 | 0.30335 | 0.13243 | 0 | 0 | 0.10407 | 0 | 0.16586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 2.4215 | 100% | US Weighted | 0 | 0 | 0 | 0.065002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065002 | 100% | US Weighted | 10.3351 | 3.1758 | 1.3864 | 7.1047 | 0 | 1.0895 | 0 | 1.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 32.4548 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.16447 | 0.045302 | 0.012251 | 6.374e-05 | 0 | 0.031126 | 0 | 0.017042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.34406 | 3.023% | CZ 1A | 5.5413 | 1.5263 | 0.41277 | 0.006374 | 0 | 1.0487 | 0 | 0.57417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.5961 | 3.023% | CZ 1A | 1.6236 | 0.44721 | 0.12094 | 0 | 0 | 0.30727 | 0 | 0.16823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.3958 | 3.023% | CZ 1A | 0 | 0 | 0 | 6.374e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.374e-05 | 3.023% | CZ 1A | 16.9974 | 4.6818 | 1.2661 | 0.0069668 | 0 | 3.2168 | 0 | 1.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 35.5574 | 3.023%
CZ 1B | 0.16166 | 0.045237 | 0.012268 | 0.0042342 | 0 | 0.094043 | 0 | 0.054737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.44598 | 0% | CZ 1B | 5.4466 | 1.5241 | 0.41332 | 0.42342 | 0 | 3.1685 | 0 | 1.8442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.3065 | 0% | CZ 1B | 1.5958 | 0.44657 | 0.1211 | 0 | 0 | 0.92836 | 0 | 0.54034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 4.3608 | 0% | CZ 1B | 0 | 0 | 0 | 0.0042342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042342 | 0% | CZ 1B | 16.7069 | 4.6751 | 1.2678 | 0.46279 | 0 | 9.719 | 0 | 5.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 46.1156 | 0%
CZ 2A | 0.16637 | 0.045194 | 0.012635 | 0.0043926 | 0 | 0.026471 | 0 | 0.019404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.34827 | 18.37% | CZ 2A | 5.6052 | 1.5227 | 0.42571 | 0.43926 | 0 | 0.89185 | 0 | 0.65377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.0249 | 18.37% | CZ 2A | 1.6423 | 0.44614 | 0.12473 | 0 | 0 | 0.26131 | 0 | 0.19155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.3946 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.0043926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043926 | 18.37% | CZ 2A | 17.1935 | 4.6707 | 1.3058 | 0.48011 | 0 | 2.7357 | 0 | 2.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 36.0182 | 18.37%
CZ 2B | 0.17675 | 0.045227 | 0.012662 | 0.010426 | 0 | 0.039647 | 0 | 0.035922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.39444 | 3.472% | CZ 2B | 5.9551 | 1.5238 | 0.42662 | 1.0426 | 0 | 1.3358 | 0 | 1.2103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 13.9806 | 3.472% | CZ 2B | 1.7449 | 0.44646 | 0.125 | 0 | 0 | 0.39138 | 0 | 0.35461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.7908 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.010426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010426 | 3.472% | CZ 2B | 18.2669 | 4.674 | 1.3086 | 1.1396 | 0 | 4.0974 | 0 | 3.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.8259 | 3.472%
CZ 3A | 0.17008 | 0.045281 | 0.013279 | 0.042063 | 0 | 0.0097806 | 0 | 0.015339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.36962 | 16.13% | CZ 3A | 5.7304 | 1.5256 | 0.44738 | 4.2063 | 0 | 0.32953 | 0 | 0.51679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.2424 | 16.13% | CZ 3A | 1.679 | 0.447 | 0.13108 | 0 | 0 | 0.096551 | 0 | 0.15142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2336 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.042063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042063 | 16.13% | CZ 3A | 17.5774 | 4.6796 | 1.3723 | 4.5975 | 0 | 1.0108 | 0 | 1.5852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 38.4498 | 16.13%
CZ 3B | 0.17345 | 0.045248 | 0.013111 | 0.02456 | 0 | 0.014095 | 0 | 0.023778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.36804 | 13.75% | CZ 3B | 5.8438 | 1.5245 | 0.44174 | 2.456 | 0 | 0.47489 | 0 | 0.80114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.0286 | 13.75% | CZ 3B | 1.7122 | 0.44668 | 0.12943 | 0 | 0 | 0.13914 | 0 | 0.23473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.3908 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.02456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02456 | 13.75% | CZ 3B | 17.9255 | 4.6762 | 1.355 | 2.6844 | 0 | 1.4567 | 0 | 2.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 38.1823 | 13.75%
CZ 3C | 0.17099 | 0.045335 | 0.013371 | 0.021224 | 0 | 0.00051904 | 0 | 0.0075098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.33275 | 0.9199% | CZ 3C | 5.761 | 1.5274 | 0.45048 | 2.1224 | 0 | 0.017487 | 0 | 0.25302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.6182 | 0.9199% | CZ 3C | 1.688 | 0.44753 | 0.13199 | 0 | 0 | 0.0051238 | 0 | 0.074135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.0753 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.021224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021224 | 0.9199% | CZ 3C | 17.6713 | 4.6852 | 1.3818 | 2.3197 | 0 | 0.053641 | 0 | 0.77611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 34.5148 | 0.9199%
CZ 4A | 0.1582 | 0.045356 | 0.013776 | 0.09307 | 0 | 0.0037738 | 0 | 0.013695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.40167 | 16.99% | CZ 4A | 5.33 | 1.5281 | 0.46414 | 9.307 | 0 | 0.12715 | 0 | 0.46141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 19.7043 | 16.99% | CZ 4A | 1.5617 | 0.44774 | 0.13599 | 0 | 0 | 0.037254 | 0 | 0.13519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.0464 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.09307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09307 | 16.99% | CZ 4A | 16.3493 | 4.6874 | 1.4237 | 10.1725 | 0 | 0.39001 | 0 | 1.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 42.0653 | 16.99%
CZ 4B | 0.1594 | 0.045237 | 0.013636 | 0.044008 | 0 | 0.0043469 | 0 | 0.021659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.36209 | 0.4596% | CZ 4B | 5.3704 | 1.5241 | 0.45941 | 4.4008 | 0 | 0.14646 | 0 | 0.72973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.1174 | 0.4596% | CZ 4B | 1.5735 | 0.44657 | 0.13461 | 0 | 0 | 0.042912 | 0 | 0.21381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.14 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.044008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044008 | 0.4596% | CZ 4B | 16.4733 | 4.6751 | 1.4092 | 4.8101 | 0 | 0.44924 | 0 | 2.2384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 37.6824 | 0.4596%
CZ 4C | 0.16333 | 0.045356 | 0.013944 | 0.05981 | 0 | 0.00013517 | 0 | 0.013792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.37017 | 2.588% | CZ 4C | 5.503 | 1.5281 | 0.46979 | 5.981 | 0 | 0.004554 | 0 | 0.46469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 16.4377 | 2.588% | CZ 4C | 1.6124 | 0.44774 | 0.13765 | 0 | 0 | 0.0013343 | 0 | 0.13615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.0638 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.05981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05981 | 2.588% | CZ 4C | 16.8801 | 4.6874 | 1.441 | 6.5373 | 0 | 0.013969 | 0 | 1.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 38.6122 | 2.588%
CZ 5A | 0.17468 | 0.045237 | 0.014198 | 0.15695 | 0 | 0.00063798 | 0 | 0.012987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.47849 | 17.98% | CZ 5A | 5.8852 | 1.5241 | 0.47835 | 15.695 | 0 | 0.021495 | 0 | 0.43755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 26.5282 | 17.98% | CZ 5A | 1.7244 | 0.44657 | 0.14016 | 0 | 0 | 0.006298 | 0 | 0.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.1741 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.15695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15695 | 17.98% | CZ 5A | 18.0524 | 4.6751 | 1.4673 | 17.1547 | 0 | 0.065933 | 0 | 1.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 50.3846 | 17.98%
CZ 5B | 0.17789 | 0.045319 | 0.014073 | 0.086989 | 0 | 0.0014652 | 0 | 0.019783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.41932 | 4.178% | CZ 5B | 5.9936 | 1.5269 | 0.47416 | 8.6989 | 0 | 0.049365 | 0 | 0.66652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 19.8959 | 4.178% | CZ 5B | 1.7561 | 0.44737 | 0.13893 | 0 | 0 | 0.014464 | 0 | 0.19529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2807 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.086989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086989 | 4.178% | CZ 5B | 18.3848 | 4.6835 | 1.4544 | 9.5079 | 0 | 0.15142 | 0 | 2.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 43.8536 | 4.178%
CZ 5C | 0.17895 | 0.045329 | 0.014182 | 0.06767 | 0 | 0.00011354 | 0 | 0.012322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.39237 | 0.01929% | CZ 5C | 6.0293 | 1.5272 | 0.4778 | 6.767 | 0 | 0.0038253 | 0 | 0.41514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.7068 | 0.01929% | CZ 5C | 1.7666 | 0.44748 | 0.14 | 0 | 0 | 0.0011208 | 0 | 0.12164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2053 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.06767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06767 | 0.01929% | CZ 5C | 18.4943 | 4.6846 | 1.4656 | 7.3964 | 0 | 0.011734 | 0 | 1.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.9531 | 0.01929%
CZ 6A | 0.21114 | 0.045313 | 0.014501 | 0.23714 | 0 | 0.0006488 | 0 | 0.016771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.59931 | 1.74% | CZ 6A | 7.1137 | 1.5267 | 0.48855 | 23.7137 | 0 | 0.021859 | 0 | 0.56506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 35.916 | 1.74% | CZ 6A | 2.0843 | 0.44732 | 0.14315 | 0 | 0 | 0.0064047 | 0 | 0.16556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.5753 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.23714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23714 | 1.74% | CZ 6A | 21.8206 | 4.683 | 1.4986 | 25.9191 | 0 | 0.067051 | 0 | 1.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 63.3486 | 1.74%
CZ 6B | 0.21177 | 0.045254 | 0.01443 | 0.14325 | 0 | 0.00034062 | 0 | 0.013884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.50273 | 0.1795% | CZ 6B | 7.1348 | 1.5247 | 0.48618 | 14.325 | 0 | 0.011476 | 0 | 0.46778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 26.4364 | 0.1795% | CZ 6B | 2.0905 | 0.44673 | 0.14245 | 0 | 0 | 0.0033625 | 0 | 0.13706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.5486 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.14325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14325 | 0.1795% | CZ 6B | 21.8854 | 4.6768 | 1.4913 | 15.6572 | 0 | 0.035202 | 0 | 1.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 52.8079 | 0.1795%
CZ 7 | 0.21101 | 0.045373 | 0.014868 | 0.22438 | 0 | 0.00022167 | 0 | 0.01442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.58407 | 0.1907% | CZ 7 | 7.1093 | 1.5287 | 0.50094 | 22.438 | 0 | 0.0074685 | 0 | 0.48582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 34.5567 | 0.1907% | CZ 7 | 2.083 | 0.4479 | 0.14677 | 0 | 0 | 0.0021883 | 0 | 0.14234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.5508 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.22438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22438 | 0.1907% | CZ 7 | 21.8072 | 4.6891 | 1.5366 | 24.5248 | 0 | 0.022909 | 0 | 1.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 61.6978 | 0.1907%
CZ 8 | 0.21378 | 0.045562 | 0.01536 | 0.21894 | 0 | 0.00012435 | 0 | 0.01762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.58519 | 0.009711% | CZ 8 | 7.2028 | 1.5351 | 0.51751 | 21.8939 | 0 | 0.0041897 | 0 | 0.59366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 34.2335 | 0.009711% | CZ 8 | 2.1104 | 0.44977 | 0.15163 | 0 | 0 | 0.0012276 | 0 | 0.17394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.6155 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.21894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21894 | 0.009711% | CZ 8 | 22.0938 | 4.7087 | 1.5874 | 23.93 | 0 | 0.012851 | 0 | 1.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 61.7808 | 0.009711%
US Weighted | 0.16972 | 0.045269 | 0.013414 | 0.065791 | 0 | 0.011554 | 0 | 0.017433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073801 | 0.39698 | 100% | US Weighted | 5.718 | 1.5252 | 0.45196 | 6.5791 | 0 | 0.38927 | 0 | 0.58734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.7374 | 100% | US Weighted | 1.6754 | 0.44688 | 0.13242 | 0 | 0 | 0.11406 | 0 | 0.17209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72854 | 3.2694 | 100% | US Weighted | 0 | 0 | 0 | 0.065791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065791 | 100% | US Weighted | 17.5396 | 4.6784 | 1.3863 | 7.191 | 0 | 1.194 | 0 | 1.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 41.418 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.17401 | 0.045302 | 0.012262 | 8.7415e-05 | 0 | 0.041009 | 0 | 0.022811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.36958 | 3.023% | CZ 1A | 5.8626 | 1.5263 | 0.41314 | 0.0087415 | 0 | 1.3817 | 0 | 0.76853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.4577 | 3.023% | CZ 1A | 1.7177 | 0.44721 | 0.12105 | 0 | 0 | 0.40483 | 0 | 0.22518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.6475 | 3.023% | CZ 1A | 0 | 0 | 0 | 8.7415e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7415e-05 | 3.023% | CZ 1A | 17.9831 | 4.6818 | 1.2673 | 0.0095545 | 0 | 4.2382 | 0 | 2.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 38.1956 | 3.023%
CZ 1B | 0.17156 | 0.045237 | 0.012268 | 0.0049262 | 0 | 0.10551 | 0 | 0.080683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.49428 | 0% | CZ 1B | 5.7801 | 1.5241 | 0.41332 | 0.49262 | 0 | 3.5547 | 0 | 2.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 16.9798 | 0% | CZ 1B | 1.6936 | 0.44657 | 0.1211 | 0 | 0 | 1.0415 | 0 | 0.79648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 4.8308 | 0% | CZ 1B | 0 | 0 | 0 | 0.0049262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049262 | 0% | CZ 1B | 17.7299 | 4.6751 | 1.2678 | 0.53843 | 0 | 10.9036 | 0 | 8.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 51.1116 | 0%
CZ 2A | 0.17552 | 0.045194 | 0.012641 | 0.0051338 | 0 | 0.032764 | 0 | 0.024811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.37016 | 18.37% | CZ 2A | 5.9134 | 1.5227 | 0.42589 | 0.51338 | 0 | 1.1039 | 0 | 0.83593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.8119 | 18.37% | CZ 2A | 1.7326 | 0.44614 | 0.12479 | 0 | 0 | 0.32344 | 0 | 0.24493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.6035 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.0051338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051338 | 18.37% | CZ 2A | 18.139 | 4.6707 | 1.3064 | 0.56113 | 0 | 3.3861 | 0 | 2.5641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 38.2857 | 18.37%
CZ 2B | 0.18564 | 0.045227 | 0.012657 | 0.01073 | 0 | 0.045697 | 0 | 0.056737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.43079 | 3.472% | CZ 2B | 6.2544 | 1.5238 | 0.42643 | 1.073 | 0 | 1.5396 | 0 | 1.9116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.2255 | 3.472% | CZ 2B | 1.8325 | 0.44646 | 0.12495 | 0 | 0 | 0.45111 | 0 | 0.56009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 4.1467 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.01073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01073 | 3.472% | CZ 2B | 19.185 | 4.674 | 1.3081 | 1.1728 | 0 | 4.7226 | 0 | 5.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 44.5844 | 3.472%
CZ 3A | 0.17748 | 0.045281 | 0.013279 | 0.042558 | 0 | 0.012668 | 0 | 0.017869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.38324 | 16.13% | CZ 3A | 5.9797 | 1.5256 | 0.44738 | 4.2558 | 0 | 0.4268 | 0 | 0.60204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.7341 | 16.13% | CZ 3A | 1.7521 | 0.447 | 0.13108 | 0 | 0 | 0.12505 | 0 | 0.1764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.3631 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.042558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042558 | 16.13% | CZ 3A | 18.3423 | 4.6796 | 1.3723 | 4.6516 | 0 | 1.3092 | 0 | 1.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 39.8601 | 16.13%
CZ 3B | 0.18146 | 0.045248 | 0.013111 | 0.025724 | 0 | 0.016723 | 0 | 0.026163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.38254 | 13.75% | CZ 3B | 6.1138 | 1.5245 | 0.44174 | 2.5724 | 0 | 0.56342 | 0 | 0.88147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 14.594 | 13.75% | CZ 3B | 1.7913 | 0.44668 | 0.12943 | 0 | 0 | 0.16508 | 0 | 0.25827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.5223 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.025724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025724 | 13.75% | CZ 3B | 18.7536 | 4.6762 | 1.355 | 2.8116 | 0 | 1.7282 | 0 | 2.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 39.6868 | 13.75%
CZ 3C | 0.16558 | 0.045335 | 0.013365 | 0.021493 | 0 | 0.00070286 | 0 | 0.008629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.32921 | 0.9199% | CZ 3C | 5.5788 | 1.5274 | 0.4503 | 2.1493 | 0 | 0.023681 | 0 | 0.29073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.5169 | 0.9199% | CZ 3C | 1.6346 | 0.44753 | 0.13194 | 0 | 0 | 0.0069384 | 0 | 0.085183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.0377 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.021493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021493 | 0.9199% | CZ 3C | 17.1125 | 4.6852 | 1.3812 | 2.3492 | 0 | 0.072639 | 0 | 0.89178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 34.1509 | 0.9199%
CZ 4A | 0.16557 | 0.045356 | 0.013776 | 0.096949 | 0 | 0.0054607 | 0 | 0.015933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.41715 | 16.99% | CZ 4A | 5.5783 | 1.5281 | 0.46414 | 9.6949 | 0 | 0.18398 | 0 | 0.53682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 20.4829 | 16.99% | CZ 4A | 1.6344 | 0.44774 | 0.13599 | 0 | 0 | 0.053906 | 0 | 0.15729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.1609 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.096949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096949 | 16.99% | CZ 4A | 17.1108 | 4.6874 | 1.4237 | 10.5965 | 0 | 0.56435 | 0 | 1.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.6878 | 16.99%
CZ 4B | 0.16676 | 0.045237 | 0.013636 | 0.046388 | 0 | 0.0068773 | 0 | 0.028563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.38156 | 0.4596% | CZ 4B | 5.6183 | 1.5241 | 0.45941 | 4.6388 | 0 | 0.23171 | 0 | 0.96235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.9314 | 0.4596% | CZ 4B | 1.6462 | 0.44657 | 0.13461 | 0 | 0 | 0.06789 | 0 | 0.28197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.3087 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.046388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046388 | 0.4596% | CZ 4B | 17.2338 | 4.6751 | 1.4092 | 5.0702 | 0 | 0.71074 | 0 | 2.9519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 39.7093 | 0.4596%
CZ 4C | 0.1704 | 0.045356 | 0.013944 | 0.063558 | 0 | 0.00019464 | 0 | 0.015582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.38314 | 2.588% | CZ 4C | 5.7411 | 1.5281 | 0.46979 | 6.3558 | 0 | 0.0065577 | 0 | 0.52498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 17.1231 | 2.588% | CZ 4C | 1.6821 | 0.44774 | 0.13765 | 0 | 0 | 0.0019214 | 0 | 0.15382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.1548 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.063558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063558 | 2.588% | CZ 4C | 17.6104 | 4.6874 | 1.441 | 6.9469 | 0 | 0.020115 | 0 | 1.6103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 39.9745 | 2.588%
CZ 5A | 0.16572 | 0.045237 | 0.014198 | 0.16387 | 0 | 0.00085425 | 0 | 0.014517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.47851 | 17.98% | CZ 5A | 5.5835 | 1.5241 | 0.47835 | 16.3874 | 0 | 0.028781 | 0 | 0.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 26.988 | 17.98% | CZ 5A | 1.636 | 0.44657 | 0.14016 | 0 | 0 | 0.0084329 | 0 | 0.14331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.106 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.16387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16387 | 17.98% | CZ 5A | 17.127 | 4.6751 | 1.4673 | 17.9115 | 0 | 0.088284 | 0 | 1.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 50.4278 | 17.98%
CZ 5B | 0.16793 | 0.045319 | 0.014073 | 0.091626 | 0 | 0.0023465 | 0 | 0.023573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.41897 | 4.178% | CZ 5B | 5.6579 | 1.5269 | 0.47416 | 9.1626 | 0 | 0.079057 | 0 | 0.79421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 20.1914 | 4.178% | CZ 5B | 1.6578 | 0.44737 | 0.13893 | 0 | 0 | 0.023164 | 0 | 0.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.2314 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.091626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091626 | 4.178% | CZ 5B | 17.355 | 4.6835 | 1.4544 | 10.0147 | 0 | 0.2425 | 0 | 2.4362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.8447 | 4.178%
CZ 5C | 0.16964 | 0.045329 | 0.014182 | 0.072407 | 0 | 0.00012435 | 0 | 0.014019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.3898 | 0.01929% | CZ 5C | 5.7154 | 1.5272 | 0.4778 | 7.2407 | 0 | 0.0041897 | 0 | 0.47234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 17.9344 | 0.01929% | CZ 5C | 1.6746 | 0.44748 | 0.14 | 0 | 0 | 0.0012276 | 0 | 0.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.1332 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.072407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072407 | 0.01929% | CZ 5C | 17.5316 | 4.6846 | 1.4656 | 7.9141 | 0 | 0.012851 | 0 | 1.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 40.716 | 0.01929%
CZ 6A | 0.21354 | 0.045313 | 0.014501 | 0.24262 | 0 | 0.00084344 | 0 | 0.018128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.60905 | 1.74% | CZ 6A | 7.1944 | 1.5267 | 0.48855 | 24.2624 | 0 | 0.028417 | 0 | 0.61078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 36.6079 | 1.74% | CZ 6A | 2.108 | 0.44732 | 0.14315 | 0 | 0 | 0.0083261 | 0 | 0.17896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.6172 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.24262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24262 | 1.74% | CZ 6A | 22.0681 | 4.683 | 1.4986 | 26.5188 | 0 | 0.087166 | 0 | 1.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 64.3876 | 1.74%
CZ 6B | 0.21418 | 0.045254 | 0.01443 | 0.14563 | 0 | 0.00051904 | 0 | 0.024714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.51883 | 0.1795% | CZ 6B | 7.2162 | 1.5247 | 0.48618 | 14.563 | 0 | 0.017487 | 0 | 0.83265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 27.1369 | 0.1795% | CZ 6B | 2.1144 | 0.44673 | 0.14245 | 0 | 0 | 0.0051238 | 0 | 0.24397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.6842 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.14563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14563 | 0.1795% | CZ 6B | 22.1352 | 4.6768 | 1.4913 | 15.9174 | 0 | 0.053641 | 0 | 2.5541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 54.4867 | 0.1795%
CZ 7 | 0.21381 | 0.045373 | 0.014868 | 0.23246 | 0 | 0.00033521 | 0 | 0.015923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.59687 | 0.1907% | CZ 7 | 7.2035 | 1.5287 | 0.50094 | 23.2459 | 0 | 0.011294 | 0 | 0.53646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 35.5234 | 0.1907% | CZ 7 | 2.1106 | 0.4479 | 0.14677 | 0 | 0 | 0.0033091 | 0 | 0.15718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.5973 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.23246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23246 | 0.1907% | CZ 7 | 22.0961 | 4.6891 | 1.5366 | 25.4077 | 0 | 0.034643 | 0 | 1.6455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 63.068 | 0.1907%
CZ 8 | 0.2161 | 0.045562 | 0.01536 | 0.23875 | 0 | 8.11e-05 | 0 | 0.020605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.61056 | 0.009711% | CZ 8 | 7.2807 | 1.5351 | 0.51751 | 23.8747 | 0 | 0.0027324 | 0 | 0.69421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 36.4016 | 0.009711% | CZ 8 | 2.1333 | 0.44977 | 0.15163 | 0 | 0 | 0.00080059 | 0 | 0.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.6704 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.23875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23875 | 0.009711% | CZ 8 | 22.333 | 4.7087 | 1.5874 | 26.0951 | 0 | 0.0083814 | 0 | 2.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 64.5203 | 0.009711%
US Weighted | 0.17373 | 0.045269 | 0.013416 | 0.068505 | 0 | 0.014427 | 0 | 0.021008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074103 | 0.41046 | 100% | US Weighted | 5.8533 | 1.5252 | 0.45199 | 6.8505 | 0 | 0.48607 | 0 | 0.70779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 18.3715 | 100% | US Weighted | 1.715 | 0.44688 | 0.13243 | 0 | 0 | 0.14242 | 0 | 0.20738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73153 | 3.3757 | 100% | US Weighted | 0 | 0 | 0 | 0.068505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068505 | 100% | US Weighted | 17.9546 | 4.6784 | 1.3864 | 7.4876 | 0 | 1.491 | 0 | 2.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 42.8274 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.26058 | 0.066869 | 0.012662 | 9.2879e-05 | 0 | 0.065231 | 0 | 0.046757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.52749 | 3.023% | CZ 1A | 8.7793 | 2.2529 | 0.42662 | 0.0092879 | 0 | 2.1977 | 0 | 1.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.7784 | 3.023% | CZ 1A | 2.5723 | 0.66011 | 0.125 | 0 | 0 | 0.64394 | 0 | 0.46157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.2063 | 3.023% | CZ 1A | 0 | 0 | 0 | 9.2879e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2879e-05 | 3.023% | CZ 1A | 26.9299 | 6.9107 | 1.3086 | 0.010152 | 0 | 6.7414 | 0 | 4.8321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 54.5153 | 3.023%
CZ 1B | 0.26058 | 0.066788 | 0.012668 | 0.0050027 | 0 | 0.14615 | 0 | 0.13323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.69972 | 0% | CZ 1B | 8.7793 | 2.2502 | 0.4268 | 0.50027 | 0 | 4.9239 | 0 | 4.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.9064 | 0% | CZ 1B | 2.5723 | 0.65931 | 0.12505 | 0 | 0 | 1.4427 | 0 | 1.3152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 6.858 | 0% | CZ 1B | 0 | 0 | 0 | 0.0050027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0050027 | 0% | CZ 1B | 26.9299 | 6.9023 | 1.3092 | 0.54679 | 0 | 15.1038 | 0 | 13.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 72.3433 | 0%
CZ 2A | 0.26058 | 0.066734 | 0.013062 | 0.0065452 | 0 | 0.046924 | 0 | 0.036279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.50543 | 18.37% | CZ 2A | 8.7793 | 2.2484 | 0.4401 | 0.65452 | 0 | 1.581 | 0 | 1.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.4627 | 18.37% | CZ 2A | 2.5723 | 0.65878 | 0.12895 | 0 | 0 | 0.46322 | 0 | 0.35813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.9248 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.0065452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065452 | 18.37% | CZ 2A | 26.9299 | 6.8967 | 1.35 | 0.71539 | 0 | 4.8495 | 0 | 3.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 52.2731 | 18.37%
CZ 2B | 0.26058 | 0.066777 | 0.013079 | 0.0077836 | 0 | 0.065604 | 0 | 0.095892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.58502 | 3.472% | CZ 2B | 8.7793 | 2.2498 | 0.44064 | 0.77836 | 0 | 2.2103 | 0 | 3.2308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.2264 | 3.472% | CZ 2B | 2.5723 | 0.65921 | 0.12911 | 0 | 0 | 0.64762 | 0 | 0.94662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.6983 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.0077836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077836 | 3.472% | CZ 2B | 26.9299 | 6.9012 | 1.3516 | 0.85075 | 0 | 6.78 | 0 | 9.9101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 60.506 | 3.472%
CZ 3A | 0.26058 | 0.066842 | 0.013722 | 0.054432 | 0 | 0.018437 | 0 | 0.030493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.51981 | 16.13% | CZ 3A | 8.7793 | 2.252 | 0.46232 | 5.4432 | 0 | 0.62116 | 0 | 1.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.1226 | 16.13% | CZ 3A | 2.5723 | 0.65985 | 0.13546 | 0 | 0 | 0.182 | 0 | 0.30102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.594 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.054432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054432 | 16.13% | CZ 3A | 26.9299 | 6.9079 | 1.4181 | 5.9495 | 0 | 1.9054 | 0 | 3.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 54.0445 | 16.13%
CZ 3B | 0.26058 | 0.066799 | 0.013544 | 0.026407 | 0 | 0.023535 | 0 | 0.043972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.51014 | 13.75% | CZ 3B | 8.7793 | 2.2506 | 0.45631 | 2.6407 | 0 | 0.79294 | 0 | 1.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.9384 | 13.75% | CZ 3B | 2.5723 | 0.65942 | 0.1337 | 0 | 0 | 0.23233 | 0 | 0.43408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7752 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.026407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026407 | 13.75% | CZ 3B | 26.9299 | 6.9035 | 1.3997 | 2.8862 | 0 | 2.4323 | 0 | 4.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 52.8783 | 13.75%
CZ 3C | 0.26058 | 0.066799 | 0.013819 | 0.021965 | 0 | 0.00096238 | 0 | 0.010602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.45003 | 0.9199% | CZ 3C | 8.7793 | 2.2506 | 0.4656 | 2.1965 | 0 | 0.032424 | 0 | 0.35721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 16.6188 | 0.9199% | CZ 3C | 2.5723 | 0.65942 | 0.13642 | 0 | 0 | 0.0095003 | 0 | 0.10466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2257 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.021965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021965 | 0.9199% | CZ 3C | 26.9299 | 6.9035 | 1.4282 | 2.4008 | 0 | 0.099459 | 0 | 1.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 46.6399 | 0.9199%
CZ 4A | 0.26058 | 0.066723 | 0.014225 | 0.12511 | 0 | 0.0084236 | 0 | 0.031559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.58192 | 16.99% | CZ 4A | 8.7793 | 2.248 | 0.47926 | 12.5107 | 0 | 0.2838 | 0 | 1.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.9016 | 16.99% | CZ 4A | 2.5723 | 0.65867 | 0.14042 | 0 | 0 | 0.083155 | 0 | 0.31154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5095 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.12511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12511 | 16.99% | CZ 4A | 26.9299 | 6.8956 | 1.4701 | 13.6742 | 0 | 0.87054 | 0 | 3.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 60.8843 | 16.99%
CZ 4B | 0.26058 | 0.066745 | 0.014084 | 0.055858 | 0 | 0.009094 | 0 | 0.033829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.51549 | 0.4596% | CZ 4B | 8.7793 | 2.2488 | 0.47452 | 5.5858 | 0 | 0.30639 | 0 | 1.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.0717 | 0.4596% | CZ 4B | 2.5723 | 0.65888 | 0.13904 | 0 | 0 | 0.089773 | 0 | 0.33395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5374 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.055858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055858 | 0.4596% | CZ 4B | 26.9299 | 6.8979 | 1.4556 | 6.1053 | 0 | 0.93983 | 0 | 3.4961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 53.607 | 0.4596%
CZ 4C | 0.26058 | 0.066669 | 0.014409 | 0.073394 | 0 | 0.00027033 | 0 | 0.019583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.51021 | 2.588% | CZ 4C | 8.7793 | 2.2462 | 0.48545 | 7.3394 | 0 | 0.009108 | 0 | 0.65978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.0564 | 2.588% | CZ 4C | 2.5723 | 0.65814 | 0.14224 | 0 | 0 | 0.0026686 | 0 | 0.19332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3121 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.073394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073394 | 2.588% | CZ 4C | 26.9299 | 6.89 | 1.4891 | 8.022 | 0 | 0.027938 | 0 | 2.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 53.1651 | 2.588%
CZ 5A | 0.26058 | 0.066669 | 0.014657 | 0.19806 | 0 | 0.0015679 | 0 | 0.030704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.64754 | 17.98% | CZ 5A | 8.7793 | 2.2462 | 0.49383 | 19.8059 | 0 | 0.052826 | 0 | 1.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 34.9497 | 17.98% | CZ 5A | 2.5723 | 0.65814 | 0.14469 | 0 | 0 | 0.015478 | 0 | 0.3031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4371 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.19806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19806 | 17.98% | CZ 5A | 26.9299 | 6.89 | 1.5148 | 21.6479 | 0 | 0.16204 | 0 | 3.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 68.1002 | 17.98%
CZ 5B | 0.26058 | 0.066723 | 0.014533 | 0.11261 | 0 | 0.0036441 | 0 | 0.029169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.56256 | 4.178% | CZ 5B | 8.7793 | 2.248 | 0.48964 | 11.2607 | 0 | 0.12278 | 0 | 0.98275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 26.4204 | 4.178% | CZ 5B | 2.5723 | 0.65867 | 0.14347 | 0 | 0 | 0.035973 | 0 | 0.28795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4418 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.11261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11261 | 4.178% | CZ 5B | 26.9299 | 6.8956 | 1.5019 | 12.308 | 0 | 0.3766 | 0 | 3.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 58.8089 | 4.178%
CZ 5C | 0.26058 | 0.066648 | 0.014652 | 0.093562 | 0 | 5.4066e-05 | 0 | 0.016377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.52717 | 0.01929% | CZ 5C | 8.7793 | 2.2455 | 0.49365 | 9.3562 | 0 | 0.0018216 | 0 | 0.55176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.9653 | 0.01929% | CZ 5C | 2.5723 | 0.65792 | 0.14464 | 0 | 0 | 0.00053373 | 0 | 0.16167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2805 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.093562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093562 | 0.01929% | CZ 5C | 26.9299 | 6.8878 | 1.5142 | 10.2263 | 0 | 0.0055876 | 0 | 1.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 55.0387 | 0.01929%
CZ 6A | 0.26058 | 0.066718 | 0.01496 | 0.32128 | 0 | 0.0016382 | 0 | 0.042118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.78259 | 1.74% | CZ 6A | 8.7793 | 2.2478 | 0.50403 | 32.1276 | 0 | 0.055194 | 0 | 1.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 47.6702 | 1.74% | CZ 6A | 2.5723 | 0.65862 | 0.14768 | 0 | 0 | 0.016172 | 0 | 0.41577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.554 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.32128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32128 | 1.74% | CZ 6A | 26.9299 | 6.8951 | 1.5461 | 35.1155 | 0 | 0.1693 | 0 | 4.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 82.791 | 1.74%
CZ 6B | 0.26058 | 0.066664 | 0.01489 | 0.19865 | 0 | 0.00096238 | 0 | 0.033651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.6507 | 0.1795% | CZ 6B | 8.7793 | 2.246 | 0.50167 | 19.8647 | 0 | 0.032424 | 0 | 1.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 35.0951 | 0.1795% | CZ 6B | 2.5723 | 0.65808 | 0.14699 | 0 | 0 | 0.0095003 | 0 | 0.33219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4625 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.19865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19865 | 0.1795% | CZ 6B | 26.9299 | 6.8895 | 1.5388 | 21.7122 | 0 | 0.099459 | 0 | 3.4777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 68.4299 | 0.1795%
CZ 7 | 0.26058 | 0.066696 | 0.015333 | 0.29859 | 0 | 0.00053526 | 0 | 0.031332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.74837 | 0.1907% | CZ 7 | 8.7793 | 2.2471 | 0.5166 | 29.859 | 0 | 0.018034 | 0 | 1.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 45.0128 | 0.1907% | CZ 7 | 2.5723 | 0.6584 | 0.15136 | 0 | 0 | 0.0052839 | 0 | 0.30929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4401 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.29859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29859 | 0.1907% | CZ 7 | 26.9299 | 6.8928 | 1.5846 | 32.6359 | 0 | 0.055317 | 0 | 3.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 79.119 | 0.1907%
CZ 8 | 0.26058 | 0.066231 | 0.015831 | 0.31349 | 0 | 7.0286e-05 | 0 | 0.023957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.75546 | 0.009711% | CZ 8 | 8.7793 | 2.2314 | 0.53336 | 31.3493 | 0 | 0.0023681 | 0 | 0.80715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 46.24 | 0.009711% | CZ 8 | 2.5723 | 0.65381 | 0.15628 | 0 | 0 | 0.00069384 | 0 | 0.23649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.363 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.31349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31349 | 0.009711% | CZ 8 | 26.9299 | 6.8448 | 1.636 | 34.2647 | 0 | 0.0072639 | 0 | 2.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 79.941 | 0.009711%
US Weighted | 0.26058 | 0.066751 | 0.013857 | 0.084382 | 0 | 0.021034 | 0 | 0.036092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.558 | 100% | US Weighted | 8.7793 | 2.2489 | 0.46686 | 8.4382 | 0 | 0.70868 | 0 | 1.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 24.3951 | 100% | US Weighted | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.20764 | 0 | 0.35629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6754 | 100% | US Weighted | 0 | 0 | 0 | 0.084382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084382 | 100% | US Weighted | 26.9299 | 6.8984 | 1.4321 | 9.223 | 0 | 2.1738 | 0 | 3.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 58.1695 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.26058 | 0.066869 | 0.012662 | 0.010147 | 0 | 0.064966 | 0 | 0.046757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.53728 | 3.023% | CZ 1A | 8.7793 | 2.2529 | 0.42662 | 1.0147 | 0 | 2.1888 | 0 | 1.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.7749 | 3.023% | CZ 1A | 2.5723 | 0.66011 | 0.125 | 0 | 0 | 0.64133 | 0 | 0.46157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.2037 | 3.023% | CZ 1A | 0 | 0 | 0 | 0.010147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010147 | 3.023% | CZ 1A | 26.9299 | 6.9107 | 1.3086 | 1.1091 | 0 | 6.714 | 0 | 4.8321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 55.5869 | 3.023%
CZ 1B | 0.26058 | 0.066788 | 0.012668 | 0.017634 | 0 | 0.14619 | 0 | 0.14222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.72138 | 0% | CZ 1B | 8.7793 | 2.2502 | 0.4268 | 1.7634 | 0 | 4.9254 | 0 | 4.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.4738 | 0% | CZ 1B | 2.5723 | 0.65931 | 0.12505 | 0 | 0 | 1.4431 | 0 | 1.4039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 6.9471 | 0% | CZ 1B | 0 | 0 | 0 | 0.017634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017634 | 0% | CZ 1B | 26.9299 | 6.9023 | 1.3092 | 1.9274 | 0 | 15.1083 | 0 | 14.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 74.657 | 0%
CZ 2A | 0.26058 | 0.066734 | 0.013062 | 0.023657 | 0 | 0.046584 | 0 | 0.036133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.52205 | 18.37% | CZ 2A | 8.7793 | 2.2484 | 0.4401 | 2.3657 | 0 | 1.5695 | 0 | 1.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.1575 | 18.37% | CZ 2A | 2.5723 | 0.65878 | 0.12895 | 0 | 0 | 0.45986 | 0 | 0.35669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.92 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.023657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023657 | 18.37% | CZ 2A | 26.9299 | 6.8967 | 1.35 | 2.5857 | 0 | 4.8143 | 0 | 3.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 54.0931 | 18.37%
CZ 2B | 0.26058 | 0.066777 | 0.013079 | 0.017709 | 0 | 0.066064 | 0 | 0.10115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.60066 | 3.472% | CZ 2B | 8.7793 | 2.2498 | 0.44064 | 1.7709 | 0 | 2.2258 | 0 | 3.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.4115 | 3.472% | CZ 2B | 2.5723 | 0.65921 | 0.12911 | 0 | 0 | 0.65216 | 0 | 0.99849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.7547 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.017709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017709 | 3.472% | CZ 2B | 26.9299 | 6.9012 | 1.3516 | 1.9356 | 0 | 6.8275 | 0 | 10.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 62.1814 | 3.472%
CZ 3A | 0.26058 | 0.066842 | 0.013722 | 0.076805 | 0 | 0.020361 | 0 | 0.030602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.54422 | 16.13% | CZ 3A | 8.7793 | 2.252 | 0.46232 | 7.6805 | 0 | 0.68601 | 0 | 1.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.4283 | 16.13% | CZ 3A | 2.5723 | 0.65985 | 0.13546 | 0 | 0 | 0.201 | 0 | 0.30209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6141 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.076805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076805 | 16.13% | CZ 3A | 26.9299 | 6.9079 | 1.4181 | 8.3948 | 0 | 2.1043 | 0 | 3.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 56.7 | 16.13%
CZ 3B | 0.26058 | 0.066799 | 0.013544 | 0.039889 | 0 | 0.023595 | 0 | 0.044161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.52387 | 13.75% | CZ 3B | 8.7793 | 2.2506 | 0.45631 | 3.9889 | 0 | 0.79494 | 0 | 1.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.295 | 13.75% | CZ 3B | 2.5723 | 0.65942 | 0.1337 | 0 | 0 | 0.23292 | 0 | 0.43595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7777 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.039889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039889 | 13.75% | CZ 3B | 26.9299 | 6.9035 | 1.3997 | 4.3598 | 0 | 2.4384 | 0 | 4.5639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 54.3776 | 13.75%
CZ 3C | 0.26058 | 0.066799 | 0.013819 | 0.03344 | 0 | 0.0014382 | 0 | 0.011197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.46258 | 0.9199% | CZ 3C | 8.7793 | 2.2506 | 0.4656 | 3.344 | 0 | 0.048454 | 0 | 0.37725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.8023 | 0.9199% | CZ 3C | 2.5723 | 0.65942 | 0.13642 | 0 | 0 | 0.014197 | 0 | 0.11053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2363 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.03344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03344 | 0.9199% | CZ 3C | 26.9299 | 6.9035 | 1.4282 | 3.655 | 0 | 0.14863 | 0 | 1.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 48.0047 | 0.9199%
CZ 4A | 0.26058 | 0.066723 | 0.014225 | 0.15206 | 0 | 0.0094833 | 0 | 0.031575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.60995 | 16.99% | CZ 4A | 8.7793 | 2.248 | 0.47926 | 15.2059 | 0 | 0.31951 | 0 | 1.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 30.6329 | 16.99% | CZ 4A | 2.5723 | 0.65867 | 0.14042 | 0 | 0 | 0.093616 | 0 | 0.3117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5201 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.15206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15206 | 16.99% | CZ 4A | 26.9299 | 6.8956 | 1.4701 | 16.62 | 0 | 0.98006 | 0 | 3.2631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 63.9412 | 16.99%
CZ 4B | 0.26058 | 0.066745 | 0.014084 | 0.078031 | 0 | 0.010094 | 0 | 0.03384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.53868 | 0.4596% | CZ 4B | 8.7793 | 2.2488 | 0.47452 | 7.8031 | 0 | 0.34009 | 0 | 1.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.323 | 0.4596% | CZ 4B | 2.5723 | 0.65888 | 0.13904 | 0 | 0 | 0.099647 | 0 | 0.33406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5473 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.078031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078031 | 0.4596% | CZ 4B | 26.9299 | 6.8979 | 1.4556 | 8.5288 | 0 | 1.0432 | 0 | 3.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 56.1349 | 0.4596%
CZ 4C | 0.26058 | 0.066669 | 0.014409 | 0.091298 | 0 | 0.00032981 | 0 | 0.019594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.52818 | 2.588% | CZ 4C | 8.7793 | 2.2462 | 0.48545 | 9.1298 | 0 | 0.011112 | 0 | 0.66014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.8492 | 2.588% | CZ 4C | 2.5723 | 0.65814 | 0.14224 | 0 | 0 | 0.0032557 | 0 | 0.19342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3128 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.091298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091298 | 2.588% | CZ 4C | 26.9299 | 6.89 | 1.4891 | 9.9789 | 0 | 0.034084 | 0 | 2.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 55.1293 | 2.588%
CZ 5A | 0.26058 | 0.066669 | 0.014657 | 0.22629 | 0 | 0.0019518 | 0 | 0.031067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.67651 | 17.98% | CZ 5A | 8.7793 | 2.2462 | 0.49383 | 22.6285 | 0 | 0.065759 | 0 | 1.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 37.7974 | 17.98% | CZ 5A | 2.5723 | 0.65814 | 0.14469 | 0 | 0 | 0.019268 | 0 | 0.30668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4445 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.22629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22629 | 17.98% | CZ 5A | 26.9299 | 6.89 | 1.5148 | 24.733 | 0 | 0.20171 | 0 | 3.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 71.2624 | 17.98%
CZ 5B | 0.26058 | 0.066723 | 0.014533 | 0.13944 | 0 | 0.0043253 | 0 | 0.02965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.59056 | 4.178% | CZ 5B | 8.7793 | 2.248 | 0.48964 | 13.9442 | 0 | 0.14573 | 0 | 0.99896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 29.143 | 4.178% | CZ 5B | 2.5723 | 0.65867 | 0.14347 | 0 | 0 | 0.042698 | 0 | 0.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4533 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.13944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13944 | 4.178% | CZ 5B | 26.9299 | 6.8956 | 1.5019 | 15.241 | 0 | 0.44701 | 0 | 3.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 61.8621 | 4.178%
CZ 5C | 0.26058 | 0.066648 | 0.014652 | 0.11084 | 0 | 8.6506e-05 | 0 | 0.016366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.54448 | 0.01929% | CZ 5C | 8.7793 | 2.2455 | 0.49365 | 11.0841 | 0 | 0.0029145 | 0 | 0.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.6939 | 0.01929% | CZ 5C | 2.5723 | 0.65792 | 0.14464 | 0 | 0 | 0.00085396 | 0 | 0.16156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2807 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.11084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11084 | 0.01929% | CZ 5C | 26.9299 | 6.8878 | 1.5142 | 12.1149 | 0 | 0.0089401 | 0 | 1.6914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 56.9295 | 0.01929%
CZ 6A | 0.26058 | 0.066718 | 0.014966 | 0.34737 | 0 | 0.0020599 | 0 | 0.042139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.80913 | 1.74% | CZ 6A | 8.7793 | 2.2478 | 0.50422 | 34.7366 | 0 | 0.069403 | 0 | 1.4197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 50.2943 | 1.74% | CZ 6A | 2.5723 | 0.65862 | 0.14774 | 0 | 0 | 0.020335 | 0 | 0.41599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5584 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.34737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34737 | 1.74% | CZ 6A | 26.9299 | 6.8951 | 1.5466 | 37.9671 | 0 | 0.21289 | 0 | 4.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 85.6889 | 1.74%
CZ 6B | 0.26058 | 0.066664 | 0.01489 | 0.23444 | 0 | 0.0012057 | 0 | 0.033948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.68703 | 0.1795% | CZ 6B | 8.7793 | 2.246 | 0.50167 | 23.4437 | 0 | 0.040621 | 0 | 1.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 38.6922 | 0.1795% | CZ 6B | 2.5723 | 0.65808 | 0.14699 | 0 | 0 | 0.011902 | 0 | 0.33513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4678 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.23444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23444 | 0.1795% | CZ 6B | 26.9299 | 6.8895 | 1.5388 | 25.6239 | 0 | 0.1246 | 0 | 3.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 72.3975 | 0.1795%
CZ 7 | 0.26058 | 0.066696 | 0.015333 | 0.32396 | 0 | 0.00067583 | 0 | 0.031434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.77398 | 0.1907% | CZ 7 | 8.7793 | 2.2471 | 0.5166 | 32.3962 | 0 | 0.02277 | 0 | 1.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 47.5583 | 0.1907% | CZ 7 | 2.5723 | 0.6584 | 0.15136 | 0 | 0 | 0.0066716 | 0 | 0.31031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4425 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.32396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32396 | 0.1907% | CZ 7 | 26.9299 | 6.8928 | 1.5846 | 35.4091 | 0 | 0.069845 | 0 | 3.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 81.9173 | 0.1907%
CZ 8 | 0.26058 | 0.066231 | 0.015836 | 0.33568 | 0 | 8.11e-05 | 0 | 0.023978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.77769 | 0.009711% | CZ 8 | 8.7793 | 2.2314 | 0.53354 | 33.5678 | 0 | 0.0027324 | 0 | 0.80788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 48.4598 | 0.009711% | CZ 8 | 2.5723 | 0.65381 | 0.15633 | 0 | 0 | 0.00080059 | 0 | 0.23671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3634 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.33568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33568 | 0.009711% | CZ 8 | 26.9299 | 6.8448 | 1.6366 | 36.6896 | 0 | 0.0083814 | 0 | 2.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 82.3697 | 0.009711%
US Weighted | 0.26058 | 0.066751 | 0.013857 | 0.10565 | 0 | 0.021594 | 0 | 0.036386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075304 | 0.58013 | 100% | US Weighted | 8.7793 | 2.2489 | 0.46687 | 10.5655 | 0 | 0.72755 | 0 | 1.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 26.5512 | 100% | US Weighted | 2.5723 | 0.65894 | 0.13679 | 0 | 0 | 0.21317 | 0 | 0.35919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6838 | 100% | US Weighted | 0 | 0 | 0 | 0.10565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10565 | 100% | US Weighted | 26.9299 | 6.8984 | 1.4321 | 11.5481 | 0 | 2.2317 | 0 | 3.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7824 | 60.5829 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Warehouse |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 52045 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 52045 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.16399 | 0.03617 | 0.00041091 | 0.010087 | 0 | 0.037549 | 0 | 0.03065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.28036 | 3.023% | CZ 1A | 5.5251 | 1.2186 | 0.013844 | 1.0087 | 0 | 1.2651 | 0 | 1.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.1147 | 3.023% | CZ 1A | 1.6188 | 0.35706 | 0.0040563 | 0 | 0 | 0.37067 | 0 | 0.30257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.668 | 3.023% | CZ 1A | 0 | 0 | 0 | 0.010087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010087 | 3.023% | CZ 1A | 16.9477 | 3.7381 | 0.042466 | 1.1025 | 0 | 3.8806 | 0 | 3.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 29.0343 | 3.023%
CZ 1B | 0.16583 | 0.036133 | 0.00040009 | 0.012876 | 0 | 0.056591 | 0 | 0.089134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.36247 | 0% | CZ 1B | 5.5872 | 1.2174 | 0.01348 | 1.2876 | 0 | 1.9067 | 0 | 3.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 13.066 | 0% | CZ 1B | 1.637 | 0.35669 | 0.0039496 | 0 | 0 | 0.55865 | 0 | 0.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 3.4511 | 0% | CZ 1B | 0 | 0 | 0 | 0.012876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012876 | 0% | CZ 1B | 17.1382 | 3.7342 | 0.041348 | 1.4073 | 0 | 5.8485 | 0 | 9.2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 37.5366 | 0%
CZ 2A | 0.16277 | 0.036106 | 0.00042713 | 0.018732 | 0 | 0.022492 | 0 | 0.017761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.25979 | 18.37% | CZ 2A | 5.4839 | 1.2165 | 0.014391 | 1.8732 | 0 | 0.75778 | 0 | 0.59839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.9948 | 18.37% | CZ 2A | 1.6068 | 0.35642 | 0.0042164 | 0 | 0 | 0.22203 | 0 | 0.17533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.3796 | 18.37% | CZ 2A | 0 | 0 | 0 | 0.018732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018732 | 18.37% | CZ 2A | 16.8214 | 3.7314 | 0.044142 | 2.0474 | 0 | 2.3244 | 0 | 1.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 26.9597 | 18.37%
CZ 2B | 0.15612 | 0.036122 | 0.00041631 | 0.0060189 | 0 | 0.028639 | 0 | 0.066583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.2954 | 3.472% | CZ 2B | 5.26 | 1.217 | 0.014026 | 0.60189 | 0 | 0.9649 | 0 | 2.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.3518 | 3.472% | CZ 2B | 1.5412 | 0.35658 | 0.0041097 | 0 | 0 | 0.28271 | 0 | 0.65728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.8567 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.0060189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060189 | 3.472% | CZ 2B | 16.1347 | 3.7331 | 0.043024 | 0.65787 | 0 | 2.9597 | 0 | 6.8811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 30.5648 | 3.472%
CZ 3A | 0.16056 | 0.036111 | 0.00044334 | 0.033398 | 0 | 0.011495 | 0 | 0.016193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.2597 | 16.13% | CZ 3A | 5.4094 | 1.2166 | 0.014937 | 3.3398 | 0 | 0.38727 | 0 | 0.54557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.9643 | 16.13% | CZ 3A | 1.585 | 0.35648 | 0.0043766 | 0 | 0 | 0.11347 | 0 | 0.15985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.234 | 16.13% | CZ 3A | 0 | 0 | 0 | 0.033398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033398 | 16.13% | CZ 3A | 16.5929 | 3.7319 | 0.045818 | 3.6504 | 0 | 1.1879 | 0 | 1.6735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 27.0378 | 16.13%
CZ 3B | 0.15838 | 0.036149 | 0.00043253 | 0.013212 | 0 | 0.010629 | 0 | 0.02141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.24171 | 13.75% | CZ 3B | 5.336 | 1.2179 | 0.014573 | 1.3212 | 0 | 0.35812 | 0 | 0.72135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.0198 | 13.75% | CZ 3B | 1.5634 | 0.35685 | 0.0042698 | 0 | 0 | 0.10493 | 0 | 0.21136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2557 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.013212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013212 | 13.75% | CZ 3B | 16.3677 | 3.7359 | 0.044701 | 1.4441 | 0 | 1.0985 | 0 | 2.2127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 25.0589 | 13.75%
CZ 3C | 0.15997 | 0.03603 | 0.00044875 | 0.010056 | 0 | 0.00094616 | 0 | 0.003709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.21267 | 0.9199% | CZ 3C | 5.3897 | 1.2139 | 0.015119 | 1.0056 | 0 | 0.031878 | 0 | 0.12496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 7.8319 | 0.9199% | CZ 3C | 1.5792 | 0.35568 | 0.0044299 | 0 | 0 | 0.0093402 | 0 | 0.036614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.0001 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.010056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010056 | 0.9199% | CZ 3C | 16.5325 | 3.7236 | 0.046377 | 1.0992 | 0 | 0.097783 | 0 | 0.38331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 22.0381 | 0.9199%
CZ 4A | 0.16718 | 0.035879 | 0.00044875 | 0.060342 | 0 | 0.0061041 | 0 | 0.018096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.28956 | 16.99% | CZ 4A | 5.6327 | 1.2088 | 0.015119 | 6.0342 | 0 | 0.20566 | 0 | 0.60969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 13.7568 | 16.99% | CZ 4A | 1.6504 | 0.35418 | 0.0044299 | 0 | 0 | 0.060258 | 0 | 0.17864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2627 | 16.99% | CZ 4A | 0 | 0 | 0 | 0.060342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060342 | 16.99% | CZ 4A | 17.2779 | 3.7079 | 0.046377 | 6.5954 | 0 | 0.63084 | 0 | 1.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 30.2839 | 16.99%
CZ 4B | 0.16638 | 0.036073 | 0.00044875 | 0.031502 | 0 | 0.006223 | 0 | 0.014441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.25658 | 0.4596% | CZ 4B | 5.6058 | 1.2154 | 0.015119 | 3.1502 | 0 | 0.20967 | 0 | 0.48655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.7333 | 0.4596% | CZ 4B | 1.6425 | 0.3561 | 0.0044299 | 0 | 0 | 0.061432 | 0 | 0.14256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2218 | 0.4596% | CZ 4B | 0 | 0 | 0 | 0.031502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031502 | 0.4596% | CZ 4B | 17.1952 | 3.728 | 0.046377 | 3.4432 | 0 | 0.64313 | 0 | 1.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 26.7037 | 0.4596%
CZ 4C | 0.16386 | 0.035749 | 0.00046497 | 0.026877 | 0 | 0.00020005 | 0 | 0.0056608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.23431 | 2.588% | CZ 4C | 5.5207 | 1.2044 | 0.015666 | 2.6877 | 0 | 0.0067399 | 0 | 0.19072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.6765 | 2.588% | CZ 4C | 1.6176 | 0.3529 | 0.00459 | 0 | 0 | 0.0019748 | 0 | 0.055881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.0477 | 2.588% | CZ 4C | 0 | 0 | 0 | 0.026877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026877 | 2.588% | CZ 4C | 16.9343 | 3.6945 | 0.048053 | 2.9376 | 0 | 0.020674 | 0 | 0.58502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 24.3755 | 2.588%
CZ 5A | 0.1577 | 0.035922 | 0.00045956 | 0.075953 | 0 | 0.0013408 | 0 | 0.018156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.29103 | 17.98% | CZ 5A | 5.3132 | 1.2103 | 0.015484 | 7.5953 | 0 | 0.045175 | 0 | 0.61169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 14.8418 | 17.98% | CZ 5A | 1.5568 | 0.35461 | 0.0045367 | 0 | 0 | 0.013236 | 0 | 0.17923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.1232 | 17.98% | CZ 5A | 0 | 0 | 0 | 0.075953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075953 | 17.98% | CZ 5A | 16.2979 | 3.7124 | 0.047494 | 8.3016 | 0 | 0.13857 | 0 | 1.8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 30.5296 | 17.98%
CZ 5B | 0.1557 | 0.035933 | 0.00045416 | 0.053407 | 0 | 0.0030277 | 0 | 0.01024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.26026 | 4.178% | CZ 5B | 5.2456 | 1.2106 | 0.015301 | 5.3407 | 0 | 0.10201 | 0 | 0.34501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.3099 | 4.178% | CZ 5B | 1.537 | 0.35471 | 0.0044833 | 0 | 0 | 0.029889 | 0 | 0.10109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.042 | 4.178% | CZ 5B | 0 | 0 | 0 | 0.053407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053407 | 4.178% | CZ 5B | 16.0906 | 3.7135 | 0.046936 | 5.8374 | 0 | 0.3129 | 0 | 1.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 27.2149 | 4.178%
CZ 5C | 0.1549 | 0.035743 | 0.00047038 | 0.037015 | 0 | -3.244e-05 | 0 | 0.0038495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.23345 | 0.01929% | CZ 5C | 5.2189 | 1.2043 | 0.015848 | 3.7015 | 0 | -0.001093 | 0 | 0.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.3197 | 0.01929% | CZ 5C | 1.5291 | 0.35285 | 0.0046434 | 0 | 0 | -0.00032024 | 0 | 0.038001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 1.9391 | 0.01929% | CZ 5C | 0 | 0 | 0 | 0.037015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037015 | 0.01929% | CZ 5C | 16.0084 | 3.6939 | 0.048612 | 4.0457 | 0 | -0.0033525 | 0 | 0.39784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 24.3465 | 0.01929%
CZ 6A | 0.13451 | 0.035895 | 0.00046497 | 0.11845 | 0 | 0.0014598 | 0 | 0.025514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.3178 | 1.74% | CZ 6A | 4.5319 | 1.2094 | 0.015666 | 11.8451 | 0 | 0.049183 | 0 | 0.85961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 18.5615 | 1.74% | CZ 6A | 1.3279 | 0.35434 | 0.00459 | 0 | 0 | 0.014411 | 0 | 0.25187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 1.9679 | 1.74% | CZ 6A | 0 | 0 | 0 | 0.11845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11845 | 1.74% | CZ 6A | 13.9013 | 3.7096 | 0.048053 | 12.9467 | 0 | 0.15086 | 0 | 2.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 33.5487 | 1.74%
CZ 6B | 0.1341 | 0.035846 | 0.00045956 | 0.091032 | 0 | 0.0008921 | 0 | 0.020053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.28388 | 0.1795% | CZ 6B | 4.5179 | 1.2077 | 0.015484 | 9.1032 | 0 | 0.030056 | 0 | 0.67563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 15.6006 | 0.1795% | CZ 6B | 1.3237 | 0.35386 | 0.0045367 | 0 | 0 | 0.0088065 | 0 | 0.19796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 1.9037 | 0.1795% | CZ 6B | 0 | 0 | 0 | 0.091032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091032 | 0.1795% | CZ 6B | 13.8583 | 3.7046 | 0.047494 | 9.9498 | 0 | 0.092195 | 0 | 2.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 29.8801 | 0.1795%
CZ 7 | 0.13423 | 0.035749 | 0.00046497 | 0.093891 | 0 | 0.00047038 | 0 | 0.016934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.28324 | 0.1907% | CZ 7 | 4.5225 | 1.2044 | 0.015666 | 9.3891 | 0 | 0.015848 | 0 | 0.57052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 15.7687 | 0.1907% | CZ 7 | 1.3251 | 0.3529 | 0.00459 | 0 | 0 | 0.0046434 | 0 | 0.16716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 1.8692 | 0.1907% | CZ 7 | 0 | 0 | 0 | 0.093891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093891 | 0.1907% | CZ 7 | 13.8723 | 3.6945 | 0.048053 | 10.2623 | 0 | 0.048612 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 29.8311 | 0.1907%
CZ 8 | 0.1323 | 0.034516 | 0.00047578 | 0.10873 | 0 | -3.7847e-05 | 0 | 0.0065745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.28406 | 0.009711% | CZ 8 | 4.4574 | 1.1629 | 0.01603 | 10.8728 | 0 | -0.0012751 | 0 | 0.22151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 16.78 | 0.009711% | CZ 8 | 1.306 | 0.34073 | 0.0046968 | 0 | 0 | -0.00037361 | 0 | 0.064901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 1.7308 | 0.009711% | CZ 8 | 0 | 0 | 0 | 0.10873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10873 | 0.009711% | CZ 8 | 13.6728 | 3.5671 | 0.049171 | 11.884 | 0 | -0.0039113 | 0 | 0.67945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 30.0039 | 0.009711%
US Weighted | 0.16057 | 0.036021 | 0.00044234 | 0.040653 | 0 | 0.011052 | 0 | 0.019584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001503 | 0.26983 | 100% | US Weighted | 5.41 | 1.2136 | 0.014903 | 4.0653 | 0 | 0.37236 | 0 | 0.65983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.7867 | 100% | US Weighted | 1.5851 | 0.35559 | 0.0043666 | 0 | 0 | 0.1091 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014838 | 2.2624 | 100% | US Weighted | 0 | 0 | 0 | 0.040653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040653 | 100% | US Weighted | 16.5948 | 3.7226 | 0.045714 | 4.4434 | 0 | 1.1422 | 0 | 2.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 28.1281 | 100%
Building Type: | Warehouse |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 52045 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 52045 | [17 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 62.93% | 54.09% | 3.245% | 99.41% | 0% | 57.8% | 0% | 65.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 52.18% | 3.023% | CZ 1A | 62.93% | 54.09% | 3.245% | 99.41% | 0% | 57.8% | 0% | 65.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 53.87% | 3.023% | CZ 1A | 62.93% | 54.09% | 3.245% | 0% | 0% | 57.8% | 0% | 65.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 51.27% | 3.023% | CZ 1A | 0% | 0% | 0% | 99.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 99.41% | 3.023% | CZ 1A | 62.93% | 54.09% | 3.245% | 99.41% | 0% | 57.8% | 0% | 65.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 52.23% | 3.023%
CZ 1B | 63.64% | 54.1% | 3.158% | 73.01% | 0% | 38.71% | 0% | 62.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 50.25% | 0% | CZ 1B | 63.64% | 54.1% | 3.158% | 73.01% | 0% | 38.71% | 0% | 62.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 51.29% | 0% | CZ 1B | 63.64% | 54.1% | 3.158% | 0% | 0% | 38.71% | 0% | 62.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.68% | 0% | CZ 1B | 0% | 0% | 0% | 73.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 73.01% | 0% | CZ 1B | 63.64% | 54.1% | 3.158% | 73.01% | 0% | 38.71% | 0% | 62.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 50.28% | 0%
CZ 2A | 62.46% | 54.1% | 3.27% | 79.18% | 0% | 48.28% | 0% | 49.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.76% | 18.37% | CZ 2A | 62.46% | 54.1% | 3.27% | 79.18% | 0% | 48.28% | 0% | 49.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 52.17% | 18.37% | CZ 2A | 62.46% | 54.1% | 3.27% | 0% | 0% | 48.28% | 0% | 49.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.37% | 18.37% | CZ 2A | 0% | 0% | 0% | 79.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.18% | 18.37% | CZ 2A | 62.46% | 54.1% | 3.27% | 79.18% | 0% | 48.28% | 0% | 49.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.84% | 18.37%
CZ 2B | 59.91% | 54.09% | 3.183% | 33.99% | 0% | 43.35% | 0% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.18% | 3.472% | CZ 2B | 59.91% | 54.09% | 3.183% | 33.99% | 0% | 43.35% | 0% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.35% | 3.472% | CZ 2B | 59.91% | 54.09% | 3.183% | 0% | 0% | 43.35% | 0% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.64% | 3.472% | CZ 2B | 0% | 0% | 0% | 33.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.99% | 3.472% | CZ 2B | 59.91% | 54.09% | 3.183% | 33.99% | 0% | 43.35% | 0% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 49.15% | 3.472%
CZ 3A | 61.62% | 54.02% | 3.231% | 43.48% | 0% | 56.45% | 0% | 52.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.72% | 16.13% | CZ 3A | 61.62% | 54.02% | 3.231% | 43.48% | 0% | 56.45% | 0% | 52.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.8% | 16.13% | CZ 3A | 61.62% | 54.02% | 3.231% | 0% | 0% | 56.45% | 0% | 52.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.42% | 16.13% | CZ 3A | 0% | 0% | 0% | 43.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.48% | 16.13% | CZ 3A | 61.62% | 54.02% | 3.231% | 43.48% | 0% | 56.45% | 0% | 52.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.69% | 16.13%
CZ 3B | 60.78% | 54.12% | 3.194% | 33.12% | 0% | 45.05% | 0% | 48.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.14% | 13.75% | CZ 3B | 60.78% | 54.12% | 3.194% | 33.12% | 0% | 45.05% | 0% | 48.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.44% | 13.75% | CZ 3B | 60.78% | 54.12% | 3.194% | 0% | 0% | 45.05% | 0% | 48.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.21% | 13.75% | CZ 3B | 0% | 0% | 0% | 33.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.12% | 13.75% | CZ 3B | 60.78% | 54.12% | 3.194% | 33.12% | 0% | 45.05% | 0% | 48.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.08% | 13.75%
CZ 3C | 61.39% | 53.94% | 3.247% | 30.07% | 0% | 65.79% | 0% | 33.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 45.97% | 0.9199% | CZ 3C | 61.39% | 53.94% | 3.247% | 30.07% | 0% | 65.79% | 0% | 33.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 43.99% | 0.9199% | CZ 3C | 61.39% | 53.94% | 3.247% | 0% | 0% | 65.79% | 0% | 33.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.21% | 0.9199% | CZ 3C | 0% | 0% | 0% | 30.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.07% | 0.9199% | CZ 3C | 61.39% | 53.94% | 3.247% | 30.07% | 0% | 65.79% | 0% | 33.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 45.91% | 0.9199%
CZ 4A | 64.16% | 53.77% | 3.155% | 39.68% | 0% | 64.37% | 0% | 57.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.47% | 16.99% | CZ 4A | 64.16% | 53.77% | 3.155% | 39.68% | 0% | 64.37% | 0% | 57.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.91% | 16.99% | CZ 4A | 64.16% | 53.77% | 3.155% | 0% | 0% | 64.37% | 0% | 57.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 50.06% | 16.99% | CZ 4A | 0% | 0% | 0% | 39.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.68% | 16.99% | CZ 4A | 64.16% | 53.77% | 3.155% | 39.68% | 0% | 64.37% | 0% | 57.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.36% | 16.99%
CZ 4B | 63.85% | 54.05% | 3.186% | 40.37% | 0% | 61.65% | 0% | 42.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.63% | 0.4596% | CZ 4B | 63.85% | 54.05% | 3.186% | 40.37% | 0% | 61.65% | 0% | 42.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.02% | 0.4596% | CZ 4B | 63.85% | 54.05% | 3.186% | 0% | 0% | 61.65% | 0% | 42.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.86% | 0.4596% | CZ 4B | 0% | 0% | 0% | 40.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.37% | 0.4596% | CZ 4B | 63.85% | 54.05% | 3.186% | 40.37% | 0% | 61.65% | 0% | 42.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.57% | 0.4596%
CZ 4C | 62.88% | 53.62% | 3.227% | 29.44% | 0% | 60.66% | 0% | 28.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.36% | 2.588% | CZ 4C | 62.88% | 53.62% | 3.227% | 29.44% | 0% | 60.66% | 0% | 28.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 40.57% | 2.588% | CZ 4C | 62.88% | 53.62% | 3.227% | 0% | 0% | 60.66% | 0% | 28.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.48% | 2.588% | CZ 4C | 0% | 0% | 0% | 29.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.44% | 2.588% | CZ 4C | 62.88% | 53.62% | 3.227% | 29.44% | 0% | 60.66% | 0% | 28.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.22% | 2.588%
CZ 5A | 60.52% | 53.88% | 3.135% | 33.57% | 0% | 68.7% | 0% | 58.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 43.02% | 17.98% | CZ 5A | 60.52% | 53.88% | 3.135% | 33.57% | 0% | 68.7% | 0% | 58.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 39.27% | 17.98% | CZ 5A | 60.52% | 53.88% | 3.135% | 0% | 0% | 68.7% | 0% | 58.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 47.77% | 17.98% | CZ 5A | 0% | 0% | 0% | 33.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.57% | 17.98% | CZ 5A | 60.52% | 53.88% | 3.135% | 33.57% | 0% | 68.7% | 0% | 58.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.84% | 17.98%
CZ 5B | 59.75% | 53.85% | 3.125% | 38.3% | 0% | 70% | 0% | 34.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.07% | 4.178% | CZ 5B | 59.75% | 53.85% | 3.125% | 38.3% | 0% | 70% | 0% | 34.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.24% | 4.178% | CZ 5B | 59.75% | 53.85% | 3.125% | 0% | 0% | 70% | 0% | 34.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 45.85% | 4.178% | CZ 5B | 0% | 0% | 0% | 38.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.3% | 4.178% | CZ 5B | 59.75% | 53.85% | 3.125% | 38.3% | 0% | 70% | 0% | 34.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 43.99% | 4.178%
CZ 5C | 59.44% | 53.63% | 3.21% | 33.39% | 0% | -37.5% | 0% | 23.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.88% | 0.01929% | CZ 5C | 59.44% | 53.63% | 3.21% | 33.39% | 0% | -37.5% | 0% | 23.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 40.16% | 0.01929% | CZ 5C | 59.44% | 53.63% | 3.21% | 0% | 0% | -37.5% | 0% | 23.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 45.3% | 0.01929% | CZ 5C | 0% | 0% | 0% | 33.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.39% | 0.01929% | CZ 5C | 59.44% | 53.63% | 3.21% | 33.39% | 0% | -37.5% | 0% | 23.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.77% | 0.01929%
CZ 6A | 51.62% | 53.8% | 3.107% | 34.1% | 0% | 70.87% | 0% | 60.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 39.28% | 1.74% | CZ 6A | 51.62% | 53.8% | 3.107% | 34.1% | 0% | 70.87% | 0% | 60.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.91% | 1.74% | CZ 6A | 51.62% | 53.8% | 3.107% | 0% | 0% | 70.87% | 0% | 60.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 43.17% | 1.74% | CZ 6A | 0% | 0% | 0% | 34.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.1% | 1.74% | CZ 6A | 51.62% | 53.8% | 3.107% | 34.1% | 0% | 70.87% | 0% | 60.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 39.15% | 1.74%
CZ 6B | 51.46% | 53.77% | 3.086% | 38.83% | 0% | 73.99% | 0% | 59.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 41.32% | 0.1795% | CZ 6B | 51.46% | 53.77% | 3.086% | 38.83% | 0% | 73.99% | 0% | 59.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 40.32% | 0.1795% | CZ 6B | 51.46% | 53.77% | 3.086% | 0% | 0% | 73.99% | 0% | 59.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.61% | 0.1795% | CZ 6B | 0% | 0% | 0% | 38.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.83% | 0.1795% | CZ 6B | 51.46% | 53.77% | 3.086% | 38.83% | 0% | 73.99% | 0% | 59.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 41.27% | 0.1795%
CZ 7 | 51.51% | 53.6% | 3.032% | 28.98% | 0% | 69.6% | 0% | 53.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.6% | 0.1907% | CZ 7 | 51.51% | 53.6% | 3.032% | 28.98% | 0% | 69.6% | 0% | 53.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 33.16% | 0.1907% | CZ 7 | 51.51% | 53.6% | 3.032% | 0% | 0% | 69.6% | 0% | 53.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 42.08% | 0.1907% | CZ 7 | 0% | 0% | 0% | 28.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.98% | 0.1907% | CZ 7 | 51.51% | 53.6% | 3.032% | 28.98% | 0% | 69.6% | 0% | 53.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.42% | 0.1907%
CZ 8 | 50.77% | 52.11% | 3.004% | 32.39% | 0% | -46.67% | 0% | 27.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.53% | 0.009711% | CZ 8 | 50.77% | 52.11% | 3.004% | 32.39% | 0% | -46.67% | 0% | 27.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 34.63% | 0.009711% | CZ 8 | 50.77% | 52.11% | 3.004% | 0% | 0% | -46.67% | 0% | 27.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 39.67% | 0.009711% | CZ 8 | 0% | 0% | 0% | 32.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.39% | 0.009711% | CZ 8 | 50.77% | 52.11% | 3.004% | 32.39% | 0% | -46.67% | 0% | 27.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.43% | 0.009711%
US Weighted | 61.62% | 53.96% | 3.192% | 38.48% | 0% | 51.18% | 0% | 53.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.51% | 100% | US Weighted | 61.62% | 53.96% | 3.192% | 38.48% | 0% | 51.18% | 0% | 53.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 44.39% | 100% | US Weighted | 61.62% | 53.96% | 3.192% | 0% | 0% | 51.18% | 0% | 53.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.3% | 100% | US Weighted | 0% | 0% | 0% | 38.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.48% | 100% | US Weighted | 61.62% | 53.96% | 3.192% | 38.48% | 0% | 51.18% | 0% | 53.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.43% | 100%

## RestQS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Quick-service Restaurant | [14 empty] | Prototype Floor Area: | 2501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.31021 | 0.098927 | 0.67183 | 1.323 | 0 | 0.74461 | 0 | 0.72968 | 0 | 0 | 0.96082 | 0 | 0 | 4.435 | 0 | 0 | 9.2741 |  | STD2016 | 10.4516 | 3.333 | 67.1828 | 132.3043 | 0 | 25.0871 | 0 | 24.5841 | 0 | 0 | 32.3716 | 0 | 0 | 269.3289 | 0 | 0 | 564.6434 |  | STD2016 | 3.0623 | 0.97657 | 0 | 0 | 0 | 7.3505 | 0 | 7.2032 | 0 | 0 | 9.4849 | 0 | 0 | 25.9296 | 0 | 0 | 54.0071 |  | STD2016 | 0 | 0 | 0.67183 | 1.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8032 |  | STD2016 | 32.0593 | 10.2237 | 73.4309 | 144.6086 | 0 | 76.9525 | 0 | 75.4098 | 0 | 0 | 99.2973 | 0 | 0 | 469.1065 | 0 | 0 | 981.0885
STD2013 | 0.36364 | 0.1728 | 0.67178 | 1.324 | 0 | 0.75235 | 0 | 0.73434 | 0 | 0 | 0.96114 | 0 | 0 | 4.435 | 0 | 0 | 9.4151 |  | STD2013 | 12.2515 | 5.8218 | 67.178 | 132.4045 | 0 | 25.3479 | 0 | 24.7413 | 0 | 0 | 32.3824 | 0 | 0 | 269.3289 | 0 | 0 | 569.4564 |  | STD2013 | 3.5897 | 1.7058 | 0 | 0 | 0 | 7.4269 | 0 | 7.2492 | 0 | 0 | 9.4881 | 0 | 0 | 25.9296 | 0 | 0 | 55.3893 |  | STD2013 | 0 | 0 | 0.67178 | 1.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8041 |  | STD2013 | 37.5806 | 17.858 | 73.4256 | 144.7182 | 0 | 77.7527 | 0 | 75.8918 | 0 | 0 | 99.3305 | 0 | 0 | 469.1065 | 0 | 0 | 995.6638
STD2010 | 0.39235 | 0.1728 | 0.67168 | 1.3206 | 0 | 0.82149 | 0 | 1.1817 | 0 | 0 | 1.2196 | 0 | 0 | 4.435 | 0 | 0 | 10.2152 |  | STD2010 | 13.2189 | 5.8218 | 67.1684 | 132.0622 | 0 | 27.6776 | 0 | 39.8148 | 0 | 0 | 41.089 | 0 | 0 | 269.3289 | 0 | 0 | 596.1816 |  | STD2010 | 3.8732 | 1.7058 | 0 | 0 | 0 | 8.1095 | 0 | 11.6657 | 0 | 0 | 12.0391 | 0 | 0 | 25.9296 | 0 | 0 | 63.3229 |  | STD2010 | 0 | 0 | 0.67168 | 1.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8006 |  | STD2010 | 40.548 | 17.858 | 73.4151 | 144.344 | 0 | 84.8986 | 0 | 122.1287 | 0 | 0 | 126.037 | 0 | 0 | 469.1065 | 0 | 0 | 1078.3358
STD2007 | 0.84473 | 0.30807 | 0.67168 | 1.2767 | 0 | 1.1315 | 0 | 1.4887 | 0 | 0 | 1.22 | 0 | 0 | 4.4383 | 0 | 0 | 11.3796 |  | STD2007 | 28.4604 | 10.3794 | 67.1684 | 127.6707 | 0 | 38.1207 | 0 | 50.1562 | 0 | 0 | 41.1029 | 0 | 0 | 269.4388 | 0 | 0 | 632.4975 |  | STD2007 | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.1694 | 0 | 14.6958 | 0 | 0 | 12.0432 | 0 | 0 | 25.9618 | 0 | 0 | 75.2502 |  | STD2007 | 0 | 0 | 0.67168 | 1.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.7567 |  | STD2007 | 87.2998 | 31.8381 | 73.4151 | 139.5441 | 0 | 116.9321 | 0 | 153.85 | 0 | 0 | 126.0798 | 0 | 0 | 469.4437 | 0 | 0 | 1198.4026
STD2004 | 0.84473 | 0.30807 | 0.67145 | 1.3603 | 0 | 1.1555 | 0 | 1.4612 | 0 | 0 | 1.2183 | 0 | 0 | 4.4383 | 0 | 0 | 11.4578 |  | STD2004 | 28.4604 | 10.3794 | 67.1449 | 136.0332 | 0 | 38.9292 | 0 | 49.2294 | 0 | 0 | 41.0466 | 0 | 0 | 269.4388 | 0 | 0 | 640.6619 |  | STD2004 | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.4063 | 0 | 14.4242 | 0 | 0 | 12.0267 | 0 | 0 | 25.9618 | 0 | 0 | 75.199 |  | STD2004 | 0 | 0 | 0.67145 | 1.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8401 |  | STD2004 | 87.2998 | 31.8381 | 73.3893 | 148.6843 | 0 | 119.4121 | 0 | 151.0071 | 0 | 0 | 125.9072 | 0 | 0 | 469.4437 | 0 | 0 | 1206.9815
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -0.00023532 | 0.083625 | 0 | 0.023996 | 0 | -0.027509 | 0 | 0 | -0.0016702 | 0 | 0 | 0 | 0 | 0 | 0.078207 |  | 2004-2007 | 0 | 0 | -0.023532 | 8.3625 | 0 | 0.80847 | 0 | -0.92681 | 0 | 0 | -0.056271 | 0 | 0 | 0 | 0 | 0 | 8.1643 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | 0.23688 | 0 | -0.27156 | 0 | 0 | -0.016488 | 0 | 0 | 0 | 0 | 0 | -0.05116 |  | 2004-2007 | 0 | 0 | -0.00023532 | 0.083625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083389 |  | 2004-2007 | 0 | 0 | -0.02572 | 9.1402 | 0 | 2.4799 | 0 | -2.8429 | 0 | 0 | -0.17261 | 0 | 0 | 0 | 0 | 0 | 8.5788
2007-2010 | 0.45238 | 0.13527 | 5.7517e-08 | -0.043915 | 0 | 0.30996 | 0 | 0.30694 | 0 | 0 | 0.00041382 | 0 | 0 | 0.0032628 | 0 | 0 | 1.1643 |  | 2007-2010 | 15.2414 | 4.5576 | 5.7517e-06 | -4.3915 | 0 | 10.4432 | 0 | 10.3414 | 0 | 0 | 0.013942 | 0 | 0 | 0.10993 | 0 | 0 | 36.316 |  | 2007-2010 | 4.4657 | 1.3354 | 0 | 0 | 0 | 3.0598 | 0 | 3.03 | 0 | 0 | 0.0040851 | 0 | 0 | 0.032209 | 0 | 0 | 11.9273 |  | 2007-2010 | 0 | 0 | 5.7517e-08 | -0.043915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.043914 |  | 2007-2010 | 46.7518 | 13.9801 | 6.2866e-06 | -4.7999 | 0 | 32.0335 | 0 | 31.7213 | 0 | 0 | 0.042767 | 0 | 0 | 0.3372 | 0 | 0 | 120.0668
2010-2013 | 0.028713 | 0 | -9.6129e-05 | -0.0034235 | 0 | 0.069145 | 0 | 0.4474 | 0 | 0 | 0.25842 | 0 | 0 | 0 | 0 | 0 | 0.80015 |  | 2010-2013 | 0.9674 | 0 | -0.0096129 | -0.34235 | 0 | 2.3296 | 0 | 15.0736 | 0 | 0 | 8.7065 | 0 | 0 | 0 | 0 | 0 | 26.7251 |  | 2010-2013 | 0.28345 | 0 | 0 | 0 | 0 | 0.68257 | 0 | 4.4166 | 0 | 0 | 2.551 | 0 | 0 | 0 | 0 | 0 | 7.9336 |  | 2010-2013 | 0 | 0 | -9.6129e-05 | -0.0034235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0035196 |  | 2010-2013 | 2.9674 | 0 | -0.010507 | -0.37419 | 0 | 7.1459 | 0 | 46.2369 | 0 | 0 | 26.7065 | 0 | 0 | 0 | 0 | 0 | 82.672
2013-2016 | 0.053425 | 0.073871 | -4.8354e-05 | 0.0010023 | 0 | 0.0077434 | 0 | 0.0046631 | 0 | 0 | 0.00032157 | 0 | 0 | 0 | 0 | 0 | 0.14098 |  | 2013-2016 | 1.8 | 2.4888 | -0.0048354 | 0.10023 | 0 | 0.26089 | 0 | 0.15711 | 0 | 0 | 0.010834 | 0 | 0 | 0 | 0 | 0 | 4.8131 |  | 2013-2016 | 0.5274 | 0.72923 | 0 | 0 | 0 | 0.076441 | 0 | 0.046032 | 0 | 0 | 0.0031744 | 0 | 0 | 0 | 0 | 0 | 1.3823 |  | 2013-2016 | 0 | 0 | -4.8354e-05 | 0.0010023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00095398 |  | 2013-2016 | 5.5213 | 7.6343 | -0.0052851 | 0.10956 | 0 | 0.80026 | 0 | 0.48191 | 0 | 0 | 0.033233 | 0 | 0 | 0 | 0 | 0 | 14.5753
2004-2016 | 0.53452 | 0.20914 | -0.00037974 | 0.037289 | 0 | 0.41085 | 0 | 0.73149 | 0 | 0 | 0.25748 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1837 |  | 2004-2016 | 18.0088 | 7.0464 | -0.037974 | 3.7289 | 0 | 13.8421 | 0 | 24.6452 | 0 | 0 | 8.675 | 0 | 0 | 0.10993 | 0 | 0 | 76.0185 |  | 2004-2016 | 5.2766 | 2.0646 | 0 | 0 | 0 | 4.0557 | 0 | 7.2211 | 0 | 0 | 2.5418 | 0 | 0 | 0.032209 | 0 | 0 | 21.192 |  | 2004-2016 | 0 | 0 | -0.00037974 | 0.037289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036909 |  | 2004-2016 | 55.2405 | 21.6144 | -0.041506 | 4.0757 | 0 | 42.4596 | 0 | 75.5972 | 0 | 0 | 26.6099 | 0 | 0 | 0.3372 | 0 | 0 | 225.893
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.03505% | 6.147% |  | 2.077% |  | -1.883% |  |  | -0.1371% |  |  | 0% |  |  | 0.6826% |  | 2004-2007 | 0% | 0% | -0.03505% | 6.147% |  | 2.077% |  | -1.883% |  |  | -0.1371% |  |  | 0% |  |  | 1.274% |  | 2004-2007 | 0% | 0% |  |  |  | 2.077% |  | -1.883% |  |  | -0.1371% |  |  | 0% |  |  | -0.06803% |  | 2004-2007 |  |  | -0.03505% | 6.147% | [9 empty] | 0% |  |  | 2.172% |  | 2004-2007 | 0% | 0% | -0.03505% | 6.147% |  | 2.077% |  | -1.883% |  |  | -0.1371% |  |  | 0% |  |  | 0.7108%
2007-2010 | 53.55% | 43.91% | 8.563e-06% | -3.44% |  | 27.39% |  | 20.62% |  |  | 0.03392% |  |  | 0.07352% |  |  | 10.23% |  | 2007-2010 | 53.55% | 43.91% | 8.563e-06% | -3.44% |  | 27.39% |  | 20.62% |  |  | 0.03392% |  |  | 0.0408% |  |  | 5.742% |  | 2007-2010 | 53.55% | 43.91% |  |  |  | 27.39% |  | 20.62% |  |  | 0.03392% |  |  | 0.1241% |  |  | 15.85% |  | 2007-2010 |  |  | 8.563e-06% | -3.44% | [9 empty] | 0% |  |  | -1.169% |  | 2007-2010 | 53.55% | 43.91% | 8.563e-06% | -3.44% |  | 27.39% |  | 20.62% |  |  | 0.03392% |  |  | 0.07183% |  |  | 10.02%
2010-2013 | 7.318% | 0% | -0.01431% | -0.2592% |  | 8.417% |  | 37.86% |  |  | 21.19% |  |  | 0% |  |  | 7.833% |  | 2010-2013 | 7.318% | 0% | -0.01431% | -0.2592% |  | 8.417% |  | 37.86% |  |  | 21.19% |  |  | 0% |  |  | 4.483% |  | 2010-2013 | 7.318% | 0% |  |  |  | 8.417% |  | 37.86% |  |  | 21.19% |  |  | 0% |  |  | 12.53% |  | 2010-2013 |  |  | -0.01431% | -0.2592% | [9 empty] | 0% |  |  | -0.09261% |  | 2010-2013 | 7.318% | 0% | -0.01431% | -0.2592% |  | 8.417% |  | 37.86% |  |  | 21.19% |  |  | 0% |  |  | 7.667%
2013-2016 | 14.69% | 42.75% | -0.007198% | 0.0757% |  | 1.029% |  | 0.635% |  |  | 0.03346% |  |  | 0% |  |  | 1.497% |  | 2013-2016 | 14.69% | 42.75% | -0.007198% | 0.0757% |  | 1.029% |  | 0.635% |  |  | 0.03346% |  |  | 0% |  |  | 0.8452% |  | 2013-2016 | 14.69% | 42.75% |  |  |  | 1.029% |  | 0.635% |  |  | 0.03346% |  |  | 0% |  |  | 2.496% |  | 2013-2016 |  |  | -0.007198% | 0.0757% | [9 empty] | 0% |  |  | 0.02508% |  | 2013-2016 | 14.69% | 42.75% | -0.007198% | 0.0757% |  | 1.029% |  | 0.635% |  |  | 0.03346% |  |  | 0% |  |  | 1.464%
2004-2016 | 63.28% | 67.89% | -0.05656% | 2.741% |  | 35.56% |  | 50.06% |  |  | 21.13% |  |  | 0.07352% |  |  | 19.06% |  | 2004-2016 | 63.28% | 67.89% | -0.05656% | 2.741% |  | 35.56% |  | 50.06% |  |  | 21.13% |  |  | 0.0408% |  |  | 11.87% |  | 2004-2016 | 63.28% | 67.89% |  |  |  | 35.56% |  | 50.06% |  |  | 21.13% |  |  | 0.1241% |  |  | 28.18% |  | 2004-2016 |  |  | -0.05656% | 2.741% | [9 empty] | 0% |  |  | 0.9611% |  | 2004-2016 | 63.28% | 67.89% | -0.05656% | 2.741% |  | 35.56% |  | 50.06% |  |  | 21.13% |  |  | 0.07183% |  |  | 18.72%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.30817 | 0.098897 | 0.51446 | 0.12612 | 0 | 1.7936 | 0 | 0.88951 | 0 | 0 | 0.99864 | 0 | 0 | 4.435 | 0 | 0 | 9.1644 | 3.013% | CZ 1A | 10.3826 | 3.332 | 51.4459 | 12.6123 | 0 | 60.4309 | 0 | 29.969 | 0 | 0 | 33.646 | 0 | 0 | 269.3289 | 0 | 0 | 471.1476 | 3.013% | CZ 1A | 3.0421 | 0.97628 | 0 | 0 | 0 | 17.7063 | 0 | 8.7809 | 0 | 0 | 9.8583 | 0 | 0 | 25.9296 | 0 | 0 | 66.2935 | 3.013% | CZ 1A | 0 | 0 | 0.51446 | 0.12612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4489 | 3.013% | CZ 1A | 31.8479 | 10.2206 | 56.2304 | 13.7852 | 0 | 185.3667 | 0 | 91.9276 | 0 | 0 | 103.2063 | 0 | 0 | 469.1065 | 0 | 0 | 961.6913 | 3.013%
CZ 1B | 0.30929 | 0.098672 | 0.51582 | 0.32058 | 0 | 2.2591 | 0 | 1.0692 | 0 | 0 | 0.99268 | 0 | 0 | 4.435 | 0 | 0 | 10.0003 | 0% | CZ 1B | 10.4206 | 3.3244 | 51.5823 | 32.0575 | 0 | 76.1129 | 0 | 36.0228 | 0 | 0 | 33.4451 | 0 | 0 | 269.3289 | 0 | 0 | 512.2944 | 0% | CZ 1B | 3.0532 | 0.97405 | 0 | 0 | 0 | 22.3011 | 0 | 10.5547 | 0 | 0 | 9.7994 | 0 | 0 | 25.9296 | 0 | 0 | 72.6121 | 0% | CZ 1B | 0 | 0 | 0.51582 | 0.32058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6447 | 0% | CZ 1B | 31.9642 | 10.1974 | 56.3795 | 35.0389 | 0 | 233.47 | 0 | 110.4968 | 0 | 0 | 102.5901 | 0 | 0 | 469.1065 | 0 | 0 | 1049.2433 | 0%
CZ 2A | 0.30772 | 0.098672 | 0.56289 | 0.44871 | 0 | 1.6118 | 0 | 0.85125 | 0 | 0 | 0.98717 | 0 | 0 | 4.435 | 0 | 0 | 9.3032 | 16.92% | CZ 2A | 10.3675 | 3.3244 | 56.2892 | 44.8707 | 0 | 54.3052 | 0 | 28.6802 | 0 | 0 | 33.2594 | 0 | 0 | 269.3289 | 0 | 0 | 500.4254 | 16.92% | CZ 2A | 3.0377 | 0.97405 | 0 | 0 | 0 | 15.9114 | 0 | 8.4033 | 0 | 0 | 9.745 | 0 | 0 | 25.9296 | 0 | 0 | 64.0011 | 16.92% | CZ 2A | 0 | 0 | 0.56289 | 0.44871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.8199 | 16.92% | CZ 2A | 31.8014 | 10.1974 | 61.5241 | 49.0436 | 0 | 166.5766 | 0 | 87.9742 | 0 | 0 | 102.0203 | 0 | 0 | 469.1065 | 0 | 0 | 978.2441 | 16.92%
CZ 2B | 0.30682 | 0.098784 | 0.56611 | 0.50104 | 0 | 1.1974 | 0 | 0.95893 | 0 | 0 | 0.974 | 0 | 0 | 4.435 | 0 | 0 | 9.0381 | 3.461% | CZ 2B | 10.3372 | 3.3282 | 56.6113 | 50.1043 | 0 | 40.3441 | 0 | 32.3079 | 0 | 0 | 32.8158 | 0 | 0 | 269.3289 | 0 | 0 | 495.1777 | 3.461% | CZ 2B | 3.0288 | 0.97517 | 0 | 0 | 0 | 11.8208 | 0 | 9.4662 | 0 | 0 | 9.615 | 0 | 0 | 25.9296 | 0 | 0 | 60.8357 | 3.461% | CZ 2B | 0 | 0 | 0.56611 | 0.50104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.8755 | 3.461% | CZ 2B | 31.7084 | 10.209 | 61.8762 | 54.764 | 0 | 123.7522 | 0 | 99.1018 | 0 | 0 | 100.6599 | 0 | 0 | 469.1065 | 0 | 0 | 951.178 | 3.461%
CZ 3A | 0.30963 | 0.098784 | 0.64577 | 1.0817 | 0 | 0.83134 | 0 | 0.7554 | 0 | 0 | 0.96557 | 0 | 0 | 4.435 | 0 | 0 | 9.1231 | 16.34% | CZ 3A | 10.4319 | 3.3282 | 64.5774 | 108.1671 | 0 | 28.0093 | 0 | 25.4506 | 0 | 0 | 32.5315 | 0 | 0 | 269.3289 | 0 | 0 | 541.8249 | 16.34% | CZ 3A | 3.0566 | 0.97517 | 0 | 0 | 0 | 8.2067 | 0 | 7.457 | 0 | 0 | 9.5317 | 0 | 0 | 25.9296 | 0 | 0 | 55.1568 | 16.34% | CZ 3A | 0 | 0 | 0.64577 | 1.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5358 | 16.34% | CZ 3A | 31.9991 | 10.209 | 70.5831 | 118.2267 | 0 | 85.9161 | 0 | 78.0675 | 0 | 0 | 99.7878 | 0 | 0 | 469.1065 | 0 | 0 | 963.8958 | 16.34%
CZ 3B | 0.30873 | 0.098784 | 0.62451 | 0.77546 | 0 | 0.79522 | 0 | 0.86161 | 0 | 0 | 0.96523 | 0 | 0 | 4.435 | 0 | 0 | 8.8645 | 10.77% | CZ 3B | 10.4016 | 3.3282 | 62.4513 | 77.5459 | 0 | 26.7925 | 0 | 29.029 | 0 | 0 | 32.5202 | 0 | 0 | 269.3289 | 0 | 0 | 511.3975 | 10.77% | CZ 3B | 3.0477 | 0.97517 | 0 | 0 | 0 | 7.8502 | 0 | 8.5055 | 0 | 0 | 9.5284 | 0 | 0 | 25.9296 | 0 | 0 | 55.8366 | 10.77% | CZ 3B | 0 | 0 | 0.62451 | 0.77546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2083 | 10.77% | CZ 3B | 31.9061 | 10.209 | 68.2593 | 84.7577 | 0 | 82.1837 | 0 | 89.0439 | 0 | 0 | 99.7529 | 0 | 0 | 469.1065 | 0 | 0 | 935.2191 | 10.77%
CZ 3C | 0.31042 | 0.099122 | 0.65487 | 0.78459 | 0 | 0.18474 | 0 | 0.59001 | 0 | 0 | 0.96804 | 0 | 0 | 4.435 | 0 | 0 | 8.0268 | 1.179% | CZ 3C | 10.4585 | 3.3396 | 65.4869 | 78.4592 | 0 | 6.2243 | 0 | 19.8783 | 0 | 0 | 32.6149 | 0 | 0 | 269.3289 | 0 | 0 | 485.7906 | 1.179% | CZ 3C | 3.0643 | 0.9785 | 0 | 0 | 0 | 1.8237 | 0 | 5.8243 | 0 | 0 | 9.5562 | 0 | 0 | 25.9296 | 0 | 0 | 47.1767 | 1.179% | CZ 3C | 0 | 0 | 0.65487 | 0.78459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2478 | 1.179% | CZ 3C | 32.0805 | 10.2439 | 71.5772 | 85.756 | 0 | 19.0925 | 0 | 60.975 | 0 | 0 | 100.0436 | 0 | 0 | 469.1065 | 0 | 0 | 848.8751 | 1.179%
CZ 4A | 0.31345 | 0.099347 | 0.71103 | 1.6242 | 0 | 0.47041 | 0 | 0.6394 | 0 | 0 | 0.95026 | 0 | 0 | 4.435 | 0 | 0 | 9.2431 | 15.63% | CZ 4A | 10.5608 | 3.3472 | 71.1033 | 162.4212 | 0 | 15.8488 | 0 | 21.5424 | 0 | 0 | 32.016 | 0 | 0 | 269.3289 | 0 | 0 | 586.1686 | 15.63% | CZ 4A | 3.0943 | 0.98072 | 0 | 0 | 0 | 4.6437 | 0 | 6.3119 | 0 | 0 | 9.3807 | 0 | 0 | 25.9296 | 0 | 0 | 50.341 | 15.63% | CZ 4A | 0 | 0 | 0.71103 | 1.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1436 | 15.63% | CZ 4A | 32.3944 | 10.2671 | 77.7159 | 177.5264 | 0 | 48.6149 | 0 | 66.0795 | 0 | 0 | 98.2065 | 0 | 0 | 469.1065 | 0 | 0 | 979.9112 | 15.63%
CZ 4B | 0.30839 | 0.098784 | 0.69205 | 1.1133 | 0 | 0.43643 | 0 | 0.70994 | 0 | 0 | 0.95611 | 0 | 0 | 4.435 | 0 | 0 | 8.75 | 0.9812% | CZ 4B | 10.3902 | 3.3282 | 69.2047 | 111.3278 | 0 | 14.704 | 0 | 23.9191 | 0 | 0 | 32.2131 | 0 | 0 | 269.3289 | 0 | 0 | 534.416 | 0.9812% | CZ 4B | 3.0443 | 0.97517 | 0 | 0 | 0 | 4.3083 | 0 | 7.0083 | 0 | 0 | 9.4384 | 0 | 0 | 25.9296 | 0 | 0 | 50.7042 | 0.9812% | CZ 4B | 0 | 0 | 0.69205 | 1.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.6136 | 0.9812% | CZ 4B | 31.8712 | 10.209 | 75.6407 | 121.6813 | 0 | 45.1033 | 0 | 73.37 | 0 | 0 | 98.8111 | 0 | 0 | 469.1065 | 0 | 0 | 925.793 | 0.9812%
CZ 4C | 0.3148 | 0.099347 | 0.73101 | 1.473 | 0 | 0.087871 | 0 | 0.55535 | 0 | 0 | 0.94284 | 0 | 0 | 4.435 | 0 | 0 | 8.6392 | 2.427% | CZ 4C | 10.6063 | 3.3472 | 73.1005 | 147.3001 | 0 | 2.9605 | 0 | 18.7108 | 0 | 0 | 31.7658 | 0 | 0 | 269.3289 | 0 | 0 | 557.1201 | 2.427% | CZ 4C | 3.1076 | 0.98072 | 0 | 0 | 0 | 0.86743 | 0 | 5.4823 | 0 | 0 | 9.3074 | 0 | 0 | 25.9296 | 0 | 0 | 45.6751 | 2.427% | CZ 4C | 0 | 0 | 0.73101 | 1.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0123 | 2.427% | CZ 4C | 32.5339 | 10.2671 | 79.8989 | 160.999 | 0 | 9.0811 | 0 | 57.3937 | 0 | 0 | 97.439 | 0 | 0 | 469.1065 | 0 | 0 | 916.7193 | 2.427%
CZ 5A | 0.31177 | 0.098897 | 0.76591 | 2.2377 | 0 | 0.23548 | 0 | 0.60711 | 0 | 0 | 0.94228 | 0 | 0 | 4.435 | 0 | 0 | 9.6341 | 20.98% | CZ 5A | 10.504 | 3.332 | 76.5909 | 223.7659 | 0 | 7.9339 | 0 | 20.4545 | 0 | 0 | 31.7469 | 0 | 0 | 269.3289 | 0 | 0 | 643.6569 | 20.98% | CZ 5A | 3.0777 | 0.97628 | 0 | 0 | 0 | 2.3246 | 0 | 5.9932 | 0 | 0 | 9.3018 | 0 | 0 | 25.9296 | 0 | 0 | 47.6032 | 20.98% | CZ 5A | 0 | 0 | 0.76591 | 2.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8119 | 20.98% | CZ 5A | 32.22 | 10.2206 | 83.7139 | 244.5762 | 0 | 24.3365 | 0 | 62.7424 | 0 | 0 | 97.3809 | 0 | 0 | 469.1065 | 0 | 0 | 1024.2969 | 20.98%
CZ 5B | 0.31064 | 0.099122 | 0.7498 | 1.6784 | 0 | 0.30232 | 0 | 0.68103 | 0 | 0 | 0.94891 | 0 | 0 | 4.435 | 0 | 0 | 9.2052 | 4.38% | CZ 5B | 10.466 | 3.3396 | 74.9803 | 167.8368 | 0 | 10.1855 | 0 | 22.9449 | 0 | 0 | 31.9705 | 0 | 0 | 269.3289 | 0 | 0 | 591.0525 | 4.38% | CZ 5B | 3.0666 | 0.9785 | 0 | 0 | 0 | 2.9844 | 0 | 6.7229 | 0 | 0 | 9.3674 | 0 | 0 | 25.9296 | 0 | 0 | 49.0493 | 4.38% | CZ 5B | 0 | 0 | 0.7498 | 1.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2365 | 4.38% | CZ 5B | 32.1037 | 10.2439 | 81.9534 | 183.4456 | 0 | 31.2433 | 0 | 70.3817 | 0 | 0 | 98.0669 | 0 | 0 | 469.1065 | 0 | 0 | 976.545 | 4.38%
CZ 5C | 0.31435 | 0.099234 | 0.7622 | 1.6904 | 0 | 0.02779 | 0 | 0.90684 | 0 | 0 | 0.93755 | 0 | 0 | 4.435 | 0 | 0 | 9.1733 | 0.01288% | CZ 5C | 10.5911 | 3.3434 | 76.2195 | 169.0381 | 0 | 0.9363 | 0 | 30.5528 | 0 | 0 | 31.5877 | 0 | 0 | 269.3289 | 0 | 0 | 591.5978 | 0.01288% | CZ 5C | 3.1032 | 0.97961 | 0 | 0 | 0 | 0.27433 | 0 | 8.952 | 0 | 0 | 9.2552 | 0 | 0 | 25.9296 | 0 | 0 | 48.4939 | 0.01288% | CZ 5C | 0 | 0 | 0.7622 | 1.6904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2609 | 0.01288% | CZ 5C | 32.4874 | 10.2555 | 83.3079 | 184.7587 | 0 | 2.872 | 0 | 93.7182 | 0 | 0 | 96.8926 | 0 | 0 | 469.1065 | 0 | 0 | 973.3988 | 0.01288%
CZ 6A | 0.30805 | 0.099122 | 0.80631 | 2.8558 | 0 | 0.28375 | 0 | 0.63568 | 0 | 0 | 0.94014 | 0 | 0 | 4.435 | 0 | 0 | 10.3638 | 2.983% | CZ 6A | 10.3789 | 3.3396 | 80.6308 | 285.5768 | 0 | 9.5601 | 0 | 21.4173 | 0 | 0 | 31.6749 | 0 | 0 | 269.3289 | 0 | 0 | 711.9071 | 2.983% | CZ 6A | 3.041 | 0.9785 | 0 | 0 | 0 | 2.8011 | 0 | 6.2753 | 0 | 0 | 9.2807 | 0 | 0 | 25.9296 | 0 | 0 | 48.3062 | 2.983% | CZ 6A | 0 | 0 | 0.80631 | 2.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.4704 | 2.983% | CZ 6A | 31.8363 | 10.2439 | 88.1294 | 312.1354 | 0 | 29.3247 | 0 | 65.6958 | 0 | 0 | 97.16 | 0 | 0 | 469.1065 | 0 | 0 | 1103.632 | 2.983%
CZ 6B | 0.3067 | 0.098897 | 0.79589 | 2.3174 | 0 | 0.18969 | 0 | 0.64772 | 0 | 0 | 0.93856 | 0 | 0 | 4.435 | 0 | 0 | 9.7298 | 0.4478% | CZ 6B | 10.3334 | 3.332 | 79.5886 | 231.7358 | 0 | 6.3911 | 0 | 21.8229 | 0 | 0 | 31.6218 | 0 | 0 | 269.3289 | 0 | 0 | 654.1544 | 0.4478% | CZ 6B | 3.0277 | 0.97628 | 0 | 0 | 0 | 1.8726 | 0 | 6.3941 | 0 | 0 | 9.2652 | 0 | 0 | 25.9296 | 0 | 0 | 47.4655 | 0.4478% | CZ 6B | 0 | 0 | 0.79589 | 2.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.9216 | 0.4478% | CZ 6B | 31.6968 | 10.2206 | 86.9903 | 253.2872 | 0 | 19.6041 | 0 | 66.9399 | 0 | 0 | 96.9972 | 0 | 0 | 469.1065 | 0 | 0 | 1034.8426 | 0.4478%
CZ 7 | 0.30704 | 0.099347 | 0.85448 | 3.5148 | 0 | 0.18024 | 0 | 0.61645 | 0 | 0 | 0.93485 | 0 | 0 | 4.435 | 0 | 0 | 10.9422 | 0.4375% | CZ 7 | 10.3447 | 3.3472 | 85.4476 | 351.4806 | 0 | 6.0727 | 0 | 20.7691 | 0 | 0 | 31.4967 | 0 | 0 | 269.3289 | 0 | 0 | 778.2873 | 0.4375% | CZ 7 | 3.031 | 0.98072 | 0 | 0 | 0 | 1.7793 | 0 | 6.0853 | 0 | 0 | 9.2285 | 0 | 0 | 25.9296 | 0 | 0 | 47.0345 | 0.4375% | CZ 7 | 0 | 0 | 0.85448 | 3.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1776 | 0.4375% | CZ 7 | 31.7316 | 10.2671 | 93.3942 | 384.1683 | 0 | 18.6274 | 0 | 63.7075 | 0 | 0 | 96.6135 | 0 | 0 | 469.1065 | 0 | 0 | 1167.6161 | 0.4375%
CZ 8 | 0.3148 | 0.10115 | 0.91955 | 4.769 | 0 | 0.041854 | 0 | 0.57943 | 0 | 0 | 0.92529 | 0 | 0 | 4.435 | 0 | 0 | 12.086 | 0.03762% | CZ 8 | 10.6063 | 3.4078 | 91.9546 | 476.8987 | 0 | 1.4101 | 0 | 19.522 | 0 | 0 | 31.1745 | 0 | 0 | 269.3289 | 0 | 0 | 904.3028 | 0.03762% | CZ 8 | 3.1076 | 0.99849 | 0 | 0 | 0 | 0.41317 | 0 | 5.7199 | 0 | 0 | 9.1341 | 0 | 0 | 25.9296 | 0 | 0 | 45.303 | 0.03762% | CZ 8 | 0 | 0 | 0.91955 | 4.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 7.4969 | 0.03762% | CZ 8 | 32.5339 | 10.4532 | 100.5063 | 521.2503 | 0 | 4.3255 | 0 | 59.882 | 0 | 0 | 95.6251 | 0 | 0 | 469.1065 | 0 | 0 | 1293.6828 | 0.03762%
US Weighted | 0.31021 | 0.098927 | 0.67183 | 1.323 | 0 | 0.74461 | 0 | 0.72968 | 0 | 0 | 0.96082 | 0 | 0 | 4.435 | 0 | 0 | 9.2741 | 100% | US Weighted | 10.4516 | 3.333 | 67.1828 | 132.3043 | 0 | 25.0871 | 0 | 24.5841 | 0 | 0 | 32.3716 | 0 | 0 | 269.3289 | 0 | 0 | 564.6434 | 100% | US Weighted | 3.0623 | 0.97657 | 0 | 0 | 0 | 7.3505 | 0 | 7.2032 | 0 | 0 | 9.4849 | 0 | 0 | 25.9296 | 0 | 0 | 54.0071 | 100% | US Weighted | 0 | 0 | 0.67183 | 1.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8032 | 100% | US Weighted | 32.0593 | 10.2237 | 73.4309 | 144.6086 | 0 | 76.9525 | 0 | 75.4098 | 0 | 0 | 99.2973 | 0 | 0 | 469.1065 | 0 | 0 | 981.0885 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.36307 | 0.17293 | 0.51442 | 0.12722 | 0 | 1.8109 | 0 | 0.89435 | 0 | 0 | 0.99876 | 0 | 0 | 4.435 | 0 | 0 | 9.3166 | 3.013% | CZ 1A | 12.2325 | 5.8263 | 51.4421 | 12.7222 | 0 | 61.0109 | 0 | 30.132 | 0 | 0 | 33.6498 | 0 | 0 | 269.3289 | 0 | 0 | 476.3446 | 3.013% | CZ 1A | 3.5841 | 1.7071 | 0 | 0 | 0 | 17.8762 | 0 | 8.8287 | 0 | 0 | 9.8594 | 0 | 0 | 25.9296 | 0 | 0 | 67.7851 | 3.013% | CZ 1A | 0 | 0 | 0.51442 | 0.12722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.45 | 3.013% | CZ 1A | 37.5222 | 17.8716 | 56.2262 | 13.9054 | 0 | 187.1458 | 0 | 92.4276 | 0 | 0 | 103.218 | 0 | 0 | 469.1065 | 0 | 0 | 977.4231 | 3.013%
CZ 1B | 0.36442 | 0.17259 | 0.51579 | 0.31967 | 0 | 2.2704 | 0 | 1.0723 | 0 | 0 | 0.99291 | 0 | 0 | 4.435 | 0 | 0 | 10.143 | 0% | CZ 1B | 12.278 | 5.8149 | 51.5785 | 31.9666 | 0 | 76.492 | 0 | 36.1289 | 0 | 0 | 33.4527 | 0 | 0 | 269.3289 | 0 | 0 | 517.0404 | 0% | CZ 1B | 3.5974 | 1.7038 | 0 | 0 | 0 | 22.4121 | 0 | 10.5858 | 0 | 0 | 9.8016 | 0 | 0 | 25.9296 | 0 | 0 | 74.0304 | 0% | CZ 1B | 0 | 0 | 0.51579 | 0.31967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6438 | 0% | CZ 1B | 37.6617 | 17.8367 | 56.3753 | 34.9395 | 0 | 234.6328 | 0 | 110.8224 | 0 | 0 | 102.6133 | 0 | 0 | 469.1065 | 0 | 0 | 1063.9881 | 0%
CZ 2A | 0.36273 | 0.17259 | 0.56285 | 0.44954 | 0 | 1.6254 | 0 | 0.85576 | 0 | 0 | 0.98739 | 0 | 0 | 4.435 | 0 | 0 | 9.4513 | 16.92% | CZ 2A | 12.2211 | 5.8149 | 56.2854 | 44.954 | 0 | 54.7638 | 0 | 28.8318 | 0 | 0 | 33.2669 | 0 | 0 | 269.3289 | 0 | 0 | 505.4669 | 16.92% | CZ 2A | 3.5808 | 1.7038 | 0 | 0 | 0 | 16.0458 | 0 | 8.4477 | 0 | 0 | 9.7472 | 0 | 0 | 25.9296 | 0 | 0 | 65.4549 | 16.92% | CZ 2A | 0 | 0 | 0.56285 | 0.44954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.8207 | 16.92% | CZ 2A | 37.4873 | 17.8367 | 61.5199 | 49.1348 | 0 | 167.9835 | 0 | 88.4393 | 0 | 0 | 102.0436 | 0 | 0 | 469.1065 | 0 | 0 | 993.5516 | 16.92%
CZ 2B | 0.36172 | 0.1727 | 0.56608 | 0.50559 | 0 | 1.2068 | 0 | 0.96388 | 0 | 0 | 0.97412 | 0 | 0 | 4.435 | 0 | 0 | 9.1859 | 3.461% | CZ 2B | 12.187 | 5.8187 | 56.6075 | 50.5591 | 0 | 40.6587 | 0 | 32.4747 | 0 | 0 | 32.8196 | 0 | 0 | 269.3289 | 0 | 0 | 500.4542 | 3.461% | CZ 2B | 3.5708 | 1.7049 | 0 | 0 | 0 | 11.913 | 0 | 9.5151 | 0 | 0 | 9.6162 | 0 | 0 | 25.9296 | 0 | 0 | 62.2495 | 3.461% | CZ 2B | 0 | 0 | 0.56608 | 0.50559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.88 | 3.461% | CZ 2B | 37.3826 | 17.8483 | 61.872 | 55.2611 | 0 | 124.7173 | 0 | 99.6134 | 0 | 0 | 100.6715 | 0 | 0 | 469.1065 | 0 | 0 | 966.4728 | 3.461%
CZ 3A | 0.36397 | 0.1727 | 0.64574 | 1.0874 | 0 | 0.83843 | 0 | 0.75945 | 0 | 0 | 0.9659 | 0 | 0 | 4.435 | 0 | 0 | 9.2685 | 16.34% | CZ 3A | 12.2628 | 5.8187 | 64.5736 | 108.7356 | 0 | 28.2481 | 0 | 25.587 | 0 | 0 | 32.5429 | 0 | 0 | 269.3289 | 0 | 0 | 547.0976 | 16.34% | CZ 3A | 3.593 | 1.7049 | 0 | 0 | 0 | 8.2767 | 0 | 7.497 | 0 | 0 | 9.5351 | 0 | 0 | 25.9296 | 0 | 0 | 56.5363 | 16.34% | CZ 3A | 0 | 0 | 0.64574 | 1.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5414 | 16.34% | CZ 3A | 37.6152 | 17.8483 | 70.5789 | 118.848 | 0 | 86.6487 | 0 | 78.4861 | 0 | 0 | 99.8227 | 0 | 0 | 469.1065 | 0 | 0 | 978.9544 | 16.34%
CZ 3B | 0.36307 | 0.1727 | 0.62448 | 0.78103 | 0 | 0.80198 | 0 | 0.86656 | 0 | 0 | 0.96557 | 0 | 0 | 4.435 | 0 | 0 | 9.0104 | 10.77% | CZ 3B | 12.2325 | 5.8187 | 62.4475 | 78.103 | 0 | 27.0199 | 0 | 29.1958 | 0 | 0 | 32.5315 | 0 | 0 | 269.3289 | 0 | 0 | 516.6778 | 10.77% | CZ 3B | 3.5841 | 1.7049 | 0 | 0 | 0 | 7.9168 | 0 | 8.5544 | 0 | 0 | 9.5317 | 0 | 0 | 25.9296 | 0 | 0 | 57.2216 | 10.77% | CZ 3B | 0 | 0 | 0.62448 | 0.78103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2138 | 10.77% | CZ 3B | 37.5222 | 17.8483 | 68.2552 | 85.3666 | 0 | 82.8813 | 0 | 89.5556 | 0 | 0 | 99.7878 | 0 | 0 | 469.1065 | 0 | 0 | 950.3234 | 10.77%
CZ 3C | 0.36476 | 0.17304 | 0.65487 | 0.79009 | 0 | 0.18823 | 0 | 0.59282 | 0 | 0 | 0.96849 | 0 | 0 | 4.435 | 0 | 0 | 8.1673 | 1.179% | CZ 3C | 12.2894 | 5.8301 | 65.4869 | 79.0088 | 0 | 6.3418 | 0 | 19.973 | 0 | 0 | 32.6301 | 0 | 0 | 269.3289 | 0 | 0 | 490.8889 | 1.179% | CZ 3C | 3.6008 | 1.7082 | 0 | 0 | 0 | 1.8581 | 0 | 5.8521 | 0 | 0 | 9.5606 | 0 | 0 | 25.9296 | 0 | 0 | 48.5095 | 1.179% | CZ 3C | 0 | 0 | 0.65487 | 0.79009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2533 | 1.179% | CZ 3C | 37.6966 | 17.8832 | 71.5772 | 86.3566 | 0 | 19.4529 | 0 | 61.2657 | 0 | 0 | 100.0901 | 0 | 0 | 469.1065 | 0 | 0 | 863.4288 | 1.179%
CZ 4A | 0.3651 | 0.17304 | 0.711 | 1.6236 | 0 | 0.47671 | 0 | 0.64322 | 0 | 0 | 0.9506 | 0 | 0 | 4.435 | 0 | 0 | 9.3783 | 15.63% | CZ 4A | 12.3007 | 5.8301 | 71.0995 | 162.3606 | 0 | 16.0611 | 0 | 21.6713 | 0 | 0 | 32.0274 | 0 | 0 | 269.3289 | 0 | 0 | 590.6795 | 15.63% | CZ 4A | 3.6041 | 1.7082 | 0 | 0 | 0 | 4.7059 | 0 | 6.3497 | 0 | 0 | 9.384 | 0 | 0 | 25.9296 | 0 | 0 | 51.6816 | 15.63% | CZ 4A | 0 | 0 | 0.711 | 1.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1429 | 15.63% | CZ 4A | 37.7315 | 17.8832 | 77.7118 | 177.4601 | 0 | 49.266 | 0 | 66.4748 | 0 | 0 | 98.2413 | 0 | 0 | 469.1065 | 0 | 0 | 993.8753 | 15.63%
CZ 4B | 0.36105 | 0.17259 | 0.69197 | 1.114 | 0 | 0.44205 | 0 | 0.71489 | 0 | 0 | 0.95668 | 0 | 0 | 4.435 | 0 | 0 | 8.8883 | 0.9812% | CZ 4B | 12.1643 | 5.8149 | 69.1971 | 111.4036 | 0 | 14.8935 | 0 | 24.0859 | 0 | 0 | 32.2321 | 0 | 0 | 269.3289 | 0 | 0 | 539.1202 | 0.9812% | CZ 4B | 3.5641 | 1.7038 | 0 | 0 | 0 | 4.3638 | 0 | 7.0572 | 0 | 0 | 9.444 | 0 | 0 | 25.9296 | 0 | 0 | 52.0625 | 0.9812% | CZ 4B | 0 | 0 | 0.69197 | 1.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.6143 | 0.9812% | CZ 4B | 37.3129 | 17.8367 | 75.6324 | 121.7641 | 0 | 45.6847 | 0 | 73.8816 | 0 | 0 | 98.8692 | 0 | 0 | 469.1065 | 0 | 0 | 940.0881 | 0.9812%
CZ 4C | 0.36622 | 0.17304 | 0.73093 | 1.4693 | 0 | 0.091134 | 0 | 0.5612 | 0 | 0 | 0.94329 | 0 | 0 | 4.435 | 0 | 0 | 8.7701 | 2.427% | CZ 4C | 12.3386 | 5.8301 | 73.093 | 146.9325 | 0 | 3.0704 | 0 | 18.9079 | 0 | 0 | 31.781 | 0 | 0 | 269.3289 | 0 | 0 | 561.2823 | 2.427% | CZ 4C | 3.6152 | 1.7082 | 0 | 0 | 0 | 0.89964 | 0 | 5.54 | 0 | 0 | 9.3118 | 0 | 0 | 25.9296 | 0 | 0 | 47.0045 | 2.427% | CZ 4C | 0 | 0 | 0.73093 | 1.4693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0086 | 2.427% | CZ 4C | 37.8477 | 17.8832 | 79.8906 | 160.5972 | 0 | 9.4183 | 0 | 57.9983 | 0 | 0 | 97.4856 | 0 | 0 | 469.1065 | 0 | 0 | 930.2275 | 2.427%
CZ 5A | 0.36363 | 0.17282 | 0.76583 | 2.2332 | 0 | 0.24111 | 0 | 0.61273 | 0 | 0 | 0.94261 | 0 | 0 | 4.435 | 0 | 0 | 9.767 | 20.98% | CZ 5A | 12.2515 | 5.8225 | 76.5833 | 223.3225 | 0 | 8.1234 | 0 | 20.644 | 0 | 0 | 31.7582 | 0 | 0 | 269.3289 | 0 | 0 | 647.8343 | 20.98% | CZ 5A | 3.5897 | 1.706 | 0 | 0 | 0 | 2.3802 | 0 | 6.0487 | 0 | 0 | 9.3052 | 0 | 0 | 25.9296 | 0 | 0 | 48.9593 | 20.98% | CZ 5A | 0 | 0 | 0.76583 | 2.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8074 | 20.98% | CZ 5A | 37.5803 | 17.8599 | 83.7056 | 244.0915 | 0 | 24.9179 | 0 | 63.3238 | 0 | 0 | 97.4158 | 0 | 0 | 469.1065 | 0 | 0 | 1038.0013 | 20.98%
CZ 5B | 0.36296 | 0.17293 | 0.74973 | 1.6756 | 0 | 0.30862 | 0 | 0.68766 | 0 | 0 | 0.94948 | 0 | 0 | 4.435 | 0 | 0 | 9.3419 | 4.38% | CZ 5B | 12.2287 | 5.8263 | 74.9727 | 167.5563 | 0 | 10.3978 | 0 | 23.1686 | 0 | 0 | 31.9895 | 0 | 0 | 269.3289 | 0 | 0 | 595.4687 | 4.38% | CZ 5B | 3.583 | 1.7071 | 0 | 0 | 0 | 3.0466 | 0 | 6.7884 | 0 | 0 | 9.3729 | 0 | 0 | 25.9296 | 0 | 0 | 50.4276 | 4.38% | CZ 5B | 0 | 0 | 0.74973 | 1.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2336 | 4.38% | CZ 5B | 37.5105 | 17.8716 | 81.9451 | 183.1391 | 0 | 31.8944 | 0 | 71.0677 | 0 | 0 | 98.1251 | 0 | 0 | 469.1065 | 0 | 0 | 990.66 | 4.38%
CZ 5C | 0.36611 | 0.17293 | 0.76216 | 1.6841 | 0 | 0.02959 | 0 | 0.91932 | 0 | 0 | 0.93811 | 0 | 0 | 4.435 | 0 | 0 | 9.3073 | 0.01288% | CZ 5C | 12.3348 | 5.8263 | 76.2157 | 168.409 | 0 | 0.99695 | 0 | 30.9736 | 0 | 0 | 31.6066 | 0 | 0 | 269.3289 | 0 | 0 | 595.6918 | 0.01288% | CZ 5C | 3.6141 | 1.7071 | 0 | 0 | 0 | 0.29211 | 0 | 9.0753 | 0 | 0 | 9.2607 | 0 | 0 | 25.9296 | 0 | 0 | 49.8789 | 0.01288% | CZ 5C | 0 | 0 | 0.76216 | 1.6841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2546 | 0.01288% | CZ 5C | 37.8361 | 17.8716 | 83.3038 | 184.0711 | 0 | 3.0581 | 0 | 95.0089 | 0 | 0 | 96.9507 | 0 | 0 | 469.1065 | 0 | 0 | 987.2066 | 0.01288%
CZ 6A | 0.36397 | 0.17293 | 0.80627 | 2.8629 | 0 | 0.28634 | 0 | 0.63793 | 0 | 0 | 0.94048 | 0 | 0 | 4.435 | 0 | 0 | 10.5058 | 2.983% | CZ 6A | 12.2628 | 5.8263 | 80.627 | 286.2893 | 0 | 9.6473 | 0 | 21.4931 | 0 | 0 | 31.6862 | 0 | 0 | 269.3289 | 0 | 0 | 717.1608 | 2.983% | CZ 6A | 3.593 | 1.7071 | 0 | 0 | 0 | 2.8266 | 0 | 6.2975 | 0 | 0 | 9.2841 | 0 | 0 | 25.9296 | 0 | 0 | 49.6379 | 2.983% | CZ 6A | 0 | 0 | 0.80627 | 2.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.4775 | 2.983% | CZ 6A | 37.6152 | 17.8716 | 88.1253 | 312.9142 | 0 | 29.5922 | 0 | 65.9283 | 0 | 0 | 97.1949 | 0 | 0 | 469.1065 | 0 | 0 | 1118.3481 | 2.983%
CZ 6B | 0.36206 | 0.1727 | 0.79585 | 2.3249 | 0 | 0.19149 | 0 | 0.65009 | 0 | 0 | 0.93913 | 0 | 0 | 4.435 | 0 | 0 | 9.8712 | 0.4478% | CZ 6B | 12.1984 | 5.8187 | 79.5848 | 232.4937 | 0 | 6.4517 | 0 | 21.9025 | 0 | 0 | 31.6407 | 0 | 0 | 269.3289 | 0 | 0 | 659.4194 | 0.4478% | CZ 6B | 3.5741 | 1.7049 | 0 | 0 | 0 | 1.8904 | 0 | 6.4174 | 0 | 0 | 9.2707 | 0 | 0 | 25.9296 | 0 | 0 | 48.7872 | 0.4478% | CZ 6B | 0 | 0 | 0.79585 | 2.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.9291 | 0.4478% | CZ 6B | 37.4175 | 17.8483 | 86.9862 | 254.1157 | 0 | 19.7901 | 0 | 67.1841 | 0 | 0 | 97.0553 | 0 | 0 | 469.1065 | 0 | 0 | 1049.5037 | 0.4478%
CZ 7 | 0.36105 | 0.17304 | 0.85444 | 3.5273 | 0 | 0.1826 | 0 | 0.62016 | 0 | 0 | 0.9353 | 0 | 0 | 4.435 | 0 | 0 | 11.0889 | 0.4375% | CZ 7 | 12.1643 | 5.8301 | 85.4438 | 352.7312 | 0 | 6.1523 | 0 | 20.8942 | 0 | 0 | 31.5119 | 0 | 0 | 269.3289 | 0 | 0 | 784.0564 | 0.4375% | CZ 7 | 3.5641 | 1.7082 | 0 | 0 | 0 | 1.8026 | 0 | 6.122 | 0 | 0 | 9.233 | 0 | 0 | 25.9296 | 0 | 0 | 48.3595 | 0.4375% | CZ 7 | 0 | 0 | 0.85444 | 3.5273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1901 | 0.4375% | CZ 7 | 37.3129 | 17.8832 | 93.39 | 385.5352 | 0 | 18.8715 | 0 | 64.0912 | 0 | 0 | 96.66 | 0 | 0 | 469.1065 | 0 | 0 | 1182.8505 | 0.4375%
CZ 8 | 0.36881 | 0.17428 | 0.91951 | 4.7867 | 0 | 0.042641 | 0 | 0.58292 | 0 | 0 | 0.92562 | 0 | 0 | 4.435 | 0 | 0 | 12.2355 | 0.03762% | CZ 8 | 12.4258 | 5.8718 | 91.9508 | 478.6685 | 0 | 1.4367 | 0 | 19.6395 | 0 | 0 | 31.1859 | 0 | 0 | 269.3289 | 0 | 0 | 910.5077 | 0.03762% | CZ 8 | 3.6408 | 1.7204 | 0 | 0 | 0 | 0.42094 | 0 | 5.7544 | 0 | 0 | 9.1375 | 0 | 0 | 25.9296 | 0 | 0 | 46.6036 | 0.03762% | CZ 8 | 0 | 0 | 0.91951 | 4.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 7.5145 | 0.03762% | CZ 8 | 38.1152 | 18.0111 | 100.5022 | 523.1847 | 0 | 4.4068 | 0 | 60.2424 | 0 | 0 | 95.66 | 0 | 0 | 469.1065 | 0 | 0 | 1309.2289 | 0.03762%
US Weighted | 0.36364 | 0.1728 | 0.67178 | 1.324 | 0 | 0.75235 | 0 | 0.73434 | 0 | 0 | 0.96114 | 0 | 0 | 4.435 | 0 | 0 | 9.4151 | 100% | US Weighted | 12.2515 | 5.8218 | 67.178 | 132.4045 | 0 | 25.3479 | 0 | 24.7413 | 0 | 0 | 32.3824 | 0 | 0 | 269.3289 | 0 | 0 | 569.4564 | 100% | US Weighted | 3.5897 | 1.7058 | 0 | 0 | 0 | 7.4269 | 0 | 7.2492 | 0 | 0 | 9.4881 | 0 | 0 | 25.9296 | 0 | 0 | 55.3893 | 100% | US Weighted | 0 | 0 | 0.67178 | 1.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8041 | 100% | US Weighted | 37.5806 | 17.858 | 73.4256 | 144.7182 | 0 | 77.7527 | 0 | 75.8918 | 0 | 0 | 99.3305 | 0 | 0 | 469.1065 | 0 | 0 | 995.6638 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.39806 | 0.17293 | 0.5148 | 0.066396 | 0 | 1.9867 | 0 | 1.281 | 0 | 0 | 1.2506 | 0 | 0 | 4.435 | 0 | 0 | 10.1055 | 3.013% | CZ 1A | 13.4114 | 5.8263 | 51.48 | 6.6396 | 0 | 66.9357 | 0 | 43.1606 | 0 | 0 | 42.1333 | 0 | 0 | 269.3289 | 0 | 0 | 498.9157 | 3.013% | CZ 1A | 3.9295 | 1.7071 | 0 | 0 | 0 | 19.6122 | 0 | 12.6461 | 0 | 0 | 12.3451 | 0 | 0 | 25.9296 | 0 | 0 | 76.1695 | 3.013% | CZ 1A | 0 | 0 | 0.5148 | 0.066396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3895 | 3.013% | CZ 1A | 41.1383 | 17.8716 | 56.2676 | 7.2571 | 0 | 205.3197 | 0 | 132.3915 | 0 | 0 | 129.2405 | 0 | 0 | 469.1065 | 0 | 0 | 1058.5928 | 3.013%
CZ 1B | 0.39682 | 0.17259 | 0.51548 | 0.31292 | 0 | 2.3736 | 0 | 1.439 | 0 | 0 | 1.2521 | 0 | 0 | 4.435 | 0 | 0 | 10.8976 | 0% | CZ 1B | 13.3697 | 5.8149 | 51.5482 | 31.292 | 0 | 79.9718 | 0 | 48.4827 | 0 | 0 | 42.1864 | 0 | 0 | 269.3289 | 0 | 0 | 541.9945 | 0% | CZ 1B | 3.9173 | 1.7038 | 0 | 0 | 0 | 23.4317 | 0 | 14.2054 | 0 | 0 | 12.3606 | 0 | 0 | 25.9296 | 0 | 0 | 81.5485 | 0% | CZ 1B | 0 | 0 | 0.51548 | 0.31292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6367 | 0% | CZ 1B | 41.0104 | 17.8367 | 56.3422 | 34.2021 | 0 | 245.3069 | 0 | 148.7166 | 0 | 0 | 129.4032 | 0 | 0 | 469.1065 | 0 | 0 | 1141.9247 | 0%
CZ 2A | 0.39829 | 0.17259 | 0.56293 | 0.44177 | 0 | 1.7852 | 0 | 1.2737 | 0 | 0 | 1.2428 | 0 | 0 | 4.435 | 0 | 0 | 10.3123 | 16.92% | CZ 2A | 13.419 | 5.8149 | 56.293 | 44.1771 | 0 | 60.1466 | 0 | 42.9142 | 0 | 0 | 41.8718 | 0 | 0 | 269.3289 | 0 | 0 | 533.9654 | 16.92% | CZ 2A | 3.9318 | 1.7038 | 0 | 0 | 0 | 17.623 | 0 | 12.5739 | 0 | 0 | 12.2684 | 0 | 0 | 25.9296 | 0 | 0 | 74.0304 | 16.92% | CZ 2A | 0 | 0 | 0.56293 | 0.44177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.813 | 16.92% | CZ 2A | 41.1616 | 17.8367 | 61.5282 | 48.2856 | 0 | 184.4947 | 0 | 131.6357 | 0 | 0 | 128.4382 | 0 | 0 | 469.1065 | 0 | 0 | 1082.4872 | 16.92%
CZ 2B | 0.3993 | 0.1727 | 0.56577 | 0.50464 | 0 | 1.2805 | 0 | 1.3601 | 0 | 0 | 1.2347 | 0 | 0 | 4.435 | 0 | 0 | 9.9527 | 3.461% | CZ 2B | 13.4531 | 5.8187 | 56.5772 | 50.4643 | 0 | 43.1416 | 0 | 45.8254 | 0 | 0 | 41.5988 | 0 | 0 | 269.3289 | 0 | 0 | 526.2081 | 3.461% | CZ 2B | 3.9418 | 1.7049 | 0 | 0 | 0 | 12.6405 | 0 | 13.4269 | 0 | 0 | 12.1885 | 0 | 0 | 25.9296 | 0 | 0 | 69.8321 | 3.461% | CZ 2B | 0 | 0 | 0.56577 | 0.50464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.8787 | 3.461% | CZ 2B | 41.2663 | 17.8483 | 61.8389 | 55.1575 | 0 | 132.3334 | 0 | 140.5657 | 0 | 0 | 127.601 | 0 | 0 | 469.1065 | 0 | 0 | 1045.7175 | 3.461%
CZ 3A | 0.3912 | 0.1727 | 0.64562 | 1.0836 | 0 | 0.91212 | 0 | 1.192 | 0 | 0 | 1.2241 | 0 | 0 | 4.435 | 0 | 0 | 10.0564 | 16.34% | CZ 3A | 13.1802 | 5.8187 | 64.5622 | 108.3566 | 0 | 30.731 | 0 | 40.1622 | 0 | 0 | 41.2425 | 0 | 0 | 269.3289 | 0 | 0 | 573.3822 | 16.34% | CZ 3A | 3.8618 | 1.7049 | 0 | 0 | 0 | 9.0042 | 0 | 11.7675 | 0 | 0 | 12.0841 | 0 | 0 | 25.9296 | 0 | 0 | 64.352 | 16.34% | CZ 3A | 0 | 0 | 0.64562 | 1.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5375 | 16.34% | CZ 3A | 40.4291 | 17.8483 | 70.5665 | 118.4338 | 0 | 94.2647 | 0 | 123.1941 | 0 | 0 | 126.508 | 0 | 0 | 469.1065 | 0 | 0 | 1060.351 | 16.34%
CZ 3B | 0.3903 | 0.1727 | 0.6241 | 0.78186 | 0 | 0.85204 | 0 | 1.2646 | 0 | 0 | 1.2269 | 0 | 0 | 4.435 | 0 | 0 | 9.7475 | 10.77% | CZ 3B | 13.1498 | 5.8187 | 62.4096 | 78.1864 | 0 | 28.7068 | 0 | 42.6071 | 0 | 0 | 41.3373 | 0 | 0 | 269.3289 | 0 | 0 | 541.5446 | 10.77% | CZ 3B | 3.8529 | 1.7049 | 0 | 0 | 0 | 8.4111 | 0 | 12.4839 | 0 | 0 | 12.1118 | 0 | 0 | 25.9296 | 0 | 0 | 64.4942 | 10.77% | CZ 3B | 0 | 0 | 0.6241 | 0.78186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2143 | 10.77% | CZ 3B | 40.336 | 17.8483 | 68.2137 | 85.4577 | 0 | 88.0556 | 0 | 130.6939 | 0 | 0 | 126.7987 | 0 | 0 | 469.1065 | 0 | 0 | 1026.5105 | 10.77%
CZ 3C | 0.39131 | 0.17304 | 0.65457 | 0.82874 | 0 | 0.2401 | 0 | 1.3649 | 0 | 0 | 1.2285 | 0 | 0 | 4.435 | 0 | 0 | 9.3161 | 1.179% | CZ 3C | 13.184 | 5.8301 | 65.4566 | 82.8743 | 0 | 8.0893 | 0 | 45.9846 | 0 | 0 | 41.3903 | 0 | 0 | 269.3289 | 0 | 0 | 532.138 | 1.179% | CZ 3C | 3.8629 | 1.7082 | 0 | 0 | 0 | 2.3702 | 0 | 13.4735 | 0 | 0 | 12.1274 | 0 | 0 | 25.9296 | 0 | 0 | 59.4718 | 1.179% | CZ 3C | 0 | 0 | 0.65457 | 0.82874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2916 | 1.179% | CZ 3C | 40.4407 | 17.8832 | 71.5441 | 90.5816 | 0 | 24.8132 | 0 | 141.0541 | 0 | 0 | 126.9615 | 0 | 0 | 469.1065 | 0 | 0 | 982.3848 | 1.179%
CZ 4A | 0.39109 | 0.17304 | 0.71096 | 1.6253 | 0 | 0.52441 | 0 | 1.0675 | 0 | 0 | 1.2089 | 0 | 0 | 4.435 | 0 | 0 | 10.1362 | 15.63% | CZ 4A | 13.1764 | 5.8301 | 71.0958 | 162.5273 | 0 | 17.6683 | 0 | 35.9659 | 0 | 0 | 40.7308 | 0 | 0 | 269.3289 | 0 | 0 | 616.3233 | 15.63% | CZ 4A | 3.8607 | 1.7082 | 0 | 0 | 0 | 5.1768 | 0 | 10.538 | 0 | 0 | 11.9341 | 0 | 0 | 25.9296 | 0 | 0 | 59.1475 | 15.63% | CZ 4A | 0 | 0 | 0.71096 | 1.6253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1445 | 15.63% | CZ 4A | 40.4174 | 17.8832 | 77.7077 | 177.6424 | 0 | 54.1961 | 0 | 110.3224 | 0 | 0 | 124.9383 | 0 | 0 | 469.1065 | 0 | 0 | 1072.2139 | 15.63%
CZ 4B | 0.38726 | 0.17259 | 0.69197 | 1.0626 | 0 | 0.4955 | 0 | 1.4296 | 0 | 0 | 1.2144 | 0 | 0 | 4.435 | 0 | 0 | 9.8889 | 0.9812% | CZ 4B | 13.0475 | 5.8149 | 69.1971 | 106.2609 | 0 | 16.6941 | 0 | 48.1643 | 0 | 0 | 40.9165 | 0 | 0 | 269.3289 | 0 | 0 | 569.4241 | 0.9812% | CZ 4B | 3.8229 | 1.7038 | 0 | 0 | 0 | 4.8914 | 0 | 14.1121 | 0 | 0 | 11.9885 | 0 | 0 | 25.9296 | 0 | 0 | 62.4484 | 0.9812% | CZ 4B | 0 | 0 | 0.69197 | 1.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5629 | 0.9812% | CZ 4B | 40.0221 | 17.8367 | 75.6324 | 116.1431 | 0 | 51.2078 | 0 | 147.7399 | 0 | 0 | 125.508 | 0 | 0 | 469.1065 | 0 | 0 | 1043.1966 | 0.9812%
CZ 4C | 0.39255 | 0.17304 | 0.73074 | 1.4563 | 0 | 0.11217 | 0 | 1.2485 | 0 | 0 | 1.204 | 0 | 0 | 4.435 | 0 | 0 | 9.7522 | 2.427% | CZ 4C | 13.2257 | 5.8301 | 73.074 | 145.625 | 0 | 3.7793 | 0 | 42.0651 | 0 | 0 | 40.564 | 0 | 0 | 269.3289 | 0 | 0 | 593.492 | 2.427% | CZ 4C | 3.8751 | 1.7082 | 0 | 0 | 0 | 1.1073 | 0 | 12.3251 | 0 | 0 | 11.8852 | 0 | 0 | 25.9296 | 0 | 0 | 56.8306 | 2.427% | CZ 4C | 0 | 0 | 0.73074 | 1.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.9953 | 2.427% | CZ 4C | 40.5686 | 17.8832 | 79.8699 | 159.1682 | 0 | 11.5927 | 0 | 129.0312 | 0 | 0 | 124.4266 | 0 | 0 | 469.1065 | 0 | 0 | 1031.6468 | 2.427%
CZ 5A | 0.38985 | 0.17282 | 0.76572 | 2.2458 | 0 | 0.26586 | 0 | 1.0389 | 0 | 0 | 1.202 | 0 | 0 | 4.435 | 0 | 0 | 10.5159 | 20.98% | CZ 5A | 13.1347 | 5.8225 | 76.572 | 224.5807 | 0 | 8.9574 | 0 | 35.0031 | 0 | 0 | 40.4957 | 0 | 0 | 269.3289 | 0 | 0 | 673.8949 | 20.98% | CZ 5A | 3.8485 | 1.706 | 0 | 0 | 0 | 2.6245 | 0 | 10.2559 | 0 | 0 | 11.8653 | 0 | 0 | 25.9296 | 0 | 0 | 56.2297 | 20.98% | CZ 5A | 0 | 0 | 0.76572 | 2.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8198 | 20.98% | CZ 5A | 40.2895 | 17.8599 | 83.6931 | 245.4667 | 0 | 27.476 | 0 | 107.369 | 0 | 0 | 124.2173 | 0 | 0 | 469.1065 | 0 | 0 | 1115.4781 | 20.98%
CZ 5B | 0.38906 | 0.17293 | 0.74965 | 1.6219 | 0 | 0.34417 | 0 | 1.3895 | 0 | 0 | 1.2081 | 0 | 0 | 4.435 | 0 | 0 | 10.3104 | 4.38% | CZ 5B | 13.1081 | 5.8263 | 74.9651 | 162.1938 | 0 | 11.5957 | 0 | 46.8148 | 0 | 0 | 40.7042 | 0 | 0 | 269.3289 | 0 | 0 | 624.5369 | 4.38% | CZ 5B | 3.8407 | 1.7071 | 0 | 0 | 0 | 3.3975 | 0 | 13.7167 | 0 | 0 | 11.9263 | 0 | 0 | 25.9296 | 0 | 0 | 60.518 | 4.38% | CZ 5B | 0 | 0 | 0.74965 | 1.6219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1799 | 4.38% | CZ 5B | 40.2081 | 17.8716 | 81.9368 | 177.2779 | 0 | 35.5687 | 0 | 143.6005 | 0 | 0 | 124.8569 | 0 | 0 | 469.1065 | 0 | 0 | 1090.427 | 4.38%
CZ 5C | 0.3921 | 0.17293 | 0.76212 | 1.7683 | 0 | 0.033528 | 0 | 1.1672 | 0 | 0 | 1.1976 | 0 | 0 | 4.435 | 0 | 0 | 9.9287 | 0.01288% | CZ 5C | 13.2105 | 5.8263 | 76.2119 | 176.8299 | 0 | 1.1296 | 0 | 39.3244 | 0 | 0 | 40.3479 | 0 | 0 | 269.3289 | 0 | 0 | 622.2093 | 0.01288% | CZ 5C | 3.8707 | 1.7071 | 0 | 0 | 0 | 0.33098 | 0 | 11.5221 | 0 | 0 | 11.8219 | 0 | 0 | 25.9296 | 0 | 0 | 55.1824 | 0.01288% | CZ 5C | 0 | 0 | 0.76212 | 1.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.3387 | 0.01288% | CZ 5C | 40.5221 | 17.8716 | 83.2996 | 193.275 | 0 | 3.465 | 0 | 120.6244 | 0 | 0 | 123.7639 | 0 | 0 | 469.1065 | 0 | 0 | 1051.9281 | 0.01288%
CZ 6A | 0.3903 | 0.17293 | 0.80604 | 2.879 | 0 | 0.31087 | 0 | 1.0521 | 0 | 0 | 1.2013 | 0 | 0 | 4.435 | 0 | 0 | 11.2475 | 2.983% | CZ 6A | 13.1498 | 5.8263 | 80.6042 | 287.9037 | 0 | 10.4736 | 0 | 35.4466 | 0 | 0 | 40.473 | 0 | 0 | 269.3289 | 0 | 0 | 743.2061 | 2.983% | CZ 6A | 3.8529 | 1.7071 | 0 | 0 | 0 | 3.0688 | 0 | 10.3858 | 0 | 0 | 11.8586 | 0 | 0 | 25.9296 | 0 | 0 | 56.8028 | 2.983% | CZ 6A | 0 | 0 | 0.80604 | 2.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.4934 | 2.983% | CZ 6A | 40.336 | 17.8716 | 88.1004 | 314.6788 | 0 | 32.127 | 0 | 108.7294 | 0 | 0 | 124.1476 | 0 | 0 | 469.1065 | 0 | 0 | 1195.0973 | 2.983%
CZ 6B | 0.38861 | 0.1727 | 0.79558 | 2.2742 | 0 | 0.21602 | 0 | 1.3459 | 0 | 0 | 1.2004 | 0 | 0 | 4.435 | 0 | 0 | 10.8284 | 0.4478% | CZ 6B | 13.093 | 5.8187 | 79.5583 | 227.4231 | 0 | 7.2781 | 0 | 45.344 | 0 | 0 | 40.4427 | 0 | 0 | 269.3289 | 0 | 0 | 688.2866 | 0.4478% | CZ 6B | 3.8362 | 1.7049 | 0 | 0 | 0 | 2.1325 | 0 | 13.2858 | 0 | 0 | 11.8497 | 0 | 0 | 25.9296 | 0 | 0 | 58.7387 | 0.4478% | CZ 6B | 0 | 0 | 0.79558 | 2.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8781 | 0.4478% | CZ 6B | 40.1616 | 17.8483 | 86.9572 | 248.5734 | 0 | 22.3249 | 0 | 139.089 | 0 | 0 | 124.0546 | 0 | 0 | 469.1065 | 0 | 0 | 1148.1155 | 0.4478%
CZ 7 | 0.3903 | 0.17304 | 0.85417 | 3.4918 | 0 | 0.21141 | 0 | 1.2509 | 0 | 0 | 1.1961 | 0 | 0 | 4.435 | 0 | 0 | 12.0027 | 0.4375% | CZ 7 | 13.1498 | 5.8301 | 85.4172 | 349.1764 | 0 | 7.1227 | 0 | 42.1447 | 0 | 0 | 40.2986 | 0 | 0 | 269.3289 | 0 | 0 | 812.4684 | 0.4375% | CZ 7 | 3.8529 | 1.7082 | 0 | 0 | 0 | 2.0869 | 0 | 12.3484 | 0 | 0 | 11.8075 | 0 | 0 | 25.9296 | 0 | 0 | 57.7336 | 0.4375% | CZ 7 | 0 | 0 | 0.85417 | 3.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1543 | 0.4375% | CZ 7 | 40.336 | 17.8832 | 93.361 | 381.6498 | 0 | 21.8482 | 0 | 129.2753 | 0 | 0 | 123.6127 | 0 | 0 | 469.1065 | 0 | 0 | 1277.0729 | 0.4375%
CZ 8 | 0.39784 | 0.17428 | 0.91924 | 4.763 | 0 | 0.055243 | 0 | 1.1827 | 0 | 0 | 1.1877 | 0 | 0 | 4.435 | 0 | 0 | 13.115 | 0.03762% | CZ 8 | 13.4038 | 5.8718 | 91.9242 | 476.2999 | 0 | 1.8612 | 0 | 39.8475 | 0 | 0 | 40.0143 | 0 | 0 | 269.3289 | 0 | 0 | 938.5516 | 0.03762% | CZ 8 | 3.9273 | 1.7204 | 0 | 0 | 0 | 0.54534 | 0 | 11.6753 | 0 | 0 | 11.7242 | 0 | 0 | 25.9296 | 0 | 0 | 55.5222 | 0.03762% | CZ 8 | 0 | 0 | 0.91924 | 4.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 7.4906 | 0.03762% | CZ 8 | 41.1151 | 18.0111 | 100.4732 | 520.5958 | 0 | 5.7091 | 0 | 122.229 | 0 | 0 | 122.7406 | 0 | 0 | 469.1065 | 0 | 0 | 1399.9805 | 0.03762%
US Weighted | 0.39235 | 0.1728 | 0.67168 | 1.3206 | 0 | 0.82149 | 0 | 1.1817 | 0 | 0 | 1.2196 | 0 | 0 | 4.435 | 0 | 0 | 10.2152 | 100% | US Weighted | 13.2189 | 5.8218 | 67.1684 | 132.0622 | 0 | 27.6776 | 0 | 39.8148 | 0 | 0 | 41.089 | 0 | 0 | 269.3289 | 0 | 0 | 596.1816 | 100% | US Weighted | 3.8732 | 1.7058 | 0 | 0 | 0 | 8.1095 | 0 | 11.6657 | 0 | 0 | 12.0391 | 0 | 0 | 25.9296 | 0 | 0 | 63.3229 | 100% | US Weighted | 0 | 0 | 0.67168 | 1.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8006 | 100% | US Weighted | 40.548 | 17.858 | 73.4151 | 144.344 | 0 | 84.8986 | 0 | 122.1287 | 0 | 0 | 126.037 | 0 | 0 | 469.1065 | 0 | 0 | 1078.3358 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.84473 | 0.30862 | 0.51484 | 0.064388 | 0 | 2.6675 | 0 | 1.4999 | 0 | 0 | 1.2503 | 0 | 0 | 4.4383 | 0 | 0 | 11.5885 | 3.013% | CZ 1A | 28.4604 | 10.3978 | 51.4838 | 6.4388 | 0 | 89.873 | 0 | 50.5334 | 0 | 0 | 42.1257 | 0 | 0 | 269.4388 | 0 | 0 | 548.7517 | 3.013% | CZ 1A | 8.3389 | 3.0466 | 0 | 0 | 0 | 26.3328 | 0 | 14.8063 | 0 | 0 | 12.3428 | 0 | 0 | 25.9618 | 0 | 0 | 90.8292 | 3.013% | CZ 1A | 0 | 0 | 0.51484 | 0.064388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3875 | 3.013% | CZ 1A | 87.2998 | 31.8944 | 56.2718 | 7.0376 | 0 | 275.6781 | 0 | 155.0072 | 0 | 0 | 129.2172 | 0 | 0 | 469.4437 | 0 | 0 | 1211.8497 | 3.013%
CZ 1B | 0.84473 | 0.30828 | 0.51548 | 0.27809 | 0 | 3.0299 | 0 | 1.7976 | 0 | 0 | 1.2527 | 0 | 0 | 4.4383 | 0 | 0 | 12.465 | 0% | CZ 1B | 28.4604 | 10.3864 | 51.5482 | 27.8092 | 0 | 102.0828 | 0 | 60.5636 | 0 | 0 | 42.2053 | 0 | 0 | 269.4388 | 0 | 0 | 592.4947 | 0% | CZ 1B | 8.3389 | 3.0432 | 0 | 0 | 0 | 29.9103 | 0 | 17.7451 | 0 | 0 | 12.3662 | 0 | 0 | 25.9618 | 0 | 0 | 97.3655 | 0% | CZ 1B | 0 | 0 | 0.51548 | 0.27809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6019 | 0% | CZ 1B | 87.2998 | 31.8595 | 56.3422 | 30.3955 | 0 | 313.1305 | 0 | 185.7737 | 0 | 0 | 129.4614 | 0 | 0 | 469.4437 | 0 | 0 | 1303.7063 | 0%
CZ 2A | 0.84473 | 0.30817 | 0.56293 | 0.39713 | 0 | 2.364 | 0 | 1.5652 | 0 | 0 | 1.2431 | 0 | 0 | 4.4383 | 0 | 0 | 11.7235 | 16.92% | CZ 2A | 28.4604 | 10.3826 | 56.293 | 39.7128 | 0 | 79.6458 | 0 | 52.7358 | 0 | 0 | 41.8831 | 0 | 0 | 269.4388 | 0 | 0 | 578.5523 | 16.92% | CZ 2A | 8.3389 | 3.0421 | 0 | 0 | 0 | 23.3362 | 0 | 15.4516 | 0 | 0 | 12.2718 | 0 | 0 | 25.9618 | 0 | 0 | 88.4024 | 16.92% | CZ 2A | 0 | 0 | 0.56293 | 0.39713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7684 | 16.92% | CZ 2A | 87.2998 | 31.8479 | 61.5282 | 43.4061 | 0 | 244.3069 | 0 | 161.7628 | 0 | 0 | 128.473 | 0 | 0 | 469.4437 | 0 | 0 | 1228.0684 | 16.92%
CZ 2B | 0.84473 | 0.30839 | 0.56573 | 0.4484 | 0 | 1.6821 | 0 | 1.7787 | 0 | 0 | 1.235 | 0 | 0 | 4.4383 | 0 | 0 | 11.3014 | 3.461% | CZ 2B | 28.4604 | 10.3902 | 56.5734 | 44.8404 | 0 | 56.6743 | 0 | 59.9267 | 0 | 0 | 41.6102 | 0 | 0 | 269.4388 | 0 | 0 | 567.9144 | 3.461% | CZ 2B | 8.3389 | 3.0443 | 0 | 0 | 0 | 16.6056 | 0 | 17.5585 | 0 | 0 | 12.1918 | 0 | 0 | 25.9618 | 0 | 0 | 83.701 | 3.461% | CZ 2B | 0 | 0 | 0.56573 | 0.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.8225 | 3.461% | CZ 2B | 87.2998 | 31.8712 | 61.8348 | 49.0105 | 0 | 173.8438 | 0 | 183.8203 | 0 | 0 | 127.6359 | 0 | 0 | 469.4437 | 0 | 0 | 1184.7599 | 3.461%
CZ 3A | 0.84473 | 0.30828 | 0.64562 | 0.98674 | 0 | 1.286 | 0 | 1.5508 | 0 | 0 | 1.2245 | 0 | 0 | 4.4383 | 0 | 0 | 11.2849 | 16.34% | CZ 3A | 28.4604 | 10.3864 | 64.5622 | 98.6738 | 0 | 43.3274 | 0 | 52.2506 | 0 | 0 | 41.2539 | 0 | 0 | 269.4388 | 0 | 0 | 608.3535 | 16.34% | CZ 3A | 8.3389 | 3.0432 | 0 | 0 | 0 | 12.6949 | 0 | 15.3094 | 0 | 0 | 12.0874 | 0 | 0 | 25.9618 | 0 | 0 | 77.4357 | 16.34% | CZ 3A | 0 | 0 | 0.64562 | 0.98674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4407 | 16.34% | CZ 3A | 87.2998 | 31.8595 | 70.5665 | 107.8505 | 0 | 132.9031 | 0 | 160.2744 | 0 | 0 | 126.5429 | 0 | 0 | 469.4437 | 0 | 0 | 1186.7404 | 16.34%
CZ 3B | 0.84473 | 0.30828 | 0.6241 | 0.69568 | 0 | 1.1454 | 0 | 1.6874 | 0 | 0 | 1.2273 | 0 | 0 | 4.4383 | 0 | 0 | 10.9711 | 10.77% | CZ 3B | 28.4604 | 10.3864 | 62.4096 | 69.5685 | 0 | 38.589 | 0 | 56.8525 | 0 | 0 | 41.3486 | 0 | 0 | 269.4388 | 0 | 0 | 577.0539 | 10.77% | CZ 3B | 8.3389 | 3.0432 | 0 | 0 | 0 | 11.3066 | 0 | 16.6578 | 0 | 0 | 12.1152 | 0 | 0 | 25.9618 | 0 | 0 | 77.4235 | 10.77% | CZ 3B | 0 | 0 | 0.6241 | 0.69568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1281 | 10.77% | CZ 3B | 87.2998 | 31.8595 | 68.2137 | 76.0384 | 0 | 118.3687 | 0 | 174.3903 | 0 | 0 | 126.8335 | 0 | 0 | 469.4437 | 0 | 0 | 1152.4477 | 10.77%
CZ 3C | 0.84473 | 0.30828 | 0.65453 | 0.79539 | 0 | 0.32527 | 0 | 1.4285 | 0 | 0 | 1.2292 | 0 | 0 | 4.4383 | 0 | 0 | 10.0242 | 1.179% | CZ 3C | 28.4604 | 10.3864 | 65.4528 | 79.5393 | 0 | 10.9588 | 0 | 48.1302 | 0 | 0 | 41.4131 | 0 | 0 | 269.4388 | 0 | 0 | 553.7798 | 1.179% | CZ 3C | 8.3389 | 3.0432 | 0 | 0 | 0 | 3.2109 | 0 | 14.1021 | 0 | 0 | 12.134 | 0 | 0 | 25.9618 | 0 | 0 | 66.7911 | 1.179% | CZ 3C | 0 | 0 | 0.65453 | 0.79539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2582 | 1.179% | CZ 3C | 87.2998 | 31.8595 | 71.5399 | 86.9365 | 0 | 33.6153 | 0 | 147.6353 | 0 | 0 | 127.0312 | 0 | 0 | 469.4437 | 0 | 0 | 1055.3612 | 1.179%
CZ 4A | 0.84473 | 0.30783 | 0.711 | 1.6985 | 0 | 0.78499 | 0 | 1.4473 | 0 | 0 | 1.2092 | 0 | 0 | 4.4383 | 0 | 0 | 11.4417 | 15.63% | CZ 4A | 28.4604 | 10.3713 | 71.0995 | 169.8453 | 0 | 26.4475 | 0 | 48.7632 | 0 | 0 | 40.7383 | 0 | 0 | 269.4388 | 0 | 0 | 665.1644 | 15.63% | CZ 4A | 8.3389 | 3.0388 | 0 | 0 | 0 | 7.7491 | 0 | 14.2876 | 0 | 0 | 11.9363 | 0 | 0 | 25.9618 | 0 | 0 | 71.3126 | 15.63% | CZ 4A | 0 | 0 | 0.711 | 1.6985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2178 | 15.63% | CZ 4A | 87.2998 | 31.813 | 77.7118 | 185.641 | 0 | 81.1256 | 0 | 149.5771 | 0 | 0 | 124.9615 | 0 | 0 | 469.4437 | 0 | 0 | 1207.5734 | 15.63%
CZ 4B | 0.84473 | 0.30805 | 0.69038 | 1.5393 | 0 | 0.65987 | 0 | 1.6526 | 0 | 0 | 1.2335 | 0 | 0 | 4.4383 | 0 | 0 | 11.3666 | 0.9812% | CZ 4B | 28.4604 | 10.3789 | 69.0379 | 153.9284 | 0 | 22.2323 | 0 | 55.6774 | 0 | 0 | 41.5571 | 0 | 0 | 269.4388 | 0 | 0 | 650.7111 | 0.9812% | CZ 4B | 8.3389 | 3.041 | 0 | 0 | 0 | 6.5141 | 0 | 16.3135 | 0 | 0 | 12.1762 | 0 | 0 | 25.9618 | 0 | 0 | 72.3455 | 0.9812% | CZ 4B | 0 | 0 | 0.69038 | 1.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.038 | 0.9812% | CZ 4B | 87.2998 | 31.8363 | 75.4584 | 168.2437 | 0 | 68.1957 | 0 | 170.7858 | 0 | 0 | 127.4731 | 0 | 0 | 469.4437 | 0 | 0 | 1198.7365 | 0.9812%
CZ 4C | 0.84473 | 0.30749 | 0.73074 | 1.5574 | 0 | 0.1475 | 0 | 1.3525 | 0 | 0 | 1.2042 | 0 | 0 | 4.4383 | 0 | 0 | 10.5828 | 2.427% | CZ 4C | 28.4604 | 10.3599 | 73.074 | 155.7437 | 0 | 4.9696 | 0 | 45.5677 | 0 | 0 | 40.5716 | 0 | 0 | 269.4388 | 0 | 0 | 628.1855 | 2.427% | CZ 4C | 8.3389 | 3.0355 | 0 | 0 | 0 | 1.4561 | 0 | 13.3513 | 0 | 0 | 11.8875 | 0 | 0 | 25.9618 | 0 | 0 | 64.0311 | 2.427% | CZ 4C | 0 | 0 | 0.73074 | 1.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0965 | 2.427% | CZ 4C | 87.2998 | 31.7782 | 79.8699 | 170.2278 | 0 | 15.2437 | 0 | 139.775 | 0 | 0 | 124.4499 | 0 | 0 | 469.4437 | 0 | 0 | 1118.088 | 2.427%
CZ 5A | 0.84473 | 0.30794 | 0.76576 | 2.1438 | 0 | 0.40931 | 0 | 1.3032 | 0 | 0 | 1.202 | 0 | 0 | 4.4383 | 0 | 0 | 11.4149 | 20.98% | CZ 5A | 28.4604 | 10.3751 | 76.5757 | 214.3787 | 0 | 13.7905 | 0 | 43.9073 | 0 | 0 | 40.4957 | 0 | 0 | 269.4388 | 0 | 0 | 697.4222 | 20.98% | CZ 5A | 8.3389 | 3.0399 | 0 | 0 | 0 | 4.0406 | 0 | 12.8649 | 0 | 0 | 11.8653 | 0 | 0 | 25.9618 | 0 | 0 | 66.1113 | 20.98% | CZ 5A | 0 | 0 | 0.76576 | 2.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.7179 | 20.98% | CZ 5A | 87.2998 | 31.8247 | 83.6973 | 234.3159 | 0 | 42.3011 | 0 | 134.6822 | 0 | 0 | 124.2173 | 0 | 0 | 469.4437 | 0 | 0 | 1207.782 | 20.98%
CZ 5B | 0.84473 | 0.30794 | 0.74965 | 1.568 | 0 | 0.46332 | 0 | 1.4658 | 0 | 0 | 1.2087 | 0 | 0 | 4.4383 | 0 | 0 | 11.0464 | 4.38% | CZ 5B | 28.4604 | 10.3751 | 74.9651 | 156.7972 | 0 | 15.61 | 0 | 49.3849 | 0 | 0 | 40.7232 | 0 | 0 | 269.4388 | 0 | 0 | 645.7546 | 4.38% | CZ 5B | 8.3389 | 3.0399 | 0 | 0 | 0 | 4.5737 | 0 | 14.4698 | 0 | 0 | 11.9319 | 0 | 0 | 25.9618 | 0 | 0 | 68.316 | 4.38% | CZ 5B | 0 | 0 | 0.74965 | 1.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1259 | 4.38% | CZ 5B | 87.2998 | 31.8247 | 81.9368 | 171.3794 | 0 | 47.8823 | 0 | 151.484 | 0 | 0 | 124.915 | 0 | 0 | 469.4437 | 0 | 0 | 1166.1657 | 4.38%
CZ 5C | 0.84473 | 0.30749 | 0.76204 | 1.7009 | 0 | 0.048605 | 0 | 1.2301 | 0 | 0 | 1.1986 | 0 | 0 | 4.4383 | 0 | 0 | 10.5307 | 0.01288% | CZ 5C | 28.4604 | 10.3599 | 76.2043 | 170.0879 | 0 | 1.6376 | 0 | 41.4434 | 0 | 0 | 40.382 | 0 | 0 | 269.4388 | 0 | 0 | 638.0143 | 0.01288% | CZ 5C | 8.3389 | 3.0355 | 0 | 0 | 0 | 0.47981 | 0 | 12.1429 | 0 | 0 | 11.8319 | 0 | 0 | 25.9618 | 0 | 0 | 61.7908 | 0.01288% | CZ 5C | 0 | 0 | 0.76204 | 1.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2712 | 0.01288% | CZ 5C | 87.2998 | 31.7782 | 83.2913 | 185.9061 | 0 | 5.0231 | 0 | 127.1242 | 0 | 0 | 123.8685 | 0 | 0 | 469.4437 | 0 | 0 | 1113.7349 | 0.01288%
CZ 6A | 0.84473 | 0.30772 | 0.80612 | 2.7719 | 0 | 0.46399 | 0 | 1.3273 | 0 | 0 | 1.2012 | 0 | 0 | 4.4383 | 0 | 0 | 12.1612 | 2.983% | CZ 6A | 28.4604 | 10.3675 | 80.6118 | 277.1939 | 0 | 15.6327 | 0 | 44.7186 | 0 | 0 | 40.4692 | 0 | 0 | 269.4388 | 0 | 0 | 766.8928 | 2.983% | CZ 6A | 8.3389 | 3.0377 | 0 | 0 | 0 | 4.5804 | 0 | 13.1025 | 0 | 0 | 11.8575 | 0 | 0 | 25.9618 | 0 | 0 | 66.8788 | 2.983% | CZ 6A | 0 | 0 | 0.80612 | 2.7719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.3864 | 2.983% | CZ 6A | 87.2998 | 31.8014 | 88.1087 | 302.9729 | 0 | 47.9521 | 0 | 137.1705 | 0 | 0 | 124.136 | 0 | 0 | 469.4437 | 0 | 0 | 1288.885 | 2.983%
CZ 6B | 0.84473 | 0.30749 | 0.79558 | 2.2235 | 0 | 0.29827 | 0 | 1.415 | 0 | 0 | 1.2007 | 0 | 0 | 4.4383 | 0 | 0 | 11.5236 | 0.4478% | CZ 6B | 28.4604 | 10.3599 | 79.5583 | 222.3524 | 0 | 10.0491 | 0 | 47.6753 | 0 | 0 | 40.454 | 0 | 0 | 269.4388 | 0 | 0 | 708.3481 | 0.4478% | CZ 6B | 8.3389 | 3.0355 | 0 | 0 | 0 | 2.9444 | 0 | 13.9689 | 0 | 0 | 11.853 | 0 | 0 | 25.9618 | 0 | 0 | 66.1024 | 0.4478% | CZ 6B | 0 | 0 | 0.79558 | 2.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8274 | 0.4478% | CZ 6B | 87.2998 | 31.7782 | 86.9572 | 243.0311 | 0 | 30.8247 | 0 | 146.24 | 0 | 0 | 124.0894 | 0 | 0 | 469.4437 | 0 | 0 | 1219.6641 | 0.4478%
CZ 7 | 0.84473 | 0.30738 | 0.85421 | 3.4437 | 0 | 0.31694 | 0 | 1.2984 | 0 | 0 | 1.1965 | 0 | 0 | 4.4383 | 0 | 0 | 12.7001 | 0.4375% | CZ 7 | 28.4604 | 10.3561 | 85.421 | 344.371 | 0 | 10.6783 | 0 | 43.7443 | 0 | 0 | 40.3138 | 0 | 0 | 269.4388 | 0 | 0 | 832.7838 | 0.4375% | CZ 7 | 8.3389 | 3.0343 | 0 | 0 | 0 | 3.1287 | 0 | 12.8171 | 0 | 0 | 11.8119 | 0 | 0 | 25.9618 | 0 | 0 | 65.0929 | 0.4375% | CZ 7 | 0 | 0 | 0.85421 | 3.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1062 | 0.4375% | CZ 7 | 87.2998 | 31.7665 | 93.3652 | 376.3975 | 0 | 32.7549 | 0 | 134.1822 | 0 | 0 | 123.6592 | 0 | 0 | 469.4437 | 0 | 0 | 1348.869 | 0.4375%
CZ 8 | 0.84473 | 0.30569 | 0.91924 | 4.7085 | 0 | 0.096084 | 0 | 1.2474 | 0 | 0 | 1.1883 | 0 | 0 | 4.4383 | 0 | 0 | 13.7483 | 0.03762% | CZ 8 | 28.4604 | 10.2993 | 91.9242 | 470.854 | 0 | 3.2372 | 0 | 42.0272 | 0 | 0 | 40.0371 | 0 | 0 | 269.4388 | 0 | 0 | 956.2781 | 0.03762% | CZ 8 | 8.3389 | 3.0177 | 0 | 0 | 0 | 0.94851 | 0 | 12.314 | 0 | 0 | 11.7309 | 0 | 0 | 25.9618 | 0 | 0 | 62.3117 | 0.03762% | CZ 8 | 0 | 0 | 0.91924 | 4.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 7.4361 | 0.03762% | CZ 8 | 87.2998 | 31.5921 | 100.4732 | 514.6434 | 0 | 9.9299 | 0 | 128.9149 | 0 | 0 | 122.8104 | 0 | 0 | 469.4437 | 0 | 0 | 1465.1075 | 0.03762%
US Weighted | 0.84473 | 0.30807 | 0.67168 | 1.2767 | 0 | 1.1315 | 0 | 1.4887 | 0 | 0 | 1.22 | 0 | 0 | 4.4383 | 0 | 0 | 11.3796 | 100% | US Weighted | 28.4604 | 10.3794 | 67.1684 | 127.6707 | 0 | 38.1207 | 0 | 50.1562 | 0 | 0 | 41.1029 | 0 | 0 | 269.4388 | 0 | 0 | 632.4975 | 100% | US Weighted | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.1694 | 0 | 14.6958 | 0 | 0 | 12.0432 | 0 | 0 | 25.9618 | 0 | 0 | 75.2502 | 100% | US Weighted | 0 | 0 | 0.67168 | 1.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.7567 | 100% | US Weighted | 87.2998 | 31.8381 | 73.4151 | 139.5441 | 0 | 116.9321 | 0 | 153.85 | 0 | 0 | 126.0798 | 0 | 0 | 469.4437 | 0 | 0 | 1198.4026 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.84473 | 0.30862 | 0.5148 | 0.032895 | 0 | 2.6826 | 0 | 1.429 | 0 | 0 | 1.2429 | 0 | 0 | 4.4383 | 0 | 0 | 11.4938 | 3.013% | CZ 1A | 28.4604 | 10.3978 | 51.48 | 3.2895 | 0 | 90.381 | 0 | 48.1453 | 0 | 0 | 41.8755 | 0 | 0 | 269.4388 | 0 | 0 | 543.4683 | 3.013% | CZ 1A | 8.3389 | 3.0466 | 0 | 0 | 0 | 26.4816 | 0 | 14.1066 | 0 | 0 | 12.2695 | 0 | 0 | 25.9618 | 0 | 0 | 90.205 | 3.013% | CZ 1A | 0 | 0 | 0.5148 | 0.032895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.356 | 3.013% | CZ 1A | 87.2998 | 31.8944 | 56.2676 | 3.5954 | 0 | 277.2362 | 0 | 147.6818 | 0 | 0 | 128.4498 | 0 | 0 | 469.4437 | 0 | 0 | 1201.8687 | 3.013%
CZ 1B | 0.84473 | 0.30828 | 0.51571 | 0.21151 | 0 | 3.2813 | 0 | 1.7506 | 0 | 0 | 1.2443 | 0 | 0 | 4.4383 | 0 | 0 | 12.5945 | 0% | CZ 1B | 28.4604 | 10.3864 | 51.571 | 21.1506 | 0 | 110.5511 | 0 | 58.9791 | 0 | 0 | 41.921 | 0 | 0 | 269.4388 | 0 | 0 | 592.4584 | 0% | CZ 1B | 8.3389 | 3.0432 | 0 | 0 | 0 | 32.3915 | 0 | 17.2809 | 0 | 0 | 12.2829 | 0 | 0 | 25.9618 | 0 | 0 | 99.2992 | 0% | CZ 1B | 0 | 0 | 0.51571 | 0.21151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5355 | 0% | CZ 1B | 87.2998 | 31.8595 | 56.3671 | 23.1176 | 0 | 339.1065 | 0 | 180.9134 | 0 | 0 | 128.5893 | 0 | 0 | 469.4437 | 0 | 0 | 1316.6969 | 0%
CZ 2A | 0.84473 | 0.30817 | 0.56285 | 0.34585 | 0 | 2.3906 | 0 | 1.5018 | 0 | 0 | 1.2372 | 0 | 0 | 4.4383 | 0 | 0 | 11.6294 | 16.92% | CZ 2A | 28.4604 | 10.3826 | 56.2854 | 34.5853 | 0 | 80.5442 | 0 | 50.5979 | 0 | 0 | 41.6822 | 0 | 0 | 269.4388 | 0 | 0 | 571.9768 | 16.92% | CZ 2A | 8.3389 | 3.0421 | 0 | 0 | 0 | 23.5994 | 0 | 14.8252 | 0 | 0 | 12.2129 | 0 | 0 | 25.9618 | 0 | 0 | 87.9804 | 16.92% | CZ 2A | 0 | 0 | 0.56285 | 0.34585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.717 | 16.92% | CZ 2A | 87.2998 | 31.8479 | 61.5199 | 37.8017 | 0 | 247.0626 | 0 | 155.2048 | 0 | 0 | 127.8568 | 0 | 0 | 469.4437 | 0 | 0 | 1218.0373 | 16.92%
CZ 2B | 0.84473 | 0.30839 | 0.56566 | 0.38091 | 0 | 1.7354 | 0 | 1.7665 | 0 | 0 | 1.2337 | 0 | 0 | 4.4383 | 0 | 0 | 11.2735 | 3.461% | CZ 2B | 28.4604 | 10.3902 | 56.5658 | 38.0908 | 0 | 58.4673 | 0 | 59.5173 | 0 | 0 | 41.5647 | 0 | 0 | 269.4388 | 0 | 0 | 562.4954 | 3.461% | CZ 2B | 8.3389 | 3.0443 | 0 | 0 | 0 | 17.1309 | 0 | 17.4386 | 0 | 0 | 12.1785 | 0 | 0 | 25.9618 | 0 | 0 | 84.093 | 3.461% | CZ 2B | 0 | 0 | 0.56566 | 0.38091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7549 | 3.461% | CZ 2B | 87.2998 | 31.8712 | 61.8265 | 41.6332 | 0 | 179.3437 | 0 | 182.5645 | 0 | 0 | 127.4963 | 0 | 0 | 469.4437 | 0 | 0 | 1181.4788 | 3.461%
CZ 3A | 0.84473 | 0.30828 | 0.64539 | 0.96582 | 0 | 1.302 | 0 | 1.4988 | 0 | 0 | 1.2222 | 0 | 0 | 4.4383 | 0 | 0 | 11.2254 | 16.34% | CZ 3A | 28.4604 | 10.3864 | 64.5395 | 96.5818 | 0 | 43.8657 | 0 | 50.4955 | 0 | 0 | 41.1781 | 0 | 0 | 269.4388 | 0 | 0 | 604.9462 | 16.34% | CZ 3A | 8.3389 | 3.0432 | 0 | 0 | 0 | 12.8526 | 0 | 14.7952 | 0 | 0 | 12.0652 | 0 | 0 | 25.9618 | 0 | 0 | 77.057 | 16.34% | CZ 3A | 0 | 0 | 0.64539 | 0.96582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4195 | 16.34% | CZ 3A | 87.2998 | 31.8595 | 70.5417 | 105.564 | 0 | 134.5543 | 0 | 154.8909 | 0 | 0 | 126.3103 | 0 | 0 | 469.4437 | 0 | 0 | 1180.4641 | 16.34%
CZ 3B | 0.84473 | 0.30828 | 0.62398 | 0.64214 | 0 | 1.1934 | 0 | 1.682 | 0 | 0 | 1.2266 | 0 | 0 | 4.4383 | 0 | 0 | 10.9594 | 10.77% | CZ 3B | 28.4604 | 10.3864 | 62.3983 | 64.2136 | 0 | 40.2077 | 0 | 56.6705 | 0 | 0 | 41.3259 | 0 | 0 | 269.4388 | 0 | 0 | 573.1015 | 10.77% | CZ 3B | 8.3389 | 3.0432 | 0 | 0 | 0 | 11.7808 | 0 | 16.6045 | 0 | 0 | 12.1085 | 0 | 0 | 25.9618 | 0 | 0 | 77.8378 | 10.77% | CZ 3B | 0 | 0 | 0.62398 | 0.64214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.0744 | 10.77% | CZ 3B | 87.2998 | 31.8595 | 68.2013 | 70.1854 | 0 | 123.3336 | 0 | 173.8322 | 0 | 0 | 126.7638 | 0 | 0 | 469.4437 | 0 | 0 | 1150.9194 | 10.77%
CZ 3C | 0.84473 | 0.30828 | 0.65415 | 0.6637 | 0 | 0.41831 | 0 | 1.3838 | 0 | 0 | 1.2279 | 0 | 0 | 4.4383 | 0 | 0 | 9.9391 | 1.179% | CZ 3C | 28.4604 | 10.3864 | 65.4149 | 66.3699 | 0 | 14.0937 | 0 | 46.6215 | 0 | 0 | 41.3714 | 0 | 0 | 269.4388 | 0 | 0 | 542.157 | 1.179% | CZ 3C | 8.3389 | 3.0432 | 0 | 0 | 0 | 4.1295 | 0 | 13.6601 | 0 | 0 | 12.1218 | 0 | 0 | 25.9618 | 0 | 0 | 67.2553 | 1.179% | CZ 3C | 0 | 0 | 0.65415 | 0.6637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1262 | 1.179% | CZ 3C | 87.2998 | 31.8595 | 71.4985 | 72.5423 | 0 | 43.2313 | 0 | 143.0075 | 0 | 0 | 126.9033 | 0 | 0 | 469.4437 | 0 | 0 | 1045.786 | 1.179%
CZ 4A | 0.84473 | 0.30783 | 0.7105 | 1.7773 | 0 | 0.79162 | 0 | 1.3798 | 0 | 0 | 1.2098 | 0 | 0 | 4.4383 | 0 | 0 | 11.4599 | 15.63% | CZ 4A | 28.4604 | 10.3713 | 71.0503 | 177.728 | 0 | 26.6712 | 0 | 46.4888 | 0 | 0 | 40.7611 | 0 | 0 | 269.4388 | 0 | 0 | 670.9698 | 15.63% | CZ 4A | 8.3389 | 3.0388 | 0 | 0 | 0 | 7.8147 | 0 | 13.6212 | 0 | 0 | 11.943 | 0 | 0 | 25.9618 | 0 | 0 | 70.7184 | 15.63% | CZ 4A | 0 | 0 | 0.7105 | 1.7773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2961 | 15.63% | CZ 4A | 87.2998 | 31.813 | 77.658 | 194.2567 | 0 | 81.8116 | 0 | 142.6005 | 0 | 0 | 125.0313 | 0 | 0 | 469.4437 | 0 | 0 | 1209.9146 | 15.63%
CZ 4B | 0.84473 | 0.30805 | 0.69186 | 1.0885 | 0 | 0.70848 | 0 | 1.6387 | 0 | 0 | 1.2143 | 0 | 0 | 4.4383 | 0 | 0 | 10.9329 | 0.9812% | CZ 4B | 28.4604 | 10.3789 | 69.1857 | 108.8493 | 0 | 23.8699 | 0 | 55.2111 | 0 | 0 | 40.9127 | 0 | 0 | 269.4388 | 0 | 0 | 606.3067 | 0.9812% | CZ 4B | 8.3389 | 3.041 | 0 | 0 | 0 | 6.9939 | 0 | 16.1769 | 0 | 0 | 11.9874 | 0 | 0 | 25.9618 | 0 | 0 | 72.4999 | 0.9812% | CZ 4B | 0 | 0 | 0.69186 | 1.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5887 | 0.9812% | CZ 4B | 87.2998 | 31.8363 | 75.62 | 118.9723 | 0 | 73.2188 | 0 | 169.3556 | 0 | 0 | 125.4964 | 0 | 0 | 469.4437 | 0 | 0 | 1151.2428 | 0.9812%
CZ 4C | 0.84473 | 0.30749 | 0.73006 | 1.6253 | 0 | 0.1844 | 0 | 1.2816 | 0 | 0 | 1.2077 | 0 | 0 | 4.4383 | 0 | 0 | 10.6196 | 2.427% | CZ 4C | 28.4604 | 10.3599 | 73.0058 | 162.5349 | 0 | 6.2129 | 0 | 43.1795 | 0 | 0 | 40.6891 | 0 | 0 | 269.4388 | 0 | 0 | 633.8813 | 2.427% | CZ 4C | 8.3389 | 3.0355 | 0 | 0 | 0 | 1.8204 | 0 | 12.6516 | 0 | 0 | 11.9219 | 0 | 0 | 25.9618 | 0 | 0 | 63.7301 | 2.427% | CZ 4C | 0 | 0 | 0.73006 | 1.6253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.1637 | 2.427% | CZ 4C | 87.2998 | 31.7782 | 79.7953 | 177.6507 | 0 | 19.0576 | 0 | 132.4497 | 0 | 0 | 124.8104 | 0 | 0 | 469.4437 | 0 | 0 | 1122.2852 | 2.427%
CZ 5A | 0.84473 | 0.30794 | 0.76538 | 2.4902 | 0 | 0.42574 | 0 | 1.3112 | 0 | 0 | 1.2029 | 0 | 0 | 4.4383 | 0 | 0 | 11.7863 | 20.98% | CZ 5A | 28.4604 | 10.3751 | 76.5378 | 249.0209 | 0 | 14.3439 | 0 | 44.1765 | 0 | 0 | 40.5261 | 0 | 0 | 269.4388 | 0 | 0 | 732.8794 | 20.98% | CZ 5A | 8.3389 | 3.0399 | 0 | 0 | 0 | 4.2028 | 0 | 12.9437 | 0 | 0 | 11.8741 | 0 | 0 | 25.9618 | 0 | 0 | 66.3612 | 20.98% | CZ 5A | 0 | 0 | 0.76538 | 2.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.0639 | 20.98% | CZ 5A | 87.2998 | 31.8247 | 83.6559 | 272.1798 | 0 | 43.9987 | 0 | 135.5077 | 0 | 0 | 124.3104 | 0 | 0 | 469.4437 | 0 | 0 | 1248.2206 | 20.98%
CZ 5B | 0.84473 | 0.30794 | 0.74969 | 1.7217 | 0 | 0.50585 | 0 | 1.5817 | 0 | 0 | 1.2068 | 0 | 0 | 4.4383 | 0 | 0 | 11.3566 | 4.38% | CZ 5B | 28.4604 | 10.3751 | 74.9689 | 172.1722 | 0 | 17.0429 | 0 | 53.2893 | 0 | 0 | 40.6587 | 0 | 0 | 269.4388 | 0 | 0 | 666.4062 | 4.38% | CZ 5B | 8.3389 | 3.0399 | 0 | 0 | 0 | 4.9936 | 0 | 15.6138 | 0 | 0 | 11.913 | 0 | 0 | 25.9618 | 0 | 0 | 69.8609 | 4.38% | CZ 5B | 0 | 0 | 0.74969 | 1.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2797 | 4.38% | CZ 5B | 87.2998 | 31.8247 | 81.941 | 188.1843 | 0 | 52.2776 | 0 | 163.4604 | 0 | 0 | 124.7173 | 0 | 0 | 469.4437 | 0 | 0 | 1199.1487 | 4.38%
CZ 5C | 0.84473 | 0.30749 | 0.76129 | 2.0365 | 0 | 0.071782 | 0 | 1.1814 | 0 | 0 | 1.2026 | 0 | 0 | 4.4383 | 0 | 0 | 10.844 | 0.01288% | CZ 5C | 28.4604 | 10.3599 | 76.1285 | 203.6499 | 0 | 2.4184 | 0 | 39.8021 | 0 | 0 | 40.5185 | 0 | 0 | 269.4388 | 0 | 0 | 670.7765 | 0.01288% | CZ 5C | 8.3389 | 3.0355 | 0 | 0 | 0 | 0.70861 | 0 | 11.662 | 0 | 0 | 11.8719 | 0 | 0 | 25.9618 | 0 | 0 | 61.5787 | 0.01288% | CZ 5C | 0 | 0 | 0.76129 | 2.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.6061 | 0.01288% | CZ 5C | 87.2998 | 31.7782 | 83.2085 | 222.5894 | 0 | 7.4184 | 0 | 122.0895 | 0 | 0 | 124.2871 | 0 | 0 | 469.4437 | 0 | 0 | 1148.1145 | 0.01288%
CZ 6A | 0.84473 | 0.30772 | 0.80589 | 3.2199 | 0 | 0.47828 | 0 | 1.3497 | 0 | 0 | 1.1999 | 0 | 0 | 4.4383 | 0 | 0 | 12.6444 | 2.983% | CZ 6A | 28.4604 | 10.3675 | 80.5891 | 321.9887 | 0 | 16.1141 | 0 | 45.4729 | 0 | 0 | 40.4275 | 0 | 0 | 269.4388 | 0 | 0 | 812.859 | 2.983% | CZ 6A | 8.3389 | 3.0377 | 0 | 0 | 0 | 4.7214 | 0 | 13.3236 | 0 | 0 | 11.8453 | 0 | 0 | 25.9618 | 0 | 0 | 67.2287 | 2.983% | CZ 6A | 0 | 0 | 0.80589 | 3.2199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.8341 | 2.983% | CZ 6A | 87.2998 | 31.8014 | 88.0839 | 351.9337 | 0 | 49.4288 | 0 | 139.4843 | 0 | 0 | 124.008 | 0 | 0 | 469.4437 | 0 | 0 | 1341.4837 | 2.983%
CZ 6B | 0.84473 | 0.30749 | 0.79558 | 2.5061 | 0 | 0.31705 | 0 | 1.489 | 0 | 0 | 1.1992 | 0 | 0 | 4.4383 | 0 | 0 | 11.8974 | 0.4478% | CZ 6B | 28.4604 | 10.3599 | 79.5583 | 250.6088 | 0 | 10.6821 | 0 | 50.1657 | 0 | 0 | 40.4048 | 0 | 0 | 269.4388 | 0 | 0 | 739.6787 | 0.4478% | CZ 6B | 8.3389 | 3.0355 | 0 | 0 | 0 | 3.1299 | 0 | 14.6986 | 0 | 0 | 11.8386 | 0 | 0 | 25.9618 | 0 | 0 | 67.0032 | 0.4478% | CZ 6B | 0 | 0 | 0.79558 | 2.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.11 | 0.4478% | CZ 6B | 87.2998 | 31.7782 | 86.9572 | 273.9154 | 0 | 32.7665 | 0 | 153.8793 | 0 | 0 | 123.9383 | 0 | 0 | 469.4437 | 0 | 0 | 1259.9783 | 0.4478%
CZ 7 | 0.84473 | 0.30738 | 0.85402 | 3.9978 | 0 | 0.33348 | 0 | 1.3185 | 0 | 0 | 1.196 | 0 | 0 | 4.4383 | 0 | 0 | 13.2901 | 0.4375% | CZ 7 | 28.4604 | 10.3561 | 85.4021 | 399.7772 | 0 | 11.2356 | 0 | 44.4229 | 0 | 0 | 40.2948 | 0 | 0 | 269.4388 | 0 | 0 | 889.3878 | 0.4375% | CZ 7 | 8.3389 | 3.0343 | 0 | 0 | 0 | 3.292 | 0 | 13.0159 | 0 | 0 | 11.8064 | 0 | 0 | 25.9618 | 0 | 0 | 65.4494 | 0.4375% | CZ 7 | 0 | 0 | 0.85402 | 3.9978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.6601 | 0.4375% | CZ 7 | 87.2998 | 31.7665 | 93.3445 | 436.9565 | 0 | 34.4641 | 0 | 136.2635 | 0 | 0 | 123.6011 | 0 | 0 | 469.4437 | 0 | 0 | 1413.1397 | 0.4375%
CZ 8 | 0.84473 | 0.30569 | 0.9186 | 5.4096 | 0 | 0.10475 | 0 | 1.2009 | 0 | 0 | 1.1943 | 0 | 0 | 4.4383 | 0 | 0 | 14.4168 | 0.03762% | CZ 8 | 28.4604 | 10.2993 | 91.8598 | 540.9569 | 0 | 3.5291 | 0 | 40.4616 | 0 | 0 | 40.238 | 0 | 0 | 269.4388 | 0 | 0 | 1025.2438 | 0.03762% | CZ 8 | 8.3389 | 3.0177 | 0 | 0 | 0 | 1.034 | 0 | 11.8553 | 0 | 0 | 11.7897 | 0 | 0 | 25.9618 | 0 | 0 | 61.9974 | 0.03762% | CZ 8 | 0 | 0 | 0.9186 | 5.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 8.1365 | 0.03762% | CZ 8 | 87.2998 | 31.5921 | 100.4028 | 591.2659 | 0 | 10.8253 | 0 | 124.1127 | 0 | 0 | 123.4267 | 0 | 0 | 469.4437 | 0 | 0 | 1538.3689 | 0.03762%
US Weighted | 0.84473 | 0.30807 | 0.67145 | 1.3603 | 0 | 1.1555 | 0 | 1.4612 | 0 | 0 | 1.2183 | 0 | 0 | 4.4383 | 0 | 0 | 11.4578 | 100% | US Weighted | 28.4604 | 10.3794 | 67.1449 | 136.0332 | 0 | 38.9292 | 0 | 49.2294 | 0 | 0 | 41.0466 | 0 | 0 | 269.4388 | 0 | 0 | 640.6619 | 100% | US Weighted | 8.3389 | 3.0412 | 0 | 0 | 0 | 11.4063 | 0 | 14.4242 | 0 | 0 | 12.0267 | 0 | 0 | 25.9618 | 0 | 0 | 75.199 | 100% | US Weighted | 0 | 0 | 0.67145 | 1.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8401 | 100% | US Weighted | 87.2998 | 31.8381 | 73.3893 | 148.6843 | 0 | 119.4121 | 0 | 151.0071 | 0 | 0 | 125.9072 | 0 | 0 | 469.4437 | 0 | 0 | 1206.9815 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 2501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 2501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.53656 | 0.20972 | 0.00034108 | -0.093228 | 0 | 0.88895 | 0 | 0.53949 | 0 | 0 | 0.24426 | 0 | 0 | 0.0032628 | 0 | 0 | 2.3294 | 3.013% | CZ 1A | 18.0777 | 7.0658 | 0.034108 | -9.3228 | 0 | 29.9501 | 0 | 18.1763 | 0 | 0 | 8.2295 | 0 | 0 | 0.10993 | 0 | 0 | 72.3207 | 3.013% | CZ 1A | 5.2968 | 2.0703 | 0 | 0 | 0 | 8.7754 | 0 | 5.3256 | 0 | 0 | 2.4113 | 0 | 0 | 0.032209 | 0 | 0 | 23.9115 | 3.013% | CZ 1A | 0 | 0 | 0.00034108 | -0.093228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.092887 | 3.013% | CZ 1A | 55.4519 | 21.6738 | 0.03728 | -10.1898 | 0 | 91.8694 | 0 | 55.7542 | 0 | 0 | 25.2435 | 0 | 0 | 0.3372 | 0 | 0 | 240.1775 | 3.013%
CZ 1B | 0.53544 | 0.20961 | -0.00011369 | -0.10907 | 0 | 1.0222 | 0 | 0.68136 | 0 | 0 | 0.25157 | 0 | 0 | 0.0032628 | 0 | 0 | 2.5942 | 0% | CZ 1B | 18.0398 | 7.062 | -0.011369 | -10.9069 | 0 | 34.4383 | 0 | 22.9563 | 0 | 0 | 8.4759 | 0 | 0 | 0.10993 | 0 | 0 | 80.164 | 0% | CZ 1B | 5.2857 | 2.0692 | 0 | 0 | 0 | 10.0904 | 0 | 6.7262 | 0 | 0 | 2.4835 | 0 | 0 | 0.032209 | 0 | 0 | 26.6871 | 0% | CZ 1B | 0 | 0 | -0.00011369 | -0.10907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10918 | 0% | CZ 1B | 55.3356 | 21.6622 | -0.012427 | -11.9213 | 0 | 105.6365 | 0 | 70.4166 | 0 | 0 | 25.9992 | 0 | 0 | 0.3372 | 0 | 0 | 267.4536 | 0%
CZ 2A | 0.53701 | 0.20949 | -3.7898e-05 | -0.10285 | 0 | 0.7788 | 0 | 0.65054 | 0 | 0 | 0.25 | 0 | 0 | 0.0032628 | 0 | 0 | 2.3262 | 16.92% | CZ 2A | 18.0929 | 7.0582 | -0.0037898 | -10.2854 | 0 | 26.239 | 0 | 21.9177 | 0 | 0 | 8.4229 | 0 | 0 | 0.10993 | 0 | 0 | 71.5514 | 16.92% | CZ 2A | 5.3012 | 2.0681 | 0 | 0 | 0 | 7.688 | 0 | 6.4219 | 0 | 0 | 2.4679 | 0 | 0 | 0.032209 | 0 | 0 | 23.9793 | 16.92% | CZ 2A | 0 | 0 | -3.7898e-05 | -0.10285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10289 | 16.92% | CZ 2A | 55.4984 | 21.6505 | -0.0041422 | -11.2419 | 0 | 80.486 | 0 | 67.2306 | 0 | 0 | 25.8365 | 0 | 0 | 0.3372 | 0 | 0 | 239.7932 | 16.92%
CZ 2B | 0.53791 | 0.20961 | -0.00045477 | -0.12014 | 0 | 0.53791 | 0 | 0.8076 | 0 | 0 | 0.25967 | 0 | 0 | 0.0032628 | 0 | 0 | 2.2354 | 3.461% | CZ 2B | 18.1232 | 7.062 | -0.045477 | -12.0135 | 0 | 18.1232 | 0 | 27.2094 | 0 | 0 | 8.7489 | 0 | 0 | 0.10993 | 0 | 0 | 67.3177 | 3.461% | CZ 2B | 5.3101 | 2.0692 | 0 | 0 | 0 | 5.3101 | 0 | 7.9724 | 0 | 0 | 2.5634 | 0 | 0 | 0.032209 | 0 | 0 | 23.2574 | 3.461% | CZ 2B | 0 | 0 | -0.00045477 | -0.12014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.12059 | 3.461% | CZ 2B | 55.5914 | 21.6622 | -0.049706 | -13.1308 | 0 | 55.5914 | 0 | 83.4627 | 0 | 0 | 26.8364 | 0 | 0 | 0.3372 | 0 | 0 | 230.3009 | 3.461%
CZ 3A | 0.5351 | 0.20949 | -0.00037898 | -0.11585 | 0 | 0.47063 | 0 | 0.74336 | 0 | 0 | 0.25664 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1023 | 16.34% | CZ 3A | 18.0284 | 7.0582 | -0.037898 | -11.5853 | 0 | 15.8564 | 0 | 25.045 | 0 | 0 | 8.6465 | 0 | 0 | 0.10993 | 0 | 0 | 63.1213 | 16.34% | CZ 3A | 5.2823 | 2.0681 | 0 | 0 | 0 | 4.6459 | 0 | 7.3382 | 0 | 0 | 2.5334 | 0 | 0 | 0.032209 | 0 | 0 | 21.9001 | 16.34% | CZ 3A | 0 | 0 | -0.00037898 | -0.11585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11623 | 16.34% | CZ 3A | 55.3007 | 21.6505 | -0.041422 | -12.6627 | 0 | 48.6381 | 0 | 76.8234 | 0 | 0 | 26.5225 | 0 | 0 | 0.3372 | 0 | 0 | 216.5683 | 16.34%
CZ 3B | 0.536 | 0.20949 | -0.00053057 | -0.13332 | 0 | 0.39817 | 0 | 0.82043 | 0 | 0 | 0.26136 | 0 | 0 | 0.0032628 | 0 | 0 | 2.0949 | 10.77% | CZ 3B | 18.0588 | 7.0582 | -0.053057 | -13.3323 | 0 | 13.4152 | 0 | 27.6416 | 0 | 0 | 8.8057 | 0 | 0 | 0.10993 | 0 | 0 | 61.704 | 10.77% | CZ 3B | 5.2912 | 2.0681 | 0 | 0 | 0 | 3.9306 | 0 | 8.099 | 0 | 0 | 2.5801 | 0 | 0 | 0.032209 | 0 | 0 | 22.0012 | 10.77% | CZ 3B | 0 | 0 | -0.00053057 | -0.13332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13385 | 10.77% | CZ 3B | 55.3937 | 21.6505 | -0.057991 | -14.5723 | 0 | 41.15 | 0 | 84.7882 | 0 | 0 | 27.0108 | 0 | 0 | 0.3372 | 0 | 0 | 215.7003 | 10.77%
CZ 3C | 0.53431 | 0.20916 | -0.00072005 | -0.12089 | 0 | 0.23357 | 0 | 0.79376 | 0 | 0 | 0.2599 | 0 | 0 | 0.0032628 | 0 | 0 | 1.9124 | 1.179% | CZ 3C | 18.0019 | 7.0469 | -0.072005 | -12.0893 | 0 | 7.8694 | 0 | 26.7432 | 0 | 0 | 8.7565 | 0 | 0 | 0.10993 | 0 | 0 | 56.3664 | 1.179% | CZ 3C | 5.2746 | 2.0647 | 0 | 0 | 0 | 2.3057 | 0 | 7.8358 | 0 | 0 | 2.5656 | 0 | 0 | 0.032209 | 0 | 0 | 20.0786 | 1.179% | CZ 3C | 0 | 0 | -0.00072005 | -0.12089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.12161 | 1.179% | CZ 3C | 55.2193 | 21.6157 | -0.078702 | -13.2136 | 0 | 24.1388 | 0 | 82.0325 | 0 | 0 | 26.8597 | 0 | 0 | 0.3372 | 0 | 0 | 196.9109 | 1.179%
CZ 4A | 0.53127 | 0.20848 | -0.00053057 | 0.15307 | 0 | 0.32122 | 0 | 0.74043 | 0 | 0 | 0.25956 | 0 | 0 | 0.0032628 | 0 | 0 | 2.2168 | 15.63% | CZ 4A | 17.8996 | 7.0241 | -0.053057 | 15.3068 | 0 | 10.8224 | 0 | 24.9464 | 0 | 0 | 8.7451 | 0 | 0 | 0.10993 | 0 | 0 | 84.8012 | 15.63% | CZ 4A | 5.2446 | 2.0581 | 0 | 0 | 0 | 3.171 | 0 | 7.3093 | 0 | 0 | 2.5623 | 0 | 0 | 0.032209 | 0 | 0 | 20.3774 | 15.63% | CZ 4A | 0 | 0 | -0.00053057 | 0.15307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15254 | 15.63% | CZ 4A | 54.9054 | 21.5459 | -0.057991 | 16.7303 | 0 | 33.1967 | 0 | 76.521 | 0 | 0 | 26.8248 | 0 | 0 | 0.3372 | 0 | 0 | 230.0034 | 15.63%
CZ 4B | 0.53634 | 0.20927 | -0.00018949 | -0.024785 | 0 | 0.27205 | 0 | 0.92877 | 0 | 0 | 0.25821 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1829 | 0.9812% | CZ 4B | 18.0701 | 7.0506 | -0.018949 | -2.4785 | 0 | 9.1658 | 0 | 31.292 | 0 | 0 | 8.6996 | 0 | 0 | 0.10993 | 0 | 0 | 71.8907 | 0.9812% | CZ 4B | 5.2945 | 2.0658 | 0 | 0 | 0 | 2.6856 | 0 | 9.1686 | 0 | 0 | 2.549 | 0 | 0 | 0.032209 | 0 | 0 | 21.7957 | 0.9812% | CZ 4B | 0 | 0 | -0.00018949 | -0.024785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.024974 | 0.9812% | CZ 4B | 55.4286 | 21.6273 | -0.020711 | -2.709 | 0 | 28.1155 | 0 | 95.9856 | 0 | 0 | 26.6853 | 0 | 0 | 0.3372 | 0 | 0 | 225.4497 | 0.9812%
CZ 4C | 0.52992 | 0.20814 | -0.00094744 | 0.15235 | 0 | 0.096534 | 0 | 0.72626 | 0 | 0 | 0.26485 | 0 | 0 | 0.0032628 | 0 | 0 | 1.9804 | 2.427% | CZ 4C | 17.8541 | 7.0127 | -0.094744 | 15.2348 | 0 | 3.2524 | 0 | 24.4688 | 0 | 0 | 8.9232 | 0 | 0 | 0.10993 | 0 | 0 | 76.7612 | 2.427% | CZ 4C | 5.2312 | 2.0547 | 0 | 0 | 0 | 0.95295 | 0 | 7.1694 | 0 | 0 | 2.6145 | 0 | 0 | 0.032209 | 0 | 0 | 18.055 | 2.427% | CZ 4C | 0 | 0 | -0.00094744 | 0.15235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1514 | 2.427% | CZ 4C | 54.7659 | 21.511 | -0.10355 | 16.6516 | 0 | 9.9765 | 0 | 75.056 | 0 | 0 | 27.3713 | 0 | 0 | 0.3372 | 0 | 0 | 205.5659 | 2.427%
CZ 5A | 0.53296 | 0.20904 | -0.00053057 | 0.25255 | 0 | 0.19026 | 0 | 0.70409 | 0 | 0 | 0.26057 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1522 | 20.98% | CZ 5A | 17.9564 | 7.0431 | -0.053057 | 25.2549 | 0 | 6.41 | 0 | 23.722 | 0 | 0 | 8.7792 | 0 | 0 | 0.10993 | 0 | 0 | 89.2225 | 20.98% | CZ 5A | 5.2612 | 2.0636 | 0 | 0 | 0 | 1.8781 | 0 | 6.9506 | 0 | 0 | 2.5723 | 0 | 0 | 0.032209 | 0 | 0 | 18.7581 | 20.98% | CZ 5A | 0 | 0 | -0.00053057 | 0.25255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25202 | 20.98% | CZ 5A | 55.0798 | 21.604 | -0.057991 | 27.6036 | 0 | 19.6622 | 0 | 72.7653 | 0 | 0 | 26.9295 | 0 | 0 | 0.3372 | 0 | 0 | 223.9237 | 20.98%
CZ 5B | 0.53409 | 0.20882 | -0.00011369 | 0.043355 | 0 | 0.20353 | 0 | 0.90065 | 0 | 0 | 0.25787 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1515 | 4.38% | CZ 5B | 17.9943 | 7.0355 | -0.011369 | 4.3355 | 0 | 6.8573 | 0 | 30.3443 | 0 | 0 | 8.6882 | 0 | 0 | 0.10993 | 0 | 0 | 75.3537 | 4.38% | CZ 5B | 5.2723 | 2.0614 | 0 | 0 | 0 | 2.0092 | 0 | 8.8909 | 0 | 0 | 2.5456 | 0 | 0 | 0.032209 | 0 | 0 | 20.8117 | 4.38% | CZ 5B | 0 | 0 | -0.00011369 | 0.043355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043241 | 4.38% | CZ 5B | 55.1961 | 21.5808 | -0.012427 | 4.7387 | 0 | 21.0343 | 0 | 93.0787 | 0 | 0 | 26.6504 | 0 | 0 | 0.3372 | 0 | 0 | 222.6037 | 4.38%
CZ 5C | 0.53037 | 0.20826 | -0.00090954 | 0.34612 | 0 | 0.043992 | 0 | 0.27453 | 0 | 0 | 0.26507 | 0 | 0 | 0.0032628 | 0 | 0 | 1.6707 | 0.01288% | CZ 5C | 17.8692 | 7.0165 | -0.090954 | 34.6118 | 0 | 1.4822 | 0 | 9.2492 | 0 | 0 | 8.9308 | 0 | 0 | 0.10993 | 0 | 0 | 79.1788 | 0.01288% | CZ 5C | 5.2357 | 2.0558 | 0 | 0 | 0 | 0.43427 | 0 | 2.71 | 0 | 0 | 2.6167 | 0 | 0 | 0.032209 | 0 | 0 | 13.0848 | 0.01288% | CZ 5C | 0 | 0 | -0.00090954 | 0.34612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34521 | 0.01288% | CZ 5C | 54.8124 | 21.5226 | -0.099413 | 37.8307 | 0 | 4.5464 | 0 | 28.3713 | 0 | 0 | 27.3946 | 0 | 0 | 0.3372 | 0 | 0 | 174.7157 | 0.01288%
CZ 6A | 0.53668 | 0.20859 | -0.00041687 | 0.36412 | 0 | 0.19453 | 0 | 0.71399 | 0 | 0 | 0.25979 | 0 | 0 | 0.0032628 | 0 | 0 | 2.2805 | 2.983% | CZ 6A | 18.0815 | 7.0279 | -0.041687 | 36.4119 | 0 | 6.5541 | 0 | 24.0556 | 0 | 0 | 8.7527 | 0 | 0 | 0.10993 | 0 | 0 | 100.9519 | 2.983% | CZ 6A | 5.2979 | 2.0592 | 0 | 0 | 0 | 1.9203 | 0 | 7.0483 | 0 | 0 | 2.5645 | 0 | 0 | 0.032209 | 0 | 0 | 18.9224 | 2.983% | CZ 6A | 0 | 0 | -0.00041687 | 0.36412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3637 | 2.983% | CZ 6A | 55.4635 | 21.5575 | -0.045564 | 39.7983 | 0 | 20.1041 | 0 | 73.7886 | 0 | 0 | 26.8481 | 0 | 0 | 0.3372 | 0 | 0 | 237.8516 | 2.983%
CZ 6B | 0.53803 | 0.20859 | -0.00030318 | 0.18873 | 0 | 0.12736 | 0 | 0.84124 | 0 | 0 | 0.26069 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1676 | 0.4478% | CZ 6B | 18.127 | 7.0279 | -0.030318 | 18.873 | 0 | 4.291 | 0 | 28.3429 | 0 | 0 | 8.783 | 0 | 0 | 0.10993 | 0 | 0 | 85.5244 | 0.4478% | CZ 6B | 5.3112 | 2.0592 | 0 | 0 | 0 | 1.2573 | 0 | 8.3045 | 0 | 0 | 2.5734 | 0 | 0 | 0.032209 | 0 | 0 | 19.5377 | 0.4478% | CZ 6B | 0 | 0 | -0.00030318 | 0.18873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18843 | 0.4478% | CZ 6B | 55.603 | 21.5575 | -0.033138 | 20.6282 | 0 | 13.1624 | 0 | 86.9394 | 0 | 0 | 26.9411 | 0 | 0 | 0.3372 | 0 | 0 | 225.1356 | 0.4478%
CZ 7 | 0.53769 | 0.20803 | -0.00045477 | 0.48297 | 0 | 0.15324 | 0 | 0.70207 | 0 | 0 | 0.26114 | 0 | 0 | 0.0032628 | 0 | 0 | 2.3479 | 0.4375% | CZ 7 | 18.1156 | 7.009 | -0.045477 | 48.2966 | 0 | 5.1629 | 0 | 23.6538 | 0 | 0 | 8.7981 | 0 | 0 | 0.10993 | 0 | 0 | 111.1005 | 0.4375% | CZ 7 | 5.3079 | 2.0536 | 0 | 0 | 0 | 1.5127 | 0 | 6.9306 | 0 | 0 | 2.5779 | 0 | 0 | 0.032209 | 0 | 0 | 18.4149 | 0.4375% | CZ 7 | 0 | 0 | -0.00045477 | 0.48297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48251 | 0.4375% | CZ 7 | 55.5682 | 21.4994 | -0.049706 | 52.7882 | 0 | 15.8368 | 0 | 72.556 | 0 | 0 | 26.9876 | 0 | 0 | 0.3372 | 0 | 0 | 245.5236 | 0.4375%
CZ 8 | 0.52992 | 0.20454 | -0.00094744 | 0.64058 | 0 | 0.062893 | 0 | 0.62151 | 0 | 0 | 0.26901 | 0 | 0 | 0.0032628 | 0 | 0 | 2.3308 | 0.03762% | CZ 8 | 17.8541 | 6.8914 | -0.094744 | 64.0582 | 0 | 2.119 | 0 | 20.9397 | 0 | 0 | 9.0635 | 0 | 0 | 0.10993 | 0 | 0 | 120.941 | 0.03762% | CZ 8 | 5.2312 | 2.0192 | 0 | 0 | 0 | 0.62086 | 0 | 6.1353 | 0 | 0 | 2.6556 | 0 | 0 | 0.032209 | 0 | 0 | 16.6944 | 0.03762% | CZ 8 | 0 | 0 | -0.00094744 | 0.64058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63963 | 0.03762% | CZ 8 | 54.7659 | 21.1389 | -0.10355 | 70.0156 | 0 | 6.4998 | 0 | 64.2307 | 0 | 0 | 27.8015 | 0 | 0 | 0.3372 | 0 | 0 | 244.6861 | 0.03762%
US Weighted | 0.53452 | 0.20914 | -0.00037974 | 0.037289 | 0 | 0.41085 | 0 | 0.73149 | 0 | 0 | 0.25748 | 0 | 0 | 0.0032628 | 0 | 0 | 2.1837 | 100% | US Weighted | 18.0088 | 7.0464 | -0.037974 | 3.7289 | 0 | 13.8421 | 0 | 24.6452 | 0 | 0 | 8.675 | 0 | 0 | 0.10993 | 0 | 0 | 76.0185 | 100% | US Weighted | 5.2766 | 2.0646 | 0 | 0 | 0 | 4.0557 | 0 | 7.2211 | 0 | 0 | 2.5418 | 0 | 0 | 0.032209 | 0 | 0 | 21.192 | 100% | US Weighted | 0 | 0 | -0.00037974 | 0.037289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036909 | 100% | US Weighted | 55.2405 | 21.6144 | -0.041506 | 4.0757 | 0 | 42.4596 | 0 | 75.5972 | 0 | 0 | 26.6099 | 0 | 0 | 0.3372 | 0 | 0 | 225.893 | 100%
Building Type: | Quick-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 2501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 2501 | [17 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 63.52% | 67.95% | 0.06625% | -283.4% | 0% | 33.14% | 0% | 37.75% | 0% | 0% | 19.65% | 0% | 0% | 0.07352% | 0% | 0% | 20.27% | 3.013% | CZ 1A | 63.52% | 67.95% | 0.06625% | -283.4% | 0% | 33.14% | 0% | 37.75% | 0% | 0% | 19.65% | 0% | 0% | 0.0408% | 0% | 0% | 13.31% | 3.013% | CZ 1A | 63.52% | 67.95% | 0% | 0% | 0% | 33.14% | 0% | 37.75% | 0% | 0% | 19.65% | 0% | 0% | 0.1241% | 0% | 0% | 26.51% | 3.013% | CZ 1A | 0% | 0% | 0.06625% | -283.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.943% | 3.013% | CZ 1A | 63.52% | 67.95% | 0.06625% | -283.4% | 0% | 33.14% | 0% | 37.75% | 0% | 0% | 19.65% | 0% | 0% | 0.07183% | 0% | 0% | 19.98% | 3.013%
CZ 1B | 63.39% | 67.99% | -0.02205% | -51.57% | 0% | 31.15% | 0% | 38.92% | 0% | 0% | 20.22% | 0% | 0% | 0.07352% | 0% | 0% | 20.6% | 0% | CZ 1B | 63.39% | 67.99% | -0.02205% | -51.57% | 0% | 31.15% | 0% | 38.92% | 0% | 0% | 20.22% | 0% | 0% | 0.0408% | 0% | 0% | 13.53% | 0% | CZ 1B | 63.39% | 67.99% | 0% | 0% | 0% | 31.15% | 0% | 38.92% | 0% | 0% | 20.22% | 0% | 0% | 0.1241% | 0% | 0% | 26.88% | 0% | CZ 1B | 0% | 0% | -0.02205% | -51.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -4.306% | 0% | CZ 1B | 63.39% | 67.99% | -0.02205% | -51.57% | 0% | 31.15% | 0% | 38.92% | 0% | 0% | 20.22% | 0% | 0% | 0.07183% | 0% | 0% | 20.31% | 0%
CZ 2A | 63.57% | 67.98% | -0.006733% | -29.74% | 0% | 32.58% | 0% | 43.32% | 0% | 0% | 20.21% | 0% | 0% | 0.07352% | 0% | 0% | 20% | 16.92% | CZ 2A | 63.57% | 67.98% | -0.006733% | -29.74% | 0% | 32.58% | 0% | 43.32% | 0% | 0% | 20.21% | 0% | 0% | 0.0408% | 0% | 0% | 12.51% | 16.92% | CZ 2A | 63.57% | 67.98% | 0% | 0% | 0% | 32.58% | 0% | 43.32% | 0% | 0% | 20.21% | 0% | 0% | 0.1241% | 0% | 0% | 27.26% | 16.92% | CZ 2A | 0% | 0% | -0.006733% | -29.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.787% | 16.92% | CZ 2A | 63.57% | 67.98% | -0.006733% | -29.74% | 0% | 32.58% | 0% | 43.32% | 0% | 0% | 20.21% | 0% | 0% | 0.07183% | 0% | 0% | 19.69% | 16.92%
CZ 2B | 63.68% | 67.97% | -0.0804% | -31.54% | 0% | 31% | 0% | 45.72% | 0% | 0% | 21.05% | 0% | 0% | 0.07352% | 0% | 0% | 19.83% | 3.461% | CZ 2B | 63.68% | 67.97% | -0.0804% | -31.54% | 0% | 31% | 0% | 45.72% | 0% | 0% | 21.05% | 0% | 0% | 0.0408% | 0% | 0% | 11.97% | 3.461% | CZ 2B | 63.68% | 67.97% | 0% | 0% | 0% | 31% | 0% | 45.72% | 0% | 0% | 21.05% | 0% | 0% | 0.1241% | 0% | 0% | 27.66% | 3.461% | CZ 2B | 0% | 0% | -0.0804% | -31.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -4.377% | 3.461% | CZ 2B | 63.68% | 67.97% | -0.0804% | -31.54% | 0% | 31% | 0% | 45.72% | 0% | 0% | 21.05% | 0% | 0% | 0.07183% | 0% | 0% | 19.49% | 3.461%
CZ 3A | 63.35% | 67.96% | -0.05872% | -12% | 0% | 36.15% | 0% | 49.6% | 0% | 0% | 21% | 0% | 0% | 0.07352% | 0% | 0% | 18.73% | 16.34% | CZ 3A | 63.35% | 67.96% | -0.05872% | -12% | 0% | 36.15% | 0% | 49.6% | 0% | 0% | 21% | 0% | 0% | 0.0408% | 0% | 0% | 10.43% | 16.34% | CZ 3A | 63.35% | 67.96% | 0% | 0% | 0% | 36.15% | 0% | 49.6% | 0% | 0% | 21% | 0% | 0% | 0.1241% | 0% | 0% | 28.42% | 16.34% | CZ 3A | 0% | 0% | -0.05872% | -12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.399% | 16.34% | CZ 3A | 63.35% | 67.96% | -0.05872% | -12% | 0% | 36.15% | 0% | 49.6% | 0% | 0% | 21% | 0% | 0% | 0.07183% | 0% | 0% | 18.35% | 16.34%
CZ 3B | 63.45% | 67.96% | -0.08503% | -20.76% | 0% | 33.36% | 0% | 48.78% | 0% | 0% | 21.31% | 0% | 0% | 0.07352% | 0% | 0% | 19.11% | 10.77% | CZ 3B | 63.45% | 67.96% | -0.08503% | -20.76% | 0% | 33.36% | 0% | 48.78% | 0% | 0% | 21.31% | 0% | 0% | 0.0408% | 0% | 0% | 10.77% | 10.77% | CZ 3B | 63.45% | 67.96% | 0% | 0% | 0% | 33.36% | 0% | 48.78% | 0% | 0% | 21.31% | 0% | 0% | 0.1241% | 0% | 0% | 28.27% | 10.77% | CZ 3B | 0% | 0% | -0.08503% | -20.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -4.354% | 10.77% | CZ 3B | 63.45% | 67.96% | -0.08503% | -20.76% | 0% | 33.36% | 0% | 48.78% | 0% | 0% | 21.31% | 0% | 0% | 0.07183% | 0% | 0% | 18.74% | 10.77%
CZ 3C | 63.25% | 67.85% | -0.1101% | -18.22% | 0% | 55.84% | 0% | 57.36% | 0% | 0% | 21.17% | 0% | 0% | 0.07352% | 0% | 0% | 19.24% | 1.179% | CZ 3C | 63.25% | 67.85% | -0.1101% | -18.22% | 0% | 55.84% | 0% | 57.36% | 0% | 0% | 21.17% | 0% | 0% | 0.0408% | 0% | 0% | 10.4% | 1.179% | CZ 3C | 63.25% | 67.85% | 0% | 0% | 0% | 55.84% | 0% | 57.36% | 0% | 0% | 21.17% | 0% | 0% | 0.1241% | 0% | 0% | 29.85% | 1.179% | CZ 3C | 0% | 0% | -0.1101% | -18.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.89% | 1.179% | CZ 3C | 63.25% | 67.85% | -0.1101% | -18.22% | 0% | 55.84% | 0% | 57.36% | 0% | 0% | 21.17% | 0% | 0% | 0.07183% | 0% | 0% | 18.83% | 1.179%
CZ 4A | 62.89% | 67.73% | -0.07467% | 8.612% | 0% | 40.58% | 0% | 53.66% | 0% | 0% | 21.45% | 0% | 0% | 0.07352% | 0% | 0% | 19.34% | 15.63% | CZ 4A | 62.89% | 67.73% | -0.07467% | 8.612% | 0% | 40.58% | 0% | 53.66% | 0% | 0% | 21.45% | 0% | 0% | 0.0408% | 0% | 0% | 12.64% | 15.63% | CZ 4A | 62.89% | 67.73% | 0% | 0% | 0% | 40.58% | 0% | 53.66% | 0% | 0% | 21.45% | 0% | 0% | 0.1241% | 0% | 0% | 28.81% | 15.63% | CZ 4A | 0% | 0% | -0.07467% | 8.612% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.551% | 15.63% | CZ 4A | 62.89% | 67.73% | -0.07467% | 8.612% | 0% | 40.58% | 0% | 53.66% | 0% | 0% | 21.45% | 0% | 0% | 0.07183% | 0% | 0% | 19.01% | 15.63%
CZ 4B | 63.49% | 67.93% | -0.02739% | -2.277% | 0% | 38.4% | 0% | 56.68% | 0% | 0% | 21.26% | 0% | 0% | 0.07352% | 0% | 0% | 19.97% | 0.9812% | CZ 4B | 63.49% | 67.93% | -0.02739% | -2.277% | 0% | 38.4% | 0% | 56.68% | 0% | 0% | 21.26% | 0% | 0% | 0.0408% | 0% | 0% | 11.86% | 0.9812% | CZ 4B | 63.49% | 67.93% | 0% | 0% | 0% | 38.4% | 0% | 56.68% | 0% | 0% | 21.26% | 0% | 0% | 0.1241% | 0% | 0% | 30.06% | 0.9812% | CZ 4B | 0% | 0% | -0.02739% | -2.277% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.6959% | 0.9812% | CZ 4B | 63.49% | 67.93% | -0.02739% | -2.277% | 0% | 38.4% | 0% | 56.68% | 0% | 0% | 21.26% | 0% | 0% | 0.07183% | 0% | 0% | 19.58% | 0.9812%
CZ 4C | 62.73% | 67.69% | -0.1298% | 9.373% | 0% | 52.35% | 0% | 56.67% | 0% | 0% | 21.93% | 0% | 0% | 0.07352% | 0% | 0% | 18.65% | 2.427% | CZ 4C | 62.73% | 67.69% | -0.1298% | 9.373% | 0% | 52.35% | 0% | 56.67% | 0% | 0% | 21.93% | 0% | 0% | 0.0408% | 0% | 0% | 12.11% | 2.427% | CZ 4C | 62.73% | 67.69% | 0% | 0% | 0% | 52.35% | 0% | 56.67% | 0% | 0% | 21.93% | 0% | 0% | 0.1241% | 0% | 0% | 28.33% | 2.427% | CZ 4C | 0% | 0% | -0.1298% | 9.373% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.636% | 2.427% | CZ 4C | 62.73% | 67.69% | -0.1298% | 9.373% | 0% | 52.35% | 0% | 56.67% | 0% | 0% | 21.93% | 0% | 0% | 0.07183% | 0% | 0% | 18.32% | 2.427%
CZ 5A | 63.09% | 67.88% | -0.06932% | 10.14% | 0% | 44.69% | 0% | 53.7% | 0% | 0% | 21.66% | 0% | 0% | 0.07352% | 0% | 0% | 18.26% | 20.98% | CZ 5A | 63.09% | 67.88% | -0.06932% | 10.14% | 0% | 44.69% | 0% | 53.7% | 0% | 0% | 21.66% | 0% | 0% | 0.0408% | 0% | 0% | 12.17% | 20.98% | CZ 5A | 63.09% | 67.88% | 0% | 0% | 0% | 44.69% | 0% | 53.7% | 0% | 0% | 21.66% | 0% | 0% | 0.1241% | 0% | 0% | 28.27% | 20.98% | CZ 5A | 0% | 0% | -0.06932% | 10.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.977% | 20.98% | CZ 5A | 63.09% | 67.88% | -0.06932% | 10.14% | 0% | 44.69% | 0% | 53.7% | 0% | 0% | 21.66% | 0% | 0% | 0.07183% | 0% | 0% | 17.94% | 20.98%
CZ 5B | 63.23% | 67.81% | -0.01517% | 2.518% | 0% | 40.24% | 0% | 56.94% | 0% | 0% | 21.37% | 0% | 0% | 0.07352% | 0% | 0% | 18.94% | 4.38% | CZ 5B | 63.23% | 67.81% | -0.01517% | 2.518% | 0% | 40.24% | 0% | 56.94% | 0% | 0% | 21.37% | 0% | 0% | 0.0408% | 0% | 0% | 11.31% | 4.38% | CZ 5B | 63.23% | 67.81% | 0% | 0% | 0% | 40.24% | 0% | 56.94% | 0% | 0% | 21.37% | 0% | 0% | 0.1241% | 0% | 0% | 29.79% | 4.38% | CZ 5B | 0% | 0% | -0.01517% | 2.518% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.01% | 4.38% | CZ 5B | 63.23% | 67.81% | -0.01517% | 2.518% | 0% | 40.24% | 0% | 56.94% | 0% | 0% | 21.37% | 0% | 0% | 0.07183% | 0% | 0% | 18.56% | 4.38%
CZ 5C | 62.79% | 67.73% | -0.1195% | 17% | 0% | 61.29% | 0% | 23.24% | 0% | 0% | 22.04% | 0% | 0% | 0.07352% | 0% | 0% | 15.41% | 0.01288% | CZ 5C | 62.79% | 67.73% | -0.1195% | 17% | 0% | 61.29% | 0% | 23.24% | 0% | 0% | 22.04% | 0% | 0% | 0.0408% | 0% | 0% | 11.8% | 0.01288% | CZ 5C | 62.79% | 67.73% | 0% | 0% | 0% | 61.29% | 0% | 23.24% | 0% | 0% | 22.04% | 0% | 0% | 0.1241% | 0% | 0% | 21.25% | 0.01288% | CZ 5C | 0% | 0% | -0.1195% | 17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.495% | 0.01288% | CZ 5C | 62.79% | 67.73% | -0.1195% | 17% | 0% | 61.29% | 0% | 23.24% | 0% | 0% | 22.04% | 0% | 0% | 0.07183% | 0% | 0% | 15.22% | 0.01288%
CZ 6A | 63.53% | 67.79% | -0.05173% | 11.31% | 0% | 40.67% | 0% | 52.9% | 0% | 0% | 21.65% | 0% | 0% | 0.07352% | 0% | 0% | 18.04% | 2.983% | CZ 6A | 63.53% | 67.79% | -0.05173% | 11.31% | 0% | 40.67% | 0% | 52.9% | 0% | 0% | 21.65% | 0% | 0% | 0.0408% | 0% | 0% | 12.42% | 2.983% | CZ 6A | 63.53% | 67.79% | 0% | 0% | 0% | 40.67% | 0% | 52.9% | 0% | 0% | 21.65% | 0% | 0% | 0.1241% | 0% | 0% | 28.15% | 2.983% | CZ 6A | 0% | 0% | -0.05173% | 11.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.234% | 2.983% | CZ 6A | 63.53% | 67.79% | -0.05173% | 11.31% | 0% | 40.67% | 0% | 52.9% | 0% | 0% | 21.65% | 0% | 0% | 0.07183% | 0% | 0% | 17.73% | 2.983%
CZ 6B | 63.69% | 67.84% | -0.03811% | 7.531% | 0% | 40.17% | 0% | 56.5% | 0% | 0% | 21.74% | 0% | 0% | 0.07352% | 0% | 0% | 18.22% | 0.4478% | CZ 6B | 63.69% | 67.84% | -0.03811% | 7.531% | 0% | 40.17% | 0% | 56.5% | 0% | 0% | 21.74% | 0% | 0% | 0.0408% | 0% | 0% | 11.56% | 0.4478% | CZ 6B | 63.69% | 67.84% | 0% | 0% | 0% | 40.17% | 0% | 56.5% | 0% | 0% | 21.74% | 0% | 0% | 0.1241% | 0% | 0% | 29.16% | 0.4478% | CZ 6B | 0% | 0% | -0.03811% | 7.531% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.687% | 0.4478% | CZ 6B | 63.69% | 67.84% | -0.03811% | 7.531% | 0% | 40.17% | 0% | 56.5% | 0% | 0% | 21.74% | 0% | 0% | 0.07183% | 0% | 0% | 17.87% | 0.4478%
CZ 7 | 63.65% | 67.68% | -0.05325% | 12.08% | 0% | 45.95% | 0% | 53.25% | 0% | 0% | 21.83% | 0% | 0% | 0.07352% | 0% | 0% | 17.67% | 0.4375% | CZ 7 | 63.65% | 67.68% | -0.05325% | 12.08% | 0% | 45.95% | 0% | 53.25% | 0% | 0% | 21.83% | 0% | 0% | 0.0408% | 0% | 0% | 12.49% | 0.4375% | CZ 7 | 63.65% | 67.68% | 0% | 0% | 0% | 45.95% | 0% | 53.25% | 0% | 0% | 21.83% | 0% | 0% | 0.1241% | 0% | 0% | 28.14% | 0.4375% | CZ 7 | 0% | 0% | -0.05325% | 12.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.245% | 0.4375% | CZ 7 | 63.65% | 67.68% | -0.05325% | 12.08% | 0% | 45.95% | 0% | 53.25% | 0% | 0% | 21.83% | 0% | 0% | 0.07183% | 0% | 0% | 17.37% | 0.4375%
CZ 8 | 62.73% | 66.91% | -0.1031% | 11.84% | 0% | 60.04% | 0% | 51.75% | 0% | 0% | 22.52% | 0% | 0% | 0.07352% | 0% | 0% | 16.17% | 0.03762% | CZ 8 | 62.73% | 66.91% | -0.1031% | 11.84% | 0% | 60.04% | 0% | 51.75% | 0% | 0% | 22.52% | 0% | 0% | 0.0408% | 0% | 0% | 11.8% | 0.03762% | CZ 8 | 62.73% | 66.91% | 0% | 0% | 0% | 60.04% | 0% | 51.75% | 0% | 0% | 22.52% | 0% | 0% | 0.1241% | 0% | 0% | 26.93% | 0.03762% | CZ 8 | 0% | 0% | -0.1031% | 11.84% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.861% | 0.03762% | CZ 8 | 62.73% | 66.91% | -0.1031% | 11.84% | 0% | 60.04% | 0% | 51.75% | 0% | 0% | 22.52% | 0% | 0% | 0.07183% | 0% | 0% | 15.91% | 0.03762%
US Weighted | 63.28% | 67.89% | -0.05656% | 2.741% | 0% | 35.56% | 0% | 50.06% | 0% | 0% | 21.13% | 0% | 0% | 0.07352% | 0% | 0% | 19.06% | 100% | US Weighted | 63.28% | 67.89% | -0.05656% | 2.741% | 0% | 35.56% | 0% | 50.06% | 0% | 0% | 21.13% | 0% | 0% | 0.0408% | 0% | 0% | 11.87% | 100% | US Weighted | 63.28% | 67.89% | 0% | 0% | 0% | 35.56% | 0% | 50.06% | 0% | 0% | 21.13% | 0% | 0% | 0.1241% | 0% | 0% | 28.18% | 100% | US Weighted | 0% | 0% | -0.05656% | 2.741% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.9611% | 100% | US Weighted | 63.28% | 67.89% | -0.05656% | 2.741% | 0% | 35.56% | 0% | 50.06% | 0% | 0% | 21.13% | 0% | 0% | 0.07183% | 0% | 0% | 18.72% | 100%

## RestFS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Full-service Restaurant | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.2851 | 0.09532 | 0.91773 | 0.81467 | 0 | 0.61795 | 0 | 0.51877 | 0 | 0.0023014 | 0.42917 | 0 | 0 | 2.9421 | 0 | 0 | 6.6231 |  | STD2016 | 9.6055 | 3.2115 | 66.1897 | 81.4672 | 0 | 20.8198 | 0 | 17.4782 | 0 | 0.077539 | 14.4593 | 0 | 0 | 152.7879 | 0 | 0 | 366.0967 |  | STD2016 | 2.8144 | 0.94097 | 3.8088 | 0 | 0 | 6.1002 | 0 | 5.1211 | 0 | 0.022719 | 4.2366 | 0 | 0 | 21.0545 | 0 | 0 | 44.0993 |  | STD2016 | 0 | 0 | 0.5319 | 0.81467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1559 |  | STD2016 | 29.4642 | 9.851 | 98.0114 | 89.0436 | 0 | 63.8629 | 0 | 53.613 | 0 | 0.23785 | 44.3528 | 0 | 0 | 308.8753 | 0 | 0 | 697.3122
STD2013 | 0.36468 | 0.16886 | 0.91804 | 0.80978 | 0 | 0.62673 | 0 | 0.52415 | 0 | 0.0023014 | 0.42933 | 0 | 0 | 2.9421 | 0 | 0 | 6.786 |  | STD2013 | 12.2867 | 5.6893 | 66.2199 | 80.9781 | 0 | 21.1158 | 0 | 17.6596 | 0 | 0.077539 | 14.4649 | 0 | 0 | 152.7879 | 0 | 0 | 371.2798 |  | STD2013 | 3.6 | 1.667 | 3.8088 | 0 | 0 | 6.1869 | 0 | 5.1743 | 0 | 0.022719 | 4.2382 | 0 | 0 | 21.0545 | 0 | 0 | 45.7524 |  | STD2013 | 0 | 0 | 0.53221 | 0.80978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1513 |  | STD2013 | 37.6885 | 17.4515 | 98.0443 | 88.509 | 0 | 64.7709 | 0 | 54.1694 | 0 | 0.23785 | 44.37 | 0 | 0 | 308.8753 | 0 | 0 | 714.1168
STD2010 | 0.39218 | 0.16886 | 0.91799 | 0.84055 | 0 | 0.6705 | 0 | 0.79228 | 0 | 0.0023014 | 0.54646 | 0 | 0 | 2.9429 | 0 | 0 | 7.2741 |  | STD2010 | 13.2131 | 5.6893 | 66.2157 | 84.0554 | 0 | 22.5901 | 0 | 26.6933 | 0 | 0.077539 | 18.4111 | 0 | 0 | 152.8155 | 0 | 0 | 389.7611 |  | STD2010 | 3.8714 | 1.667 | 3.8088 | 0 | 0 | 6.6189 | 0 | 7.8211 | 0 | 0.022719 | 5.3945 | 0 | 0 | 21.0625 | 0 | 0 | 50.2669 |  | STD2010 | 0 | 0 | 0.53217 | 0.84055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.182 |  | STD2010 | 40.53 | 17.4515 | 98.0396 | 91.8725 | 0 | 69.2934 | 0 | 81.8796 | 0 | 0.23785 | 56.4746 | 0 | 0 | 308.9599 | 0 | 0 | 764.7389
STD2007 | 0.94947 | 0.29693 | 0.92972 | 0.86576 | 0 | 0.97855 | 0 | 1.2692 | 0 | 0.0023014 | 0.54481 | 0 | 0 | 2.945 | 0 | 0 | 8.7817 |  | STD2007 | 31.9893 | 10.004 | 66.6533 | 86.5756 | 0 | 32.969 | 0 | 42.76 | 0 | 0.077539 | 18.3555 | 0 | 0 | 152.8844 | 0 | 0 | 442.2687 |  | STD2007 | 9.3729 | 2.9312 | 3.9182 | 0 | 0 | 9.6599 | 0 | 12.5287 | 0 | 0.022719 | 5.3782 | 0 | 0 | 21.0827 | 0 | 0 | 64.8945 |  | STD2007 | 0 | 0 | 0.53281 | 0.86576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2079 |  | STD2007 | 98.1244 | 30.6864 | 99.2552 | 94.6272 | 0 | 101.1297 | 0 | 131.1629 | 0 | 0.23785 | 56.3041 | 0 | 0 | 309.1713 | 0 | 0 | 920.699
STD2004 | 0.94947 | 0.29693 | 0.92814 | 1.0548 | 0 | 1.0686 | 0 | 1.3067 | 0 | 0.0023014 | 0.5525 | 0 | 0 | 2.945 | 0 | 0 | 9.1044 |  | STD2004 | 31.9893 | 10.004 | 66.5328 | 105.4827 | 0 | 36.0027 | 0 | 44.0252 | 0 | 0.077539 | 18.6145 | 0 | 0 | 152.8844 | 0 | 0 | 465.6131 |  | STD2004 | 9.3729 | 2.9312 | 3.9126 | 0 | 0 | 10.5488 | 0 | 12.8994 | 0 | 0.022719 | 5.4541 | 0 | 0 | 21.0827 | 0 | 0 | 66.2244 |  | STD2004 | 0 | 0 | 0.53179 | 1.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3959 |  | STD2004 | 98.1244 | 30.6864 | 99.0862 | 115.2926 | 0 | 110.4354 | 0 | 135.0436 | 0 | 0.23785 | 57.0985 | 0 | 0 | 309.1713 | 0 | 0 | 955.1762
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -0.0015768 | 0.18907 | 0 | 0.090044 | 0 | 0.037551 | 0 | 0 | 0.007686 | 0 | 0 | 0 | 0 | 0 | 0.32277 |  | 2004-2007 | 0 | 0 | -0.12047 | 18.9071 | 0 | 3.0337 | 0 | 1.2651 | 0 | 0 | 0.25895 | 0 | 0 | 0 | 0 | 0 | 23.3444 |  | 2004-2007 | 0 | 0 | -0.005539 | 0 | 0 | 0.88888 | 0 | 0.37069 | 0 | 0 | 0.075874 | 0 | 0 | 0 | 0 | 0 | 1.3299 |  | 2004-2007 | 0 | 0 | -0.0010157 | 0.18907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18806 |  | 2004-2007 | 0 | 0 | -0.169 | 20.6654 | 0 | 9.3057 | 0 | 3.8807 | 0 | 0 | 0.79432 | 0 | 0 | 0 | 0 | 0 | 34.4772
2007-2010 | 0.55729 | 0.12806 | 0.011726 | 0.025203 | 0 | 0.30805 | 0 | 0.47687 | 0 | 0 | -0.0016496 | 0 | 0 | 0.0020457 | 0 | 0 | 1.5076 |  | 2007-2010 | 18.7762 | 4.3146 | 0.43751 | 2.5203 | 0 | 10.3789 | 0 | 16.0667 | 0 | 0 | -0.055576 | 0 | 0 | 0.068924 | 0 | 0 | 52.5075 |  | 2007-2010 | 5.5014 | 1.2642 | 0.10943 | 0 | 0 | 3.041 | 0 | 4.7075 | 0 | 0 | -0.016284 | 0 | 0 | 0.020195 | 0 | 0 | 14.6275 |  | 2007-2010 | 0 | 0 | 0.00064024 | 0.025203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025843 |  | 2007-2010 | 57.5944 | 13.2348 | 1.2156 | 2.7546 | 0 | 31.8364 | 0 | 49.2833 | 0 | 0 | -0.17048 | 0 | 0 | 0.21142 | 0 | 0 | 155.9601
2010-2013 | 0.027495 | 0 | -4.3645e-05 | 0.030773 | 0 | 0.043761 | 0 | 0.26813 | 0 | 0 | 0.11713 | 0 | 0 | 0.00081829 | 0 | 0 | 0.48806 |  | 2010-2013 | 0.92636 | 0 | -0.0041669 | 3.0773 | 0 | 1.4744 | 0 | 9.0337 | 0 | 0 | 3.9462 | 0 | 0 | 0.02757 | 0 | 0 | 18.4813 |  | 2010-2013 | 0.27142 | 0 | -2.941e-05 | 0 | 0 | 0.43199 | 0 | 2.6469 | 0 | 0 | 1.1562 | 0 | 0 | 0.0080779 | 0 | 0 | 4.5146 |  | 2010-2013 | 0 | 0 | -4.0665e-05 | 0.030773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030732 |  | 2010-2013 | 2.8415 | 0 | -0.0047526 | 3.3635 | 0 | 4.5225 | 0 | 27.7102 | 0 | 0 | 12.1046 | 0 | 0 | 0.084567 | 0 | 0 | 50.6221
2013-2016 | 0.079579 | 0.073544 | 0.00030158 | -0.004891 | 0 | 0.0087851 | 0 | 0.0053839 | 0 | 0 | 0.00016632 | 0 | 0 | 0 | 0 | 0 | 0.16287 |  | 2013-2016 | 2.6812 | 2.4778 | 0.030174 | -0.4891 | 0 | 0.29598 | 0 | 0.18139 | 0 | 0 | 0.0056037 | 0 | 0 | 0 | 0 | 0 | 5.183 |  | 2013-2016 | 0.78558 | 0.726 | -2.4521e-06 | 0 | 0 | 0.086723 | 0 | 0.053148 | 0 | 0 | 0.0016419 | 0 | 0 | 0 | 0 | 0 | 1.6531 |  | 2013-2016 | 0 | 0 | 0.00030183 | -0.004891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0045892 |  | 2013-2016 | 8.2243 | 7.6005 | 0.032964 | -0.53459 | 0 | 0.90791 | 0 | 0.55641 | 0 | 0 | 0.017189 | 0 | 0 | 0 | 0 | 0 | 16.8046
2004-2016 | 0.66437 | 0.20161 | 0.010407 | 0.24016 | 0 | 0.45064 | 0 | 0.78794 | 0 | 0 | 0.12333 | 0 | 0 | 0.002864 | 0 | 0 | 2.4813 |  | 2004-2016 | 22.3837 | 6.7925 | 0.34304 | 24.0155 | 0 | 15.183 | 0 | 26.547 | 0 | 0 | 4.1552 | 0 | 0 | 0.096493 | 0 | 0 | 99.5163 |  | 2004-2016 | 6.5584 | 1.9902 | 0.10386 | 0 | 0 | 4.4486 | 0 | 7.7783 | 0 | 0 | 1.2175 | 0 | 0 | 0.028273 | 0 | 0 | 22.1251 |  | 2004-2016 | 0 | 0 | -0.00011429 | 0.24016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24004 |  | 2004-2016 | 68.6602 | 20.8353 | 1.0748 | 26.249 | 0 | 46.5725 | 0 | 81.4306 | 0 | 0 | 12.7456 | 0 | 0 | 0.29599 | 0 | 0 | 257.864
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.1699% | 17.92% |  | 8.426% |  | 2.874% |  | 0% | 1.391% |  |  | 0% |  |  | 3.545% |  | 2004-2007 | 0% | 0% | -0.1811% | 17.92% |  | 8.426% |  | 2.874% |  | 0% | 1.391% |  |  | 0% |  |  | 5.014% |  | 2004-2007 | 0% | 0% | -0.1416% |  |  | 8.426% |  | 2.874% |  | 0% | 1.391% |  |  | 0% |  |  | 2.008% |  | 2004-2007 |  |  | -0.191% | 17.92% | [9 empty] | 0% |  |  | 7.849% |  | 2004-2007 | 0% | 0% | -0.1706% | 17.92% |  | 8.426% |  | 2.874% |  | 0% | 1.391% |  |  | 0% |  |  | 3.61%
2007-2010 | 58.7% | 43.13% | 1.261% | 2.911% |  | 31.48% |  | 37.57% |  | 0% | -0.3028% |  |  | 0.06946% |  |  | 17.17% |  | 2007-2010 | 58.7% | 43.13% | 0.6564% | 2.911% |  | 31.48% |  | 37.57% |  | 0% | -0.3028% |  |  | 0.04508% |  |  | 11.87% |  | 2007-2010 | 58.7% | 43.13% | 2.793% |  |  | 31.48% |  | 37.57% |  | 0% | -0.3028% |  |  | 0.09579% |  |  | 22.54% |  | 2007-2010 |  |  | 0.1202% | 2.911% | [9 empty] | 0% |  |  | 1.17% |  | 2007-2010 | 58.7% | 43.13% | 1.225% | 2.911% |  | 31.48% |  | 37.57% |  | 0% | -0.3028% |  |  | 0.06838% |  |  | 16.94%
2010-2013 | 7.011% | 0% | -0.004754% | 3.661% |  | 6.527% |  | 33.84% |  | 0% | 21.43% |  |  | 0.02781% |  |  | 6.71% |  | 2010-2013 | 7.011% | 0% | -0.006293% | 3.661% |  | 6.527% |  | 33.84% |  | 0% | 21.43% |  |  | 0.01804% |  |  | 4.742% |  | 2010-2013 | 7.011% | 0% | -0.0007722% |  |  | 6.527% |  | 33.84% |  | 0% | 21.43% |  |  | 0.03835% |  |  | 8.981% |  | 2010-2013 |  |  | -0.007641% | 3.661% | [9 empty] | 0% |  |  | 1.408% |  | 2010-2013 | 7.011% | 0% | -0.004848% | 3.661% |  | 6.527% |  | 33.84% |  | 0% | 21.43% |  |  | 0.02737% |  |  | 6.62%
2013-2016 | 21.82% | 43.55% | 0.03285% | -0.604% |  | 1.402% |  | 1.027% |  | 0% | 0.03874% |  |  | 0% |  |  | 2.4% |  | 2013-2016 | 21.82% | 43.55% | 0.04557% | -0.604% |  | 1.402% |  | 1.027% |  | 0% | 0.03874% |  |  | 0% |  |  | 1.396% |  | 2013-2016 | 21.82% | 43.55% | -6.438e-05% |  |  | 1.402% |  | 1.027% |  | 0% | 0.03874% |  |  | 0% |  |  | 3.613% |  | 2013-2016 |  |  | 0.05671% | -0.604% | [9 empty] | 0% |  |  | -0.2133% |  | 2013-2016 | 21.82% | 43.55% | 0.03362% | -0.604% |  | 1.402% |  | 1.027% |  | 0% | 0.03874% |  |  | 0% |  |  | 2.353%
2004-2016 | 69.97% | 67.9% | 1.121% | 22.77% |  | 42.17% |  | 60.3% |  | 0% | 22.32% |  |  | 0.09725% |  |  | 27.25% |  | 2004-2016 | 69.97% | 67.9% | 0.5156% | 22.77% |  | 42.17% |  | 60.3% |  | 0% | 22.32% |  |  | 0.06312% |  |  | 21.37% |  | 2004-2016 | 69.97% | 67.9% | 2.654% |  |  | 42.17% |  | 60.3% |  | 0% | 22.32% |  |  | 0.1341% |  |  | 33.41% |  | 2004-2016 |  |  | -0.02149% | 22.77% | [9 empty] | 0% |  |  | 10.02% |  | 2004-2016 | 69.97% | 67.9% | 1.085% | 22.77% |  | 42.17% |  | 60.3% |  | 0% | 22.32% |  |  | 0.09574% |  |  | 27%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.28379 | 0.095279 | 0.79029 | 0.02193 | 0 | 1.4981 | 0 | 0.60727 | 0 | 0.0023014 | 0.4408 | 0 | 0 | 2.9421 | 0 | 0 | 6.6819 | 2.444% | CZ 1A | 9.5615 | 3.2101 | 53.463 | 2.193 | 0 | 50.4729 | 0 | 20.46 | 0 | 0.077539 | 14.8514 | 0 | 0 | 152.7879 | 0 | 0 | 307.0773 | 2.444% | CZ 1A | 2.8015 | 0.94057 | 3.8062 | 0 | 0 | 14.7886 | 0 | 5.9948 | 0 | 0.022719 | 4.3514 | 0 | 0 | 21.0545 | 0 | 0 | 53.7602 | 2.444% | CZ 1A | 0 | 0 | 0.40473 | 0.02193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.236 | 2.444% | CZ 1A | 29.329 | 9.8468 | 84.0836 | 2.3969 | 0 | 154.8215 | 0 | 62.7595 | 0 | 0.23785 | 45.5553 | 0 | 0 | 308.8753 | 0 | 0 | 697.9056 | 2.444%
CZ 1B | 0.28461 | 0.095126 | 0.79109 | 0.12353 | 0 | 1.8402 | 0 | 0.92497 | 0 | 0.0023014 | 0.44085 | 0 | 0 | 2.9421 | 0 | 0 | 7.4448 | 0% | CZ 1B | 9.589 | 3.205 | 53.5422 | 12.3533 | 0 | 62.0004 | 0 | 31.1639 | 0 | 0.077539 | 14.8531 | 0 | 0 | 152.7879 | 0 | 0 | 339.5724 | 0% | CZ 1B | 2.8096 | 0.93905 | 3.8062 | 0 | 0 | 18.1661 | 0 | 9.131 | 0 | 0.022719 | 4.352 | 0 | 0 | 21.0545 | 0 | 0 | 60.2811 | 0% | CZ 1B | 0 | 0 | 0.40552 | 0.12353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3383 | 0% | CZ 1B | 29.4135 | 9.8309 | 84.1702 | 13.5022 | 0 | 190.1811 | 0 | 95.5927 | 0 | 0.23785 | 45.5606 | 0 | 0 | 308.8753 | 0 | 0 | 777.3644 | 0%
CZ 2A | 0.28318 | 0.095075 | 0.82883 | 0.2167 | 0 | 1.297 | 0 | 0.56395 | 0 | 0.0023014 | 0.43876 | 0 | 0 | 2.9421 | 0 | 0 | 6.6679 | 17.24% | CZ 2A | 9.5408 | 3.2032 | 57.3132 | 21.6696 | 0 | 43.6994 | 0 | 19.0006 | 0 | 0.077539 | 14.7824 | 0 | 0 | 152.7879 | 0 | 0 | 322.0746 | 17.24% | CZ 2A | 2.7954 | 0.93855 | 3.8067 | 0 | 0 | 12.8039 | 0 | 5.5672 | 0 | 0.022719 | 4.3313 | 0 | 0 | 21.0545 | 0 | 0 | 51.3202 | 17.24% | CZ 2A | 0 | 0 | 0.44321 | 0.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4692 | 17.24% | CZ 2A | 29.2655 | 9.8257 | 88.2952 | 23.6848 | 0 | 134.0443 | 0 | 58.2827 | 0 | 0.23785 | 45.3439 | 0 | 0 | 308.8753 | 0 | 0 | 697.8553 | 17.24%
CZ 2B | 0.28216 | 0.095177 | 0.83158 | 0.21154 | 0 | 0.98461 | 0 | 0.84903 | 0 | 0.0023014 | 0.43364 | 0 | 0 | 2.9421 | 0 | 0 | 6.6321 | 3.722% | CZ 2B | 9.5063 | 3.2067 | 57.5819 | 21.1545 | 0 | 33.173 | 0 | 28.6051 | 0 | 0.077539 | 14.6101 | 0 | 0 | 152.7879 | 0 | 0 | 320.7031 | 3.722% | CZ 2B | 2.7854 | 0.93956 | 3.8077 | 0 | 0 | 9.7197 | 0 | 8.3813 | 0 | 0.022719 | 4.2808 | 0 | 0 | 21.0545 | 0 | 0 | 50.9916 | 3.722% | CZ 2B | 0 | 0 | 0.44586 | 0.21154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4667 | 3.722% | CZ 2B | 29.1598 | 9.8362 | 88.5957 | 23.1218 | 0 | 101.7555 | 0 | 87.7438 | 0 | 0.23785 | 44.8153 | 0 | 0 | 308.8753 | 0 | 0 | 694.1415 | 3.722%
CZ 3A | 0.28568 | 0.095177 | 0.89517 | 0.6188 | 0 | 0.69227 | 0 | 0.50197 | 0 | 0.0023014 | 0.43124 | 0 | 0 | 2.9421 | 0 | 0 | 6.4647 | 18.17% | CZ 3A | 9.6252 | 3.2067 | 63.9369 | 61.8803 | 0 | 23.3238 | 0 | 16.9122 | 0 | 0.077539 | 14.5291 | 0 | 0 | 152.7879 | 0 | 0 | 346.2796 | 18.17% | CZ 3A | 2.8202 | 0.93956 | 3.8082 | 0 | 0 | 6.8339 | 0 | 4.9553 | 0 | 0.022719 | 4.257 | 0 | 0 | 21.0545 | 0 | 0 | 44.6913 | 18.17% | CZ 3A | 0 | 0 | 0.5094 | 0.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9375 | 18.17% | CZ 3A | 29.5245 | 9.8362 | 95.5451 | 67.6352 | 0 | 71.5439 | 0 | 51.8767 | 0 | 0.23785 | 44.5669 | 0 | 0 | 308.8753 | 0 | 0 | 679.6417 | 18.17%
CZ 3B | 0.2843 | 0.095177 | 0.87842 | 0.36762 | 0 | 0.69386 | 0 | 0.78106 | 0 | 0.0023014 | 0.43016 | 0 | 0 | 2.9421 | 0 | 0 | 6.475 | 7.194% | CZ 3B | 9.5787 | 3.2067 | 62.2624 | 36.7619 | 0 | 23.3772 | 0 | 26.3151 | 0 | 0.077539 | 14.493 | 0 | 0 | 152.7879 | 0 | 0 | 328.8605 | 7.194% | CZ 3B | 2.8066 | 0.93956 | 3.8082 | 0 | 0 | 6.8495 | 0 | 7.7103 | 0 | 0.022719 | 4.2464 | 0 | 0 | 21.0545 | 0 | 0 | 47.4378 | 7.194% | CZ 3B | 0 | 0 | 0.49265 | 0.36762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6696 | 7.194% | CZ 3B | 29.3818 | 9.8362 | 93.7149 | 40.1808 | 0 | 71.7077 | 0 | 80.7194 | 0 | 0.23785 | 44.4559 | 0 | 0 | 308.8753 | 0 | 0 | 679.11 | 7.194%
CZ 3C | 0.28579 | 0.095484 | 0.90247 | 0.38734 | 0 | 0.17869 | 0 | 0.40781 | 0 | 0.0023014 | 0.43298 | 0 | 0 | 2.9421 | 0 | 0 | 5.635 | 0.8731% | CZ 3C | 9.6287 | 3.217 | 64.6707 | 38.7344 | 0 | 6.0205 | 0 | 13.74 | 0 | 0.077539 | 14.5877 | 0 | 0 | 152.7879 | 0 | 0 | 303.4644 | 0.8731% | CZ 3C | 2.8212 | 0.94259 | 3.8077 | 0 | 0 | 1.764 | 0 | 4.0258 | 0 | 0.022719 | 4.2742 | 0 | 0 | 21.0545 | 0 | 0 | 38.7127 | 0.8731% | CZ 3C | 0 | 0 | 0.51675 | 0.38734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7134 | 0.8731% | CZ 3C | 29.5351 | 9.8679 | 96.3438 | 42.3367 | 0 | 18.4674 | 0 | 42.1462 | 0 | 0.23785 | 44.7466 | 0 | 0 | 308.8753 | 0 | 0 | 592.5569 | 0.8731%
CZ 4A | 0.28722 | 0.095637 | 0.9475 | 1.0286 | 0 | 0.39897 | 0 | 0.44776 | 0 | 0.0023014 | 0.42551 | 0 | 0 | 2.9421 | 0 | 0 | 6.5756 | 18.87% | CZ 4A | 9.6769 | 3.2222 | 69.16 | 102.8576 | 0 | 13.4419 | 0 | 15.0857 | 0 | 0.077539 | 14.3362 | 0 | 0 | 152.7879 | 0 | 0 | 380.6459 | 18.87% | CZ 4A | 2.8353 | 0.9441 | 3.8097 | 0 | 0 | 3.9385 | 0 | 4.4201 | 0 | 0.022719 | 4.2005 | 0 | 0 | 21.0545 | 0 | 0 | 41.2254 | 18.87% | CZ 4A | 0 | 0 | 0.56158 | 1.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3994 | 18.87% | CZ 4A | 29.6831 | 9.8838 | 101.2642 | 112.4234 | 0 | 41.2318 | 0 | 46.2741 | 0 | 0.23785 | 43.975 | 0 | 0 | 308.8753 | 0 | 0 | 693.8486 | 18.87%
CZ 4B | 0.28272 | 0.095177 | 0.93267 | 0.61264 | 0 | 0.35831 | 0 | 0.53613 | 0 | 0.0023014 | 0.42669 | 0 | 0 | 2.9421 | 0 | 0 | 6.1887 | 0.9164% | CZ 4B | 9.5253 | 3.2067 | 67.6803 | 61.2636 | 0 | 12.072 | 0 | 18.0632 | 0 | 0.077539 | 14.3758 | 0 | 0 | 152.7879 | 0 | 0 | 339.0522 | 0.9164% | CZ 4B | 2.7909 | 0.93956 | 3.8092 | 0 | 0 | 3.5371 | 0 | 5.2925 | 0 | 0.022719 | 4.2121 | 0 | 0 | 21.0545 | 0 | 0 | 41.6586 | 0.9164% | CZ 4B | 0 | 0 | 0.5468 | 0.61264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9687 | 0.9164% | CZ 4B | 29.218 | 9.8362 | 99.6434 | 66.9611 | 0 | 37.0299 | 0 | 55.4074 | 0 | 0.23785 | 44.0965 | 0 | 0 | 308.8753 | 0 | 0 | 651.3057 | 0.9164%
CZ 4C | 0.2885 | 0.095689 | 0.96333 | 0.90249 | 0 | 0.08592 | 0 | 0.39099 | 0 | 0.0023014 | 0.42362 | 0 | 0 | 2.9421 | 0 | 0 | 6.095 | 1.521% | CZ 4C | 9.72 | 3.2239 | 70.7397 | 90.2493 | 0 | 2.8948 | 0 | 13.1731 | 0 | 0.077539 | 14.2724 | 0 | 0 | 152.7879 | 0 | 0 | 357.1387 | 1.521% | CZ 4C | 2.848 | 0.94461 | 3.8102 | 0 | 0 | 0.84818 | 0 | 3.8597 | 0 | 0.022719 | 4.1818 | 0 | 0 | 21.0545 | 0 | 0 | 37.5697 | 1.521% | CZ 4C | 0 | 0 | 0.57736 | 0.90249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2891 | 1.521% | CZ 4C | 29.8152 | 9.8891 | 102.9942 | 98.6425 | 0 | 8.8796 | 0 | 40.4073 | 0 | 0.23785 | 43.7794 | 0 | 0 | 308.8753 | 0 | 0 | 643.5205 | 1.521%
CZ 5A | 0.28563 | 0.095331 | 0.9915 | 1.4386 | 0 | 0.21194 | 0 | 0.42602 | 0 | 0.0023014 | 0.4229 | 0 | 0 | 2.9421 | 0 | 0 | 6.8163 | 20.24% | CZ 5A | 9.6235 | 3.2118 | 73.5563 | 143.8556 | 0 | 7.1405 | 0 | 14.3534 | 0 | 0.077539 | 14.2483 | 0 | 0 | 152.7879 | 0 | 0 | 418.8549 | 20.24% | CZ 5A | 2.8197 | 0.94107 | 3.8102 | 0 | 0 | 2.0922 | 0 | 4.2055 | 0 | 0.022719 | 4.1747 | 0 | 0 | 21.0545 | 0 | 0 | 39.1206 | 20.24% | CZ 5A | 0 | 0 | 0.60552 | 1.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8534 | 20.24% | CZ 5A | 29.5192 | 9.8521 | 106.0728 | 157.2342 | 0 | 21.9029 | 0 | 44.0278 | 0 | 0.23785 | 43.7054 | 0 | 0 | 308.8753 | 0 | 0 | 721.4276 | 20.24%
CZ 5B | 0.28471 | 0.095535 | 0.97897 | 0.99176 | 0 | 0.24958 | 0 | 0.5168 | 0 | 0.0023014 | 0.42423 | 0 | 0 | 2.9421 | 0 | 0 | 6.486 | 4.792% | CZ 5B | 9.5925 | 3.2187 | 72.3074 | 99.1763 | 0 | 8.4087 | 0 | 17.4119 | 0 | 0.077539 | 14.2931 | 0 | 0 | 152.7879 | 0 | 0 | 377.2739 | 4.792% | CZ 5B | 2.8106 | 0.94309 | 3.8097 | 0 | 0 | 2.4638 | 0 | 5.1017 | 0 | 0.022719 | 4.1879 | 0 | 0 | 21.0545 | 0 | 0 | 40.3939 | 4.792% | CZ 5B | 0 | 0 | 0.59305 | 0.99176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3941 | 4.792% | CZ 5B | 29.4241 | 9.8732 | 104.7043 | 108.3997 | 0 | 25.793 | 0 | 53.4095 | 0 | 0.23785 | 43.8428 | 0 | 0 | 308.8753 | 0 | 0 | 684.5597 | 4.792%
CZ 5C | 0.28824 | 0.095637 | 0.98841 | 1.1046 | 0 | 0.025009 | 0 | 0.37539 | 0 | 0.0023014 | 0.42106 | 0 | 0 | 2.9421 | 0 | 0 | 6.2428 | 0.02749% | CZ 5C | 9.7114 | 3.2222 | 73.2445 | 110.4632 | 0 | 0.84259 | 0 | 12.6475 | 0 | 0.077539 | 14.1862 | 0 | 0 | 152.7879 | 0 | 0 | 377.1831 | 0.02749% | CZ 5C | 2.8454 | 0.9441 | 3.8107 | 0 | 0 | 0.24688 | 0 | 3.7057 | 0 | 0.022719 | 4.1566 | 0 | 0 | 21.0545 | 0 | 0 | 36.7866 | 0.02749% | CZ 5C | 0 | 0 | 0.60239 | 1.1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.5163 | 0.02749% | CZ 5C | 29.7888 | 9.8838 | 105.7354 | 120.7363 | 0 | 2.5846 | 0 | 38.7952 | 0 | 0.23785 | 43.5151 | 0 | 0 | 308.8753 | 0 | 0 | 660.1524 | 0.02749%
CZ 6A | 0.28287 | 0.095484 | 1.024 | 1.8563 | 0 | 0.24692 | 0 | 0.44136 | 0 | 0.0023014 | 0.42234 | 0 | 0 | 2.9421 | 0 | 0 | 7.3136 | 3.027% | CZ 6A | 9.5304 | 3.217 | 76.8001 | 185.6271 | 0 | 8.3191 | 0 | 14.8703 | 0 | 0.077539 | 14.2293 | 0 | 0 | 152.7879 | 0 | 0 | 465.4589 | 3.027% | CZ 6A | 2.7924 | 0.94259 | 3.8107 | 0 | 0 | 2.4375 | 0 | 4.357 | 0 | 0.022719 | 4.1692 | 0 | 0 | 21.0545 | 0 | 0 | 39.5866 | 3.027% | CZ 6A | 0 | 0 | 0.63794 | 1.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3035 | 3.027% | CZ 6A | 29.2338 | 9.8679 | 109.6216 | 202.8904 | 0 | 25.5182 | 0 | 45.6134 | 0 | 0.23785 | 43.6473 | 0 | 0 | 308.8753 | 0 | 0 | 775.5059 | 3.027%
CZ 6B | 0.28118 | 0.095331 | 1.0158 | 1.4464 | 0 | 0.16095 | 0 | 0.47036 | 0 | 0.0023014 | 0.42188 | 0 | 0 | 2.9421 | 0 | 0 | 6.8362 | 0.4857% | CZ 6B | 9.4736 | 3.2118 | 75.9784 | 144.636 | 0 | 5.4226 | 0 | 15.8473 | 0 | 0.077539 | 14.2138 | 0 | 0 | 152.7879 | 0 | 0 | 421.649 | 0.4857% | CZ 6B | 2.7758 | 0.94107 | 3.8107 | 0 | 0 | 1.5888 | 0 | 4.6433 | 0 | 0.022719 | 4.1646 | 0 | 0 | 21.0545 | 0 | 0 | 39.0015 | 0.4857% | CZ 6B | 0 | 0 | 0.62972 | 1.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8854 | 0.4857% | CZ 6B | 29.0594 | 9.8521 | 108.7235 | 158.0871 | 0 | 16.6333 | 0 | 48.6103 | 0 | 0.23785 | 43.5997 | 0 | 0 | 308.8753 | 0 | 0 | 723.6786 | 0.4857%
CZ 7 | 0.28164 | 0.095637 | 1.0626 | 2.2957 | 0 | 0.16504 | 0 | 0.42945 | 0 | 0.0023014 | 0.42075 | 0 | 0 | 2.9421 | 0 | 0 | 7.6953 | 0.4495% | CZ 7 | 9.4891 | 3.2222 | 80.6641 | 229.5709 | 0 | 5.5604 | 0 | 14.4688 | 0 | 0.077539 | 14.1759 | 0 | 0 | 152.7879 | 0 | 0 | 510.0168 | 0.4495% | CZ 7 | 2.7803 | 0.9441 | 3.8107 | 0 | 0 | 1.6292 | 0 | 4.2394 | 0 | 0.022719 | 4.1535 | 0 | 0 | 21.0545 | 0 | 0 | 38.6344 | 0.4495% | CZ 7 | 0 | 0 | 0.67658 | 2.2957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.7816 | 0.4495% | CZ 7 | 29.107 | 9.8838 | 113.845 | 250.921 | 0 | 17.0562 | 0 | 44.3819 | 0 | 0.23785 | 43.4834 | 0 | 0 | 308.8753 | 0 | 0 | 817.7914 | 0.4495%
CZ 8 | 0.28973 | 0.097274 | 1.1148 | 3.1428 | 0 | 0.043216 | 0 | 0.407 | 0 | 0.0023014 | 0.41758 | 0 | 0 | 2.9421 | 0 | 0 | 8.4568 | 0.02085% | CZ 8 | 9.7613 | 3.2773 | 85.8786 | 314.2818 | 0 | 1.456 | 0 | 13.7124 | 0 | 0.077539 | 14.0691 | 0 | 0 | 152.7879 | 0 | 0 | 595.302 | 0.02085% | CZ 8 | 2.8601 | 0.96026 | 3.8117 | 0 | 0 | 0.42661 | 0 | 4.0177 | 0 | 0.022719 | 4.1222 | 0 | 0 | 21.0545 | 0 | 0 | 37.2758 | 0.02085% | CZ 8 | 0 | 0 | 0.72869 | 3.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.6808 | 0.02085% | CZ 8 | 29.9421 | 10.0529 | 119.5513 | 343.51 | 0 | 4.4662 | 0 | 42.0616 | 0 | 0.23785 | 43.1557 | 0 | 0 | 308.8753 | 0 | 0 | 901.853 | 0.02085%
US Weighted | 0.2851 | 0.09532 | 0.91773 | 0.81467 | 0 | 0.61795 | 0 | 0.51877 | 0 | 0.0023014 | 0.42917 | 0 | 0 | 2.9421 | 0 | 0 | 6.6231 | 100% | US Weighted | 9.6055 | 3.2115 | 66.1897 | 81.4672 | 0 | 20.8198 | 0 | 17.4782 | 0 | 0.077539 | 14.4593 | 0 | 0 | 152.7879 | 0 | 0 | 366.0967 | 100% | US Weighted | 2.8144 | 0.94097 | 3.8088 | 0 | 0 | 6.1002 | 0 | 5.1211 | 0 | 0.022719 | 4.2366 | 0 | 0 | 21.0545 | 0 | 0 | 44.0993 | 100% | US Weighted | 0 | 0 | 0.5319 | 0.81467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1559 | 100% | US Weighted | 29.4642 | 9.851 | 98.0114 | 89.0436 | 0 | 63.8629 | 0 | 53.613 | 0 | 0.23785 | 44.3528 | 0 | 0 | 308.8753 | 0 | 0 | 697.3122 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.36434 | 0.16898 | 0.79055 | 0.021378 | 0 | 1.5214 | 0 | 0.61407 | 0 | 0.0023014 | 0.4409 | 0 | 0 | 2.9421 | 0 | 0 | 6.866 | 2.444% | CZ 1A | 12.2753 | 5.6931 | 53.4888 | 2.1378 | 0 | 51.2569 | 0 | 20.6892 | 0 | 0.077539 | 14.8548 | 0 | 0 | 152.7879 | 0 | 0 | 313.2615 | 2.444% | CZ 1A | 3.5967 | 1.6681 | 3.8062 | 0 | 0 | 15.0183 | 0 | 6.0619 | 0 | 0.022719 | 4.3525 | 0 | 0 | 21.0545 | 0 | 0 | 55.5808 | 2.444% | CZ 1A | 0 | 0 | 0.40498 | 0.021378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2357 | 2.444% | CZ 1A | 37.6536 | 17.4631 | 84.1118 | 2.3367 | 0 | 157.2263 | 0 | 63.4624 | 0 | 0.23785 | 45.5659 | 0 | 0 | 308.8753 | 0 | 0 | 716.9329 | 2.444%
CZ 1B | 0.36485 | 0.16877 | 0.79133 | 0.12093 | 0 | 1.861 | 0 | 0.93402 | 0 | 0.0023014 | 0.4408 | 0 | 0 | 2.9421 | 0 | 0 | 7.6261 | 0% | CZ 1B | 12.2926 | 5.6862 | 53.5664 | 12.0932 | 0 | 62.7 | 0 | 31.4689 | 0 | 0.077539 | 14.8514 | 0 | 0 | 152.7879 | 0 | 0 | 345.524 | 0% | CZ 1B | 3.6017 | 1.6661 | 3.8062 | 0 | 0 | 18.3711 | 0 | 9.2204 | 0 | 0.022719 | 4.3514 | 0 | 0 | 21.0545 | 0 | 0 | 62.0941 | 0% | CZ 1B | 0 | 0 | 0.40576 | 0.12093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.336 | 0% | CZ 1B | 37.7064 | 17.442 | 84.1965 | 13.2179 | 0 | 192.327 | 0 | 96.5282 | 0 | 0.23785 | 45.5553 | 0 | 0 | 308.8753 | 0 | 0 | 796.0865 | 0%
CZ 2A | 0.36327 | 0.16867 | 0.82907 | 0.21549 | 0 | 1.316 | 0 | 0.57439 | 0 | 0.0023014 | 0.43886 | 0 | 0 | 2.9421 | 0 | 0 | 6.8502 | 17.24% | CZ 2A | 12.2391 | 5.6828 | 57.3373 | 21.549 | 0 | 44.3387 | 0 | 19.3521 | 0 | 0.077539 | 14.7859 | 0 | 0 | 152.7879 | 0 | 0 | 328.1503 | 17.24% | CZ 2A | 3.5861 | 1.6651 | 3.8067 | 0 | 0 | 12.9912 | 0 | 5.6702 | 0 | 0.022719 | 4.3323 | 0 | 0 | 21.0545 | 0 | 0 | 53.1287 | 17.24% | CZ 2A | 0 | 0 | 0.44345 | 0.21549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4682 | 17.24% | CZ 2A | 37.5426 | 17.4314 | 88.3216 | 23.553 | 0 | 136.0052 | 0 | 59.3609 | 0 | 0.23785 | 45.3545 | 0 | 0 | 308.8753 | 0 | 0 | 716.6824 | 17.24%
CZ 2B | 0.3623 | 0.16882 | 0.83186 | 0.20841 | 0 | 0.9976 | 0 | 0.86007 | 0 | 0.0023014 | 0.43364 | 0 | 0 | 2.9421 | 0 | 0 | 6.8071 | 3.722% | CZ 2B | 12.2064 | 5.6879 | 57.6095 | 20.841 | 0 | 33.6107 | 0 | 28.9773 | 0 | 0.077539 | 14.6101 | 0 | 0 | 152.7879 | 0 | 0 | 326.4083 | 3.722% | CZ 2B | 3.5765 | 1.6666 | 3.8077 | 0 | 0 | 9.8479 | 0 | 8.4903 | 0 | 0.022719 | 4.2808 | 0 | 0 | 21.0545 | 0 | 0 | 52.747 | 3.722% | CZ 2B | 0 | 0 | 0.44614 | 0.20841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4638 | 3.722% | CZ 2B | 37.4421 | 17.4473 | 88.6259 | 22.7792 | 0 | 103.098 | 0 | 88.8854 | 0 | 0.23785 | 44.8153 | 0 | 0 | 308.8753 | 0 | 0 | 712.2064 | 3.722%
CZ 3A | 0.36485 | 0.16877 | 0.89546 | 0.61589 | 0 | 0.70173 | 0 | 0.50621 | 0 | 0.0023014 | 0.43139 | 0 | 0 | 2.9421 | 0 | 0 | 6.6287 | 18.17% | CZ 3A | 12.2926 | 5.6862 | 63.9662 | 61.5892 | 0 | 23.6426 | 0 | 17.0552 | 0 | 0.077539 | 14.5343 | 0 | 0 | 152.7879 | 0 | 0 | 351.6316 | 18.17% | CZ 3A | 3.6017 | 1.6661 | 3.8082 | 0 | 0 | 6.9273 | 0 | 4.9972 | 0 | 0.022719 | 4.2586 | 0 | 0 | 21.0545 | 0 | 0 | 46.3362 | 18.17% | CZ 3A | 0 | 0 | 0.50969 | 0.61589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9349 | 18.17% | CZ 3A | 37.7064 | 17.442 | 95.5771 | 67.317 | 0 | 72.5217 | 0 | 52.3154 | 0 | 0.23785 | 44.5828 | 0 | 0 | 308.8753 | 0 | 0 | 696.5755 | 18.17%
CZ 3B | 0.36312 | 0.16877 | 0.87872 | 0.36355 | 0 | 0.70235 | 0 | 0.79031 | 0 | 0.0023014 | 0.43027 | 0 | 0 | 2.9421 | 0 | 0 | 6.6415 | 7.194% | CZ 3B | 12.234 | 5.6862 | 62.2917 | 36.3554 | 0 | 23.6633 | 0 | 26.627 | 0 | 0.077539 | 14.4964 | 0 | 0 | 152.7879 | 0 | 0 | 334.2194 | 7.194% | CZ 3B | 3.5846 | 1.6661 | 3.8082 | 0 | 0 | 6.9333 | 0 | 7.8017 | 0 | 0.022719 | 4.2474 | 0 | 0 | 21.0545 | 0 | 0 | 49.1185 | 7.194% | CZ 3B | 0 | 0 | 0.49294 | 0.36355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6658 | 7.194% | CZ 3B | 37.5267 | 17.442 | 93.747 | 39.7364 | 0 | 72.5851 | 0 | 81.6761 | 0 | 0.23785 | 44.4665 | 0 | 0 | 308.8753 | 0 | 0 | 696.293 | 7.194%
CZ 3C | 0.36496 | 0.16908 | 0.90275 | 0.38393 | 0 | 0.18273 | 0 | 0.41114 | 0 | 0.0023014 | 0.43313 | 0 | 0 | 2.9421 | 0 | 0 | 5.7921 | 0.8731% | CZ 3C | 12.296 | 5.6966 | 64.6983 | 38.3933 | 0 | 6.1566 | 0 | 13.852 | 0 | 0.077539 | 14.5929 | 0 | 0 | 152.7879 | 0 | 0 | 308.5511 | 0.8731% | CZ 3C | 3.6027 | 1.6691 | 3.8077 | 0 | 0 | 1.8039 | 0 | 4.0586 | 0 | 0.022719 | 4.2757 | 0 | 0 | 21.0545 | 0 | 0 | 40.2949 | 0.8731% | CZ 3C | 0 | 0 | 0.51703 | 0.38393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7103 | 0.8731% | CZ 3C | 37.717 | 17.4737 | 96.3739 | 41.9639 | 0 | 18.8849 | 0 | 42.4897 | 0 | 0.23785 | 44.7625 | 0 | 0 | 308.8753 | 0 | 0 | 608.7788 | 0.8731%
CZ 4A | 0.36675 | 0.16913 | 0.94781 | 1.022 | 0 | 0.40388 | 0 | 0.44991 | 0 | 0.0023014 | 0.42571 | 0 | 0 | 2.9421 | 0 | 0 | 6.7296 | 18.87% | CZ 4A | 12.3563 | 5.6983 | 69.191 | 102.2013 | 0 | 13.6073 | 0 | 15.1581 | 0 | 0.077539 | 14.343 | 0 | 0 | 152.7879 | 0 | 0 | 385.4208 | 18.87% | CZ 4A | 3.6204 | 1.6696 | 3.8097 | 0 | 0 | 3.9869 | 0 | 4.4413 | 0 | 0.022719 | 4.2025 | 0 | 0 | 21.0545 | 0 | 0 | 42.8077 | 18.87% | CZ 4A | 0 | 0 | 0.56189 | 1.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3932 | 18.87% | CZ 4A | 37.902 | 17.479 | 101.2981 | 111.706 | 0 | 41.7392 | 0 | 46.4961 | 0 | 0.23785 | 43.9961 | 0 | 0 | 308.8753 | 0 | 0 | 709.7297 | 18.87%
CZ 4B | 0.36112 | 0.16872 | 0.933 | 0.60562 | 0 | 0.36189 | 0 | 0.54022 | 0 | 0.0023014 | 0.42679 | 0 | 0 | 2.9421 | 0 | 0 | 6.3418 | 0.9164% | CZ 4B | 12.1668 | 5.6845 | 67.713 | 60.5624 | 0 | 12.1926 | 0 | 18.2011 | 0 | 0.077539 | 14.3792 | 0 | 0 | 152.7879 | 0 | 0 | 343.765 | 0.9164% | CZ 4B | 3.5649 | 1.6656 | 3.8092 | 0 | 0 | 3.5724 | 0 | 5.3329 | 0 | 0.022719 | 4.2131 | 0 | 0 | 21.0545 | 0 | 0 | 43.2353 | 0.9164% | CZ 4B | 0 | 0 | 0.54712 | 0.60562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.962 | 0.9164% | CZ 4B | 37.3206 | 17.4367 | 99.6792 | 66.1948 | 0 | 37.3999 | 0 | 55.8302 | 0 | 0.23785 | 44.1071 | 0 | 0 | 308.8753 | 0 | 0 | 667.0816 | 0.9164%
CZ 4C | 0.3667 | 0.16908 | 0.96364 | 0.89014 | 0 | 0.088887 | 0 | 0.396 | 0 | 0.0023014 | 0.42387 | 0 | 0 | 2.9421 | 0 | 0 | 6.2427 | 1.521% | CZ 4C | 12.3546 | 5.6966 | 70.7707 | 89.0142 | 0 | 2.9947 | 0 | 13.3419 | 0 | 0.077539 | 14.281 | 0 | 0 | 152.7879 | 0 | 0 | 361.3192 | 1.521% | CZ 4C | 3.6199 | 1.6691 | 3.8102 | 0 | 0 | 0.87746 | 0 | 3.9092 | 0 | 0.022719 | 4.1843 | 0 | 0 | 21.0545 | 0 | 0 | 39.1474 | 1.521% | CZ 4C | 0 | 0 | 0.57767 | 0.89014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2771 | 1.521% | CZ 4C | 37.8967 | 17.4737 | 103.0281 | 97.2925 | 0 | 9.1861 | 0 | 40.9253 | 0 | 0.23785 | 43.8058 | 0 | 0 | 308.8753 | 0 | 0 | 658.7214 | 1.521%
CZ 5A | 0.36506 | 0.16882 | 0.99184 | 1.4301 | 0 | 0.21608 | 0 | 0.42955 | 0 | 0.0023014 | 0.42316 | 0 | 0 | 2.9421 | 0 | 0 | 6.969 | 20.24% | CZ 5A | 12.2995 | 5.6879 | 73.5908 | 143.0115 | 0 | 7.2801 | 0 | 14.4723 | 0 | 0.077539 | 14.2569 | 0 | 0 | 152.7879 | 0 | 0 | 423.4643 | 20.24% | CZ 5A | 3.6037 | 1.6666 | 3.8102 | 0 | 0 | 2.1331 | 0 | 4.2404 | 0 | 0.022719 | 4.1773 | 0 | 0 | 21.0545 | 0 | 0 | 40.7084 | 20.24% | CZ 5A | 0 | 0 | 0.60587 | 1.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8453 | 20.24% | CZ 5A | 37.7276 | 17.4473 | 106.1104 | 156.3116 | 0 | 22.331 | 0 | 44.3925 | 0 | 0.23785 | 43.7318 | 0 | 0 | 308.8753 | 0 | 0 | 737.1654 | 20.24%
CZ 5B | 0.36383 | 0.16903 | 0.97932 | 0.97945 | 0 | 0.25346 | 0 | 0.52176 | 0 | 0.0023014 | 0.42433 | 0 | 0 | 2.9421 | 0 | 0 | 6.6356 | 4.792% | CZ 5B | 12.2581 | 5.6948 | 72.3418 | 97.9445 | 0 | 8.5397 | 0 | 17.579 | 0 | 0.077539 | 14.2965 | 0 | 0 | 152.7879 | 0 | 0 | 381.5199 | 4.792% | CZ 5B | 3.5916 | 1.6686 | 3.8097 | 0 | 0 | 2.5021 | 0 | 5.1507 | 0 | 0.022719 | 4.1889 | 0 | 0 | 21.0545 | 0 | 0 | 41.9888 | 4.792% | CZ 5B | 0 | 0 | 0.59339 | 0.97945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3821 | 4.792% | CZ 5B | 37.6007 | 17.4684 | 104.7419 | 107.0534 | 0 | 26.1947 | 0 | 53.9222 | 0 | 0.23785 | 43.8534 | 0 | 0 | 308.8753 | 0 | 0 | 699.9479 | 4.792%
CZ 5C | 0.36828 | 0.16903 | 0.98876 | 1.0942 | 0 | 0.025981 | 0 | 0.37912 | 0 | 0.0023014 | 0.42132 | 0 | 0 | 2.9421 | 0 | 0 | 6.3911 | 0.02749% | CZ 5C | 12.408 | 5.6948 | 73.279 | 109.4159 | 0 | 0.87533 | 0 | 12.7733 | 0 | 0.077539 | 14.1949 | 0 | 0 | 152.7879 | 0 | 0 | 381.5066 | 0.02749% | CZ 5C | 3.6355 | 1.6686 | 3.8107 | 0 | 0 | 0.25647 | 0 | 3.7426 | 0 | 0.022719 | 4.1591 | 0 | 0 | 21.0545 | 0 | 0 | 38.3502 | 0.02749% | CZ 5C | 0 | 0 | 0.60273 | 1.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.5062 | 0.02749% | CZ 5C | 38.0605 | 17.4684 | 105.773 | 119.5915 | 0 | 2.685 | 0 | 39.1811 | 0 | 0.23785 | 43.5416 | 0 | 0 | 308.8753 | 0 | 0 | 675.4143 | 0.02749%
CZ 6A | 0.36542 | 0.16893 | 1.0243 | 1.8583 | 0 | 0.24856 | 0 | 0.44285 | 0 | 0.0023014 | 0.42259 | 0 | 0 | 2.9421 | 0 | 0 | 7.4754 | 3.027% | CZ 6A | 12.3115 | 5.6914 | 76.8363 | 185.8338 | 0 | 8.3742 | 0 | 14.9203 | 0 | 0.077539 | 14.2379 | 0 | 0 | 152.7879 | 0 | 0 | 471.0709 | 3.027% | CZ 6A | 3.6073 | 1.6676 | 3.8107 | 0 | 0 | 2.4537 | 0 | 4.3716 | 0 | 0.022719 | 4.1717 | 0 | 0 | 21.0545 | 0 | 0 | 41.1598 | 3.027% | CZ 6A | 0 | 0 | 0.6383 | 1.8583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3059 | 3.027% | CZ 6A | 37.7646 | 17.4578 | 109.6612 | 203.1164 | 0 | 25.6873 | 0 | 45.7667 | 0 | 0.23785 | 43.6737 | 0 | 0 | 308.8753 | 0 | 0 | 792.2408 | 3.027%
CZ 6B | 0.3626 | 0.16872 | 1.016 | 1.4471 | 0 | 0.16197 | 0 | 0.47159 | 0 | 0.0023014 | 0.42203 | 0 | 0 | 2.9421 | 0 | 0 | 6.9944 | 0.4857% | CZ 6B | 12.2167 | 5.6845 | 76.0094 | 144.7066 | 0 | 5.457 | 0 | 15.8887 | 0 | 0.077539 | 14.219 | 0 | 0 | 152.7879 | 0 | 0 | 427.0474 | 0.4857% | CZ 6B | 3.5795 | 1.6656 | 3.8102 | 0 | 0 | 1.5989 | 0 | 4.6554 | 0 | 0.022719 | 4.1662 | 0 | 0 | 21.0545 | 0 | 0 | 40.5529 | 0.4857% | CZ 6B | 0 | 0 | 0.63005 | 1.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8864 | 0.4857% | CZ 6B | 37.4739 | 17.4367 | 108.754 | 158.1643 | 0 | 16.739 | 0 | 48.7372 | 0 | 0.23785 | 43.6155 | 0 | 0 | 308.8753 | 0 | 0 | 740.0338 | 0.4857%
CZ 7 | 0.36051 | 0.16903 | 1.063 | 2.3009 | 0 | 0.1676 | 0 | 0.43333 | 0 | 0.0023014 | 0.42096 | 0 | 0 | 2.9421 | 0 | 0 | 7.8598 | 0.4495% | CZ 7 | 12.1461 | 5.6948 | 80.7037 | 230.0946 | 0 | 5.6466 | 0 | 14.5998 | 0 | 0.077539 | 14.1828 | 0 | 0 | 152.7879 | 0 | 0 | 515.9338 | 0.4495% | CZ 7 | 3.5588 | 1.6686 | 3.8107 | 0 | 0 | 1.6544 | 0 | 4.2777 | 0 | 0.022719 | 4.1556 | 0 | 0 | 21.0545 | 0 | 0 | 40.2031 | 0.4495% | CZ 7 | 0 | 0 | 0.67698 | 2.3009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.7872 | 0.4495% | CZ 7 | 37.2571 | 17.4684 | 113.8883 | 251.4934 | 0 | 17.3204 | 0 | 44.7836 | 0 | 0.23785 | 43.5046 | 0 | 0 | 308.8753 | 0 | 0 | 834.829 | 0.4495%
CZ 8 | 0.3693 | 0.1701 | 1.1152 | 3.1479 | 0 | 0.044136 | 0 | 0.41073 | 0 | 0.0023014 | 0.41779 | 0 | 0 | 2.9421 | 0 | 0 | 8.6196 | 0.02085% | CZ 8 | 12.4425 | 5.731 | 85.9182 | 314.7866 | 0 | 1.487 | 0 | 13.8382 | 0 | 0.077539 | 14.076 | 0 | 0 | 152.7879 | 0 | 0 | 601.1449 | 0.02085% | CZ 8 | 3.6456 | 1.6792 | 3.8117 | 0 | 0 | 0.4357 | 0 | 4.0546 | 0 | 0.022719 | 4.1243 | 0 | 0 | 21.0545 | 0 | 0 | 38.8283 | 0.02085% | CZ 8 | 0 | 0 | 0.72909 | 3.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.6863 | 0.02085% | CZ 8 | 38.1662 | 17.5794 | 119.5946 | 344.0617 | 0 | 4.5613 | 0 | 42.4475 | 0 | 0.23785 | 43.1769 | 0 | 0 | 308.8753 | 0 | 0 | 918.7008 | 0.02085%
US Weighted | 0.36468 | 0.16886 | 0.91804 | 0.80978 | 0 | 0.62673 | 0 | 0.52415 | 0 | 0.0023014 | 0.42933 | 0 | 0 | 2.9421 | 0 | 0 | 6.786 | 100% | US Weighted | 12.2867 | 5.6893 | 66.2199 | 80.9781 | 0 | 21.1158 | 0 | 17.6596 | 0 | 0.077539 | 14.4649 | 0 | 0 | 152.7879 | 0 | 0 | 371.2798 | 100% | US Weighted | 3.6 | 1.667 | 3.8088 | 0 | 0 | 6.1869 | 0 | 5.1743 | 0 | 0.022719 | 4.2382 | 0 | 0 | 21.0545 | 0 | 0 | 45.7524 | 100% | US Weighted | 0 | 0 | 0.53221 | 0.80978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.1513 | 100% | US Weighted | 37.6885 | 17.4515 | 98.0443 | 88.509 | 0 | 64.7709 | 0 | 54.1694 | 0 | 0.23785 | 44.37 | 0 | 0 | 308.8753 | 0 | 0 | 714.1168 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.39856 | 0.16898 | 0.79076 | 0.027856 | 0 | 1.6316 | 0 | 0.87582 | 0 | 0.0023014 | 0.55582 | 0 | 0 | 2.9429 | 0 | 0 | 7.3946 | 2.444% | CZ 1A | 13.4281 | 5.6931 | 53.5061 | 2.7856 | 0 | 54.9719 | 0 | 29.508 | 0 | 0.077539 | 18.7266 | 0 | 0 | 152.8155 | 0 | 0 | 331.5123 | 2.444% | CZ 1A | 3.9344 | 1.6681 | 3.8067 | 0 | 0 | 16.1068 | 0 | 8.6458 | 0 | 0.022719 | 5.4869 | 0 | 0 | 21.0625 | 0 | 0 | 60.734 | 2.444% | CZ 1A | 0 | 0 | 0.40514 | 0.027856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2423 | 2.444% | CZ 1A | 41.1895 | 17.4631 | 84.134 | 3.0446 | 0 | 168.6218 | 0 | 90.5134 | 0 | 0.23785 | 57.4423 | 0 | 0 | 308.9599 | 0 | 0 | 771.6065 | 2.444%
CZ 1B | 0.39574 | 0.16877 | 0.79114 | 0.13514 | 0 | 1.9433 | 0 | 1.1731 | 0 | 0.0023014 | 0.55853 | 0 | 0 | 2.9429 | 0 | 0 | 8.111 | 0% | CZ 1B | 13.3333 | 5.6862 | 53.5509 | 13.5144 | 0 | 65.4724 | 0 | 39.5244 | 0 | 0.077539 | 18.8179 | 0 | 0 | 152.8155 | 0 | 0 | 362.7925 | 0% | CZ 1B | 3.9067 | 1.6661 | 3.8057 | 0 | 0 | 19.1834 | 0 | 11.5806 | 0 | 0.022719 | 5.5137 | 0 | 0 | 21.0625 | 0 | 0 | 66.7414 | 0% | CZ 1B | 0 | 0 | 0.40562 | 0.13514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3501 | 0% | CZ 1B | 40.8988 | 17.442 | 84.1762 | 14.7712 | 0 | 200.8313 | 0 | 121.2377 | 0 | 0.23785 | 57.7224 | 0 | 0 | 308.9599 | 0 | 0 | 846.2774 | 0%
CZ 2A | 0.39856 | 0.16867 | 0.8291 | 0.23907 | 0 | 1.4233 | 0 | 0.85537 | 0 | 0.0023014 | 0.5548 | 0 | 0 | 2.9429 | 0 | 0 | 7.4141 | 17.24% | CZ 2A | 13.4281 | 5.6828 | 57.3407 | 23.9073 | 0 | 47.952 | 0 | 28.8188 | 0 | 0.077539 | 18.6921 | 0 | 0 | 152.8155 | 0 | 0 | 348.7148 | 17.24% | CZ 2A | 3.9344 | 1.6651 | 3.8067 | 0 | 0 | 14.0499 | 0 | 8.4439 | 0 | 0.022719 | 5.4768 | 0 | 0 | 21.0625 | 0 | 0 | 58.4621 | 17.24% | CZ 2A | 0 | 0 | 0.44349 | 0.23907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4919 | 17.24% | CZ 2A | 41.1895 | 17.4314 | 88.3253 | 26.1307 | 0 | 147.0888 | 0 | 88.3992 | 0 | 0.23785 | 57.3366 | 0 | 0 | 308.9599 | 0 | 0 | 775.0993 | 17.24%
CZ 2B | 0.40122 | 0.16882 | 0.83164 | 0.22731 | 0 | 1.0625 | 0 | 1.1177 | 0 | 0.0023014 | 0.55188 | 0 | 0 | 2.9429 | 0 | 0 | 7.3063 | 3.722% | CZ 2B | 13.5177 | 5.6879 | 57.5905 | 22.7307 | 0 | 35.7973 | 0 | 37.6582 | 0 | 0.077539 | 18.5939 | 0 | 0 | 152.8155 | 0 | 0 | 344.4694 | 3.722% | CZ 2B | 3.9607 | 1.6666 | 3.8072 | 0 | 0 | 10.4886 | 0 | 11.0339 | 0 | 0.022719 | 5.448 | 0 | 0 | 21.0625 | 0 | 0 | 57.4902 | 3.722% | CZ 2B | 0 | 0 | 0.44597 | 0.22731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4826 | 3.722% | CZ 2B | 41.4644 | 17.4473 | 88.6018 | 24.8447 | 0 | 109.8053 | 0 | 115.5135 | 0 | 0.23785 | 57.0353 | 0 | 0 | 308.9599 | 0 | 0 | 763.9099 | 3.722%
CZ 3A | 0.39119 | 0.16877 | 0.89541 | 0.65384 | 0 | 0.7451 | 0 | 0.78852 | 0 | 0.0023014 | 0.54861 | 0 | 0 | 2.9429 | 0 | 0 | 7.1367 | 18.17% | CZ 3A | 13.18 | 5.6862 | 63.961 | 65.3842 | 0 | 25.1038 | 0 | 26.5667 | 0 | 0.077539 | 18.4836 | 0 | 0 | 152.8155 | 0 | 0 | 371.2585 | 18.17% | CZ 3A | 3.8617 | 1.6661 | 3.8082 | 0 | 0 | 7.3554 | 0 | 7.784 | 0 | 0.022719 | 5.4157 | 0 | 0 | 21.0625 | 0 | 0 | 50.9764 | 18.17% | CZ 3A | 0 | 0 | 0.50964 | 0.65384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9728 | 18.17% | CZ 3A | 40.4284 | 17.442 | 95.5715 | 71.465 | 0 | 77.0037 | 0 | 81.4911 | 0 | 0.23785 | 56.697 | 0 | 0 | 308.9599 | 0 | 0 | 749.2965 | 18.17%
CZ 3B | 0.3913 | 0.16877 | 0.87861 | 0.36243 | 0 | 0.72633 | 0 | 0.97351 | 0 | 0.0023014 | 0.54795 | 0 | 0 | 2.9429 | 0 | 0 | 6.9941 | 7.194% | CZ 3B | 13.1834 | 5.6862 | 62.2814 | 36.2434 | 0 | 24.4714 | 0 | 32.7991 | 0 | 0.077539 | 18.4612 | 0 | 0 | 152.8155 | 0 | 0 | 346.0192 | 7.194% | CZ 3B | 3.8627 | 1.6661 | 3.8082 | 0 | 0 | 7.1701 | 0 | 9.6101 | 0 | 0.022719 | 5.4091 | 0 | 0 | 21.0625 | 0 | 0 | 52.6117 | 7.194% | CZ 3B | 0 | 0 | 0.49284 | 0.36243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6646 | 7.194% | CZ 3B | 40.439 | 17.442 | 93.7357 | 39.614 | 0 | 75.064 | 0 | 100.6086 | 0 | 0.23785 | 56.6283 | 0 | 0 | 308.9599 | 0 | 0 | 732.7293 | 7.194%
CZ 3C | 0.39155 | 0.16908 | 0.90271 | 0.44602 | 0 | 0.20938 | 0 | 0.72142 | 0 | 0.0023014 | 0.55015 | 0 | 0 | 2.9429 | 0 | 0 | 6.3355 | 0.8731% | CZ 3C | 13.192 | 5.6966 | 64.6949 | 44.6018 | 0 | 7.0544 | 0 | 24.306 | 0 | 0.077539 | 18.5353 | 0 | 0 | 152.8155 | 0 | 0 | 330.9739 | 0.8731% | CZ 3C | 3.8653 | 1.6691 | 3.8077 | 0 | 0 | 2.0669 | 0 | 7.1217 | 0 | 0.022719 | 5.4309 | 0 | 0 | 21.0625 | 0 | 0 | 45.0468 | 0.8731% | CZ 3C | 0 | 0 | 0.51699 | 0.44602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7723 | 0.8731% | CZ 3C | 40.4654 | 17.4737 | 96.3702 | 48.7498 | 0 | 21.6386 | 0 | 74.5566 | 0 | 0.23785 | 56.8556 | 0 | 0 | 308.9599 | 0 | 0 | 665.3077 | 0.8731%
CZ 4A | 0.39012 | 0.16913 | 0.94776 | 1.0536 | 0 | 0.43175 | 0 | 0.72178 | 0 | 0.0023014 | 0.54309 | 0 | 0 | 2.9429 | 0 | 0 | 7.2025 | 18.87% | CZ 4A | 13.1438 | 5.6983 | 69.1859 | 105.3624 | 0 | 14.5464 | 0 | 24.318 | 0 | 0.077539 | 18.2975 | 0 | 0 | 152.8155 | 0 | 0 | 403.4453 | 18.87% | CZ 4A | 3.8511 | 1.6696 | 3.8097 | 0 | 0 | 4.2621 | 0 | 7.1252 | 0 | 0.022719 | 5.3612 | 0 | 0 | 21.0625 | 0 | 0 | 47.1642 | 18.87% | CZ 4A | 0 | 0 | 0.56183 | 1.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4248 | 18.87% | CZ 4A | 40.3174 | 17.479 | 101.2925 | 115.1611 | 0 | 44.6198 | 0 | 74.5936 | 0 | 0.23785 | 56.1262 | 0 | 0 | 308.9599 | 0 | 0 | 758.7873 | 18.87%
CZ 4B | 0.38725 | 0.16872 | 0.93293 | 0.66097 | 0 | 0.38797 | 0 | 0.8077 | 0 | 0.0023014 | 0.54442 | 0 | 0 | 2.9429 | 0 | 0 | 6.8352 | 0.9164% | CZ 4B | 13.0473 | 5.6845 | 67.7061 | 66.0974 | 0 | 13.0714 | 0 | 27.2128 | 0 | 0.077539 | 18.3423 | 0 | 0 | 152.8155 | 0 | 0 | 364.0549 | 0.9164% | CZ 4B | 3.8229 | 1.6656 | 3.8092 | 0 | 0 | 3.8299 | 0 | 7.9734 | 0 | 0.022719 | 5.3743 | 0 | 0 | 21.0625 | 0 | 0 | 47.5605 | 0.9164% | CZ 4B | 0 | 0 | 0.54705 | 0.66097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0173 | 0.9164% | CZ 4B | 40.0214 | 17.4367 | 99.6717 | 72.2445 | 0 | 40.0954 | 0 | 83.4731 | 0 | 0.23785 | 56.2636 | 0 | 0 | 308.9599 | 0 | 0 | 718.4042 | 0.9164%
CZ 4C | 0.39135 | 0.16908 | 0.96347 | 0.95331 | 0 | 0.097632 | 0 | 0.68399 | 0 | 0.0023014 | 0.54191 | 0 | 0 | 2.9429 | 0 | 0 | 6.746 | 1.521% | CZ 4C | 13.1851 | 5.6966 | 70.757 | 95.3312 | 0 | 3.2894 | 0 | 23.0447 | 0 | 0.077539 | 18.2579 | 0 | 0 | 152.8155 | 0 | 0 | 382.4549 | 1.521% | CZ 4C | 3.8632 | 1.6691 | 3.8097 | 0 | 0 | 0.96379 | 0 | 6.7521 | 0 | 0.022719 | 5.3496 | 0 | 0 | 21.0625 | 0 | 0 | 43.4928 | 1.521% | CZ 4C | 0 | 0 | 0.57754 | 0.95331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3402 | 1.521% | CZ 4C | 40.4443 | 17.4737 | 103.0097 | 104.1971 | 0 | 10.0899 | 0 | 70.6876 | 0 | 0.23785 | 56.0046 | 0 | 0 | 308.9599 | 0 | 0 | 711.1046 | 1.521%
CZ 5A | 0.38915 | 0.16882 | 0.99179 | 1.4674 | 0 | 0.23163 | 0 | 0.70035 | 0 | 0.0023014 | 0.54058 | 0 | 0 | 2.9429 | 0 | 0 | 7.4349 | 20.24% | CZ 5A | 13.111 | 5.6879 | 73.5856 | 146.7377 | 0 | 7.8039 | 0 | 23.5961 | 0 | 0.077539 | 18.2131 | 0 | 0 | 152.8155 | 0 | 0 | 441.6283 | 20.24% | CZ 5A | 3.8415 | 1.6666 | 3.8102 | 0 | 0 | 2.2865 | 0 | 6.9136 | 0 | 0.022719 | 5.3364 | 0 | 0 | 21.0625 | 0 | 0 | 44.9402 | 20.24% | CZ 5A | 0 | 0 | 0.60581 | 1.4674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8825 | 20.24% | CZ 5A | 40.217 | 17.4473 | 106.1048 | 160.3843 | 0 | 23.9378 | 0 | 72.379 | 0 | 0.23785 | 55.8672 | 0 | 0 | 308.9599 | 0 | 0 | 785.5351 | 20.24%
CZ 5B | 0.38858 | 0.16903 | 0.97928 | 1.0244 | 0 | 0.2729 | 0 | 0.78776 | 0 | 0.0023014 | 0.54176 | 0 | 0 | 2.9429 | 0 | 0 | 7.1089 | 4.792% | CZ 5B | 13.0921 | 5.6948 | 72.3384 | 102.439 | 0 | 9.1944 | 0 | 26.5408 | 0 | 0.077539 | 18.2527 | 0 | 0 | 152.8155 | 0 | 0 | 400.4453 | 4.792% | CZ 5B | 3.836 | 1.6686 | 3.8097 | 0 | 0 | 2.694 | 0 | 7.7765 | 0 | 0.022719 | 5.3481 | 0 | 0 | 21.0625 | 0 | 0 | 46.218 | 4.792% | CZ 5B | 0 | 0 | 0.59336 | 1.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.427 | 4.792% | CZ 5B | 40.1589 | 17.4684 | 104.7382 | 111.9658 | 0 | 28.2032 | 0 | 81.4118 | 0 | 0.23785 | 55.9888 | 0 | 0 | 308.9599 | 0 | 0 | 749.1328 | 4.792%
CZ 5C | 0.39104 | 0.16903 | 0.98865 | 1.1556 | 0 | 0.031862 | 0 | 0.66419 | 0 | 0.0023014 | 0.53951 | 0 | 0 | 2.9429 | 0 | 0 | 6.8852 | 0.02749% | CZ 5C | 13.1748 | 5.6948 | 73.2686 | 115.5641 | 0 | 1.0735 | 0 | 22.3778 | 0 | 0.077539 | 18.1769 | 0 | 0 | 152.8155 | 0 | 0 | 402.2236 | 0.02749% | CZ 5C | 3.8602 | 1.6686 | 3.8107 | 0 | 0 | 0.31453 | 0 | 6.5567 | 0 | 0.022719 | 5.3258 | 0 | 0 | 21.0625 | 0 | 0 | 42.6219 | 0.02749% | CZ 5C | 0 | 0 | 0.60263 | 1.1556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.5676 | 0.02749% | CZ 5C | 40.4126 | 17.4684 | 105.7617 | 126.3116 | 0 | 3.2928 | 0 | 68.6422 | 0 | 0.23785 | 55.7562 | 0 | 0 | 308.9599 | 0 | 0 | 726.8432 | 0.02749%
CZ 6A | 0.38945 | 0.16893 | 1.0242 | 1.8898 | 0 | 0.26477 | 0 | 0.71186 | 0 | 0.0023014 | 0.54022 | 0 | 0 | 2.9429 | 0 | 0 | 7.9344 | 3.027% | CZ 6A | 13.1214 | 5.6914 | 76.8277 | 188.976 | 0 | 8.9205 | 0 | 23.9838 | 0 | 0.077539 | 18.2011 | 0 | 0 | 152.8155 | 0 | 0 | 488.6147 | 3.027% | CZ 6A | 3.8446 | 1.6676 | 3.8102 | 0 | 0 | 2.6137 | 0 | 7.0272 | 0 | 0.022719 | 5.3329 | 0 | 0 | 21.0625 | 0 | 0 | 45.3815 | 3.027% | CZ 6A | 0 | 0 | 0.63823 | 1.8898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3373 | 3.027% | CZ 6A | 40.2487 | 17.4578 | 109.6484 | 206.5508 | 0 | 27.3628 | 0 | 73.5682 | 0 | 0.23785 | 55.8302 | 0 | 0 | 308.9599 | 0 | 0 | 839.8646 | 3.027%
CZ 6B | 0.38797 | 0.16872 | 1.016 | 1.4875 | 0 | 0.17404 | 0 | 0.74367 | 0 | 0.0023014 | 0.53987 | 0 | 0 | 2.9429 | 0 | 0 | 7.463 | 0.4857% | CZ 6B | 13.0714 | 5.6845 | 76.0042 | 148.748 | 0 | 5.8637 | 0 | 25.0555 | 0 | 0.077539 | 18.189 | 0 | 0 | 152.8155 | 0 | 0 | 445.5094 | 0.4857% | CZ 6B | 3.8299 | 1.6656 | 3.8102 | 0 | 0 | 1.7181 | 0 | 7.3413 | 0 | 0.022719 | 5.3294 | 0 | 0 | 21.0625 | 0 | 0 | 44.7797 | 0.4857% | CZ 6B | 0 | 0 | 0.63 | 1.4875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.9268 | 0.4857% | CZ 6B | 40.0954 | 17.4367 | 108.7483 | 162.5816 | 0 | 17.9864 | 0 | 76.8558 | 0 | 0.23785 | 55.7932 | 0 | 0 | 308.9599 | 0 | 0 | 788.6952 | 0.4857%
CZ 7 | 0.38951 | 0.16903 | 1.063 | 2.3419 | 0 | 0.17982 | 0 | 0.70184 | 0 | 0.0023014 | 0.53854 | 0 | 0 | 2.9429 | 0 | 0 | 8.3288 | 0.4495% | CZ 7 | 13.1231 | 5.6948 | 80.7003 | 234.1859 | 0 | 6.0584 | 0 | 23.646 | 0 | 0.077539 | 18.1442 | 0 | 0 | 152.8155 | 0 | 0 | 534.4458 | 0.4495% | CZ 7 | 3.8451 | 1.6686 | 3.8107 | 0 | 0 | 1.7751 | 0 | 6.9283 | 0 | 0.022719 | 5.3162 | 0 | 0 | 21.0625 | 0 | 0 | 44.4293 | 0.4495% | CZ 7 | 0 | 0 | 0.67694 | 2.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.8281 | 0.4495% | CZ 7 | 40.254 | 17.4684 | 113.8845 | 255.9652 | 0 | 18.5836 | 0 | 72.5323 | 0 | 0.23785 | 55.6558 | 0 | 0 | 308.9599 | 0 | 0 | 883.5416 | 0.4495%
CZ 8 | 0.3962 | 0.1701 | 1.1152 | 3.1947 | 0 | 0.050222 | 0 | 0.68123 | 0 | 0.0023014 | 0.53552 | 0 | 0 | 2.9429 | 0 | 0 | 9.0884 | 0.02085% | CZ 8 | 13.3488 | 5.731 | 85.9148 | 319.4688 | 0 | 1.6921 | 0 | 22.9516 | 0 | 0.077539 | 18.0425 | 0 | 0 | 152.8155 | 0 | 0 | 620.0427 | 0.02085% | CZ 8 | 3.9112 | 1.6792 | 3.8117 | 0 | 0 | 0.49578 | 0 | 6.7248 | 0 | 0.022719 | 5.2865 | 0 | 0 | 21.0625 | 0 | 0 | 42.9945 | 0.02085% | CZ 8 | 0 | 0 | 0.72905 | 3.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.733 | 0.02085% | CZ 8 | 40.9464 | 17.5794 | 119.5908 | 349.1794 | 0 | 5.1903 | 0 | 70.4022 | 0 | 0.23785 | 55.344 | 0 | 0 | 308.9599 | 0 | 0 | 967.4302 | 0.02085%
US Weighted | 0.39218 | 0.16886 | 0.91799 | 0.84055 | 0 | 0.6705 | 0 | 0.79228 | 0 | 0.0023014 | 0.54646 | 0 | 0 | 2.9429 | 0 | 0 | 7.2741 | 100% | US Weighted | 13.2131 | 5.6893 | 66.2157 | 84.0554 | 0 | 22.5901 | 0 | 26.6933 | 0 | 0.077539 | 18.4111 | 0 | 0 | 152.8155 | 0 | 0 | 389.7611 | 100% | US Weighted | 3.8714 | 1.667 | 3.8088 | 0 | 0 | 6.6189 | 0 | 7.8211 | 0 | 0.022719 | 5.3945 | 0 | 0 | 21.0625 | 0 | 0 | 50.2669 | 100% | US Weighted | 0 | 0 | 0.53217 | 0.84055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.182 | 100% | US Weighted | 40.53 | 17.4515 | 98.0396 | 91.8725 | 0 | 69.2934 | 0 | 81.8796 | 0 | 0.23785 | 56.4746 | 0 | 0 | 308.9599 | 0 | 0 | 764.7389 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.94947 | 0.2975 | 0.80186 | 0.039966 | 0 | 2.1647 | 0 | 1.1112 | 0 | 0.0023014 | 0.55623 | 0 | 0 | 2.945 | 0 | 0 | 8.8682 | 2.444% | CZ 1A | 31.9893 | 10.0232 | 53.9041 | 3.9966 | 0 | 72.9334 | 0 | 37.4377 | 0 | 0.077539 | 18.7404 | 0 | 0 | 152.8844 | 0 | 0 | 381.9867 | 2.444% | CZ 1A | 9.3729 | 2.9368 | 3.9127 | 0 | 0 | 21.3695 | 0 | 10.9692 | 0 | 0.022719 | 5.4909 | 0 | 0 | 21.0827 | 0 | 0 | 75.1575 | 2.444% | CZ 1A | 0 | 0 | 0.4055 | 0.039966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2548 | 2.444% | CZ 1A | 98.1244 | 30.7455 | 85.2835 | 4.3683 | 0 | 223.7173 | 0 | 114.837 | 0 | 0.23785 | 57.4846 | 0 | 0 | 309.1713 | 0 | 0 | 923.9697 | 2.444%
CZ 1B | 0.94947 | 0.29709 | 0.80217 | 0.14002 | 0 | 2.5195 | 0 | 1.5717 | 0 | 0.0023014 | 0.55833 | 0 | 0 | 2.945 | 0 | 0 | 9.7855 | 0% | CZ 1B | 31.9893 | 10.0095 | 53.9489 | 14.0019 | 0 | 84.8848 | 0 | 52.9524 | 0 | 0.077539 | 18.811 | 0 | 0 | 152.8844 | 0 | 0 | 419.5598 | 0% | CZ 1B | 9.3729 | 2.9328 | 3.9107 | 0 | 0 | 24.8713 | 0 | 15.5151 | 0 | 0.022719 | 5.5116 | 0 | 0 | 21.0827 | 0 | 0 | 83.2197 | 0% | CZ 1B | 0 | 0 | 0.40602 | 0.14002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3553 | 0% | CZ 1B | 98.1244 | 30.7032 | 85.3189 | 15.3041 | 0 | 260.3772 | 0 | 162.4272 | 0 | 0.23785 | 57.7013 | 0 | 0 | 309.1713 | 0 | 0 | 1019.3654 | 0%
CZ 2A | 0.94947 | 0.29699 | 0.8405 | 0.22965 | 0 | 2.0303 | 0 | 1.4706 | 0 | 0.0023014 | 0.55383 | 0 | 0 | 2.945 | 0 | 0 | 9.3186 | 17.24% | CZ 2A | 31.9893 | 10.006 | 57.7612 | 22.965 | 0 | 68.4052 | 0 | 49.5459 | 0 | 0.077539 | 18.6594 | 0 | 0 | 152.8844 | 0 | 0 | 412.2938 | 17.24% | CZ 2A | 9.3729 | 2.9318 | 3.9137 | 0 | 0 | 20.0427 | 0 | 14.5169 | 0 | 0.022719 | 5.4672 | 0 | 0 | 21.0827 | 0 | 0 | 77.3507 | 17.24% | CZ 2A | 0 | 0 | 0.44404 | 0.22965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.483 | 17.24% | CZ 2A | 98.1244 | 30.6926 | 89.5061 | 25.1008 | 0 | 209.8272 | 0 | 151.9779 | 0 | 0.23785 | 57.2362 | 0 | 0 | 309.1713 | 0 | 0 | 971.8742 | 17.24%
CZ 2B | 0.94947 | 0.29724 | 0.84277 | 0.24667 | 0 | 1.3978 | 0 | 1.5795 | 0 | 0.0023014 | 0.55173 | 0 | 0 | 2.945 | 0 | 0 | 8.8125 | 3.722% | CZ 2B | 31.9893 | 10.0146 | 57.992 | 24.667 | 0 | 47.0956 | 0 | 53.2161 | 0 | 0.077539 | 18.5888 | 0 | 0 | 152.8844 | 0 | 0 | 396.5253 | 3.722% | CZ 2B | 9.3729 | 2.9343 | 3.9132 | 0 | 0 | 13.799 | 0 | 15.5923 | 0 | 0.022719 | 5.4465 | 0 | 0 | 21.0827 | 0 | 0 | 72.1637 | 3.722% | CZ 2B | 0 | 0 | 0.44636 | 0.24667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.5023 | 3.722% | CZ 2B | 98.1244 | 30.719 | 89.755 | 26.9611 | 0 | 144.462 | 0 | 163.2359 | 0 | 0.23785 | 57.0195 | 0 | 0 | 309.1713 | 0 | 0 | 919.686 | 3.722%
CZ 3A | 0.94947 | 0.29714 | 0.90709 | 0.61017 | 0 | 1.1449 | 0 | 1.4399 | 0 | 0.0023014 | 0.54672 | 0 | 0 | 2.945 | 0 | 0 | 8.8426 | 18.17% | CZ 3A | 31.9893 | 10.0112 | 64.3969 | 61.0172 | 0 | 38.5732 | 0 | 48.512 | 0 | 0.077539 | 18.4199 | 0 | 0 | 152.8844 | 0 | 0 | 425.8817 | 18.17% | CZ 3A | 9.3729 | 2.9333 | 3.9173 | 0 | 0 | 11.302 | 0 | 14.214 | 0 | 0.022719 | 5.397 | 0 | 0 | 21.0827 | 0 | 0 | 68.2419 | 18.17% | CZ 3A | 0 | 0 | 0.51027 | 0.61017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9297 | 18.17% | CZ 3A | 98.1244 | 30.7085 | 96.7828 | 66.6918 | 0 | 118.3201 | 0 | 148.8066 | 0 | 0.23785 | 56.5015 | 0 | 0 | 309.1713 | 0 | 0 | 925.3449 | 18.17%
CZ 3B | 0.94947 | 0.29714 | 0.88978 | 0.3921 | 0 | 0.99151 | 0 | 1.5396 | 0 | 0.0023014 | 0.54876 | 0 | 0 | 2.945 | 0 | 0 | 8.5556 | 7.194% | CZ 3B | 31.9893 | 10.0112 | 62.6794 | 39.2099 | 0 | 33.4056 | 0 | 51.8703 | 0 | 0.077539 | 18.4888 | 0 | 0 | 152.8844 | 0 | 0 | 400.6164 | 7.194% | CZ 3B | 9.3729 | 2.9333 | 3.9152 | 0 | 0 | 9.7879 | 0 | 15.198 | 0 | 0.022719 | 5.4172 | 0 | 0 | 21.0827 | 0 | 0 | 67.7299 | 7.194% | CZ 3B | 0 | 0 | 0.49317 | 0.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6946 | 7.194% | CZ 3B | 98.1244 | 30.7085 | 94.892 | 42.8564 | 0 | 102.4691 | 0 | 159.108 | 0 | 0.23785 | 56.7129 | 0 | 0 | 309.1713 | 0 | 0 | 894.2803 | 7.194%
CZ 3C | 0.94947 | 0.29709 | 0.91424 | 0.49661 | 0 | 0.28809 | 0 | 1.0665 | 0 | 0.0023014 | 0.54887 | 0 | 0 | 2.945 | 0 | 0 | 7.5082 | 0.8731% | CZ 3C | 31.9893 | 10.0095 | 65.1222 | 49.6613 | 0 | 9.7062 | 0 | 35.9334 | 0 | 0.077539 | 18.4923 | 0 | 0 | 152.8844 | 0 | 0 | 373.876 | 0.8731% | CZ 3C | 9.3729 | 2.9328 | 3.9157 | 0 | 0 | 2.8439 | 0 | 10.5285 | 0 | 0.022719 | 5.4182 | 0 | 0 | 21.0827 | 0 | 0 | 56.1175 | 0.8731% | CZ 3C | 0 | 0 | 0.51758 | 0.49661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8235 | 0.8731% | CZ 3C | 98.1244 | 30.7032 | 97.5653 | 54.2798 | 0 | 29.7729 | 0 | 110.2228 | 0 | 0.23785 | 56.7235 | 0 | 0 | 309.1713 | 0 | 0 | 786.8011 | 0.8731%
CZ 4A | 0.94947 | 0.29673 | 0.95977 | 1.1196 | 0 | 0.66532 | 0 | 1.0583 | 0 | 0.0023014 | 0.54063 | 0 | 0 | 2.945 | 0 | 0 | 8.5371 | 18.87% | CZ 4A | 31.9893 | 9.9974 | 69.6408 | 111.9603 | 0 | 22.4157 | 0 | 35.6543 | 0 | 0.077539 | 18.2148 | 0 | 0 | 152.8844 | 0 | 0 | 452.8345 | 18.87% | CZ 4A | 9.3729 | 2.9292 | 3.9208 | 0 | 0 | 6.5678 | 0 | 10.4467 | 0 | 0.022719 | 5.3369 | 0 | 0 | 21.0827 | 0 | 0 | 59.6798 | 18.87% | CZ 4A | 0 | 0 | 0.56259 | 1.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4915 | 18.87% | CZ 4A | 98.1244 | 30.6662 | 102.5381 | 122.3726 | 0 | 68.7584 | 0 | 109.3666 | 0 | 0.23785 | 55.8725 | 0 | 0 | 309.1713 | 0 | 0 | 897.108 | 18.87%
CZ 4B | 0.94947 | 0.29694 | 0.94437 | 0.69496 | 0 | 0.57781 | 0 | 1.5669 | 0 | 0.0023014 | 0.54432 | 0 | 0 | 2.945 | 0 | 0 | 8.522 | 0.9164% | CZ 4B | 31.9893 | 10.0043 | 68.1214 | 69.4963 | 0 | 19.4675 | 0 | 52.7905 | 0 | 0.077539 | 18.3389 | 0 | 0 | 152.8844 | 0 | 0 | 423.17 | 0.9164% | CZ 4B | 9.3729 | 2.9313 | 3.9178 | 0 | 0 | 5.704 | 0 | 15.4676 | 0 | 0.022719 | 5.3733 | 0 | 0 | 21.0827 | 0 | 0 | 63.8722 | 0.9164% | CZ 4B | 0 | 0 | 0.5475 | 0.69496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0518 | 0.9164% | CZ 4B | 98.1244 | 30.6873 | 100.857 | 75.9594 | 0 | 59.715 | 0 | 161.9304 | 0 | 0.23785 | 56.2531 | 0 | 0 | 309.1713 | 0 | 0 | 892.9358 | 0.9164%
CZ 4C | 0.94947 | 0.29637 | 0.9756 | 1.0094 | 0 | 0.132 | 0 | 1.0263 | 0 | 0.0023014 | 0.539 | 0 | 0 | 2.945 | 0 | 0 | 7.8754 | 1.521% | CZ 4C | 31.9893 | 9.9853 | 71.2205 | 100.942 | 0 | 4.4473 | 0 | 34.5774 | 0 | 0.077539 | 18.1597 | 0 | 0 | 152.8844 | 0 | 0 | 424.2833 | 1.521% | CZ 4C | 9.3729 | 2.9257 | 3.9213 | 0 | 0 | 1.3031 | 0 | 10.1312 | 0 | 0.022719 | 5.3208 | 0 | 0 | 21.0827 | 0 | 0 | 54.0803 | 1.521% | CZ 4C | 0 | 0 | 0.57837 | 1.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3971 | 1.521% | CZ 4C | 98.1244 | 30.6292 | 104.2681 | 110.3296 | 0 | 13.6418 | 0 | 106.0632 | 0 | 0.23785 | 55.7034 | 0 | 0 | 309.1713 | 0 | 0 | 828.1688 | 1.521%
CZ 5A | 0.94947 | 0.29678 | 1.0039 | 1.5296 | 0 | 0.36035 | 0 | 1.0111 | 0 | 0.0023014 | 0.53782 | 0 | 0 | 2.945 | 0 | 0 | 8.6364 | 20.24% | CZ 5A | 31.9893 | 9.9991 | 74.0456 | 152.9617 | 0 | 12.1409 | 0 | 34.0673 | 0 | 0.077539 | 18.1201 | 0 | 0 | 152.8844 | 0 | 0 | 486.286 | 20.24% | CZ 5A | 9.3729 | 2.9297 | 3.9218 | 0 | 0 | 3.5573 | 0 | 9.9817 | 0 | 0.022719 | 5.3092 | 0 | 0 | 21.0827 | 0 | 0 | 56.1781 | 20.24% | CZ 5A | 0 | 0 | 0.60661 | 1.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.9455 | 20.24% | CZ 5A | 98.1244 | 30.6715 | 107.3595 | 167.1871 | 0 | 37.2413 | 0 | 104.4987 | 0 | 0.23785 | 55.5818 | 0 | 0 | 309.1713 | 0 | 0 | 910.0734 | 20.24%
CZ 5B | 0.94947 | 0.29683 | 0.99086 | 1.0449 | 0 | 0.43605 | 0 | 1.477 | 0 | 0.0023014 | 0.54166 | 0 | 0 | 2.945 | 0 | 0 | 8.6841 | 4.792% | CZ 5B | 31.9893 | 10.0008 | 72.7605 | 104.4942 | 0 | 14.6911 | 0 | 49.7613 | 0 | 0.077539 | 18.2493 | 0 | 0 | 152.8844 | 0 | 0 | 454.9084 | 4.792% | CZ 5B | 9.3729 | 2.9302 | 3.9193 | 0 | 0 | 4.3045 | 0 | 14.5801 | 0 | 0.022719 | 5.347 | 0 | 0 | 21.0827 | 0 | 0 | 61.5594 | 4.792% | CZ 5B | 0 | 0 | 0.59384 | 1.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4481 | 4.792% | CZ 5B | 98.1244 | 30.6768 | 105.9378 | 114.2121 | 0 | 45.0638 | 0 | 152.6386 | 0 | 0.23785 | 55.9782 | 0 | 0 | 309.1713 | 0 | 0 | 912.0408 | 4.792%
CZ 5C | 0.94947 | 0.29637 | 1.0009 | 1.1655 | 0 | 0.040505 | 0 | 0.97745 | 0 | 0.0023014 | 0.53623 | 0 | 0 | 2.945 | 0 | 0 | 7.9137 | 0.02749% | CZ 5C | 31.9893 | 9.9853 | 73.7356 | 116.5512 | 0 | 1.3647 | 0 | 32.9318 | 0 | 0.077539 | 18.0667 | 0 | 0 | 152.8844 | 0 | 0 | 437.5864 | 0.02749% | CZ 5C | 9.3729 | 2.9257 | 3.9228 | 0 | 0 | 0.39985 | 0 | 9.649 | 0 | 0.022719 | 5.2935 | 0 | 0 | 21.0827 | 0 | 0 | 52.6692 | 0.02749% | CZ 5C | 0 | 0 | 0.60347 | 1.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.5783 | 0.02749% | CZ 5C | 98.1244 | 30.6292 | 107.0274 | 127.3904 | 0 | 4.1861 | 0 | 101.0156 | 0 | 0.23785 | 55.418 | 0 | 0 | 309.1713 | 0 | 0 | 833.2002 | 0.02749%
CZ 6A | 0.94947 | 0.29668 | 1.0364 | 1.9949 | 0 | 0.40434 | 0 | 1.0231 | 0 | 0.0023014 | 0.53716 | 0 | 0 | 2.945 | 0 | 0 | 9.1894 | 3.027% | CZ 6A | 31.9893 | 9.9957 | 77.2963 | 199.4895 | 0 | 13.6228 | 0 | 34.4705 | 0 | 0.077539 | 18.0977 | 0 | 0 | 152.8844 | 0 | 0 | 537.9237 | 3.027% | CZ 6A | 9.3729 | 2.9287 | 3.9223 | 0 | 0 | 3.9915 | 0 | 10.0999 | 0 | 0.022719 | 5.3026 | 0 | 0 | 21.0827 | 0 | 0 | 56.7233 | 3.027% | CZ 6A | 0 | 0 | 0.6391 | 1.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.4433 | 3.027% | CZ 6A | 98.1244 | 30.6609 | 110.9159 | 218.042 | 0 | 41.7868 | 0 | 105.7355 | 0 | 0.23785 | 55.5131 | 0 | 0 | 309.1713 | 0 | 0 | 970.1877 | 3.027%
CZ 6B | 0.94947 | 0.29648 | 1.0279 | 1.5045 | 0 | 0.28482 | 0 | 1.4023 | 0 | 0.0023014 | 0.53792 | 0 | 0 | 2.945 | 0 | 0 | 8.9508 | 0.4857% | CZ 6B | 31.9893 | 9.9888 | 76.4539 | 150.4518 | 0 | 9.5959 | 0 | 47.2473 | 0 | 0.077539 | 18.1235 | 0 | 0 | 152.8844 | 0 | 0 | 496.8124 | 0.4857% | CZ 6B | 9.3729 | 2.9267 | 3.9213 | 0 | 0 | 2.8116 | 0 | 13.8435 | 0 | 0.022719 | 5.3102 | 0 | 0 | 21.0827 | 0 | 0 | 59.2916 | 0.4857% | CZ 6B | 0 | 0 | 0.63071 | 1.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.9445 | 0.4857% | CZ 6B | 98.1244 | 30.6398 | 109.9883 | 164.4438 | 0 | 29.4347 | 0 | 144.9271 | 0 | 0.23785 | 55.5924 | 0 | 0 | 309.1713 | 0 | 0 | 942.5596 | 0.4857%
CZ 7 | 0.94947 | 0.29627 | 1.0753 | 2.488 | 0 | 0.28241 | 0 | 1.0116 | 0 | 0.0023014 | 0.53547 | 0 | 0 | 2.945 | 0 | 0 | 9.5857 | 0.4495% | CZ 7 | 31.9893 | 9.9819 | 81.1724 | 248.8011 | 0 | 9.5149 | 0 | 34.0811 | 0 | 0.077539 | 18.0408 | 0 | 0 | 152.8844 | 0 | 0 | 586.5434 | 0.4495% | CZ 7 | 9.3729 | 2.9247 | 3.9233 | 0 | 0 | 2.7879 | 0 | 9.9858 | 0 | 0.022719 | 5.286 | 0 | 0 | 21.0827 | 0 | 0 | 55.3859 | 0.4495% | CZ 7 | 0 | 0 | 0.67782 | 2.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.9751 | 0.4495% | CZ 7 | 98.1244 | 30.6186 | 115.1592 | 271.9396 | 0 | 29.1863 | 0 | 104.541 | 0 | 0.23785 | 55.3387 | 0 | 0 | 309.1713 | 0 | 0 | 1014.3169 | 0.4495%
CZ 8 | 0.94947 | 0.29463 | 1.1276 | 3.4242 | 0 | 0.085971 | 0 | 0.97918 | 0 | 0.0023014 | 0.53214 | 0 | 0 | 2.945 | 0 | 0 | 10.3405 | 0.02085% | CZ 8 | 31.9893 | 9.9268 | 86.3955 | 342.4218 | 0 | 2.8965 | 0 | 32.9904 | 0 | 0.077539 | 17.9288 | 0 | 0 | 152.8844 | 0 | 0 | 677.5109 | 0.02085% | CZ 8 | 9.3729 | 2.9085 | 3.9248 | 0 | 0 | 0.84868 | 0 | 9.6662 | 0 | 0.022719 | 5.2531 | 0 | 0 | 21.0827 | 0 | 0 | 53.0797 | 0.02085% | CZ 8 | 0 | 0 | 0.73 | 3.4242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.9635 | 0.02085% | CZ 8 | 98.1244 | 30.4495 | 120.8783 | 374.267 | 0 | 8.8848 | 0 | 101.1953 | 0 | 0.23785 | 54.9951 | 0 | 0 | 309.1713 | 0 | 0 | 1098.2036 | 0.02085%
US Weighted | 0.94947 | 0.29693 | 0.92972 | 0.86576 | 0 | 0.97855 | 0 | 1.2692 | 0 | 0.0023014 | 0.54481 | 0 | 0 | 2.945 | 0 | 0 | 8.7817 | 100% | US Weighted | 31.9893 | 10.004 | 66.6533 | 86.5756 | 0 | 32.969 | 0 | 42.76 | 0 | 0.077539 | 18.3555 | 0 | 0 | 152.8844 | 0 | 0 | 442.2687 | 100% | US Weighted | 9.3729 | 2.9312 | 3.9182 | 0 | 0 | 9.6599 | 0 | 12.5287 | 0 | 0.022719 | 5.3782 | 0 | 0 | 21.0827 | 0 | 0 | 64.8945 | 100% | US Weighted | 0 | 0 | 0.53281 | 0.86576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2079 | 100% | US Weighted | 98.1244 | 30.6864 | 99.2552 | 94.6272 | 0 | 101.1297 | 0 | 131.1629 | 0 | 0.23785 | 56.3041 | 0 | 0 | 309.1713 | 0 | 0 | 920.699 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.94947 | 0.2975 | 0.80188 | 0.021568 | 0 | 2.0835 | 0 | 1.0746 | 0 | 0.0023014 | 0.55306 | 0 | 0 | 2.945 | 0 | 0 | 8.7288 | 2.444% | CZ 1A | 31.9893 | 10.0232 | 53.9058 | 2.1568 | 0 | 70.1972 | 0 | 36.204 | 0 | 0.077539 | 18.6336 | 0 | 0 | 152.8844 | 0 | 0 | 376.0717 | 2.444% | CZ 1A | 9.3729 | 2.9368 | 3.9127 | 0 | 0 | 20.5678 | 0 | 10.6078 | 0 | 0.022719 | 5.4596 | 0 | 0 | 21.0827 | 0 | 0 | 73.963 | 2.444% | CZ 1A | 0 | 0 | 0.40552 | 0.021568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2364 | 2.444% | CZ 1A | 98.1244 | 30.7455 | 85.2854 | 2.3574 | 0 | 215.324 | 0 | 111.0526 | 0 | 0.23785 | 57.1569 | 0 | 0 | 309.1713 | 0 | 0 | 909.4553 | 2.444%
CZ 1B | 0.94947 | 0.29709 | 0.80236 | 0.11292 | 0 | 2.5707 | 0 | 1.6239 | 0 | 0.0023014 | 0.55465 | 0 | 0 | 2.945 | 0 | 0 | 9.8584 | 0% | CZ 1B | 31.9893 | 10.0095 | 53.9644 | 11.2922 | 0 | 86.6114 | 0 | 54.7117 | 0 | 0.077539 | 18.687 | 0 | 0 | 152.8844 | 0 | 0 | 420.2272 | 0% | CZ 1B | 9.3729 | 2.9328 | 3.9112 | 0 | 0 | 25.3771 | 0 | 16.0305 | 0 | 0.022719 | 5.4753 | 0 | 0 | 21.0827 | 0 | 0 | 84.2052 | 0% | CZ 1B | 0 | 0 | 0.40616 | 0.11292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3284 | 0% | CZ 1B | 98.1244 | 30.7032 | 85.3392 | 12.3423 | 0 | 265.6732 | 0 | 167.8237 | 0 | 0.23785 | 57.3207 | 0 | 0 | 309.1713 | 0 | 0 | 1026.7359 | 0%
CZ 2A | 0.94947 | 0.29699 | 0.84015 | 0.23594 | 0 | 2.0492 | 0 | 1.5281 | 0 | 0.0023014 | 0.55296 | 0 | 0 | 2.945 | 0 | 0 | 9.4 | 17.24% | CZ 2A | 31.9893 | 10.006 | 57.7336 | 23.5938 | 0 | 69.041 | 0 | 51.4826 | 0 | 0.077539 | 18.6301 | 0 | 0 | 152.8844 | 0 | 0 | 415.4383 | 17.24% | CZ 2A | 9.3729 | 2.9318 | 3.9127 | 0 | 0 | 20.229 | 0 | 15.0844 | 0 | 0.022719 | 5.4586 | 0 | 0 | 21.0827 | 0 | 0 | 78.0948 | 17.24% | CZ 2A | 0 | 0 | 0.4438 | 0.23594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.489 | 17.24% | CZ 2A | 98.1244 | 30.6926 | 89.4692 | 25.788 | 0 | 211.7775 | 0 | 157.9187 | 0 | 0.23785 | 57.1463 | 0 | 0 | 309.1713 | 0 | 0 | 980.3259 | 17.24%
CZ 2B | 0.94947 | 0.29724 | 0.84229 | 0.23716 | 0 | 1.6037 | 0 | 1.6752 | 0 | 0.0023014 | 0.55408 | 0 | 0 | 2.945 | 0 | 0 | 9.1065 | 3.722% | CZ 2B | 31.9893 | 10.0146 | 57.9541 | 23.7161 | 0 | 54.0328 | 0 | 56.4417 | 0 | 0.077539 | 18.668 | 0 | 0 | 152.8844 | 0 | 0 | 405.7786 | 3.722% | CZ 2B | 9.3729 | 2.9343 | 3.9117 | 0 | 0 | 15.8316 | 0 | 16.5374 | 0 | 0.022719 | 5.4697 | 0 | 0 | 21.0827 | 0 | 0 | 75.1631 | 3.722% | CZ 2B | 0 | 0 | 0.44604 | 0.23716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4925 | 3.722% | CZ 2B | 98.1244 | 30.719 | 89.7034 | 25.9217 | 0 | 165.7412 | 0 | 173.1303 | 0 | 0.23785 | 57.2626 | 0 | 0 | 309.1713 | 0 | 0 | 950.0117 | 3.722%
CZ 3A | 0.94947 | 0.29714 | 0.90581 | 0.70836 | 0 | 1.2256 | 0 | 1.5126 | 0 | 0.0023014 | 0.55255 | 0 | 0 | 2.945 | 0 | 0 | 9.0988 | 18.17% | CZ 3A | 31.9893 | 10.0112 | 64.2987 | 70.8365 | 0 | 41.2923 | 0 | 50.9605 | 0 | 0.077539 | 18.6163 | 0 | 0 | 152.8844 | 0 | 0 | 440.9667 | 18.17% | CZ 3A | 9.3729 | 2.9333 | 3.9127 | 0 | 0 | 12.0986 | 0 | 14.9314 | 0 | 0.022719 | 5.4546 | 0 | 0 | 21.0827 | 0 | 0 | 69.809 | 18.17% | CZ 3A | 0 | 0 | 0.50945 | 0.70836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0271 | 18.17% | CZ 3A | 98.1244 | 30.7085 | 96.6449 | 77.4243 | 0 | 126.6606 | 0 | 156.3172 | 0 | 0.23785 | 57.104 | 0 | 0 | 309.1713 | 0 | 0 | 952.393 | 18.17%
CZ 3B | 0.94947 | 0.29714 | 0.88877 | 0.44123 | 0 | 1.0635 | 0 | 1.6235 | 0 | 0.0023014 | 0.55393 | 0 | 0 | 2.945 | 0 | 0 | 8.7649 | 7.194% | CZ 3B | 31.9893 | 10.0112 | 62.6019 | 44.1229 | 0 | 35.8318 | 0 | 54.6997 | 0 | 0.077539 | 18.6628 | 0 | 0 | 152.8844 | 0 | 0 | 410.8815 | 7.194% | CZ 3B | 9.3729 | 2.9333 | 3.9117 | 0 | 0 | 10.4987 | 0 | 16.027 | 0 | 0.022719 | 5.4682 | 0 | 0 | 21.0827 | 0 | 0 | 69.3172 | 7.194% | CZ 3B | 0 | 0 | 0.49251 | 0.44123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.743 | 7.194% | CZ 3B | 98.1244 | 30.7085 | 94.7834 | 48.2264 | 0 | 109.911 | 0 | 167.7867 | 0 | 0.23785 | 57.2467 | 0 | 0 | 309.1713 | 0 | 0 | 916.1962 | 7.194%
CZ 3C | 0.94947 | 0.29709 | 0.91335 | 0.47706 | 0 | 0.36889 | 0 | 1.0615 | 0 | 0.0023014 | 0.55265 | 0 | 0 | 2.945 | 0 | 0 | 7.5673 | 0.8731% | CZ 3C | 31.9893 | 10.0095 | 65.0533 | 47.7061 | 0 | 12.4287 | 0 | 35.7628 | 0 | 0.077539 | 18.6198 | 0 | 0 | 152.8844 | 0 | 0 | 374.5313 | 0.8731% | CZ 3C | 9.3729 | 2.9328 | 3.9127 | 0 | 0 | 3.6416 | 0 | 10.4785 | 0 | 0.022719 | 5.4556 | 0 | 0 | 21.0827 | 0 | 0 | 56.8995 | 0.8731% | CZ 3C | 0 | 0 | 0.51699 | 0.47706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8034 | 0.8731% | CZ 3C | 98.1244 | 30.7032 | 97.4696 | 52.1428 | 0 | 38.124 | 0 | 109.6996 | 0 | 0.23785 | 57.1146 | 0 | 0 | 309.1713 | 0 | 0 | 792.7872 | 0.8731%
CZ 4A | 0.94947 | 0.29673 | 0.95752 | 1.3988 | 0 | 0.77073 | 0 | 1.0395 | 0 | 0.0023014 | 0.55214 | 0 | 0 | 2.945 | 0 | 0 | 8.9121 | 18.87% | CZ 4A | 31.9893 | 9.9974 | 69.4702 | 139.8762 | 0 | 25.967 | 0 | 35.0219 | 0 | 0.077539 | 18.6025 | 0 | 0 | 152.8844 | 0 | 0 | 483.8865 | 18.87% | CZ 4A | 9.3729 | 2.9292 | 3.9127 | 0 | 0 | 7.6083 | 0 | 10.2614 | 0 | 0.022719 | 5.4505 | 0 | 0 | 21.0827 | 0 | 0 | 60.6406 | 18.87% | CZ 4A | 0 | 0 | 0.56116 | 1.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.7692 | 18.87% | CZ 4A | 98.1244 | 30.6662 | 102.2973 | 152.8847 | 0 | 79.6518 | 0 | 107.4268 | 0 | 0.23785 | 57.0617 | 0 | 0 | 309.1713 | 0 | 0 | 937.5221 | 18.87%
CZ 4B | 0.94947 | 0.29694 | 0.94291 | 0.84787 | 0 | 0.63862 | 0 | 1.6668 | 0 | 0.0023014 | 0.55245 | 0 | 0 | 2.945 | 0 | 0 | 8.8423 | 0.9164% | CZ 4B | 31.9893 | 10.0043 | 68.0094 | 84.7867 | 0 | 21.5163 | 0 | 56.1557 | 0 | 0.077539 | 18.6129 | 0 | 0 | 152.8844 | 0 | 0 | 444.0364 | 0.9164% | CZ 4B | 9.3729 | 2.9313 | 3.9127 | 0 | 0 | 6.3043 | 0 | 16.4536 | 0 | 0.022719 | 5.4536 | 0 | 0 | 21.0827 | 0 | 0 | 65.5337 | 0.9164% | CZ 4B | 0 | 0 | 0.54655 | 0.84787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2037 | 0.9164% | CZ 4B | 98.1244 | 30.6873 | 100.7006 | 92.6719 | 0 | 65.9994 | 0 | 172.2529 | 0 | 0.23785 | 57.0935 | 0 | 0 | 309.1713 | 0 | 0 | 926.9391 | 0.9164%
CZ 4C | 0.94947 | 0.29637 | 0.97315 | 1.3072 | 0 | 0.16969 | 0 | 1.0125 | 0 | 0.0023014 | 0.5524 | 0 | 0 | 2.945 | 0 | 0 | 8.208 | 1.521% | CZ 4C | 31.9893 | 9.9853 | 71.0327 | 130.7168 | 0 | 5.7172 | 0 | 34.1121 | 0 | 0.077539 | 18.6112 | 0 | 0 | 152.8844 | 0 | 0 | 455.1265 | 1.521% | CZ 4C | 9.3729 | 2.9257 | 3.9127 | 0 | 0 | 1.6751 | 0 | 9.9949 | 0 | 0.022719 | 5.4531 | 0 | 0 | 21.0827 | 0 | 0 | 54.4398 | 1.521% | CZ 4C | 0 | 0 | 0.57679 | 1.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.6933 | 1.521% | CZ 4C | 98.1244 | 30.6292 | 104.0051 | 142.8734 | 0 | 17.5371 | 0 | 104.6361 | 0 | 0.23785 | 57.0882 | 0 | 0 | 309.1713 | 0 | 0 | 864.3026 | 1.521%
CZ 5A | 0.94947 | 0.29678 | 1.0013 | 1.9223 | 0 | 0.51399 | 0 | 1.0145 | 0 | 0.0023014 | 0.55188 | 0 | 0 | 2.945 | 0 | 0 | 9.1975 | 20.24% | CZ 5A | 31.9893 | 9.9991 | 73.8493 | 192.2284 | 0 | 17.3171 | 0 | 34.1793 | 0 | 0.077539 | 18.5939 | 0 | 0 | 152.8844 | 0 | 0 | 531.1183 | 20.24% | CZ 5A | 9.3729 | 2.9297 | 3.9127 | 0 | 0 | 5.0739 | 0 | 10.0145 | 0 | 0.022719 | 5.448 | 0 | 0 | 21.0827 | 0 | 0 | 57.8572 | 20.24% | CZ 5A | 0 | 0 | 0.60495 | 1.9223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3365 | 20.24% | CZ 5A | 98.1244 | 30.6715 | 107.0836 | 210.1056 | 0 | 53.1188 | 0 | 104.8422 | 0 | 0.23785 | 57.0353 | 0 | 0 | 309.1713 | 0 | 0 | 970.3906 | 20.24%
CZ 5B | 0.94947 | 0.29683 | 0.98899 | 1.3186 | 0 | 0.51107 | 0 | 1.6258 | 0 | 0.0023014 | 0.55229 | 0 | 0 | 2.945 | 0 | 0 | 9.1904 | 4.792% | CZ 5B | 31.9893 | 10.0008 | 72.6175 | 131.8623 | 0 | 17.2189 | 0 | 54.7772 | 0 | 0.077539 | 18.6077 | 0 | 0 | 152.8844 | 0 | 0 | 490.0357 | 4.792% | CZ 5B | 9.3729 | 2.9302 | 3.9127 | 0 | 0 | 5.0451 | 0 | 16.0497 | 0 | 0.022719 | 5.4521 | 0 | 0 | 21.0827 | 0 | 0 | 63.8682 | 4.792% | CZ 5B | 0 | 0 | 0.59264 | 1.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.7206 | 4.792% | CZ 5B | 98.1244 | 30.6768 | 105.7373 | 144.1255 | 0 | 52.8175 | 0 | 168.0245 | 0 | 0.23785 | 57.0776 | 0 | 0 | 309.1713 | 0 | 0 | 965.9928 | 4.792%
CZ 5C | 0.94947 | 0.29637 | 0.99795 | 1.6423 | 0 | 0.074106 | 0 | 0.97775 | 0 | 0.0023014 | 0.5524 | 0 | 0 | 2.945 | 0 | 0 | 8.4376 | 0.02749% | CZ 5C | 31.9893 | 9.9853 | 73.5133 | 164.2297 | 0 | 2.4968 | 0 | 32.9421 | 0 | 0.077539 | 18.6112 | 0 | 0 | 152.8844 | 0 | 0 | 486.7296 | 0.02749% | CZ 5C | 9.3729 | 2.9257 | 3.9127 | 0 | 0 | 0.73155 | 0 | 9.652 | 0 | 0.022719 | 5.4531 | 0 | 0 | 21.0827 | 0 | 0 | 53.1534 | 0.02749% | CZ 5C | 0 | 0 | 0.60159 | 1.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.0532 | 0.02749% | CZ 5C | 98.1244 | 30.6292 | 106.7164 | 179.5031 | 0 | 7.6586 | 0 | 101.0473 | 0 | 0.23785 | 57.0882 | 0 | 0 | 309.1713 | 0 | 0 | 890.1763 | 0.02749%
CZ 6A | 0.94947 | 0.29668 | 1.034 | 2.4049 | 0 | 0.53168 | 0 | 1.026 | 0 | 0.0023014 | 0.55081 | 0 | 0 | 2.945 | 0 | 0 | 9.7409 | 3.027% | CZ 6A | 31.9893 | 9.9957 | 77.1068 | 240.4944 | 0 | 17.9133 | 0 | 34.5687 | 0 | 0.077539 | 18.5577 | 0 | 0 | 152.8844 | 0 | 0 | 583.5879 | 3.027% | CZ 6A | 9.3729 | 2.9287 | 3.9137 | 0 | 0 | 5.2486 | 0 | 10.1286 | 0 | 0.022719 | 5.4374 | 0 | 0 | 21.0827 | 0 | 0 | 58.1354 | 3.027% | CZ 6A | 0 | 0 | 0.63749 | 2.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.8517 | 3.027% | CZ 6A | 98.1244 | 30.6609 | 110.6509 | 262.8604 | 0 | 54.9476 | 0 | 106.0367 | 0 | 0.23785 | 56.9243 | 0 | 0 | 309.1713 | 0 | 0 | 1029.6144 | 3.027%
CZ 6B | 0.94947 | 0.29648 | 1.0256 | 1.8463 | 0 | 0.35069 | 0 | 1.5383 | 0 | 0.0023014 | 0.55168 | 0 | 0 | 2.945 | 0 | 0 | 9.5057 | 0.4857% | CZ 6B | 31.9893 | 9.9888 | 76.2713 | 184.6297 | 0 | 11.8153 | 0 | 51.8273 | 0 | 0.077539 | 18.587 | 0 | 0 | 152.8844 | 0 | 0 | 538.0705 | 0.4857% | CZ 6B | 9.3729 | 2.9267 | 3.9132 | 0 | 0 | 3.4619 | 0 | 15.1854 | 0 | 0.022719 | 5.446 | 0 | 0 | 21.0827 | 0 | 0 | 61.4115 | 0.4857% | CZ 6B | 0 | 0 | 0.62916 | 1.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.2847 | 0.4857% | CZ 6B | 98.1244 | 30.6398 | 109.7343 | 201.8002 | 0 | 36.2423 | 0 | 158.9758 | 0 | 0.23785 | 57.0142 | 0 | 0 | 309.1713 | 0 | 0 | 1001.9402 | 0.4857%
CZ 7 | 0.94947 | 0.29627 | 1.0725 | 2.9493 | 0 | 0.42306 | 0 | 1.0226 | 0 | 0.0023014 | 0.55045 | 0 | 0 | 2.945 | 0 | 0 | 10.211 | 0.4495% | CZ 7 | 31.9893 | 9.9819 | 80.9656 | 294.9327 | 0 | 14.2534 | 0 | 34.4516 | 0 | 0.077539 | 18.5457 | 0 | 0 | 152.8844 | 0 | 0 | 638.0821 | 0.4495% | CZ 7 | 9.3729 | 2.9247 | 3.9137 | 0 | 0 | 4.1763 | 0 | 10.0943 | 0 | 0.022719 | 5.4339 | 0 | 0 | 21.0827 | 0 | 0 | 57.0212 | 0.4495% | CZ 7 | 0 | 0 | 0.67608 | 2.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.4347 | 0.4495% | CZ 7 | 98.1244 | 30.6186 | 114.8686 | 322.3615 | 0 | 43.7213 | 0 | 105.6773 | 0 | 0.23785 | 56.8873 | 0 | 0 | 309.1713 | 0 | 0 | 1081.6681 | 0.4495%
CZ 8 | 0.94947 | 0.29463 | 1.1246 | 3.9396 | 0 | 0.23971 | 0 | 0.97366 | 0 | 0.0023014 | 0.54943 | 0 | 0 | 2.945 | 0 | 0 | 11.0184 | 0.02085% | CZ 8 | 31.9893 | 9.9268 | 86.1716 | 393.9608 | 0 | 8.0761 | 0 | 32.8043 | 0 | 0.077539 | 18.5112 | 0 | 0 | 152.8844 | 0 | 0 | 734.402 | 0.02085% | CZ 8 | 9.3729 | 2.9085 | 3.9142 | 0 | 0 | 2.3663 | 0 | 9.6117 | 0 | 0.022719 | 5.4238 | 0 | 0 | 21.0827 | 0 | 0 | 54.7028 | 0.02085% | CZ 8 | 0 | 0 | 0.72812 | 3.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 5.477 | 0.02085% | CZ 8 | 98.1244 | 30.4495 | 120.5621 | 430.5992 | 0 | 24.7729 | 0 | 100.6244 | 0 | 0.23785 | 56.7816 | 0 | 0 | 309.1713 | 0 | 0 | 1171.3232 | 0.02085%
US Weighted | 0.94947 | 0.29693 | 0.92814 | 1.0548 | 0 | 1.0686 | 0 | 1.3067 | 0 | 0.0023014 | 0.5525 | 0 | 0 | 2.945 | 0 | 0 | 9.1044 | 100% | US Weighted | 31.9893 | 10.004 | 66.5328 | 105.4827 | 0 | 36.0027 | 0 | 44.0252 | 0 | 0.077539 | 18.6145 | 0 | 0 | 152.8844 | 0 | 0 | 465.6131 | 100% | US Weighted | 9.3729 | 2.9312 | 3.9126 | 0 | 0 | 10.5488 | 0 | 12.8994 | 0 | 0.022719 | 5.4541 | 0 | 0 | 21.0827 | 0 | 0 | 66.2244 | 100% | US Weighted | 0 | 0 | 0.53179 | 1.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3959 | 100% | US Weighted | 98.1244 | 30.6864 | 99.0862 | 115.2926 | 0 | 110.4354 | 0 | 135.0436 | 0 | 0.23785 | 57.0985 | 0 | 0 | 309.1713 | 0 | 0 | 955.1762 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.66568 | 0.20222 | 0.011584 | -0.00036176 | 0 | 0.58543 | 0 | 0.46729 | 0 | 0 | 0.11226 | 0 | 0 | 0.002864 | 0 | 0 | 2.047 | 2.444% | CZ 1A | 22.4278 | 6.8131 | 0.44282 | -0.036176 | 0 | 19.7243 | 0 | 15.7439 | 0 | 0 | 3.7822 | 0 | 0 | 0.096493 | 0 | 0 | 68.9944 | 2.444% | CZ 1A | 6.5713 | 1.9962 | 0.10653 | 0 | 0 | 5.7792 | 0 | 4.613 | 0 | 0 | 1.1082 | 0 | 0 | 0.028273 | 0 | 0 | 20.2028 | 2.444% | CZ 1A | 0 | 0 | 0.00079243 | -0.00036176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00043067 | 2.444% | CZ 1A | 68.7954 | 20.8987 | 1.2018 | -0.039541 | 0 | 60.5026 | 0 | 48.2932 | 0 | 0 | 11.6016 | 0 | 0 | 0.29599 | 0 | 0 | 211.5497 | 2.444%
CZ 1B | 0.66486 | 0.20196 | 0.011275 | -0.010612 | 0 | 0.73048 | 0 | 0.69892 | 0 | 0 | 0.11379 | 0 | 0 | 0.002864 | 0 | 0 | 2.4135 | 0% | CZ 1B | 22.4002 | 6.8045 | 0.42214 | -1.0612 | 0 | 24.611 | 0 | 23.5478 | 0 | 0 | 3.8339 | 0 | 0 | 0.096493 | 0 | 0 | 80.6549 | 0% | CZ 1B | 6.5633 | 1.9937 | 0.10501 | 0 | 0 | 7.211 | 0 | 6.8995 | 0 | 0 | 1.1233 | 0 | 0 | 0.028273 | 0 | 0 | 23.9241 | 0% | CZ 1B | 0 | 0 | 0.00063739 | -0.010612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0099743 | 0% | CZ 1B | 68.7109 | 20.8722 | 1.169 | -1.1599 | 0 | 75.4921 | 0 | 72.231 | 0 | 0 | 11.7601 | 0 | 0 | 0.29599 | 0 | 0 | 249.3715 | 0%
CZ 2A | 0.66629 | 0.20191 | 0.011326 | 0.019242 | 0 | 0.75216 | 0 | 0.9641 | 0 | 0 | 0.1142 | 0 | 0 | 0.002864 | 0 | 0 | 2.7321 | 17.24% | CZ 2A | 22.4485 | 6.8028 | 0.42042 | 1.9242 | 0 | 25.3416 | 0 | 32.4821 | 0 | 0 | 3.8477 | 0 | 0 | 0.096493 | 0 | 0 | 93.3637 | 17.24% | CZ 2A | 6.5774 | 1.9932 | 0.10602 | 0 | 0 | 7.4251 | 0 | 9.5172 | 0 | 0 | 1.1274 | 0 | 0 | 0.028273 | 0 | 0 | 26.7746 | 17.24% | CZ 2A | 0 | 0 | 0.00058571 | 0.019242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019828 | 17.24% | CZ 2A | 68.8589 | 20.867 | 1.174 | 2.1032 | 0 | 77.7331 | 0 | 99.6361 | 0 | 0 | 11.8024 | 0 | 0 | 0.29599 | 0 | 0 | 282.4706 | 17.24%
CZ 2B | 0.66731 | 0.20207 | 0.010708 | 0.025616 | 0 | 0.61914 | 0 | 0.82622 | 0 | 0 | 0.12044 | 0 | 0 | 0.002864 | 0 | 0 | 2.4744 | 3.722% | CZ 2B | 22.4829 | 6.8079 | 0.37218 | 2.5616 | 0 | 20.8598 | 0 | 27.8366 | 0 | 0 | 4.0579 | 0 | 0 | 0.096493 | 0 | 0 | 85.0755 | 3.722% | CZ 2B | 6.5875 | 1.9947 | 0.104 | 0 | 0 | 6.1119 | 0 | 8.1561 | 0 | 0 | 1.189 | 0 | 0 | 0.028273 | 0 | 0 | 24.1715 | 3.722% | CZ 2B | 0 | 0 | 0.00017227 | 0.025616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025788 | 3.722% | CZ 2B | 68.9646 | 20.8828 | 1.1076 | 2.7999 | 0 | 63.9857 | 0 | 85.3865 | 0 | 0 | 12.4472 | 0 | 0 | 0.29599 | 0 | 0 | 255.8703 | 3.722%
CZ 3A | 0.66379 | 0.20196 | 0.010638 | 0.089562 | 0 | 0.53332 | 0 | 1.0106 | 0 | 0 | 0.12131 | 0 | 0 | 0.002864 | 0 | 0 | 2.634 | 18.17% | CZ 3A | 22.3641 | 6.8045 | 0.36185 | 8.9562 | 0 | 17.9684 | 0 | 34.0484 | 0 | 0 | 4.0872 | 0 | 0 | 0.096493 | 0 | 0 | 94.6871 | 18.17% | CZ 3A | 6.5527 | 1.9937 | 0.10451 | 0 | 0 | 5.2648 | 0 | 9.9762 | 0 | 0 | 1.1975 | 0 | 0 | 0.028273 | 0 | 0 | 25.1176 | 18.17% | CZ 3A | 0 | 0 | 5.168e-05 | 0.089562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089614 | 18.17% | CZ 3A | 68.5999 | 20.8722 | 1.0997 | 9.7891 | 0 | 55.1167 | 0 | 104.4405 | 0 | 0 | 12.5371 | 0 | 0 | 0.29599 | 0 | 0 | 272.7513 | 18.17%
CZ 3B | 0.66517 | 0.20196 | 0.010347 | 0.07361 | 0 | 0.36966 | 0 | 0.84248 | 0 | 0 | 0.12377 | 0 | 0 | 0.002864 | 0 | 0 | 2.2899 | 7.194% | CZ 3B | 22.4106 | 6.8045 | 0.33945 | 7.361 | 0 | 12.4545 | 0 | 28.3845 | 0 | 0 | 4.1699 | 0 | 0 | 0.096493 | 0 | 0 | 82.021 | 7.194% | CZ 3B | 6.5663 | 1.9937 | 0.1035 | 0 | 0 | 3.6492 | 0 | 8.3167 | 0 | 0 | 1.2218 | 0 | 0 | 0.028273 | 0 | 0 | 21.8794 | 7.194% | CZ 3B | 0 | 0 | -0.00013781 | 0.07361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073472 | 7.194% | CZ 3B | 68.7426 | 20.8722 | 1.0685 | 8.0456 | 0 | 38.2032 | 0 | 87.0672 | 0 | 0 | 12.7908 | 0 | 0 | 0.29599 | 0 | 0 | 237.0861 | 7.194%
CZ 3C | 0.66368 | 0.20161 | 0.010879 | 0.089717 | 0 | 0.1902 | 0 | 0.65366 | 0 | 0 | 0.11967 | 0 | 0 | 0.002864 | 0 | 0 | 1.9323 | 0.8731% | CZ 3C | 22.3606 | 6.7924 | 0.38252 | 8.9717 | 0 | 6.4082 | 0 | 22.0229 | 0 | 0 | 4.032 | 0 | 0 | 0.096493 | 0 | 0 | 71.0669 | 0.8731% | CZ 3C | 6.5517 | 1.9902 | 0.10501 | 0 | 0 | 1.8776 | 0 | 6.4527 | 0 | 0 | 1.1814 | 0 | 0 | 0.028273 | 0 | 0 | 18.1868 | 0.8731% | CZ 3C | 0 | 0 | 0.00024117 | 0.089717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089958 | 0.8731% | CZ 3C | 68.5893 | 20.8353 | 1.1257 | 9.8061 | 0 | 19.6566 | 0 | 67.5534 | 0 | 0 | 12.368 | 0 | 0 | 0.29599 | 0 | 0 | 200.2303 | 0.8731%
CZ 4A | 0.66225 | 0.20109 | 0.01002 | 0.37019 | 0 | 0.37176 | 0 | 0.59172 | 0 | 0 | 0.12663 | 0 | 0 | 0.002864 | 0 | 0 | 2.3365 | 18.87% | CZ 4A | 22.3124 | 6.7752 | 0.31017 | 37.0186 | 0 | 12.5252 | 0 | 19.9362 | 0 | 0 | 4.2664 | 0 | 0 | 0.096493 | 0 | 0 | 103.2406 | 18.87% | CZ 4A | 6.5375 | 1.9851 | 0.10299 | 0 | 0 | 3.6699 | 0 | 5.8413 | 0 | 0 | 1.2501 | 0 | 0 | 0.028273 | 0 | 0 | 19.4152 | 18.87% | CZ 4A | 0 | 0 | -0.00041344 | 0.37019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36977 | 18.87% | CZ 4A | 68.4413 | 20.7824 | 1.033 | 40.4613 | 0 | 38.4199 | 0 | 61.1527 | 0 | 0 | 13.0868 | 0 | 0 | 0.29599 | 0 | 0 | 243.6735 | 18.87%
CZ 4B | 0.66675 | 0.20176 | 0.010243 | 0.23523 | 0 | 0.28031 | 0 | 1.1306 | 0 | 0 | 0.12576 | 0 | 0 | 0.002864 | 0 | 0 | 2.6535 | 0.9164% | CZ 4B | 22.464 | 6.7976 | 0.32912 | 23.5232 | 0 | 9.4443 | 0 | 38.0925 | 0 | 0 | 4.2371 | 0 | 0 | 0.096493 | 0 | 0 | 104.9842 | 0.9164% | CZ 4B | 6.582 | 1.9917 | 0.1035 | 0 | 0 | 2.7672 | 0 | 11.1611 | 0 | 0 | 1.2415 | 0 | 0 | 0.028273 | 0 | 0 | 23.8752 | 0.9164% | CZ 4B | 0 | 0 | -0.00024117 | 0.23523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23499 | 0.9164% | CZ 4B | 68.9064 | 20.8511 | 1.0572 | 25.7108 | 0 | 28.9696 | 0 | 116.8455 | 0 | 0 | 12.9969 | 0 | 0 | 0.29599 | 0 | 0 | 275.6335 | 0.9164%
CZ 4C | 0.66097 | 0.20069 | 0.0098135 | 0.40467 | 0 | 0.083772 | 0 | 0.62149 | 0 | 0 | 0.12878 | 0 | 0 | 0.002864 | 0 | 0 | 2.113 | 1.521% | CZ 4C | 22.2693 | 6.7614 | 0.29294 | 40.4674 | 0 | 2.8224 | 0 | 20.9391 | 0 | 0 | 4.3388 | 0 | 0 | 0.096493 | 0 | 0 | 97.9878 | 1.521% | CZ 4C | 6.5249 | 1.9811 | 0.10249 | 0 | 0 | 0.82697 | 0 | 6.1351 | 0 | 0 | 1.2713 | 0 | 0 | 0.028273 | 0 | 0 | 16.8701 | 1.521% | CZ 4C | 0 | 0 | -0.00056848 | 0.40467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40411 | 1.521% | CZ 4C | 68.3092 | 20.7401 | 1.0108 | 44.2309 | 0 | 8.6576 | 0 | 64.2288 | 0 | 0 | 13.3088 | 0 | 0 | 0.29599 | 0 | 0 | 220.7821 | 1.521%
CZ 5A | 0.66384 | 0.20145 | 0.0098135 | 0.48373 | 0 | 0.30205 | 0 | 0.58845 | 0 | 0 | 0.12898 | 0 | 0 | 0.002864 | 0 | 0 | 2.3812 | 20.24% | CZ 5A | 22.3658 | 6.7873 | 0.29294 | 48.3728 | 0 | 10.1766 | 0 | 19.8259 | 0 | 0 | 4.3456 | 0 | 0 | 0.096493 | 0 | 0 | 112.2634 | 20.24% | CZ 5A | 6.5532 | 1.9887 | 0.10249 | 0 | 0 | 2.9817 | 0 | 5.809 | 0 | 0 | 1.2733 | 0 | 0 | 0.028273 | 0 | 0 | 18.7366 | 20.24% | CZ 5A | 0 | 0 | -0.00056848 | 0.48373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48316 | 20.24% | CZ 5A | 68.6052 | 20.8194 | 1.0108 | 52.8715 | 0 | 31.2159 | 0 | 60.8144 | 0 | 0 | 13.3299 | 0 | 0 | 0.29599 | 0 | 0 | 248.963 | 20.24%
CZ 5B | 0.66476 | 0.2013 | 0.01002 | 0.32686 | 0 | 0.26149 | 0 | 1.109 | 0 | 0 | 0.12806 | 0 | 0 | 0.002864 | 0 | 0 | 2.7044 | 4.792% | CZ 5B | 22.3968 | 6.7821 | 0.31017 | 32.6861 | 0 | 8.8102 | 0 | 37.3653 | 0 | 0 | 4.3146 | 0 | 0 | 0.096493 | 0 | 0 | 112.7618 | 4.792% | CZ 5B | 6.5623 | 1.9872 | 0.10299 | 0 | 0 | 2.5814 | 0 | 10.948 | 0 | 0 | 1.2642 | 0 | 0 | 0.028273 | 0 | 0 | 23.4743 | 4.792% | CZ 5B | 0 | 0 | -0.00041344 | 0.32686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32645 | 4.792% | CZ 5B | 68.7003 | 20.8035 | 1.033 | 35.7259 | 0 | 27.0245 | 0 | 114.615 | 0 | 0 | 13.2348 | 0 | 0 | 0.29599 | 0 | 0 | 281.4331 | 4.792%
CZ 5C | 0.66123 | 0.20074 | 0.0095385 | 0.53766 | 0 | 0.049097 | 0 | 0.60236 | 0 | 0 | 0.13134 | 0 | 0 | 0.002864 | 0 | 0 | 2.1948 | 0.02749% | CZ 5C | 22.2779 | 6.7631 | 0.26882 | 53.7665 | 0 | 1.6542 | 0 | 20.2946 | 0 | 0 | 4.4249 | 0 | 0 | 0.096493 | 0 | 0 | 109.5465 | 0.02749% | CZ 5C | 6.5274 | 1.9816 | 0.10198 | 0 | 0 | 0.48467 | 0 | 5.9463 | 0 | 0 | 1.2965 | 0 | 0 | 0.028273 | 0 | 0 | 16.3668 | 0.02749% | CZ 5C | 0 | 0 | -0.00079243 | 0.53766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53687 | 0.02749% | CZ 5C | 68.3356 | 20.7454 | 0.98105 | 58.7668 | 0 | 5.074 | 0 | 62.2521 | 0 | 0 | 13.573 | 0 | 0 | 0.29599 | 0 | 0 | 230.0239 | 0.02749%
CZ 6A | 0.6666 | 0.2012 | 0.0099853 | 0.54867 | 0 | 0.28476 | 0 | 0.58467 | 0 | 0 | 0.12847 | 0 | 0 | 0.002864 | 0 | 0 | 2.4272 | 3.027% | CZ 6A | 22.4588 | 6.7787 | 0.30672 | 54.8673 | 0 | 9.5942 | 0 | 19.6984 | 0 | 0 | 4.3284 | 0 | 0 | 0.096493 | 0 | 0 | 118.129 | 3.027% | CZ 6A | 6.5804 | 1.9861 | 0.10299 | 0 | 0 | 2.8111 | 0 | 5.7716 | 0 | 0 | 1.2682 | 0 | 0 | 0.028273 | 0 | 0 | 18.5488 | 3.027% | CZ 6A | 0 | 0 | -0.0004479 | 0.54867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54822 | 3.027% | CZ 6A | 68.8906 | 20.793 | 1.0293 | 59.9699 | 0 | 29.4294 | 0 | 60.4233 | 0 | 0 | 13.2771 | 0 | 0 | 0.29599 | 0 | 0 | 254.1085 | 3.027%
CZ 6B | 0.66829 | 0.20115 | 0.0098135 | 0.39994 | 0 | 0.18974 | 0 | 1.0679 | 0 | 0 | 0.1298 | 0 | 0 | 0.002864 | 0 | 0 | 2.6695 | 0.4857% | CZ 6B | 22.5157 | 6.7769 | 0.29294 | 39.9937 | 0 | 6.3927 | 0 | 35.9799 | 0 | 0 | 4.3732 | 0 | 0 | 0.096493 | 0 | 0 | 116.4216 | 0.4857% | CZ 6B | 6.5971 | 1.9856 | 0.10249 | 0 | 0 | 1.8731 | 0 | 10.5421 | 0 | 0 | 1.2814 | 0 | 0 | 0.028273 | 0 | 0 | 22.41 | 0.4857% | CZ 6B | 0 | 0 | -0.00056848 | 0.39994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39937 | 0.4857% | CZ 6B | 69.065 | 20.7877 | 1.0108 | 43.7131 | 0 | 19.609 | 0 | 110.3655 | 0 | 0 | 13.4145 | 0 | 0 | 0.29599 | 0 | 0 | 278.2616 | 0.4857%
CZ 7 | 0.66783 | 0.20063 | 0.0099336 | 0.65362 | 0 | 0.25802 | 0 | 0.59311 | 0 | 0 | 0.1297 | 0 | 0 | 0.002864 | 0 | 0 | 2.5157 | 0.4495% | CZ 7 | 22.5002 | 6.7597 | 0.30155 | 65.3618 | 0 | 8.693 | 0 | 19.9827 | 0 | 0 | 4.3698 | 0 | 0 | 0.096493 | 0 | 0 | 128.0653 | 0.4495% | CZ 7 | 6.5926 | 1.9806 | 0.10299 | 0 | 0 | 2.5471 | 0 | 5.8549 | 0 | 0 | 1.2803 | 0 | 0 | 0.028273 | 0 | 0 | 18.3867 | 0.4495% | CZ 7 | 0 | 0 | -0.00049958 | 0.65362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65312 | 0.4495% | CZ 7 | 69.0174 | 20.7348 | 1.0236 | 71.4405 | 0 | 26.6651 | 0 | 61.2954 | 0 | 0 | 13.4039 | 0 | 0 | 0.29599 | 0 | 0 | 263.8767 | 0.4495%
CZ 8 | 0.65974 | 0.19736 | 0.0098135 | 0.79679 | 0 | 0.19649 | 0 | 0.56666 | 0 | 0 | 0.13185 | 0 | 0 | 0.002864 | 0 | 0 | 2.5616 | 0.02085% | CZ 8 | 22.2279 | 6.6494 | 0.29294 | 79.679 | 0 | 6.6201 | 0 | 19.0919 | 0 | 0 | 4.4421 | 0 | 0 | 0.096493 | 0 | 0 | 139.0999 | 0.02085% | CZ 8 | 6.5128 | 1.9483 | 0.10249 | 0 | 0 | 1.9397 | 0 | 5.5939 | 0 | 0 | 1.3015 | 0 | 0 | 0.028273 | 0 | 0 | 17.427 | 0.02085% | CZ 8 | 0 | 0 | -0.00056848 | 0.79679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79622 | 0.02085% | CZ 8 | 68.1823 | 20.3966 | 1.0108 | 87.0891 | 0 | 20.3067 | 0 | 58.5628 | 0 | 0 | 13.6259 | 0 | 0 | 0.29599 | 0 | 0 | 269.4702 | 0.02085%
US Weighted | 0.66437 | 0.20161 | 0.010407 | 0.24016 | 0 | 0.45064 | 0 | 0.78794 | 0 | 0 | 0.12333 | 0 | 0 | 0.002864 | 0 | 0 | 2.4813 | 100% | US Weighted | 22.3837 | 6.7925 | 0.34304 | 24.0155 | 0 | 15.183 | 0 | 26.547 | 0 | 0 | 4.1552 | 0 | 0 | 0.096493 | 0 | 0 | 99.5163 | 100% | US Weighted | 6.5584 | 1.9902 | 0.10386 | 0 | 0 | 4.4486 | 0 | 7.7783 | 0 | 0 | 1.2175 | 0 | 0 | 0.028273 | 0 | 0 | 22.1251 | 100% | US Weighted | 0 | 0 | -0.00011429 | 0.24016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24004 | 100% | US Weighted | 68.6602 | 20.8353 | 1.0748 | 26.249 | 0 | 46.5725 | 0 | 81.4306 | 0 | 0 | 12.7456 | 0 | 0 | 0.29599 | 0 | 0 | 257.864 | 100%
Building Type: | Full-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 70.11% | 67.97% | 1.445% | -1.677% | 0% | 28.1% | 0% | 43.49% | 0% | 0% | 20.3% | 0% | 0% | 0.09725% | 0% | 0% | 23.45% | 2.444% | CZ 1A | 70.11% | 67.97% | 0.8215% | -1.677% | 0% | 28.1% | 0% | 43.49% | 0% | 0% | 20.3% | 0% | 0% | 0.06312% | 0% | 0% | 18.35% | 2.444% | CZ 1A | 70.11% | 67.97% | 2.723% | 0% | 0% | 28.1% | 0% | 43.49% | 0% | 0% | 20.3% | 0% | 0% | 0.1341% | 0% | 0% | 27.31% | 2.444% | CZ 1A | 0% | 0% | 0.1954% | -1.677% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.03483% | 2.444% | CZ 1A | 70.11% | 67.97% | 1.409% | -1.677% | 0% | 28.1% | 0% | 43.49% | 0% | 0% | 20.3% | 0% | 0% | 0.09574% | 0% | 0% | 23.26% | 2.444%
CZ 1B | 70.02% | 67.98% | 1.405% | -9.397% | 0% | 28.42% | 0% | 43.04% | 0% | 0% | 20.52% | 0% | 0% | 0.09725% | 0% | 0% | 24.48% | 0% | CZ 1B | 70.02% | 67.98% | 0.7823% | -9.397% | 0% | 28.42% | 0% | 43.04% | 0% | 0% | 20.52% | 0% | 0% | 0.06312% | 0% | 0% | 19.19% | 0% | CZ 1B | 70.02% | 67.98% | 2.685% | 0% | 0% | 28.42% | 0% | 43.04% | 0% | 0% | 20.52% | 0% | 0% | 0.1341% | 0% | 0% | 28.41% | 0% | CZ 1B | 0% | 0% | 0.1569% | -9.397% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.7509% | 0% | CZ 1B | 70.02% | 67.98% | 1.37% | -9.397% | 0% | 28.42% | 0% | 43.04% | 0% | 0% | 20.52% | 0% | 0% | 0.09574% | 0% | 0% | 24.29% | 0%
CZ 2A | 70.18% | 67.99% | 1.348% | 8.156% | 0% | 36.71% | 0% | 63.09% | 0% | 0% | 20.65% | 0% | 0% | 0.09725% | 0% | 0% | 29.06% | 17.24% | CZ 2A | 70.18% | 67.99% | 0.7282% | 8.156% | 0% | 36.71% | 0% | 63.09% | 0% | 0% | 20.65% | 0% | 0% | 0.06312% | 0% | 0% | 22.47% | 17.24% | CZ 2A | 70.18% | 67.99% | 2.71% | 0% | 0% | 36.71% | 0% | 63.09% | 0% | 0% | 20.65% | 0% | 0% | 0.1341% | 0% | 0% | 34.28% | 17.24% | CZ 2A | 0% | 0% | 0.132% | 8.156% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.332% | 17.24% | CZ 2A | 70.18% | 67.99% | 1.312% | 8.156% | 0% | 36.71% | 0% | 63.09% | 0% | 0% | 20.65% | 0% | 0% | 0.09574% | 0% | 0% | 28.81% | 17.24%
CZ 2B | 70.28% | 67.98% | 1.271% | 10.8% | 0% | 38.61% | 0% | 49.32% | 0% | 0% | 21.74% | 0% | 0% | 0.09725% | 0% | 0% | 27.17% | 3.722% | CZ 2B | 70.28% | 67.98% | 0.6422% | 10.8% | 0% | 38.61% | 0% | 49.32% | 0% | 0% | 21.74% | 0% | 0% | 0.06312% | 0% | 0% | 20.97% | 3.722% | CZ 2B | 70.28% | 67.98% | 2.659% | 0% | 0% | 38.61% | 0% | 49.32% | 0% | 0% | 21.74% | 0% | 0% | 0.1341% | 0% | 0% | 32.16% | 3.722% | CZ 2B | 0% | 0% | 0.03862% | 10.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.728% | 3.722% | CZ 2B | 70.28% | 67.98% | 1.235% | 10.8% | 0% | 38.61% | 0% | 49.32% | 0% | 0% | 21.74% | 0% | 0% | 0.09574% | 0% | 0% | 26.93% | 3.722%
CZ 3A | 69.91% | 67.97% | 1.174% | 12.64% | 0% | 43.52% | 0% | 66.81% | 0% | 0% | 21.95% | 0% | 0% | 0.09725% | 0% | 0% | 28.95% | 18.17% | CZ 3A | 69.91% | 67.97% | 0.5628% | 12.64% | 0% | 43.52% | 0% | 66.81% | 0% | 0% | 21.95% | 0% | 0% | 0.06312% | 0% | 0% | 21.47% | 18.17% | CZ 3A | 69.91% | 67.97% | 2.671% | 0% | 0% | 43.52% | 0% | 66.81% | 0% | 0% | 21.95% | 0% | 0% | 0.1341% | 0% | 0% | 35.98% | 18.17% | CZ 3A | 0% | 0% | 0.01014% | 12.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.421% | 18.17% | CZ 3A | 69.91% | 67.97% | 1.138% | 12.64% | 0% | 43.52% | 0% | 66.81% | 0% | 0% | 21.95% | 0% | 0% | 0.09574% | 0% | 0% | 28.64% | 18.17%
CZ 3B | 70.06% | 67.97% | 1.164% | 16.68% | 0% | 34.76% | 0% | 51.89% | 0% | 0% | 22.34% | 0% | 0% | 0.09725% | 0% | 0% | 26.13% | 7.194% | CZ 3B | 70.06% | 67.97% | 0.5422% | 16.68% | 0% | 34.76% | 0% | 51.89% | 0% | 0% | 22.34% | 0% | 0% | 0.06312% | 0% | 0% | 19.96% | 7.194% | CZ 3B | 70.06% | 67.97% | 2.646% | 0% | 0% | 34.76% | 0% | 51.89% | 0% | 0% | 22.34% | 0% | 0% | 0.1341% | 0% | 0% | 31.56% | 7.194% | CZ 3B | 0% | 0% | -0.02798% | 16.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.215% | 7.194% | CZ 3B | 70.06% | 67.97% | 1.127% | 16.68% | 0% | 34.76% | 0% | 51.89% | 0% | 0% | 22.34% | 0% | 0% | 0.09574% | 0% | 0% | 25.88% | 7.194%
CZ 3C | 69.9% | 67.86% | 1.191% | 18.81% | 0% | 51.56% | 0% | 61.58% | 0% | 0% | 21.65% | 0% | 0% | 0.09725% | 0% | 0% | 25.53% | 0.8731% | CZ 3C | 69.9% | 67.86% | 0.588% | 18.81% | 0% | 51.56% | 0% | 61.58% | 0% | 0% | 21.65% | 0% | 0% | 0.06312% | 0% | 0% | 18.97% | 0.8731% | CZ 3C | 69.9% | 67.86% | 2.684% | 0% | 0% | 51.56% | 0% | 61.58% | 0% | 0% | 21.65% | 0% | 0% | 0.1341% | 0% | 0% | 31.96% | 0.8731% | CZ 3C | 0% | 0% | 0.04665% | 18.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.988% | 0.8731% | CZ 3C | 69.9% | 67.86% | 1.155% | 18.81% | 0% | 51.56% | 0% | 61.58% | 0% | 0% | 21.65% | 0% | 0% | 0.09574% | 0% | 0% | 25.26% | 0.8731%
CZ 4A | 69.75% | 67.77% | 1.046% | 26.47% | 0% | 48.23% | 0% | 56.92% | 0% | 0% | 22.93% | 0% | 0% | 0.09725% | 0% | 0% | 26.22% | 18.87% | CZ 4A | 69.75% | 67.77% | 0.4465% | 26.47% | 0% | 48.23% | 0% | 56.92% | 0% | 0% | 22.93% | 0% | 0% | 0.06312% | 0% | 0% | 21.34% | 18.87% | CZ 4A | 69.75% | 67.77% | 2.632% | 0% | 0% | 48.23% | 0% | 56.92% | 0% | 0% | 22.93% | 0% | 0% | 0.1341% | 0% | 0% | 32.02% | 18.87% | CZ 4A | 0% | 0% | -0.07368% | 26.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.35% | 18.87% | CZ 4A | 69.75% | 67.77% | 1.01% | 26.47% | 0% | 48.23% | 0% | 56.92% | 0% | 0% | 22.93% | 0% | 0% | 0.09574% | 0% | 0% | 25.99% | 18.87%
CZ 4B | 70.22% | 67.95% | 1.086% | 27.74% | 0% | 43.89% | 0% | 67.83% | 0% | 0% | 22.76% | 0% | 0% | 0.09725% | 0% | 0% | 30.01% | 0.9164% | CZ 4B | 70.22% | 67.95% | 0.4839% | 27.74% | 0% | 43.89% | 0% | 67.83% | 0% | 0% | 22.76% | 0% | 0% | 0.06312% | 0% | 0% | 23.64% | 0.9164% | CZ 4B | 70.22% | 67.95% | 2.645% | 0% | 0% | 43.89% | 0% | 67.83% | 0% | 0% | 22.76% | 0% | 0% | 0.1341% | 0% | 0% | 36.43% | 0.9164% | CZ 4B | 0% | 0% | -0.04413% | 27.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.66% | 0.9164% | CZ 4B | 70.22% | 67.95% | 1.05% | 27.74% | 0% | 43.89% | 0% | 67.83% | 0% | 0% | 22.76% | 0% | 0% | 0.09574% | 0% | 0% | 29.74% | 0.9164%
CZ 4C | 69.61% | 67.71% | 1.008% | 30.96% | 0% | 49.37% | 0% | 61.38% | 0% | 0% | 23.31% | 0% | 0% | 0.09725% | 0% | 0% | 25.74% | 1.521% | CZ 4C | 69.61% | 67.71% | 0.4124% | 30.96% | 0% | 49.37% | 0% | 61.38% | 0% | 0% | 23.31% | 0% | 0% | 0.06312% | 0% | 0% | 21.53% | 1.521% | CZ 4C | 69.61% | 67.71% | 2.619% | 0% | 0% | 49.37% | 0% | 61.38% | 0% | 0% | 23.31% | 0% | 0% | 0.1341% | 0% | 0% | 30.99% | 1.521% | CZ 4C | 0% | 0% | -0.09856% | 30.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15% | 1.521% | CZ 4C | 69.61% | 67.71% | 0.9719% | 30.96% | 0% | 49.37% | 0% | 61.38% | 0% | 0% | 23.31% | 0% | 0% | 0.09574% | 0% | 0% | 25.54% | 1.521%
CZ 5A | 69.92% | 67.88% | 0.9801% | 25.16% | 0% | 58.77% | 0% | 58.01% | 0% | 0% | 23.37% | 0% | 0% | 0.09725% | 0% | 0% | 25.89% | 20.24% | CZ 5A | 69.92% | 67.88% | 0.3967% | 25.16% | 0% | 58.77% | 0% | 58.01% | 0% | 0% | 23.37% | 0% | 0% | 0.06312% | 0% | 0% | 21.14% | 20.24% | CZ 5A | 69.92% | 67.88% | 2.619% | 0% | 0% | 58.77% | 0% | 58.01% | 0% | 0% | 23.37% | 0% | 0% | 0.1341% | 0% | 0% | 32.38% | 20.24% | CZ 5A | 0% | 0% | -0.09397% | 25.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.48% | 20.24% | CZ 5A | 69.92% | 67.88% | 0.9439% | 25.16% | 0% | 58.77% | 0% | 58.01% | 0% | 0% | 23.37% | 0% | 0% | 0.09574% | 0% | 0% | 25.66% | 20.24%
CZ 5B | 70.01% | 67.82% | 1.013% | 24.79% | 0% | 51.17% | 0% | 68.21% | 0% | 0% | 23.19% | 0% | 0% | 0.09725% | 0% | 0% | 29.43% | 4.792% | CZ 5B | 70.01% | 67.82% | 0.4271% | 24.79% | 0% | 51.17% | 0% | 68.21% | 0% | 0% | 23.19% | 0% | 0% | 0.06312% | 0% | 0% | 23.01% | 4.792% | CZ 5B | 70.01% | 67.82% | 2.632% | 0% | 0% | 51.17% | 0% | 68.21% | 0% | 0% | 23.19% | 0% | 0% | 0.1341% | 0% | 0% | 36.75% | 4.792% | CZ 5B | 0% | 0% | -0.06976% | 24.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12% | 4.792% | CZ 5B | 70.01% | 67.82% | 0.977% | 24.79% | 0% | 51.17% | 0% | 68.21% | 0% | 0% | 23.19% | 0% | 0% | 0.09574% | 0% | 0% | 29.13% | 4.792%
CZ 5C | 69.64% | 67.73% | 0.9558% | 32.74% | 0% | 66.25% | 0% | 61.61% | 0% | 0% | 23.78% | 0% | 0% | 0.09725% | 0% | 0% | 26.01% | 0.02749% | CZ 5C | 69.64% | 67.73% | 0.3657% | 32.74% | 0% | 66.25% | 0% | 61.61% | 0% | 0% | 23.78% | 0% | 0% | 0.06312% | 0% | 0% | 22.51% | 0.02749% | CZ 5C | 69.64% | 67.73% | 2.606% | 0% | 0% | 66.25% | 0% | 61.61% | 0% | 0% | 23.78% | 0% | 0% | 0.1341% | 0% | 0% | 30.79% | 0.02749% | CZ 5C | 0% | 0% | -0.1317% | 32.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.58% | 0.02749% | CZ 5C | 69.64% | 67.73% | 0.9193% | 32.74% | 0% | 66.25% | 0% | 61.61% | 0% | 0% | 23.78% | 0% | 0% | 0.09574% | 0% | 0% | 25.84% | 0.02749%
CZ 6A | 70.21% | 67.82% | 0.9657% | 22.81% | 0% | 53.56% | 0% | 56.98% | 0% | 0% | 23.32% | 0% | 0% | 0.09725% | 0% | 0% | 24.92% | 3.027% | CZ 6A | 70.21% | 67.82% | 0.3978% | 22.81% | 0% | 53.56% | 0% | 56.98% | 0% | 0% | 23.32% | 0% | 0% | 0.06312% | 0% | 0% | 20.24% | 3.027% | CZ 6A | 70.21% | 67.82% | 2.632% | 0% | 0% | 53.56% | 0% | 56.98% | 0% | 0% | 23.32% | 0% | 0% | 0.1341% | 0% | 0% | 31.91% | 3.027% | CZ 6A | 0% | 0% | -0.07026% | 22.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.23% | 3.027% | CZ 6A | 70.21% | 67.82% | 0.9302% | 22.81% | 0% | 53.56% | 0% | 56.98% | 0% | 0% | 23.32% | 0% | 0% | 0.09574% | 0% | 0% | 24.68% | 3.027%
CZ 6B | 70.39% | 67.85% | 0.9569% | 21.66% | 0% | 54.11% | 0% | 69.42% | 0% | 0% | 23.53% | 0% | 0% | 0.09725% | 0% | 0% | 28.08% | 0.4857% | CZ 6B | 70.39% | 67.85% | 0.3841% | 21.66% | 0% | 54.11% | 0% | 69.42% | 0% | 0% | 23.53% | 0% | 0% | 0.06312% | 0% | 0% | 21.64% | 0.4857% | CZ 6B | 70.39% | 67.85% | 2.619% | 0% | 0% | 54.11% | 0% | 69.42% | 0% | 0% | 23.53% | 0% | 0% | 0.1341% | 0% | 0% | 36.49% | 0.4857% | CZ 6B | 0% | 0% | -0.09036% | 21.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.16% | 0.4857% | CZ 6B | 70.39% | 67.85% | 0.9211% | 21.66% | 0% | 54.11% | 0% | 69.42% | 0% | 0% | 23.53% | 0% | 0% | 0.09574% | 0% | 0% | 27.77% | 0.4857%
CZ 7 | 70.34% | 67.72% | 0.9262% | 22.16% | 0% | 60.99% | 0% | 58% | 0% | 0% | 23.56% | 0% | 0% | 0.09725% | 0% | 0% | 24.64% | 0.4495% | CZ 7 | 70.34% | 67.72% | 0.3724% | 22.16% | 0% | 60.99% | 0% | 58% | 0% | 0% | 23.56% | 0% | 0% | 0.06312% | 0% | 0% | 20.07% | 0.4495% | CZ 7 | 70.34% | 67.72% | 2.632% | 0% | 0% | 60.99% | 0% | 58% | 0% | 0% | 23.56% | 0% | 0% | 0.1341% | 0% | 0% | 32.25% | 0.4495% | CZ 7 | 0% | 0% | -0.07389% | 22.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.73% | 0.4495% | CZ 7 | 70.34% | 67.72% | 0.8911% | 22.16% | 0% | 60.99% | 0% | 58% | 0% | 0% | 23.56% | 0% | 0% | 0.09574% | 0% | 0% | 24.4% | 0.4495%
CZ 8 | 69.49% | 66.98% | 0.8726% | 20.23% | 0% | 81.97% | 0% | 58.2% | 0% | 0% | 24% | 0% | 0% | 0.09725% | 0% | 0% | 23.25% | 0.02085% | CZ 8 | 69.49% | 66.98% | 0.3399% | 20.23% | 0% | 81.97% | 0% | 58.2% | 0% | 0% | 24% | 0% | 0% | 0.06312% | 0% | 0% | 18.94% | 0.02085% | CZ 8 | 69.49% | 66.98% | 2.618% | 0% | 0% | 81.97% | 0% | 58.2% | 0% | 0% | 24% | 0% | 0% | 0.1341% | 0% | 0% | 31.86% | 0.02085% | CZ 8 | 0% | 0% | -0.07808% | 20.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.54% | 0.02085% | CZ 8 | 69.49% | 66.98% | 0.8384% | 20.23% | 0% | 81.97% | 0% | 58.2% | 0% | 0% | 24% | 0% | 0% | 0.09574% | 0% | 0% | 23.01% | 0.02085%
US Weighted | 69.97% | 67.9% | 1.121% | 22.77% | 0% | 42.17% | 0% | 60.3% | 0% | 0% | 22.32% | 0% | 0% | 0.09725% | 0% | 0% | 27.25% | 100% | US Weighted | 69.97% | 67.9% | 0.5156% | 22.77% | 0% | 42.17% | 0% | 60.3% | 0% | 0% | 22.32% | 0% | 0% | 0.06312% | 0% | 0% | 21.37% | 100% | US Weighted | 69.97% | 67.9% | 2.654% | 0% | 0% | 42.17% | 0% | 60.3% | 0% | 0% | 22.32% | 0% | 0% | 0.1341% | 0% | 0% | 33.41% | 100% | US Weighted | 0% | 0% | -0.02149% | 22.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.02% | 100% | US Weighted | 69.97% | 67.9% | 1.085% | 22.77% | 0% | 42.17% | 0% | 60.3% | 0% | 0% | 22.32% | 0% | 0% | 0.09574% | 0% | 0% | 27% | 100%

## AptMR
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Mid-rise Apartment | [14 empty] | Prototype Floor Area: | 33741 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.092829 | 0.021634 | 0.3129 | 0.029273 | 0 | 0.12212 | 0 | 0.16073 | 0.023109 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1888 |  | STD2016 | 3.1276 | 0.72887 | 10.5421 | 2.9273 | 0 | 4.1144 | 0 | 5.4153 | 0.77859 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.9945 |  | STD2016 | 0.91638 | 0.21356 | 3.0888 | 0 | 0 | 1.2055 | 0 | 1.5867 | 0.22813 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.4467 |  | STD2016 | 0 | 0 | 0 | 0.029273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029273 |  | STD2016 | 9.5935 | 2.2358 | 32.3369 | 3.1995 | 0 | 12.6205 | 0 | 16.6109 | 2.3883 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 123.035
STD2013 | 0.11767 | 0.032866 | 0.31286 | 0.028713 | 0 | 0.12795 | 0 | 0.16832 | 0.022032 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2366 |  | STD2013 | 3.9646 | 1.1073 | 10.5407 | 2.8713 | 0 | 4.3109 | 0 | 5.6709 | 0.74228 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.5684 |  | STD2013 | 1.1616 | 0.32444 | 3.0884 | 0 | 0 | 1.2631 | 0 | 1.6616 | 0.21749 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9243 |  | STD2013 | 0 | 0 | 0 | 0.028713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028713 |  | STD2013 | 12.1611 | 3.3966 | 32.3327 | 3.1383 | 0 | 13.2232 | 0 | 17.3949 | 2.2769 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 127.9733
STD2010 | 0.1376 | 0.032866 | 0.31321 | 0.054862 | 0 | 0.15099 | 0 | 0.18035 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2964 |  | STD2010 | 4.6361 | 1.1073 | 10.5526 | 5.4862 | 0 | 5.0872 | 0 | 6.0764 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 47.3157 |  | STD2010 | 1.3584 | 0.32444 | 3.0919 | 0 | 0 | 1.4906 | 0 | 1.7804 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.256 |  | STD2010 | 0 | 0 | 0 | 0.054862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054862 |  | STD2010 | 14.221 | 3.3966 | 32.3694 | 5.9964 | 0 | 15.6047 | 0 | 18.6387 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 134.3048
STD2007 | 0.1263 | 0.060824 | 0.3133 | 0.074881 | 0 | 0.15226 | 0 | 0.19351 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3528 |  | STD2007 | 4.2551 | 2.0493 | 10.5555 | 7.4881 | 0 | 5.1298 | 0 | 6.5198 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.5427 |  | STD2007 | 1.2468 | 0.60043 | 3.0928 | 0 | 0 | 1.503 | 0 | 1.9103 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.615 |  | STD2007 | 0 | 0 | 0 | 0.074881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074881 |  | STD2007 | 13.0522 | 6.286 | 32.3782 | 8.1845 | 0 | 15.7352 | 0 | 19.999 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 140.251
STD2004 | 0.1263 | 0.060824 | 0.31333 | 0.084013 | 0 | 0.19457 | 0 | 0.20917 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4199 |  | STD2004 | 4.2551 | 2.0493 | 10.5565 | 8.4013 | 0 | 6.5554 | 0 | 7.0472 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 53.4099 |  | STD2004 | 1.2468 | 0.60043 | 3.0931 | 0 | 0 | 1.9207 | 0 | 2.0648 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.1875 |  | STD2004 | 0 | 0 | 0 | 0.084013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084013 |  | STD2004 | 13.0522 | 6.286 | 32.3813 | 9.1826 | 0 | 20.108 | 0 | 21.6167 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 147.2427
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 3.0143e-05 | 0.009132 | 0 | 0.042312 | 0 | 0.015653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067127 |  | 2004-2007 | 0 | 0 | 0.0010156 | 0.9132 | 0 | 1.4256 | 0 | 0.52736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8672 |  | 2004-2007 | 0 | 0 | 0.00029757 | 0 | 0 | 0.41769 | 0 | 0.15452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57251 |  | 2004-2007 | 0 | 0 | 0 | 0.009132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009132 |  | 2004-2007 | 0 | 0 | 0.0031152 | 0.99812 | 0 | 4.3728 | 0 | 1.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9917
2007-2010 | -0.011309 | 0.027958 | 8.5584e-05 | 0.020019 | 0 | 0.0012627 | 0 | 0.013163 | 0 | 0 | 0 | 0.0035777 | 0 | 0 | 0 | 0.0016262 | 0.056383 |  | 2007-2010 | -0.38101 | 0.94196 | 0.0028835 | 2.0019 | 0 | 0.042543 | 0 | 0.44347 | 0 | 0 | 0 | 0.12054 | 0 | 0 | 0 | 0.054791 | 3.2271 |  | 2007-2010 | -0.11163 | 0.27599 | 0.00084485 | 0 | 0 | 0.012465 | 0 | 0.12994 | 0 | 0 | 0 | 0.035318 | 0 | 0 | 0 | 0.016054 | 0.35898 |  | 2007-2010 | 0 | 0 | 0 | 0.020019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020019 |  | 2007-2010 | -1.1687 | 2.8894 | 0.0088448 | 2.1881 | 0 | 0.1305 | 0 | 1.3603 | 0 | 0 | 0 | 0.36974 | 0 | 0 | 0 | 0.16807 | 5.9462
2010-2013 | 0.019932 | 0 | 0.00035449 | 0.026149 | 0 | 0.023043 | 0 | 0.012035 | -0.022032 | 0 | 0 | 0.00027521 | 0 | 0 | 0 | 0 | 0.059758 |  | 2010-2013 | 0.67154 | 0 | 0.011943 | 2.6149 | 0 | 0.77637 | 0 | 0.40549 | -0.74228 | 0 | 0 | 0.0092723 | 0 | 0 | 0 | 0 | 3.7473 |  | 2010-2013 | 0.19676 | 0 | 0.0034994 | 0 | 0 | 0.22748 | 0 | 0.11881 | -0.21749 | 0 | 0 | 0.0027168 | 0 | 0 | 0 | 0 | 0.33178 |  | 2010-2013 | 0 | 0 | 0 | 0.026149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026149 |  | 2010-2013 | 2.0599 | 0 | 0.036635 | 2.8581 | 0 | 2.3815 | 0 | 1.2438 | -2.2769 | 0 | 0 | 0.028442 | 0 | 0 | 0 | 0 | 6.3315
2013-2016 | 0.024844 | 0.011232 | -4.0103e-05 | -0.00055982 | 0 | 0.0058319 | 0 | 0.0075862 | -0.0010778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047817 |  | 2013-2016 | 0.83703 | 0.37844 | -0.0013511 | -0.055982 | 0 | 0.19649 | 0 | 0.25559 | -0.036314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5739 |  | 2013-2016 | 0.24525 | 0.11088 | -0.00039589 | 0 | 0 | 0.05757 | 0 | 0.074889 | -0.01064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47756 |  | 2013-2016 | 0 | 0 | 0 | -0.00055982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00055982 |  | 2013-2016 | 2.5675 | 1.1608 | -0.0041445 | -0.061188 | 0 | 0.6027 | 0 | 0.78401 | -0.11139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9383
2004-2016 | 0.033467 | 0.03919 | 0.00043011 | 0.05474 | 0 | 0.07245 | 0 | 0.048437 | -0.023109 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.23108 |  | 2004-2016 | 1.1276 | 1.3204 | 0.014491 | 5.474 | 0 | 2.441 | 0 | 1.6319 | -0.77859 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 11.4154 |  | 2004-2016 | 0.33038 | 0.38688 | 0.0042459 | 0 | 0 | 0.71521 | 0 | 0.47815 | -0.22813 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.7408 |  | 2004-2016 | 0 | 0 | 0 | 0.05474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05474 |  | 2004-2016 | 3.4587 | 4.0502 | 0.044451 | 5.9831 | 0 | 7.4875 | 0 | 5.0058 | -2.3883 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 24.2077
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.00962% | 10.87% |  | 21.75% |  | 7.483% |  |  |  | 0% |  |  |  | 0% | 4.728% |  | 2004-2007 | 0% | 0% | 0.00962% | 10.87% |  | 21.75% |  | 7.483% |  |  |  | 0% |  |  |  | 0% | 5.368% |  | 2004-2007 | 0% | 0% | 0.00962% |  |  | 21.75% |  | 7.483% |  |  |  | 0% |  |  |  | 0% | 4.341% |  | 2004-2007 |  |  |  | 10.87% | [12 empty] | 10.87% |  | 2004-2007 | 0% | 0% | 0.00962% | 10.87% |  | 21.75% |  | 7.483% |  |  |  | 0% |  |  |  | 0% | 4.748%
2007-2010 | -8.954% | 45.97% | 0.02732% | 26.73% |  | 0.8293% |  | 6.802% |  |  |  | 3.311% |  |  |  | 0.5025% | 4.168% |  | 2007-2010 | -8.954% | 45.97% | 0.02732% | 26.73% |  | 0.8293% |  | 6.802% |  |  |  | 3.311% |  |  |  | 0.5025% | 6.385% |  | 2007-2010 | -8.954% | 45.97% | 0.02732% |  |  | 0.8293% |  | 6.802% |  |  |  | 3.311% |  |  |  | 0.5025% | 2.846% |  | 2007-2010 |  |  |  | 26.73% | [12 empty] | 26.73% |  | 2007-2010 | -8.954% | 45.97% | 0.02732% | 26.73% |  | 0.8293% |  | 6.802% |  |  |  | 3.311% |  |  |  | 0.5025% | 4.24%
2010-2013 | 14.48% | 0% | 0.1132% | 47.66% |  | 15.26% |  | 6.673% |  |  |  | 0.2634% |  |  |  | 0% | 4.61% |  | 2010-2013 | 14.48% | 0% | 0.1132% | 47.66% |  | 15.26% |  | 6.673% |  |  |  | 0.2634% |  |  |  | 0% | 7.92% |  | 2010-2013 | 14.48% | 0% | 0.1132% |  |  | 15.26% |  | 6.673% |  |  |  | 0.2634% |  |  |  | 0% | 2.707% |  | 2010-2013 |  |  |  | 47.66% | [12 empty] | 47.66% |  | 2010-2013 | 14.48% | 0% | 0.1132% | 47.66% |  | 15.26% |  | 6.673% |  |  |  | 0.2634% |  |  |  | 0% | 4.714%
2013-2016 | 21.11% | 34.18% | -0.01282% | -1.95% |  | 4.558% |  | 4.507% | -4.892% |  |  | 0% |  |  |  | 0% | 3.867% |  | 2013-2016 | 21.11% | 34.18% | -0.01282% | -1.95% |  | 4.558% |  | 4.507% | -4.892% |  |  | 0% |  |  |  | 0% | 3.612% |  | 2013-2016 | 21.11% | 34.18% | -0.01282% |  |  | 4.558% |  | 4.507% | -4.892% |  |  | 0% |  |  |  | 0% | 4.005% |  | 2013-2016 |  |  |  | -1.95% | [12 empty] | -1.95% |  | 2013-2016 | 21.11% | 34.18% | -0.01282% | -1.95% |  | 4.558% |  | 4.507% | -4.892% |  |  | 0% |  |  |  | 0% | 3.859%
2004-2016 | 26.5% | 64.43% | 0.1373% | 65.16% |  | 37.24% |  | 23.16% |  |  |  | 3.565% |  |  |  | 0.5025% | 16.27% |  | 2004-2016 | 26.5% | 64.43% | 0.1373% | 65.16% |  | 37.24% |  | 23.16% |  |  |  | 3.565% |  |  |  | 0.5025% | 21.37% |  | 2004-2016 | 26.5% | 64.43% | 0.1373% |  |  | 37.24% |  | 23.16% |  |  |  | 3.565% |  |  |  | 0.5025% | 13.2% |  | 2004-2016 |  |  |  | 65.16% | [12 empty] | 65.16% |  | 2004-2016 | 26.5% | 64.43% | 0.1373% | 65.16% |  | 37.24% |  | 23.16% |  |  |  | 3.565% |  |  |  | 0.5025% | 16.44%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.092829 | 0.021675 | 0.2464 | 0 | 0 | 0.26353 | 0 | 0.15754 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2082 | 4.661% | CZ 1A | 3.1276 | 0.73026 | 8.3018 | 0 | 0 | 8.8786 | 0 | 5.3077 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.7064 | 4.661% | CZ 1A | 0.91638 | 0.21397 | 2.4324 | 0 | 0 | 2.6014 | 0 | 1.5551 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.927 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 9.5935 | 2.24 | 25.465 | 0 | 0 | 27.2344 | 0 | 16.2808 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 124.8634 | 4.661%
CZ 1B | 0.092829 | 0.02165 | 0.24729 | 0.00072194 | 0 | 0.29011 | 0 | 0.20526 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2841 | 0% | CZ 1B | 3.1276 | 0.72942 | 8.3316 | 0.072194 | 0 | 9.7744 | 0 | 6.9154 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.311 | 0% | CZ 1B | 0.91638 | 0.21372 | 2.4411 | 0 | 0 | 2.8639 | 0 | 2.0262 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.669 | 0% | CZ 1B | 0 | 0 | 0 | 0.00072194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072194 | 0% | CZ 1B | 9.5935 | 2.2374 | 25.5563 | 0.078908 | 0 | 29.9821 | 0 | 21.2125 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 132.7104 | 0%
CZ 2A | 0.092829 | 0.021633 | 0.26692 | 0.0033793 | 0 | 0.20905 | 0 | 0.1488 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1688 | 16.19% | CZ 2A | 3.1276 | 0.72886 | 8.993 | 0.33793 | 0 | 7.0433 | 0 | 5.0135 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 39.6046 | 16.19% | CZ 2A | 0.91638 | 0.21355 | 2.6349 | 0 | 0 | 2.0637 | 0 | 1.469 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.5051 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.0033793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033793 | 16.19% | CZ 2A | 9.5935 | 2.2357 | 27.5852 | 0.36936 | 0 | 21.6046 | 0 | 15.3785 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 120.8165 | 16.19%
CZ 2B | 0.092829 | 0.021641 | 0.26828 | 0.0019551 | 0 | 0.18085 | 0 | 0.19373 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1855 | 1.276% | CZ 2B | 3.1276 | 0.72914 | 9.0388 | 0.19551 | 0 | 6.0933 | 0 | 6.5271 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.0719 | 1.276% | CZ 2B | 0.91638 | 0.21364 | 2.6484 | 0 | 0 | 1.7853 | 0 | 1.9124 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.6838 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0019551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019551 | 1.276% | CZ 2B | 9.5935 | 2.2366 | 27.7257 | 0.2137 | 0 | 18.6906 | 0 | 20.0214 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 122.5311 | 1.276%
CZ 3A | 0.092829 | 0.021666 | 0.302 | 0.035027 | 0 | 0.11999 | 0 | 0.15477 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1525 | 11.24% | CZ 3A | 3.1276 | 0.72998 | 10.1748 | 3.5027 | 0 | 4.0427 | 0 | 5.2144 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.1526 | 11.24% | CZ 3A | 0.91638 | 0.21388 | 2.9812 | 0 | 0 | 1.1845 | 0 | 1.5278 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.0314 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.035027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035027 | 11.24% | CZ 3A | 9.5935 | 2.2392 | 31.2103 | 3.8284 | 0 | 12.4007 | 0 | 15.9947 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 119.3163 | 11.24%
CZ 3B | 0.092829 | 0.02165 | 0.29274 | 0.0036181 | 0 | 0.13951 | 0 | 0.18096 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1976 | 11.78% | CZ 3B | 3.1276 | 0.72942 | 9.8629 | 0.36181 | 0 | 4.7005 | 0 | 6.0969 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.5883 | 11.78% | CZ 3B | 0.91638 | 0.21372 | 2.8898 | 0 | 0 | 1.3772 | 0 | 1.7864 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.7864 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.0036181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036181 | 11.78% | CZ 3B | 9.5935 | 2.2374 | 30.2536 | 0.39546 | 0 | 14.4183 | 0 | 18.7018 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 123.7868 | 11.78%
CZ 3C | 0.092829 | 0.02165 | 0.30539 | 0.0025535 | 0 | 0.062756 | 0 | 0.13585 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.0473 | 3.558% | CZ 3C | 3.1276 | 0.72942 | 10.2891 | 0.25535 | 0 | 2.1144 | 0 | 4.5771 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 35.4534 | 3.558% | CZ 3C | 0.91638 | 0.21372 | 3.0147 | 0 | 0 | 0.61951 | 0 | 1.3411 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 10.313 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0025535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025535 | 3.558% | CZ 3C | 9.5935 | 2.2374 | 31.561 | 0.27909 | 0 | 6.4856 | 0 | 14.04 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 108.2463 | 3.558%
CZ 4A | 0.092829 | 0.021625 | 0.32926 | 0.030785 | 0 | 0.1038 | 0 | 0.16499 | 0.043642 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2132 | 21.56% | CZ 4A | 3.1276 | 0.72858 | 11.0933 | 3.0785 | 0 | 3.497 | 0 | 5.5589 | 1.4704 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.9147 | 21.56% | CZ 4A | 0.91638 | 0.21347 | 3.2503 | 0 | 0 | 1.0246 | 0 | 1.6287 | 0.43081 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.672 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.030785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030785 | 21.56% | CZ 4A | 9.5935 | 2.2348 | 34.0277 | 3.3648 | 0 | 10.7269 | 0 | 17.0514 | 4.5102 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 125.559 | 21.56%
CZ 4B | 0.092829 | 0.021633 | 0.32129 | 0.020023 | 0 | 0.11269 | 0 | 0.19896 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1937 | 0.2995% | CZ 4B | 3.1276 | 0.72886 | 10.8249 | 2.0023 | 0 | 3.7966 | 0 | 6.7033 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.544 | 0.2995% | CZ 4B | 0.91638 | 0.21355 | 3.1717 | 0 | 0 | 1.1124 | 0 | 1.9641 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.5857 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.020023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020023 | 0.2995% | CZ 4B | 9.5935 | 2.2357 | 33.2046 | 2.1885 | 0 | 11.6457 | 0 | 20.5618 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 123.4795 | 0.2995%
CZ 4C | 0.092829 | 0.021608 | 0.33778 | 0.040375 | 0 | 0.038971 | 0 | 0.15753 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1153 | 4.986% | CZ 4C | 3.1276 | 0.72801 | 11.3804 | 4.0375 | 0 | 1.313 | 0 | 5.3074 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.2544 | 4.986% | CZ 4C | 0.91638 | 0.21331 | 3.3345 | 0 | 0 | 0.38471 | 0 | 1.5551 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 10.6116 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.040375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040375 | 4.986% | CZ 4C | 9.5935 | 2.2331 | 34.9086 | 4.413 | 0 | 4.0275 | 0 | 16.28 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 115.5054 | 4.986%
CZ 5A | 0.092829 | 0.021608 | 0.35247 | 0.057297 | 0 | 0.066526 | 0 | 0.15231 | 0.045443 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2147 | 15.67% | CZ 5A | 3.1276 | 0.72801 | 11.8752 | 5.7297 | 0 | 2.2414 | 0 | 5.1315 | 1.531 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.7249 | 15.67% | CZ 5A | 0.91638 | 0.21331 | 3.4794 | 0 | 0 | 0.65672 | 0 | 1.5035 | 0.4486 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.4256 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.057297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057297 | 15.67% | CZ 5A | 9.5935 | 2.2331 | 36.4263 | 6.2626 | 0 | 6.8752 | 0 | 15.7404 | 4.6964 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 125.8772 | 15.67%
CZ 5B | 0.092829 | 0.021625 | 0.34585 | 0.055086 | 0 | 0.078643 | 0 | 0.1871 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2074 | 4.35% | CZ 5B | 3.1276 | 0.72858 | 11.6524 | 5.5086 | 0 | 2.6496 | 0 | 6.3037 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.331 | 4.35% | CZ 5B | 0.91638 | 0.21347 | 3.4142 | 0 | 0 | 0.77634 | 0 | 1.847 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.375 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.055086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055086 | 4.35% | CZ 5B | 9.5935 | 2.2348 | 35.7429 | 6.0209 | 0 | 8.1275 | 0 | 19.3362 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 125.1055 | 4.35%
CZ 5C | 0.092829 | 0.0216 | 0.35097 | 0.038993 | 0 | 0.029064 | 0 | 0.14471 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1044 | 0.08141% | CZ 5C | 3.1276 | 0.72773 | 11.8247 | 3.8993 | 0 | 0.97921 | 0 | 4.8755 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 39.7945 | 0.08141% | CZ 5C | 0.91638 | 0.21323 | 3.4646 | 0 | 0 | 0.28691 | 0 | 1.4285 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 10.5173 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.038993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038993 | 0.08141% | CZ 5C | 9.5935 | 2.2323 | 36.2712 | 4.2619 | 0 | 3.0036 | 0 | 14.9553 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 114.3675 | 0.08141%
CZ 6A | 0.092829 | 0.021625 | 0.36956 | 0.10278 | 0 | 0.070854 | 0 | 0.15965 | 0.043642 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2872 | 3.16% | CZ 6A | 3.1276 | 0.72858 | 12.451 | 10.2776 | 0 | 2.3872 | 0 | 5.3788 | 1.4704 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 50.1815 | 3.16% | CZ 6A | 0.91638 | 0.21347 | 3.6481 | 0 | 0 | 0.69945 | 0 | 1.576 | 0.43081 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.6918 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.10278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10278 | 3.16% | CZ 6A | 9.5935 | 2.2348 | 38.1923 | 11.2335 | 0 | 7.3225 | 0 | 16.4989 | 4.5102 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 133.6354 | 3.16%
CZ 6B | 0.092829 | 0.021608 | 0.36515 | 0.060758 | 0 | 0.063031 | 0 | 0.1808 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2504 | 0.7689% | CZ 6B | 3.1276 | 0.72801 | 12.3026 | 6.0758 | 0 | 2.1236 | 0 | 6.0913 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 46.1581 | 0.7689% | CZ 6B | 0.91638 | 0.21331 | 3.6047 | 0 | 0 | 0.62222 | 0 | 1.7848 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.7441 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.060758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060758 | 0.7689% | CZ 6B | 9.5935 | 2.2331 | 37.7372 | 6.6408 | 0 | 6.5141 | 0 | 18.6846 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 129.59 | 0.7689%
CZ 7 | 0.092829 | 0.021616 | 0.38973 | 0.097633 | 0 | 0.067043 | 0 | 0.16617 | 0.041832 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.3031 | 0.4265% | CZ 7 | 3.1276 | 0.72829 | 13.1307 | 9.7633 | 0 | 2.2588 | 0 | 5.5985 | 1.4094 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 50.3769 | 0.4265% | CZ 7 | 0.91638 | 0.21339 | 3.8473 | 0 | 0 | 0.66182 | 0 | 1.6404 | 0.41295 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.8998 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.097633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097633 | 0.4265% | CZ 7 | 9.5935 | 2.234 | 40.2772 | 10.6713 | 0 | 6.9286 | 0 | 17.1729 | 4.3232 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 135.2503 | 0.4265%
CZ 8 | 0.092829 | 0.021466 | 0.41715 | 0.13449 | 0 | 0.053265 | 0 | 0.17619 | 0.041832 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.3635 | 0% | CZ 8 | 3.1276 | 0.72324 | 14.0545 | 13.4491 | 0 | 1.7946 | 0 | 5.9362 | 1.4094 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 54.8551 | 0% | CZ 8 | 0.91638 | 0.21191 | 4.118 | 0 | 0 | 0.52582 | 0 | 1.7393 | 0.41295 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.132 | 0% | CZ 8 | 0 | 0 | 0 | 0.13449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13449 | 0% | CZ 8 | 9.5935 | 2.2185 | 43.111 | 14.6999 | 0 | 5.5048 | 0 | 18.2089 | 4.3232 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 141.7094 | 0%
US Weighted | 0.092829 | 0.021634 | 0.3129 | 0.029273 | 0 | 0.12212 | 0 | 0.16073 | 0.023109 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1888 | 100% | US Weighted | 3.1276 | 0.72887 | 10.5421 | 2.9273 | 0 | 4.1144 | 0 | 5.4153 | 0.77859 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.9945 | 100% | US Weighted | 0.91638 | 0.21356 | 3.0888 | 0 | 0 | 1.2055 | 0 | 1.5867 | 0.22813 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.4467 | 100% | US Weighted | 0 | 0 | 0 | 0.029273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029273 | 100% | US Weighted | 9.5935 | 2.2358 | 32.3369 | 3.1995 | 0 | 12.6205 | 0 | 16.6109 | 2.3883 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 123.035 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.11767 | 0.032925 | 0.24639 | 0 | 0 | 0.27094 | 0 | 0.16246 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2566 | 4.661% | CZ 1A | 3.9646 | 1.1093 | 8.3012 | 0 | 0 | 9.1284 | 0 | 5.4734 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.3374 | 4.661% | CZ 1A | 1.1616 | 0.32502 | 2.4323 | 0 | 0 | 2.6746 | 0 | 1.6037 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.4049 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 12.1611 | 3.4027 | 25.4633 | 0 | 0 | 28.0006 | 0 | 16.7893 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 129.8666 | 4.661%
CZ 1B | 0.11767 | 0.032892 | 0.24726 | 0.00059834 | 0 | 0.29676 | 0 | 0.20976 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.3312 | 0% | CZ 1B | 3.9646 | 1.1082 | 8.3307 | 0.059834 | 0 | 9.9983 | 0 | 7.0672 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.8893 | 0% | CZ 1B | 1.1616 | 0.3247 | 2.4409 | 0 | 0 | 2.9295 | 0 | 2.0707 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 13.135 | 0% | CZ 1B | 0 | 0 | 0 | 0.00059834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00059834 | 0% | CZ 1B | 12.1611 | 3.3992 | 25.5538 | 0.065398 | 0 | 30.669 | 0 | 21.6779 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 137.576 | 0%
CZ 2A | 0.11767 | 0.032858 | 0.26689 | 0.0031968 | 0 | 0.2156 | 0 | 0.15482 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2173 | 16.19% | CZ 2A | 3.9646 | 1.1071 | 8.9921 | 0.31968 | 0 | 7.2638 | 0 | 5.2161 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.2239 | 16.19% | CZ 2A | 1.1616 | 0.32437 | 2.6347 | 0 | 0 | 2.1283 | 0 | 1.5283 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9849 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.0031968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031968 | 16.19% | CZ 2A | 12.1611 | 3.3958 | 27.5826 | 0.3494 | 0 | 22.2812 | 0 | 15.9999 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 125.8196 | 16.19%
CZ 2B | 0.11767 | 0.032883 | 0.26825 | 0.0018006 | 0 | 0.18738 | 0 | 0.20064 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2349 | 1.276% | CZ 2B | 3.9646 | 1.1079 | 9.0379 | 0.18006 | 0 | 6.313 | 0 | 6.7598 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.7237 | 1.276% | CZ 2B | 1.1616 | 0.32461 | 2.6481 | 0 | 0 | 1.8497 | 0 | 1.9806 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.1723 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0018006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018006 | 1.276% | CZ 2B | 12.1611 | 3.3984 | 27.7231 | 0.19681 | 0 | 19.3646 | 0 | 20.735 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 127.6286 | 1.276%
CZ 3A | 0.11767 | 0.032917 | 0.30196 | 0.034226 | 0 | 0.12437 | 0 | 0.16068 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1981 | 11.24% | CZ 3A | 3.9646 | 1.109 | 10.1736 | 3.4226 | 0 | 4.1902 | 0 | 5.4136 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.6342 | 11.24% | CZ 3A | 1.1616 | 0.32494 | 2.9809 | 0 | 0 | 1.2277 | 0 | 1.5862 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.489 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.034226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034226 | 11.24% | CZ 3A | 12.1611 | 3.4018 | 31.2068 | 3.7409 | 0 | 12.8532 | 0 | 16.6058 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 124.0191 | 11.24%
CZ 3B | 0.11767 | 0.032892 | 0.29271 | 0.0035282 | 0 | 0.14456 | 0 | 0.18652 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2441 | 11.78% | CZ 3B | 3.9646 | 1.1082 | 9.8618 | 0.35282 | 0 | 4.8705 | 0 | 6.2841 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.1511 | 11.78% | CZ 3B | 1.1616 | 0.3247 | 2.8895 | 0 | 0 | 1.427 | 0 | 1.8412 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.2469 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.0035282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0035282 | 11.78% | CZ 3B | 12.1611 | 3.3992 | 30.2501 | 0.38563 | 0 | 14.9398 | 0 | 19.2759 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 128.5983 | 11.78%
CZ 3C | 0.11767 | 0.032892 | 0.30536 | 0.0023006 | 0 | 0.066809 | 0 | 0.14021 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.0915 | 3.558% | CZ 3C | 3.9646 | 1.1082 | 10.288 | 0.23006 | 0 | 2.2509 | 0 | 4.7238 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 36.926 | 3.558% | CZ 3C | 1.1616 | 0.3247 | 3.0144 | 0 | 0 | 0.65952 | 0 | 1.3841 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 10.7519 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0023006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023006 | 3.558% | CZ 3C | 12.1611 | 3.3992 | 31.5576 | 0.25146 | 0 | 6.9045 | 0 | 14.4899 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 112.8133 | 3.558%
CZ 4A | 0.11767 | 0.032858 | 0.32923 | 0.030226 | 0 | 0.10772 | 0 | 0.16861 | 0.041832 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2544 | 21.56% | CZ 4A | 3.9646 | 1.1071 | 11.0922 | 3.0226 | 0 | 3.6291 | 0 | 5.6808 | 1.4094 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.2662 | 21.56% | CZ 4A | 1.1616 | 0.32437 | 3.25 | 0 | 0 | 1.0633 | 0 | 1.6645 | 0.41295 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.0844 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.030226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030226 | 21.56% | CZ 4A | 12.1611 | 3.3958 | 34.0243 | 3.3037 | 0 | 11.132 | 0 | 17.4254 | 4.3232 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 129.815 | 21.56%
CZ 4B | 0.11767 | 0.032867 | 0.32125 | 0.018065 | 0 | 0.11789 | 0 | 0.20406 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.238 | 0.2995% | CZ 4B | 3.9646 | 1.1073 | 10.8235 | 1.8065 | 0 | 3.9719 | 0 | 6.8752 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.9096 | 0.2995% | CZ 4B | 1.1616 | 0.32445 | 3.1713 | 0 | 0 | 1.1638 | 0 | 2.0144 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.0432 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.018065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018065 | 0.2995% | CZ 4B | 12.1611 | 3.3967 | 33.2003 | 1.9745 | 0 | 12.1835 | 0 | 21.0892 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 128.0549 | 0.2995%
CZ 4C | 0.11767 | 0.032825 | 0.33768 | 0.035617 | 0 | 0.046685 | 0 | 0.17196 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1687 | 4.986% | CZ 4C | 3.9646 | 1.1059 | 11.3771 | 3.5617 | 0 | 1.5729 | 0 | 5.7938 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.7364 | 4.986% | CZ 4C | 1.1616 | 0.32404 | 3.3335 | 0 | 0 | 0.46086 | 0 | 1.6976 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.1852 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.035617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035617 | 4.986% | CZ 4C | 12.1611 | 3.3923 | 34.8982 | 3.8929 | 0 | 4.8248 | 0 | 17.7719 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 120.9908 | 4.986%
CZ 5A | 0.11767 | 0.032825 | 0.35242 | 0.057786 | 0 | 0.073714 | 0 | 0.16539 | 0.041832 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2679 | 15.67% | CZ 5A | 3.9646 | 1.1059 | 11.8736 | 5.7786 | 0 | 2.4836 | 0 | 5.5724 | 1.4094 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 46.5485 | 15.67% | CZ 5A | 1.1616 | 0.32404 | 3.479 | 0 | 0 | 0.72768 | 0 | 1.6327 | 0.41295 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9456 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.057786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057786 | 15.67% | CZ 5A | 12.1611 | 3.3923 | 36.4212 | 6.316 | 0 | 7.6181 | 0 | 17.0927 | 4.3232 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 131.3742 | 15.67%
CZ 5B | 0.11767 | 0.032858 | 0.34576 | 0.05037 | 0 | 0.089118 | 0 | 0.20269 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2647 | 4.35% | CZ 5B | 3.9646 | 1.1071 | 11.6493 | 5.037 | 0 | 3.0025 | 0 | 6.8289 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 45.9499 | 4.35% | CZ 5B | 1.1616 | 0.32437 | 3.4133 | 0 | 0 | 0.87974 | 0 | 2.0009 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9875 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.05037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05037 | 4.35% | CZ 5B | 12.1611 | 3.3958 | 35.7334 | 5.5054 | 0 | 9.21 | 0 | 20.947 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 131.0023 | 4.35%
CZ 5C | 0.11767 | 0.032817 | 0.35085 | 0.033661 | 0 | 0.036319 | 0 | 0.15916 | 0 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.1567 | 0.08141% | CZ 5C | 3.9646 | 1.1056 | 11.8207 | 3.3661 | 0 | 1.2237 | 0 | 5.3625 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.2037 | 0.08141% | CZ 5C | 1.1616 | 0.32395 | 3.4635 | 0 | 0 | 0.35853 | 0 | 1.5712 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.0864 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.033661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033661 | 0.08141% | CZ 5C | 12.1611 | 3.3915 | 36.2591 | 3.6792 | 0 | 3.7535 | 0 | 16.4489 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 119.7429 | 0.08141%
CZ 6A | 0.11767 | 0.03285 | 0.36951 | 0.10446 | 0 | 0.077392 | 0 | 0.17266 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.3408 | 3.16% | CZ 6A | 3.9646 | 1.1068 | 12.4496 | 10.4456 | 0 | 2.6075 | 0 | 5.8171 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 52.1003 | 3.16% | CZ 6A | 1.1616 | 0.32428 | 3.6477 | 0 | 0 | 0.76399 | 0 | 1.7044 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.2048 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.10446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10446 | 3.16% | CZ 6A | 12.1611 | 3.3949 | 38.188 | 11.4171 | 0 | 7.9982 | 0 | 17.8434 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 139.1893 | 3.16%
CZ 6B | 0.11767 | 0.032825 | 0.36508 | 0.05766 | 0 | 0.071546 | 0 | 0.19597 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.307 | 0.7689% | CZ 6B | 3.9646 | 1.1059 | 12.3001 | 5.766 | 0 | 2.4105 | 0 | 6.6027 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 47.8589 | 0.7689% | CZ 6B | 1.1616 | 0.32404 | 3.6039 | 0 | 0 | 0.70628 | 0 | 1.9346 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.3332 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.05766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05766 | 0.7689% | CZ 6B | 12.1611 | 3.3923 | 37.7295 | 6.3022 | 0 | 7.394 | 0 | 20.2532 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 135.419 | 0.7689%
CZ 7 | 0.11767 | 0.032842 | 0.38974 | 0.10901 | 0 | 0.068794 | 0 | 0.1752 | 0.04003 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.3595 | 0.4265% | CZ 7 | 3.9646 | 1.1065 | 13.1309 | 10.9013 | 0 | 2.3178 | 0 | 5.9028 | 1.3487 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 53.033 | 0.4265% | CZ 7 | 1.1616 | 0.3242 | 3.8474 | 0 | 0 | 0.67911 | 0 | 1.7295 | 0.39517 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.3446 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.10901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10901 | 0.4265% | CZ 7 | 12.1611 | 3.3941 | 40.278 | 11.9151 | 0 | 7.1096 | 0 | 18.1063 | 4.137 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 141.1508 | 0.4265%
CZ 8 | 0.11767 | 0.032616 | 0.41718 | 0.15356 | 0 | 0.053541 | 0 | 0.1851 | 0.038229 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.4241 | 0% | CZ 8 | 3.9646 | 1.0989 | 14.0553 | 15.3565 | 0 | 1.8039 | 0 | 6.2363 | 1.288 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 58.164 | 0% | CZ 8 | 1.1616 | 0.32198 | 4.1182 | 0 | 0 | 0.52854 | 0 | 1.8272 | 0.37738 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 12.5426 | 0% | CZ 8 | 0 | 0 | 0 | 0.15356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15356 | 0% | CZ 8 | 12.1611 | 3.3708 | 43.1136 | 16.7846 | 0 | 5.5332 | 0 | 19.1293 | 3.9508 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 148.0932 | 0%
US Weighted | 0.11767 | 0.032866 | 0.31286 | 0.028713 | 0 | 0.12795 | 0 | 0.16832 | 0.022032 | 0 | 0 | 0.10421 | 0 | 0 | 0 | 0.32202 | 1.2366 | 100% | US Weighted | 3.9646 | 1.1073 | 10.5407 | 2.8713 | 0 | 4.3109 | 0 | 5.6709 | 0.74228 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.5684 | 100% | US Weighted | 1.1616 | 0.32444 | 3.0884 | 0 | 0 | 1.2631 | 0 | 1.6616 | 0.21749 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1789 | 11.9243 | 100% | US Weighted | 0 | 0 | 0 | 0.028713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028713 | 100% | US Weighted | 12.1611 | 3.3966 | 32.3327 | 3.1383 | 0 | 13.2232 | 0 | 17.3949 | 2.2769 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2796 | 127.9733 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1376 | 0.032925 | 0.24676 | 0 | 0 | 0.33761 | 0 | 0.18366 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3651 | 4.661% | CZ 1A | 4.6361 | 1.1093 | 8.3138 | 0 | 0 | 11.3745 | 0 | 6.1877 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 45.9913 | 4.661% | CZ 1A | 1.3584 | 0.32502 | 2.436 | 0 | 0 | 3.3327 | 0 | 1.813 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 13.4754 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 14.221 | 3.4027 | 25.502 | 0 | 0 | 34.8905 | 0 | 18.9802 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 141.0744 | 4.661%
CZ 1B | 0.1376 | 0.032892 | 0.24748 | 0.0010506 | 0 | 0.35138 | 0 | 0.23956 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.4365 | 0% | CZ 1B | 4.6361 | 1.1082 | 8.338 | 0.10506 | 0 | 11.8387 | 0 | 8.0711 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 48.4669 | 0% | CZ 1B | 1.3584 | 0.3247 | 2.443 | 0 | 0 | 3.4687 | 0 | 2.3648 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 14.17 | 0% | CZ 1B | 0 | 0 | 0 | 0.0010506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010506 | 0% | CZ 1B | 14.221 | 3.3992 | 25.5762 | 0.11483 | 0 | 36.3143 | 0 | 24.7574 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 148.4609 | 0%
CZ 2A | 0.1376 | 0.032858 | 0.26718 | 0.003767 | 0 | 0.2701 | 0 | 0.17883 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3168 | 16.19% | CZ 2A | 4.6361 | 1.1071 | 9.0017 | 0.3767 | 0 | 9.1 | 0 | 6.025 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.6164 | 16.19% | CZ 2A | 1.3584 | 0.32437 | 2.6375 | 0 | 0 | 2.6663 | 0 | 1.7653 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.9622 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.003767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003767 | 16.19% | CZ 2A | 14.221 | 3.3958 | 27.6119 | 0.41173 | 0 | 27.9136 | 0 | 18.4812 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 136.1132 | 16.19%
CZ 2B | 0.1376 | 0.032883 | 0.26847 | 0.0023737 | 0 | 0.22967 | 0 | 0.22773 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3252 | 1.276% | CZ 2B | 4.6361 | 1.1079 | 9.0452 | 0.23737 | 0 | 7.7381 | 0 | 7.6727 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.8072 | 1.276% | CZ 2B | 1.3584 | 0.32461 | 2.6503 | 0 | 0 | 2.2673 | 0 | 2.2481 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 13.059 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0023737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023737 | 1.276% | CZ 2B | 14.221 | 3.3984 | 27.7455 | 0.25944 | 0 | 23.7361 | 0 | 23.5352 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 136.9737 | 1.276%
CZ 3A | 0.1376 | 0.032917 | 0.30213 | 0.030195 | 0 | 0.15709 | 0 | 0.17151 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.258 | 11.24% | CZ 3A | 4.6361 | 1.109 | 10.1793 | 3.0195 | 0 | 5.2925 | 0 | 5.7786 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.3848 | 11.24% | CZ 3A | 1.3584 | 0.32494 | 2.9825 | 0 | 0 | 1.5507 | 0 | 1.6931 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.12 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.030195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030195 | 11.24% | CZ 3A | 14.221 | 3.4018 | 31.224 | 3.3003 | 0 | 16.2343 | 0 | 17.7253 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 130.1848 | 11.24%
CZ 3B | 0.1376 | 0.032892 | 0.29306 | 0.0084919 | 0 | 0.16611 | 0 | 0.19897 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2636 | 11.78% | CZ 3B | 4.6361 | 1.1082 | 9.8736 | 0.84919 | 0 | 5.5965 | 0 | 6.7036 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 43.1369 | 11.78% | CZ 3B | 1.3584 | 0.3247 | 2.893 | 0 | 0 | 1.6398 | 0 | 1.9641 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.3903 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.0084919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084919 | 11.78% | CZ 3B | 14.221 | 3.3992 | 30.2863 | 0.92816 | 0 | 17.1668 | 0 | 20.5626 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 130.6422 | 11.78%
CZ 3C | 0.1376 | 0.032892 | 0.30567 | 0.0019046 | 0 | 0.099292 | 0 | 0.15144 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.1553 | 3.558% | CZ 3C | 4.6361 | 1.1082 | 10.2984 | 0.19046 | 0 | 3.3453 | 0 | 5.1023 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 39.0505 | 3.558% | CZ 3C | 1.3584 | 0.3247 | 3.0174 | 0 | 0 | 0.98018 | 0 | 1.495 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 11.386 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0019046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019046 | 3.558% | CZ 3C | 14.221 | 3.3992 | 31.5895 | 0.20817 | 0 | 10.2615 | 0 | 15.6508 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 119.4082 | 3.558%
CZ 4A | 0.1376 | 0.032858 | 0.3297 | 0.076354 | 0 | 0.11686 | 0 | 0.17504 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2949 | 21.56% | CZ 4A | 4.6361 | 1.1071 | 11.1082 | 7.6354 | 0 | 3.9373 | 0 | 5.8974 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 48.6913 | 21.56% | CZ 4A | 1.3584 | 0.32437 | 3.2547 | 0 | 0 | 1.1536 | 0 | 1.728 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.0294 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.076354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076354 | 21.56% | CZ 4A | 14.221 | 3.3958 | 34.0734 | 8.3455 | 0 | 12.0775 | 0 | 18.0899 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 134.2811 | 21.56%
CZ 4B | 0.1376 | 0.032867 | 0.32154 | 0.022293 | 0 | 0.13596 | 0 | 0.21295 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2897 | 0.2995% | CZ 4B | 4.6361 | 1.1073 | 10.8334 | 2.2293 | 0 | 4.5808 | 0 | 7.1745 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.9312 | 0.2995% | CZ 4B | 1.3584 | 0.32445 | 3.1742 | 0 | 0 | 1.3422 | 0 | 2.1021 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.5116 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.022293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022293 | 0.2995% | CZ 4B | 14.221 | 3.3967 | 33.2305 | 2.4366 | 0 | 14.0512 | 0 | 22.0071 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 133.4211 | 0.2995%
CZ 4C | 0.1376 | 0.032825 | 0.33793 | 0.041282 | 0 | 0.055659 | 0 | 0.17675 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2086 | 4.986% | CZ 4C | 4.6361 | 1.1059 | 11.3855 | 4.1282 | 0 | 1.8752 | 0 | 5.955 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 43.4559 | 4.986% | CZ 4C | 1.3584 | 0.32404 | 3.336 | 0 | 0 | 0.54945 | 0 | 1.7448 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 11.523 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.041282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041282 | 4.986% | CZ 4C | 14.221 | 3.3923 | 34.9241 | 4.5122 | 0 | 5.7522 | 0 | 18.2666 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 125.1464 | 4.986%
CZ 5A | 0.1376 | 0.032825 | 0.35287 | 0.13057 | 0 | 0.074607 | 0 | 0.17321 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3282 | 15.67% | CZ 5A | 4.6361 | 1.1059 | 11.8887 | 13.057 | 0 | 2.5136 | 0 | 5.8359 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 53.407 | 15.67% | CZ 5A | 1.3584 | 0.32404 | 3.4834 | 0 | 0 | 0.73649 | 0 | 1.7099 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 11.8226 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.13057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13057 | 15.67% | CZ 5A | 14.221 | 3.3923 | 36.4677 | 14.2713 | 0 | 7.7103 | 0 | 17.9012 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 138.0418 | 15.67%
CZ 5B | 0.1376 | 0.032858 | 0.34605 | 0.061497 | 0 | 0.10268 | 0 | 0.21326 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3205 | 4.35% | CZ 5B | 4.6361 | 1.1071 | 11.6589 | 6.1497 | 0 | 3.4594 | 0 | 7.1852 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 48.5661 | 4.35% | CZ 5B | 1.3584 | 0.32437 | 3.4161 | 0 | 0 | 1.0136 | 0 | 2.1053 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.428 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.061497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061497 | 4.35% | CZ 5B | 14.221 | 3.3958 | 35.7627 | 6.7216 | 0 | 10.6114 | 0 | 22.0399 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 136.8304 | 4.35%
CZ 5C | 0.1376 | 0.032817 | 0.35109 | 0.043684 | 0 | 0.040981 | 0 | 0.16447 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.1972 | 0.08141% | CZ 5C | 4.6361 | 1.1056 | 11.8289 | 4.3684 | 0 | 1.3807 | 0 | 5.5412 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 43.2307 | 0.08141% | CZ 5C | 1.3584 | 0.32395 | 3.4659 | 0 | 0 | 0.40455 | 0 | 1.6236 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 11.3867 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.043684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043684 | 0.08141% | CZ 5C | 14.221 | 3.3915 | 36.2841 | 4.7747 | 0 | 4.2353 | 0 | 16.9971 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 123.9816 | 0.08141%
CZ 6A | 0.1376 | 0.03285 | 0.36992 | 0.19543 | 0 | 0.07926 | 0 | 0.18248 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.4241 | 3.16% | CZ 6A | 4.6361 | 1.1068 | 12.4633 | 19.5432 | 0 | 2.6704 | 0 | 6.1481 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 60.9376 | 3.16% | CZ 6A | 1.3584 | 0.32428 | 3.6518 | 0 | 0 | 0.78243 | 0 | 1.8014 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.1286 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.19543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19543 | 3.16% | CZ 6A | 14.221 | 3.3949 | 38.2302 | 21.3607 | 0 | 8.1913 | 0 | 18.8587 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 148.3348 | 3.16%
CZ 6B | 0.1376 | 0.032825 | 0.36555 | 0.12295 | 0 | 0.067109 | 0 | 0.20737 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.3599 | 0.7689% | CZ 6B | 4.6361 | 1.1059 | 12.3161 | 12.2949 | 0 | 2.261 | 0 | 6.9868 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 53.9706 | 0.7689% | CZ 6B | 1.3584 | 0.32404 | 3.6086 | 0 | 0 | 0.66248 | 0 | 2.0471 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.211 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.12295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12295 | 0.7689% | CZ 6B | 14.221 | 3.3923 | 37.7786 | 13.4383 | 0 | 6.9355 | 0 | 21.4314 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 141.2752 | 0.7689%
CZ 7 | 0.1376 | 0.032842 | 0.39017 | 0.2069 | 0 | 0.061905 | 0 | 0.17319 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.4291 | 0.4265% | CZ 7 | 4.6361 | 1.1065 | 13.1455 | 20.6904 | 0 | 2.0857 | 0 | 5.8351 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 61.8691 | 0.4265% | CZ 7 | 1.3584 | 0.3242 | 3.8516 | 0 | 0 | 0.61111 | 0 | 1.7097 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.0654 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2069 | 0.4265% | CZ 7 | 14.221 | 3.3941 | 40.3229 | 22.6146 | 0 | 6.3977 | 0 | 17.8986 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 148.9268 | 0.4265%
CZ 8 | 0.1376 | 0.032616 | 0.41753 | 0.2759 | 0 | 0.04154 | 0 | 0.1791 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.5108 | 0% | CZ 8 | 4.6361 | 1.0989 | 14.0674 | 27.5904 | 0 | 1.3996 | 0 | 6.0343 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 69.1964 | 0% | CZ 8 | 1.3584 | 0.32198 | 4.1218 | 0 | 0 | 0.41007 | 0 | 1.768 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.1906 | 0% | CZ 8 | 0 | 0 | 0 | 0.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2759 | 0% | CZ 8 | 14.221 | 3.3708 | 43.1507 | 30.1563 | 0 | 4.293 | 0 | 18.5096 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 157.7794 | 0%
US Weighted | 0.1376 | 0.032866 | 0.31321 | 0.054862 | 0 | 0.15099 | 0 | 0.18035 | 0 | 0 | 0 | 0.10449 | 0 | 0 | 0 | 0.32202 | 1.2964 | 100% | US Weighted | 4.6361 | 1.1073 | 10.5526 | 5.4862 | 0 | 5.0872 | 0 | 6.0764 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 47.3157 | 100% | US Weighted | 1.3584 | 0.32444 | 3.0919 | 0 | 0 | 1.4906 | 0 | 1.7804 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1789 | 12.256 | 100% | US Weighted | 0 | 0 | 0 | 0.054862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054862 | 100% | US Weighted | 14.221 | 3.3966 | 32.3694 | 5.9964 | 0 | 15.6047 | 0 | 18.6387 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2796 | 134.3048 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1263 | 0.060938 | 0.24676 | 0 | 0 | 0.35482 | 0 | 0.20069 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4212 | 4.661% | CZ 1A | 4.2551 | 2.0531 | 8.3138 | 0 | 0 | 11.9545 | 0 | 6.7617 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 47.8834 | 4.661% | CZ 1A | 1.2468 | 0.60156 | 2.436 | 0 | 0 | 3.5027 | 0 | 1.9812 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 14.0298 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 13.0522 | 6.2977 | 25.502 | 0 | 0 | 36.6694 | 0 | 20.741 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 146.8783 | 4.661%
CZ 1B | 0.1263 | 0.060863 | 0.24748 | 0.00096914 | 0 | 0.36338 | 0 | 0.26026 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.491 | 0% | CZ 1B | 4.2551 | 2.0506 | 8.338 | 0.096914 | 0 | 12.2428 | 0 | 8.7685 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.297 | 0% | CZ 1B | 1.2468 | 0.60082 | 2.443 | 0 | 0 | 3.5871 | 0 | 2.5692 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 14.7086 | 0% | CZ 1B | 0 | 0 | 0 | 0.00096914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00096914 | 0% | CZ 1B | 13.0522 | 6.29 | 25.5762 | 0.10593 | 0 | 37.5537 | 0 | 26.8966 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 154.0904 | 0%
CZ 2A | 0.1263 | 0.060813 | 0.26722 | 0.0051519 | 0 | 0.27861 | 0 | 0.19297 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3628 | 16.19% | CZ 2A | 4.2551 | 2.0489 | 9.0031 | 0.51519 | 0 | 9.3869 | 0 | 6.5015 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 46.2558 | 16.19% | CZ 2A | 1.2468 | 0.60032 | 2.6379 | 0 | 0 | 2.7504 | 0 | 1.905 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.402 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.0051519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051519 | 16.19% | CZ 2A | 13.0522 | 6.2848 | 27.6162 | 0.5631 | 0 | 28.7936 | 0 | 19.9429 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 140.8687 | 16.19%
CZ 2B | 0.1263 | 0.060855 | 0.2685 | 0.003031 | 0 | 0.23735 | 0 | 0.25136 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3791 | 1.276% | CZ 2B | 4.2551 | 2.0503 | 9.0464 | 0.3031 | 0 | 7.9966 | 0 | 8.4687 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 46.6653 | 1.276% | CZ 2B | 1.2468 | 0.60074 | 2.6506 | 0 | 0 | 2.343 | 0 | 2.4813 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.5841 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.003031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003031 | 1.276% | CZ 2B | 13.0522 | 6.2891 | 27.749 | 0.33129 | 0 | 24.529 | 0 | 25.9769 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 142.5434 | 1.276%
CZ 3A | 0.1263 | 0.060913 | 0.30222 | 0.042563 | 0 | 0.15963 | 0 | 0.18644 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3098 | 11.24% | CZ 3A | 4.2551 | 2.0523 | 10.1824 | 4.2563 | 0 | 5.3782 | 0 | 6.2815 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 46.9509 | 11.24% | CZ 3A | 1.2468 | 0.60131 | 2.9834 | 0 | 0 | 1.5758 | 0 | 1.8405 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.5095 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.042563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042563 | 11.24% | CZ 3A | 13.0522 | 6.2951 | 31.2335 | 4.6522 | 0 | 16.4972 | 0 | 19.2681 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 135.6142 | 11.24%
CZ 3B | 0.1263 | 0.060871 | 0.29312 | 0.011374 | 0 | 0.16874 | 0 | 0.21788 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.31 | 11.78% | CZ 3B | 4.2551 | 2.0509 | 9.8758 | 1.1374 | 0 | 5.6853 | 0 | 7.3408 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 44.8904 | 11.78% | CZ 3B | 1.2468 | 0.6009 | 2.8936 | 0 | 0 | 1.6658 | 0 | 2.1509 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.8196 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.011374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011374 | 11.78% | CZ 3B | 13.0522 | 6.2908 | 30.2932 | 1.2432 | 0 | 17.4392 | 0 | 22.5174 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 135.4519 | 11.78%
CZ 3C | 0.1263 | 0.060871 | 0.30572 | 0.0027445 | 0 | 0.097174 | 0 | 0.16428 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.1888 | 3.558% | CZ 3C | 4.2551 | 2.0509 | 10.3001 | 0.27445 | 0 | 3.274 | 0 | 5.535 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 40.2345 | 3.558% | CZ 3C | 1.2468 | 0.6009 | 3.0179 | 0 | 0 | 0.95927 | 0 | 1.6217 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 11.7083 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0027445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027445 | 3.558% | CZ 3C | 13.0522 | 6.2908 | 31.5946 | 0.29997 | 0 | 10.0426 | 0 | 16.9781 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 122.8742 | 3.558%
CZ 4A | 0.1263 | 0.060805 | 0.32981 | 0.10794 | 0 | 0.11537 | 0 | 0.18678 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3587 | 21.56% | CZ 4A | 4.2551 | 2.0486 | 11.1118 | 10.794 | 0 | 3.887 | 0 | 6.2931 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 52.9347 | 21.56% | CZ 4A | 1.2468 | 0.60024 | 3.2558 | 0 | 0 | 1.1389 | 0 | 1.8439 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.3472 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.10794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10794 | 21.56% | CZ 4A | 13.0522 | 6.2839 | 34.0846 | 11.7978 | 0 | 11.9232 | 0 | 19.3034 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 141.0611 | 21.56%
CZ 4B | 0.1263 | 0.06083 | 0.32166 | 0.030945 | 0 | 0.13158 | 0 | 0.22604 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3291 | 0.2995% | CZ 4B | 4.2551 | 2.0495 | 10.8373 | 3.0945 | 0 | 4.433 | 0 | 7.6156 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 46.8301 | 0.2995% | CZ 4B | 1.2468 | 0.60049 | 3.1753 | 0 | 0 | 1.2989 | 0 | 2.2314 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.8145 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.030945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030945 | 0.2995% | CZ 4B | 13.0522 | 6.2865 | 33.2426 | 3.3823 | 0 | 13.5978 | 0 | 23.3603 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 137.5376 | 0.2995%
CZ 4C | 0.1263 | 0.060755 | 0.3381 | 0.058058 | 0 | 0.049287 | 0 | 0.18457 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.2488 | 4.986% | CZ 4C | 4.2551 | 2.0469 | 11.3911 | 5.8058 | 0 | 1.6606 | 0 | 6.2183 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 45.923 | 4.986% | CZ 4C | 1.2468 | 0.59975 | 3.3376 | 0 | 0 | 0.48655 | 0 | 1.822 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 11.7543 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.058058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058058 | 4.986% | CZ 4C | 13.0522 | 6.2788 | 34.9413 | 6.3458 | 0 | 5.0937 | 0 | 19.0742 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 129.4018 | 4.986%
CZ 5A | 0.1263 | 0.060755 | 0.35298 | 0.176 | 0 | 0.071137 | 0 | 0.18271 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4016 | 15.67% | CZ 5A | 4.2551 | 2.0469 | 11.8924 | 17.6001 | 0 | 2.3967 | 0 | 6.1559 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 58.8923 | 15.67% | CZ 5A | 1.2468 | 0.59975 | 3.4845 | 0 | 0 | 0.70224 | 0 | 1.8037 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.0986 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.176 | 15.67% | CZ 5A | 13.0522 | 6.2788 | 36.4789 | 19.2369 | 0 | 7.3518 | 0 | 18.8828 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 145.8973 | 15.67%
CZ 5B | 0.1263 | 0.060805 | 0.34615 | 0.080281 | 0 | 0.098166 | 0 | 0.22435 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3678 | 4.35% | CZ 5B | 4.2551 | 2.0486 | 11.6625 | 8.0281 | 0 | 3.3074 | 0 | 7.5586 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 51.4055 | 4.35% | CZ 5B | 1.2468 | 0.60024 | 3.4171 | 0 | 0 | 0.96907 | 0 | 2.2147 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.7096 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.080281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080281 | 4.35% | CZ 5B | 13.0522 | 6.2839 | 35.7739 | 8.7747 | 0 | 10.1451 | 0 | 23.1853 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 141.8311 | 4.35%
CZ 5C | 0.1263 | 0.060738 | 0.35123 | 0.05346 | 0 | 0.035293 | 0 | 0.16941 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.2281 | 0.08141% | CZ 5C | 4.2551 | 2.0464 | 11.8334 | 5.346 | 0 | 1.1891 | 0 | 5.7078 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 44.9228 | 0.08141% | CZ 5C | 1.2468 | 0.59958 | 3.4672 | 0 | 0 | 0.34841 | 0 | 1.6724 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 11.596 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.05346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05346 | 0.08141% | CZ 5C | 13.0522 | 6.277 | 36.2979 | 5.8432 | 0 | 3.6475 | 0 | 17.5081 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 127.2418 | 0.08141%
CZ 6A | 0.1263 | 0.060796 | 0.37002 | 0.25605 | 0 | 0.076433 | 0 | 0.19376 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5151 | 3.16% | CZ 6A | 4.2551 | 2.0483 | 12.4667 | 25.6046 | 0 | 2.5752 | 0 | 6.5282 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 68.0233 | 3.16% | CZ 6A | 1.2468 | 0.60016 | 3.6527 | 0 | 0 | 0.75452 | 0 | 1.9128 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.4287 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.25605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25605 | 3.16% | CZ 6A | 13.0522 | 6.2831 | 38.2406 | 27.9859 | 0 | 7.8991 | 0 | 20.0248 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 158.1015 | 3.16%
CZ 6B | 0.1263 | 0.060746 | 0.36569 | 0.16147 | 0 | 0.062439 | 0 | 0.21909 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4275 | 0.7689% | CZ 6B | 4.2551 | 2.0466 | 12.3209 | 16.1472 | 0 | 2.1037 | 0 | 7.3816 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 58.8002 | 0.7689% | CZ 6B | 1.2468 | 0.59967 | 3.61 | 0 | 0 | 0.61638 | 0 | 2.1628 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.4973 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.16147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16147 | 0.7689% | CZ 6B | 13.0522 | 6.2779 | 37.7933 | 17.6489 | 0 | 6.4529 | 0 | 22.6423 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 148.4834 | 0.7689%
CZ 7 | 0.1263 | 0.06078 | 0.39025 | 0.25357 | 0 | 0.058528 | 0 | 0.18108 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5022 | 0.4265% | CZ 7 | 4.2551 | 2.0478 | 13.1484 | 25.3571 | 0 | 1.9719 | 0 | 6.1009 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 67.4263 | 0.4265% | CZ 7 | 1.2468 | 0.6 | 3.8525 | 0 | 0 | 0.57777 | 0 | 1.7876 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.3263 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.25357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25357 | 0.4265% | CZ 7 | 13.0522 | 6.2814 | 40.3315 | 27.7154 | 0 | 6.0486 | 0 | 18.7139 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 156.7589 | 0.4265%
CZ 8 | 0.1263 | 0.060354 | 0.41761 | 0.30477 | 0 | 0.037112 | 0 | 0.18477 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5626 | 0% | CZ 8 | 4.2551 | 2.0334 | 14.07 | 30.4773 | 0 | 1.2504 | 0 | 6.2251 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 72.8563 | 0% | CZ 8 | 1.2468 | 0.5958 | 4.1225 | 0 | 0 | 0.36635 | 0 | 1.8239 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.4171 | 0% | CZ 8 | 0 | 0 | 0 | 0.30477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30477 | 0% | CZ 8 | 13.0522 | 6.2374 | 43.1584 | 33.3117 | 0 | 3.8353 | 0 | 19.0949 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 163.3058 | 0%
US Weighted | 0.1263 | 0.060824 | 0.3133 | 0.074881 | 0 | 0.15226 | 0 | 0.19351 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3528 | 100% | US Weighted | 4.2551 | 2.0493 | 10.5555 | 7.4881 | 0 | 5.1298 | 0 | 6.5198 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.5427 | 100% | US Weighted | 1.2468 | 0.60043 | 3.0928 | 0 | 0 | 1.503 | 0 | 1.9103 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.615 | 100% | US Weighted | 0 | 0 | 0 | 0.074881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074881 | 100% | US Weighted | 13.0522 | 6.286 | 32.3782 | 8.1845 | 0 | 15.7352 | 0 | 19.999 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 140.251 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.1263 | 0.060938 | 0.24677 | 0 | 0 | 0.43487 | 0 | 0.20522 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5058 | 4.661% | CZ 1A | 4.2551 | 2.0531 | 8.3141 | 0 | 0 | 14.6516 | 0 | 6.9143 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.7333 | 4.661% | CZ 1A | 1.2468 | 0.60156 | 2.436 | 0 | 0 | 4.2929 | 0 | 2.0259 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 14.8649 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 13.0522 | 6.2977 | 25.5029 | 0 | 0 | 44.9425 | 0 | 21.209 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 155.6203 | 4.661%
CZ 1B | 0.1263 | 0.060863 | 0.2475 | 0.0012894 | 0 | 0.4459 | 0 | 0.2662 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5798 | 0% | CZ 1B | 4.2551 | 2.0506 | 8.3386 | 0.12894 | 0 | 15.023 | 0 | 8.9688 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 53.3102 | 0% | CZ 1B | 1.2468 | 0.60082 | 2.4432 | 0 | 0 | 4.4017 | 0 | 2.6279 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 15.5821 | 0% | CZ 1B | 0 | 0 | 0 | 0.0012894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012894 | 0% | CZ 1B | 13.0522 | 6.29 | 25.5779 | 0.14093 | 0 | 46.0819 | 0 | 27.5111 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 163.2699 | 0%
CZ 2A | 0.1263 | 0.060813 | 0.26728 | 0.0089694 | 0 | 0.35532 | 0 | 0.21709 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4675 | 16.19% | CZ 2A | 4.2551 | 2.0489 | 9.0051 | 0.89694 | 0 | 11.9713 | 0 | 7.3141 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.0366 | 16.19% | CZ 2A | 1.2468 | 0.60032 | 2.6385 | 0 | 0 | 3.5076 | 0 | 2.143 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 14.3979 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.0089694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089694 | 16.19% | CZ 2A | 13.0522 | 6.2848 | 27.6223 | 0.98036 | 0 | 36.7211 | 0 | 22.4355 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 151.7121 | 16.19%
CZ 2B | 0.1263 | 0.060855 | 0.2686 | 0.0062643 | 0 | 0.30947 | 0 | 0.28687 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4901 | 1.276% | CZ 2B | 4.2551 | 2.0503 | 9.0494 | 0.62643 | 0 | 10.4265 | 0 | 9.6651 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 50.618 | 1.276% | CZ 2B | 1.2468 | 0.60074 | 2.6515 | 0 | 0 | 3.055 | 0 | 2.8319 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 14.6475 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0062643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062643 | 1.276% | CZ 2B | 13.0522 | 6.2891 | 27.7584 | 0.68469 | 0 | 31.9825 | 0 | 29.6468 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 154.0297 | 1.276%
CZ 3A | 0.1263 | 0.060913 | 0.3022 | 0.045322 | 0 | 0.2128 | 0 | 0.20877 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.388 | 11.24% | CZ 3A | 4.2551 | 2.0523 | 10.1818 | 4.5322 | 0 | 7.1697 | 0 | 7.0337 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 49.7699 | 11.24% | CZ 3A | 1.2468 | 0.60131 | 2.9833 | 0 | 0 | 2.1007 | 0 | 2.0609 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.2546 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.045322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045322 | 11.24% | CZ 3A | 13.0522 | 6.2951 | 31.2318 | 4.9537 | 0 | 21.9925 | 0 | 21.5753 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 143.7166 | 11.24%
CZ 3B | 0.1263 | 0.060871 | 0.29311 | 0.013225 | 0 | 0.23008 | 0 | 0.24526 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4006 | 11.78% | CZ 3B | 4.2551 | 2.0509 | 9.8752 | 1.3225 | 0 | 7.7519 | 0 | 8.2633 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 48.064 | 11.78% | CZ 3B | 1.2468 | 0.6009 | 2.8934 | 0 | 0 | 2.2713 | 0 | 2.4211 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.6953 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.013225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013225 | 11.78% | CZ 3B | 13.0522 | 6.2908 | 30.2915 | 1.4455 | 0 | 23.7783 | 0 | 25.3469 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 144.8212 | 11.78%
CZ 3C | 0.1263 | 0.060871 | 0.3057 | 0.0041631 | 0 | 0.166 | 0 | 0.22646 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3212 | 3.558% | CZ 3C | 4.2551 | 2.0509 | 10.2995 | 0.41631 | 0 | 5.5929 | 0 | 7.6297 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 44.7894 | 3.558% | CZ 3C | 1.2468 | 0.6009 | 3.0178 | 0 | 0 | 1.6387 | 0 | 2.2355 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.0013 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0041631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041631 | 3.558% | CZ 3C | 13.0522 | 6.2908 | 31.5929 | 0.45502 | 0 | 17.1556 | 0 | 23.4034 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 136.5659 | 3.558%
CZ 4A | 0.1263 | 0.060805 | 0.32985 | 0.12101 | 0 | 0.14011 | 0 | 0.19315 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4029 | 21.56% | CZ 4A | 4.2551 | 2.0486 | 11.1132 | 12.101 | 0 | 4.7204 | 0 | 6.5074 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 55.291 | 21.56% | CZ 4A | 1.2468 | 0.60024 | 3.2562 | 0 | 0 | 1.3831 | 0 | 1.9067 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.6547 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.12101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12101 | 21.56% | CZ 4A | 13.0522 | 6.2839 | 34.0889 | 13.2264 | 0 | 14.4795 | 0 | 19.961 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 145.708 | 21.56%
CZ 4B | 0.1263 | 0.06083 | 0.32172 | 0.038808 | 0 | 0.1595 | 0 | 0.23432 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.3732 | 0.2995% | CZ 4B | 4.2551 | 2.0495 | 10.8393 | 3.8808 | 0 | 5.3737 | 0 | 7.8946 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 48.838 | 0.2995% | CZ 4B | 1.2468 | 0.60049 | 3.1759 | 0 | 0 | 1.5745 | 0 | 2.3131 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.1725 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.038808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038808 | 0.2995% | CZ 4B | 13.0522 | 6.2865 | 33.2486 | 4.2417 | 0 | 16.4834 | 0 | 24.2161 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 142.1444 | 0.2995%
CZ 4C | 0.1263 | 0.060755 | 0.33817 | 0.069129 | 0 | 0.057444 | 0 | 0.18882 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.2723 | 4.986% | CZ 4C | 4.2551 | 2.0469 | 11.3936 | 6.9129 | 0 | 1.9354 | 0 | 6.3616 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 47.4507 | 4.986% | CZ 4C | 1.2468 | 0.59975 | 3.3383 | 0 | 0 | 0.56706 | 0 | 1.864 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 11.8776 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.069129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069129 | 4.986% | CZ 4C | 13.0522 | 6.2788 | 34.9491 | 7.5558 | 0 | 5.9366 | 0 | 19.5137 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 131.9021 | 4.986%
CZ 5A | 0.1263 | 0.060755 | 0.35302 | 0.19392 | 0 | 0.085365 | 0 | 0.18804 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4391 | 15.67% | CZ 5A | 4.2551 | 2.0469 | 11.8938 | 19.3918 | 0 | 2.8761 | 0 | 6.3355 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 61.3443 | 15.67% | CZ 5A | 1.2468 | 0.59975 | 3.4849 | 0 | 0 | 0.84269 | 0 | 1.8563 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.2921 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.19392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19392 | 15.67% | CZ 5A | 13.0522 | 6.2788 | 36.4832 | 21.1952 | 0 | 8.8222 | 0 | 19.4336 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 149.881 | 15.67%
CZ 5B | 0.1263 | 0.060805 | 0.34621 | 0.094102 | 0 | 0.11823 | 0 | 0.23216 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4095 | 4.35% | CZ 5B | 4.2551 | 2.0486 | 11.6645 | 9.4102 | 0 | 3.9834 | 0 | 7.8219 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 53.7288 | 4.35% | CZ 5B | 1.2468 | 0.60024 | 3.4177 | 0 | 0 | 1.1671 | 0 | 2.2918 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.9854 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.094102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094102 | 4.35% | CZ 5B | 13.0522 | 6.2839 | 35.7799 | 10.2853 | 0 | 12.2188 | 0 | 23.9929 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 146.229 | 4.35%
CZ 5C | 0.1263 | 0.060738 | 0.35132 | 0.0665 | 0 | 0.039922 | 0 | 0.17259 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.2491 | 0.08141% | CZ 5C | 4.2551 | 2.0464 | 11.8365 | 6.65 | 0 | 1.345 | 0 | 5.8148 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 46.4929 | 0.08141% | CZ 5C | 1.2468 | 0.59958 | 3.4681 | 0 | 0 | 0.3941 | 0 | 1.7037 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 11.674 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0665 | 0.08141% | CZ 5C | 13.0522 | 6.277 | 36.3074 | 7.2684 | 0 | 4.1258 | 0 | 17.8365 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 129.4833 | 0.08141%
CZ 6A | 0.1263 | 0.060796 | 0.37006 | 0.28001 | 0 | 0.091945 | 0 | 0.19964 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5605 | 3.16% | CZ 6A | 4.2551 | 2.0483 | 12.4678 | 28.0011 | 0 | 3.0978 | 0 | 6.7263 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 71.1415 | 3.16% | CZ 6A | 1.2468 | 0.60016 | 3.6531 | 0 | 0 | 0.90765 | 0 | 1.9708 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.6402 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.28001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28001 | 3.16% | CZ 6A | 13.0522 | 6.2831 | 38.244 | 30.6052 | 0 | 9.5022 | 0 | 20.6324 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 162.935 | 3.16%
CZ 6B | 0.1263 | 0.060746 | 0.36574 | 0.18214 | 0 | 0.074682 | 0 | 0.2254 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4667 | 0.7689% | CZ 6B | 4.2551 | 2.0466 | 12.3226 | 18.2145 | 0 | 2.5162 | 0 | 7.594 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 61.494 | 0.7689% | CZ 6B | 1.2468 | 0.59967 | 3.6105 | 0 | 0 | 0.73723 | 0 | 2.225 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.6809 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.18214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18214 | 0.7689% | CZ 6B | 13.0522 | 6.2779 | 37.7984 | 19.9084 | 0 | 7.7181 | 0 | 23.2939 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 152.6649 | 0.7689%
CZ 7 | 0.1263 | 0.06078 | 0.39027 | 0.29229 | 0 | 0.077534 | 0 | 0.20877 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.5876 | 0.4265% | CZ 7 | 4.2551 | 2.0478 | 13.1489 | 29.2289 | 0 | 2.6122 | 0 | 7.0337 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 72.8718 | 0.4265% | CZ 7 | 1.2468 | 0.6 | 3.8526 | 0 | 0 | 0.76539 | 0 | 2.0609 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.7874 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.29229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29229 | 0.4265% | CZ 7 | 13.0522 | 6.2814 | 40.3332 | 31.9472 | 0 | 8.0129 | 0 | 21.5753 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 165.8181 | 0.4265%
CZ 8 | 0.1263 | 0.060354 | 0.4176 | 0.32962 | 0 | 0.050388 | 0 | 0.20642 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.6224 | 0% | CZ 8 | 4.2551 | 2.0334 | 14.0697 | 32.9619 | 0 | 1.6977 | 0 | 6.9548 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 76.5177 | 0% | CZ 8 | 1.2468 | 0.5958 | 4.1224 | 0 | 0 | 0.49742 | 0 | 2.0377 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 12.7618 | 0% | CZ 8 | 0 | 0 | 0 | 0.32962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32962 | 0% | CZ 8 | 13.0522 | 6.2374 | 43.1576 | 36.0274 | 0 | 5.2075 | 0 | 21.3332 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 169.6311 | 0%
US Weighted | 0.1263 | 0.060824 | 0.31333 | 0.084013 | 0 | 0.19457 | 0 | 0.20917 | 0 | 0 | 0 | 0.10807 | 0 | 0 | 0 | 0.32365 | 1.4199 | 100% | US Weighted | 4.2551 | 2.0493 | 10.5565 | 8.4013 | 0 | 6.5554 | 0 | 7.0472 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9042 | 53.4099 | 100% | US Weighted | 1.2468 | 0.60043 | 3.0931 | 0 | 0 | 1.9207 | 0 | 2.0648 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1949 | 13.1875 | 100% | US Weighted | 0 | 0 | 0 | 0.084013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084013 | 100% | US Weighted | 13.0522 | 6.286 | 32.3813 | 9.1826 | 0 | 20.108 | 0 | 21.6167 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4477 | 147.2427 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 33741 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 33741 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.033467 | 0.039263 | 0.00036695 | 0 | 0 | 0.17135 | 0 | 0.047686 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.29761 | 4.661% | CZ 1A | 1.1276 | 1.3228 | 0.012363 | 0 | 0 | 5.773 | 0 | 1.6066 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 10.027 | 4.661% | CZ 1A | 0.33038 | 0.38759 | 0.0036224 | 0 | 0 | 1.6915 | 0 | 0.47074 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.9379 | 4.661% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.661% | CZ 1A | 3.4587 | 4.0577 | 0.037923 | 0 | 0 | 17.7081 | 0 | 4.9282 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 30.7569 | 4.661%
CZ 1B | 0.033467 | 0.039213 | 0.00020849 | 0.00056744 | 0 | 0.15579 | 0 | 0.060946 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.29567 | 0% | CZ 1B | 1.1276 | 1.3212 | 0.0070244 | 0.056744 | 0 | 5.2487 | 0 | 2.0534 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 9.9991 | 0% | CZ 1B | 0.33038 | 0.3871 | 0.0020582 | 0 | 0 | 1.5379 | 0 | 0.60164 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.9131 | 0% | CZ 1B | 0 | 0 | 0 | 0.00056744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056744 | 0% | CZ 1B | 3.4587 | 4.0525 | 0.021547 | 0.062021 | 0 | 16.0998 | 0 | 6.2986 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 30.5595 | 0%
CZ 2A | 0.033467 | 0.03918 | 0.00035861 | 0.0055901 | 0 | 0.14627 | 0 | 0.068285 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.29863 | 16.19% | CZ 2A | 1.1276 | 1.32 | 0.012082 | 0.55901 | 0 | 4.9281 | 0 | 2.3006 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 10.432 | 16.19% | CZ 2A | 0.33038 | 0.38677 | 0.00354 | 0 | 0 | 1.4439 | 0 | 0.67409 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.8928 | 16.19% | CZ 2A | 0 | 0 | 0 | 0.0055901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055901 | 16.19% | CZ 2A | 3.4587 | 4.0491 | 0.037061 | 0.611 | 0 | 15.1164 | 0 | 7.057 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 30.8956 | 16.19%
CZ 2B | 0.033467 | 0.039213 | 0.00031691 | 0.0043092 | 0 | 0.12861 | 0 | 0.093137 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.30454 | 1.276% | CZ 2B | 1.1276 | 1.3212 | 0.010677 | 0.43092 | 0 | 4.3332 | 0 | 3.138 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 10.5461 | 1.276% | CZ 2B | 0.33038 | 0.3871 | 0.0031284 | 0 | 0 | 1.2696 | 0 | 0.91942 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.9638 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0043092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043092 | 1.276% | CZ 2B | 3.4587 | 4.0525 | 0.032751 | 0.47099 | 0 | 13.2919 | 0 | 9.6254 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 31.4985 | 1.276%
CZ 3A | 0.033467 | 0.039246 | 0.00020849 | 0.010295 | 0 | 0.092812 | 0 | 0.053999 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.23551 | 11.24% | CZ 3A | 1.1276 | 1.3223 | 0.0070244 | 1.0295 | 0 | 3.127 | 0 | 1.8193 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 8.6173 | 11.24% | CZ 3A | 0.33038 | 0.38743 | 0.0020582 | 0 | 0 | 0.91621 | 0 | 0.53306 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.2232 | 11.24% | CZ 3A | 0 | 0 | 0 | 0.010295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010295 | 11.24% | CZ 3A | 3.4587 | 4.056 | 0.021547 | 1.1253 | 0 | 9.5918 | 0 | 5.5806 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 24.4002 | 11.24%
CZ 3B | 0.033467 | 0.039221 | 0.00036695 | 0.0096071 | 0 | 0.090569 | 0 | 0.064299 | -0.04003 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.20298 | 11.78% | CZ 3B | 1.1276 | 1.3214 | 0.012363 | 0.96071 | 0 | 3.0514 | 0 | 2.1663 | -1.3487 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 7.4757 | 11.78% | CZ 3B | 0.33038 | 0.38718 | 0.0036224 | 0 | 0 | 0.89407 | 0 | 0.63474 | -0.39517 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.9089 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.0096071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096071 | 11.78% | CZ 3B | 3.4587 | 4.0534 | 0.037923 | 1.0501 | 0 | 9.36 | 0 | 6.6451 | -4.137 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 21.0344 | 11.78%
CZ 3C | 0.033467 | 0.039221 | 0.00030857 | 0.0016096 | 0 | 0.10325 | 0 | 0.090602 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.27393 | 3.558% | CZ 3C | 1.1276 | 1.3214 | 0.010396 | 0.16096 | 0 | 3.4785 | 0 | 3.0525 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 9.336 | 3.558% | CZ 3C | 0.33038 | 0.38718 | 0.0030461 | 0 | 0 | 1.0192 | 0 | 0.89439 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 2.6883 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0016096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016096 | 3.558% | CZ 3C | 3.4587 | 4.0534 | 0.031889 | 0.17593 | 0 | 10.67 | 0 | 9.3634 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 28.3196 | 3.558%
CZ 4A | 0.033467 | 0.03918 | 0.00059212 | 0.090225 | 0 | 0.036311 | 0 | 0.028155 | -0.043642 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.18977 | 21.56% | CZ 4A | 1.1276 | 1.32 | 0.019949 | 9.0225 | 0 | 1.2234 | 0 | 0.94858 | -1.4704 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 12.3763 | 21.56% | CZ 4A | 0.33038 | 0.38677 | 0.0058452 | 0 | 0 | 0.35845 | 0 | 0.27793 | -0.43081 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.98265 | 21.56% | CZ 4A | 0 | 0 | 0 | 0.090225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090225 | 21.56% | CZ 4A | 3.4587 | 4.0491 | 0.061193 | 9.8616 | 0 | 3.7526 | 0 | 2.9097 | -4.5102 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 20.149 | 21.56%
CZ 4B | 0.033467 | 0.039196 | 0.00042532 | 0.018784 | 0 | 0.046811 | 0 | 0.03536 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.17952 | 0.2995% | CZ 4B | 1.1276 | 1.3206 | 0.01433 | 1.8784 | 0 | 1.5771 | 0 | 1.1913 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 7.294 | 0.2995% | CZ 4B | 0.33038 | 0.38693 | 0.0041987 | 0 | 0 | 0.4621 | 0 | 0.34906 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.5868 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.018784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018784 | 0.2995% | CZ 4B | 3.4587 | 4.0508 | 0.043956 | 2.0531 | 0 | 4.8377 | 0 | 3.6544 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 18.6649 | 0.2995%
CZ 4C | 0.033467 | 0.039146 | 0.00039196 | 0.028754 | 0 | 0.018472 | 0 | 0.03129 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.157 | 4.986% | CZ 4C | 1.1276 | 1.3189 | 0.013206 | 2.8754 | 0 | 0.62237 | 0 | 1.0542 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 7.1963 | 4.986% | CZ 4C | 0.33038 | 0.38644 | 0.0038693 | 0 | 0 | 0.18235 | 0 | 0.30889 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.266 | 4.986% | CZ 4C | 0 | 0 | 0 | 0.028754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028754 | 4.986% | CZ 4C | 3.4587 | 4.0456 | 0.040508 | 3.1428 | 0 | 1.9091 | 0 | 3.2338 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 16.3967 | 4.986%
CZ 5A | 0.033467 | 0.039146 | 0.00055042 | 0.13662 | 0 | 0.018839 | 0 | 0.035735 | -0.045443 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.2244 | 15.67% | CZ 5A | 1.1276 | 1.3189 | 0.018545 | 13.662 | 0 | 0.63473 | 0 | 1.204 | -1.531 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 16.6193 | 15.67% | CZ 5A | 0.33038 | 0.38644 | 0.0054335 | 0 | 0 | 0.18598 | 0 | 0.35277 | -0.4486 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.86649 | 15.67% | CZ 5A | 0 | 0 | 0 | 0.13662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13662 | 15.67% | CZ 5A | 3.4587 | 4.0456 | 0.056884 | 14.9326 | 0 | 1.947 | 0 | 3.6931 | -4.6964 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 24.0039 | 15.67%
CZ 5B | 0.033467 | 0.03918 | 0.00035861 | 0.039016 | 0 | 0.039588 | 0 | 0.045059 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.20215 | 4.35% | CZ 5B | 1.1276 | 1.32 | 0.012082 | 3.9016 | 0 | 1.3338 | 0 | 1.5181 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 9.3978 | 4.35% | CZ 5B | 0.33038 | 0.38677 | 0.00354 | 0 | 0 | 0.3908 | 0 | 0.44481 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.6104 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.039016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039016 | 4.35% | CZ 5B | 3.4587 | 4.0491 | 0.037061 | 4.2644 | 0 | 4.0913 | 0 | 4.6567 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 21.1236 | 4.35%
CZ 5C | 0.033467 | 0.039138 | 0.00035027 | 0.027507 | 0 | 0.010858 | 0 | 0.02788 | 0 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.14468 | 0.08141% | CZ 5C | 1.1276 | 1.3186 | 0.011801 | 2.7507 | 0 | 0.36583 | 0 | 0.93931 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 6.6984 | 0.08141% | CZ 5C | 0.33038 | 0.38636 | 0.0034577 | 0 | 0 | 0.10719 | 0 | 0.27522 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.1567 | 0.08141% | CZ 5C | 0 | 0 | 0 | 0.027507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027507 | 0.08141% | CZ 5C | 3.4587 | 4.0448 | 0.036199 | 3.0065 | 0 | 1.1222 | 0 | 2.8813 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 15.1158 | 0.08141%
CZ 6A | 0.033467 | 0.039171 | 0.00050038 | 0.17723 | 0 | 0.021091 | 0 | 0.039997 | -0.043642 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.2733 | 3.16% | CZ 6A | 1.1276 | 1.3198 | 0.016859 | 17.7234 | 0 | 0.71059 | 0 | 1.3476 | -1.4704 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 20.96 | 3.16% | CZ 6A | 0.33038 | 0.38669 | 0.0049396 | 0 | 0 | 0.2082 | 0 | 0.39484 | -0.43081 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.94832 | 3.16% | CZ 6A | 0 | 0 | 0 | 0.17723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17723 | 3.16% | CZ 6A | 3.4587 | 4.0482 | 0.051713 | 19.3717 | 0 | 2.1797 | 0 | 4.1336 | -4.5102 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 29.2997 | 3.16%
CZ 6B | 0.033467 | 0.039138 | 0.00059212 | 0.12139 | 0 | 0.011651 | 0 | 0.044601 | -0.04003 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.21628 | 0.7689% | CZ 6B | 1.1276 | 1.3186 | 0.019949 | 12.1387 | 0 | 0.39253 | 0 | 1.5027 | -1.3487 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 15.3359 | 0.7689% | CZ 6B | 0.33038 | 0.38636 | 0.0058452 | 0 | 0 | 0.11501 | 0 | 0.44028 | -0.39517 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.93679 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.12139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12139 | 0.7689% | CZ 6B | 3.4587 | 4.0448 | 0.061193 | 13.2676 | 0 | 1.204 | 0 | 4.6093 | -4.137 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 23.0748 | 0.7689%
CZ 7 | 0.033467 | 0.039163 | 0.00054208 | 0.19466 | 0 | 0.010491 | 0 | 0.042599 | -0.041832 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.28457 | 0.4265% | CZ 7 | 1.1276 | 1.3195 | 0.018264 | 19.4656 | 0 | 0.35347 | 0 | 1.4352 | -1.4094 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 22.4949 | 0.4265% | CZ 7 | 0.33038 | 0.38661 | 0.0053512 | 0 | 0 | 0.10357 | 0 | 0.42052 | -0.41295 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.88756 | 0.4265% | CZ 7 | 0 | 0 | 0 | 0.19466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19466 | 0.4265% | CZ 7 | 3.4587 | 4.0474 | 0.056022 | 21.2759 | 0 | 1.0842 | 0 | 4.4025 | -4.3232 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 30.5678 | 0.4265%
CZ 8 | 0.033467 | 0.038888 | 0.00045034 | 0.19513 | 0 | -0.0028772 | 0 | 0.030231 | -0.041832 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.25894 | 0% | CZ 8 | 1.1276 | 1.3102 | 0.015173 | 19.5128 | 0 | -0.096937 | 0 | 1.0185 | -1.4094 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 21.6626 | 0% | CZ 8 | 0.33038 | 0.38389 | 0.0044456 | 0 | 0 | -0.028403 | 0 | 0.29843 | -0.41295 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 0.62988 | 0% | CZ 8 | 0 | 0 | 0 | 0.19513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19513 | 0% | CZ 8 | 3.4587 | 4.0189 | 0.046541 | 21.3275 | 0 | -0.29735 | 0 | 3.1243 | -4.3232 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 27.9217 | 0%
US Weighted | 0.033467 | 0.03919 | 0.00043011 | 0.05474 | 0 | 0.07245 | 0 | 0.048437 | -0.023109 | 0 | 0 | 0.0038529 | 0 | 0 | 0 | 0.0016262 | 0.23108 | 100% | US Weighted | 1.1276 | 1.3204 | 0.014491 | 5.474 | 0 | 2.441 | 0 | 1.6319 | -0.77859 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054791 | 11.4154 | 100% | US Weighted | 0.33038 | 0.38688 | 0.0042459 | 0 | 0 | 0.71521 | 0 | 0.47815 | -0.22813 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.016054 | 1.7408 | 100% | US Weighted | 0 | 0 | 0 | 0.05474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05474 | 100% | US Weighted | 3.4587 | 4.0502 | 0.044451 | 5.9831 | 0 | 7.4875 | 0 | 5.0058 | -2.3883 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.16807 | 24.2077 | 100%
Building Type: | Mid-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 33741 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 33741 | [17 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 26.5% | 64.43% | 0.1487% | 0% | 0% | 39.4% | 0% | 23.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 19.76% | 4.661% | CZ 1A | 26.5% | 64.43% | 0.1487% | 0% | 0% | 39.4% | 0% | 23.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 19.76% | 4.661% | CZ 1A | 26.5% | 64.43% | 0.1487% | 0% | 0% | 39.4% | 0% | 23.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 19.76% | 4.661% | CZ 1A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.661% | CZ 1A | 26.5% | 64.43% | 0.1487% | 0% | 0% | 39.4% | 0% | 23.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 19.76% | 4.661%
CZ 1B | 26.5% | 64.43% | 0.08424% | 44.01% | 0% | 34.94% | 0% | 22.89% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 18.72% | 0% | CZ 1B | 26.5% | 64.43% | 0.08424% | 44.01% | 0% | 34.94% | 0% | 22.89% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 18.76% | 0% | CZ 1B | 26.5% | 64.43% | 0.08424% | 0% | 0% | 34.94% | 0% | 22.89% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 18.7% | 0% | CZ 1B | 0% | 0% | 0% | 44.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.01% | 0% | CZ 1B | 26.5% | 64.43% | 0.08424% | 44.01% | 0% | 34.94% | 0% | 22.89% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 18.72% | 0%
CZ 2A | 26.5% | 64.43% | 0.1342% | 62.32% | 0% | 41.17% | 0% | 31.45% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.35% | 16.19% | CZ 2A | 26.5% | 64.43% | 0.1342% | 62.32% | 0% | 41.17% | 0% | 31.45% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.85% | 16.19% | CZ 2A | 26.5% | 64.43% | 0.1342% | 0% | 0% | 41.17% | 0% | 31.45% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.09% | 16.19% | CZ 2A | 0% | 0% | 0% | 62.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.32% | 16.19% | CZ 2A | 26.5% | 64.43% | 0.1342% | 62.32% | 0% | 41.17% | 0% | 31.45% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.36% | 16.19%
CZ 2B | 26.5% | 64.44% | 0.118% | 68.79% | 0% | 41.56% | 0% | 32.47% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.44% | 1.276% | CZ 2B | 26.5% | 64.44% | 0.118% | 68.79% | 0% | 41.56% | 0% | 32.47% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.83% | 1.276% | CZ 2B | 26.5% | 64.44% | 0.118% | 0% | 0% | 41.56% | 0% | 32.47% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.23% | 1.276% | CZ 2B | 0% | 0% | 0% | 68.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 68.79% | 1.276% | CZ 2B | 26.5% | 64.44% | 0.118% | 68.79% | 0% | 41.56% | 0% | 32.47% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.45% | 1.276%
CZ 3A | 26.5% | 64.43% | 0.06899% | 22.72% | 0% | 43.61% | 0% | 25.87% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.97% | 11.24% | CZ 3A | 26.5% | 64.43% | 0.06899% | 22.72% | 0% | 43.61% | 0% | 25.87% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 17.31% | 11.24% | CZ 3A | 26.5% | 64.43% | 0.06899% | 0% | 0% | 43.61% | 0% | 25.87% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.77% | 11.24% | CZ 3A | 0% | 0% | 0% | 22.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.72% | 11.24% | CZ 3A | 26.5% | 64.43% | 0.06899% | 22.72% | 0% | 43.61% | 0% | 25.87% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.98% | 11.24%
CZ 3B | 26.5% | 64.43% | 0.1252% | 72.64% | 0% | 39.36% | 0% | 26.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.49% | 11.78% | CZ 3B | 26.5% | 64.43% | 0.1252% | 72.64% | 0% | 39.36% | 0% | 26.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 15.55% | 11.78% | CZ 3B | 26.5% | 64.43% | 0.1252% | 0% | 0% | 39.36% | 0% | 26.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.94% | 11.78% | CZ 3B | 0% | 0% | 0% | 72.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 72.64% | 11.78% | CZ 3B | 26.5% | 64.43% | 0.1252% | 72.64% | 0% | 39.36% | 0% | 26.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.52% | 11.78%
CZ 3C | 26.5% | 64.43% | 0.1009% | 38.66% | 0% | 62.2% | 0% | 40.01% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.73% | 3.558% | CZ 3C | 26.5% | 64.43% | 0.1009% | 38.66% | 0% | 62.2% | 0% | 40.01% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.84% | 3.558% | CZ 3C | 26.5% | 64.43% | 0.1009% | 0% | 0% | 62.2% | 0% | 40.01% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.68% | 3.558% | CZ 3C | 0% | 0% | 0% | 38.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.66% | 3.558% | CZ 3C | 26.5% | 64.43% | 0.1009% | 38.66% | 0% | 62.2% | 0% | 40.01% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 20.74% | 3.558%
CZ 4A | 26.5% | 64.44% | 0.1795% | 74.56% | 0% | 25.92% | 0% | 14.58% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.53% | 21.56% | CZ 4A | 26.5% | 64.44% | 0.1795% | 74.56% | 0% | 25.92% | 0% | 14.58% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 22.38% | 21.56% | CZ 4A | 26.5% | 64.44% | 0.1795% | 0% | 0% | 25.92% | 0% | 14.58% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 7.765% | 21.56% | CZ 4A | 0% | 0% | 0% | 74.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 74.56% | 21.56% | CZ 4A | 26.5% | 64.44% | 0.1795% | 74.56% | 0% | 25.92% | 0% | 14.58% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.83% | 21.56%
CZ 4B | 26.5% | 64.44% | 0.1322% | 48.4% | 0% | 29.35% | 0% | 15.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.07% | 0.2995% | CZ 4B | 26.5% | 64.44% | 0.1322% | 48.4% | 0% | 29.35% | 0% | 15.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.94% | 0.2995% | CZ 4B | 26.5% | 64.44% | 0.1322% | 0% | 0% | 29.35% | 0% | 15.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 12.05% | 0.2995% | CZ 4B | 0% | 0% | 0% | 48.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 48.4% | 0.2995% | CZ 4B | 26.5% | 64.44% | 0.1322% | 48.4% | 0% | 29.35% | 0% | 15.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.13% | 0.2995%
CZ 4C | 26.5% | 64.43% | 0.1159% | 41.59% | 0% | 32.16% | 0% | 16.57% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 12.34% | 4.986% | CZ 4C | 26.5% | 64.43% | 0.1159% | 41.59% | 0% | 32.16% | 0% | 16.57% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 15.17% | 4.986% | CZ 4C | 26.5% | 64.43% | 0.1159% | 0% | 0% | 32.16% | 0% | 16.57% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 10.66% | 4.986% | CZ 4C | 0% | 0% | 0% | 41.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.59% | 4.986% | CZ 4C | 26.5% | 64.43% | 0.1159% | 41.59% | 0% | 32.16% | 0% | 16.57% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 12.43% | 4.986%
CZ 5A | 26.5% | 64.43% | 0.1559% | 70.45% | 0% | 22.07% | 0% | 19% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 15.59% | 15.67% | CZ 5A | 26.5% | 64.43% | 0.1559% | 70.45% | 0% | 22.07% | 0% | 19% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 27.09% | 15.67% | CZ 5A | 26.5% | 64.43% | 0.1559% | 0% | 0% | 22.07% | 0% | 19% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 7.049% | 15.67% | CZ 5A | 0% | 0% | 0% | 70.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 70.45% | 15.67% | CZ 5A | 26.5% | 64.43% | 0.1559% | 70.45% | 0% | 22.07% | 0% | 19% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.02% | 15.67%
CZ 5B | 26.5% | 64.44% | 0.1036% | 41.46% | 0% | 33.48% | 0% | 19.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.34% | 4.35% | CZ 5B | 26.5% | 64.44% | 0.1036% | 41.46% | 0% | 33.48% | 0% | 19.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 17.49% | 4.35% | CZ 5B | 26.5% | 64.44% | 0.1036% | 0% | 0% | 33.48% | 0% | 19.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 12.4% | 4.35% | CZ 5B | 0% | 0% | 0% | 41.46% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.46% | 4.35% | CZ 5B | 26.5% | 64.44% | 0.1036% | 41.46% | 0% | 33.48% | 0% | 19.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.45% | 4.35%
CZ 5C | 26.5% | 64.44% | 0.0997% | 41.36% | 0% | 27.2% | 0% | 16.15% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 11.58% | 0.08141% | CZ 5C | 26.5% | 64.44% | 0.0997% | 41.36% | 0% | 27.2% | 0% | 16.15% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.41% | 0.08141% | CZ 5C | 26.5% | 64.44% | 0.0997% | 0% | 0% | 27.2% | 0% | 16.15% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 9.908% | 0.08141% | CZ 5C | 0% | 0% | 0% | 41.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.36% | 0.08141% | CZ 5C | 26.5% | 64.44% | 0.0997% | 41.36% | 0% | 27.2% | 0% | 16.15% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 11.67% | 0.08141%
CZ 6A | 26.5% | 64.43% | 0.1352% | 63.3% | 0% | 22.94% | 0% | 20.03% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 17.51% | 3.16% | CZ 6A | 26.5% | 64.43% | 0.1352% | 63.3% | 0% | 22.94% | 0% | 20.03% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 29.46% | 3.16% | CZ 6A | 26.5% | 64.43% | 0.1352% | 0% | 0% | 22.94% | 0% | 20.03% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 7.502% | 3.16% | CZ 6A | 0% | 0% | 0% | 63.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 63.3% | 3.16% | CZ 6A | 26.5% | 64.43% | 0.1352% | 63.3% | 0% | 22.94% | 0% | 20.03% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 17.98% | 3.16%
CZ 6B | 26.5% | 64.43% | 0.1619% | 66.64% | 0% | 15.6% | 0% | 19.79% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 14.75% | 0.7689% | CZ 6B | 26.5% | 64.43% | 0.1619% | 66.64% | 0% | 15.6% | 0% | 19.79% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 24.94% | 0.7689% | CZ 6B | 26.5% | 64.43% | 0.1619% | 0% | 0% | 15.6% | 0% | 19.79% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 7.387% | 0.7689% | CZ 6B | 0% | 0% | 0% | 66.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 66.64% | 0.7689% | CZ 6B | 26.5% | 64.43% | 0.1619% | 66.64% | 0% | 15.6% | 0% | 19.79% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 15.11% | 0.7689%
CZ 7 | 26.5% | 64.43% | 0.1389% | 66.6% | 0% | 13.53% | 0% | 20.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 17.92% | 0.4265% | CZ 7 | 26.5% | 64.43% | 0.1389% | 66.6% | 0% | 13.53% | 0% | 20.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 30.87% | 0.4265% | CZ 7 | 26.5% | 64.43% | 0.1389% | 0% | 0% | 13.53% | 0% | 20.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 6.941% | 0.4265% | CZ 7 | 0% | 0% | 0% | 66.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 66.6% | 0.4265% | CZ 7 | 26.5% | 64.43% | 0.1389% | 66.6% | 0% | 13.53% | 0% | 20.41% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 18.43% | 0.4265%
CZ 8 | 26.5% | 64.43% | 0.1078% | 59.2% | 0% | -5.71% | 0% | 14.65% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 15.96% | 0% | CZ 8 | 26.5% | 64.43% | 0.1078% | 59.2% | 0% | -5.71% | 0% | 14.65% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 28.31% | 0% | CZ 8 | 26.5% | 64.43% | 0.1078% | 0% | 0% | -5.71% | 0% | 14.65% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 4.936% | 0% | CZ 8 | 0% | 0% | 0% | 59.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 59.2% | 0% | CZ 8 | 26.5% | 64.43% | 0.1078% | 59.2% | 0% | -5.71% | 0% | 14.65% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.46% | 0%
US Weighted | 26.5% | 64.43% | 0.1373% | 65.16% | 0% | 37.24% | 0% | 23.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.27% | 100% | US Weighted | 26.5% | 64.43% | 0.1373% | 65.16% | 0% | 37.24% | 0% | 23.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 21.37% | 100% | US Weighted | 26.5% | 64.43% | 0.1373% | 0% | 0% | 37.24% | 0% | 23.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 13.2% | 100% | US Weighted | 0% | 0% | 0% | 65.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.16% | 100% | US Weighted | 26.5% | 64.43% | 0.1373% | 65.16% | 0% | 37.24% | 0% | 23.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.5025% | 16.44% | 100%

## AptHR
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | High-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | High-rise Apartment | [14 empty] | Prototype Floor Area: | 84352 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2016 | 0.09162 | 0.03934 | 0.11539 | 0.041876 | 0 | 0.18918 | 0.0046632 | 0.17245 | 0.024658 | 0.015573 | 0 | 0.052844 | 0.0048288 | 0 | 0 | 0.32437 | 1.0768 |  | STD2016 | 3.0868 | 1.3254 | 11.5391 | 2.8403 | 0 | 6.3739 | 0.15711 | 5.8101 | 0.83076 | 0.52469 | 0 | 1.7804 | 0.16269 | 0 | 0 | 10.9284 | 45.3598 |  | STD2016 | 0.90444 | 0.38835 | 0 | 0.20057 | 0 | 1.8676 | 0.046033 | 1.7024 | 0.24341 | 0.15373 | 0 | 0.52166 | 0.047668 | 0 | 0 | 3.202 | 9.2778 |  | STD2016 | 0 | 0 | 0.11539 | 0.021558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13695 |  | STD2016 | 9.4686 | 4.0657 | 12.6122 | 4.456 | 0 | 19.5515 | 0.48192 | 17.8221 | 2.5483 | 1.6094 | 0 | 5.4612 | 0.49904 | 0 | 0 | 33.522 | 112.0981
STD2013 | 0.11511 | 0.056198 | 0.11574 | 0.041163 | 0 | 0.19479 | 0.0095199 | 0.1784 | 0.023788 | 0.016057 | 0 | 0.052844 | 0.0069449 | 0 | 0 | 0.32437 | 1.1349 |  | STD2013 | 3.8783 | 1.8934 | 11.574 | 2.7867 | 0 | 6.5628 | 0.32074 | 6.0107 | 0.80147 | 0.54099 | 0 | 1.7804 | 0.23399 | 0 | 0 | 10.9284 | 47.3119 |  | STD2013 | 1.1363 | 0.55477 | 0 | 0.19796 | 0 | 1.9229 | 0.093977 | 1.7611 | 0.23483 | 0.15851 | 0 | 0.52166 | 0.068558 | 0 | 0 | 3.202 | 9.8527 |  | STD2013 | 0 | 0 | 0.11574 | 0.02111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13685 |  | STD2013 | 11.8964 | 5.8079 | 12.6504 | 4.3798 | 0 | 20.1308 | 0.98384 | 18.4374 | 2.4584 | 1.6594 | 0 | 5.4612 | 0.71773 | 0 | 0 | 33.522 | 118.1053
STD2010 | 0.13891 | 0.056198 | 0.11574 | 0.073858 | 0 | 0.2447 | 0.011197 | 0.1961 | 0 | 0.01733 | 0 | 0.052954 | 0.0069446 | 0 | 0 | 0.32437 | 1.2383 |  | STD2010 | 4.6802 | 1.8934 | 11.5738 | 5.0894 | 0 | 8.2444 | 0.37725 | 6.6071 | 0 | 0.58386 | 0 | 1.7841 | 0.23397 | 0 | 0 | 10.9284 | 51.996 |  | STD2010 | 1.3713 | 0.55477 | 0 | 0.34188 | 0 | 2.4156 | 0.11053 | 1.9359 | 0 | 0.17107 | 0 | 0.52274 | 0.068554 | 0 | 0 | 3.202 | 10.6944 |  | STD2010 | 0 | 0 | 0.11574 | 0.039226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15496 |  | STD2010 | 14.3562 | 5.8079 | 12.6502 | 7.8665 | 0 | 25.2891 | 1.1572 | 20.2667 | 0 | 1.791 | 0 | 5.4726 | 0.7177 | 0 | 0 | 33.522 | 128.897
STD2007 | 0.11995 | 0.071191 | 0.1158 | 0.11381 | 0 | 0.2464 | 0.011528 | 0.21059 | 0 | 0.022911 | 0 | 0.054385 | 0.012067 | 0 | 0 | 0.32502 | 1.3036 |  | STD2007 | 4.0414 | 2.3985 | 11.5803 | 7.9784 | 0 | 8.3016 | 0.38839 | 7.095 | 0 | 0.77192 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 55.7447 |  | STD2007 | 1.1841 | 0.70277 | 0 | 0.50656 | 0 | 2.4324 | 0.1138 | 2.0788 | 0 | 0.22617 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 11.1091 |  | STD2007 | 0 | 0 | 0.1158 | 0.062495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1783 |  | STD2007 | 12.3966 | 7.3573 | 12.6572 | 12.1339 | 0 | 25.4644 | 1.1914 | 21.7635 | 0 | 2.3678 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 135.7889
STD2004 | 0.11995 | 0.071191 | 0.1158 | 0.12529 | 0 | 0.25413 | 0.011941 | 0.22257 | 0 | 0.023958 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3363 |  | STD2004 | 4.0414 | 2.3985 | 11.5802 | 8.7804 | 0 | 8.5619 | 0.40231 | 7.4988 | 0 | 0.80718 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 57.26 |  | STD2004 | 1.1841 | 0.70277 | 0 | 0.55808 | 0 | 2.5086 | 0.11788 | 2.1972 | 0 | 0.2365 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 11.3696 |  | STD2004 | 0 | 0 | 0.1158 | 0.068757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18456 |  | STD2004 | 12.3966 | 7.3573 | 12.6572 | 13.3577 | 0 | 26.2629 | 1.2341 | 23.002 | 0 | 2.476 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 139.2006
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -3.3862e-07 | 0.011481 | 0 | 0.0077267 | 0.0004132 | 0.011984 | 0 | 0.0010467 | 0 | 0 | -1.6937e-07 | 0 | 0 | 0 | 0.032652 |  | 2004-2007 | 0 | 0 | -3.3862e-05 | 0.80208 | 0 | 0.26032 | 0.013921 | 0.40377 | 0 | 0.035266 | 0 | 0 | -5.7063e-06 | 0 | 0 | 0 | 1.5153 |  | 2004-2007 | 0 | 0 | 0 | 0.051514 | 0 | 0.076275 | 0.004079 | 0.11831 | 0 | 0.010333 | 0 | 0 | -1.672e-06 | 0 | 0 | 0 | 0.26051 |  | 2004-2007 | 0 | 0 | -3.3862e-07 | 0.0062627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062623 |  | 2004-2007 | 0 | 0 | -3.7011e-05 | 1.2238 | 0 | 0.79852 | 0.042703 | 1.2385 | 0 | 0.10818 | 0 | 0 | -1.7504e-05 | 0 | 0 | 0 | 3.4117
2007-2010 | -0.018961 | 0.014993 | 6.434e-05 | 0.039951 | 0 | 0.0016965 | 0.0003307 | 0.014483 | 0 | 0.0055816 | 0 | 0.0014311 | 0.005122 | 0 | 0 | 0.0006505 | 0.065342 |  | 2007-2010 | -0.63883 | 0.50513 | 0.006434 | 2.8889 | 0 | 0.057157 | 0.011142 | 0.48796 | 0 | 0.18805 | 0 | 0.048216 | 0.17257 | 0 | 0 | 0.021916 | 3.7487 |  | 2007-2010 | -0.18718 | 0.148 | 0 | 0.16469 | 0 | 0.016747 | 0.0032645 | 0.14297 | 0 | 0.055099 | 0 | 0.014127 | 0.050562 | 0 | 0 | 0.0064215 | 0.4147 |  | 2007-2010 | 0 | 0 | 6.434e-05 | 0.023269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023333 |  | 2007-2010 | -1.9596 | 1.5495 | 0.0070323 | 4.2673 | 0 | 0.17532 | 0.034176 | 1.4968 | 0 | 0.57683 | 0 | 0.1479 | 0.52934 | 0 | 0 | 0.067227 | 6.8918
2010-2013 | 0.023802 | 0 | -1.381e-06 | 0.032695 | 0 | 0.049912 | 0.0016772 | 0.017701 | -0.023788 | 0.0012727 | 0 | 0.00011008 | -3.6471e-07 | 0 | 0 | 0 | 0.10338 |  | 2010-2013 | 0.80192 | 0 | -0.0001381 | 2.3028 | 0 | 1.6816 | 0.056508 | 0.59637 | -0.80147 | 0.042878 | 0 | 0.0037089 | -1.2288e-05 | 0 | 0 | 0 | 4.6842 |  | 2010-2013 | 0.23496 | 0 | 0 | 0.14392 | 0 | 0.49272 | 0.016557 | 0.17474 | -0.23483 | 0.012563 | 0 | 0.0010867 | -3.6003e-06 | 0 | 0 | 0 | 0.84171 |  | 2010-2013 | 0 | 0 | -1.381e-06 | 0.018116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018115 |  | 2010-2013 | 2.4598 | 0 | -0.00015095 | 3.4868 | 0 | 5.1583 | 0.17333 | 1.8293 | -2.4584 | 0.13152 | 0 | 0.011377 | -3.7692e-05 | 0 | 0 | 0 | 10.7918
2013-2016 | 0.023491 | 0.016858 | 0.00034871 | -0.00071214 | 0 | 0.0056056 | 0.0048567 | 0.0059538 | -0.00086935 | 0.00048375 | 0 | 0 | 0.0021161 | 0 | 0 | 0 | 0.058133 |  | 2013-2016 | 0.79146 | 0.56798 | 0.034871 | -0.053663 | 0 | 0.18886 | 0.16363 | 0.20059 | -0.02929 | 0.016298 | 0 | 0 | 0.071297 | 0 | 0 | 0 | 1.952 |  | 2013-2016 | 0.2319 | 0.16642 | 0 | -0.0026128 | 0 | 0.055337 | 0.047943 | 0.058774 | -0.0085819 | 0.0047754 | 0 | 0 | 0.02089 | 0 | 0 | 0 | 0.57484 |  | 2013-2016 | 0 | 0 | 0.00034871 | -0.00044746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.8753e-05 |  | 2013-2016 | 2.4277 | 1.7422 | 0.038114 | -0.076261 | 0 | 0.57932 | 0.50192 | 0.61531 | -0.089844 | 0.049994 | 0 | 0 | 0.2187 | 0 | 0 | 0 | 6.0072
2004-2016 | 0.028332 | 0.031851 | 0.00041133 | 0.083415 | 0 | 0.064941 | 0.0072778 | 0.050122 | -0.024658 | 0.0083847 | 0 | 0.0015412 | 0.0072376 | 0 | 0 | 0.0006505 | 0.25951 |  | 2004-2016 | 0.95454 | 1.0731 | 0.041133 | 5.9401 | 0 | 2.188 | 0.2452 | 1.6887 | -0.83076 | 0.28249 | 0 | 0.051925 | 0.24385 | 0 | 0 | 0.021916 | 11.9002 |  | 2004-2016 | 0.27968 | 0.31442 | 0 | 0.35751 | 0 | 0.64108 | 0.071844 | 0.49479 | -0.24341 | 0.082771 | 0 | 0.015214 | 0.071447 | 0 | 0 | 0.0064215 | 2.0918 |  | 2004-2016 | 0 | 0 | 0.00041133 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047611 |  | 2004-2016 | 2.928 | 3.2917 | 0.044958 | 8.9017 | 0 | 6.7114 | 0.75213 | 5.18 | -2.5483 | 0.86653 | 0 | 0.15928 | 0.74798 | 0 | 0 | 0.067227 | 27.1025
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.0002924% | 9.164% |  | 3.04% | 3.46% | 5.385% |  | 4.369% |  | 0% | -0.001404% |  |  | 0% | 2.443% |  | 2004-2007 | 0% | 0% | -0.0002924% | 9.135% |  | 3.04% | 3.46% | 5.385% |  | 4.369% |  | 0% | -0.001404% |  |  | 0% | 2.646% |  | 2004-2007 | 0% | 0% |  | 9.231% |  | 3.04% | 3.46% | 5.385% |  | 4.369% |  | 0% | -0.001404% |  |  | 0% | 2.291% |  | 2004-2007 |  |  | -0.0002924% | 9.108% | [12 empty] | 3.393% |  | 2004-2007 | 0% | 0% | -0.0002924% | 9.162% |  | 3.04% | 3.46% | 5.385% |  | 4.369% |  | 0% | -0.001404% |  |  | 0% | 2.451%
2007-2010 | -15.81% | 21.06% | 0.05556% | 35.1% |  | 0.6885% | 2.869% | 6.877% |  | 24.36% |  | 2.631% | 42.45% |  |  | 0.2001% | 5.012% |  | 2007-2010 | -15.81% | 21.06% | 0.05556% | 36.21% |  | 0.6885% | 2.869% | 6.877% |  | 24.36% |  | 2.631% | 42.45% |  |  | 0.2001% | 6.725% |  | 2007-2010 | -15.81% | 21.06% |  | 32.51% |  | 0.6885% | 2.869% | 6.877% |  | 24.36% |  | 2.631% | 42.45% |  |  | 0.2001% | 3.733% |  | 2007-2010 |  |  | 0.05556% | 37.23% | [12 empty] | 13.09% |  | 2007-2010 | -15.81% | 21.06% | 0.05556% | 35.17% |  | 0.6885% | 2.869% | 6.877% |  | 24.36% |  | 2.631% | 42.45% |  |  | 0.2001% | 5.075%
2010-2013 | 17.13% | 0% | -0.001193% | 44.27% |  | 20.4% | 14.98% | 9.026% |  | 7.344% |  | 0.2079% | -0.005252% |  |  | 0% | 8.348% |  | 2010-2013 | 17.13% | 0% | -0.001193% | 45.25% |  | 20.4% | 14.98% | 9.026% |  | 7.344% |  | 0.2079% | -0.005252% |  |  | 0% | 9.009% |  | 2010-2013 | 17.13% | 0% |  | 42.1% |  | 20.4% | 14.98% | 9.026% |  | 7.344% |  | 0.2079% | -0.005252% |  |  | 0% | 7.871% |  | 2010-2013 |  |  | -0.001193% | 46.18% | [12 empty] | 11.69% |  | 2010-2013 | 17.13% | 0% | -0.001193% | 44.32% |  | 20.4% | 14.98% | 9.026% |  | 7.344% |  | 0.2079% | -0.005252% |  |  | 0% | 8.372%
2013-2016 | 20.41% | 30% | 0.3013% | -1.73% |  | 2.878% | 51.02% | 3.337% | -3.655% | 3.013% |  | 0% | 30.47% |  |  | 0% | 5.122% |  | 2013-2016 | 20.41% | 30% | 0.3013% | -1.926% |  | 2.878% | 51.02% | 3.337% | -3.655% | 3.013% |  | 0% | 30.47% |  |  | 0% | 4.126% |  | 2013-2016 | 20.41% | 30% |  | -1.32% |  | 2.878% | 51.02% | 3.337% | -3.655% | 3.013% |  | 0% | 30.47% |  |  | 0% | 5.834% |  | 2013-2016 |  |  | 0.3013% | -2.12% | [12 empty] | -0.07216% |  | 2013-2016 | 20.41% | 30% | 0.3013% | -1.741% |  | 2.878% | 51.02% | 3.337% | -3.655% | 3.013% |  | 0% | 30.47% |  |  | 0% | 5.086%
2004-2016 | 23.62% | 44.74% | 0.3552% | 66.58% |  | 25.55% | 60.95% | 22.52% |  | 35% |  | 2.834% | 59.98% |  |  | 0.2001% | 19.42% |  | 2004-2016 | 23.62% | 44.74% | 0.3552% | 67.65% |  | 25.55% | 60.95% | 22.52% |  | 35% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.78% |  | 2004-2016 | 23.62% | 44.74% |  | 64.06% |  | 25.55% | 60.95% | 22.52% |  | 35% |  | 2.834% | 59.98% |  |  | 0.2001% | 18.4% |  | 2004-2016 |  |  | 0.3552% | 68.65% | [12 empty] | 25.8% |  | 2004-2016 | 23.62% | 44.74% | 0.3552% | 66.64% |  | 25.55% | 60.95% | 22.52% |  | 35% |  | 2.834% | 59.98% |  |  | 0.2001% | 19.47%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.09162 | 0.039407 | 0.091292 | 0 | 0 | 0.35595 | 0.0088468 | 0.15947 | 0 | 0.015852 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 1.1445 | 18.81% | CZ 1A | 3.0868 | 1.3277 | 9.1292 | 0 | 0 | 11.9925 | 0.29806 | 5.3729 | 0 | 0.53409 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 44.6127 | 18.81% | CZ 1A | 0.90444 | 0.38901 | 0 | 0 | 0 | 3.5138 | 0.087332 | 1.5743 | 0 | 0.15649 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 10.3967 | 18.81% | CZ 1A | 0 | 0 | 0.091292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091292 | 18.81% | CZ 1A | 9.4686 | 4.0726 | 9.9782 | 0 | 0 | 36.7861 | 0.91428 | 16.4809 | 0 | 1.6383 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 118.821 | 18.81%
CZ 1B | 0.09162 | 0.039357 | 0.091513 | 0.00030357 | 0 | 0.34988 | 0.011882 | 0.22137 | 0 | 0.01773 | 0 | 0.052844 | 0.0048337 | 0 | 0 | 0.32437 | 1.2057 | 0% | CZ 1B | 3.0868 | 1.326 | 9.1513 | 0.010228 | 0 | 11.7882 | 0.40034 | 7.4582 | 0 | 0.59736 | 0 | 1.7804 | 0.16286 | 0 | 0 | 10.9284 | 46.6901 | 0% | CZ 1B | 0.90444 | 0.38852 | 0 | 0.0029967 | 0 | 3.4539 | 0.1173 | 2.1853 | 0 | 0.17503 | 0 | 0.52166 | 0.047717 | 0 | 0 | 3.202 | 10.9989 | 0% | CZ 1B | 0 | 0 | 0.091513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091513 | 0% | CZ 1B | 9.4686 | 4.0674 | 10.0024 | 0.031372 | 0 | 36.1594 | 1.228 | 22.8774 | 0 | 1.8324 | 0 | 5.4612 | 0.49955 | 0 | 0 | 33.522 | 125.1497 | 0%
CZ 2A | 0.09162 | 0.039327 | 0.10019 | 0.0042774 | 0 | 0.27571 | 0.0093605 | 0.16049 | 0 | 0.015705 | 0 | 0.052844 | 0.0048304 | 0 | 0 | 0.32437 | 1.0787 | 16.53% | CZ 2A | 3.0868 | 1.325 | 10.0189 | 0.24857 | 0 | 9.2893 | 0.31537 | 5.4071 | 0 | 0.52914 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 43.0917 | 16.53% | CZ 2A | 0.90444 | 0.38822 | 0 | 0.026674 | 0 | 2.7218 | 0.092404 | 1.5843 | 0 | 0.15504 | 0 | 0.52166 | 0.047684 | 0 | 0 | 3.202 | 9.6442 | 16.53% | CZ 2A | 0 | 0 | 0.10019 | 0.0015754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10176 | 16.53% | CZ 2A | 9.4686 | 4.0643 | 10.9506 | 0.45144 | 0 | 28.4941 | 0.96738 | 16.5857 | 0 | 1.6231 | 0 | 5.4612 | 0.4992 | 0 | 0 | 33.522 | 112.0877 | 16.53%
CZ 2B | 0.09162 | 0.03935 | 0.10075 | 0.0014598 | 0 | 0.22329 | 0.003019 | 0.21126 | 0 | 0.014264 | 0 | 0.052844 | 0.0048304 | 0 | 0 | 0.32437 | 1.067 | 0.8505% | CZ 2B | 3.0868 | 1.3258 | 10.0746 | 0.069226 | 0 | 7.5231 | 0.10171 | 7.1175 | 0 | 0.48059 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 42.6509 | 0.8505% | CZ 2B | 0.90444 | 0.38845 | 0 | 0.011427 | 0 | 2.2043 | 0.029802 | 2.0854 | 0 | 0.14081 | 0 | 0.52166 | 0.047684 | 0 | 0 | 3.202 | 9.536 | 0.8505% | CZ 2B | 0 | 0 | 0.10075 | 0.00030226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10105 | 0.8505% | CZ 2B | 9.4686 | 4.0667 | 11.0115 | 0.15267 | 0 | 23.0763 | 0.312 | 21.8325 | 0 | 1.4742 | 0 | 5.4612 | 0.4992 | 0 | 0 | 33.522 | 110.8769 | 0.8505%
CZ 3A | 0.09162 | 0.03939 | 0.11542 | 0.063325 | 0 | 0.14601 | 0.0037262 | 0.16386 | 0 | 0.014488 | 0 | 0.052844 | 0.0048337 | 0 | 0 | 0.32437 | 1.0199 | 6.888% | CZ 3A | 3.0868 | 1.3271 | 11.5417 | 4.3752 | 0 | 4.9192 | 0.12554 | 5.5207 | 0 | 0.48812 | 0 | 1.7804 | 0.16286 | 0 | 0 | 10.9284 | 44.256 | 6.888% | CZ 3A | 0.90444 | 0.38885 | 0 | 0.2914 | 0 | 1.4413 | 0.036784 | 1.6176 | 0 | 0.14302 | 0 | 0.52166 | 0.047717 | 0 | 0 | 3.202 | 8.5948 | 6.888% | CZ 3A | 0 | 0 | 0.11542 | 0.033806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14922 | 6.888% | CZ 3A | 9.4686 | 4.0708 | 12.6151 | 6.7457 | 0 | 15.0891 | 0.38509 | 16.9342 | 0 | 1.4973 | 0 | 5.4612 | 0.49955 | 0 | 0 | 33.522 | 106.2888 | 6.888%
CZ 3B | 0.09162 | 0.039363 | 0.11152 | 0.003624 | 0 | 0.17233 | 0.0022584 | 0.19417 | 0.042593 | 0.01345 | 0 | 0.052844 | 0.0048304 | 0 | 0 | 0.32437 | 1.053 | 8.26% | CZ 3B | 3.0868 | 1.3262 | 11.1524 | 0.17239 | 0 | 5.8059 | 0.076089 | 6.5418 | 1.435 | 0.45316 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 42.9214 | 8.26% | CZ 3B | 0.90444 | 0.38858 | 0 | 0.028288 | 0 | 1.7011 | 0.022294 | 1.9167 | 0.42046 | 0.13278 | 0 | 0.52166 | 0.047684 | 0 | 0 | 3.202 | 9.2861 | 8.26% | CZ 3B | 0 | 0 | 0.11152 | 0.00075846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11228 | 8.26% | CZ 3B | 9.4686 | 4.0681 | 12.1896 | 0.37904 | 0 | 17.8092 | 0.2334 | 20.0663 | 4.4018 | 1.39 | 0 | 5.4612 | 0.4992 | 0 | 0 | 33.522 | 109.4885 | 8.26%
CZ 3C | 0.09162 | 0.039363 | 0.11716 | 0.0020269 | 0 | 0.04762 | 0.00062715 | 0.14393 | 0 | 0.0099376 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 0.83432 | 1.931% | CZ 3C | 3.0868 | 1.3262 | 11.7164 | 0.095635 | 0 | 1.6044 | 0.02113 | 4.8491 | 0 | 0.33482 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 35.906 | 1.931% | CZ 3C | 0.90444 | 0.38858 | 0 | 0.015939 | 0 | 0.47009 | 0.006191 | 1.4208 | 0 | 0.098101 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 7.0755 | 1.931% | CZ 3C | 0 | 0 | 0.11716 | 0.00041238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11758 | 1.931% | CZ 3C | 9.4686 | 4.0681 | 12.806 | 0.21193 | 0 | 4.9213 | 0.064813 | 14.8743 | 0 | 1.027 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 86.9242 | 1.931%
CZ 4A | 0.09162 | 0.039317 | 0.12741 | 0.059343 | 0 | 0.13255 | 0.0028589 | 0.18435 | 0.049088 | 0.017343 | 0 | 0.052844 | 0.0048304 | 0 | 0 | 0.32437 | 1.0859 | 26.53% | CZ 4A | 3.0868 | 1.3246 | 12.7413 | 3.9754 | 0 | 4.466 | 0.09632 | 6.211 | 1.6538 | 0.58432 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 47.0112 | 26.53% | CZ 4A | 0.90444 | 0.38812 | 0 | 0.29164 | 0 | 1.3085 | 0.028222 | 1.8198 | 0.48458 | 0.17121 | 0 | 0.52166 | 0.047684 | 0 | 0 | 3.202 | 9.1679 | 26.53% | CZ 4A | 0 | 0 | 0.12741 | 0.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15721 | 26.53% | CZ 4A | 9.4686 | 4.0633 | 13.9263 | 6.3103 | 0 | 13.6991 | 0.29545 | 19.0517 | 5.073 | 1.7924 | 0 | 5.4612 | 0.4992 | 0 | 0 | 33.522 | 113.1625 | 26.53%
CZ 4B | 0.09162 | 0.039333 | 0.12403 | 0.021377 | 0 | 0.14858 | 0.0016913 | 0.22291 | 0 | 0.013831 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 1.0454 | 0% | CZ 4B | 3.0868 | 1.3252 | 12.4032 | 1.3389 | 0 | 5.0058 | 0.056983 | 7.5104 | 0 | 0.46598 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 44.0648 | 0% | CZ 4B | 0.90444 | 0.38829 | 0 | 0.11891 | 0 | 1.4667 | 0.016696 | 2.2005 | 0 | 0.13653 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 9.0034 | 0% | CZ 4B | 0 | 0 | 0.12403 | 0.0093307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13336 | 0% | CZ 4B | 9.4686 | 4.065 | 13.5567 | 2.2648 | 0 | 15.3549 | 0.17479 | 23.0374 | 0 | 1.4293 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 108.8336 | 0%
CZ 4C | 0.09162 | 0.039287 | 0.13104 | 0.05972 | 0 | 0.040094 | 0.00049371 | 0.17962 | 0 | 0.01339 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 0.9373 | 3.991% | CZ 4C | 3.0868 | 1.3236 | 13.1041 | 4.0761 | 0 | 1.3508 | 0.016634 | 6.0516 | 0 | 0.45114 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 42.3324 | 3.991% | CZ 4C | 0.90444 | 0.38783 | 0 | 0.28225 | 0 | 0.3958 | 0.0048738 | 1.7731 | 0 | 0.13218 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 7.6518 | 3.991% | CZ 4C | 0 | 0 | 0.13104 | 0.031128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16217 | 3.991% | CZ 4C | 9.4686 | 4.0601 | 14.3227 | 6.3572 | 0 | 4.1436 | 0.051023 | 18.5628 | 0 | 1.3838 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 97.8321 | 3.991%
CZ 5A | 0.09162 | 0.039287 | 0.13757 | 0.11182 | 0 | 0.076705 | 0.0012009 | 0.16819 | 0.054865 | 0.015168 | 0 | 0.052844 | 0.0048237 | 0 | 0 | 0.32437 | 1.0785 | 13.96% | CZ 5A | 3.0868 | 1.3236 | 13.7575 | 7.7021 | 0 | 2.5843 | 0.040461 | 5.6666 | 1.8485 | 0.51105 | 0 | 1.7804 | 0.16252 | 0 | 0 | 10.9284 | 49.3923 | 13.96% | CZ 5A | 0.90444 | 0.38783 | 0 | 0.51813 | 0 | 0.75721 | 0.011855 | 1.6603 | 0.54161 | 0.14974 | 0 | 0.52166 | 0.047618 | 0 | 0 | 3.202 | 8.7024 | 13.96% | CZ 5A | 0 | 0 | 0.13757 | 0.059337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19691 | 13.96% | CZ 5A | 9.4686 | 4.0601 | 15.0369 | 11.9099 | 0 | 7.9272 | 0.12411 | 17.3817 | 5.6701 | 1.5676 | 0 | 5.4612 | 0.49851 | 0 | 0 | 33.522 | 112.6281 | 13.96%
CZ 5B | 0.09162 | 0.03932 | 0.13472 | 0.079112 | 0 | 0.099743 | 0.00099743 | 0.20841 | 0 | 0.012636 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 1.0486 | 1.287% | CZ 5B | 3.0868 | 1.3248 | 13.4719 | 5.455 | 0 | 3.3605 | 0.033605 | 7.0218 | 0 | 0.42574 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 47.0517 | 1.287% | CZ 5B | 0.90444 | 0.38816 | 0 | 0.36566 | 0 | 0.98463 | 0.0098463 | 2.0574 | 0 | 0.12474 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 8.6062 | 1.287% | CZ 5B | 0 | 0 | 0.13472 | 0.04207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17679 | 1.287% | CZ 5B | 9.4686 | 4.0636 | 14.7248 | 8.4264 | 0 | 10.3081 | 0.10308 | 21.5388 | 0 | 1.3059 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 109.4214 | 1.287%
CZ 5C | 0.09162 | 0.039273 | 0.1368 | 0.048253 | 0 | 0.0305 | 0.00032692 | 0.1695 | 0 | 0.012239 | 0 | 0.052844 | 0.0048304 | 0 | 0 | 0.32437 | 0.91055 | 0% | CZ 5C | 3.0868 | 1.3232 | 13.68 | 3.2924 | 0 | 1.0276 | 0.011014 | 5.7106 | 0 | 0.41237 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.4156 | 0% | CZ 5C | 0.90444 | 0.38769 | 0 | 0.22821 | 0 | 0.30109 | 0.0032272 | 1.6732 | 0 | 0.12082 | 0 | 0.52166 | 0.047684 | 0 | 0 | 3.202 | 7.3901 | 0% | CZ 5C | 0 | 0 | 0.1368 | 0.025135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16194 | 0% | CZ 5C | 9.4686 | 4.0588 | 14.9523 | 5.1364 | 0 | 3.1521 | 0.033786 | 17.5169 | 0 | 1.2649 | 0 | 5.4612 | 0.4992 | 0 | 0 | 33.522 | 95.0661 | 0%
CZ 6A | 0.09162 | 0.039317 | 0.1451 | 0.19035 | 0 | 0.086326 | 0.0014878 | 0.17847 | 0.051256 | 0.017066 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 1.183 | 0.6958% | CZ 6A | 3.0868 | 1.3246 | 14.5095 | 13.2715 | 0 | 2.9085 | 0.050127 | 6.0128 | 1.7269 | 0.575 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 56.3373 | 0.6958% | CZ 6A | 0.90444 | 0.38812 | 0 | 0.85804 | 0 | 0.85218 | 0.014687 | 1.7618 | 0.50598 | 0.16847 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 9.225 | 0.6958% | CZ 6A | 0 | 0 | 0.1451 | 0.10343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24853 | 0.6958% | CZ 6A | 9.4686 | 4.0633 | 15.8589 | 20.2878 | 0 | 8.9215 | 0.15376 | 18.4439 | 5.2971 | 1.7638 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 123.7407 | 0.6958%
CZ 6B | 0.09162 | 0.039283 | 0.14318 | 0.11691 | 0 | 0.070577 | 0.00073723 | 0.20626 | 0.036094 | 0.01343 | 0 | 0.052844 | 0.004827 | 0 | 0 | 0.32437 | 1.1001 | 0.179% | CZ 6B | 3.0868 | 1.3235 | 14.318 | 8.0522 | 0 | 2.3779 | 0.024839 | 6.9494 | 1.2161 | 0.45249 | 0 | 1.7804 | 0.16263 | 0 | 0 | 10.9284 | 50.6727 | 0.179% | CZ 6B | 0.90444 | 0.38779 | 0 | 0.54168 | 0 | 0.69672 | 0.0072777 | 2.0362 | 0.35631 | 0.13258 | 0 | 0.52166 | 0.047651 | 0 | 0 | 3.202 | 8.8343 | 0.179% | CZ 6B | 0 | 0 | 0.14318 | 0.062034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20521 | 0.179% | CZ 6B | 9.4686 | 4.0598 | 15.6496 | 12.4512 | 0 | 7.2939 | 0.07619 | 21.3167 | 3.7302 | 1.388 | 0 | 5.4612 | 0.49886 | 0 | 0 | 33.522 | 114.9164 | 0.179%
CZ 7 | 0.09162 | 0.0393 | 0.15405 | 0.17739 | 0 | 0.086743 | 0.0012376 | 0.19661 | 0.037539 | 0.016596 | 0 | 0.052844 | 0.0048337 | 0 | 0 | 0.32437 | 1.1831 | 0.09387% | CZ 7 | 3.0868 | 1.3241 | 15.4045 | 12.4678 | 0 | 2.9225 | 0.041697 | 6.6243 | 1.2647 | 0.55915 | 0 | 1.7804 | 0.16286 | 0 | 0 | 10.9284 | 56.5673 | 0.09387% | CZ 7 | 0.90444 | 0.38796 | 0 | 0.78477 | 0 | 0.8563 | 0.012217 | 1.9409 | 0.37057 | 0.16383 | 0 | 0.52166 | 0.047717 | 0 | 0 | 3.202 | 9.1924 | 0.09387% | CZ 7 | 0 | 0 | 0.15405 | 0.097894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25194 | 0.09387% | CZ 7 | 9.4686 | 4.0615 | 16.8371 | 18.9156 | 0 | 8.9646 | 0.1279 | 20.3194 | 3.8795 | 1.7151 | 0 | 5.4612 | 0.49955 | 0 | 0 | 33.522 | 123.7722 | 0.09387%
CZ 8 | 0.09162 | 0.03903 | 0.16609 | 0.24467 | 0 | 0.067035 | 0.00064716 | 0.22191 | 0.031764 | 0.015398 | 0 | 0.052844 | 0.0048237 | 0 | 0 | 0.32437 | 1.2602 | 0% | CZ 8 | 3.0868 | 1.315 | 16.6092 | 17.1659 | 0 | 2.2585 | 0.021804 | 7.4765 | 1.0702 | 0.5188 | 0 | 1.7804 | 0.16252 | 0 | 0 | 10.9284 | 62.3941 | 0% | CZ 8 | 0.90444 | 0.38529 | 0 | 1.0869 | 0 | 0.66174 | 0.0063886 | 2.1906 | 0.31357 | 0.15201 | 0 | 0.52166 | 0.047618 | 0 | 0 | 3.202 | 9.4723 | 0% | CZ 8 | 0 | 0 | 0.16609 | 0.13456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30065 | 0% | CZ 8 | 9.4686 | 4.0336 | 18.1538 | 26.0867 | 0 | 6.9278 | 0.066882 | 22.9336 | 3.2827 | 1.5914 | 0 | 5.4612 | 0.49851 | 0 | 0 | 33.522 | 132.0268 | 0%
US Weighted | 0.09162 | 0.03934 | 0.11539 | 0.041876 | 0 | 0.18918 | 0.0046632 | 0.17245 | 0.024658 | 0.015573 | 0 | 0.052844 | 0.0048288 | 0 | 0 | 0.32437 | 1.0768 | 100% | US Weighted | 3.0868 | 1.3254 | 11.5391 | 2.8403 | 0 | 6.3739 | 0.15711 | 5.8101 | 0.83076 | 0.52469 | 0 | 1.7804 | 0.16269 | 0 | 0 | 10.9284 | 45.3598 | 100% | US Weighted | 0.90444 | 0.38835 | 0 | 0.20057 | 0 | 1.8676 | 0.046033 | 1.7024 | 0.24341 | 0.15373 | 0 | 0.52166 | 0.047668 | 0 | 0 | 3.202 | 9.2778 | 100% | US Weighted | 0 | 0 | 0.11539 | 0.021558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13695 | 100% | US Weighted | 9.4686 | 4.0657 | 12.6122 | 4.456 | 0 | 19.5515 | 0.48192 | 17.8221 | 2.5483 | 1.6094 | 0 | 5.4612 | 0.49904 | 0 | 0 | 33.522 | 112.0981 | 100%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.11511 | 0.056293 | 0.091525 | 0 | 0 | 0.36139 | 0.0179 | 0.16188 | 0 | 0.016069 | 0 | 0.052844 | 0.006942 | 0 | 0 | 0.32437 | 1.2043 | 18.81% | CZ 1A | 3.8783 | 1.8966 | 9.1525 | 0 | 0 | 12.176 | 0.60309 | 5.4541 | 0 | 0.54139 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 46.6447 | 18.81% | CZ 1A | 1.1363 | 0.55571 | 0 | 0 | 0 | 3.5676 | 0.17671 | 1.5981 | 0 | 0.15863 | 0 | 0.52166 | 0.068529 | 0 | 0 | 3.202 | 10.9852 | 18.81% | CZ 1A | 0 | 0 | 0.091525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091525 | 18.81% | CZ 1A | 11.8964 | 5.8177 | 10.0037 | 0 | 0 | 37.3488 | 1.8499 | 16.7301 | 0 | 1.6607 | 0 | 5.4612 | 0.71743 | 0 | 0 | 33.522 | 125.008 | 18.81%
CZ 1B | 0.11511 | 0.056223 | 0.091746 | 0.00026354 | 0 | 0.35469 | 0.01801 | 0.22356 | 0 | 0.017964 | 0 | 0.052844 | 0.0069487 | 0 | 0 | 0.32437 | 1.2617 | 0% | CZ 1B | 3.8783 | 1.8943 | 9.1746 | 0.0088789 | 0 | 11.9501 | 0.6068 | 7.5322 | 0 | 0.60523 | 0 | 1.7804 | 0.23411 | 0 | 0 | 10.9284 | 48.5932 | 0% | CZ 1B | 1.1363 | 0.55502 | 0 | 0.0026015 | 0 | 3.5014 | 0.17779 | 2.2069 | 0 | 0.17733 | 0 | 0.52166 | 0.068595 | 0 | 0 | 3.202 | 11.5497 | 0% | CZ 1B | 0 | 0 | 0.091746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091746 | 0% | CZ 1B | 11.8964 | 5.8105 | 10.0278 | 0.027235 | 0 | 36.6558 | 1.8613 | 23.1043 | 0 | 1.8565 | 0 | 5.4612 | 0.71812 | 0 | 0 | 33.522 | 130.9411 | 0%
CZ 2A | 0.11511 | 0.05618 | 0.10046 | 0.0043241 | 0 | 0.28149 | 0.014825 | 0.1661 | 0 | 0.016209 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.1389 | 16.53% | CZ 2A | 3.8783 | 1.8928 | 10.0457 | 0.2497 | 0 | 9.4838 | 0.49947 | 5.5963 | 0 | 0.54611 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 45.1351 | 16.53% | CZ 2A | 1.1363 | 0.55459 | 0 | 0.027201 | 0 | 2.7788 | 0.14634 | 1.6397 | 0 | 0.16001 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 10.2352 | 16.53% | CZ 2A | 0 | 0 | 0.10046 | 0.0015686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10203 | 16.53% | CZ 2A | 11.8964 | 5.806 | 10.98 | 0.45621 | 0 | 29.0909 | 1.5321 | 17.1663 | 0 | 1.6752 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 118.3039 | 16.53%
CZ 2B | 0.11511 | 0.056213 | 0.10102 | 0.0015067 | 0 | 0.2286 | 0.0090036 | 0.21644 | 0 | 0.014678 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.1267 | 0.8505% | CZ 2B | 3.8783 | 1.8939 | 10.1021 | 0.071923 | 0 | 7.7018 | 0.30335 | 7.2921 | 0 | 0.49452 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 44.6808 | 0.8505% | CZ 2B | 1.1363 | 0.55492 | 0 | 0.011723 | 0 | 2.2566 | 0.08888 | 2.1366 | 0 | 0.1449 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 10.1222 | 0.8505% | CZ 2B | 0 | 0 | 0.10102 | 0.00031912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10134 | 0.8505% | CZ 2B | 11.8964 | 5.8094 | 11.0416 | 0.15761 | 0 | 23.6245 | 0.93049 | 22.3679 | 0 | 1.5169 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 117.0458 | 0.8505%
CZ 3A | 0.11511 | 0.05627 | 0.11577 | 0.064369 | 0 | 0.14908 | 0.0072422 | 0.16784 | 0 | 0.014825 | 0 | 0.052844 | 0.006942 | 0 | 0 | 0.32437 | 1.0747 | 6.888% | CZ 3A | 3.8783 | 1.8958 | 11.5768 | 4.4433 | 0 | 5.0228 | 0.244 | 5.6548 | 0 | 0.49947 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 46.1579 | 6.888% | CZ 3A | 1.1363 | 0.55548 | 0 | 0.29681 | 0 | 1.4717 | 0.071493 | 1.6568 | 0 | 0.14634 | 0 | 0.52166 | 0.068529 | 0 | 0 | 3.202 | 9.1272 | 6.888% | CZ 3A | 0 | 0 | 0.11577 | 0.034303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15007 | 6.888% | CZ 3A | 11.8964 | 5.8153 | 12.6534 | 6.8565 | 0 | 15.407 | 0.74846 | 17.3455 | 0 | 1.5321 | 0 | 5.4612 | 0.71743 | 0 | 0 | 33.522 | 111.9553 | 6.888%
CZ 3B | 0.11511 | 0.056233 | 0.11185 | 0.0039109 | 0 | 0.17525 | 0.0071088 | 0.19754 | 0.042593 | 0.01369 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.1075 | 8.26% | CZ 3B | 3.8783 | 1.8946 | 11.1854 | 0.18958 | 0 | 5.9046 | 0.23951 | 6.6555 | 1.435 | 0.46126 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 44.7866 | 8.26% | CZ 3B | 1.1363 | 0.55511 | 0 | 0.03 | 0 | 1.7301 | 0.070176 | 1.9501 | 0.42046 | 0.13515 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 9.8196 | 8.26% | CZ 3B | 0 | 0 | 0.11185 | 0.00087195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11273 | 8.26% | CZ 3B | 11.8964 | 5.8115 | 12.2257 | 0.40937 | 0 | 18.1119 | 0.73467 | 20.4152 | 4.4018 | 1.4149 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 115.1224 | 8.26%
CZ 3C | 0.11511 | 0.05623 | 0.11752 | 0.0019834 | 0 | 0.049608 | 0.0023752 | 0.1474 | 0 | 0.010318 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 0.8847 | 1.931% | CZ 3C | 3.8783 | 1.8945 | 11.7518 | 0.092826 | 0 | 1.6714 | 0.080023 | 4.9661 | 0 | 0.34763 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 37.6253 | 1.931% | CZ 3C | 1.1363 | 0.55508 | 0 | 0.015708 | 0 | 0.48971 | 0.023447 | 1.4551 | 0 | 0.10185 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 7.5695 | 1.931% | CZ 3C | 0 | 0 | 0.11752 | 0.00039215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11791 | 1.931% | CZ 3C | 11.8964 | 5.8111 | 12.8447 | 0.20731 | 0 | 5.1268 | 0.24546 | 15.2332 | 0 | 1.0663 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 92.1323 | 1.931%
CZ 4A | 0.11511 | 0.056166 | 0.12782 | 0.055374 | 0 | 0.13703 | 0.0066384 | 0.18679 | 0.049088 | 0.01758 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.1358 | 26.53% | CZ 4A | 3.8783 | 1.8923 | 12.7821 | 3.6952 | 0 | 4.6168 | 0.22366 | 6.2932 | 1.6538 | 0.5923 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 48.5706 | 26.53% | CZ 4A | 1.1363 | 0.55446 | 0 | 0.27425 | 0 | 1.3527 | 0.065532 | 1.8439 | 0.48458 | 0.17355 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 9.6776 | 26.53% | CZ 4A | 0 | 0 | 0.12782 | 0.027592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15541 | 26.53% | CZ 4A | 11.8964 | 5.8046 | 13.9709 | 5.8869 | 0 | 14.1617 | 0.68606 | 19.3037 | 5.073 | 1.8168 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 118.3012 | 26.53%
CZ 4B | 0.11511 | 0.05619 | 0.12442 | 0.019162 | 0 | 0.15385 | 0.0058511 | 0.22598 | 0 | 0.014044 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.0988 | 0% | CZ 4B | 3.8783 | 1.8931 | 12.4423 | 1.1885 | 0 | 5.1836 | 0.19714 | 7.6136 | 0 | 0.47317 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 45.8126 | 0% | CZ 4B | 1.1363 | 0.55469 | 0 | 0.10834 | 0 | 1.5188 | 0.057761 | 2.2308 | 0 | 0.13864 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 9.5376 | 0% | CZ 4B | 0 | 0 | 0.12442 | 0.0081869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13261 | 0% | CZ 4B | 11.8964 | 5.807 | 13.5995 | 2.0291 | 0 | 15.9003 | 0.6047 | 23.3542 | 0 | 1.4514 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 114.3436 | 0%
CZ 4C | 0.11511 | 0.05612 | 0.13147 | 0.052554 | 0 | 0.051206 | 0.0022751 | 0.19807 | 0 | 0.014788 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.0057 | 3.991% | CZ 4C | 3.8783 | 1.8908 | 13.147 | 3.5458 | 0 | 1.7252 | 0.076651 | 6.6733 | 0 | 0.49823 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 44.378 | 3.991% | CZ 4C | 1.1363 | 0.55399 | 0 | 0.25452 | 0 | 0.50549 | 0.022459 | 1.9553 | 0 | 0.14598 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 8.3663 | 3.991% | CZ 4C | 0 | 0 | 0.13147 | 0.026771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15824 | 3.991% | CZ 4C | 11.8964 | 5.7998 | 14.3697 | 5.5906 | 0 | 5.2919 | 0.23512 | 20.4697 | 0 | 1.5283 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 104.8825 | 3.991%
CZ 5A | 0.11511 | 0.05612 | 0.13803 | 0.11537 | 0 | 0.085212 | 0.0039263 | 0.18349 | 0.049088 | 0.016329 | 0 | 0.052844 | 0.0069487 | 0 | 0 | 0.32437 | 1.1468 | 13.96% | CZ 5A | 3.8783 | 1.8908 | 13.8032 | 7.9445 | 0 | 2.8709 | 0.13229 | 6.1821 | 1.6538 | 0.55016 | 0 | 1.7804 | 0.23411 | 0 | 0 | 10.9284 | 51.849 | 13.96% | CZ 5A | 1.1363 | 0.55399 | 0 | 0.53486 | 0 | 0.84118 | 0.03876 | 1.8114 | 0.48458 | 0.1612 | 0 | 0.52166 | 0.068595 | 0 | 0 | 3.202 | 9.3546 | 13.96% | CZ 5A | 0 | 0 | 0.13803 | 0.06119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19922 | 13.96% | CZ 5A | 11.8964 | 5.7998 | 15.0869 | 12.2876 | 0 | 8.8064 | 0.40577 | 18.9631 | 5.073 | 1.6876 | 0 | 5.4612 | 0.71812 | 0 | 0 | 33.522 | 119.7078 | 13.96%
CZ 5B | 0.11511 | 0.05617 | 0.13516 | 0.072419 | 0 | 0.11593 | 0.0043166 | 0.228 | 0 | 0.013821 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.1251 | 1.287% | CZ 5B | 3.8783 | 1.8925 | 13.5163 | 4.9545 | 0 | 3.906 | 0.14543 | 7.6819 | 0 | 0.46564 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 49.3833 | 1.287% | CZ 5B | 1.1363 | 0.55449 | 0 | 0.34054 | 0 | 1.1444 | 0.042612 | 2.2508 | 0 | 0.13643 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 9.3979 | 1.287% | CZ 5B | 0 | 0 | 0.13516 | 0.037923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17309 | 1.287% | CZ 5B | 11.8964 | 5.8049 | 14.7733 | 7.7101 | 0 | 11.9812 | 0.44611 | 23.5635 | 0 | 1.4283 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 117.3048 | 1.287%
CZ 5C | 0.11511 | 0.056106 | 0.13726 | 0.040197 | 0 | 0.042226 | 0.0018114 | 0.18948 | 0 | 0.013717 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 0.98006 | 0% | CZ 5C | 3.8783 | 1.8903 | 13.7255 | 2.696 | 0 | 1.4227 | 0.061029 | 6.3839 | 0 | 0.46215 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 43.4627 | 0% | CZ 5C | 1.1363 | 0.55386 | 0 | 0.19706 | 0 | 0.41684 | 0.017881 | 1.8705 | 0 | 0.13541 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 8.1201 | 0% | CZ 5C | 0 | 0 | 0.13726 | 0.020235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15749 | 0% | CZ 5C | 11.8964 | 5.7984 | 15.002 | 4.2746 | 0 | 4.3639 | 0.1872 | 19.5819 | 0 | 1.4176 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 102.2231 | 0%
CZ 6A | 0.11511 | 0.056163 | 0.14559 | 0.20396 | 0 | 0.092751 | 0.0043333 | 0.19207 | 0.042593 | 0.018094 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.2548 | 0.6958% | CZ 6A | 3.8783 | 1.8922 | 14.5594 | 14.2427 | 0 | 3.1249 | 0.146 | 6.4713 | 1.435 | 0.60961 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 59.3023 | 0.6958% | CZ 6A | 1.1363 | 0.55442 | 0 | 0.916 | 0 | 0.91561 | 0.042777 | 1.8961 | 0.42046 | 0.17862 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 9.8526 | 0.6958% | CZ 6A | 0 | 0 | 0.14559 | 0.11116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25676 | 0.6958% | CZ 6A | 11.8964 | 5.8043 | 15.9134 | 21.7399 | 0 | 9.5855 | 0.44783 | 19.8502 | 4.4018 | 1.8699 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 131.2102 | 0.6958%
CZ 6B | 0.11511 | 0.056116 | 0.14367 | 0.11364 | 0 | 0.080952 | 0.0031057 | 0.22424 | 0.035374 | 0.014585 | 0 | 0.052844 | 0.006942 | 0 | 0 | 0.32437 | 1.1709 | 0.179% | CZ 6B | 3.8783 | 1.8907 | 14.3669 | 7.8136 | 0 | 2.7274 | 0.10464 | 7.5549 | 1.1918 | 0.49138 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 52.9623 | 0.179% | CZ 6B | 1.1363 | 0.55396 | 0 | 0.52864 | 0 | 0.79913 | 0.030659 | 2.2136 | 0.3492 | 0.14397 | 0 | 0.52166 | 0.068529 | 0 | 0 | 3.202 | 9.5477 | 0.179% | CZ 6B | 0 | 0 | 0.14367 | 0.060094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20376 | 0.179% | CZ 6B | 11.8964 | 5.7994 | 15.7031 | 12.1025 | 0 | 8.3661 | 0.32096 | 23.1739 | 3.6558 | 1.5073 | 0 | 5.4612 | 0.71743 | 0 | 0 | 33.522 | 122.226 | 0.179%
CZ 7 | 0.11511 | 0.056143 | 0.15459 | 0.20552 | 0 | 0.086703 | 0.0038463 | 0.20693 | 0.036094 | 0.017343 | 0 | 0.052844 | 0.006942 | 0 | 0 | 0.32437 | 1.2664 | 0.09387% | CZ 7 | 3.8783 | 1.8916 | 15.4591 | 14.4409 | 0 | 2.9212 | 0.12959 | 6.9718 | 1.2161 | 0.58432 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 60.4355 | 0.09387% | CZ 7 | 1.1363 | 0.55423 | 0 | 0.90984 | 0 | 0.8559 | 0.037969 | 2.0427 | 0.35631 | 0.17121 | 0 | 0.52166 | 0.068529 | 0 | 0 | 3.202 | 9.8567 | 0.09387% | CZ 7 | 0 | 0 | 0.15459 | 0.11336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26795 | 0.09387% | CZ 7 | 11.8964 | 5.8022 | 16.8968 | 21.9151 | 0 | 8.9605 | 0.3975 | 21.3853 | 3.7302 | 1.7924 | 0 | 5.4612 | 0.71743 | 0 | 0 | 33.522 | 132.477 | 0.09387%
CZ 8 | 0.11511 | 0.055753 | 0.1667 | 0.29263 | 0 | 0.064183 | 0.0025686 | 0.23183 | 0.025987 | 0.016069 | 0 | 0.052844 | 0.0069453 | 0 | 0 | 0.32437 | 1.355 | 0% | CZ 8 | 3.8783 | 1.8784 | 16.6703 | 20.5615 | 0 | 2.1624 | 0.086542 | 7.8107 | 0.87553 | 0.54139 | 0 | 1.7804 | 0.234 | 0 | 0 | 10.9284 | 67.4079 | 0% | CZ 8 | 1.1363 | 0.55037 | 0 | 1.2955 | 0 | 0.63359 | 0.025357 | 2.2885 | 0.25653 | 0.15863 | 0 | 0.52166 | 0.068562 | 0 | 0 | 3.202 | 10.1371 | 0% | CZ 8 | 0 | 0 | 0.1667 | 0.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3281 | 0% | CZ 8 | 11.8964 | 5.7618 | 18.2206 | 31.2034 | 0 | 6.633 | 0.26546 | 23.9586 | 2.6856 | 1.6607 | 0 | 5.4612 | 0.71777 | 0 | 0 | 33.522 | 141.9866 | 0%
US Weighted | 0.11511 | 0.056198 | 0.11574 | 0.041163 | 0 | 0.19479 | 0.0095199 | 0.1784 | 0.023788 | 0.016057 | 0 | 0.052844 | 0.0069449 | 0 | 0 | 0.32437 | 1.1349 | 100% | US Weighted | 3.8783 | 1.8934 | 11.574 | 2.7867 | 0 | 6.5628 | 0.32074 | 6.0107 | 0.80147 | 0.54099 | 0 | 1.7804 | 0.23399 | 0 | 0 | 10.9284 | 47.3119 | 100% | US Weighted | 1.1363 | 0.55477 | 0 | 0.19796 | 0 | 1.9229 | 0.093977 | 1.7611 | 0.23483 | 0.15851 | 0 | 0.52166 | 0.068558 | 0 | 0 | 3.202 | 9.8527 | 100% | US Weighted | 0 | 0 | 0.11574 | 0.02111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13685 | 100% | US Weighted | 11.8964 | 5.8079 | 12.6504 | 4.3798 | 0 | 20.1308 | 0.98384 | 18.4374 | 2.4584 | 1.6594 | 0 | 5.4612 | 0.71773 | 0 | 0 | 33.522 | 118.1053 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.13891 | 0.056293 | 0.091522 | 0 | 0 | 0.47612 | 0.022007 | 0.19284 | 0 | 0.018354 | 0 | 0.052954 | 0.006942 | 0 | 0 | 0.32437 | 1.3803 | 18.81% | CZ 1A | 4.6802 | 1.8966 | 9.1522 | 0 | 0 | 16.0415 | 0.74145 | 6.4971 | 0 | 0.61838 | 0 | 1.7841 | 0.23389 | 0 | 0 | 10.9284 | 52.5739 | 18.81% | CZ 1A | 1.3713 | 0.55571 | 0 | 0 | 0 | 4.7001 | 0.21724 | 1.9037 | 0 | 0.18119 | 0 | 0.52274 | 0.068529 | 0 | 0 | 3.202 | 12.7225 | 18.81% | CZ 1A | 0 | 0 | 0.091522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091522 | 18.81% | CZ 1A | 14.3562 | 5.8177 | 10.0034 | 0 | 0 | 49.2058 | 2.2743 | 19.9294 | 0 | 1.8968 | 0 | 5.4726 | 0.71743 | 0 | 0 | 33.522 | 143.1957 | 18.81%
CZ 1B | 0.13891 | 0.056223 | 0.091747 | 0.00059379 | 0 | 0.43886 | 0.02156 | 0.26933 | 0 | 0.02125 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.4227 | 0% | CZ 1B | 4.6802 | 1.8943 | 9.1747 | 0.020006 | 0 | 14.7858 | 0.72639 | 9.0741 | 0 | 0.71594 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 54.0179 | 0% | CZ 1B | 1.3713 | 0.55502 | 0 | 0.0058617 | 0 | 4.3322 | 0.21283 | 2.6587 | 0 | 0.20977 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 13.1391 | 0% | CZ 1B | 0 | 0 | 0.091747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091747 | 0% | CZ 1B | 14.3562 | 5.8105 | 10.0279 | 0.061366 | 0 | 45.3542 | 2.2281 | 27.8339 | 0 | 2.1961 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 147.5807 | 0%
CZ 2A | 0.13891 | 0.05618 | 0.10046 | 0.0048513 | 0 | 0.36945 | 0.018427 | 0.20152 | 0 | 0.018955 | 0 | 0.052954 | 0.006942 | 0 | 0 | 0.32437 | 1.293 | 16.53% | CZ 2A | 4.6802 | 1.8928 | 10.0459 | 0.2615 | 0 | 12.4473 | 0.62085 | 6.7895 | 0 | 0.63861 | 0 | 1.7841 | 0.23389 | 0 | 0 | 10.9284 | 50.3231 | 16.53% | CZ 2A | 1.3713 | 0.55459 | 0 | 0.033293 | 0 | 3.6471 | 0.18191 | 1.9893 | 0 | 0.18711 | 0 | 0.52274 | 0.068529 | 0 | 0 | 3.202 | 11.7579 | 16.53% | CZ 2A | 0 | 0 | 0.10046 | 0.0014787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10194 | 16.53% | CZ 2A | 14.3562 | 5.806 | 10.9802 | 0.51017 | 0 | 38.181 | 1.9044 | 20.8261 | 0 | 1.9589 | 0 | 5.4726 | 0.71743 | 0 | 0 | 33.522 | 134.235 | 16.53%
CZ 2B | 0.13891 | 0.056213 | 0.10102 | 0.0019015 | 0 | 0.30292 | 0.011192 | 0.25691 | 0 | 0.017387 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.2707 | 0.8505% | CZ 2B | 4.6802 | 1.8939 | 10.1019 | 0.085522 | 0 | 10.2058 | 0.37707 | 8.6557 | 0 | 0.58579 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 49.5325 | 0.8505% | CZ 2B | 1.3713 | 0.55492 | 0 | 0.015576 | 0 | 2.9903 | 0.11048 | 2.5361 | 0 | 0.17164 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 11.5437 | 0.8505% | CZ 2B | 0 | 0 | 0.10102 | 0.00032361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10134 | 0.8505% | CZ 2B | 14.3562 | 5.8094 | 11.0414 | 0.19844 | 0 | 31.3056 | 1.1566 | 26.5508 | 0 | 1.7968 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 131.9276 | 0.8505%
CZ 3A | 0.13891 | 0.05627 | 0.11576 | 0.050633 | 0 | 0.20219 | 0.0090703 | 0.18247 | 0 | 0.016286 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.1559 | 6.888% | CZ 3A | 4.6802 | 1.8958 | 11.5765 | 3.4191 | 0 | 6.8122 | 0.30559 | 6.1477 | 0 | 0.5487 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 48.3323 | 6.888% | CZ 3A | 1.3713 | 0.55548 | 0 | 0.24477 | 0 | 1.996 | 0.089539 | 1.8013 | 0 | 0.16077 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 10.0124 | 6.888% | CZ 3A | 0 | 0 | 0.11576 | 0.025837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1416 | 6.888% | CZ 3A | 14.3562 | 5.8153 | 12.6531 | 5.3865 | 0 | 20.8958 | 0.93738 | 18.8576 | 0 | 1.6831 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 120.2973 | 6.888%
CZ 3B | 0.13891 | 0.056233 | 0.11185 | 0.0071786 | 0 | 0.21996 | 0.0082196 | 0.21379 | 0 | 0.014748 | 0 | 0.052954 | 0.006942 | 0 | 0 | 0.32437 | 1.1552 | 8.26% | CZ 3B | 4.6802 | 1.8946 | 11.1853 | 0.38938 | 0 | 7.4107 | 0.27693 | 7.203 | 0 | 0.49688 | 0 | 1.7841 | 0.23389 | 0 | 0 | 10.9284 | 46.4834 | 8.26% | CZ 3B | 1.3713 | 0.55511 | 0 | 0.048902 | 0 | 2.1713 | 0.081141 | 2.1105 | 0 | 0.14559 | 0 | 0.52274 | 0.068529 | 0 | 0 | 3.202 | 10.2771 | 8.26% | CZ 3B | 0 | 0 | 0.11185 | 0.0022248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11408 | 8.26% | CZ 3B | 14.3562 | 5.8115 | 12.2256 | 0.75513 | 0 | 22.7316 | 0.84947 | 22.0945 | 0 | 1.5242 | 0 | 5.4726 | 0.71743 | 0 | 0 | 33.522 | 120.0601 | 8.26%
CZ 3C | 0.13891 | 0.05623 | 0.11752 | 0.0011638 | 0 | 0.089302 | 0.003863 | 0.16291 | 0 | 0.011919 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 0.96609 | 1.931% | CZ 3C | 4.6802 | 1.8945 | 11.7519 | 0.043606 | 0 | 3.0087 | 0.13015 | 5.4889 | 0 | 0.40158 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 40.3461 | 1.931% | CZ 3C | 1.3713 | 0.55508 | 0 | 0.010834 | 0 | 0.88156 | 0.038134 | 1.6082 | 0 | 0.11766 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 8.3762 | 1.931% | CZ 3C | 0 | 0 | 0.11752 | 6.6295e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11758 | 1.931% | CZ 3C | 14.3562 | 5.8111 | 12.8448 | 0.12067 | 0 | 9.229 | 0.39922 | 16.8367 | 0 | 1.2318 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 100.5422 | 1.931%
CZ 4A | 0.13891 | 0.056166 | 0.12782 | 0.12273 | 0 | 0.15193 | 0.0068252 | 0.19313 | 0 | 0.01788 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.1997 | 26.53% | CZ 4A | 4.6802 | 1.8923 | 12.782 | 8.4388 | 0 | 5.1189 | 0.22995 | 6.507 | 0 | 0.60242 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 53.1982 | 26.53% | CZ 4A | 1.3713 | 0.55446 | 0 | 0.57086 | 0 | 1.4998 | 0.067376 | 1.9066 | 0 | 0.17651 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 9.9402 | 26.53% | CZ 4A | 0 | 0 | 0.12782 | 0.064905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19273 | 26.53% | CZ 4A | 14.3562 | 5.8046 | 13.9708 | 13.0704 | 0 | 15.7017 | 0.70536 | 19.9598 | 0 | 1.8479 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 125.1291 | 26.53%
CZ 4B | 0.13891 | 0.05619 | 0.12442 | 0.022802 | 0 | 0.18116 | 0.0063816 | 0.2334 | 0 | 0.014541 | 0 | 0.052954 | 0.006942 | 0 | 0 | 0.32437 | 1.1621 | 0% | CZ 4B | 4.6802 | 1.8931 | 12.442 | 1.4071 | 0 | 6.1034 | 0.21501 | 7.8635 | 0 | 0.48992 | 0 | 1.7841 | 0.23389 | 0 | 0 | 10.9284 | 48.0407 | 0% | CZ 4B | 1.3713 | 0.55469 | 0 | 0.12998 | 0 | 1.7883 | 0.062997 | 2.304 | 0 | 0.14355 | 0 | 0.52274 | 0.068529 | 0 | 0 | 3.202 | 10.1481 | 0% | CZ 4B | 0 | 0 | 0.12442 | 0.0096353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13406 | 0% | CZ 4B | 14.3562 | 5.807 | 13.5991 | 2.4139 | 0 | 18.7218 | 0.65951 | 24.1206 | 0 | 1.5028 | 0 | 5.4726 | 0.71743 | 0 | 0 | 33.522 | 120.8929 | 0%
CZ 4C | 0.13891 | 0.05612 | 0.13147 | 0.058847 | 0 | 0.060159 | 0.0024419 | 0.20223 | 0 | 0.015178 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 1.0496 | 3.991% | CZ 4C | 4.6802 | 1.8908 | 13.1466 | 3.9432 | 0 | 2.0269 | 0.082271 | 6.8135 | 0 | 0.51138 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 46.0415 | 3.991% | CZ 4C | 1.3713 | 0.55399 | 0 | 0.28903 | 0 | 0.59387 | 0.024105 | 1.9964 | 0 | 0.14984 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 8.7719 | 3.991% | CZ 4C | 0 | 0 | 0.13147 | 0.029568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16103 | 3.991% | CZ 4C | 14.3562 | 5.7998 | 14.3693 | 6.2576 | 0 | 6.2173 | 0.25236 | 20.8999 | 0 | 1.5686 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 109.4338 | 3.991%
CZ 5A | 0.13891 | 0.05612 | 0.13803 | 0.21553 | 0 | 0.088474 | 0.0038163 | 0.19061 | 0 | 0.016629 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 1.2324 | 13.96% | CZ 5A | 4.6802 | 1.8908 | 13.803 | 15.0903 | 0 | 2.9809 | 0.12858 | 6.4221 | 0 | 0.56027 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 58.5027 | 13.96% | CZ 5A | 1.3713 | 0.55399 | 0 | 0.96217 | 0 | 0.87339 | 0.037673 | 1.8817 | 0 | 0.16416 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 9.6377 | 13.96% | CZ 5A | 0 | 0 | 0.13803 | 0.11806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25609 | 13.96% | CZ 5A | 14.3562 | 5.7998 | 15.0866 | 22.9775 | 0 | 9.1435 | 0.3944 | 19.6992 | 0 | 1.7186 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 128.8884 | 13.96%
CZ 5B | 0.13891 | 0.05617 | 0.13516 | 0.085257 | 0 | 0.13522 | 0.0046636 | 0.23644 | 0 | 0.014334 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 1.1904 | 1.287% | CZ 5B | 4.6802 | 1.8925 | 13.5161 | 5.7892 | 0 | 4.5558 | 0.15712 | 7.966 | 0 | 0.48295 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 51.9865 | 1.287% | CZ 5B | 1.3713 | 0.55449 | 0 | 0.40739 | 0 | 1.3348 | 0.046037 | 2.334 | 0 | 0.1415 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 9.983 | 1.287% | CZ 5B | 0 | 0 | 0.13516 | 0.043988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17915 | 1.287% | CZ 5B | 14.3562 | 5.8049 | 14.7731 | 9.0729 | 0 | 13.9745 | 0.48196 | 24.435 | 0 | 1.4814 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 124.0927 | 1.287%
CZ 5C | 0.13891 | 0.056106 | 0.13725 | 0.051127 | 0 | 0.044704 | 0.0018014 | 0.19264 | 0 | 0.013977 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 1.0208 | 0% | CZ 5C | 4.6802 | 1.8903 | 13.7254 | 3.4254 | 0 | 1.5062 | 0.060692 | 6.4904 | 0 | 0.47092 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 45.1962 | 0% | CZ 5C | 1.3713 | 0.55386 | 0 | 0.2512 | 0 | 0.44131 | 0.017783 | 1.9017 | 0 | 0.13798 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 8.4685 | 0% | CZ 5C | 0 | 0 | 0.13725 | 0.025681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16294 | 0% | CZ 5C | 14.3562 | 5.7984 | 15.0019 | 5.4367 | 0 | 4.62 | 0.18617 | 19.9088 | 0 | 1.4445 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 106.4654 | 0%
CZ 6A | 0.13891 | 0.056163 | 0.14559 | 0.31728 | 0 | 0.099043 | 0.0043567 | 0.20231 | 0 | 0.018568 | 0 | 0.052954 | 0.006942 | 0 | 0 | 0.32437 | 1.3665 | 0.6958% | CZ 6A | 4.6802 | 1.8922 | 14.5592 | 22.3148 | 0 | 3.3369 | 0.14678 | 6.8162 | 0 | 0.62557 | 0 | 1.7841 | 0.23389 | 0 | 0 | 10.9284 | 67.3184 | 0.6958% | CZ 6A | 1.3713 | 0.55442 | 0 | 1.4013 | 0 | 0.97772 | 0.043008 | 1.9972 | 0 | 0.18329 | 0 | 0.52274 | 0.068529 | 0 | 0 | 3.202 | 10.3215 | 0.6958% | CZ 6A | 0 | 0 | 0.14559 | 0.17532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32091 | 0.6958% | CZ 6A | 14.3562 | 5.8043 | 15.9132 | 33.8332 | 0 | 10.2357 | 0.45025 | 20.9082 | 0 | 1.9189 | 0 | 5.4726 | 0.71743 | 0 | 0 | 33.522 | 143.1319 | 0.6958%
CZ 6B | 0.13891 | 0.056116 | 0.14367 | 0.18939 | 0 | 0.081736 | 0.0028956 | 0.23434 | 0 | 0.015148 | 0 | 0.052954 | 0.0069487 | 0 | 0 | 0.32437 | 1.2465 | 0.179% | CZ 6B | 4.6802 | 1.8907 | 14.3668 | 13.1051 | 0 | 2.7538 | 0.097556 | 7.8953 | 0 | 0.51037 | 0 | 1.7841 | 0.23411 | 0 | 0 | 10.9284 | 58.2465 | 0.179% | CZ 6B | 1.3713 | 0.55396 | 0 | 0.86858 | 0 | 0.80687 | 0.028584 | 2.3133 | 0 | 0.14954 | 0 | 0.52274 | 0.068595 | 0 | 0 | 3.202 | 9.8855 | 0.179% | CZ 6B | 0 | 0 | 0.14367 | 0.10141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24507 | 0.179% | CZ 6B | 14.3562 | 5.7994 | 15.7029 | 20.1769 | 0 | 8.4471 | 0.29925 | 24.2182 | 0 | 1.5655 | 0 | 5.4726 | 0.71812 | 0 | 0 | 33.522 | 130.2783 | 0.179%
CZ 7 | 0.13891 | 0.056143 | 0.15459 | 0.31495 | 0 | 0.077259 | 0.0032425 | 0.19669 | 0 | 0.016503 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.3426 | 0.09387% | CZ 7 | 4.6802 | 1.8916 | 15.4588 | 22.3143 | 0 | 2.603 | 0.10924 | 6.6267 | 0 | 0.556 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 67.1863 | 0.09387% | CZ 7 | 1.3713 | 0.55423 | 0 | 1.3668 | 0 | 0.76268 | 0.032009 | 1.9416 | 0 | 0.16291 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 9.9849 | 0.09387% | CZ 7 | 0 | 0 | 0.15459 | 0.17649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33108 | 0.09387% | CZ 7 | 14.3562 | 5.8022 | 16.8964 | 33.5998 | 0 | 7.9845 | 0.3351 | 20.3269 | 0 | 1.7055 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 140.719 | 0.09387%
CZ 8 | 0.13891 | 0.055753 | 0.1667 | 0.40083 | 0 | 0.052474 | 0.0019782 | 0.21866 | 0 | 0.015155 | 0 | 0.052954 | 0.0069453 | 0 | 0 | 0.32437 | 1.4347 | 0% | CZ 8 | 4.6802 | 1.8784 | 16.6701 | 28.048 | 0 | 1.7679 | 0.066648 | 7.3671 | 0 | 0.5106 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 73.9354 | 0% | CZ 8 | 1.3713 | 0.55037 | 0 | 1.7918 | 0 | 0.518 | 0.019528 | 2.1585 | 0 | 0.1496 | 0 | 0.52274 | 0.068562 | 0 | 0 | 3.202 | 10.3525 | 0% | CZ 8 | 0 | 0 | 0.1667 | 0.21933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38603 | 0% | CZ 8 | 14.3562 | 5.7618 | 18.2204 | 42.7305 | 0 | 5.423 | 0.20444 | 22.5978 | 0 | 1.5662 | 0 | 5.4726 | 0.71777 | 0 | 0 | 33.522 | 150.5727 | 0%
US Weighted | 0.13891 | 0.056198 | 0.11574 | 0.073858 | 0 | 0.2447 | 0.011197 | 0.1961 | 0 | 0.01733 | 0 | 0.052954 | 0.0069446 | 0 | 0 | 0.32437 | 1.2383 | 100% | US Weighted | 4.6802 | 1.8934 | 11.5738 | 5.0894 | 0 | 8.2444 | 0.37725 | 6.6071 | 0 | 0.58386 | 0 | 1.7841 | 0.23397 | 0 | 0 | 10.9284 | 51.996 | 100% | US Weighted | 1.3713 | 0.55477 | 0 | 0.34188 | 0 | 2.4156 | 0.11053 | 1.9359 | 0 | 0.17107 | 0 | 0.52274 | 0.068554 | 0 | 0 | 3.202 | 10.6944 | 100% | US Weighted | 0 | 0 | 0.11574 | 0.039226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15496 | 100% | US Weighted | 14.3562 | 5.8079 | 12.6502 | 7.8665 | 0 | 25.2891 | 1.1572 | 20.2667 | 0 | 1.791 | 0 | 5.4726 | 0.7177 | 0 | 0 | 33.522 | 128.897 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.11995 | 0.071308 | 0.091564 | 0 | 0 | 0.49673 | 0.023381 | 0.21 | 0 | 0.024962 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.4294 | 18.81% | CZ 1A | 4.0414 | 2.4025 | 9.1564 | 0 | 0 | 16.7358 | 0.78775 | 7.0753 | 0 | 0.84103 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 54.2294 | 18.81% | CZ 1A | 1.1841 | 0.70393 | 0 | 0 | 0 | 4.9036 | 0.23081 | 2.0731 | 0 | 0.24642 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 13.2064 | 18.81% | CZ 1A | 0 | 0 | 0.091564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091564 | 18.81% | CZ 1A | 12.3966 | 7.3694 | 10.0079 | 0 | 0 | 51.3357 | 2.4164 | 21.7029 | 0 | 2.5798 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 148.2657 | 18.81%
CZ 1B | 0.11995 | 0.071225 | 0.091786 | 0.00062381 | 0 | 0.44603 | 0.022324 | 0.29212 | 0 | 0.027688 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.4632 | 0% | CZ 1B | 4.0414 | 2.3997 | 9.1786 | 0.021017 | 0 | 15.0276 | 0.75213 | 9.8419 | 0 | 0.93285 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 55.3843 | 0% | CZ 1B | 1.1841 | 0.70311 | 0 | 0.0061581 | 0 | 4.4031 | 0.22037 | 2.8837 | 0 | 0.27333 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 13.5383 | 0% | CZ 1B | 0 | 0 | 0.091786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091786 | 0% | CZ 1B | 12.3966 | 7.3608 | 10.0322 | 0.064469 | 0 | 46.0958 | 2.3071 | 30.1893 | 0 | 2.8614 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 151.7644 | 0%
CZ 2A | 0.11995 | 0.071168 | 0.10051 | 0.0095597 | 0 | 0.37333 | 0.019065 | 0.21492 | 0 | 0.024906 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3249 | 16.53% | CZ 2A | 4.0414 | 2.3978 | 10.051 | 0.57153 | 0 | 12.5781 | 0.64232 | 7.2411 | 0 | 0.83912 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 51.5515 | 16.53% | CZ 2A | 1.1841 | 0.70255 | 0 | 0.057234 | 0 | 3.6854 | 0.1882 | 2.1216 | 0 | 0.24586 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 12.0494 | 16.53% | CZ 2A | 0 | 0 | 0.10051 | 0.003762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10427 | 16.53% | CZ 2A | 12.3966 | 7.3549 | 10.9857 | 1.0104 | 0 | 38.5823 | 1.9703 | 22.2114 | 0 | 2.5739 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 137.5422 | 16.53%
CZ 2B | 0.11995 | 0.071211 | 0.10107 | 0.0031417 | 0 | 0.30537 | 0.011395 | 0.28293 | 0 | 0.022461 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.309 | 0.8505% | CZ 2B | 4.0414 | 2.3992 | 10.1069 | 0.15093 | 0 | 10.2886 | 0.38393 | 9.5325 | 0 | 0.75673 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 50.8494 | 0.8505% | CZ 2B | 1.1841 | 0.70297 | 0 | 0.024303 | 0 | 3.0146 | 0.11249 | 2.793 | 0 | 0.22172 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 11.9177 | 0.8505% | CZ 2B | 0 | 0 | 0.10107 | 0.00067981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10175 | 0.8505% | CZ 2B | 12.3966 | 7.3594 | 11.0468 | 0.32873 | 0 | 31.5593 | 1.1777 | 29.2402 | 0 | 2.3212 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 135.887 | 0.8505%
CZ 3A | 0.11995 | 0.071281 | 0.11583 | 0.082458 | 0 | 0.20222 | 0.0092504 | 0.19697 | 0 | 0.021617 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.211 | 6.888% | CZ 3A | 4.0414 | 2.4016 | 11.5825 | 5.6998 | 0 | 6.8131 | 0.31166 | 6.6364 | 0 | 0.7283 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 51.404 | 6.888% | CZ 3A | 1.1841 | 0.70367 | 0 | 0.37903 | 0 | 1.9962 | 0.091317 | 1.9445 | 0 | 0.21339 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.3767 | 6.888% | CZ 3A | 0 | 0 | 0.11583 | 0.044061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15989 | 6.888% | CZ 3A | 12.3966 | 7.3667 | 12.6597 | 8.784 | 0 | 20.8985 | 0.956 | 20.3566 | 0 | 2.234 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 126.1092 | 6.888%
CZ 3B | 0.11995 | 0.071235 | 0.11191 | 0.015027 | 0 | 0.21731 | 0.0081763 | 0.23315 | 0 | 0.018995 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.1872 | 8.26% | CZ 3B | 4.0414 | 2.4 | 11.1913 | 0.90191 | 0 | 7.3216 | 0.27547 | 7.8552 | 0 | 0.63996 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 47.8161 | 8.26% | CZ 3B | 1.1841 | 0.7032 | 0 | 0.08944 | 0 | 2.1452 | 0.080713 | 2.3016 | 0 | 0.18751 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.5563 | 8.26% | CZ 3B | 0 | 0 | 0.11191 | 0.0059666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11788 | 8.26% | CZ 3B | 12.3966 | 7.3618 | 12.2321 | 1.5885 | 0 | 22.4586 | 0.84499 | 24.0951 | 0 | 1.963 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 123.3977 | 8.26%
CZ 3C | 0.11995 | 0.071231 | 0.11758 | 0.0029798 | 0 | 0.081035 | 0.0035627 | 0.17414 | 0 | 0.015105 | 0 | 0.054385 | 0.012063 | 0 | 0 | 0.32502 | 0.97705 | 1.931% | CZ 3C | 4.0414 | 2.3999 | 11.7582 | 0.14137 | 0 | 2.7302 | 0.12003 | 5.8671 | 0 | 0.50891 | 0 | 1.8323 | 0.40641 | 0 | 0 | 10.9503 | 40.7561 | 1.931% | CZ 3C | 1.1841 | 0.70317 | 0 | 0.023315 | 0 | 0.79995 | 0.03517 | 1.7191 | 0 | 0.14911 | 0 | 0.53687 | 0.11908 | 0 | 0 | 3.2084 | 8.4783 | 1.931% | CZ 3C | 0 | 0 | 0.11758 | 0.000618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1182 | 1.931% | CZ 3C | 12.3966 | 7.3615 | 12.8517 | 0.31163 | 0 | 8.3747 | 0.3682 | 17.9968 | 0 | 1.561 | 0 | 5.6205 | 1.2466 | 0 | 0 | 33.5892 | 101.6785 | 1.931%
CZ 4A | 0.11995 | 0.071151 | 0.1279 | 0.19337 | 0 | 0.14784 | 0.0068486 | 0.20721 | 0 | 0.023655 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.2894 | 26.53% | CZ 4A | 4.0414 | 2.3972 | 12.7898 | 13.561 | 0 | 4.981 | 0.23074 | 6.9811 | 0 | 0.79697 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 58.9683 | 26.53% | CZ 4A | 1.1841 | 0.70238 | 0 | 0.85989 | 0 | 1.4594 | 0.067607 | 2.0455 | 0 | 0.23351 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 10.4168 | 26.53% | CZ 4A | 0 | 0 | 0.1279 | 0.10626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23416 | 26.53% | CZ 4A | 12.3966 | 7.3532 | 13.9792 | 20.6166 | 0 | 15.2787 | 0.70778 | 21.414 | 0 | 2.4446 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 134.6475 | 26.53%
CZ 4B | 0.11995 | 0.071178 | 0.12448 | 0.041562 | 0 | 0.17028 | 0.0060246 | 0.2489 | 0 | 0.018244 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.1921 | 0% | CZ 4B | 4.0414 | 2.3981 | 12.4483 | 2.7151 | 0 | 5.737 | 0.20298 | 8.386 | 0 | 0.61467 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 49.7329 | 0% | CZ 4B | 1.1841 | 0.70264 | 0 | 0.21454 | 0 | 1.681 | 0.059473 | 2.4571 | 0 | 0.1801 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.3434 | 0% | CZ 4B | 0 | 0 | 0.12448 | 0.019829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14431 | 0% | CZ 4B | 12.3966 | 7.356 | 13.606 | 4.4134 | 0 | 17.5979 | 0.62262 | 25.7234 | 0 | 1.8855 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 124.0583 | 0%
CZ 4C | 0.11995 | 0.071094 | 0.13154 | 0.097275 | 0 | 0.048907 | 0.0020182 | 0.21089 | 0 | 0.019025 | 0 | 0.054385 | 0.012063 | 0 | 0 | 0.32502 | 1.0922 | 3.991% | CZ 4C | 4.0414 | 2.3953 | 13.1543 | 6.69 | 0 | 1.6478 | 0.067997 | 7.1052 | 0 | 0.64097 | 0 | 1.8323 | 0.40641 | 0 | 0 | 10.9503 | 48.9319 | 3.991% | CZ 4C | 1.1841 | 0.70182 | 0 | 0.45221 | 0 | 0.4828 | 0.019923 | 2.0818 | 0 | 0.1878 | 0 | 0.53687 | 0.11908 | 0 | 0 | 3.2084 | 8.9749 | 3.991% | CZ 4C | 0 | 0 | 0.13154 | 0.051466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18301 | 3.991% | CZ 4C | 12.3966 | 7.3474 | 14.3776 | 10.3594 | 0 | 5.0544 | 0.20858 | 21.7946 | 0 | 1.9661 | 0 | 5.6205 | 1.2466 | 0 | 0 | 33.5892 | 113.961 | 3.991%
CZ 5A | 0.11995 | 0.071094 | 0.13812 | 0.31772 | 0 | 0.083144 | 0.0036595 | 0.20179 | 0 | 0.02192 | 0 | 0.054385 | 0.012063 | 0 | 0 | 0.32502 | 1.3489 | 13.96% | CZ 5A | 4.0414 | 2.3953 | 13.8115 | 22.5533 | 0 | 2.8013 | 0.12329 | 6.7988 | 0 | 0.73853 | 0 | 1.8323 | 0.40641 | 0 | 0 | 10.9503 | 66.4524 | 13.96% | CZ 5A | 1.1841 | 0.70182 | 0 | 1.3724 | 0 | 0.82077 | 0.036125 | 1.992 | 0 | 0.21639 | 0 | 0.53687 | 0.11908 | 0 | 0 | 3.2084 | 10.1881 | 13.96% | CZ 5A | 0 | 0 | 0.13812 | 0.17869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31681 | 13.96% | CZ 5A | 12.3966 | 7.3474 | 15.096 | 33.899 | 0 | 8.5926 | 0.37819 | 20.8548 | 0 | 2.2654 | 0 | 5.6205 | 1.2466 | 0 | 0 | 33.5892 | 141.2862 | 13.96%
CZ 5B | 0.11995 | 0.071155 | 0.13524 | 0.12742 | 0 | 0.12489 | 0.0043033 | 0.24891 | 0 | 0.017824 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.2412 | 1.287% | CZ 5B | 4.0414 | 2.3973 | 13.524 | 8.8171 | 0 | 4.2078 | 0.14499 | 8.3861 | 0 | 0.60051 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 55.3084 | 1.287% | CZ 5B | 1.1841 | 0.70241 | 0 | 0.58439 | 0 | 1.2329 | 0.042481 | 2.4571 | 0 | 0.17595 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.2438 | 1.287% | CZ 5B | 0 | 0 | 0.13524 | 0.068225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20347 | 1.287% | CZ 5B | 12.3966 | 7.3536 | 14.7817 | 13.575 | 0 | 12.9072 | 0.44473 | 25.7237 | 0 | 1.842 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 129.4816 | 1.287%
CZ 5C | 0.11995 | 0.071071 | 0.13733 | 0.072578 | 0 | 0.033386 | 0.0013844 | 0.1977 | 0 | 0.0172 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.0421 | 0% | CZ 5C | 4.0414 | 2.3945 | 13.7334 | 4.9788 | 0 | 1.1248 | 0.046643 | 6.6608 | 0 | 0.57949 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 46.749 | 0% | CZ 5C | 1.1841 | 0.70159 | 0 | 0.33929 | 0 | 0.32957 | 0.013666 | 1.9516 | 0 | 0.16979 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 8.5541 | 0% | CZ 5C | 0 | 0 | 0.13733 | 0.038208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17554 | 0% | CZ 5C | 12.3966 | 7.345 | 15.0106 | 7.7282 | 0 | 3.4503 | 0.14307 | 20.4314 | 0 | 1.7775 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 108.7393 | 0%
CZ 6A | 0.11995 | 0.071145 | 0.14568 | 0.45255 | 0 | 0.094339 | 0.0043734 | 0.22665 | 0 | 0.02603 | 0 | 0.054385 | 0.012073 | 0 | 0 | 0.32502 | 1.5322 | 0.6958% | CZ 6A | 4.0414 | 2.397 | 14.5682 | 32.032 | 0 | 3.1784 | 0.14735 | 7.6361 | 0 | 0.87699 | 0 | 1.8323 | 0.40675 | 0 | 0 | 10.9503 | 78.0669 | 0.6958% | CZ 6A | 1.1841 | 0.70231 | 0 | 1.9686 | 0 | 0.93128 | 0.043172 | 2.2374 | 0 | 0.25696 | 0 | 0.53687 | 0.11918 | 0 | 0 | 3.2084 | 11.1884 | 0.6958% | CZ 6A | 0 | 0 | 0.14568 | 0.25313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39881 | 0.6958% | CZ 6A | 12.3966 | 7.3525 | 15.923 | 48.2769 | 0 | 9.7496 | 0.45197 | 23.4232 | 0 | 2.6901 | 0 | 5.6205 | 1.2477 | 0 | 0 | 33.5892 | 160.7213 | 0.6958%
CZ 6B | 0.11995 | 0.071088 | 0.14376 | 0.27986 | 0 | 0.073543 | 0.0026153 | 0.24863 | 0 | 0.019061 | 0 | 0.054385 | 0.012073 | 0 | 0 | 0.32502 | 1.35 | 0.179% | CZ 6B | 4.0414 | 2.3951 | 14.3757 | 19.5263 | 0 | 2.4778 | 0.088115 | 8.3767 | 0 | 0.64221 | 0 | 1.8323 | 0.40675 | 0 | 0 | 10.9503 | 65.1126 | 0.179% | CZ 6B | 1.1841 | 0.70176 | 0 | 1.2594 | 0 | 0.72599 | 0.025818 | 2.4544 | 0 | 0.18817 | 0 | 0.53687 | 0.11918 | 0 | 0 | 3.2084 | 10.4041 | 0.179% | CZ 6B | 0 | 0 | 0.14376 | 0.15228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29604 | 0.179% | CZ 6B | 12.3966 | 7.3467 | 15.7126 | 29.8287 | 0 | 7.6004 | 0.27029 | 25.6947 | 0 | 1.9699 | 0 | 5.6205 | 1.2477 | 0 | 0 | 33.5892 | 141.2773 | 0.179%
CZ 7 | 0.11995 | 0.071121 | 0.15469 | 0.42365 | 0 | 0.070567 | 0.0030257 | 0.20691 | 0 | 0.021466 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.4628 | 0.09387% | CZ 7 | 4.0414 | 2.3962 | 15.4687 | 30.1377 | 0 | 2.3775 | 0.10194 | 6.9711 | 0 | 0.72324 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 75.407 | 0.09387% | CZ 7 | 1.1841 | 0.70208 | 0 | 1.8203 | 0 | 0.69662 | 0.029868 | 2.0425 | 0 | 0.21191 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.5519 | 0.09387% | CZ 7 | 0 | 0 | 0.15469 | 0.23925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39394 | 0.09387% | CZ 7 | 12.3966 | 7.3501 | 16.9072 | 45.2071 | 0 | 7.2929 | 0.31269 | 21.3833 | 0 | 2.2185 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 153.5255 | 0.09387%
CZ 8 | 0.11995 | 0.070627 | 0.1668 | 0.47987 | 0 | 0.043647 | 0.0016679 | 0.22511 | 0 | 0.018618 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.5178 | 0% | CZ 8 | 4.0414 | 2.3796 | 16.6799 | 33.4925 | 0 | 1.4705 | 0.056196 | 7.5843 | 0 | 0.62726 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 79.5208 | 0% | CZ 8 | 1.1841 | 0.69721 | 0 | 2.1579 | 0 | 0.43087 | 0.016465 | 2.2222 | 0 | 0.18379 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 10.7569 | 0% | CZ 8 | 0 | 0 | 0.1668 | 0.26128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42808 | 0% | CZ 8 | 12.3966 | 7.2991 | 18.2312 | 51.1483 | 0 | 4.5107 | 0.17238 | 23.2642 | 0 | 1.9241 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 159.4033 | 0%
US Weighted | 0.11995 | 0.071191 | 0.1158 | 0.11381 | 0 | 0.2464 | 0.011528 | 0.21059 | 0 | 0.022911 | 0 | 0.054385 | 0.012067 | 0 | 0 | 0.32502 | 1.3036 | 100% | US Weighted | 4.0414 | 2.3985 | 11.5803 | 7.9784 | 0 | 8.3016 | 0.38839 | 7.095 | 0 | 0.77192 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 55.7447 | 100% | US Weighted | 1.1841 | 0.70277 | 0 | 0.50656 | 0 | 2.4324 | 0.1138 | 2.0788 | 0 | 0.22617 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 11.1091 | 100% | US Weighted | 0 | 0 | 0.1158 | 0.062495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1783 | 100% | US Weighted | 12.3966 | 7.3573 | 12.6572 | 12.1339 | 0 | 25.4644 | 1.1914 | 21.7635 | 0 | 2.3678 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 135.7889 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  |  | Natural Gas Rate, $/therm: | 1 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.11995 | 0.071308 | 0.091564 | 0 | 0 | 0.49806 | 0.023465 | 0.21139 | 0 | 0.025083 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.4323 | 18.81% | CZ 1A | 4.0414 | 2.4025 | 9.1564 | 0 | 0 | 16.7805 | 0.79056 | 7.1219 | 0 | 0.84507 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 54.3276 | 18.81% | CZ 1A | 1.1841 | 0.70393 | 0 | 0 | 0 | 4.9167 | 0.23164 | 2.0867 | 0 | 0.24761 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 13.2352 | 18.81% | CZ 1A | 0 | 0 | 0.091564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091564 | 18.81% | CZ 1A | 12.3966 | 7.3694 | 10.0079 | 0 | 0 | 51.4729 | 2.425 | 21.8459 | 0 | 2.5922 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 148.567 | 18.81%
CZ 1B | 0.11995 | 0.071225 | 0.091786 | 0.00071722 | 0 | 0.44785 | 0.022454 | 0.29458 | 0 | 0.027865 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.4679 | 0% | CZ 1B | 4.0414 | 2.3997 | 9.1786 | 0.024164 | 0 | 15.0888 | 0.75651 | 9.9248 | 0 | 0.93881 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 55.5419 | 0% | CZ 1B | 1.1841 | 0.70311 | 0 | 0.0070801 | 0 | 4.421 | 0.22166 | 2.908 | 0 | 0.27507 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 13.5844 | 0% | CZ 1B | 0 | 0 | 0.091786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091786 | 0% | CZ 1B | 12.3966 | 7.3608 | 10.0322 | 0.074122 | 0 | 46.2837 | 2.3205 | 30.4434 | 0 | 2.8797 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 152.2478 | 0%
CZ 2A | 0.11995 | 0.071168 | 0.10051 | 0.017576 | 0 | 0.38578 | 0.019969 | 0.23522 | 0 | 0.026821 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3685 | 16.53% | CZ 2A | 4.0414 | 2.3978 | 10.051 | 1.1002 | 0 | 12.9974 | 0.67278 | 7.9251 | 0 | 0.90363 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 53.2785 | 16.53% | CZ 2A | 1.1841 | 0.70255 | 0 | 0.09787 | 0 | 3.8082 | 0.19712 | 2.322 | 0 | 0.26476 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 12.4412 | 16.53% | CZ 2A | 0 | 0 | 0.10051 | 0.0076621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10817 | 16.53% | CZ 2A | 12.3966 | 7.3549 | 10.9857 | 1.8621 | 0 | 39.8685 | 2.0637 | 24.3095 | 0 | 2.7718 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 142.0696 | 16.53%
CZ 2B | 0.11995 | 0.071211 | 0.10107 | 0.0074323 | 0 | 0.3205 | 0.012169 | 0.31658 | 0 | 0.025149 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3655 | 0.8505% | CZ 2B | 4.0414 | 2.3992 | 10.107 | 0.38489 | 0 | 10.7983 | 0.41001 | 10.6662 | 0 | 0.84732 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 52.8434 | 0.8505% | CZ 2B | 1.1841 | 0.70297 | 0 | 0.053348 | 0 | 3.1639 | 0.12013 | 3.1252 | 0 | 0.24827 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 12.4624 | 0.8505% | CZ 2B | 0 | 0 | 0.10107 | 0.0020282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1031 | 0.8505% | CZ 2B | 12.3966 | 7.3594 | 11.0469 | 0.78018 | 0 | 33.1228 | 1.2577 | 32.7177 | 0 | 2.5991 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 141.737 | 0.8505%
CZ 3A | 0.11995 | 0.071281 | 0.11583 | 0.077613 | 0 | 0.2255 | 0.010455 | 0.22395 | 0 | 0.024195 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.2602 | 6.888% | CZ 3A | 4.0414 | 2.4016 | 11.5825 | 5.3049 | 0 | 7.5975 | 0.35224 | 7.5453 | 0 | 0.81518 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 52.8298 | 6.888% | CZ 3A | 1.1841 | 0.70367 | 0 | 0.3657 | 0 | 2.2261 | 0.10321 | 2.2108 | 0 | 0.23885 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 10.8968 | 6.888% | CZ 3A | 0 | 0 | 0.11583 | 0.040568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15639 | 6.888% | CZ 3A | 12.3966 | 7.3667 | 12.6597 | 8.2626 | 0 | 23.3046 | 1.0805 | 23.1446 | 0 | 2.5005 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 131.1724 | 6.888%
CZ 3B | 0.11995 | 0.071235 | 0.11191 | 0.013271 | 0 | 0.25426 | 0.0095773 | 0.26548 | 0 | 0.02165 | 0 | 0.054385 | 0.012073 | 0 | 0 | 0.32502 | 1.2588 | 8.26% | CZ 3B | 4.0414 | 2.4 | 11.1912 | 0.76662 | 0 | 8.5666 | 0.32268 | 8.9446 | 0 | 0.72942 | 0 | 1.8323 | 0.40675 | 0 | 0 | 10.9503 | 50.1519 | 8.26% | CZ 3B | 1.1841 | 0.7032 | 0 | 0.083447 | 0 | 2.51 | 0.094544 | 2.6208 | 0 | 0.21372 | 0 | 0.53687 | 0.11918 | 0 | 0 | 3.2084 | 11.2743 | 8.26% | CZ 3B | 0 | 0 | 0.11191 | 0.0048182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11673 | 8.26% | CZ 3B | 12.3966 | 7.3618 | 12.2319 | 1.4002 | 0 | 26.2774 | 0.98978 | 27.4368 | 0 | 2.2374 | 0 | 5.6205 | 1.2477 | 0 | 0 | 33.5892 | 130.7894 | 8.26%
CZ 3C | 0.11995 | 0.071231 | 0.11758 | 0.0034249 | 0 | 0.1544 | 0.0067285 | 0.26273 | 0 | 0.022994 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.1505 | 1.931% | CZ 3C | 4.0414 | 2.3999 | 11.7583 | 0.15093 | 0 | 5.2019 | 0.22669 | 8.852 | 0 | 0.77472 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 46.5951 | 1.931% | CZ 3C | 1.1841 | 0.70317 | 0 | 0.028518 | 0 | 1.5242 | 0.066421 | 2.5936 | 0 | 0.22699 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.1915 | 1.931% | CZ 3C | 0 | 0 | 0.11758 | 0.00053598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11812 | 1.931% | CZ 3C | 12.3966 | 7.3615 | 12.8518 | 0.35714 | 0 | 15.9565 | 0.69537 | 27.1527 | 0 | 2.3764 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 119.605 | 1.931%
CZ 4A | 0.11995 | 0.071151 | 0.1279 | 0.21408 | 0 | 0.14645 | 0.0068319 | 0.21121 | 0 | 0.023918 | 0 | 0.054385 | 0.012063 | 0 | 0 | 0.32502 | 1.3129 | 26.53% | CZ 4A | 4.0414 | 2.3972 | 12.7897 | 15.0343 | 0 | 4.934 | 0.23018 | 7.1159 | 0 | 0.80585 | 0 | 1.8323 | 0.40641 | 0 | 0 | 10.9503 | 60.5375 | 26.53% | CZ 4A | 1.1841 | 0.70238 | 0 | 0.94887 | 0 | 1.4457 | 0.067442 | 2.0849 | 0 | 0.23611 | 0 | 0.53687 | 0.11908 | 0 | 0 | 3.2084 | 10.5339 | 26.53% | CZ 4A | 0 | 0 | 0.1279 | 0.11796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24585 | 26.53% | CZ 4A | 12.3966 | 7.3532 | 13.9791 | 22.8265 | 0 | 15.1346 | 0.70605 | 21.8273 | 0 | 2.4719 | 0 | 5.6205 | 1.2466 | 0 | 0 | 33.5892 | 137.1517 | 26.53%
CZ 4B | 0.11995 | 0.071178 | 0.12449 | 0.052345 | 0 | 0.16766 | 0.0059446 | 0.25421 | 0 | 0.018634 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.2059 | 0% | CZ 4B | 4.0414 | 2.3981 | 12.4486 | 3.4563 | 0 | 5.6488 | 0.20028 | 8.5649 | 0 | 0.62782 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 50.5756 | 0% | CZ 4B | 1.1841 | 0.70264 | 0 | 0.26473 | 0 | 1.6551 | 0.058683 | 2.5095 | 0 | 0.18395 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.4232 | 0% | CZ 4B | 0 | 0 | 0.12449 | 0.025528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15001 | 0% | CZ 4B | 12.3966 | 7.356 | 13.6064 | 5.5617 | 0 | 17.3273 | 0.61435 | 26.2722 | 0 | 1.9258 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 125.5173 | 0%
CZ 4C | 0.11995 | 0.071094 | 0.13154 | 0.1138 | 0 | 0.045862 | 0.0018948 | 0.21318 | 0 | 0.019221 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.108 | 3.991% | CZ 4C | 4.0414 | 2.3953 | 13.1543 | 7.8539 | 0 | 1.5452 | 0.063839 | 7.1823 | 0 | 0.6476 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 50.0729 | 3.991% | CZ 4C | 1.1841 | 0.70182 | 0 | 0.52492 | 0 | 0.45273 | 0.018705 | 2.1044 | 0 | 0.18975 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 9.0409 | 3.991% | CZ 4C | 0 | 0 | 0.13154 | 0.060624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19217 | 3.991% | CZ 4C | 12.3966 | 7.3474 | 14.3776 | 12.1216 | 0 | 4.7397 | 0.19582 | 22.0311 | 0 | 1.9865 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 115.6529 | 3.991%
CZ 5A | 0.11995 | 0.071094 | 0.13812 | 0.34523 | 0 | 0.081406 | 0.0036028 | 0.20557 | 0 | 0.022237 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3787 | 13.96% | CZ 5A | 4.0414 | 2.3953 | 13.8115 | 24.5023 | 0 | 2.7427 | 0.12138 | 6.9261 | 0 | 0.7492 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 68.4791 | 13.96% | CZ 5A | 1.1841 | 0.70182 | 0 | 1.4918 | 0 | 0.80361 | 0.035565 | 2.0294 | 0 | 0.21952 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 10.3302 | 13.96% | CZ 5A | 0 | 0 | 0.13812 | 0.19411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33222 | 13.96% | CZ 5A | 12.3966 | 7.3474 | 15.096 | 36.8335 | 0 | 8.413 | 0.37233 | 21.2454 | 0 | 2.2981 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 144.4589 | 13.96%
CZ 5B | 0.11995 | 0.071155 | 0.13524 | 0.14728 | 0 | 0.1217 | 0.0042032 | 0.25363 | 0 | 0.018167 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.2628 | 1.287% | CZ 5B | 4.0414 | 2.3973 | 13.5242 | 10.1951 | 0 | 4.1004 | 0.14161 | 8.5454 | 0 | 0.61209 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 56.7467 | 1.287% | CZ 5B | 1.1841 | 0.70241 | 0 | 0.67482 | 0 | 1.2014 | 0.041493 | 2.5038 | 0 | 0.17934 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.3519 | 1.287% | CZ 5B | 0 | 0 | 0.13524 | 0.078919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21416 | 1.287% | CZ 5B | 12.3966 | 7.3536 | 14.7819 | 15.6905 | 0 | 12.5776 | 0.43439 | 26.2122 | 0 | 1.8775 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 131.7814 | 1.287%
CZ 5C | 0.11995 | 0.071071 | 0.13733 | 0.089638 | 0 | 0.029599 | 0.0012343 | 0.19946 | 0 | 0.017353 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.0571 | 0% | CZ 5C | 4.0414 | 2.3945 | 13.7333 | 6.1758 | 0 | 0.99725 | 0.041585 | 6.72 | 0 | 0.58466 | 0 | 1.8323 | 0.40652 | 0 | 0 | 10.9503 | 47.8777 | 0% | CZ 5C | 1.1841 | 0.70159 | 0 | 0.41506 | 0 | 0.29219 | 0.012184 | 1.969 | 0 | 0.17131 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 8.6099 | 0% | CZ 5C | 0 | 0 | 0.13733 | 0.047592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18493 | 0% | CZ 5C | 12.3966 | 7.345 | 15.0105 | 9.5471 | 0 | 3.059 | 0.12756 | 20.6131 | 0 | 1.7934 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 110.3489 | 0%
CZ 6A | 0.11995 | 0.071145 | 0.14568 | 0.48651 | 0 | 0.092915 | 0.0043734 | 0.23547 | 0 | 0.026851 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.5744 | 0.6958% | CZ 6A | 4.0414 | 2.397 | 14.5681 | 34.4209 | 0 | 3.1304 | 0.14735 | 7.9335 | 0 | 0.90464 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 80.7326 | 0.6958% | CZ 6A | 1.1841 | 0.70231 | 0 | 2.1185 | 0 | 0.91722 | 0.043172 | 2.3245 | 0 | 0.26506 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 11.4194 | 0.6958% | CZ 6A | 0 | 0 | 0.14568 | 0.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41758 | 0.6958% | CZ 6A | 12.3966 | 7.3525 | 15.9229 | 51.8981 | 0 | 9.6024 | 0.45197 | 24.3354 | 0 | 2.7749 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 165.1918 | 0.6958%
CZ 6B | 0.11995 | 0.071088 | 0.14376 | 0.31107 | 0 | 0.071571 | 0.002552 | 0.25329 | 0 | 0.019408 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.3842 | 0.179% | CZ 6B | 4.0414 | 2.3951 | 14.3757 | 21.6544 | 0 | 2.4114 | 0.08598 | 8.5337 | 0 | 0.6539 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 67.3407 | 0.179% | CZ 6B | 1.1841 | 0.70176 | 0 | 1.4073 | 0 | 0.70653 | 0.025192 | 2.5004 | 0 | 0.19159 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 10.5813 | 0.179% | CZ 6B | 0 | 0 | 0.14376 | 0.16851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31227 | 0.179% | CZ 6B | 12.3966 | 7.3467 | 15.7126 | 33.1512 | 0 | 7.3967 | 0.26374 | 26.1764 | 0 | 2.0058 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 144.9067 | 0.179%
CZ 7 | 0.11995 | 0.071121 | 0.15469 | 0.47506 | 0 | 0.07857 | 0.0034426 | 0.24102 | 0 | 0.024412 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.5597 | 0.09387% | CZ 7 | 4.0414 | 2.3962 | 15.4687 | 33.6747 | 0 | 2.6472 | 0.11599 | 8.1203 | 0 | 0.82248 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 80.4761 | 0.09387% | CZ 7 | 1.1841 | 0.70208 | 0 | 2.0592 | 0 | 0.77562 | 0.033985 | 2.3792 | 0 | 0.24099 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 11.2397 | 0.09387% | CZ 7 | 0 | 0 | 0.15469 | 0.26647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42115 | 0.09387% | CZ 7 | 12.3966 | 7.3501 | 16.9072 | 50.6823 | 0 | 8.12 | 0.35578 | 24.9084 | 0 | 2.5229 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 163.7003 | 0.09387%
CZ 8 | 0.11995 | 0.070627 | 0.1668 | 0.50798 | 0 | 0.052127 | 0.0020082 | 0.25596 | 0 | 0.0212 | 0 | 0.054385 | 0.012069 | 0 | 0 | 0.32502 | 1.5881 | 0% | CZ 8 | 4.0414 | 2.3796 | 16.6801 | 35.5451 | 0 | 1.7562 | 0.06766 | 8.6238 | 0 | 0.71425 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 82.9974 | 0% | CZ 8 | 1.1841 | 0.69721 | 0 | 2.2707 | 0 | 0.51458 | 0.019824 | 2.5268 | 0 | 0.20928 | 0 | 0.53687 | 0.11914 | 0 | 0 | 3.2084 | 11.287 | 0% | CZ 8 | 0 | 0 | 0.1668 | 0.27795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44475 | 0% | CZ 8 | 12.3966 | 7.2991 | 18.2313 | 54.1523 | 0 | 5.3871 | 0.20754 | 26.4529 | 0 | 2.1909 | 0 | 5.6205 | 1.2473 | 0 | 0 | 33.5892 | 166.7747 | 0%
US Weighted | 0.11995 | 0.071191 | 0.1158 | 0.12529 | 0 | 0.25413 | 0.011941 | 0.22257 | 0 | 0.023958 | 0 | 0.054385 | 0.012066 | 0 | 0 | 0.32502 | 1.3363 | 100% | US Weighted | 4.0414 | 2.3985 | 11.5802 | 8.7804 | 0 | 8.5619 | 0.40231 | 7.4988 | 0 | 0.80718 | 0 | 1.8323 | 0.40654 | 0 | 0 | 10.9503 | 57.26 | 100% | US Weighted | 1.1841 | 0.70277 | 0 | 0.55808 | 0 | 2.5086 | 0.11788 | 2.1972 | 0 | 0.2365 | 0 | 0.53687 | 0.11911 | 0 | 0 | 3.2084 | 11.3696 | 100% | US Weighted | 0 | 0 | 0.1158 | 0.068757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18456 | 100% | US Weighted | 12.3966 | 7.3573 | 12.6572 | 13.3577 | 0 | 26.2629 | 1.2341 | 23.002 | 0 | 2.476 | 0 | 5.6205 | 1.247 | 0 | 0 | 33.5892 | 139.2006 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 84352 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 84352 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 0.028332 | 0.031901 | 0.00027192 | 0 | 0 | 0.14211 | 0.014618 | 0.051913 | 0 | 0.0092304 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.28781 | 18.81% | CZ 1A | 0.95454 | 1.0748 | 0.027192 | 0 | 0 | 4.788 | 0.4925 | 1.749 | 0 | 0.31099 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 9.7149 | 18.81% | CZ 1A | 0.27968 | 0.31492 | 0 | 0 | 0 | 1.4029 | 0.1443 | 0.51247 | 0 | 0.091119 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 2.8385 | 18.81% | CZ 1A | 0 | 0 | 0.00027192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00027192 | 18.81% | CZ 1A | 2.928 | 3.2969 | 0.029721 | 0 | 0 | 14.6868 | 1.5107 | 5.365 | 0 | 0.95393 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 29.746 | 18.81%
CZ 1B | 0.028332 | 0.031868 | 0.00027305 | 0.00041365 | 0 | 0.097965 | 0.010571 | 0.073209 | 0 | 0.010134 | 0 | 0.0015412 | 0.0072322 | 0 | 0 | 0.0006505 | 0.26219 | 0% | CZ 1B | 0.95454 | 1.0737 | 0.027305 | 0.013937 | 0 | 3.3006 | 0.35617 | 2.4665 | 0 | 0.34145 | 0 | 0.051925 | 0.24367 | 0 | 0 | 0.021916 | 8.8517 | 0% | CZ 1B | 0.27968 | 0.31459 | 0 | 0.0040834 | 0 | 0.96708 | 0.10436 | 0.7227 | 0 | 0.10004 | 0 | 0.015214 | 0.071394 | 0 | 0 | 0.0064215 | 2.5856 | 0% | CZ 1B | 0 | 0 | 0.00027305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00027305 | 0% | CZ 1B | 2.928 | 3.2934 | 0.029844 | 0.042749 | 0 | 10.1243 | 1.0925 | 7.5659 | 0 | 1.0474 | 0 | 0.15928 | 0.74742 | 0 | 0 | 0.067227 | 27.0981 | 0%
CZ 2A | 0.028332 | 0.031841 | 0.00032136 | 0.013299 | 0 | 0.11006 | 0.010608 | 0.074737 | 0 | 0.011115 | 0 | 0.0015412 | 0.0072355 | 0 | 0 | 0.0006505 | 0.28974 | 16.53% | CZ 2A | 0.95454 | 1.0728 | 0.032136 | 0.85167 | 0 | 3.7081 | 0.35741 | 2.518 | 0 | 0.37449 | 0 | 0.051925 | 0.24378 | 0 | 0 | 0.021916 | 10.1868 | 16.53% | CZ 2A | 0.27968 | 0.31432 | 0 | 0.071196 | 0 | 1.0865 | 0.10472 | 0.73778 | 0 | 0.10973 | 0 | 0.015214 | 0.071427 | 0 | 0 | 0.0064215 | 2.797 | 16.53% | CZ 2A | 0 | 0 | 0.00032136 | 0.0060868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064081 | 16.53% | CZ 2A | 2.928 | 3.2907 | 0.035125 | 1.4106 | 0 | 11.3744 | 1.0963 | 7.7238 | 0 | 1.1487 | 0 | 0.15928 | 0.74777 | 0 | 0 | 0.067227 | 29.982 | 16.53%
CZ 2B | 0.028332 | 0.031861 | 0.00032361 | 0.0059725 | 0 | 0.097211 | 0.0091503 | 0.10533 | 0 | 0.010885 | 0 | 0.0015412 | 0.0072355 | 0 | 0 | 0.0006505 | 0.29849 | 0.8505% | CZ 2B | 0.95454 | 1.0735 | 0.032361 | 0.31567 | 0 | 3.2752 | 0.30829 | 3.5487 | 0 | 0.36673 | 0 | 0.051925 | 0.24378 | 0 | 0 | 0.021916 | 10.1925 | 0.8505% | CZ 2B | 0.27968 | 0.31452 | 0 | 0.041921 | 0 | 0.95964 | 0.090329 | 1.0398 | 0 | 0.10745 | 0 | 0.015214 | 0.071427 | 0 | 0 | 0.0064215 | 2.9264 | 0.8505% | CZ 2B | 0 | 0 | 0.00032361 | 0.0017259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020495 | 0.8505% | CZ 2B | 2.928 | 3.2927 | 0.035371 | 0.62751 | 0 | 10.0464 | 0.94566 | 10.8852 | 0 | 1.1249 | 0 | 0.15928 | 0.74777 | 0 | 0 | 0.067227 | 30.8601 | 0.8505%
CZ 3A | 0.028332 | 0.031891 | 0.00040788 | 0.014288 | 0 | 0.079494 | 0.0067285 | 0.060093 | 0 | 0.0097074 | 0 | 0.0015412 | 0.0072322 | 0 | 0 | 0.0006505 | 0.24037 | 6.888% | CZ 3A | 0.95454 | 1.0745 | 0.040788 | 0.92977 | 0 | 2.6783 | 0.22669 | 2.0246 | 0 | 0.32706 | 0 | 0.051925 | 0.24367 | 0 | 0 | 0.021916 | 8.5737 | 6.888% | CZ 3A | 0.27968 | 0.31482 | 0 | 0.074292 | 0 | 0.78474 | 0.066421 | 0.59322 | 0 | 0.095829 | 0 | 0.015214 | 0.071394 | 0 | 0 | 0.0064215 | 2.302 | 6.888% | CZ 3A | 0 | 0 | 0.00040788 | 0.0067621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00717 | 6.888% | CZ 3A | 2.928 | 3.2958 | 0.044582 | 1.5169 | 0 | 8.2155 | 0.69537 | 6.2104 | 0 | 1.0032 | 0 | 0.15928 | 0.74742 | 0 | 0 | 0.067227 | 24.8836 | 6.888%
CZ 3B | 0.028332 | 0.031871 | 0.00038766 | 0.0096473 | 0 | 0.081939 | 0.0073189 | 0.071318 | -0.042593 | 0.0081996 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.20586 | 8.26% | CZ 3B | 0.95454 | 1.0738 | 0.038766 | 0.59423 | 0 | 2.7607 | 0.24659 | 2.4028 | -1.435 | 0.27626 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 7.2305 | 8.26% | CZ 3B | 0.27968 | 0.31462 | 0 | 0.055159 | 0 | 0.80888 | 0.07225 | 0.70403 | -0.42046 | 0.080944 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 1.9882 | 8.26% | CZ 3B | 0 | 0 | 0.00038766 | 0.0040597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044474 | 8.26% | CZ 3B | 2.928 | 3.2938 | 0.042371 | 1.0212 | 0 | 8.4682 | 0.75639 | 7.3705 | -4.4018 | 0.8474 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 21.3009 | 8.26%
CZ 3C | 0.028332 | 0.031868 | 0.00041912 | 0.0013979 | 0 | 0.10678 | 0.0061013 | 0.11881 | 0 | 0.013057 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.31619 | 1.931% | CZ 3C | 0.95454 | 1.0737 | 0.041912 | 0.055294 | 0 | 3.5975 | 0.20556 | 4.0028 | 0 | 0.4399 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 10.6891 | 1.931% | CZ 3C | 0.27968 | 0.31459 | 0 | 0.01258 | 0 | 1.0541 | 0.06023 | 1.1728 | 0 | 0.12889 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 3.116 | 1.931% | CZ 3C | 0 | 0 | 0.00041912 | 0.0001236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00054272 | 1.931% | CZ 3C | 2.928 | 3.2934 | 0.04581 | 0.14521 | 0 | 11.0352 | 0.63055 | 12.2784 | 0 | 1.3494 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 32.6808 | 1.931%
CZ 4A | 0.028332 | 0.031834 | 0.00048317 | 0.15474 | 0 | 0.013891 | 0.003973 | 0.026857 | -0.049088 | 0.006575 | 0 | 0.0015412 | 0.0072322 | 0 | 0 | 0.0006505 | 0.22702 | 26.53% | CZ 4A | 0.95454 | 1.0726 | 0.048317 | 11.0589 | 0 | 0.468 | 0.13386 | 0.90487 | -1.6538 | 0.22152 | 0 | 0.051925 | 0.24367 | 0 | 0 | 0.021916 | 13.5262 | 26.53% | CZ 4A | 0.27968 | 0.31426 | 0 | 0.65723 | 0 | 0.13712 | 0.039221 | 0.26513 | -0.48458 | 0.064907 | 0 | 0.015214 | 0.071394 | 0 | 0 | 0.0064215 | 1.366 | 26.53% | CZ 4A | 0 | 0 | 0.00048317 | 0.088158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088641 | 26.53% | CZ 4A | 2.928 | 3.29 | 0.05281 | 16.5162 | 0 | 1.4355 | 0.4106 | 2.7756 | -5.073 | 0.67951 | 0 | 0.15928 | 0.74742 | 0 | 0 | 0.067227 | 23.9891 | 26.53%
CZ 4B | 0.028332 | 0.031844 | 0.00045395 | 0.030969 | 0 | 0.019085 | 0.0042533 | 0.031301 | 0 | 0.0048037 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.16047 | 0% | CZ 4B | 0.95454 | 1.0729 | 0.045395 | 2.1174 | 0 | 0.64299 | 0.1433 | 1.0546 | 0 | 0.16184 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 6.5108 | 0% | CZ 4B | 0.27968 | 0.31436 | 0 | 0.14582 | 0 | 0.1884 | 0.041987 | 0.30899 | 0 | 0.04742 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 1.4198 | 0% | CZ 4B | 0 | 0 | 0.00045395 | 0.016197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016651 | 0% | CZ 4B | 2.928 | 3.291 | 0.049617 | 3.2969 | 0 | 1.9723 | 0.43956 | 3.2348 | 0 | 0.49644 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 16.6836 | 0%
CZ 4C | 0.028332 | 0.031808 | 0.00050227 | 0.054078 | 0 | 0.0057678 | 0.0014011 | 0.033559 | 0 | 0.0058311 | 0 | 0.0015412 | 0.0072389 | 0 | 0 | 0.0006505 | 0.17071 | 3.991% | CZ 4C | 0.95454 | 1.0717 | 0.050227 | 3.7778 | 0 | 0.19433 | 0.047205 | 1.1307 | 0 | 0.19646 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 7.7406 | 3.991% | CZ 4C | 0.27968 | 0.314 | 0 | 0.24267 | 0 | 0.056937 | 0.013831 | 0.33128 | 0 | 0.057563 | 0 | 0.015214 | 0.07146 | 0 | 0 | 0.0064215 | 1.3891 | 3.991% | CZ 4C | 0 | 0 | 0.00050227 | 0.029496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029998 | 3.991% | CZ 4C | 2.928 | 3.2872 | 0.054898 | 5.7644 | 0 | 0.59608 | 0.1448 | 3.4682 | 0 | 0.60263 | 0 | 0.15928 | 0.74811 | 0 | 0 | 0.067227 | 17.8208 | 3.991%
CZ 5A | 0.028332 | 0.031808 | 0.00054047 | 0.2334 | 0 | 0.0047003 | 0.0024018 | 0.037385 | -0.054865 | 0.0070687 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.30021 | 13.96% | CZ 5A | 0.95454 | 1.0717 | 0.054047 | 16.8002 | 0 | 0.15836 | 0.080922 | 1.2596 | -1.8485 | 0.23816 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 19.0868 | 13.96% | CZ 5A | 0.27968 | 0.314 | 0 | 0.97363 | 0 | 0.046399 | 0.02371 | 0.36906 | -0.54161 | 0.06978 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 1.6278 | 13.96% | CZ 5A | 0 | 0 | 0.00054047 | 0.13477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13531 | 13.96% | CZ 5A | 2.928 | 3.2872 | 0.059074 | 24.9236 | 0 | 0.48576 | 0.24822 | 3.8636 | -5.6701 | 0.73053 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 31.8308 | 13.96%
CZ 5B | 0.028332 | 0.031834 | 0.00052249 | 0.068166 | 0 | 0.02196 | 0.0032058 | 0.045221 | 0 | 0.0055309 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.21421 | 1.287% | CZ 5B | 0.95454 | 1.0726 | 0.052249 | 4.74 | 0 | 0.73987 | 0.10801 | 1.5236 | 0 | 0.18635 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 9.695 | 1.287% | CZ 5B | 0.27968 | 0.31426 | 0 | 0.30915 | 0 | 0.21678 | 0.031646 | 0.44641 | 0 | 0.054599 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 1.7457 | 1.287% | CZ 5B | 0 | 0 | 0.00052249 | 0.036849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037371 | 1.287% | CZ 5B | 2.928 | 3.29 | 0.057109 | 7.2641 | 0 | 2.2695 | 0.33131 | 4.6735 | 0 | 0.5716 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 22.36 | 1.287%
CZ 5C | 0.028332 | 0.031798 | 0.00053261 | 0.041385 | 0 | -0.00090069 | 0.00090736 | 0.02996 | 0 | 0.0051139 | 0 | 0.0015412 | 0.0072355 | 0 | 0 | 0.0006505 | 0.14655 | 0% | CZ 5C | 0.95454 | 1.0713 | 0.053261 | 2.8834 | 0 | -0.030346 | 0.030571 | 1.0094 | 0 | 0.1723 | 0 | 0.051925 | 0.24378 | 0 | 0 | 0.021916 | 6.4621 | 0% | CZ 5C | 0.27968 | 0.3139 | 0 | 0.18685 | 0 | -0.0088913 | 0.0089572 | 0.29575 | 0 | 0.050483 | 0 | 0.015214 | 0.071427 | 0 | 0 | 0.0064215 | 1.2198 | 0% | CZ 5C | 0 | 0 | 0.00053261 | 0.022457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02299 | 0% | CZ 5C | 2.928 | 3.2862 | 0.058214 | 4.4107 | 0 | -0.093083 | 0.093773 | 3.0962 | 0 | 0.52851 | 0 | 0.15928 | 0.74777 | 0 | 0 | 0.067227 | 15.2828 | 0%
CZ 6A | 0.028332 | 0.031828 | 0.00058542 | 0.29616 | 0 | 0.0065884 | 0.0028855 | 0.057007 | -0.051256 | 0.0097842 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.39135 | 0.6958% | CZ 6A | 0.95454 | 1.0723 | 0.058542 | 21.1494 | 0 | 0.22197 | 0.097219 | 1.9207 | -1.7269 | 0.32965 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 24.3953 | 0.6958% | CZ 6A | 0.27968 | 0.31419 | 0 | 1.2605 | 0 | 0.065038 | 0.028485 | 0.56275 | -0.50598 | 0.096586 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 2.1944 | 0.6958% | CZ 6A | 0 | 0 | 0.00058542 | 0.16847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16906 | 0.6958% | CZ 6A | 2.928 | 3.2893 | 0.063986 | 31.6103 | 0 | 0.68089 | 0.29821 | 5.8915 | -5.2971 | 1.0112 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 41.4511 | 0.6958%
CZ 6B | 0.028332 | 0.031804 | 0.00057643 | 0.19416 | 0 | 0.00099409 | 0.0018147 | 0.047023 | -0.036094 | 0.0059779 | 0 | 0.0015412 | 0.0072422 | 0 | 0 | 0.0006505 | 0.28403 | 0.179% | CZ 6B | 0.95454 | 1.0715 | 0.057643 | 13.6022 | 0 | 0.033493 | 0.061141 | 1.5843 | -1.2161 | 0.20141 | 0 | 0.051925 | 0.244 | 0 | 0 | 0.021916 | 16.668 | 0.179% | CZ 6B | 0.27968 | 0.31396 | 0 | 0.86559 | 0 | 0.0098134 | 0.017914 | 0.46419 | -0.35631 | 0.059012 | 0 | 0.015214 | 0.071493 | 0 | 0 | 0.0064215 | 1.747 | 0.179% | CZ 6B | 0 | 0 | 0.00057643 | 0.10648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10706 | 0.179% | CZ 6B | 2.928 | 3.2869 | 0.063004 | 20.7001 | 0 | 0.10274 | 0.18755 | 4.8596 | -3.7302 | 0.6178 | 0 | 0.15928 | 0.74846 | 0 | 0 | 0.067227 | 29.9904 | 0.179%
CZ 7 | 0.028332 | 0.031821 | 0.0006416 | 0.29767 | 0 | -0.0081729 | 0.002205 | 0.044404 | -0.037539 | 0.007816 | 0 | 0.0015412 | 0.0072355 | 0 | 0 | 0.0006505 | 0.3766 | 0.09387% | CZ 7 | 0.95454 | 1.0721 | 0.06416 | 21.2068 | 0 | -0.27536 | 0.074291 | 1.496 | -1.2647 | 0.26333 | 0 | 0.051925 | 0.24378 | 0 | 0 | 0.021916 | 23.9088 | 0.09387% | CZ 7 | 0.27968 | 0.31413 | 0 | 1.2744 | 0 | -0.08068 | 0.021767 | 0.43834 | -0.37057 | 0.077157 | 0 | 0.015214 | 0.071427 | 0 | 0 | 0.0064215 | 2.0473 | 0.09387% | CZ 7 | 0 | 0 | 0.0006416 | 0.16857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16922 | 0.09387% | CZ 7 | 2.928 | 3.2886 | 0.070127 | 31.7667 | 0 | -0.84464 | 0.22788 | 4.589 | -3.8795 | 0.80775 | 0 | 0.15928 | 0.74777 | 0 | 0 | 0.067227 | 39.9281 | 0.09387%
CZ 8 | 0.028332 | 0.031598 | 0.00070902 | 0.26331 | 0 | -0.014908 | 0.001361 | 0.034053 | -0.031764 | 0.0058011 | 0 | 0.0015412 | 0.0072456 | 0 | 0 | 0.0006505 | 0.32793 | 0% | CZ 8 | 0.95454 | 1.0646 | 0.070902 | 18.3792 | 0 | -0.50228 | 0.045856 | 1.1473 | -1.0702 | 0.19545 | 0 | 0.051925 | 0.24411 | 0 | 0 | 0.021916 | 20.6033 | 0% | CZ 8 | 0.27968 | 0.31192 | 0 | 1.1838 | 0 | -0.14717 | 0.013436 | 0.33616 | -0.31357 | 0.057267 | 0 | 0.015214 | 0.071526 | 0 | 0 | 0.0064215 | 1.8147 | 0% | CZ 8 | 0 | 0 | 0.00070902 | 0.14339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1441 | 0% | CZ 8 | 2.928 | 3.2655 | 0.077496 | 28.0656 | 0 | -1.5407 | 0.14066 | 3.5192 | -3.2827 | 0.59952 | 0 | 0.15928 | 0.7488 | 0 | 0 | 0.067227 | 34.7479 | 0%
US Weighted | 0.028332 | 0.031851 | 0.00041133 | 0.083415 | 0 | 0.064941 | 0.0072778 | 0.050122 | -0.024658 | 0.0083847 | 0 | 0.0015412 | 0.0072376 | 0 | 0 | 0.0006505 | 0.25951 | 100% | US Weighted | 0.95454 | 1.0731 | 0.041133 | 5.9401 | 0 | 2.188 | 0.2452 | 1.6887 | -0.83076 | 0.28249 | 0 | 0.051925 | 0.24385 | 0 | 0 | 0.021916 | 11.9002 | 100% | US Weighted | 0.27968 | 0.31442 | 0 | 0.35751 | 0 | 0.64108 | 0.071844 | 0.49479 | -0.24341 | 0.082771 | 0 | 0.015214 | 0.071447 | 0 | 0 | 0.0064215 | 2.0918 | 100% | US Weighted | 0 | 0 | 0.00041133 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047611 | 100% | US Weighted | 2.928 | 3.2917 | 0.044958 | 8.9017 | 0 | 6.7114 | 0.75213 | 5.18 | -2.5483 | 0.86653 | 0 | 0.15928 | 0.74798 | 0 | 0 | 0.067227 | 27.1025 | 100%
Building Type: | High-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2016 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2016 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1013 |  |  |  | Natural Gas Rate, $/therm: | 1 |  |  |  |  | Prototype Floor Area: | 84352 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 84352 | [17 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 1A | 23.62% | 44.74% | 0.297% | 0% | 0% | 28.53% | 62.3% | 24.56% | 0% | 36.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 20.09% | 18.81% | CZ 1A | 23.62% | 44.74% | 0.297% | 0% | 0% | 28.53% | 62.3% | 24.56% | 0% | 36.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 17.88% | 18.81% | CZ 1A | 23.62% | 44.74% | 0% | 0% | 0% | 28.53% | 62.3% | 24.56% | 0% | 36.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 21.45% | 18.81% | CZ 1A | 0% | 0% | 0.297% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.297% | 18.81% | CZ 1A | 23.62% | 44.74% | 0.297% | 0% | 0% | 28.53% | 62.3% | 24.56% | 0% | 36.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 20.02% | 18.81%
CZ 1B | 23.62% | 44.74% | 0.2975% | 57.67% | 0% | 21.87% | 47.08% | 24.85% | 0% | 36.37% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 17.86% | 0% | CZ 1B | 23.62% | 44.74% | 0.2975% | 57.67% | 0% | 21.87% | 47.08% | 24.85% | 0% | 36.37% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 15.94% | 0% | CZ 1B | 23.62% | 44.74% | 0% | 57.67% | 0% | 21.87% | 47.08% | 24.85% | 0% | 36.37% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 19.03% | 0% | CZ 1B | 0% | 0% | 0.2975% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2975% | 0% | CZ 1B | 23.62% | 44.74% | 0.2975% | 57.67% | 0% | 21.87% | 47.08% | 24.85% | 0% | 36.37% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 17.8% | 0%
CZ 2A | 23.62% | 44.74% | 0.3197% | 75.66% | 0% | 28.53% | 53.12% | 31.77% | 0% | 41.44% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 21.17% | 16.53% | CZ 2A | 23.62% | 44.74% | 0.3197% | 77.41% | 0% | 28.53% | 53.12% | 31.77% | 0% | 41.44% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 19.12% | 16.53% | CZ 2A | 23.62% | 44.74% | 0% | 72.75% | 0% | 28.53% | 53.12% | 31.77% | 0% | 41.44% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 22.48% | 16.53% | CZ 2A | 0% | 0% | 0.3197% | 79.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.924% | 16.53% | CZ 2A | 23.62% | 44.74% | 0.3197% | 75.76% | 0% | 28.53% | 53.12% | 31.77% | 0% | 41.44% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 21.1% | 16.53%
CZ 2B | 23.62% | 44.74% | 0.3202% | 80.36% | 0% | 30.33% | 75.19% | 33.27% | 0% | 43.28% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 21.86% | 0.8505% | CZ 2B | 23.62% | 44.74% | 0.3202% | 82.01% | 0% | 30.33% | 75.19% | 33.27% | 0% | 43.28% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 19.29% | 0.8505% | CZ 2B | 23.62% | 44.74% | 0% | 78.58% | 0% | 30.33% | 75.19% | 33.27% | 0% | 43.28% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 23.48% | 0.8505% | CZ 2B | 0% | 0% | 0.3202% | 85.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.988% | 0.8505% | CZ 2B | 23.62% | 44.74% | 0.3202% | 80.43% | 0% | 30.33% | 75.19% | 33.27% | 0% | 43.28% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 21.77% | 0.8505%
CZ 3A | 23.62% | 44.74% | 0.3522% | 18.41% | 0% | 35.25% | 64.36% | 26.83% | 0% | 40.12% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 19.07% | 6.888% | CZ 3A | 23.62% | 44.74% | 0.3522% | 17.53% | 0% | 35.25% | 64.36% | 26.83% | 0% | 40.12% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 16.23% | 6.888% | CZ 3A | 23.62% | 44.74% | 0% | 20.32% | 0% | 35.25% | 64.36% | 26.83% | 0% | 40.12% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 21.13% | 6.888% | CZ 3A | 0% | 0% | 0.3522% | 16.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.585% | 6.888% | CZ 3A | 23.62% | 44.74% | 0.3522% | 18.36% | 0% | 35.25% | 64.36% | 26.83% | 0% | 40.12% | 0% | 2.834% | 59.94% | 0% | 0% | 0.2001% | 18.97% | 6.888%
CZ 3B | 23.62% | 44.74% | 0.3464% | 72.69% | 0% | 32.23% | 76.42% | 26.86% | 0% | 37.87% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 16.35% | 8.26% | CZ 3B | 23.62% | 44.74% | 0.3464% | 77.51% | 0% | 32.23% | 76.42% | 26.86% | 0% | 37.87% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 14.42% | 8.26% | CZ 3B | 23.62% | 44.74% | 0% | 66.1% | 0% | 32.23% | 76.42% | 26.86% | 0% | 37.87% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 17.64% | 8.26% | CZ 3B | 0% | 0% | 0.3464% | 84.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.81% | 8.26% | CZ 3B | 23.62% | 44.74% | 0.3464% | 72.93% | 0% | 32.23% | 76.42% | 26.86% | 0% | 37.87% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 16.29% | 8.26%
CZ 3C | 23.62% | 44.74% | 0.3564% | 40.82% | 0% | 69.16% | 90.68% | 45.22% | 0% | 56.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 27.48% | 1.931% | CZ 3C | 23.62% | 44.74% | 0.3564% | 36.64% | 0% | 69.16% | 90.68% | 45.22% | 0% | 56.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 22.94% | 1.931% | CZ 3C | 23.62% | 44.74% | 0% | 44.11% | 0% | 69.16% | 90.68% | 45.22% | 0% | 56.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 30.57% | 1.931% | CZ 3C | 0% | 0% | 0.3564% | 23.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4595% | 1.931% | CZ 3C | 23.62% | 44.74% | 0.3564% | 40.66% | 0% | 69.16% | 90.68% | 45.22% | 0% | 56.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 27.32% | 1.931%
CZ 4A | 23.62% | 44.74% | 0.3778% | 72.28% | 0% | 9.485% | 58.15% | 12.72% | 0% | 27.49% | 0% | 2.834% | 59.96% | 0% | 0% | 0.2001% | 17.29% | 26.53% | CZ 4A | 23.62% | 44.74% | 0.3778% | 73.56% | 0% | 9.485% | 58.15% | 12.72% | 0% | 27.49% | 0% | 2.834% | 59.96% | 0% | 0% | 0.2001% | 22.34% | 26.53% | CZ 4A | 23.62% | 44.74% | 0% | 69.26% | 0% | 9.485% | 58.15% | 12.72% | 0% | 27.49% | 0% | 2.834% | 59.96% | 0% | 0% | 0.2001% | 12.97% | 26.53% | CZ 4A | 0% | 0% | 0.3778% | 74.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.05% | 26.53% | CZ 4A | 23.62% | 44.74% | 0.3778% | 72.36% | 0% | 9.485% | 58.15% | 12.72% | 0% | 27.49% | 0% | 2.834% | 59.96% | 0% | 0% | 0.2001% | 17.49% | 26.53%
CZ 4B | 23.62% | 44.74% | 0.3647% | 59.16% | 0% | 11.38% | 71.55% | 12.31% | 0% | 25.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 13.31% | 0% | CZ 4B | 23.62% | 44.74% | 0.3647% | 61.26% | 0% | 11.38% | 71.55% | 12.31% | 0% | 25.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 12.87% | 0% | CZ 4B | 23.62% | 44.74% | 0% | 55.08% | 0% | 11.38% | 71.55% | 12.31% | 0% | 25.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 13.62% | 0% | CZ 4B | 0% | 0% | 0.3647% | 63.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.1% | 0% | CZ 4B | 23.62% | 44.74% | 0.3647% | 59.28% | 0% | 11.38% | 71.55% | 12.31% | 0% | 25.78% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 13.29% | 0%
CZ 4C | 23.62% | 44.74% | 0.3818% | 47.52% | 0% | 12.58% | 73.94% | 15.74% | 0% | 30.34% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 15.41% | 3.991% | CZ 4C | 23.62% | 44.74% | 0.3818% | 48.1% | 0% | 12.58% | 73.94% | 15.74% | 0% | 30.34% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 15.46% | 3.991% | CZ 4C | 23.62% | 44.74% | 0% | 46.23% | 0% | 12.58% | 73.94% | 15.74% | 0% | 30.34% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 15.36% | 3.991% | CZ 4C | 0% | 0% | 0.3818% | 48.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.61% | 3.991% | CZ 4C | 23.62% | 44.74% | 0.3818% | 47.55% | 0% | 12.58% | 73.94% | 15.74% | 0% | 30.34% | 0% | 2.834% | 59.99% | 0% | 0% | 0.2001% | 15.41% | 3.991%
CZ 5A | 23.62% | 44.74% | 0.3913% | 67.61% | 0% | 5.774% | 66.67% | 18.19% | 0% | 31.79% | 0% | 2.834% | 60.02% | 0% | 0% | 0.2001% | 21.77% | 13.96% | CZ 5A | 23.62% | 44.74% | 0.3913% | 68.57% | 0% | 5.774% | 66.67% | 18.19% | 0% | 31.79% | 0% | 2.834% | 60.02% | 0% | 0% | 0.2001% | 27.87% | 13.96% | CZ 5A | 23.62% | 44.74% | 0% | 65.27% | 0% | 5.774% | 66.67% | 18.19% | 0% | 31.79% | 0% | 2.834% | 60.02% | 0% | 0% | 0.2001% | 15.76% | 13.96% | CZ 5A | 0% | 0% | 0.3913% | 69.43% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.73% | 13.96% | CZ 5A | 23.62% | 44.74% | 0.3913% | 67.67% | 0% | 5.774% | 66.67% | 18.19% | 0% | 31.79% | 0% | 2.834% | 60.02% | 0% | 0% | 0.2001% | 22.03% | 13.96%
CZ 5B | 23.62% | 44.74% | 0.3863% | 46.28% | 0% | 18.04% | 76.27% | 17.83% | 0% | 30.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 16.96% | 1.287% | CZ 5B | 23.62% | 44.74% | 0.3863% | 46.49% | 0% | 18.04% | 76.27% | 17.83% | 0% | 30.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 17.08% | 1.287% | CZ 5B | 23.62% | 44.74% | 0% | 45.81% | 0% | 18.04% | 76.27% | 17.83% | 0% | 30.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 16.86% | 1.287% | CZ 5B | 0% | 0% | 0.3863% | 46.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.45% | 1.287% | CZ 5B | 23.62% | 44.74% | 0.3863% | 46.3% | 0% | 18.04% | 76.27% | 17.83% | 0% | 30.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 16.97% | 1.287%
CZ 5C | 23.62% | 44.74% | 0.3878% | 46.17% | 0% | -3.043% | 73.51% | 15.02% | 0% | 29.47% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 13.86% | 0% | CZ 5C | 23.62% | 44.74% | 0.3878% | 46.69% | 0% | -3.043% | 73.51% | 15.02% | 0% | 29.47% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 13.5% | 0% | CZ 5C | 23.62% | 44.74% | 0% | 45.02% | 0% | -3.043% | 73.51% | 15.02% | 0% | 29.47% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 14.17% | 0% | CZ 5C | 0% | 0% | 0.3878% | 47.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.43% | 0% | CZ 5C | 23.62% | 44.74% | 0.3878% | 46.2% | 0% | -3.043% | 73.51% | 15.02% | 0% | 29.47% | 0% | 2.834% | 59.97% | 0% | 0% | 0.2001% | 13.85% | 0%
CZ 6A | 23.62% | 44.74% | 0.4019% | 60.87% | 0% | 7.091% | 65.98% | 24.21% | 0% | 36.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 24.86% | 0.6958% | CZ 6A | 23.62% | 44.74% | 0.4019% | 61.44% | 0% | 7.091% | 65.98% | 24.21% | 0% | 36.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 30.22% | 0.6958% | CZ 6A | 23.62% | 44.74% | 0% | 59.5% | 0% | 7.091% | 65.98% | 24.21% | 0% | 36.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 19.22% | 0.6958% | CZ 6A | 0% | 0% | 0.4019% | 61.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.48% | 0.6958% | CZ 6A | 23.62% | 44.74% | 0.4019% | 60.91% | 0% | 7.091% | 65.98% | 24.21% | 0% | 36.44% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 25.09% | 0.6958%
CZ 6B | 23.62% | 44.74% | 0.401% | 62.42% | 0% | 1.389% | 71.11% | 18.56% | 0% | 30.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 20.52% | 0.179% | CZ 6B | 23.62% | 44.74% | 0.401% | 62.82% | 0% | 1.389% | 71.11% | 18.56% | 0% | 30.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 24.75% | 0.179% | CZ 6B | 23.62% | 44.74% | 0% | 61.51% | 0% | 1.389% | 71.11% | 18.56% | 0% | 30.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 16.51% | 0.179% | CZ 6B | 0% | 0% | 0.401% | 63.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.28% | 0.179% | CZ 6B | 23.62% | 44.74% | 0.401% | 62.44% | 0% | 1.389% | 71.11% | 18.56% | 0% | 30.8% | 0% | 2.834% | 60.01% | 0% | 0% | 0.2001% | 20.7% | 0.179%
CZ 7 | 23.62% | 44.74% | 0.4148% | 62.66% | 0% | -10.4% | 64.05% | 18.42% | 0% | 32.02% | 0% | 2.834% | 59.95% | 0% | 0% | 0.2001% | 24.15% | 0.09387% | CZ 7 | 23.62% | 44.74% | 0.4148% | 62.98% | 0% | -10.4% | 64.05% | 18.42% | 0% | 32.02% | 0% | 2.834% | 59.95% | 0% | 0% | 0.2001% | 29.71% | 0.09387% | CZ 7 | 23.62% | 44.74% | 0% | 61.89% | 0% | -10.4% | 64.05% | 18.42% | 0% | 32.02% | 0% | 2.834% | 59.95% | 0% | 0% | 0.2001% | 18.21% | 0.09387% | CZ 7 | 0% | 0% | 0.4148% | 63.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.18% | 0.09387% | CZ 7 | 23.62% | 44.74% | 0.4148% | 62.68% | 0% | -10.4% | 64.05% | 18.42% | 0% | 32.02% | 0% | 2.834% | 59.95% | 0% | 0% | 0.2001% | 24.39% | 0.09387%
CZ 8 | 23.62% | 44.74% | 0.4251% | 51.83% | 0% | -28.6% | 67.77% | 13.3% | 0% | 27.36% | 0% | 2.834% | 60.03% | 0% | 0% | 0.2001% | 20.65% | 0% | CZ 8 | 23.62% | 44.74% | 0.4251% | 51.71% | 0% | -28.6% | 67.77% | 13.3% | 0% | 27.36% | 0% | 2.834% | 60.03% | 0% | 0% | 0.2001% | 24.82% | 0% | CZ 8 | 23.62% | 44.74% | 0% | 52.13% | 0% | -28.6% | 67.77% | 13.3% | 0% | 27.36% | 0% | 2.834% | 60.03% | 0% | 0% | 0.2001% | 16.08% | 0% | CZ 8 | 0% | 0% | 0.4251% | 51.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.4% | 0% | CZ 8 | 23.62% | 44.74% | 0.4251% | 51.83% | 0% | -28.6% | 67.77% | 13.3% | 0% | 27.36% | 0% | 2.834% | 60.03% | 0% | 0% | 0.2001% | 20.84% | 0%
US Weighted | 23.62% | 44.74% | 0.3552% | 66.58% | 0% | 25.55% | 60.95% | 22.52% | 0% | 35% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 19.42% | 100% | US Weighted | 23.62% | 44.74% | 0.3552% | 67.65% | 0% | 25.55% | 60.95% | 22.52% | 0% | 35% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 20.78% | 100% | US Weighted | 23.62% | 44.74% | 0% | 64.06% | 0% | 25.55% | 60.95% | 22.52% | 0% | 35% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 18.4% | 100% | US Weighted | 0% | 0% | 0.3552% | 68.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.8% | 100% | US Weighted | 23.62% | 44.74% | 0.3552% | 66.64% | 0% | 25.55% | 60.95% | 22.52% | 0% | 35% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 19.47% | 100%