## Intro
| PNNL | 2014-06-20 | Reid Hart, PE & PNNL Codes Team
This spreadsheet contains detailed end use data results from the Progress Indicator analysis
of ASHRAE Standard 90.1 conducted by PNNL.
The spreadsheet includes a list (DetPri tab) of all detailed ECIs by end use and prototype,
sorted by remaining use after 90.1-2013 and sorted by savings of 90.1-2013 vs. 90.1-2004.
Data includes detailed results for each of the prototypes at the detailed end use level. A tab
for each prototype includes a matrix of tables with a summary and detail for each climate
zone. In addition to ECI, both site and source energy use index (EUI) results are included as is
end use for gas and electric. Vertically, tables are included for:
US average summary results, based on construction weighting
Separate climate zone detail tables for energy cost and use after Standard 90.1 in 2004, 2007, 2010, and 2013
Percentage savings from Standard 90.1-2004 to 90.1-2013
End uses are from energy plus simulation of the prototype models, and are defined as follows:
| Simple Breakdown | Detailed Breakdown | End Use Description
| Light.int | Light.int | Interior Lighting
| Light.ext | Light.ext | Exterior Lighting
| SHW | SHW | Service Hot Water
| Heat | Heat | Space Heating
|  | Humidify | Humidification (Dehumidification in Heat and Cool)
| Cool | Cool | Mechanical Cooling (including unitary heat rejection)
|  | Ht.Rej | Heat rejection, cooling towers (unitary is in cool)
| Fan.Aux | Fans | HVAC supply, return and exhaust fans
|  | Ht.Rcvy | Heat recovery fan and wheel energy
|  | Pumps | Hydronic pumping, including SHW recirculation
| Misc | Refrig | Refrigeration equipment and kitchen refrigerators and freezers
|  | Elevator | Elevators
|  | Txfmr | In-building transformers
| Equip | Cook | Cooking
|  | IT | Computer room IT equipment and telephone equipment
|  | Equip | Other plug loads and equipment incl. non-kitchen refrigerators
The 16 building prototypes are listed below and further detail and description can be found at:
http://www.energycodes.gov/commercial-prototype-building-models
Related analysis results can be found here:
http://www.energycodes.gov/development/commercial/cost_effectiveness
(Rounded)
|  |  |  | TSD | E+
|  |  |  | Floor area | Floor area
| Abbrev. | Tab | Building Prototype | (ft²) | (ft²)
| OfcS | SmOffice | Small Office | 5500 | 5502
| OfcM | MdOffice | Medium Office | 53630 | 53628
| OfcL | LgOffice | Large Office | 498640 | 498588
| RtlB | RetailStore | Standalone Retail | 24690 | 24692
| RtlS | StripMall | Strip Mall | 22500 | 22500
| SchP | PriSchool | Primary School | 73970 | 73959
| SchS | SecSchool | Secondary School | 210910 | 210887
| MedC | Clinic | Outpatient Healthcare | 40950 | 40946
| MedH | Hospital | Hospital | 241410 | 241501
| HotS | SmHotel | Small Hotel | 43210 | 43202
| HotL | LgHotel | Large Hotel | 122120 | 122120
| Whse | Warehouse | Warehouse | 52050 | 52045
| Fast | FastFood | Quick-service Restaurant | 2500 | 2501
| Rest | Restaurant | Full-service Restaurant | 5500 | 5502
| AptM | MidApartment | Mid-rise Apartment | 33740 | 33741
| AptH | HiApartment | High-rise Apartment | 84360 | 84352

## DetPri
Priority sort by remaining ECI (after 90.1-2013) by end use and Prototype |  |  |  |  | Priority sort by past cost savings (90.1-2013 vs. 90.1-2004) by end use and Prototype
Prototype | End Use | ECI | Bar - Remaining ECI |  | Prototype | End Use | ECI Savings | Bar - unsaved
Fast Food | Cook | 4.469 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++++ | Lg Office | Humidify | -685%
Restaurant | Cook | 2.977 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++ | Fast Food | SHW | -0.0651% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Heat | 1.3731 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Md Office | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Refrig | 0.97705 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Sm Hotel | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | SHW | 0.92479 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Restaurant | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Clinic | Equip | 0.87639 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Lg Hotel | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Lg Office | IT | 0.85794 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Pri School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Restaurant | Heat | 0.81604 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Sec School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Fans | 0.76157 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Hospital | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | Cool | 0.75108 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  | Fast Food | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Fast Food | SHW | 0.67271 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Restaurant | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Equip | 0.63204 | XXXXXXXXXXXXXXXXXXXXXXXXX |  | Lg Office | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Light.Int | 0.6179 | XXXXXXXXXXXXXXXXXXXXXXXX |  | Sm Hotel | SHW | 0.07377% | XXXXXXXXXXXXXXXXXXX
Restaurant | Cool | 0.59382 | XXXXXXXXXXXXXXXXXXXXXXX |  | Hi Apartment | SHW | 0.08263% | XXXXXXXXXXXXXXXXXXX
Clinic | Cool | 0.57012 | XXXXXXXXXXXXXXXXXXXXXX |  | Mid Apartment | SHW | 0.1041% | XXXXXXXXXXXXXXXXXXX
Restaurant | Fans | 0.56032 | XXXXXXXXXXXXXXXXXXXXXX |  | Sec School | SHW | 0.1462% | XXXXXXXXXXXXXXXXXXX
Clinic | Elevator | 0.44756 | XXXXXXXXXXXXXXXXX |  | Sm Office | SHW | 0.1668% | XXXXXXXXXXXXXXXXXXX
Restaurant | Refrig | 0.43488 | XXXXXXXXXXXXXXXXX |  | Hi Apartment | Equip | 0.1991% | XXXXXXXXXXXXXXXXXXX
Retail Store | Light.Int | 0.43204 | XXXXXXXXXXXXXXXXX |  | Lg Office | SHW | 0.2229% | XXXXXXXXXXXXXXXXXXX
Hospital | Light.Int | 0.41699 | XXXXXXXXXXXXXXXX |  | Lg Hotel | SHW | 0.334% | XXXXXXXXXXXXXXXXXXX
Restaurant | Light.Int | 0.37178 | XXXXXXXXXXXXXX |  | Retail Store | Equip | 0.4407% | XXXXXXXXXXXXXXXXXXX
Fast Food | Light.Int | 0.37087 | XXXXXXXXXXXXXX |  | Strip Mall | Equip | 0.4428% | XXXXXXXXXXXXXXXXXXX
Lg Hotel | Cool | 0.36727 | XXXXXXXXXXXXXX |  | Mid Apartment | Equip | 0.4999% | XXXXXXXXXXXXXXXXXXX
Pri School | Equip | 0.36238 | XXXXXXXXXXXXXX |  | Hospital | SHW | 0.5753% | XXXXXXXXXXXXXXXXXXX
Clinic | Light.Int | 0.35314 | XXXXXXXXXXXXXX |  | Clinic | Equip | 0.9072% | XXXXXXXXXXXXXXXXXXX
Hospital | Fans | 0.34464 | XXXXXXXXXXXXX |  | Restaurant | SHW | 1.166% | XXXXXXXXXXXXXXXXXXX
Clinic | Heat | 0.33999 | XXXXXXXXXXXXX |  | Clinic | SHW | 1.211% | XXXXXXXXXXXXXXXXXXX
Hi Apartment | Equip | 0.33045 | XXXXXXXXXXXXX |  | Hospital | Elevator | 1.297% | XXXXXXXXXXXXXXXXXXX
Mid Apartment | Equip | 0.32806 | XXXXXXXXXXXXX |  | Md Office | SHW | 1.491% | XXXXXXXXXXXXXXXXXXX
Mid Apartment | SHW | 0.32239 | XXXXXXXXXXXX |  | Clinic | Elevator | 1.955% | XXXXXXXXXXXXXXXXXXX
Lg Hotel | Cook | 0.31637 | XXXXXXXXXXXX |  | Warehouse | Equip | 1.996% | XXXXXXXXXXXXXXXXXXX
Md Office | Equip | 0.31254 | XXXXXXXXXXXX |  | Retail Store | SHW | 2.143% | XXXXXXXXXXXXXXXXXXX
Lg Office | Equip | 0.30673 | XXXXXXXXXXXX |  | Pri School | Pumps | 2.739% | XXXXXXXXXXXXXXXXXXX
Hospital | Heat | 0.3056 | XXXXXXXXXXXX |  | Lg Office | Elevator | 2.833% | XXXXXXXXXXXXXXXXXXX
Hospital | Cool | 0.29901 | XXXXXXXXXXX |  | Hi Apartment | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Hospital | Elevator | 0.29763 | XXXXXXXXXXX |  | Lg Hotel | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Sm Hotel | Equip | 0.29576 | XXXXXXXXXXX |  | Hospital | Equip | 3.169% | XXXXXXXXXXXXXXXXXXX
Hospital | Cook | 0.29079 | XXXXXXXXXXX |  | Warehouse | SHW | 3.19% | XXXXXXXXXXXXXXXXXXX
Pri School | Light.Int | 0.27405 | XXXXXXXXXX |  | Pri School | SHW | 3.516% | XXXXXXXXXXXXXXXXXXX
Clinic | Fans | 0.26101 | XXXXXXXXXX |  | Mid Apartment | Elevator | 3.565% | XXXXXXXXXXXXXXXXXXX
Sec School | Equip | 0.25915 | XXXXXXXXXX |  | Sm Hotel | Elevator | 3.566% | XXXXXXXXXXXXXXXXXXX
Sec School | Light.Int | 0.25199 | XXXXXXXXXX |  | Hi Apartment | Light.Int | 5.14% | XXXXXXXXXXXXXXXXXX
Sm Office | Equip | 0.2516 | XXXXXXXXXX |  | Md Office | Elevator | 5.47% | XXXXXXXXXXXXXXXXXX
Sm Office | Light.Int | 0.23798 | XXXXXXXXX |  | Sm Hotel | Fans | 6.717% | XXXXXXXXXXXXXXXXXX
Lg Office | Cool | 0.23004 | XXXXXXXXX |  | Sm Hotel | Equip | 7.288% | XXXXXXXXXXXXXXXXXX
Sec School | Cool | 0.22937 | XXXXXXXXX |  | Fast Food | Heat | 8.128% | XXXXXXXXXXXXXXXXXX
Retail Store | Equip | 0.22558 | XXXXXXXXX |  | Strip Mall | SHW | 8.303% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Elevator | 0.22311 | XXXXXXXX |  | Mid Apartment | Light.Int | 8.535% | XXXXXXXXXXXXXXXXXX
Pri School | Cool | 0.21633 | XXXXXXXX |  | Sm Office | Equip | 8.542% | XXXXXXXXXXXXXXXXXX
Retail Store | Fans | 0.21495 | XXXXXXXX |  | Md Office | Equip | 8.826% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Light.Int | 0.21495 | XXXXXXXX |  | Lg Hotel | Equip | 9.051% | XXXXXXXXXXXXXXXXXX
Sm Hotel | Light.Int | 0.21352 | XXXXXXXX |  | Sec School | Refrig | 9.101% | XXXXXXXXXXXXXXXXXX
Lg Hotel | Equip | 0.20483 | XXXXXXXX |  | Lg Office | Equip | 9.145% | XXXXXXXXXXXXXXXXXX
Strip Mall | Cool | 0.20011 | XXXXXXXX |  | Pri School | Refrig | 9.96% | XXXXXXXXXXXXXXXXXX
Lg Office | Light.Int | 0.19606 | XXXXXXX |  | Sec School | Equip | 10.17% | XXXXXXXXXXXXXXXXX
Sm Hotel | Cool | 0.19011 | XXXXXXX |  | Lg Office | Fans | 12.89% | XXXXXXXXXXXXXXXXX
Hi Apartment | Cool | 0.18726 | XXXXXXX |  | Sec School | Elevator | 13.14% | XXXXXXXXXXXXXXXXX
Hi Apartment | Fans | 0.18591 | XXXXXXX |  | Pri School | Equip | 14.74% | XXXXXXXXXXXXXXXXX
Sm Hotel | Fans | 0.18497 | XXXXXXX |  | Hospital | Light.Int | 16.02% | XXXXXXXXXXXXXXXX
Strip Mall | Fans | 0.18267 | XXXXXXX |  | Clinic | Light.Int | 17.48% | XXXXXXXXXXXXXXXX
Lg Hotel | SHW | 0.17906 | XXXXXXX |  | Lg Hotel | Refrig | 17.54% | XXXXXXXXXXXXXXXX
Retail Store | Cool | 0.17813 | XXXXXXX |  | Clinic | Pumps | 17.69% | XXXXXXXXXXXXXXXX
Fast Food | Light.Ext | 0.17694 | XXXXXXX |  | Hi Apartment | Fans | 20.19% | XXXXXXXXXXXXXXX
Md Office | Light.Int | 0.17544 | XXXXXXX |  | Mid Apartment | Fans | 20.22% | XXXXXXXXXXXXXXX
Md Office | Cool | 0.17356 | XXXXXX |  | Fast Food | Refrig | 21.33% | XXXXXXXXXXXXXXX
Restaurant | Light.Ext | 0.17255 | XXXXXX |  | Hospital | Light.Ext | 21.33% | XXXXXXXXXXXXXXX
Mid Apartment | Fans | 0.17132 | XXXXXX |  | Hospital | Refrig | 21.87% | XXXXXXXXXXXXXXX
Warehouse | Light.Int | 0.16999 | XXXXXX |  | Hi Apartment | Ht.Rej | 21.98% | XXXXXXXXXXXXXXX
Sm Hotel | Elevator | 0.16583 | XXXXXX |  | Restaurant | Refrig | 22.03% | XXXXXXXXXXXXXXX
Strip Mall | Equip | 0.16327 | XXXXXX |  | Lg Hotel | Light.Ext | 23.24% | XXXXXXXXXXXXXXX
Lg Hotel | Fans | 0.15144 | XXXXXX |  | Strip Mall | Light.Int | 23.27% | XXXXXXXXXXXXXXX
Sm Hotel | SHW | 0.12657 | XXXXX |  | Hi Apartment | Light.Ext | 23.68% | XXXXXXXXXXXXXXX
Lg Office | Fans | 0.12572 | XXXXX |  | Sm Office | Fans | 24.21% | XXXXXXXXXXXXXXX
Pri School | Fans | 0.12348 | XXXX |  | Retail Store | Light.Int | 24.37% | XXXXXXXXXXXXXXX
Mid Apartment | Cool | 0.12063 | XXXX |  | Hi Apartment | Cool | 24.74% | XXXXXXXXXXXXXXX
Sm Hotel | Heat | 0.11578 | XXXX |  | Hospital | Ht.Rej | 25.24% | XXXXXXXXXXXXXX
Hi Apartment | SHW | 0.11322 | XXXX |  | Restaurant | Heat | 25.36% | XXXXXXXXXXXXXX
Sec School | Fans | 0.11089 | XXXX |  | Sm Hotel | Cool | 30.8% | XXXXXXXXXXXXX
Lg Office | Elevator | 0.10929 | XXXX |  | Lg Office | Light.Ext | 30.91% | XXXXXXXXXXXXX
Strip Mall | Heat | 0.10856 | XXXX |  | Md Office | Fans | 30.92% | XXXXXXXXXXXXX
Mid Apartment | Elevator | 0.10617 | XXXX |  | Sm Hotel | Light.Ext | 30.92% | XXXXXXXXXXXXX
Sm Office | Fans | 0.10441 | XXXX |  | Clinic | Cool | 30.96% | XXXXXXXXXXXXX
Pri School | Cook | 0.10384 | XXXX |  | Lg Office | Cool | 31.62% | XXXXXXXXXXXXX
Sm Office | Cool | 0.09972 | XXX |  | Fast Food | Cool | 32.09% | XXXXXXXXXXXXX
Pri School | Heat | 0.099364 | XXX |  | Warehouse | Light.Ext | 33.1% | XXXXXXXXXXXXX
Mid Apartment | Light.Int | 0.094052 | XXX |  | Lg Office | Light.Int | 33.65% | XXXXXXXXXXXXX
Sm Office | SHW | 0.093836 | XXX |  | Hi Apartment | Pumps | 33.74% | XXXXXXXXXXXXX
Lg Hotel | Heat | 0.093215 | XXX |  | Hospital | Fans | 34.59% | XXXXXXXXXXXXX
Hi Apartment | Light.Int | 0.090939 | XXX |  | Sm Hotel | Light.Int | 35.38% | XXXXXXXXXXXX
Strip Mall | Light.Ext | 0.090451 | XXX |  | Sm Office | Light.Int | 35.63% | XXXXXXXXXXXX
Md Office | Heat | 0.089351 | XXX |  | Warehouse | Light.Int | 35.97% | XXXXXXXXXXXX
Md Office | Elevator | 0.088409 | XXX |  | Md Office | Cool | 36.1% | XXXXXXXXXXXX
Hospital | Humidfy | 0.082409 | XXX |  | Warehouse | Heat | 36.39% | XXXXXXXXXXXX
Strip Mall | SHW | 0.079876 | XXX |  | Lg Hotel | Cool | 36.5% | XXXXXXXXXXXX
Clinic | Light.Ext | 0.077889 | XXX |  | Mid Apartment | Cool | 36.83% | XXXXXXXXXXXX
Clinic | Humidfy | 0.076218 | XXX |  | Clinic | Fans | 36.9% | XXXXXXXXXXXX
Warehouse | Equip | 0.075185 | XXX |  | Lg Hotel | Light.Int | 36.96% | XXXXXXXXXXXX
Sec School | Cook | 0.07308 | XX |  | Restaurant | Cool | 37.08% | XXXXXXXXXXXX
Retail Store | Light.Ext | 0.071256 | XX |  | Pri School | Fans | 37.13% | XXXXXXXXXXXX
Hi Apartment | Heat | 0.065059 | XX |  | Pri School | Ht.Rcvy | 37.71% | XXXXXXXXXXXX
Hospital | Pumps | 0.064223 | XX |  | Mid Apartment | Heat | 38.5% | XXXXXXXXXXXX
Sm Office | Light.Ext | 0.064081 | XX |  | Hospital | Cool | 38.82% | XXXXXXXXXXXX
Warehouse | Heat | 0.059903 | XX |  | Strip Mall | Heat | 39.26% | XXXXXXXXXXXX
Hospital | Ht.Rej | 0.058139 | XX |  | Hospital | Txfmr | 40.59% | XXXXXXXXXXX
Md Office | Light.Ext | 0.056061 | XX |  | Md Office | Light.Int | 40.63% | XXXXXXXXXXX
Hi Apartment | Light.Ext | 0.055358 | XX |  | Pri School | Light.Int | 41.58% | XXXXXXXXXXX
Lg Hotel | Light.Ext | 0.055156 | XX |  | Pri School | Heat | 41.99% | XXXXXXXXXXX
Hi Apartment | Elevator | 0.053835 | XX |  | Lg Office | Heat | 42.16% | XXXXXXXXXXX
Mid Apartment | Heat | 0.048911 | X |  | Hi Apartment | Txfmr | 42.49% | XXXXXXXXXXX
Hospital | SHW | 0.048881 | X |  | Hi Apartment | Heat | 42.89% | XXXXXXXXXXX
Lg Office | Heat | 0.048275 | X |  | Restaurant | Light.Ext | 42.97% | XXXXXXXXXXX
Pri School | Refrig | 0.047498 | X |  | Sm Office | Heat | 43.3% | XXXXXXXXXXX
Retail Store | Heat | 0.045903 | X |  | Fast Food | Light.Ext | 43.64% | XXXXXXXXXXX
Warehouse | Light.Ext | 0.045491 | X |  | Sec School | Light.Int | 43.74% | XXXXXXXXXXX
Md Office | Fans | 0.044594 | X |  | Lg Hotel | Fans | 43.98% | XXXXXXXXXXX
Sm Hotel | Light.Ext | 0.043656 | X |  | Lg Office | Txfmr | 44.49% | XXXXXXXXXXX
Lg Hotel | Ht.Rcvy | 0.043581 | X |  | Mid Apartment | Light.Ext | 45% | XXXXXXXXXX
Sec School | SHW | 0.042364 | X |  | Sm Hotel | Heat | 45.53% | XXXXXXXXXX
Lg Office | Light.Ext | 0.039191 | X |  | Lg Hotel | Txfmr | 45.6% | XXXXXXXXXX
Lg Office | Humidfy | 0.036809 | X |  | Pri School | Cool | 45.62% | XXXXXXXXXX
Retail Store | SHW | 0.035386 | X |  | Pri School | Light.Ext | 46.03% | XXXXXXXXXX
Sec School | Heat | 0.035029 | X |  | Warehouse | Cool | 46.27% | XXXXXXXXXX
Mid Apartment | Light.Ext | 0.03408 | X |  | Retail Store | Light.Ext | 46.66% | XXXXXXXXXX
Pri School | Ht.Rcvy | 0.032338 | X |  | Hospital | Heat | 47.04% | XXXXXXXXXX
Sec School | Ht.Rcvy | 0.031537 | X |  | Sec School | Light.Ext | 47.71% | XXXXXXXXXX
Lg Office | Pumps | 0.030507 | X |  | Strip Mall | Fans | 47.73% | XXXXXXXXXX
Sm Office | Heat | 0.028798 | X |  | Fast Food | Fans | 48.41% | XXXXXXXXXX
Clinic | SHW | 0.028459 | X |  | Sec School | Txfmr | 48.46% | XXXXXXXXXX
Hospital | Ht.Rcvy | 0.028414 | X |  | Strip Mall | Cool | 49.29% | XXXXXXXXXX
Sec School | Refrig | 0.026107 | X |  | Md Office | Txfmr | 49.48% | XXXXXXXXXX
Hospital | Refrig | 0.024782 |  |  | Pri School | Txfmr | 49.61% | XXXXXXXXXX
Pri School | SHW | 0.024515 |  |  | Clinic | Humidfy | 50.13% | XXXXXXXXX
Hospital | Light.Ext | 0.024405 |  |  | Sm Office | Cool | 50.18% | XXXXXXXXX
Lg Office | Ht.Rej | 0.022698 |  |  | Retail Store | Cool | 50.39% | XXXXXXXXX
Lg Hotel | Refrig | 0.019929 |  |  | Warehouse | Fans | 50.58% | XXXXXXXXX
Warehouse | Fans | 0.018947 |  |  | Strip Mall | Light.Ext | 50.65% | XXXXXXXXX
Retail Store | Ht.Rcvy | 0.018183 |  |  | Hospital | Pumps | 50.73% | XXXXXXXXX
Pri School | Light.Ext | 0.017771 |  |  | Clinic | Light.Ext | 50.97% | XXXXXXXXX
Lg Hotel | Pumps | 0.017044 |  |  | Sec School | Cool | 51.75% | XXXXXXXXX
Hi Apartment | Pumps | 0.016733 |  |  | Md Office | Heat | 51.96% | XXXXXXXXX
Sec School | Light.Ext | 0.015699 |  |  | Sm Office | Light.Ext | 52.1% | XXXXXXXXX
Warehouse | SHW | 0.013738 |  |  | Md Office | Light.Ext | 53.59% | XXXXXXXXX
Md Office | SHW | 0.01291 |  |  | Retail Store | Fans | 54.39% | XXXXXXXXX
Clinic | Ht.Rcvy | 0.012804 |  |  | Lg Office | Ht.Rej | 54.85% | XXXXXXXXX
Hospital | Txfmr | 0.012241 |  |  | Sec School | Fans | 55.38% | XXXXXXXX
Warehouse | Cool | 0.011858 |  |  | Lg Office | Pumps | 56.71% | XXXXXXXX
Clinic | Pumps | 0.011024 |  |  | Fast Food | Light.Int | 56.9% | XXXXXXXX
Lg Office | SHW | 0.0097886 |  |  | Sec School | Ht.Rcvy | 57.37% | XXXXXXXX
Hi Apartment | Ht.Rej | 0.0094479 |  |  | Clinic | Heat | 58.6% | XXXXXXXX
Pri School | Txfmr | 0.0093797 |  |  | Lg Hotel | Ht.Rcvy | 59.83% | XXXXXXXX
Md Office | Txfmr | 0.0091151 |  |  | Lg Hotel | Heat | 59.98% | XXXXXXXX
Sec School | Elevator | 0.0089444 |  |  | Hospital | Humidfy | 61.13% | XXXXXXX
Lg Hotel | Txfmr | 0.007309 |  |  | Restaurant | Light.Int | 61.56% | XXXXXXX
Hi Apartment | Txfmr | 0.0070705 |  |  | Restaurant | Fans | 62.26% | XXXXXXX
Sec School | Pumps | 0.0066751 |  |  | Sec School | Heat | 69.61% | XXXXXX
Lg Office | Ht.Rcvy | 0.0057228 |  |  | Lg Hotel | Pumps | 70.06% | XXXXX
Sec School | Txfmr | 0.0055594 |  |  | Retail Store | Heat | 73.65% | XXXXX
Lg Office | Txfmr | 0.0045904 |  |  | Sec School | Pumps | 77.88% | XXXX
Restaurant | Pumps | 0.0023446 |  |  | Md Office | Ht.Rcvy | -100% | New Use not required in 2004
Pri School | Pumps | 0.00047268 |  |  | Lg Office | Ht.Rcvy | -100% | New Use not required in 2004
Sm Hotel | Pumps | 0.00017252 |  |  | Retail Store | Ht.Rcvy | -100% | New Use not required in 2004
Md Office | Ht.Rcvy | 8.9871e-05 |  |  | Clinic | Ht.Rcvy | -100% | New Use not required in 2004
Md Office | Pumps | 8.0182e-05 |  |  | Hospital | Ht.Rcvy | -100% | New Use not required in 2004
#REF!
#REF!

## HiApartment
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | High-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | High-rise Apartment | [14 empty] | Prototype Floor Area: | 84352 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.090939 | 0.055358 | 0.11322 | 0.065059 | 0 | 0.18726 | 0.0094479 | 0.18591 | 0 | 0.016733 | 0 | 0.053835 | 0.0070705 | 0 | 0 | 0.33045 | 1.1153 |  | STD2013 | 3.0075 | 1.8308 | 11.4365 | 4.4858 | 0 | 6.1929 | 0.31245 | 6.1485 | 0 | 0.55339 | 0 | 1.7804 | 0.23383 | 0 | 0 | 10.9284 | 46.9104 |  | STD2013 | 0.88119 | 0.53641 | 0 | 0.29749 | 0 | 1.8145 | 0.091548 | 1.8015 | 0 | 0.16214 | 0 | 0.52166 | 0.068512 | 0 | 0 | 3.202 | 9.3769 |  | STD2013 | 0 | 0 | 0.11437 | 0.034705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14907 |  | STD2013 | 9.2251 | 5.6157 | 12.5001 | 6.9077 | 0 | 18.9959 | 0.95842 | 18.8597 | 0 | 1.6975 | 0 | 5.4612 | 0.71725 | 0 | 0 | 33.5216 | 114.4603
STD2010 | 0.11518 | 0.055358 | 0.11322 | 0.068857 | 0 | 0.24066 | 0.011366 | 0.20416 | 0 | 0.018163 | 0 | 0.053947 | 0.0070729 | 0 | 0 | 0.33045 | 1.2184 |  | STD2010 | 3.8093 | 1.8308 | 11.4362 | 4.6955 | 0 | 7.9588 | 0.3759 | 6.7519 | 0 | 0.60069 | 0 | 1.7841 | 0.23391 | 0 | 0 | 10.9284 | 50.4055 |  | STD2010 | 1.1161 | 0.53641 | 0 | 0.3223 | 0 | 2.3319 | 0.11014 | 1.9783 | 0 | 0.176 | 0 | 0.52274 | 0.068535 | 0 | 0 | 3.202 | 10.3645 |  | STD2010 | 0 | 0 | 0.11436 | 0.035955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15032 |  | STD2010 | 11.6846 | 5.6157 | 12.4997 | 7.3041 | 0 | 24.4129 | 1.153 | 20.7108 | 0 | 1.8426 | 0 | 5.4726 | 0.7175 | 0 | 0 | 33.5216 | 124.9351
STD2007 | 0.095867 | 0.072536 | 0.11332 | 0.10199 | 0 | 0.24214 | 0.011714 | 0.2197 | 0 | 0.024042 | 0 | 0.055405 | 0.012293 | 0 | 0 | 0.33111 | 1.2801 |  | STD2007 | 3.1705 | 2.3989 | 11.4461 | 7.0894 | 0 | 8.0079 | 0.38739 | 7.2657 | 0 | 0.79511 | 0 | 1.8323 | 0.40656 | 0 | 0 | 10.9502 | 53.75 |  | STD2007 | 0.92894 | 0.70287 | 0 | 0.45814 | 0 | 2.3463 | 0.1135 | 2.1288 | 0 | 0.23296 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 10.7759 |  | STD2007 | 0 | 0 | 0.11446 | 0.055258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16972 |  | STD2007 | 9.725 | 7.3583 | 12.5106 | 10.8359 | 0 | 24.5634 | 1.1883 | 22.2867 | 0 | 2.4389 | 0 | 5.6205 | 1.2471 | 0 | 0 | 33.5885 | 131.3631
STD2004 | 0.095867 | 0.072536 | 0.11332 | 0.11392 | 0 | 0.24883 | 0.01211 | 0.23296 | 0 | 0.025253 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.3136 |  | STD2004 | 3.1705 | 2.3989 | 11.446 | 7.9185 | 0 | 8.2291 | 0.40048 | 7.7043 | 0 | 0.83514 | 0 | 1.8323 | 0.40657 | 0 | 0 | 10.9502 | 55.2921 |  | STD2004 | 0.92894 | 0.70287 | 0 | 0.51187 | 0 | 2.4111 | 0.11734 | 2.2574 | 0 | 0.24469 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 11.0385 |  | STD2004 | 0 | 0 | 0.11446 | 0.061715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17618 |  | STD2004 | 9.725 | 7.3583 | 12.5105 | 12.1043 | 0 | 25.242 | 1.2284 | 23.6322 | 0 | 2.5617 | 0 | 5.6205 | 1.2471 | 0 | 0 | 33.5885 | 134.8185
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | -1.1904e-06 | 0.011939 | 0 | 0.0066895 | 0.00039589 | 0.013264 | 0 | 0.0012106 | 0 | 0 | 1.5741e-07 | 0 | 0 | 0 | 0.033498 |  | 2004-2007 | 0 | 0 | -0.00012025 | 0.82915 | 0 | 0.22123 | 0.013092 | 0.43866 | 0 | 0.040036 | 0 | 0 | 5.206e-06 | 0 | 0 | 0 | 1.5421 |  | 2004-2007 | 0 | 0 | 0 | 0.053735 | 0 | 0.064821 | 0.0038361 | 0.12853 | 0 | 0.01173 | 0 | 0 | 1.5253e-06 | 0 | 0 | 0 | 0.26265 |  | 2004-2007 | 0 | 0 | -1.2025e-06 | 0.0064575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064563 |  | 2004-2007 | 0 | 0 | -0.00013143 | 1.2684 | 0 | 0.67861 | 0.04016 | 1.3455 | 0 | 0.1228 | 0 | 0 | 1.5969e-05 | 0 | 0 | 0 | 3.4554
2007-2010 | -0.019317 | 0.017178 | 9.8481e-05 | 0.033128 | 0 | 0.0014834 | 0.00034727 | 0.015535 | 0 | 0.0058786 | 0 | 0.0014579 | 0.0052205 | 0 | 0 | 0.0006593 | 0.061669 |  | 2007-2010 | -0.63883 | 0.5681 | 0.0099475 | 2.3939 | 0 | 0.049057 | 0.011485 | 0.51377 | 0 | 0.19441 | 0 | 0.048217 | 0.17265 | 0 | 0 | 0.021804 | 3.3445 |  | 2007-2010 | -0.18718 | 0.16645 | 0 | 0.13583 | 0 | 0.014374 | 0.003365 | 0.15053 | 0 | 0.056962 | 0 | 0.014127 | 0.050586 | 0 | 0 | 0.0063884 | 0.41144 |  | 2007-2010 | 0 | 0 | 9.9475e-05 | 0.019303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019402 |  | 2007-2010 | -1.9596 | 1.7426 | 0.010873 | 3.5318 | 0 | 0.15048 | 0.035228 | 1.5759 | 0 | 0.59634 | 0 | 0.1479 | 0.52959 | 0 | 0 | 0.06688 | 6.4281
2010-2013 | 0.024245 | 0 | -3.6614e-06 | 0.0037983 | 0 | 0.053399 | 0.0019186 | 0.018247 | 0 | 0.0014302 | 0 | 0.00011215 | 2.4084e-06 | 0 | 0 | 0 | 0.10315 |  | 2010-2013 | 0.8018 | 0 | -0.00036983 | 0.2097 | 0 | 1.766 | 0.06345 | 0.60346 | 0 | 0.0473 | 0 | 0.003709 | 7.9648e-05 | 0 | 0 | -2.7662e-08 | 3.4951 |  | 2010-2013 | 0.23493 | 0 | 0 | 0.024812 | 0 | 0.51743 | 0.018591 | 0.17681 | 0 | 0.013859 | 0 | 0.0010867 | 2.3337e-05 | 0 | 0 | -8.1049e-09 | 0.98754 |  | 2010-2013 | 0 | 0 | -3.6983e-06 | 0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012464 |  | 2010-2013 | 2.4594 | 0 | -0.00040423 | 0.3964 | 0 | 5.417 | 0.19463 | 1.8511 | 0 | 0.14509 | 0 | 0.011377 | 0.00024431 | 0 | 0 | -8.485e-08 | 10.4748
2004-2013 | 0.0049278 | 0.017178 | 9.3629e-05 | 0.048865 | 0 | 0.061572 | 0.0026617 | 0.047046 | 0 | 0.0085194 | 0 | 0.0015701 | 0.0052231 | 0 | 0 | 0.0006593 | 0.19832 |  | 2004-2013 | 0.16297 | 0.5681 | 0.0094574 | 3.4327 | 0 | 2.0363 | 0.088028 | 1.5559 | 0 | 0.28175 | 0 | 0.051925 | 0.17274 | 0 | 0 | 0.021804 | 8.3817 |  | 2004-2013 | 0.047749 | 0.16645 | 0 | 0.21438 | 0 | 0.59662 | 0.025792 | 0.45587 | 0 | 0.082552 | 0 | 0.015214 | 0.050611 | 0 | 0 | 0.0063884 | 1.6616 |  | 2004-2013 | 0 | 0 | 9.4574e-05 | 0.027011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027105 |  | 2004-2013 | 0.49989 | 1.7426 | 0.010337 | 5.1966 | 0 | 6.246 | 0.27001 | 4.7725 | 0 | 0.86423 | 0 | 0.15928 | 0.52985 | 0 | 0 | 0.06688 | 20.3582
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | -0.001051% | 10.48% |  | 2.688% | 3.269% | 5.694% |  | 4.794% |  | 0% | 0.00128% |  |  | 0% | 2.55% |  | 2004-2007 | 0% | 0% | -0.001051% | 10.47% |  | 2.688% | 3.269% | 5.694% |  | 4.794% |  | 0% | 0.00128% |  |  | 0% | 2.789% |  | 2004-2007 | 0% | 0% |  | 10.5% |  | 2.688% | 3.269% | 5.694% |  | 4.794% |  | 0% | 0.00128% |  |  | 0% | 2.379% |  | 2004-2007 |  |  | -0.001051% | 10.46% | [12 empty] | 3.665% |  | 2004-2007 | 0% | 0% | -0.001051% | 10.48% |  | 2.688% | 3.269% | 5.694% |  | 4.794% |  | 0% | 0.00128% |  |  | 0% | 2.563%
2007-2010 | -20.15% | 23.68% | 0.08691% | 32.48% |  | 0.6126% | 2.965% | 7.071% |  | 24.45% |  | 2.631% | 42.47% |  |  | 0.1991% | 4.818% |  | 2007-2010 | -20.15% | 23.68% | 0.08691% | 33.77% |  | 0.6126% | 2.965% | 7.071% |  | 24.45% |  | 2.631% | 42.47% |  |  | 0.1991% | 6.222% |  | 2007-2010 | -20.15% | 23.68% |  | 29.65% |  | 0.6126% | 2.965% | 7.071% |  | 24.45% |  | 2.631% | 42.47% |  |  | 0.1991% | 3.818% |  | 2007-2010 |  |  | 0.08691% | 34.93% | [12 empty] | 11.43% |  | 2007-2010 | -20.15% | 23.68% | 0.08691% | 32.59% |  | 0.6126% | 2.965% | 7.071% |  | 24.45% |  | 2.631% | 42.47% |  |  | 0.1991% | 4.893%
2010-2013 | 21.05% | 0% | -0.003234% | 5.516% |  | 22.19% | 16.88% | 8.938% |  | 7.874% |  | 0.2079% | 0.03405% |  |  | 0% | 8.466% |  | 2010-2013 | 21.05% | 0% | -0.003234% | 4.466% |  | 22.19% | 16.88% | 8.938% |  | 7.874% |  | 0.2079% | 0.03405% |  |  | -2.531e-07% | 6.934% |  | 2010-2013 | 21.05% | 0% |  | 7.698% |  | 22.19% | 16.88% | 8.938% |  | 7.874% |  | 0.2079% | 0.03405% |  |  | -2.531e-07% | 9.528% |  | 2010-2013 |  |  | -0.003234% | 3.477% | [12 empty] | 0.8292% |  | 2010-2013 | 21.05% | 0% | -0.003234% | 5.427% |  | 22.19% | 16.88% | 8.938% |  | 7.874% |  | 0.2079% | 0.03405% |  |  | -2.531e-07% | 8.384%
2004-2013 | 5.14% | 23.68% | 0.08263% | 42.89% |  | 24.74% | 21.98% | 20.19% |  | 33.74% |  | 2.834% | 42.49% |  |  | 0.1991% | 15.1% |  | 2004-2013 | 5.14% | 23.68% | 0.08263% | 43.35% |  | 24.74% | 21.98% | 20.19% |  | 33.74% |  | 2.834% | 42.49% |  |  | 0.1991% | 15.16% |  | 2004-2013 | 5.14% | 23.68% |  | 41.88% |  | 24.74% | 21.98% | 20.19% |  | 33.74% |  | 2.834% | 42.49% |  |  | 0.1991% | 15.05% |  | 2004-2013 |  |  | 0.08263% | 43.77% | [12 empty] | 15.39% |  | 2004-2013 | 5.14% | 23.68% | 0.08263% | 42.93% |  | 24.74% | 21.98% | 20.19% |  | 33.74% |  | 2.834% | 42.49% |  |  | 0.1991% | 15.1%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.090939 | 0.055442 | 0.090241 | 0.00019433 | 0 | 0.36155 | 0.019381 | 0.17183 | 0 | 0.017577 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.1985 | 16.97% | CZ 1A | 3.0075 | 1.8336 | 9.1152 | 0.0083163 | 0 | 11.9569 | 0.64097 | 5.6828 | 0 | 0.58129 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 45.7692 | 16.97% | CZ 1A | 0.88119 | 0.53723 | 0 | 0.0016136 | 0 | 3.5033 | 0.1878 | 1.665 | 0 | 0.17032 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 10.7387 | 16.97% | CZ 1A | 0 | 0 | 0.091152 | 2.8091e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09118 | 16.97% | CZ 1A | 9.2251 | 5.6242 | 9.963 | 0.019963 | 0 | 36.6765 | 1.9661 | 17.4312 | 0 | 1.783 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 122.3893 | 16.97%
CZ 1B | 0.090939 | 0.055395 | 0.085047 | 0.00052411 | 0 | 0.33155 | 0.012551 | 0.25291 | 0 | 0.017193 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.2375 | 0% | CZ 1B | 3.0075 | 1.832 | 8.5906 | 0.018769 | 0 | 10.9647 | 0.41506 | 8.3642 | 0 | 0.56859 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 46.7041 | 0% | CZ 1B | 0.88119 | 0.53677 | 0 | 0.0048737 | 0 | 3.2126 | 0.12161 | 2.4507 | 0 | 0.1666 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 11.1665 | 0% | CZ 1B | 0 | 0 | 0.085906 | 2.1349e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085927 | 0% | CZ 1B | 9.2251 | 5.6194 | 9.3895 | 0.053356 | 0 | 33.6331 | 1.2732 | 25.6562 | 0 | 1.7441 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 126.2942 | 0%
CZ 2A | 0.090939 | 0.055347 | 0.10217 | 0.020533 | 0 | 0.23275 | 0.012204 | 0.17253 | 0 | 0.015871 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.0937 | 16.86% | CZ 2A | 3.0075 | 1.8304 | 10.3205 | 1.3634 | 0 | 7.6974 | 0.4036 | 5.7057 | 0 | 0.52487 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 43.7959 | 16.86% | CZ 2A | 0.88119 | 0.53631 | 0 | 0.10136 | 0 | 2.2553 | 0.11825 | 1.6717 | 0 | 0.15379 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.5101 | 16.86% | CZ 2A | 0 | 0 | 0.1032 | 0.010175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11338 | 16.86% | CZ 2A | 9.2251 | 5.6146 | 11.2803 | 2.1732 | 0 | 23.6108 | 1.238 | 17.5015 | 0 | 1.61 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 111.9537 | 16.86%
CZ 2B | 0.090939 | 0.05531 | 0.095222 | 0.0018517 | 0 | 0.28233 | 0.011952 | 0.22829 | 0 | 0.017431 | 0 | 0.053835 | 0.0070676 | 0 | 0 | 0.33045 | 1.1747 | 0.8505% | CZ 2B | 3.0075 | 1.8292 | 9.6184 | 0.083836 | 0 | 9.3371 | 0.39528 | 7.5499 | 0 | 0.57646 | 0 | 1.7804 | 0.23373 | 0 | 0 | 10.9284 | 45.3402 | 0.8505% | CZ 2B | 0.88119 | 0.53594 | 0 | 0.01472 | 0 | 2.7357 | 0.11582 | 2.2121 | 0 | 0.1689 | 0 | 0.52166 | 0.068484 | 0 | 0 | 3.202 | 10.4565 | 0.8505% | CZ 2B | 0 | 0 | 0.096184 | 0.00033597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09652 | 0.8505% | CZ 2B | 9.2251 | 5.6108 | 10.5129 | 0.19082 | 0 | 28.6404 | 1.2125 | 23.1585 | 0 | 1.7682 | 0 | 5.4612 | 0.71695 | 0 | 0 | 33.5216 | 120.0191 | 0.8505%
CZ 3A | 0.090939 | 0.055378 | 0.11153 | 0.079874 | 0 | 0.17298 | 0.0088292 | 0.17213 | 0 | 0.016302 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.0993 | 7.27% | CZ 3A | 3.0075 | 1.8314 | 11.2657 | 5.5329 | 0 | 5.7209 | 0.29199 | 5.6924 | 0 | 0.53914 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 46.8245 | 7.27% | CZ 3A | 0.88119 | 0.5366 | 0 | 0.36158 | 0 | 1.6762 | 0.085553 | 1.6679 | 0 | 0.15797 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.1591 | 7.27% | CZ 3A | 0 | 0 | 0.11266 | 0.042988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15565 | 7.27% | CZ 3A | 9.2251 | 5.6177 | 12.3134 | 8.484 | 0 | 17.5481 | 0.89566 | 17.4609 | 0 | 1.6538 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 112.8987 | 7.27%
CZ 3B | 0.090939 | 0.055385 | 0.10845 | 0.015664 | 0 | 0.16124 | 0.0065318 | 0.19851 | 0 | 0.013543 | 0 | 0.053835 | 0.0070744 | 0 | 0 | 0.33045 | 1.0416 | 8.26% | CZ 3B | 3.0075 | 1.8316 | 10.9541 | 0.96158 | 0 | 5.3323 | 0.21602 | 6.5649 | 0 | 0.44788 | 0 | 1.7804 | 0.23396 | 0 | 0 | 10.9284 | 42.2587 | 8.26% | CZ 3B | 0.88119 | 0.53667 | 0 | 0.088517 | 0 | 1.5624 | 0.063292 | 1.9235 | 0 | 0.13123 | 0 | 0.52166 | 0.068549 | 0 | 0 | 3.202 | 8.9789 | 8.26% | CZ 3B | 0 | 0 | 0.10954 | 0.0065947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11614 | 8.26% | CZ 3B | 9.2251 | 5.6184 | 11.9728 | 1.6475 | 0 | 16.3563 | 0.66261 | 20.1372 | 0 | 1.3738 | 0 | 5.4612 | 0.71764 | 0 | 0 | 33.5216 | 106.6942 | 8.26%
CZ 3C | 0.090939 | 0.055303 | 0.12168 | 0.017737 | 0 | 0.0070654 | 0.00030586 | 0.13419 | 0 | 0.0086491 | 0 | 0.053835 | 0.0070642 | 0 | 0 | 0.33045 | 0.82721 | 1.931% | CZ 3C | 3.0075 | 1.829 | 12.2904 | 1.0953 | 0 | 0.23366 | 0.010115 | 4.4378 | 0 | 0.28604 | 0 | 1.7804 | 0.23362 | 0 | 0 | 10.9284 | 36.1322 | 1.931% | CZ 3C | 0.88119 | 0.53588 | 0 | 0.099318 | 0 | 0.068462 | 0.0029637 | 1.3003 | 0 | 0.083808 | 0 | 0.52166 | 0.068451 | 0 | 0 | 3.202 | 6.764 | 1.931% | CZ 3C | 0 | 0 | 0.1229 | 0.0075633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13047 | 1.931% | CZ 3C | 9.2251 | 5.6101 | 13.4334 | 1.8664 | 0 | 0.71673 | 0.031027 | 13.6124 | 0 | 0.87739 | 0 | 5.4612 | 0.71661 | 0 | 0 | 33.5216 | 85.0722 | 1.931%
CZ 4A | 0.090939 | 0.055354 | 0.12302 | 0.089315 | 0 | 0.13901 | 0.0068173 | 0.19465 | 0 | 0.017913 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.1084 | 27.95% | CZ 4A | 3.0075 | 1.8306 | 12.4258 | 6.144 | 0 | 4.5973 | 0.22546 | 6.4374 | 0 | 0.59242 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 48.2031 | 27.95% | CZ 4A | 0.88119 | 0.53637 | 0 | 0.41045 | 0 | 1.347 | 0.066059 | 1.8861 | 0 | 0.17358 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.0929 | 27.95% | CZ 4A | 0 | 0 | 0.12426 | 0.047431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17169 | 27.95% | CZ 4A | 9.2251 | 5.6153 | 13.5814 | 9.4812 | 0 | 14.1016 | 0.69157 | 19.7459 | 0 | 1.8172 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 113.9594 | 27.95%
CZ 4B | 0.090939 | 0.05534 | 0.12128 | 0.021784 | 0 | 0.15089 | 0.0057468 | 0.22703 | 0 | 0.014114 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.0785 | 0% | CZ 4B | 3.0075 | 1.8302 | 12.2505 | 1.3572 | 0 | 4.9903 | 0.19005 | 7.5083 | 0 | 0.46676 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 44.5436 | 0% | CZ 4B | 0.88119 | 0.53624 | 0 | 0.12026 | 0 | 1.4621 | 0.055685 | 2.1999 | 0 | 0.13676 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.1844 | 0% | CZ 4B | 0 | 0 | 0.12251 | 0.0094678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13197 | 0% | CZ 4B | 9.2251 | 5.6139 | 13.3898 | 2.2939 | 0 | 15.3072 | 0.58297 | 23.031 | 0 | 1.4317 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 110.5758 | 0%
CZ 4C | 0.090939 | 0.055323 | 0.12787 | 0.059012 | 0 | 0.072764 | 0.0031945 | 0.20567 | 0 | 0.01565 | 0 | 0.053835 | 0.0070676 | 0 | 0 | 0.33045 | 1.0218 | 3.991% | CZ 4C | 3.0075 | 1.8296 | 12.9161 | 3.9867 | 0 | 2.4064 | 0.10565 | 6.8019 | 0 | 0.51756 | 0 | 1.7804 | 0.23373 | 0 | 0 | 10.9284 | 44.514 | 3.991% | CZ 4C | 0.88119 | 0.53608 | 0 | 0.28156 | 0 | 0.70507 | 0.030955 | 1.993 | 0 | 0.15164 | 0 | 0.52166 | 0.068484 | 0 | 0 | 3.202 | 8.3716 | 3.991% | CZ 4C | 0 | 0 | 0.12916 | 0.030258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15942 | 3.991% | CZ 4C | 9.2251 | 5.6122 | 14.1173 | 6.2548 | 0 | 7.3814 | 0.32406 | 20.8642 | 0 | 1.5876 | 0 | 5.4612 | 0.71695 | 0 | 0 | 33.5216 | 105.0665 | 3.991%
CZ 5A | 0.090939 | 0.055286 | 0.13103 | 0.17452 | 0 | 0.10775 | 0.0052098 | 0.19658 | 0 | 0.018168 | 0 | 0.053835 | 0.0070676 | 0 | 0 | 0.33045 | 1.1708 | 12.97% | CZ 5A | 3.0075 | 1.8284 | 13.2353 | 12.215 | 0 | 3.5635 | 0.1723 | 6.5013 | 0 | 0.60085 | 0 | 1.7804 | 0.23373 | 0 | 0 | 10.9284 | 54.0667 | 12.97% | CZ 5A | 0.88119 | 0.53571 | 0 | 0.77212 | 0 | 1.0441 | 0.050482 | 1.9049 | 0 | 0.17605 | 0 | 0.52166 | 0.068484 | 0 | 0 | 3.202 | 9.1566 | 12.97% | CZ 5A | 0 | 0 | 0.13235 | 0.095797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22815 | 12.97% | CZ 5A | 9.2251 | 5.6084 | 14.4662 | 18.554 | 0 | 10.9306 | 0.5285 | 19.942 | 0 | 1.843 | 0 | 5.4612 | 0.71695 | 0 | 0 | 33.5216 | 120.7977 | 12.97%
CZ 5B | 0.090939 | 0.055262 | 0.1296 | 0.068682 | 0 | 0.1083 | 0.0041189 | 0.22747 | 0 | 0.015701 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.0914 | 1.287% | CZ 5B | 3.0075 | 1.8276 | 13.0909 | 4.6585 | 0 | 3.5815 | 0.13622 | 7.5226 | 0 | 0.51925 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 47.2867 | 1.287% | CZ 5B | 0.88119 | 0.53548 | 0 | 0.32506 | 0 | 1.0494 | 0.039912 | 2.2041 | 0 | 0.15214 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 8.9794 | 1.287% | CZ 5B | 0 | 0 | 0.13091 | 0.03549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1664 | 1.287% | CZ 5B | 9.2251 | 5.606 | 14.3084 | 7.2821 | 0 | 10.9858 | 0.41784 | 23.0748 | 0 | 1.5927 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 112.1929 | 1.287%
CZ 5C | 0.090939 | 0.055228 | 0.13112 | 0.094543 | 0 | 0.038566 | 0.0017162 | 0.17999 | 0 | 0.013981 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 0.99744 | 0% | CZ 5C | 3.0075 | 1.8265 | 13.2449 | 6.5164 | 0 | 1.2754 | 0.056758 | 5.9524 | 0 | 0.46238 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 45.2848 | 0% | CZ 5C | 0.88119 | 0.53515 | 0 | 0.43264 | 0 | 0.3737 | 0.01663 | 1.744 | 0 | 0.13548 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 7.911 | 0% | CZ 5C | 0 | 0 | 0.13245 | 0.050398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18285 | 0% | CZ 5C | 9.2251 | 5.6025 | 14.4766 | 10.0378 | 0 | 3.9122 | 0.1741 | 18.2583 | 0 | 1.4183 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 102.8051 | 0%
CZ 6A | 0.090939 | 0.05529 | 0.13815 | 0.20221 | 0 | 0.066661 | 0.0031368 | 0.18663 | 0 | 0.016105 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.1505 | 1.39% | CZ 6A | 3.0075 | 1.8285 | 13.9542 | 14.2737 | 0 | 2.2046 | 0.10374 | 6.1721 | 0 | 0.53262 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 55.0196 | 1.39% | CZ 6A | 0.88119 | 0.53575 | 0 | 0.87743 | 0 | 0.64593 | 0.030395 | 1.8084 | 0 | 0.15606 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 8.7273 | 1.39% | CZ 6A | 0 | 0 | 0.13954 | 0.11279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25233 | 1.39% | CZ 6A | 9.2251 | 5.6087 | 15.252 | 21.5138 | 0 | 6.7623 | 0.3182 | 18.9323 | 0 | 1.6338 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 118.9463 | 1.39%
CZ 6B | 0.090939 | 0.055249 | 0.13918 | 0.11204 | 0 | 0.074358 | 0.0028785 | 0.22625 | 0 | 0.014668 | 0 | 0.053835 | 0.0070642 | 0 | 0 | 0.33045 | 1.1069 | 0.179% | CZ 6B | 3.0075 | 1.8272 | 14.0588 | 7.7592 | 0 | 2.4591 | 0.095196 | 7.4824 | 0 | 0.48508 | 0 | 1.7804 | 0.23362 | 0 | 0 | 10.9284 | 50.1169 | 0.179% | CZ 6B | 0.88119 | 0.53535 | 0 | 0.50739 | 0 | 0.72052 | 0.027892 | 2.1923 | 0 | 0.14213 | 0 | 0.52166 | 0.068451 | 0 | 0 | 3.202 | 8.7989 | 0.179% | CZ 6B | 0 | 0 | 0.14059 | 0.060275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20086 | 0.179% | CZ 6B | 9.2251 | 5.6046 | 15.3663 | 11.8999 | 0 | 7.5431 | 0.292 | 22.9513 | 0 | 1.4879 | 0 | 5.4612 | 0.71661 | 0 | 0 | 33.5216 | 114.0698 | 0.179%
CZ 7 | 0.090939 | 0.055252 | 0.14941 | 0.26973 | 0 | 0.056146 | 0.0025556 | 0.20371 | 0 | 0.017094 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.2362 | 0.09387% | CZ 7 | 3.0075 | 1.8273 | 15.0918 | 19.1084 | 0 | 1.8568 | 0.084519 | 6.7371 | 0 | 0.56533 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 61.2214 | 0.09387% | CZ 7 | 0.88119 | 0.53538 | 0 | 1.1606 | 0 | 0.54404 | 0.024764 | 1.974 | 0 | 0.16564 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.0777 | 0.09387% | CZ 7 | 0 | 0 | 0.15092 | 0.15147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30239 | 0.09387% | CZ 7 | 9.2251 | 5.6049 | 16.4953 | 28.7063 | 0 | 5.6956 | 0.25925 | 20.6653 | 0 | 1.7341 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 128.0862 | 0.09387%
CZ 8 | 0.090939 | 0.054912 | 0.16329 | 0.37255 | 0 | 0.052425 | 0.0021376 | 0.23313 | 0 | 0.016132 | 0 | 0.053835 | 0.007071 | 0 | 0 | 0.33045 | 1.3769 | 0% | CZ 8 | 3.0075 | 1.816 | 16.4935 | 26.2561 | 0 | 1.7338 | 0.070694 | 7.7101 | 0 | 0.53352 | 0 | 1.7804 | 0.23385 | 0 | 0 | 10.9284 | 70.5639 | 0% | CZ 8 | 0.88119 | 0.53209 | 0 | 1.6224 | 0 | 0.50799 | 0.020713 | 2.259 | 0 | 0.15632 | 0 | 0.52166 | 0.068516 | 0 | 0 | 3.202 | 9.7719 | 0% | CZ 8 | 0 | 0 | 0.16494 | 0.20719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37212 | 0% | CZ 8 | 9.2251 | 5.5705 | 18.0274 | 39.6307 | 0 | 5.3181 | 0.21685 | 23.6498 | 0 | 1.6365 | 0 | 5.4612 | 0.7173 | 0 | 0 | 33.5216 | 142.9752 | 0%
Us Weighted | 0.090939 | 0.055358 | 0.11322 | 0.065059 | 0 | 0.18726 | 0.0094479 | 0.18591 | 0 | 0.016733 | 0 | 0.053835 | 0.0070705 | 0 | 0 | 0.33045 | 1.1153 | 100% | Us Weighted | 3.0075 | 1.8308 | 11.4365 | 4.4858 | 0 | 6.1929 | 0.31245 | 6.1485 | 0 | 0.55339 | 0 | 1.7804 | 0.23383 | 0 | 0 | 10.9284 | 46.9104 | 100% | Us Weighted | 0.88119 | 0.53641 | 0 | 0.29749 | 0 | 1.8145 | 0.091548 | 1.8015 | 0 | 0.16214 | 0 | 0.52166 | 0.068512 | 0 | 0 | 3.202 | 9.3769 | 100% | Us Weighted | 0 | 0 | 0.11437 | 0.034705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14907 | 100% | Us Weighted | 9.2251 | 5.6157 | 12.5001 | 6.9077 | 0 | 18.9959 | 0.95842 | 18.8597 | 0 | 1.6975 | 0 | 5.4612 | 0.71725 | 0 | 0 | 33.5216 | 114.4603 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.11518 | 0.055442 | 0.090235 | 0.00050552 | 0 | 0.47108 | 0.02367 | 0.2051 | 0 | 0.019993 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.3727 | 16.97% | CZ 1A | 3.8093 | 1.8336 | 9.1147 | 0.024049 | 0 | 15.5794 | 0.78281 | 6.783 | 0 | 0.6612 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 51.5344 | 16.97% | CZ 1A | 1.1161 | 0.53723 | 0 | 0.0038529 | 0 | 4.5647 | 0.22936 | 1.9874 | 0 | 0.19373 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 12.4257 | 16.97% | CZ 1A | 0 | 0 | 0.091147 | 0.00010899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091256 | 16.97% | CZ 1A | 11.6846 | 5.6242 | 9.9623 | 0.052249 | 0 | 47.7881 | 2.4012 | 20.806 | 0 | 2.0282 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 140.0587 | 16.97%
CZ 1B | 0.11518 | 0.055395 | 0.085044 | 0.0012902 | 0 | 0.42341 | 0.015313 | 0.30824 | 0 | 0.020887 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.4162 | 0% | CZ 1B | 3.8093 | 1.832 | 8.5903 | 0.05136 | 0 | 14.0028 | 0.50644 | 10.194 | 0 | 0.69076 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 52.6234 | 0% | CZ 1B | 1.1161 | 0.53677 | 0 | 0.011262 | 0 | 4.1028 | 0.14838 | 2.9868 | 0 | 0.20239 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 12.8978 | 0% | CZ 1B | 0 | 0 | 0.085903 | 0.00012922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086032 | 0% | CZ 1B | 11.6846 | 5.6194 | 9.3892 | 0.13203 | 0 | 42.952 | 1.5534 | 31.2691 | 0 | 2.1188 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 144.4304 | 0%
CZ 2A | 0.11518 | 0.055347 | 0.10217 | 0.021133 | 0 | 0.30494 | 0.015256 | 0.20754 | 0 | 0.018484 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.2315 | 16.86% | CZ 2A | 3.8093 | 1.8304 | 10.3199 | 1.3489 | 0 | 10.0848 | 0.50453 | 6.8637 | 0 | 0.6113 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 48.3192 | 16.86% | CZ 2A | 1.1161 | 0.53631 | 0 | 0.11206 | 0 | 2.9548 | 0.14782 | 2.011 | 0 | 0.17911 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 10.8505 | 16.86% | CZ 2A | 0 | 0 | 0.1032 | 0.0096645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11286 | 16.86% | CZ 2A | 11.6846 | 5.6146 | 11.2796 | 2.2295 | 0 | 30.934 | 1.5476 | 21.0535 | 0 | 1.8751 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 125.93 | 16.86%
CZ 2B | 0.11518 | 0.05531 | 0.09522 | 0.0021077 | 0 | 0.36129 | 0.014505 | 0.27249 | 0 | 0.020557 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.3281 | 0.8505% | CZ 2B | 3.8093 | 1.8292 | 9.6182 | 0.092378 | 0 | 11.9483 | 0.47969 | 9.0117 | 0 | 0.67986 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 50.415 | 0.8505% | CZ 2B | 1.1161 | 0.53594 | 0 | 0.01719 | 0 | 3.5008 | 0.14055 | 2.6404 | 0 | 0.1992 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 11.9435 | 0.8505% | CZ 2B | 0 | 0 | 0.096182 | 0.00033709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096519 | 0.8505% | CZ 2B | 11.6846 | 5.6108 | 10.5127 | 0.2168 | 0 | 36.65 | 1.4714 | 27.6423 | 0 | 2.0854 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 135.5858 | 0.8505%
CZ 3A | 0.11518 | 0.055378 | 0.11153 | 0.06624 | 0 | 0.22599 | 0.010607 | 0.18676 | 0 | 0.017883 | 0 | 0.053947 | 0.0070778 | 0 | 0 | 0.33045 | 1.181 | 7.27% | CZ 3A | 3.8093 | 1.8314 | 11.2653 | 4.4982 | 0 | 7.4738 | 0.35077 | 6.1765 | 0 | 0.59141 | 0 | 1.7841 | 0.23407 | 0 | 0 | 10.9284 | 48.9433 | 7.27% | CZ 3A | 1.1161 | 0.5366 | 0 | 0.31274 | 0 | 2.1898 | 0.10278 | 1.8097 | 0 | 0.17328 | 0 | 0.52274 | 0.068582 | 0 | 0 | 3.202 | 10.0343 | 7.27% | CZ 3A | 0 | 0 | 0.11265 | 0.034308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14696 | 7.27% | CZ 3A | 11.6846 | 5.6177 | 12.313 | 7.024 | 0 | 22.9251 | 1.076 | 18.9457 | 0 | 1.8141 | 0 | 5.4726 | 0.71799 | 0 | 0 | 33.5216 | 121.1124 | 7.27%
CZ 3B | 0.11518 | 0.055385 | 0.10844 | 0.008641 | 0 | 0.21758 | 0.0081393 | 0.21521 | 0 | 0.014834 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.1349 | 8.26% | CZ 3B | 3.8093 | 1.8316 | 10.9536 | 0.47524 | 0 | 7.1957 | 0.26918 | 7.1172 | 0 | 0.49059 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 45.0889 | 8.26% | CZ 3B | 1.1161 | 0.53667 | 0 | 0.056706 | 0 | 2.1083 | 0.078869 | 2.0853 | 0 | 0.14374 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 9.919 | 8.26% | CZ 3B | 0 | 0 | 0.10954 | 0.002817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11235 | 8.26% | CZ 3B | 11.6846 | 5.6184 | 11.9723 | 0.90155 | 0 | 22.0719 | 0.82567 | 21.8312 | 0 | 1.5048 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 116.1224 | 8.26%
CZ 3C | 0.11518 | 0.055303 | 0.12167 | 0.013201 | 0 | 0.021451 | 0.00085301 | 0.15131 | 0 | 0.010195 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 0.88064 | 1.931% | CZ 3C | 3.8093 | 1.829 | 12.2903 | 0.73932 | 0 | 0.70942 | 0.02821 | 5.0041 | 0 | 0.33718 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 37.6933 | 1.931% | CZ 3C | 1.1161 | 0.53588 | 0 | 0.08473 | 0 | 0.20786 | 0.0082656 | 1.4662 | 0 | 0.098791 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 7.3111 | 1.931% | CZ 3C | 0 | 0 | 0.1229 | 0.0045013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1274 | 1.931% | CZ 3C | 11.6846 | 5.6101 | 13.4333 | 1.379 | 0 | 2.1761 | 0.086532 | 15.3496 | 0 | 1.0342 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 90.4654 | 1.931%
CZ 4A | 0.11518 | 0.055354 | 0.12301 | 0.096974 | 0 | 0.17037 | 0.0077281 | 0.20159 | 0 | 0.018545 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.1802 | 27.95% | CZ 4A | 3.8093 | 1.8306 | 12.4255 | 6.608 | 0 | 5.6344 | 0.25558 | 6.667 | 0 | 0.61332 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 50.7901 | 27.95% | CZ 4A | 1.1161 | 0.53637 | 0 | 0.45461 | 0 | 1.6509 | 0.074884 | 1.9534 | 0 | 0.1797 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 9.7592 | 27.95% | CZ 4A | 0 | 0 | 0.12425 | 0.050564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17482 | 27.95% | CZ 4A | 11.6846 | 5.6153 | 13.5811 | 10.2859 | 0 | 17.283 | 0.78396 | 20.4502 | 0 | 1.8813 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 121.2768 | 27.95%
CZ 4B | 0.11518 | 0.05534 | 0.12128 | 0.025668 | 0 | 0.17814 | 0.0062837 | 0.23467 | 0 | 0.014617 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.1427 | 0% | CZ 4B | 3.8093 | 1.8302 | 12.2501 | 1.5904 | 0 | 5.8915 | 0.20781 | 7.761 | 0 | 0.4834 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 46.7701 | 0% | CZ 4B | 1.1161 | 0.53624 | 0 | 0.14295 | 0 | 1.7262 | 0.060888 | 2.2739 | 0 | 0.14163 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 9.7912 | 0% | CZ 4B | 0 | 0 | 0.1225 | 0.011025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13353 | 0% | CZ 4B | 11.6846 | 5.6139 | 13.3893 | 2.7016 | 0 | 18.0714 | 0.63744 | 23.806 | 0 | 1.4828 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 117.0989 | 0%
CZ 4C | 0.11518 | 0.055323 | 0.12787 | 0.065271 | 0 | 0.087238 | 0.0035072 | 0.21119 | 0 | 0.016126 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.0732 | 3.991% | CZ 4C | 3.8093 | 1.8296 | 12.9157 | 4.3726 | 0 | 2.8851 | 0.11599 | 6.9842 | 0 | 0.5333 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 46.3922 | 3.991% | CZ 4C | 1.1161 | 0.53608 | 0 | 0.31669 | 0 | 0.84533 | 0.033984 | 2.0464 | 0 | 0.15626 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 8.8441 | 3.991% | CZ 4C | 0 | 0 | 0.12916 | 0.032917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16207 | 3.991% | CZ 4C | 11.6846 | 5.6122 | 14.1169 | 6.9133 | 0 | 8.8497 | 0.35578 | 21.4234 | 0 | 1.6358 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 110.3033 | 3.991%
CZ 5A | 0.11518 | 0.055286 | 0.13103 | 0.19255 | 0 | 0.1335 | 0.0060085 | 0.20534 | 0 | 0.018844 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.2492 | 12.97% | CZ 5A | 3.8093 | 1.8284 | 13.2353 | 13.3648 | 0 | 4.415 | 0.19871 | 6.7908 | 0 | 0.62321 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 57.212 | 12.97% | CZ 5A | 1.1161 | 0.53571 | 0 | 0.86785 | 0 | 1.2936 | 0.058221 | 1.9897 | 0 | 0.1826 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 9.837 | 12.97% | CZ 5A | 0 | 0 | 0.13235 | 0.10403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23638 | 12.97% | CZ 5A | 11.6846 | 5.6084 | 14.4662 | 20.4558 | 0 | 13.5424 | 0.60952 | 20.8301 | 0 | 1.9116 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 128.8205 | 12.97%
CZ 5B | 0.11518 | 0.055262 | 0.1296 | 0.080154 | 0 | 0.12727 | 0.0044792 | 0.23744 | 0 | 0.016347 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.1572 | 1.287% | CZ 5B | 3.8093 | 1.8276 | 13.0906 | 5.4015 | 0 | 4.2088 | 0.14813 | 7.8526 | 0 | 0.5406 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 49.8255 | 1.287% | CZ 5B | 1.1161 | 0.53548 | 0 | 0.38436 | 0 | 1.2332 | 0.043402 | 2.3008 | 0 | 0.1584 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 9.565 | 1.287% | CZ 5B | 0 | 0 | 0.13091 | 0.040896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1718 | 1.287% | CZ 5B | 11.6846 | 5.606 | 14.308 | 8.4939 | 0 | 12.9102 | 0.45438 | 24.0869 | 0 | 1.6582 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 118.9137 | 1.287%
CZ 5C | 0.11518 | 0.055228 | 0.13112 | 0.10995 | 0 | 0.042994 | 0.0017944 | 0.18349 | 0 | 0.014219 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.0455 | 0% | CZ 5C | 3.8093 | 1.8265 | 13.2446 | 7.5297 | 0 | 1.4219 | 0.059343 | 6.0683 | 0 | 0.47025 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 47.3763 | 0% | CZ 5C | 1.1161 | 0.53515 | 0 | 0.51009 | 0 | 0.4166 | 0.017387 | 1.778 | 0 | 0.13778 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 8.3044 | 0% | CZ 5C | 0 | 0 | 0.13245 | 0.057888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19033 | 0% | CZ 5C | 11.6846 | 5.6025 | 14.4764 | 11.6673 | 0 | 4.3614 | 0.18203 | 18.6137 | 0 | 1.4424 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 107.7423 | 0%
CZ 6A | 0.11518 | 0.05529 | 0.13815 | 0.22757 | 0 | 0.083718 | 0.0036092 | 0.19494 | 0 | 0.016778 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.2267 | 1.39% | CZ 6A | 3.8093 | 1.8285 | 13.9541 | 15.9327 | 0 | 2.7687 | 0.11936 | 6.4468 | 0 | 0.55488 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 58.3607 | 1.39% | CZ 6A | 1.1161 | 0.53575 | 0 | 1.0061 | 0 | 0.81121 | 0.034972 | 1.8889 | 0 | 0.16258 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 9.3489 | 1.39% | CZ 6A | 0 | 0 | 0.13954 | 0.12499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26453 | 1.39% | CZ 6A | 11.6846 | 5.6087 | 15.2518 | 24.1938 | 0 | 8.4926 | 0.36612 | 19.7748 | 0 | 1.702 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 126.7864 | 1.39%
CZ 6B | 0.11518 | 0.055249 | 0.13918 | 0.13436 | 0 | 0.086413 | 0.0030926 | 0.2366 | 0 | 0.015361 | 0 | 0.053947 | 0.0070744 | 0 | 0 | 0.33045 | 1.1769 | 0.179% | CZ 6B | 3.8093 | 1.8272 | 14.0586 | 9.2415 | 0 | 2.8578 | 0.10228 | 7.8246 | 0 | 0.50801 | 0 | 1.7841 | 0.23396 | 0 | 0 | 10.9284 | 53.1757 | 0.179% | CZ 6B | 1.1161 | 0.53535 | 0 | 0.61758 | 0 | 0.83732 | 0.029967 | 2.2926 | 0 | 0.14885 | 0 | 0.52274 | 0.068549 | 0 | 0 | 3.202 | 9.3711 | 0.179% | CZ 6B | 0 | 0 | 0.14059 | 0.071337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21192 | 0.179% | CZ 6B | 11.6846 | 5.6046 | 15.366 | 14.2625 | 0 | 8.7659 | 0.31372 | 24.0011 | 0 | 1.5583 | 0 | 5.4726 | 0.71764 | 0 | 0 | 33.5216 | 121.2687 | 0.179%
CZ 7 | 0.11518 | 0.055252 | 0.14941 | 0.30405 | 0 | 0.0567 | 0.0024027 | 0.19353 | 0 | 0.016377 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.2844 | 0.09387% | CZ 7 | 3.8093 | 1.8273 | 15.0917 | 21.4101 | 0 | 1.8751 | 0.079461 | 6.4001 | 0 | 0.54162 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 63.9811 | 0.09387% | CZ 7 | 1.1161 | 0.53538 | 0 | 1.3267 | 0 | 0.54941 | 0.023282 | 1.8752 | 0 | 0.15869 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 9.3781 | 0.09387% | CZ 7 | 0 | 0 | 0.15092 | 0.16882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31974 | 0.09387% | CZ 7 | 11.6846 | 5.6049 | 16.4952 | 32.3414 | 0 | 5.7518 | 0.24374 | 19.6317 | 0 | 1.6613 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 133.1263 | 0.09387%
CZ 8 | 0.11518 | 0.054912 | 0.16328 | 0.41253 | 0 | 0.050294 | 0.0018997 | 0.21981 | 0 | 0.015239 | 0 | 0.053947 | 0.007071 | 0 | 0 | 0.33045 | 1.4246 | 0% | CZ 8 | 3.8093 | 1.816 | 16.4934 | 28.6901 | 0 | 1.6633 | 0.062827 | 7.2695 | 0 | 0.50396 | 0 | 1.7841 | 0.23385 | 0 | 0 | 10.9284 | 73.2548 | 0% | CZ 8 | 1.1161 | 0.53209 | 0 | 1.8512 | 0 | 0.48734 | 0.018408 | 2.1299 | 0 | 0.14766 | 0 | 0.52274 | 0.068516 | 0 | 0 | 3.202 | 10.076 | 0% | CZ 8 | 0 | 0 | 0.16493 | 0.22372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38865 | 0% | CZ 8 | 11.6846 | 5.5705 | 18.0273 | 43.8329 | 0 | 5.1019 | 0.19271 | 22.2984 | 0 | 1.5459 | 0 | 5.4726 | 0.7173 | 0 | 0 | 33.5216 | 147.9657 | 0%
Us Weighted | 0.11518 | 0.055358 | 0.11322 | 0.068857 | 0 | 0.24066 | 0.011366 | 0.20416 | 0 | 0.018163 | 0 | 0.053947 | 0.0070729 | 0 | 0 | 0.33045 | 1.2184 | 100% | Us Weighted | 3.8093 | 1.8308 | 11.4362 | 4.6955 | 0 | 7.9588 | 0.3759 | 6.7519 | 0 | 0.60069 | 0 | 1.7841 | 0.23391 | 0 | 0 | 10.9284 | 50.4055 | 100% | Us Weighted | 1.1161 | 0.53641 | 0 | 0.3223 | 0 | 2.3319 | 0.11014 | 1.9783 | 0 | 0.176 | 0 | 0.52274 | 0.068535 | 0 | 0 | 3.202 | 10.3645 | 100% | Us Weighted | 0 | 0 | 0.11436 | 0.035955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15032 | 100% | Us Weighted | 11.6846 | 5.6157 | 12.4997 | 7.3041 | 0 | 24.4129 | 1.153 | 20.7108 | 0 | 1.8426 | 0 | 5.4726 | 0.7175 | 0 | 0 | 33.5216 | 124.9351 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.095867 | 0.072645 | 0.090311 | 0.001091 | 0 | 0.48533 | 0.024975 | 0.22039 | 0 | 0.026838 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.4163 | 16.97% | CZ 1A | 3.1705 | 2.4025 | 9.1223 | 0.056863 | 0 | 16.0507 | 0.82597 | 7.2886 | 0 | 0.88756 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 52.9941 | 16.97% | CZ 1A | 0.92894 | 0.70392 | 0 | 0.0076069 | 0 | 4.7028 | 0.24201 | 2.1355 | 0 | 0.26005 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 12.8452 | 16.97% | CZ 1A | 0 | 0 | 0.091223 | 0.000309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091532 | 16.97% | CZ 1A | 9.725 | 7.3694 | 9.9707 | 0.11341 | 0 | 49.2336 | 2.5336 | 22.357 | 0 | 2.7225 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 144.4814 | 16.97%
CZ 1B | 0.095867 | 0.072584 | 0.085117 | 0.0021228 | 0 | 0.43573 | 0.01584 | 0.34067 | 0 | 0.027103 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.4738 | 0% | CZ 1B | 3.1705 | 2.4005 | 8.5977 | 0.095749 | 0 | 14.4103 | 0.52386 | 11.2665 | 0 | 0.89632 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 54.5504 | 0% | CZ 1B | 0.92894 | 0.70333 | 0 | 0.016926 | 0 | 4.2222 | 0.15349 | 3.3011 | 0 | 0.26262 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 13.4529 | 0% | CZ 1B | 0 | 0 | 0.085977 | 0.00037979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086357 | 0% | CZ 1B | 9.725 | 7.3632 | 9.3973 | 0.21871 | 0 | 44.202 | 1.6069 | 34.5587 | 0 | 2.7494 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 150.277 | 0%
CZ 2A | 0.095867 | 0.072523 | 0.10226 | 0.032753 | 0 | 0.31312 | 0.015847 | 0.22338 | 0 | 0.024523 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2791 | 16.86% | CZ 2A | 3.1705 | 2.3984 | 10.3293 | 2.1629 | 0 | 10.3554 | 0.52408 | 7.3875 | 0 | 0.81102 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 50.3283 | 16.86% | CZ 2A | 0.92894 | 0.70274 | 0 | 0.16337 | 0 | 3.0341 | 0.15355 | 2.1645 | 0 | 0.23763 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 11.2492 | 16.86% | CZ 2A | 0 | 0 | 0.10329 | 0.016054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11935 | 16.86% | CZ 2A | 9.725 | 7.3569 | 11.29 | 3.465 | 0 | 31.7642 | 1.6076 | 22.6604 | 0 | 2.4877 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 130.8129 | 16.86%
CZ 2B | 0.095867 | 0.072472 | 0.095301 | 0.003664 | 0 | 0.36757 | 0.014936 | 0.29965 | 0 | 0.026834 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.3751 | 0.8505% | CZ 2B | 3.1705 | 2.3968 | 9.6264 | 0.17823 | 0 | 12.1561 | 0.49396 | 9.9098 | 0 | 0.88745 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 52.0082 | 0.8505% | CZ 2B | 0.92894 | 0.70224 | 0 | 0.027365 | 0 | 3.5617 | 0.14473 | 2.9035 | 0 | 0.26002 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 12.3929 | 0.8505% | CZ 2B | 0 | 0 | 0.096264 | 0.00084835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097112 | 0.8505% | CZ 2B | 9.725 | 7.3518 | 10.5216 | 0.37921 | 0 | 37.2874 | 1.5152 | 30.3972 | 0 | 2.7221 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 140.3558 | 0.8505%
CZ 3A | 0.095867 | 0.072564 | 0.11162 | 0.098627 | 0 | 0.22836 | 0.011028 | 0.20253 | 0 | 0.023864 | 0 | 0.055405 | 0.012298 | 0 | 0 | 0.33111 | 1.2433 | 7.27% | CZ 3A | 3.1705 | 2.3998 | 11.275 | 6.8437 | 0 | 7.5523 | 0.36471 | 6.698 | 0 | 0.78921 | 0 | 1.8323 | 0.40671 | 0 | 0 | 10.9502 | 52.2824 | 7.27% | CZ 3A | 0.92894 | 0.70313 | 0 | 0.44479 | 0 | 2.2128 | 0.10686 | 1.9625 | 0 | 0.23124 | 0 | 0.53687 | 0.11916 | 0 | 0 | 3.2084 | 10.4547 | 7.27% | CZ 3A | 0 | 0 | 0.11275 | 0.053256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16601 | 7.27% | CZ 3A | 9.725 | 7.3611 | 12.3236 | 10.4774 | 0 | 23.1658 | 1.1187 | 20.5453 | 0 | 2.4208 | 0 | 5.6205 | 1.2475 | 0 | 0 | 33.5885 | 127.5943 | 7.27%
CZ 3B | 0.095867 | 0.072571 | 0.10854 | 0.01729 | 0 | 0.21508 | 0.0081087 | 0.23485 | 0 | 0.019127 | 0 | 0.055405 | 0.012298 | 0 | 0 | 0.33111 | 1.1702 | 8.26% | CZ 3B | 3.1705 | 2.4 | 10.9633 | 1.0427 | 0 | 7.1129 | 0.26817 | 7.7667 | 0 | 0.63254 | 0 | 1.8323 | 0.40671 | 0 | 0 | 10.9502 | 46.5461 | 8.26% | CZ 3B | 0.92894 | 0.7032 | 0 | 0.10037 | 0 | 2.0841 | 0.078572 | 2.2756 | 0 | 0.18533 | 0 | 0.53687 | 0.11916 | 0 | 0 | 3.2084 | 10.2205 | 8.26% | CZ 3B | 0 | 0 | 0.10963 | 0.0070014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11663 | 8.26% | CZ 3B | 9.725 | 7.3618 | 11.9829 | 1.8161 | 0 | 21.8181 | 0.82257 | 23.8236 | 0 | 1.9402 | 0 | 5.6205 | 1.2475 | 0 | 0 | 33.5885 | 119.7468 | 8.26%
CZ 3C | 0.095867 | 0.072465 | 0.12177 | 0.034263 | 0 | 0.015004 | 0.00057774 | 0.16003 | 0 | 0.012901 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 0.91169 | 1.931% | CZ 3C | 3.1705 | 2.3965 | 12.3004 | 2.1716 | 0 | 0.49621 | 0.019107 | 5.2923 | 0 | 0.42664 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 39.4624 | 1.931% | CZ 3C | 0.92894 | 0.70218 | 0 | 0.18388 | 0 | 0.14539 | 0.0055982 | 1.5506 | 0 | 0.125 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 7.506 | 1.931% | CZ 3C | 0 | 0 | 0.123 | 0.01544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13844 | 1.931% | CZ 3C | 9.725 | 7.3511 | 13.4444 | 3.6127 | 0 | 1.5221 | 0.058607 | 16.2336 | 0 | 1.3087 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 93.7123 | 1.931%
CZ 4A | 0.095867 | 0.07253 | 0.12312 | 0.14626 | 0 | 0.16617 | 0.0077825 | 0.21663 | 0 | 0.024533 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.2517 | 27.95% | CZ 4A | 3.1705 | 2.3987 | 12.4364 | 10.1745 | 0 | 5.4954 | 0.25738 | 7.1644 | 0 | 0.81136 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 55.0976 | 27.95% | CZ 4A | 0.92894 | 0.7028 | 0 | 0.65591 | 0 | 1.6101 | 0.075411 | 2.0992 | 0 | 0.23773 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 10.1744 | 27.95% | CZ 4A | 0 | 0 | 0.12436 | 0.079359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20372 | 27.95% | CZ 4A | 9.725 | 7.3576 | 13.593 | 15.5406 | 0 | 16.8565 | 0.78948 | 21.976 | 0 | 2.4887 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 128.7829 | 27.95%
CZ 4B | 0.095867 | 0.072513 | 0.12138 | 0.045615 | 0 | 0.16764 | 0.0059371 | 0.25037 | 0 | 0.018345 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.1765 | 0% | CZ 4B | 3.1705 | 2.3981 | 12.2609 | 2.9835 | 0 | 5.5439 | 0.19635 | 8.2802 | 0 | 0.60669 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 48.6293 | 0% | CZ 4B | 0.92894 | 0.70264 | 0 | 0.23163 | 0 | 1.6244 | 0.05753 | 2.4261 | 0 | 0.17776 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.0133 | 0% | CZ 4B | 0 | 0 | 0.12261 | 0.021929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14454 | 0% | CZ 4B | 9.725 | 7.3559 | 13.4011 | 4.8218 | 0 | 17.0054 | 0.60228 | 25.3987 | 0 | 1.861 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 120.6275 | 0%
CZ 4C | 0.095867 | 0.072492 | 0.12797 | 0.10261 | 0 | 0.07947 | 0.0032387 | 0.22412 | 0 | 0.020557 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.1251 | 3.991% | CZ 4C | 3.1705 | 2.3974 | 12.9265 | 7.05 | 0 | 2.6282 | 0.10711 | 7.412 | 0 | 0.67986 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 49.5607 | 3.991% | CZ 4C | 0.92894 | 0.70244 | 0 | 0.47278 | 0 | 0.77005 | 0.031383 | 2.1717 | 0 | 0.1992 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 9.1409 | 3.991% | CZ 4C | 0 | 0 | 0.12927 | 0.054364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18363 | 3.991% | CZ 4C | 9.725 | 7.3538 | 14.1287 | 10.8916 | 0 | 8.0616 | 0.32855 | 22.7355 | 0 | 2.0854 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 115.7664 | 3.991%
CZ 5A | 0.095867 | 0.072442 | 0.13114 | 0.27317 | 0 | 0.12948 | 0.0060221 | 0.22054 | 0 | 0.025135 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.3526 | 12.97% | CZ 5A | 3.1705 | 2.3957 | 13.2467 | 19.2655 | 0 | 4.2822 | 0.19916 | 7.2936 | 0 | 0.83125 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 63.8736 | 12.97% | CZ 5A | 0.92894 | 0.70195 | 0 | 1.1878 | 0 | 1.2547 | 0.058353 | 2.137 | 0 | 0.24355 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 10.3766 | 12.97% | CZ 5A | 0 | 0 | 0.13247 | 0.15212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28458 | 12.97% | CZ 5A | 9.725 | 7.3487 | 14.4786 | 29.0611 | 0 | 13.1353 | 0.6109 | 22.3722 | 0 | 2.5498 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 139.7374 | 12.97%
CZ 5B | 0.095867 | 0.072411 | 0.12971 | 0.1146 | 0 | 0.11957 | 0.0042243 | 0.25399 | 0 | 0.020646 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.2098 | 1.287% | CZ 5B | 3.1705 | 2.3947 | 13.1023 | 7.8966 | 0 | 3.9543 | 0.1397 | 8.3999 | 0 | 0.68278 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 52.9298 | 1.287% | CZ 5B | 0.92894 | 0.70165 | 0 | 0.52471 | 0 | 1.1586 | 0.040933 | 2.4612 | 0 | 0.20005 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 9.8804 | 1.287% | CZ 5B | 0 | 0 | 0.13102 | 0.061058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19208 | 1.287% | CZ 5B | 9.725 | 7.3456 | 14.3208 | 12.1668 | 0 | 12.1293 | 0.42852 | 25.7659 | 0 | 2.0944 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 124.4321 | 1.287%
CZ 5C | 0.095867 | 0.072367 | 0.13124 | 0.1586 | 0 | 0.033369 | 0.0014274 | 0.18718 | 0 | 0.017648 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.0965 | 0% | CZ 5C | 3.1705 | 2.3933 | 13.2562 | 11.0844 | 0 | 1.1036 | 0.047205 | 6.1904 | 0 | 0.58365 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 51.0184 | 0% | CZ 5C | 0.92894 | 0.70122 | 0 | 0.70402 | 0 | 0.32334 | 0.013831 | 1.8138 | 0 | 0.17101 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 8.5205 | 0% | CZ 5C | 0 | 0 | 0.13256 | 0.086816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21938 | 0% | CZ 5C | 9.725 | 7.3411 | 14.489 | 16.8594 | 0 | 3.3851 | 0.14479 | 18.9884 | 0 | 1.7903 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 113.1794 | 0%
CZ 6A | 0.095867 | 0.072448 | 0.13826 | 0.31519 | 0 | 0.077679 | 0.0034222 | 0.20608 | 0 | 0.021815 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.3296 | 1.39% | CZ 6A | 3.1705 | 2.396 | 13.9657 | 22.3918 | 0 | 2.5689 | 0.11318 | 6.8152 | 0 | 0.72144 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 65.3317 | 1.39% | CZ 6A | 0.92894 | 0.70201 | 0 | 1.3471 | 0 | 0.75269 | 0.033161 | 1.9968 | 0 | 0.21138 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 9.8365 | 1.39% | CZ 6A | 0 | 0 | 0.13966 | 0.17794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3176 | 1.39% | CZ 6A | 9.725 | 7.3494 | 15.2645 | 33.5519 | 0 | 7.8799 | 0.34716 | 20.9049 | 0 | 2.2129 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 137.6916 | 1.39%
CZ 6B | 0.095867 | 0.072394 | 0.1393 | 0.1798 | 0 | 0.079024 | 0.0028411 | 0.25105 | 0 | 0.019252 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2383 | 0.179% | CZ 6B | 3.1705 | 2.3942 | 14.0707 | 12.569 | 0 | 2.6134 | 0.09396 | 8.3025 | 0 | 0.6367 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 57.0401 | 0.179% | CZ 6B | 0.92894 | 0.70149 | 0 | 0.79761 | 0 | 0.76573 | 0.02753 | 2.4326 | 0 | 0.18655 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 9.7048 | 0.179% | CZ 6B | 0 | 0 | 0.14071 | 0.098467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23917 | 0.179% | CZ 6B | 9.725 | 7.3438 | 15.3793 | 19.1126 | 0 | 8.0165 | 0.28821 | 25.467 | 0 | 1.953 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 127.7417 | 0.179%
CZ 7 | 0.095867 | 0.072397 | 0.14954 | 0.42731 | 0 | 0.049036 | 0.0021512 | 0.21119 | 0 | 0.022046 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.4283 | 0.09387% | CZ 7 | 3.1705 | 2.3943 | 15.1046 | 30.309 | 0 | 1.6217 | 0.071144 | 6.9842 | 0 | 0.72909 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 73.5737 | 0.09387% | CZ 7 | 0.92894 | 0.70152 | 0 | 1.8332 | 0 | 0.47515 | 0.020845 | 2.0464 | 0 | 0.21362 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.084 | 0.09387% | CZ 7 | 0 | 0 | 0.15105 | 0.24052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39157 | 0.09387% | CZ 7 | 9.725 | 7.3442 | 16.5093 | 45.481 | 0 | 4.9744 | 0.21823 | 21.4234 | 0 | 2.2364 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 148.3682 | 0.09387%
CZ 8 | 0.095867 | 0.071952 | 0.16343 | 0.49346 | 0 | 0.041747 | 0.0015973 | 0.22646 | 0 | 0.018715 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.512 | 0% | CZ 8 | 3.1705 | 2.3796 | 16.5084 | 34.1712 | 0 | 1.3806 | 0.052824 | 7.4892 | 0 | 0.61894 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 78.9604 | 0% | CZ 8 | 0.92894 | 0.6972 | 0 | 2.2354 | 0 | 0.40452 | 0.015477 | 2.1943 | 0 | 0.18135 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.5215 | 0% | CZ 8 | 0 | 0 | 0.16508 | 0.26542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4305 | 0% | CZ 8 | 9.725 | 7.299 | 18.0436 | 52.4123 | 0 | 4.2349 | 0.16203 | 22.9724 | 0 | 1.8985 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 157.204 | 0%
Us Weighted | 0.095867 | 0.072536 | 0.11332 | 0.10199 | 0 | 0.24214 | 0.011714 | 0.2197 | 0 | 0.024042 | 0 | 0.055405 | 0.012293 | 0 | 0 | 0.33111 | 1.2801 | 100% | Us Weighted | 3.1705 | 2.3989 | 11.4461 | 7.0894 | 0 | 8.0079 | 0.38739 | 7.2657 | 0 | 0.79511 | 0 | 1.8323 | 0.40656 | 0 | 0 | 10.9502 | 53.75 | 100% | Us Weighted | 0.92894 | 0.70287 | 0 | 0.45814 | 0 | 2.3463 | 0.1135 | 2.1288 | 0 | 0.23296 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 10.7759 | 100% | Us Weighted | 0 | 0 | 0.11446 | 0.055258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16972 | 100% | Us Weighted | 9.725 | 7.3583 | 12.5106 | 10.8359 | 0 | 24.5634 | 1.1883 | 22.2867 | 0 | 2.4389 | 0 | 5.6205 | 1.2471 | 0 | 0 | 33.5885 | 131.3631 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.095867 | 0.072645 | 0.090311 | 0.0011282 | 0 | 0.48685 | 0.025087 | 0.22208 | 0 | 0.026987 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.4198 | 16.97% | CZ 1A | 3.1705 | 2.4025 | 9.1223 | 0.058548 | 0 | 16.1007 | 0.82968 | 7.3446 | 0 | 0.8925 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 53.1104 | 16.97% | CZ 1A | 0.92894 | 0.70392 | 0 | 0.0079033 | 0 | 4.7175 | 0.24309 | 2.1519 | 0 | 0.2615 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 12.8791 | 16.97% | CZ 1A | 0 | 0 | 0.091223 | 0.00031574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091539 | 16.97% | CZ 1A | 9.725 | 7.3694 | 9.9707 | 0.11725 | 0 | 49.3871 | 2.5449 | 22.5287 | 0 | 2.7377 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 144.8369 | 16.97%
CZ 1B | 0.095867 | 0.072584 | 0.085117 | 0.0022368 | 0 | 0.43633 | 0.015915 | 0.34327 | 0 | 0.027269 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.4774 | 0% | CZ 1B | 3.1705 | 2.4005 | 8.5977 | 0.10103 | 0 | 14.4301 | 0.52633 | 11.3524 | 0 | 0.90183 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 54.6694 | 0% | CZ 1B | 0.92894 | 0.70333 | 0 | 0.017815 | 0 | 4.228 | 0.15421 | 3.3262 | 0 | 0.26423 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 13.4871 | 0% | CZ 1B | 0 | 0 | 0.085977 | 0.00040226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086379 | 0% | CZ 1B | 9.725 | 7.3632 | 9.3973 | 0.23048 | 0 | 44.2627 | 1.6145 | 34.8221 | 0 | 2.7663 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 150.6377 | 0%
CZ 2A | 0.095867 | 0.072523 | 0.10226 | 0.049683 | 0 | 0.32139 | 0.016642 | 0.24601 | 0 | 0.02662 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.3298 | 16.86% | CZ 2A | 3.1705 | 2.3984 | 10.3291 | 3.3187 | 0 | 10.6289 | 0.55038 | 8.1359 | 0 | 0.88036 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 52.6013 | 16.86% | CZ 2A | 0.92894 | 0.70274 | 0 | 0.24243 | 0 | 3.1142 | 0.16126 | 2.3838 | 0 | 0.25794 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 11.6557 | 16.86% | CZ 2A | 0 | 0 | 0.10329 | 0.024912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1282 | 16.86% | CZ 2A | 9.725 | 7.3569 | 11.2897 | 5.261 | 0 | 32.6029 | 1.6882 | 24.9561 | 0 | 2.7004 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 136.0362 | 16.86%
CZ 2B | 0.095867 | 0.072472 | 0.095301 | 0.0088022 | 0 | 0.39394 | 0.016234 | 0.33831 | 0 | 0.030138 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.4499 | 0.8505% | CZ 2B | 3.1705 | 2.3968 | 9.6264 | 0.47906 | 0 | 13.028 | 0.5369 | 11.1885 | 0 | 0.99669 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 54.6119 | 0.8505% | CZ 2B | 0.92894 | 0.70224 | 0 | 0.058485 | 0 | 3.8172 | 0.15731 | 3.2782 | 0 | 0.29203 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 13.0987 | 0.8505% | CZ 2B | 0 | 0 | 0.096264 | 0.0027945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099058 | 0.8505% | CZ 2B | 9.725 | 7.3518 | 10.5216 | 0.91771 | 0 | 39.962 | 1.6469 | 34.3194 | 0 | 3.0572 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 147.9579 | 0.8505%
CZ 3A | 0.095867 | 0.072564 | 0.11162 | 0.095545 | 0 | 0.25306 | 0.01235 | 0.23042 | 0 | 0.0266 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2968 | 7.27% | CZ 3A | 3.1705 | 2.3998 | 11.2748 | 6.5682 | 0 | 8.3691 | 0.40843 | 7.6203 | 0 | 0.87969 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 53.8799 | 7.27% | CZ 3A | 0.92894 | 0.70313 | 0 | 0.43969 | 0 | 2.4521 | 0.11967 | 2.2327 | 0 | 0.25775 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.9984 | 7.27% | CZ 3A | 0 | 0 | 0.11275 | 0.050675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16342 | 7.27% | CZ 3A | 9.725 | 7.3611 | 12.3233 | 10.1419 | 0 | 25.6714 | 1.2528 | 23.3743 | 0 | 2.6984 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 133.0045 | 7.27%
CZ 3B | 0.095867 | 0.072571 | 0.10854 | 0.01518 | 0 | 0.2524 | 0.0095293 | 0.2678 | 0 | 0.021845 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2425 | 8.26% | CZ 3B | 3.1705 | 2.4 | 10.9634 | 0.88248 | 0 | 8.3473 | 0.31515 | 8.8566 | 0 | 0.72245 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 48.847 | 8.26% | CZ 3B | 0.92894 | 0.7032 | 0 | 0.092831 | 0 | 2.4457 | 0.092337 | 2.595 | 0 | 0.21168 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.9341 | 8.26% | CZ 3B | 0 | 0 | 0.10963 | 0.0056564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11529 | 8.26% | CZ 3B | 9.725 | 7.3618 | 11.983 | 1.5901 | 0 | 25.6045 | 0.96668 | 27.1666 | 0 | 2.216 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 127.07 | 8.26%
CZ 3C | 0.095867 | 0.072465 | 0.12178 | 0.025306 | 0 | 0.048326 | 0.0019677 | 0.24922 | 0 | 0.021349 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.0351 | 1.931% | CZ 3C | 3.1705 | 2.3965 | 12.3005 | 1.4101 | 0 | 1.5982 | 0.065075 | 8.2421 | 0 | 0.70605 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 43.0782 | 1.931% | CZ 3C | 0.92894 | 0.70218 | 0 | 0.16347 | 0 | 0.46827 | 0.019067 | 2.4149 | 0 | 0.20687 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 8.7681 | 1.931% | CZ 3C | 0 | 0 | 0.12301 | 0.0085217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13153 | 1.931% | CZ 3C | 9.725 | 7.3511 | 13.4445 | 2.6428 | 0 | 4.9023 | 0.19961 | 25.2818 | 0 | 2.1657 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 106.1691 | 1.931%
CZ 4A | 0.095867 | 0.07253 | 0.12312 | 0.16391 | 0 | 0.16486 | 0.0077791 | 0.22147 | 0 | 0.024982 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2733 | 27.95% | CZ 4A | 3.1705 | 2.3987 | 12.4362 | 11.4232 | 0 | 5.4521 | 0.25726 | 7.3243 | 0 | 0.82619 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 56.4776 | 27.95% | CZ 4A | 0.92894 | 0.7028 | 0 | 0.73221 | 0 | 1.5975 | 0.075378 | 2.146 | 0 | 0.24207 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.2893 | 27.95% | CZ 4A | 0 | 0 | 0.12436 | 0.089242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2136 | 27.95% | CZ 4A | 9.725 | 7.3576 | 13.5927 | 17.4197 | 0 | 16.7238 | 0.78913 | 22.4666 | 0 | 2.5343 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 131.0651 | 27.95%
CZ 4B | 0.095867 | 0.072513 | 0.12138 | 0.056875 | 0 | 0.16522 | 0.0058657 | 0.2558 | 0 | 0.018739 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.1911 | 0% | CZ 4B | 3.1705 | 2.3981 | 12.2608 | 3.7582 | 0 | 5.4642 | 0.19399 | 8.4596 | 0 | 0.61973 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 49.5141 | 0% | CZ 4B | 0.92894 | 0.70264 | 0 | 0.28337 | 0 | 1.601 | 0.056838 | 2.4786 | 0 | 0.18158 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.0974 | 0% | CZ 4B | 0 | 0 | 0.12261 | 0.02791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15052 | 0% | CZ 4B | 9.725 | 7.3559 | 13.401 | 6.0172 | 0 | 16.7607 | 0.59504 | 25.9489 | 0 | 1.9009 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 122.1609 | 0%
CZ 4C | 0.095867 | 0.072492 | 0.12797 | 0.11831 | 0 | 0.07653 | 0.00313 | 0.22772 | 0 | 0.020897 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.1417 | 3.991% | CZ 4C | 3.1705 | 2.3974 | 12.9265 | 8.1459 | 0 | 2.5309 | 0.10351 | 7.5309 | 0 | 0.6911 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 50.6858 | 3.991% | CZ 4C | 0.92894 | 0.70244 | 0 | 0.5426 | 0 | 0.74156 | 0.030329 | 2.2065 | 0 | 0.20249 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 9.2192 | 3.991% | CZ 4C | 0 | 0 | 0.12927 | 0.06294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19221 | 3.991% | CZ 4C | 9.725 | 7.3538 | 14.1287 | 12.5598 | 0 | 7.7634 | 0.31751 | 23.1003 | 0 | 2.1199 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 117.5242 | 3.991%
CZ 5A | 0.095867 | 0.072442 | 0.13114 | 0.29875 | 0 | 0.12815 | 0.0060085 | 0.22589 | 0 | 0.025631 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.3827 | 12.97% | CZ 5A | 3.1705 | 2.3957 | 13.2465 | 21.0803 | 0 | 4.2381 | 0.19871 | 7.4706 | 0 | 0.84766 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 65.8372 | 12.97% | CZ 5A | 0.92894 | 0.70195 | 0 | 1.2973 | 0 | 1.2417 | 0.058221 | 2.1889 | 0 | 0.24836 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 10.5298 | 12.97% | CZ 5A | 0 | 0 | 0.13247 | 0.16653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29899 | 12.97% | CZ 5A | 9.725 | 7.3487 | 14.4785 | 31.783 | 0 | 12.9998 | 0.60952 | 22.9151 | 0 | 2.6001 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 142.9159 | 12.97%
CZ 5B | 0.095867 | 0.072411 | 0.12971 | 0.13223 | 0 | 0.11724 | 0.0041563 | 0.25957 | 0 | 0.021159 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.2311 | 1.287% | CZ 5B | 3.1705 | 2.3947 | 13.1022 | 9.1325 | 0 | 3.8772 | 0.13746 | 8.5845 | 0 | 0.69975 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 54.2877 | 1.287% | CZ 5B | 0.92894 | 0.70165 | 0 | 0.6024 | 0 | 1.136 | 0.040274 | 2.5152 | 0 | 0.20503 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 9.9939 | 1.287% | CZ 5B | 0 | 0 | 0.13102 | 0.070765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20179 | 1.287% | CZ 5B | 9.725 | 7.3456 | 14.3207 | 14.0411 | 0 | 11.8928 | 0.42163 | 26.332 | 0 | 2.1464 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 126.681 | 1.287%
CZ 5C | 0.095867 | 0.072367 | 0.13124 | 0.18208 | 0 | 0.030182 | 0.0012948 | 0.18826 | 0 | 0.017754 | 0 | 0.055405 | 0.012298 | 0 | 0 | 0.33111 | 1.1178 | 0% | CZ 5C | 3.1705 | 2.3933 | 13.2561 | 12.747 | 0 | 0.99815 | 0.042821 | 6.2261 | 0 | 0.58713 | 0 | 1.8323 | 0.40671 | 0 | 0 | 10.9502 | 52.6102 | 0% | CZ 5C | 0.92894 | 0.70122 | 0 | 0.80505 | 0 | 0.29246 | 0.012547 | 1.8242 | 0 | 0.17203 | 0 | 0.53687 | 0.11916 | 0 | 0 | 3.2084 | 8.6009 | 0% | CZ 5C | 0 | 0 | 0.13256 | 0.099993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23255 | 0% | CZ 5C | 9.725 | 7.3411 | 14.4889 | 19.3573 | 0 | 3.0617 | 0.13135 | 19.0977 | 0 | 1.801 | 0 | 5.6205 | 1.2475 | 0 | 0 | 33.5885 | 115.4607 | 0%
CZ 6A | 0.095867 | 0.072448 | 0.13826 | 0.34457 | 0 | 0.07599 | 0.0033645 | 0.2103 | 0 | 0.02207 | 0 | 0.055405 | 0.012291 | 0 | 0 | 0.33111 | 1.3617 | 1.39% | CZ 6A | 3.1705 | 2.396 | 13.9658 | 24.4771 | 0 | 2.5131 | 0.11127 | 6.9549 | 0 | 0.72987 | 0 | 1.8323 | 0.40648 | 0 | 0 | 10.9502 | 67.5075 | 1.39% | CZ 6A | 0.92894 | 0.70201 | 0 | 1.473 | 0 | 0.73633 | 0.032601 | 2.0378 | 0 | 0.21385 | 0 | 0.53687 | 0.1191 | 0 | 0 | 3.2084 | 9.9888 | 1.39% | CZ 6A | 0 | 0 | 0.13966 | 0.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33416 | 1.39% | CZ 6A | 9.725 | 7.3494 | 15.2646 | 36.6793 | 0 | 7.7086 | 0.3413 | 21.3334 | 0 | 2.2388 | 0 | 5.6205 | 1.2468 | 0 | 0 | 33.5885 | 141.0963 | 1.39%
CZ 6B | 0.095867 | 0.072394 | 0.1393 | 0.20613 | 0 | 0.076384 | 0.0027561 | 0.25584 | 0 | 0.01965 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.2671 | 0.179% | CZ 6B | 3.1705 | 2.3942 | 14.0706 | 14.429 | 0 | 2.5261 | 0.09115 | 8.461 | 0 | 0.64985 | 0 | 1.8323 | 0.40659 | 0 | 0 | 10.9502 | 58.9815 | 0.179% | CZ 6B | 0.92894 | 0.70149 | 0 | 0.91168 | 0 | 0.74015 | 0.026707 | 2.479 | 0 | 0.1904 | 0 | 0.53687 | 0.11913 | 0 | 0 | 3.2084 | 9.8428 | 0.179% | CZ 6B | 0 | 0 | 0.14071 | 0.11317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25388 | 0.179% | CZ 6B | 9.725 | 7.3438 | 15.3792 | 21.9144 | 0 | 7.7486 | 0.27959 | 25.9531 | 0 | 1.9933 | 0 | 5.6205 | 1.2472 | 0 | 0 | 33.5885 | 130.7932 | 0.179%
CZ 7 | 0.095867 | 0.072397 | 0.14954 | 0.47433 | 0 | 0.056227 | 0.0024979 | 0.24513 | 0 | 0.025026 | 0 | 0.055405 | 0.012298 | 0 | 0 | 0.33111 | 1.5198 | 0.09387% | CZ 7 | 3.1705 | 2.3943 | 15.1046 | 33.5513 | 0 | 1.8595 | 0.082608 | 8.1069 | 0 | 0.82765 | 0 | 1.8323 | 0.40671 | 0 | 0 | 10.9502 | 78.2866 | 0.09387% | CZ 7 | 0.92894 | 0.70152 | 0 | 2.0483 | 0 | 0.54483 | 0.024204 | 2.3753 | 0 | 0.2425 | 0 | 0.53687 | 0.11916 | 0 | 0 | 3.2084 | 10.73 | 0.09387% | CZ 7 | 0 | 0 | 0.15105 | 0.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41665 | 0.09387% | CZ 7 | 9.725 | 7.3442 | 16.5093 | 50.474 | 0 | 5.7039 | 0.25339 | 24.8671 | 0 | 2.5387 | 0 | 5.6205 | 1.2475 | 0 | 0 | 33.5885 | 157.8722 | 0.09387%
CZ 8 | 0.095867 | 0.071952 | 0.16343 | 0.52116 | 0 | 0.050474 | 0.0019405 | 0.25791 | 0 | 0.021349 | 0 | 0.055405 | 0.012298 | 0 | 0 | 0.33111 | 1.5829 | 0% | CZ 8 | 3.1705 | 2.3796 | 16.5084 | 36.217 | 0 | 1.6692 | 0.064176 | 8.5293 | 0 | 0.70605 | 0 | 1.8323 | 0.40671 | 0 | 0 | 10.9502 | 82.4334 | 0% | CZ 8 | 0.92894 | 0.6972 | 0 | 2.3427 | 0 | 0.48908 | 0.018803 | 2.4991 | 0 | 0.20687 | 0 | 0.53687 | 0.11916 | 0 | 0 | 3.2084 | 11.0471 | 0% | CZ 8 | 0 | 0 | 0.16508 | 0.28221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4473 | 0% | CZ 8 | 9.725 | 7.299 | 18.0436 | 55.372 | 0 | 5.1202 | 0.19685 | 26.1627 | 0 | 2.1657 | 0 | 5.6205 | 1.2475 | 0 | 0 | 33.5885 | 164.5417 | 0%
Us Weighted | 0.095867 | 0.072536 | 0.11332 | 0.11392 | 0 | 0.24883 | 0.01211 | 0.23296 | 0 | 0.025253 | 0 | 0.055405 | 0.012294 | 0 | 0 | 0.33111 | 1.3136 | 100% | Us Weighted | 3.1705 | 2.3989 | 11.446 | 7.9185 | 0 | 8.2291 | 0.40048 | 7.7043 | 0 | 0.83514 | 0 | 1.8323 | 0.40657 | 0 | 0 | 10.9502 | 55.2921 | 100% | Us Weighted | 0.92894 | 0.70287 | 0 | 0.51187 | 0 | 2.4111 | 0.11734 | 2.2574 | 0 | 0.24469 | 0 | 0.53687 | 0.11912 | 0 | 0 | 3.2084 | 11.0385 | 100% | Us Weighted | 0 | 0 | 0.11446 | 0.061715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17618 | 100% | Us Weighted | 9.725 | 7.3583 | 12.5105 | 12.1043 | 0 | 25.242 | 1.2284 | 23.6322 | 0 | 2.5617 | 0 | 5.6205 | 1.2471 | 0 | 0 | 33.5885 | 134.8185 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 84352 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 84352 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.0049278 | 0.017203 | 7.0082e-05 | 0.00093388 | 0 | 0.1253 | 0.005706 | 0.05025 | 0 | 0.0094103 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.22125 | 16.97% | CZ 1A | 0.16297 | 0.56893 | 0.007079 | 0.050232 | 0 | 4.1438 | 0.18871 | 1.6618 | 0 | 0.31121 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 7.3412 | 16.97% | CZ 1A | 0.047749 | 0.16669 | 0 | 0.0062897 | 0 | 1.2141 | 0.05529 | 0.48691 | 0 | 0.091185 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 2.1404 | 16.97% | CZ 1A | 0 | 0 | 7.079e-05 | 0.00028765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00035844 | 16.97% | CZ 1A | 0.49989 | 1.7451 | 0.0077373 | 0.097288 | 0 | 12.7106 | 0.57883 | 5.0975 | 0 | 0.95461 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 22.4475 | 16.97%
CZ 1B | 0.0049278 | 0.017189 | 7.0082e-05 | 0.0017127 | 0 | 0.10478 | 0.0033645 | 0.090355 | 0 | 0.010076 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.23993 | 0% | CZ 1B | 0.16297 | 0.56848 | 0.007079 | 0.082262 | 0 | 3.4654 | 0.11127 | 2.9882 | 0 | 0.33324 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 7.9653 | 0% | CZ 1B | 0.047749 | 0.16656 | 0 | 0.012942 | 0 | 1.0153 | 0.032601 | 0.87552 | 0 | 0.097639 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 2.3206 | 0% | CZ 1B | 0 | 0 | 7.079e-05 | 0.00038092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00045171 | 0% | CZ 1B | 0.49989 | 1.7437 | 0.0077373 | 0.17712 | 0 | 10.6297 | 0.3413 | 9.1658 | 0 | 1.0222 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 24.3435 | 0%
CZ 2A | 0.0049278 | 0.017176 | 8.5655e-05 | 0.029149 | 0 | 0.088642 | 0.0044384 | 0.073485 | 0 | 0.010749 | 0 | 0.0015701 | 0.00522 | 0 | 0 | 0.0006593 | 0.2361 | 16.86% | CZ 2A | 0.16297 | 0.56803 | 0.0086521 | 1.9553 | 0 | 2.9315 | 0.14678 | 2.4302 | 0 | 0.3555 | 0 | 0.051925 | 0.17263 | 0 | 0 | 0.021804 | 8.8053 | 16.86% | CZ 2A | 0.047749 | 0.16643 | 0 | 0.14107 | 0 | 0.85893 | 0.043007 | 0.71206 | 0 | 0.10416 | 0 | 0.015214 | 0.050581 | 0 | 0 | 0.0063884 | 2.1456 | 16.86% | CZ 2A | 0 | 0 | 8.6521e-05 | 0.014738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014824 | 16.86% | CZ 2A | 0.49989 | 1.7424 | 0.0094567 | 3.0877 | 0 | 8.9921 | 0.45024 | 7.4545 | 0 | 1.0904 | 0 | 0.15928 | 0.52953 | 0 | 0 | 0.06688 | 24.0824 | 16.86%
CZ 2B | 0.0049278 | 0.017162 | 7.8981e-05 | 0.0069505 | 0 | 0.11161 | 0.0042821 | 0.11002 | 0 | 0.012707 | 0 | 0.0015701 | 0.0052268 | 0 | 0 | 0.0006593 | 0.27519 | 0.8505% | CZ 2B | 0.16297 | 0.56758 | 0.0079779 | 0.39522 | 0 | 3.6909 | 0.14161 | 3.6386 | 0 | 0.42023 | 0 | 0.051925 | 0.17286 | 0 | 0 | 0.021804 | 9.2717 | 0.8505% | CZ 2B | 0.047749 | 0.1663 | 0 | 0.043765 | 0 | 1.0814 | 0.041492 | 1.0661 | 0 | 0.12313 | 0 | 0.015214 | 0.050647 | 0 | 0 | 0.0063884 | 2.6422 | 0.8505% | CZ 2B | 0 | 0 | 7.9779e-05 | 0.0024585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025383 | 0.8505% | CZ 2B | 0.49989 | 1.741 | 0.0087198 | 0.72689 | 0 | 11.3216 | 0.43438 | 11.1609 | 0 | 1.289 | 0 | 0.15928 | 0.53022 | 0 | 0 | 0.06688 | 27.9387 | 0.8505%
CZ 3A | 0.0049278 | 0.017186 | 9.0105e-05 | 0.015671 | 0 | 0.080078 | 0.0035208 | 0.058294 | 0 | 0.010297 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.19752 | 7.27% | CZ 3A | 0.16297 | 0.56837 | 0.0091015 | 1.0353 | 0 | 2.6483 | 0.11644 | 1.9279 | 0 | 0.34055 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 7.0553 | 7.27% | CZ 3A | 0.047749 | 0.16653 | 0 | 0.078111 | 0 | 0.77594 | 0.034116 | 0.56486 | 0 | 0.099779 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 1.8393 | 7.27% | CZ 3A | 0 | 0 | 9.1015e-05 | 0.0076869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077779 | 7.27% | CZ 3A | 0.49989 | 1.7434 | 0.009948 | 1.6579 | 0 | 8.1233 | 0.35716 | 5.9135 | 0 | 1.0446 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 20.1057 | 7.27%
CZ 3B | 0.0049278 | 0.017186 | 9.233e-05 | -0.00048366 | 0 | 0.091167 | 0.0029974 | 0.069295 | 0 | 0.0083024 | 0 | 0.0015701 | 0.00522 | 0 | 0 | 0.0006593 | 0.20093 | 8.26% | CZ 3B | 0.16297 | 0.56837 | 0.0093262 | -0.079101 | 0 | 3.015 | 0.09913 | 2.2917 | 0 | 0.27457 | 0 | 0.051925 | 0.17263 | 0 | 0 | 0.021804 | 6.5883 | 8.26% | CZ 3B | 0.047749 | 0.16653 | 0 | 0.0043139 | 0 | 0.88339 | 0.029045 | 0.67145 | 0 | 0.080449 | 0 | 0.015214 | 0.050581 | 0 | 0 | 0.0063884 | 1.9551 | 8.26% | CZ 3B | 0 | 0 | 9.3262e-05 | -0.00093824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00084498 | 8.26% | CZ 3B | 0.49989 | 1.7434 | 0.010194 | -0.057388 | 0 | 9.2482 | 0.30407 | 7.0294 | 0 | 0.84222 | 0 | 0.15928 | 0.52953 | 0 | 0 | 0.06688 | 20.3758 | 8.26%
CZ 3C | 0.0049278 | 0.017162 | 0.00010012 | 0.0075691 | 0 | 0.041261 | 0.0016618 | 0.11503 | 0 | 0.0127 | 0 | 0.0015701 | 0.0052302 | 0 | 0 | 0.0006593 | 0.20788 | 1.931% | CZ 3C | 0.16297 | 0.56758 | 0.010113 | 0.31479 | 0 | 1.3645 | 0.05496 | 3.8043 | 0 | 0.42001 | 0 | 0.051925 | 0.17297 | 0 | 0 | 0.021804 | 6.946 | 1.931% | CZ 3C | 0.047749 | 0.1663 | 0 | 0.064149 | 0 | 0.39981 | 0.016103 | 1.1147 | 0 | 0.12306 | 0 | 0.015214 | 0.05068 | 0 | 0 | 0.0063884 | 2.0041 | 1.931% | CZ 3C | 0 | 0 | 0.00010113 | 0.00095847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010596 | 1.931% | CZ 3C | 0.49989 | 1.741 | 0.011053 | 0.77633 | 0 | 4.1856 | 0.16858 | 11.6694 | 0 | 1.2883 | 0 | 0.15928 | 0.53057 | 0 | 0 | 0.06688 | 21.0969 | 1.931%
CZ 4A | 0.0049278 | 0.017176 | 0.00010234 | 0.074599 | 0 | 0.025849 | 0.00096176 | 0.026821 | 0 | 0.0070688 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.16496 | 27.95% | CZ 4A | 0.16297 | 0.56803 | 0.010338 | 5.2793 | 0 | 0.85485 | 0.031807 | 0.887 | 0 | 0.23377 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 8.2745 | 27.95% | CZ 4A | 0.047749 | 0.16643 | 0 | 0.32176 | 0 | 0.25047 | 0.0093193 | 0.25989 | 0 | 0.068495 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 1.1963 | 27.95% | CZ 4A | 0 | 0 | 0.00010338 | 0.041811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041914 | 27.95% | CZ 4A | 0.49989 | 1.7424 | 0.011299 | 7.9385 | 0 | 2.6222 | 0.097564 | 2.7208 | 0 | 0.71708 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 17.1056 | 27.95%
CZ 4B | 0.0049278 | 0.017172 | 0.00010123 | 0.035091 | 0 | 0.014328 | 0.00011895 | 0.028765 | 0 | 0.0046253 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.11258 | 0% | CZ 4B | 0.16297 | 0.56792 | 0.010225 | 2.4009 | 0 | 0.47384 | 0.0039337 | 0.95128 | 0 | 0.15297 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 4.9705 | 0% | CZ 4B | 0.047749 | 0.1664 | 0 | 0.1631 | 0 | 0.13883 | 0.0011526 | 0.27872 | 0 | 0.044818 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 0.913 | 0% | CZ 4B | 0 | 0 | 0.00010225 | 0.018442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018545 | 0% | CZ 4B | 0.49989 | 1.742 | 0.011176 | 3.7233 | 0 | 1.4535 | 0.012066 | 2.918 | 0 | 0.4692 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 11.5851 | 0%
CZ 4C | 0.0049278 | 0.017169 | 0.00010345 | 0.059295 | 0 | 0.0037655 | -6.4571e-05 | 0.022042 | 0 | 0.0052472 | 0 | 0.0015701 | 0.0052234 | 0 | 0 | 0.0006593 | 0.11994 | 3.991% | CZ 4C | 0.16297 | 0.5678 | 0.01045 | 4.1592 | 0 | 0.12453 | -0.0021354 | 0.72897 | 0 | 0.17353 | 0 | 0.051925 | 0.17275 | 0 | 0 | 0.021804 | 6.1718 | 3.991% | CZ 4C | 0.047749 | 0.16636 | 0 | 0.26104 | 0 | 0.036487 | -0.00062568 | 0.21359 | 0 | 0.050845 | 0 | 0.015214 | 0.050614 | 0 | 0 | 0.0063884 | 0.84766 | 3.991% | CZ 4C | 0 | 0 | 0.0001045 | 0.032682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032787 | 3.991% | CZ 4C | 0.49989 | 1.7417 | 0.011422 | 6.305 | 0 | 0.38198 | -0.0065502 | 2.236 | 0 | 0.53229 | 0 | 0.15928 | 0.52988 | 0 | 0 | 0.06688 | 12.4578 | 3.991%
CZ 5A | 0.0049278 | 0.017155 | 0.00011124 | 0.12422 | 0 | 0.020398 | 0.00079864 | 0.029308 | 0 | 0.007463 | 0 | 0.0015701 | 0.0052268 | 0 | 0 | 0.0006593 | 0.21184 | 12.97% | CZ 5A | 0.16297 | 0.56735 | 0.011236 | 8.8653 | 0 | 0.67458 | 0.026412 | 0.96927 | 0 | 0.24681 | 0 | 0.051925 | 0.17286 | 0 | 0 | 0.021804 | 11.7705 | 12.97% | CZ 5A | 0.047749 | 0.16623 | 0 | 0.52521 | 0 | 0.19765 | 0.0077387 | 0.28399 | 0 | 0.072315 | 0 | 0.015214 | 0.050647 | 0 | 0 | 0.0063884 | 1.3731 | 12.97% | CZ 5A | 0 | 0 | 0.00011236 | 0.070728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07084 | 12.97% | CZ 5A | 0.49989 | 1.7403 | 0.012281 | 13.229 | 0 | 2.0692 | 0.081016 | 2.9731 | 0 | 0.75707 | 0 | 0.15928 | 0.53022 | 0 | 0 | 0.06688 | 22.1182 | 12.97%
CZ 5B | 0.0049278 | 0.017149 | 0.00011124 | 0.063544 | 0 | 0.0089413 | 3.7383e-05 | 0.032109 | 0 | 0.0054579 | 0 | 0.0015701 | 0.00522 | 0 | 0 | 0.0006593 | 0.13973 | 1.287% | CZ 5B | 0.16297 | 0.56713 | 0.011236 | 4.474 | 0 | 0.2957 | 0.0012363 | 1.0619 | 0 | 0.1805 | 0 | 0.051925 | 0.17263 | 0 | 0 | 0.021804 | 7.001 | 1.287% | CZ 5B | 0.047749 | 0.16617 | 0 | 0.27734 | 0 | 0.08664 | 0.00036224 | 0.31113 | 0 | 0.052886 | 0 | 0.015214 | 0.050581 | 0 | 0 | 0.0063884 | 1.0145 | 1.287% | CZ 5B | 0 | 0 | 0.00011236 | 0.035275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035387 | 1.287% | CZ 5B | 0.49989 | 1.7396 | 0.012281 | 6.759 | 0 | 0.90704 | 0.0037922 | 3.2572 | 0 | 0.55367 | 0 | 0.15928 | 0.52953 | 0 | 0 | 0.06688 | 14.4881 | 1.287%
CZ 5C | 0.0049278 | 0.017138 | 0.00011124 | 0.087533 | 0 | -0.008384 | -0.00042141 | 0.0082752 | 0 | 0.0037723 | 0 | 0.0015701 | 0.0052268 | 0 | 0 | 0.0006593 | 0.12041 | 0% | CZ 5C | 0.16297 | 0.56679 | 0.011236 | 6.2306 | 0 | -0.27727 | -0.013937 | 0.27367 | 0 | 0.12475 | 0 | 0.051925 | 0.17286 | 0 | 0 | 0.021804 | 7.3254 | 0% | CZ 5C | 0.047749 | 0.16607 | 0 | 0.37241 | 0 | -0.08124 | -0.0040834 | 0.080186 | 0 | 0.036553 | 0 | 0.015214 | 0.050647 | 0 | 0 | 0.0063884 | 0.68989 | 0% | CZ 5C | 0 | 0 | 0.00011236 | 0.049595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049708 | 0% | CZ 5C | 0.49989 | 1.7386 | 0.012281 | 9.3196 | 0 | -0.8505 | -0.042749 | 0.83946 | 0 | 0.38267 | 0 | 0.15928 | 0.53022 | 0 | 0 | 0.06688 | 12.6556 | 0%
CZ 6A | 0.0049278 | 0.017159 | 0.00011458 | 0.14235 | 0 | 0.0093288 | 0.0002277 | 0.02367 | 0 | 0.0059643 | 0 | 0.0015701 | 0.00522 | 0 | 0 | 0.0006593 | 0.21119 | 1.39% | CZ 6A | 0.16297 | 0.56747 | 0.011574 | 10.2034 | 0 | 0.30852 | 0.0075302 | 0.78281 | 0 | 0.19725 | 0 | 0.051925 | 0.17263 | 0 | 0 | 0.021804 | 12.4879 | 1.39% | CZ 6A | 0.047749 | 0.16627 | 0 | 0.59555 | 0 | 0.090394 | 0.0022063 | 0.22936 | 0 | 0.057793 | 0 | 0.015214 | 0.050581 | 0 | 0 | 0.0063884 | 1.2615 | 1.39% | CZ 6A | 0 | 0 | 0.00011574 | 0.081708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081824 | 1.39% | CZ 6A | 0.49989 | 1.7406 | 0.01265 | 15.1655 | 0 | 0.94634 | 0.023098 | 2.4012 | 0 | 0.60503 | 0 | 0.15928 | 0.52953 | 0 | 0 | 0.06688 | 22.15 | 1.39%
CZ 6B | 0.0049278 | 0.017145 | 0.0001168 | 0.094094 | 0 | 0.0020255 | -0.00012234 | 0.02959 | 0 | 0.0049821 | 0 | 0.0015701 | 0.0052302 | 0 | 0 | 0.0006593 | 0.16022 | 0.179% | CZ 6B | 0.16297 | 0.56702 | 0.011798 | 6.6698 | 0 | 0.066985 | -0.0040461 | 0.9786 | 0 | 0.16477 | 0 | 0.051925 | 0.17297 | 0 | 0 | 0.021804 | 8.8646 | 0.179% | CZ 6B | 0.047749 | 0.16613 | 0 | 0.40429 | 0 | 0.019627 | -0.0011855 | 0.28673 | 0 | 0.048276 | 0 | 0.015214 | 0.05068 | 0 | 0 | 0.0063884 | 1.0439 | 0.179% | CZ 6B | 0 | 0 | 0.00011798 | 0.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053018 | 0.179% | CZ 6B | 0.49989 | 1.7393 | 0.012896 | 10.0145 | 0 | 0.20547 | -0.012411 | 3.0017 | 0 | 0.5054 | 0 | 0.15928 | 0.53057 | 0 | 0 | 0.06688 | 16.7234 | 0.179%
CZ 7 | 0.0049278 | 0.017145 | 0.00012681 | 0.2046 | 0 | 8.1563e-05 | -5.7774e-05 | 0.04142 | 0 | 0.007932 | 0 | 0.0015701 | 0.0052268 | 0 | 0 | 0.0006593 | 0.28363 | 0.09387% | CZ 7 | 0.16297 | 0.56702 | 0.01281 | 14.4428 | 0 | 0.0026974 | -0.0019107 | 1.3698 | 0 | 0.26232 | 0 | 0.051925 | 0.17286 | 0 | 0 | 0.021804 | 17.0652 | 0.09387% | CZ 7 | 0.047749 | 0.16613 | 0 | 0.88767 | 0 | 0.00079033 | -0.00055982 | 0.40136 | 0 | 0.07686 | 0 | 0.015214 | 0.050647 | 0 | 0 | 0.0063884 | 1.6523 | 0.09387% | CZ 7 | 0 | 0 | 0.0001281 | 0.11413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11426 | 0.09387% | CZ 7 | 0.49989 | 1.7393 | 0.014001 | 21.7677 | 0 | 0.008274 | -0.0058607 | 4.2018 | 0 | 0.80464 | 0 | 0.15928 | 0.53022 | 0 | 0 | 0.06688 | 29.7861 | 0.09387%
CZ 8 | 0.0049278 | 0.01704 | 0.00014684 | 0.14861 | 0 | -0.0019507 | -0.00019711 | 0.024771 | 0 | 0.0052166 | 0 | 0.0015701 | 0.0052268 | 0 | 0 | 0.0006593 | 0.20602 | 0% | CZ 8 | 0.16297 | 0.56353 | 0.014832 | 9.9609 | 0 | -0.064513 | -0.0065187 | 0.81922 | 0 | 0.17252 | 0 | 0.051925 | 0.17286 | 0 | 0 | 0.021804 | 11.8696 | 0% | CZ 8 | 0.047749 | 0.16511 | 0 | 0.72032 | 0 | -0.018902 | -0.00191 | 0.24003 | 0 | 0.050548 | 0 | 0.015214 | 0.050647 | 0 | 0 | 0.0063884 | 1.2752 | 0% | CZ 8 | 0 | 0 | 0.00014832 | 0.075025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075173 | 0% | CZ 8 | 0.49989 | 1.7286 | 0.016211 | 15.7412 | 0 | -0.19789 | -0.019995 | 2.5129 | 0 | 0.52919 | 0 | 0.15928 | 0.53022 | 0 | 0 | 0.06688 | 21.5665 | 0%
Us Weighted | 0.0049278 | 0.017178 | 9.3629e-05 | 0.048865 | 0 | 0.061572 | 0.0026617 | 0.047046 | 0 | 0.0085194 | 0 | 0.0015701 | 0.0052231 | 0 | 0 | 0.0006593 | 0.19832 | 100% | Us Weighted | 0.16297 | 0.5681 | 0.0094574 | 3.4327 | 0 | 2.0363 | 0.088028 | 1.5559 | 0 | 0.28175 | 0 | 0.051925 | 0.17274 | 0 | 0 | 0.021804 | 8.3817 | 100% | Us Weighted | 0.047749 | 0.16645 | 0 | 0.21438 | 0 | 0.59662 | 0.025792 | 0.45587 | 0 | 0.082552 | 0 | 0.015214 | 0.050611 | 0 | 0 | 0.0063884 | 1.6616 | 100% | Us Weighted | 0 | 0 | 9.4574e-05 | 0.027011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027105 | 100% | Us Weighted | 0.49989 | 1.7426 | 0.010337 | 5.1966 | 0 | 6.246 | 0.27001 | 4.7725 | 0 | 0.86423 | 0 | 0.15928 | 0.52985 | 0 | 0 | 0.06688 | 20.3582 | 100%
Building Type: | High-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | High-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 84352 | [17 empty] | Prototype Floor Area: | 84352 | [17 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 5.14% | 23.68% | 0.0776% | 82.78% | 0% | 25.74% | 22.74% | 22.63% | 0% | 34.87% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.58% | 16.97% | CZ 1A | 5.14% | 23.68% | 0.0776% | 85.8% | 0% | 25.74% | 22.74% | 22.63% | 0% | 34.87% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 13.82% | 16.97% | CZ 1A | 5.14% | 23.68% | 0% | 79.58% | 0% | 25.74% | 22.74% | 22.63% | 0% | 34.87% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 16.62% | 16.97% | CZ 1A | 0% | 0% | 0.0776% | 91.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.3916% | 16.97% | CZ 1A | 5.14% | 23.68% | 0.0776% | 82.97% | 0% | 25.74% | 22.74% | 22.63% | 0% | 34.87% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.5% | 16.97%
CZ 1B | 5.14% | 23.68% | 0.08234% | 76.57% | 0% | 24.01% | 21.14% | 26.32% | 0% | 36.95% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 16.24% | 0% | CZ 1B | 5.14% | 23.68% | 0.08234% | 81.42% | 0% | 24.01% | 21.14% | 26.32% | 0% | 36.95% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 14.57% | 0% | CZ 1B | 5.14% | 23.68% | 0% | 72.64% | 0% | 24.01% | 21.14% | 26.32% | 0% | 36.95% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 17.21% | 0% | CZ 1B | 0% | 0% | 0.08234% | 94.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.5229% | 0% | CZ 1B | 5.14% | 23.68% | 0.08234% | 76.85% | 0% | 24.01% | 21.14% | 26.32% | 0% | 36.95% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 16.16% | 0%
CZ 2A | 5.14% | 23.68% | 0.08376% | 58.67% | 0% | 27.58% | 26.67% | 29.87% | 0% | 40.38% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 17.75% | 16.86% | CZ 2A | 5.14% | 23.68% | 0.08376% | 58.92% | 0% | 27.58% | 26.67% | 29.87% | 0% | 40.38% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 16.74% | 16.86% | CZ 2A | 5.14% | 23.68% | 0% | 58.19% | 0% | 27.58% | 26.67% | 29.87% | 0% | 40.38% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 18.41% | 16.86% | CZ 2A | 0% | 0% | 0.08376% | 59.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.56% | 16.86% | CZ 2A | 5.14% | 23.68% | 0.08376% | 58.69% | 0% | 27.58% | 26.67% | 29.87% | 0% | 40.38% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 17.7% | 16.86%
CZ 2B | 5.14% | 23.68% | 0.08288% | 78.96% | 0% | 28.33% | 26.38% | 32.52% | 0% | 42.16% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 18.98% | 0.8505% | CZ 2B | 5.14% | 23.68% | 0.08288% | 82.5% | 0% | 28.33% | 26.38% | 32.52% | 0% | 42.16% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 16.98% | 0.8505% | CZ 2B | 5.14% | 23.68% | 0% | 74.83% | 0% | 28.33% | 26.38% | 32.52% | 0% | 42.16% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 20.17% | 0.8505% | CZ 2B | 0% | 0% | 0.08288% | 87.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.562% | 0.8505% | CZ 2B | 5.14% | 23.68% | 0.08288% | 79.21% | 0% | 28.33% | 26.38% | 32.52% | 0% | 42.16% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 18.88% | 0.8505%
CZ 3A | 5.14% | 23.68% | 0.08072% | 16.4% | 0% | 31.64% | 28.51% | 25.3% | 0% | 38.71% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.23% | 7.27% | CZ 3A | 5.14% | 23.68% | 0.08072% | 15.76% | 0% | 31.64% | 28.51% | 25.3% | 0% | 38.71% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 13.09% | 7.27% | CZ 3A | 5.14% | 23.68% | 0% | 17.77% | 0% | 31.64% | 28.51% | 25.3% | 0% | 38.71% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 16.72% | 7.27% | CZ 3A | 0% | 0% | 0.08072% | 15.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.759% | 7.27% | CZ 3A | 5.14% | 23.68% | 0.08072% | 16.35% | 0% | 31.64% | 28.51% | 25.3% | 0% | 38.71% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.12% | 7.27%
CZ 3B | 5.14% | 23.68% | 0.08507% | -3.186% | 0% | 36.12% | 31.46% | 25.88% | 0% | 38.01% | 0% | 2.834% | 42.46% | 0% | 0% | 0.1991% | 16.17% | 8.26% | CZ 3B | 5.14% | 23.68% | 0.08507% | -8.964% | 0% | 36.12% | 31.46% | 25.88% | 0% | 38.01% | 0% | 2.834% | 42.46% | 0% | 0% | 0.1991% | 13.49% | 8.26% | CZ 3B | 5.14% | 23.68% | 0% | 4.647% | 0% | 36.12% | 31.46% | 25.88% | 0% | 38.01% | 0% | 2.834% | 42.46% | 0% | 0% | 0.1991% | 17.88% | 8.26% | CZ 3B | 0% | 0% | 0.08507% | -16.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.7329% | 8.26% | CZ 3B | 5.14% | 23.68% | 0.08507% | -3.609% | 0% | 36.12% | 31.46% | 25.88% | 0% | 38.01% | 0% | 2.834% | 42.46% | 0% | 0% | 0.1991% | 16.04% | 8.26%
CZ 3C | 5.14% | 23.68% | 0.08221% | 29.91% | 0% | 85.38% | 84.46% | 46.16% | 0% | 59.49% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 20.08% | 1.931% | CZ 3C | 5.14% | 23.68% | 0.08221% | 22.32% | 0% | 85.38% | 84.46% | 46.16% | 0% | 59.49% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 16.12% | 1.931% | CZ 3C | 5.14% | 23.68% | 0% | 39.24% | 0% | 85.38% | 84.46% | 46.16% | 0% | 59.49% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 22.86% | 1.931% | CZ 3C | 0% | 0% | 0.08221% | 11.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.8056% | 1.931% | CZ 3C | 5.14% | 23.68% | 0.08221% | 29.38% | 0% | 85.38% | 84.46% | 46.16% | 0% | 59.49% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 19.87% | 1.931%
CZ 4A | 5.14% | 23.68% | 0.08312% | 45.51% | 0% | 15.68% | 12.36% | 12.11% | 0% | 28.3% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 12.95% | 27.95% | CZ 4A | 5.14% | 23.68% | 0.08312% | 46.22% | 0% | 15.68% | 12.36% | 12.11% | 0% | 28.3% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 14.65% | 27.95% | CZ 4A | 5.14% | 23.68% | 0% | 43.94% | 0% | 15.68% | 12.36% | 12.11% | 0% | 28.3% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 11.63% | 27.95% | CZ 4A | 0% | 0% | 0.08312% | 46.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.62% | 27.95% | CZ 4A | 5.14% | 23.68% | 0.08312% | 45.57% | 0% | 15.68% | 12.36% | 12.11% | 0% | 28.3% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 13.05% | 27.95%
CZ 4B | 5.14% | 23.68% | 0.0834% | 61.7% | 0% | 8.672% | 2.028% | 11.25% | 0% | 24.68% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 9.452% | 0% | CZ 4B | 5.14% | 23.68% | 0.0834% | 63.89% | 0% | 8.672% | 2.028% | 11.25% | 0% | 24.68% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 10.04% | 0% | CZ 4B | 5.14% | 23.68% | 0% | 57.56% | 0% | 8.672% | 2.028% | 11.25% | 0% | 24.68% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 9.042% | 0% | CZ 4B | 0% | 0% | 0.0834% | 66.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.32% | 0% | CZ 4B | 5.14% | 23.68% | 0.0834% | 61.88% | 0% | 8.672% | 2.028% | 11.25% | 0% | 24.68% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 9.483% | 0%
CZ 4C | 5.14% | 23.68% | 0.08084% | 50.12% | 0% | 4.92% | -2.063% | 9.68% | 0% | 25.11% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 10.51% | 3.991% | CZ 4C | 5.14% | 23.68% | 0.08084% | 51.06% | 0% | 4.92% | -2.063% | 9.68% | 0% | 25.11% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 12.18% | 3.991% | CZ 4C | 5.14% | 23.68% | 0% | 48.11% | 0% | 4.92% | -2.063% | 9.68% | 0% | 25.11% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 9.195% | 3.991% | CZ 4C | 0% | 0% | 0.08084% | 51.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.06% | 3.991% | CZ 4C | 5.14% | 23.68% | 0.08084% | 50.2% | 0% | 4.92% | -2.063% | 9.68% | 0% | 25.11% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 10.6% | 3.991%
CZ 5A | 5.14% | 23.68% | 0.08483% | 41.58% | 0% | 15.92% | 13.29% | 12.97% | 0% | 29.12% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 15.32% | 12.97% | CZ 5A | 5.14% | 23.68% | 0.08483% | 42.05% | 0% | 15.92% | 13.29% | 12.97% | 0% | 29.12% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 17.88% | 12.97% | CZ 5A | 5.14% | 23.68% | 0% | 40.48% | 0% | 15.92% | 13.29% | 12.97% | 0% | 29.12% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 13.04% | 12.97% | CZ 5A | 0% | 0% | 0.08483% | 42.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 23.69% | 12.97% | CZ 5A | 5.14% | 23.68% | 0.08483% | 41.62% | 0% | 15.92% | 13.29% | 12.97% | 0% | 29.12% | 0% | 2.834% | 42.51% | 0% | 0% | 0.1991% | 15.48% | 12.97%
CZ 5B | 5.14% | 23.68% | 0.08576% | 48.06% | 0% | 7.627% | 0.8994% | 12.37% | 0% | 25.8% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 11.35% | 1.287% | CZ 5B | 5.14% | 23.68% | 0.08576% | 48.99% | 0% | 7.627% | 0.8994% | 12.37% | 0% | 25.8% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 12.9% | 1.287% | CZ 5B | 5.14% | 23.68% | 0% | 46.04% | 0% | 7.627% | 0.8994% | 12.37% | 0% | 25.8% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 10.15% | 1.287% | CZ 5B | 0% | 0% | 0.08576% | 49.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.54% | 1.287% | CZ 5B | 5.14% | 23.68% | 0.08576% | 48.14% | 0% | 7.627% | 0.8994% | 12.37% | 0% | 25.8% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 11.44% | 1.287%
CZ 5C | 5.14% | 23.68% | 0.08476% | 48.07% | 0% | -27.78% | -32.55% | 4.396% | 0% | 21.25% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 10.77% | 0% | CZ 5C | 5.14% | 23.68% | 0.08476% | 48.88% | 0% | -27.78% | -32.55% | 4.396% | 0% | 21.25% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 13.92% | 0% | CZ 5C | 5.14% | 23.68% | 0% | 46.26% | 0% | -27.78% | -32.55% | 4.396% | 0% | 21.25% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 8.021% | 0% | CZ 5C | 0% | 0% | 0.08476% | 49.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.37% | 0% | CZ 5C | 5.14% | 23.68% | 0.08476% | 48.14% | 0% | -27.78% | -32.55% | 4.396% | 0% | 21.25% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 10.96% | 0%
CZ 6A | 5.14% | 23.68% | 0.08287% | 41.31% | 0% | 12.28% | 6.768% | 11.26% | 0% | 27.02% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 15.51% | 1.39% | CZ 6A | 5.14% | 23.68% | 0.08287% | 41.69% | 0% | 12.28% | 6.768% | 11.26% | 0% | 27.02% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 18.5% | 1.39% | CZ 6A | 5.14% | 23.68% | 0% | 40.43% | 0% | 12.28% | 6.768% | 11.26% | 0% | 27.02% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 12.63% | 1.39% | CZ 6A | 0% | 0% | 0.08287% | 42.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.49% | 1.39% | CZ 6A | 5.14% | 23.68% | 0.08287% | 41.35% | 0% | 12.28% | 6.768% | 11.26% | 0% | 27.02% | 0% | 2.834% | 42.47% | 0% | 0% | 0.1991% | 15.7% | 1.39%
CZ 6B | 5.14% | 23.68% | 0.08385% | 45.65% | 0% | 2.652% | -4.439% | 11.57% | 0% | 25.35% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 12.64% | 0.179% | CZ 6B | 5.14% | 23.68% | 0.08385% | 46.23% | 0% | 2.652% | -4.439% | 11.57% | 0% | 25.35% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 15.03% | 0.179% | CZ 6B | 5.14% | 23.68% | 0% | 44.35% | 0% | 2.652% | -4.439% | 11.57% | 0% | 25.35% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 10.61% | 0.179% | CZ 6B | 0% | 0% | 0.08385% | 46.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.88% | 0.179% | CZ 6B | 5.14% | 23.68% | 0.08385% | 45.7% | 0% | 2.652% | -4.439% | 11.57% | 0% | 25.35% | 0% | 2.834% | 42.54% | 0% | 0% | 0.1991% | 12.79% | 0.179%
CZ 7 | 5.14% | 23.68% | 0.08481% | 43.13% | 0% | 0.1451% | -2.313% | 16.9% | 0% | 31.69% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 18.66% | 0.09387% | CZ 7 | 5.14% | 23.68% | 0.08481% | 43.05% | 0% | 0.1451% | -2.313% | 16.9% | 0% | 31.69% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 21.8% | 0.09387% | CZ 7 | 5.14% | 23.68% | 0% | 43.34% | 0% | 0.1451% | -2.313% | 16.9% | 0% | 31.69% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 15.4% | 0.09387% | CZ 7 | 0% | 0% | 0.08481% | 42.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.42% | 0.09387% | CZ 7 | 5.14% | 23.68% | 0.08481% | 43.13% | 0% | 0.1451% | -2.313% | 16.9% | 0% | 31.69% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 18.87% | 0.09387%
CZ 8 | 5.14% | 23.68% | 0.08985% | 28.52% | 0% | -3.865% | -10.16% | 9.605% | 0% | 24.43% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 13.02% | 0% | CZ 8 | 5.14% | 23.68% | 0.08985% | 27.5% | 0% | -3.865% | -10.16% | 9.605% | 0% | 24.43% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 14.4% | 0% | CZ 8 | 5.14% | 23.68% | 0% | 30.75% | 0% | -3.865% | -10.16% | 9.605% | 0% | 24.43% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 11.54% | 0% | CZ 8 | 0% | 0% | 0.08985% | 26.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 16.81% | 0% | CZ 8 | 5.14% | 23.68% | 0.08985% | 28.43% | 0% | -3.865% | -10.16% | 9.605% | 0% | 24.43% | 0% | 2.834% | 42.5% | 0% | 0% | 0.1991% | 13.11% | 0%
Us Weighted | 5.14% | 23.68% | 0.08263% | 42.89% | 0% | 24.74% | 21.98% | 20.19% | 0% | 33.74% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.1% | 100% | Us Weighted | 5.14% | 23.68% | 0.08263% | 43.35% | 0% | 24.74% | 21.98% | 20.19% | 0% | 33.74% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.16% | 100% | Us Weighted | 5.14% | 23.68% | 0% | 41.88% | 0% | 24.74% | 21.98% | 20.19% | 0% | 33.74% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.05% | 100% | Us Weighted | 0% | 0% | 0.08263% | 43.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.39% | 100% | Us Weighted | 5.14% | 23.68% | 0.08263% | 42.93% | 0% | 24.74% | 21.98% | 20.19% | 0% | 33.74% | 0% | 2.834% | 42.49% | 0% | 0% | 0.1991% | 15.1% | 100%

## MidApartment
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Mid-rise Apartment | [14 empty] | Prototype Floor Area: | 33741 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.094052 | 0.03408 | 0.32239 | 0.048911 | 0 | 0.12063 | 0 | 0.17132 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2256 |  | STD2013 | 3.1104 | 1.1271 | 10.6619 | 4.9405 | 0 | 3.9893 | 0 | 5.6659 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.8555 |  | STD2013 | 0.91135 | 0.33023 | 3.1239 | 0 | 0 | 1.1688 | 0 | 1.6601 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.402 |  | STD2013 | 0 | 0 | 0 | 0.049405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049405 |  | STD2013 | 9.5409 | 3.4572 | 32.7041 | 5.3999 | 0 | 12.2366 | 0 | 17.3795 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 124.7674
STD2010 | 0.11436 | 0.03408 | 0.32261 | 0.053639 | 0 | 0.14794 | 0 | 0.18395 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2911 |  | STD2010 | 3.782 | 1.1271 | 10.6692 | 5.418 | 0 | 4.8927 | 0 | 6.0835 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 46.3422 |  | STD2010 | 1.1081 | 0.33023 | 3.126 | 0 | 0 | 1.4336 | 0 | 1.7825 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.9907 |  | STD2010 | 0 | 0 | 0 | 0.05418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05418 |  | STD2010 | 11.6007 | 3.4572 | 32.7265 | 5.9219 | 0 | 15.0079 | 0 | 18.6605 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 131.4524
STD2007 | 0.10283 | 0.061966 | 0.32269 | 0.069956 | 0 | 0.14966 | 0 | 0.19821 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3451 |  | STD2007 | 3.4007 | 2.0493 | 10.672 | 7.0663 | 0 | 4.9494 | 0 | 6.555 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.2374 |  | STD2007 | 0.99639 | 0.60044 | 3.1269 | 0 | 0 | 1.4502 | 0 | 1.9206 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.356 |  | STD2007 | 0 | 0 | 0 | 0.070663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070663 |  | STD2007 | 10.4312 | 6.286 | 32.7351 | 7.7235 | 0 | 15.1818 | 0 | 20.1066 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 137.0787
STD2004 | 0.10283 | 0.061966 | 0.32273 | 0.079533 | 0 | 0.19094 | 0 | 0.21474 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4125 |  | STD2004 | 3.4007 | 2.0493 | 10.673 | 8.0336 | 0 | 6.3147 | 0 | 7.1016 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 52.1177 |  | STD2004 | 0.99639 | 0.60044 | 3.1272 | 0 | 0 | 1.8502 | 0 | 2.0808 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.9165 |  | STD2004 | 0 | 0 | 0 | 0.080336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080336 |  | STD2004 | 10.4312 | 6.286 | 32.7382 | 8.7807 | 0 | 19.3696 | 0 | 21.7834 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.0037
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 3.0695e-05 | 0.0095765 | 0 | 0.041282 | 0 | 0.016529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067419 |  | 2004-2007 | 0 | 0 | 0.0010151 | 0.96733 | 0 | 1.3653 | 0 | 0.54664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8803 |  | 2004-2007 | 0 | 0 | 0.00029743 | 0 | 0 | 0.40002 | 0 | 0.16016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56048 |  | 2004-2007 | 0 | 0 | 0 | 0.0096733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096733 |  | 2004-2007 | 0 | 0 | 0.0031138 | 1.0573 | 0 | 4.1878 | 0 | 1.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.925
2007-2010 | -0.011529 | 0.027886 | 8.5042e-05 | 0.016318 | 0 | 0.0017138 | 0 | 0.014255 | 0 | 0 | 0 | 0.0036448 | 0 | 0 | 0 | 0.0016482 | 0.054022 |  | 2007-2010 | -0.38129 | 0.92223 | 0.0028125 | 1.6482 | 0 | 0.056677 | 0 | 0.47145 | 0 | 0 | 0 | 0.12054 | 0 | 0 | 0 | 0.054509 | 2.8952 |  | 2007-2010 | -0.11172 | 0.27021 | 0.00082404 | 0 | 0 | 0.016606 | 0 | 0.13813 | 0 | 0 | 0 | 0.035318 | 0 | 0 | 0 | 0.015971 | 0.36535 |  | 2007-2010 | 0 | 0 | 0 | 0.016482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016482 |  | 2007-2010 | -1.1696 | 2.8288 | 0.0086269 | 1.8015 | 0 | 0.17385 | 0 | 1.4461 | 0 | 0 | 0 | 0.36974 | 0 | 0 | 0 | 0.1672 | 5.6263
2010-2013 | 0.020306 | 0 | 0.00022036 | 0.0047281 | 0 | 0.027319 | 0 | 0.012628 | 0 | 0 | 0 | 0.00028037 | 0 | 0 | 0 | 0 | 0.065481 |  | 2010-2013 | 0.67154 | 0 | 0.0072876 | 0.47758 | 0 | 0.90347 | 0 | 0.41762 | 0 | 0 | 0 | 0.0092723 | 0 | 0 | 0 | -8.3973e-08 | 2.4868 |  | 2010-2013 | 0.19676 | 0 | 0.0021352 | 0 | 0 | 0.26471 | 0 | 0.12236 | 0 | 0 | 0 | 0.0027168 | 0 | 0 | 0 | -2.4604e-08 | 0.58869 |  | 2010-2013 | 0 | 0 | 0 | 0.0047758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047758 |  | 2010-2013 | 2.0599 | 0 | 0.022354 | 0.522 | 0 | 2.7713 | 0 | 1.281 | 0 | 0 | 0 | 0.028442 | 0 | 0 | 0 | -2.5758e-07 | 6.685
2004-2013 | 0.0087765 | 0.027886 | 0.0003361 | 0.030622 | 0 | 0.070315 | 0 | 0.043413 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.18692 |  | 2004-2013 | 0.29025 | 0.92223 | 0.011115 | 3.0932 | 0 | 2.3254 | 0 | 1.4357 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.2622 |  | 2004-2013 | 0.085042 | 0.27021 | 0.0032567 | 0 | 0 | 0.68134 | 0 | 0.42066 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.5145 |  | 2004-2013 | 0 | 0 | 0 | 0.030932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030932 |  | 2004-2013 | 0.89031 | 2.8288 | 0.034095 | 3.3808 | 0 | 7.133 | 0 | 4.4039 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 19.2363
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.009511% | 12.04% |  | 21.62% |  | 7.697% |  |  |  | 0% |  |  |  | 0% | 4.773% |  | 2004-2007 | 0% | 0% | 0.009511% | 12.04% |  | 21.62% |  | 7.697% |  |  |  | 0% |  |  |  | 0% | 5.526% |  | 2004-2007 | 0% | 0% | 0.009511% |  |  | 21.62% |  | 7.697% |  |  |  | 0% |  |  |  | 0% | 4.339% |  | 2004-2007 |  |  |  | 12.04% | [12 empty] | 12.04% |  | 2004-2007 | 0% | 0% | 0.009511% | 12.04% |  | 21.62% |  | 7.697% |  |  |  | 0% |  |  |  | 0% | 4.809%
2007-2010 | -11.21% | 45% | 0.02635% | 23.33% |  | 1.145% |  | 7.192% |  |  |  | 3.311% |  |  |  | 0.4999% | 4.016% |  | 2007-2010 | -11.21% | 45% | 0.02635% | 23.33% |  | 1.145% |  | 7.192% |  |  |  | 3.311% |  |  |  | 0.4999% | 5.88% |  | 2007-2010 | -11.21% | 45% | 0.02635% |  |  | 1.145% |  | 7.192% |  |  |  | 3.311% |  |  |  | 0.4999% | 2.957% |  | 2007-2010 |  |  |  | 23.33% | [12 empty] | 23.33% |  | 2007-2010 | -11.21% | 45% | 0.02635% | 23.33% |  | 1.145% |  | 7.192% |  |  |  | 3.311% |  |  |  | 0.4999% | 4.104%
2010-2013 | 17.76% | 0% | 0.06831% | 8.815% |  | 18.47% |  | 6.865% |  |  |  | 0.2634% |  |  |  | 0% | 5.072% |  | 2010-2013 | 17.76% | 0% | 0.06831% | 8.815% |  | 18.47% |  | 6.865% |  |  |  | 0.2634% |  |  |  | -7.74e-07% | 5.366% |  | 2010-2013 | 17.76% | 0% | 0.06831% |  |  | 18.47% |  | 6.865% |  |  |  | 0.2634% |  |  |  | -7.74e-07% | 4.91% |  | 2010-2013 |  |  |  | 8.815% | [12 empty] | 8.815% |  | 2010-2013 | 17.76% | 0% | 0.06831% | 8.815% |  | 18.47% |  | 6.865% |  |  |  | 0.2634% |  |  |  | -7.74e-07% | 5.085%
2004-2013 | 8.535% | 45% | 0.1041% | 38.5% |  | 36.83% |  | 20.22% |  |  |  | 3.565% |  |  |  | 0.4999% | 13.23% |  | 2004-2013 | 8.535% | 45% | 0.1041% | 38.5% |  | 36.83% |  | 20.22% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.85% |  | 2004-2013 | 8.535% | 45% | 0.1041% |  |  | 36.83% |  | 20.22% |  |  |  | 3.565% |  |  |  | 0.4999% | 11.73% |  | 2004-2013 |  |  |  | 38.5% | [12 empty] | 38.5% |  | 2004-2013 | 8.535% | 45% | 0.1041% | 38.5% |  | 36.83% |  | 20.22% |  |  |  | 3.565% |  |  |  | 0.4999% | 13.36%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.094052 | 0.034146 | 0.2552 | 0.00014739 | 0 | 0.27504 | 0 | 0.16718 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.26 | 3.509% | CZ 1A | 3.1104 | 1.1292 | 8.4397 | 0.014888 | 0 | 9.0961 | 0 | 5.5288 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.6797 | 3.509% | CZ 1A | 0.91135 | 0.33087 | 2.4728 | 0 | 0 | 2.6651 | 0 | 1.6199 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 12.2077 | 3.509% | CZ 1A | 0 | 0 | 0 | 0.00014888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014888 | 3.509% | CZ 1A | 9.5409 | 3.4638 | 25.8879 | 0.016273 | 0 | 27.9013 | 0 | 16.959 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 127.8184 | 3.509%
CZ 1B | 0.094052 | 0.034112 | 0.24312 | 0.00071194 | 0 | 0.2796 | 0 | 0.23377 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.3196 | 0% | CZ 1B | 3.1104 | 1.1281 | 8.0405 | 0.071913 | 0 | 9.2467 | 0 | 7.7311 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.6892 | 0% | CZ 1B | 0.91135 | 0.33054 | 2.3558 | 0 | 0 | 2.7093 | 0 | 2.2652 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 12.7798 | 0% | CZ 1B | 0 | 0 | 0 | 0.00071913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071913 | 0% | CZ 1B | 9.5409 | 3.4604 | 24.6632 | 0.078601 | 0 | 28.3632 | 0 | 23.7143 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 133.8698 | 0%
CZ 2A | 0.094052 | 0.034086 | 0.28424 | 0.010826 | 0 | 0.18523 | 0 | 0.16078 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2034 | 14.94% | CZ 2A | 3.1104 | 1.1273 | 9.4001 | 1.0936 | 0 | 6.1259 | 0 | 5.3172 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.535 | 14.94% | CZ 2A | 0.91135 | 0.33029 | 2.7542 | 0 | 0 | 1.7949 | 0 | 1.5579 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.5562 | 14.94% | CZ 2A | 0 | 0 | 0 | 0.010936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010936 | 14.94% | CZ 2A | 9.5409 | 3.4578 | 28.8338 | 1.1953 | 0 | 18.7904 | 0 | 16.31 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 122.1774 | 14.94%
CZ 2B | 0.094052 | 0.034061 | 0.26747 | 0.0022665 | 0 | 0.23455 | 0 | 0.20541 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.272 | 1.276% | CZ 2B | 3.1104 | 1.1264 | 8.8457 | 0.22894 | 0 | 7.757 | 0 | 6.7932 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.2222 | 1.276% | CZ 2B | 0.91135 | 0.33004 | 2.5918 | 0 | 0 | 2.2728 | 0 | 1.9904 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 12.3039 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0022894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022894 | 1.276% | CZ 2B | 9.5409 | 3.4552 | 27.1333 | 0.25023 | 0 | 23.7936 | 0 | 20.8374 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 129.0599 | 1.276%
CZ 3A | 0.094052 | 0.034103 | 0.30699 | 0.043203 | 0 | 0.14071 | 0 | 0.16019 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2135 | 11.27% | CZ 3A | 3.1104 | 1.1278 | 10.1526 | 4.3639 | 0 | 4.6536 | 0 | 5.2978 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.0666 | 11.27% | CZ 3A | 0.91135 | 0.33046 | 2.9747 | 0 | 0 | 1.3635 | 0 | 1.5523 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.3398 | 11.27% | CZ 3A | 0 | 0 | 0 | 0.043639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043639 | 11.27% | CZ 3A | 9.5409 | 3.4595 | 31.1419 | 4.7698 | 0 | 14.2743 | 0 | 16.2505 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 123.4861 | 11.27%
CZ 3B | 0.094052 | 0.034112 | 0.29933 | 0.011269 | 0 | 0.13191 | 0 | 0.18526 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.1902 | 11.78% | CZ 3B | 3.1104 | 1.1281 | 9.8994 | 1.1382 | 0 | 4.3625 | 0 | 6.1267 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 40.1259 | 11.78% | CZ 3B | 0.91135 | 0.33054 | 2.9005 | 0 | 0 | 1.2782 | 0 | 1.7951 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.4233 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.011382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011382 | 11.78% | CZ 3B | 9.5409 | 3.4604 | 30.3653 | 1.2441 | 0 | 13.3814 | 0 | 18.793 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 120.8343 | 11.78%
CZ 3C | 0.094052 | 0.034061 | 0.33142 | 0.010181 | 0 | 0.021487 | 0 | 0.13205 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.0575 | 3.558% | CZ 3C | 3.1104 | 1.1264 | 10.9604 | 1.0284 | 0 | 0.71059 | 0 | 4.3672 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 35.664 | 3.558% | CZ 3C | 0.91135 | 0.33004 | 3.2114 | 0 | 0 | 0.2082 | 0 | 1.2796 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 10.1481 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.010284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010284 | 3.558% | CZ 3C | 9.5409 | 3.4552 | 33.6198 | 1.1241 | 0 | 2.1797 | 0 | 13.396 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 107.3648 | 3.558%
CZ 4A | 0.094052 | 0.034086 | 0.33453 | 0.057411 | 0 | 0.10775 | 0 | 0.17302 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2351 | 23.14% | CZ 4A | 3.1104 | 1.1273 | 11.0632 | 5.7991 | 0 | 3.5634 | 0 | 5.7221 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.746 | 23.14% | CZ 4A | 0.91135 | 0.33029 | 3.2415 | 0 | 0 | 1.0441 | 0 | 1.6766 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.4113 | 23.14% | CZ 4A | 0 | 0 | 0 | 0.057991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057991 | 23.14% | CZ 4A | 9.5409 | 3.4578 | 33.9352 | 6.3384 | 0 | 10.9302 | 0 | 17.5519 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 125.8037 | 23.14%
CZ 4B | 0.094052 | 0.034078 | 0.33002 | 0.020134 | 0 | 0.11468 | 0 | 0.20335 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2305 | 0.2995% | CZ 4B | 3.1104 | 1.127 | 10.9143 | 2.0338 | 0 | 3.7926 | 0 | 6.7249 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.0636 | 0.2995% | CZ 4B | 0.91135 | 0.33021 | 3.1979 | 0 | 0 | 1.1112 | 0 | 1.9704 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.7286 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.020338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020338 | 0.2995% | CZ 4B | 9.5409 | 3.457 | 33.4784 | 2.2229 | 0 | 11.6335 | 0 | 20.628 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 125.0098 | 0.2995%
CZ 4C | 0.094052 | 0.034069 | 0.34623 | 0.039699 | 0 | 0.059524 | 0 | 0.17787 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.1857 | 5.067% | CZ 4C | 3.1104 | 1.1267 | 11.4504 | 4.01 | 0 | 1.9685 | 0 | 5.8823 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 41.9088 | 5.067% | CZ 4C | 0.91135 | 0.33013 | 3.3549 | 0 | 0 | 0.57677 | 0 | 1.7235 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.1043 | 5.067% | CZ 4C | 0 | 0 | 0 | 0.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0401 | 5.067% | CZ 4C | 9.5409 | 3.4561 | 35.1228 | 4.3829 | 0 | 6.0382 | 0 | 18.0432 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 120.6334 | 5.067%
CZ 5A | 0.094052 | 0.034044 | 0.3539 | 0.10751 | 0 | 0.085649 | 0 | 0.17425 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2836 | 15.32% | CZ 5A | 3.1104 | 1.1259 | 11.7038 | 10.8594 | 0 | 2.8325 | 0 | 5.7629 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 49.7554 | 15.32% | CZ 5A | 0.91135 | 0.32988 | 3.4292 | 0 | 0 | 0.82993 | 0 | 1.6885 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.3964 | 15.32% | CZ 5A | 0 | 0 | 0 | 0.10859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10859 | 15.32% | CZ 5A | 9.5409 | 3.4535 | 35.9003 | 11.8693 | 0 | 8.6885 | 0 | 17.6769 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 131.1786 | 15.32%
CZ 5B | 0.094052 | 0.034035 | 0.35029 | 0.048256 | 0 | 0.08299 | 0 | 0.19766 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2415 | 4.35% | CZ 5B | 3.1104 | 1.1256 | 11.5847 | 4.8743 | 0 | 2.7446 | 0 | 6.5369 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 44.3371 | 4.35% | CZ 5B | 0.91135 | 0.3298 | 3.3943 | 0 | 0 | 0.80416 | 0 | 1.9153 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.5625 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.048743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048743 | 4.35% | CZ 5B | 9.5409 | 3.4526 | 35.5348 | 5.3277 | 0 | 8.4187 | 0 | 20.0514 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 126.3753 | 4.35%
CZ 5C | 0.094052 | 0.03401 | 0.35432 | 0.061327 | 0 | 0.036015 | 0 | 0.15513 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.1691 | 0% | CZ 5C | 3.1104 | 1.1248 | 11.7179 | 6.1946 | 0 | 1.1911 | 0 | 5.1304 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 42.8296 | 0% | CZ 5C | 0.91135 | 0.32955 | 3.4333 | 0 | 0 | 0.34898 | 0 | 1.5032 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 10.734 | 0% | CZ 5C | 0 | 0 | 0 | 0.061946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061946 | 0% | CZ 5C | 9.5409 | 3.4501 | 35.9433 | 6.7707 | 0 | 3.6535 | 0 | 15.7368 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 119.1445 | 0%
CZ 6A | 0.094052 | 0.034052 | 0.37098 | 0.12643 | 0 | 0.05779 | 0 | 0.16378 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2813 | 4.28% | CZ 6A | 3.1104 | 1.1262 | 12.2689 | 12.771 | 0 | 1.9112 | 0 | 5.4164 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 50.9646 | 4.28% | CZ 6A | 0.91135 | 0.32996 | 3.5948 | 0 | 0 | 0.55998 | 0 | 1.587 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.1906 | 4.28% | CZ 6A | 0 | 0 | 0 | 0.12771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12771 | 4.28% | CZ 6A | 9.5409 | 3.4544 | 37.6335 | 13.9587 | 0 | 5.8624 | 0 | 16.6142 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 131.1133 | 4.28%
CZ 6B | 0.094052 | 0.034027 | 0.37339 | 0.078536 | 0 | 0.058632 | 0 | 0.19723 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2701 | 0.7689% | CZ 6B | 3.1104 | 1.1253 | 12.3487 | 7.9329 | 0 | 1.939 | 0 | 6.5226 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 47.3395 | 0.7689% | CZ 6B | 0.91135 | 0.32971 | 3.6181 | 0 | 0 | 0.56813 | 0 | 1.9111 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.546 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.079329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079329 | 0.7689% | CZ 6B | 9.5409 | 3.4518 | 37.8782 | 8.6706 | 0 | 5.9478 | 0 | 20.0074 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 129.5459 | 0.7689%
CZ 7 | 0.094052 | 0.034027 | 0.39797 | 0.17061 | 0 | 0.045429 | 0 | 0.17228 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.3486 | 0.4435% | CZ 7 | 3.1104 | 1.1253 | 13.1616 | 17.233 | 0 | 1.5024 | 0 | 5.6977 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 56.1908 | 0.4435% | CZ 7 | 0.91135 | 0.32971 | 3.8563 | 0 | 0 | 0.4402 | 0 | 1.6694 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.4145 | 0.4435% | CZ 7 | 0 | 0 | 0 | 0.17233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17233 | 0.4435% | CZ 7 | 9.5409 | 3.4518 | 40.3716 | 18.8356 | 0 | 4.6084 | 0 | 17.477 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 138.3345 | 0.4435%
CZ 8 | 0.094052 | 0.033814 | 0.43124 | 0.2499 | 0 | 0.037748 | 0 | 0.18413 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.4651 | 0% | CZ 8 | 3.1104 | 1.1183 | 14.2616 | 25.2428 | 0 | 1.2484 | 0 | 6.0893 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 65.4313 | 0% | CZ 8 | 0.91135 | 0.32766 | 4.1786 | 0 | 0 | 0.36577 | 0 | 1.7842 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.7751 | 0% | CZ 8 | 0 | 0 | 0 | 0.25243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25243 | 0% | CZ 8 | 9.5409 | 3.4302 | 43.7458 | 27.5904 | 0 | 3.8293 | 0 | 18.6784 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 150.8643 | 0%
Us Weighted | 0.094052 | 0.03408 | 0.32239 | 0.048911 | 0 | 0.12063 | 0 | 0.17132 | 0 | 0 | 0 | 0.10617 | 0 | 0 | 0 | 0.32806 | 1.2256 | 100% | Us Weighted | 3.1104 | 1.1271 | 10.6619 | 4.9405 | 0 | 3.9893 | 0 | 5.6659 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8494 | 43.8555 | 100% | Us Weighted | 0.91135 | 0.33023 | 3.1239 | 0 | 0 | 1.1688 | 0 | 1.6601 | 0 | 0 | 0 | 1.0288 | 0 | 0 | 0 | 3.1788 | 11.402 | 100% | Us Weighted | 0 | 0 | 0 | 0.049405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049405 | 100% | Us Weighted | 9.5409 | 3.4572 | 32.7041 | 5.3999 | 0 | 12.2366 | 0 | 17.3795 | 0 | 0 | 0 | 10.77 | 0 | 0 | 0 | 33.2792 | 124.7674 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.11436 | 0.034146 | 0.25553 | 0.00026976 | 0 | 0.34052 | 0 | 0.19059 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3699 | 3.509% | CZ 1A | 3.782 | 1.1292 | 8.4507 | 0.027248 | 0 | 11.2616 | 0 | 6.3032 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 45.3237 | 3.509% | CZ 1A | 1.1081 | 0.33087 | 2.476 | 0 | 0 | 3.2996 | 0 | 1.8468 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 13.2717 | 3.509% | CZ 1A | 0 | 0 | 0 | 0.00027248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00027248 | 3.509% | CZ 1A | 11.6007 | 3.4638 | 25.9215 | 0.029782 | 0 | 34.5437 | 0 | 19.3343 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 138.9715 | 3.509%
CZ 1B | 0.11436 | 0.034112 | 0.24333 | 0.0011402 | 0 | 0.33752 | 0 | 0.26963 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.4346 | 0% | CZ 1B | 3.782 | 1.1281 | 8.0472 | 0.11517 | 0 | 11.1624 | 0 | 8.9171 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 47.5217 | 0% | CZ 1B | 1.1081 | 0.33054 | 2.3578 | 0 | 0 | 3.2706 | 0 | 2.6127 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 13.89 | 0% | CZ 1B | 0 | 0 | 0 | 0.0011517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011517 | 0% | CZ 1B | 11.6007 | 3.4604 | 24.6839 | 0.12588 | 0 | 34.2394 | 0 | 27.3522 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 145.5403 | 0%
CZ 2A | 0.11436 | 0.034086 | 0.28446 | 0.011842 | 0 | 0.23216 | 0 | 0.18446 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2959 | 14.94% | CZ 2A | 3.782 | 1.1273 | 9.4074 | 1.1961 | 0 | 7.6777 | 0 | 6.1003 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 43.6606 | 14.94% | CZ 2A | 1.1081 | 0.33029 | 2.7563 | 0 | 0 | 2.2496 | 0 | 1.7874 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 12.442 | 14.94% | CZ 2A | 0 | 0 | 0 | 0.011961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011961 | 14.94% | CZ 2A | 11.6007 | 3.4578 | 28.8562 | 1.3074 | 0 | 23.5505 | 0 | 18.712 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 131.5623 | 14.94%
CZ 2B | 0.11436 | 0.034061 | 0.26766 | 0.0026892 | 0 | 0.28471 | 0 | 0.23626 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3742 | 1.276% | CZ 2B | 3.782 | 1.1264 | 8.8519 | 0.27164 | 0 | 9.4158 | 0 | 7.8134 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 45.631 | 1.276% | CZ 2B | 1.1081 | 0.33004 | 2.5936 | 0 | 0 | 2.7588 | 0 | 2.2893 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 13.2902 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0027164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027164 | 1.276% | CZ 2B | 11.6007 | 3.4552 | 27.1523 | 0.2969 | 0 | 28.8821 | 0 | 23.9668 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 139.4317 | 1.276%
CZ 3A | 0.11436 | 0.034103 | 0.30713 | 0.038831 | 0 | 0.17409 | 0 | 0.17154 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2746 | 11.27% | CZ 3A | 3.782 | 1.1278 | 10.1573 | 3.9223 | 0 | 5.7575 | 0 | 5.6732 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.79 | 11.27% | CZ 3A | 1.1081 | 0.33046 | 2.9761 | 0 | 0 | 1.6869 | 0 | 1.6622 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.9741 | 11.27% | CZ 3A | 0 | 0 | 0 | 0.039223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039223 | 11.27% | CZ 3A | 11.6007 | 3.4595 | 31.1565 | 4.2871 | 0 | 17.6605 | 0 | 17.402 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 129.6441 | 11.27%
CZ 3B | 0.11436 | 0.034112 | 0.29947 | 0.0095861 | 0 | 0.16281 | 0 | 0.19813 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.253 | 11.78% | CZ 3B | 3.782 | 1.1281 | 9.9039 | 0.9683 | 0 | 5.3844 | 0 | 6.5524 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 42.0888 | 11.78% | CZ 3B | 1.1081 | 0.33054 | 2.9018 | 0 | 0 | 1.5776 | 0 | 1.9198 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 12.0482 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.009683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009683 | 11.78% | CZ 3B | 11.6007 | 3.4604 | 30.3791 | 1.0583 | 0 | 16.516 | 0 | 20.0988 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 127.191 | 11.78%
CZ 3C | 0.11436 | 0.034061 | 0.33143 | 0.0084209 | 0 | 0.039991 | 0 | 0.14375 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.1065 | 3.558% | CZ 3C | 3.782 | 1.1264 | 10.9609 | 0.85059 | 0 | 1.3226 | 0 | 4.7539 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 37.1661 | 3.558% | CZ 3C | 1.1081 | 0.33004 | 3.2115 | 0 | 0 | 0.38751 | 0 | 1.3929 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 10.6404 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0085059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085059 | 3.558% | CZ 3C | 11.6007 | 3.4552 | 33.6215 | 0.9297 | 0 | 4.0568 | 0 | 14.5819 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 112.3236 | 3.558%
CZ 4A | 0.11436 | 0.034086 | 0.33479 | 0.063463 | 0 | 0.12835 | 0 | 0.18086 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2904 | 23.14% | CZ 4A | 3.782 | 1.1273 | 11.0719 | 6.4104 | 0 | 4.2447 | 0 | 5.9815 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 46.9875 | 23.14% | CZ 4A | 1.1081 | 0.33029 | 3.244 | 0 | 0 | 1.2437 | 0 | 1.7526 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.889 | 23.14% | CZ 4A | 0 | 0 | 0 | 0.064104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064104 | 23.14% | CZ 4A | 11.6007 | 3.4578 | 33.9619 | 7.0065 | 0 | 13.0202 | 0 | 18.3474 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 131.4723 | 23.14%
CZ 4B | 0.11436 | 0.034078 | 0.33031 | 0.024473 | 0 | 0.13291 | 0 | 0.2122 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2828 | 0.2995% | CZ 4B | 3.782 | 1.127 | 10.9239 | 2.472 | 0 | 4.3956 | 0 | 7.0177 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 44.0879 | 0.2995% | CZ 4B | 1.1081 | 0.33021 | 3.2007 | 0 | 0 | 1.2879 | 0 | 2.0562 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 12.1933 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.02472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02472 | 0.2995% | CZ 4B | 11.6007 | 3.457 | 33.5077 | 2.7019 | 0 | 13.4831 | 0 | 21.526 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 130.354 | 0.2995%
CZ 4C | 0.11436 | 0.034069 | 0.3465 | 0.045133 | 0 | 0.071342 | 0 | 0.18431 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2302 | 5.067% | CZ 4C | 3.782 | 1.1267 | 11.4594 | 4.5589 | 0 | 2.3594 | 0 | 6.0952 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 43.7513 | 5.067% | CZ 4C | 1.1081 | 0.33013 | 3.3576 | 0 | 0 | 0.69129 | 0 | 1.7859 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.4833 | 5.067% | CZ 4C | 0 | 0 | 0 | 0.045589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045589 | 5.067% | CZ 4C | 11.6007 | 3.4561 | 35.1504 | 4.9829 | 0 | 7.2371 | 0 | 18.6965 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 125.2014 | 5.067%
CZ 5A | 0.11436 | 0.034044 | 0.35415 | 0.12129 | 0 | 0.10307 | 0 | 0.18394 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3454 | 15.32% | CZ 5A | 3.782 | 1.1259 | 11.7123 | 12.2519 | 0 | 3.4085 | 0 | 6.0832 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 52.7335 | 15.32% | CZ 5A | 1.1081 | 0.32988 | 3.4317 | 0 | 0 | 0.99869 | 0 | 1.7824 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.861 | 15.32% | CZ 5A | 0 | 0 | 0 | 0.12252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12252 | 15.32% | CZ 5A | 11.6007 | 3.4535 | 35.9261 | 13.3913 | 0 | 10.4553 | 0 | 18.6594 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 137.5641 | 15.32%
CZ 5B | 0.11436 | 0.034035 | 0.35055 | 0.057978 | 0 | 0.096108 | 0 | 0.20919 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2967 | 4.35% | CZ 5B | 3.782 | 1.1256 | 11.5931 | 5.8564 | 0 | 3.1784 | 0 | 6.9182 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 46.8235 | 4.35% | CZ 5B | 1.1081 | 0.3298 | 3.3968 | 0 | 0 | 0.93127 | 0 | 2.027 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 12.0033 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.058564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058564 | 4.35% | CZ 5B | 11.6007 | 3.4526 | 35.5607 | 6.401 | 0 | 9.7495 | 0 | 21.2209 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 132.0631 | 4.35%
CZ 5C | 0.11436 | 0.03401 | 0.35458 | 0.073608 | 0 | 0.043058 | 0 | 0.16002 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2141 | 0% | CZ 5C | 3.782 | 1.1248 | 11.7263 | 7.4351 | 0 | 1.424 | 0 | 5.2922 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 45.1541 | 0% | CZ 5C | 1.1081 | 0.32955 | 3.4358 | 0 | 0 | 0.41723 | 0 | 1.5506 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.0516 | 0% | CZ 5C | 0 | 0 | 0 | 0.074351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074351 | 0% | CZ 5C | 11.6007 | 3.4501 | 35.9692 | 8.1266 | 0 | 4.3679 | 0 | 16.2333 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 123.8255 | 0%
CZ 6A | 0.11436 | 0.034052 | 0.37125 | 0.14629 | 0 | 0.070815 | 0 | 0.17381 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3451 | 4.28% | CZ 6A | 3.782 | 1.1262 | 12.2779 | 14.777 | 0 | 2.3419 | 0 | 5.7482 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 54.4229 | 4.28% | CZ 6A | 1.1081 | 0.32996 | 3.5974 | 0 | 0 | 0.68618 | 0 | 1.6842 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.6162 | 4.28% | CZ 6A | 0 | 0 | 0 | 0.14777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14777 | 4.28% | CZ 6A | 11.6007 | 3.4544 | 37.6611 | 16.1512 | 0 | 7.1837 | 0 | 17.6321 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 137.7608 | 4.28%
CZ 6B | 0.11436 | 0.034027 | 0.37365 | 0.097202 | 0 | 0.067884 | 0 | 0.20911 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3307 | 0.7689% | CZ 6B | 3.782 | 1.1253 | 12.3571 | 9.8184 | 0 | 2.245 | 0 | 6.9154 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 50.6129 | 0.7689% | CZ 6B | 1.1081 | 0.32971 | 3.6206 | 0 | 0 | 0.65778 | 0 | 2.0262 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.9527 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.098184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098184 | 0.7689% | CZ 6B | 11.6007 | 3.4518 | 37.9041 | 10.7315 | 0 | 6.8863 | 0 | 21.2123 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 135.8644 | 0.7689%
CZ 7 | 0.11436 | 0.034027 | 0.39823 | 0.19379 | 0 | 0.050484 | 0 | 0.17011 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.3955 | 0.4435% | CZ 7 | 3.782 | 1.1253 | 13.17 | 19.5743 | 0 | 1.6696 | 0 | 5.6257 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 59.3167 | 0.4435% | CZ 7 | 1.1081 | 0.32971 | 3.8588 | 0 | 0 | 0.48918 | 0 | 1.6483 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.6444 | 0.4435% | CZ 7 | 0 | 0 | 0 | 0.19574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19574 | 0.4435% | CZ 7 | 11.6007 | 3.4518 | 40.3975 | 21.3948 | 0 | 5.1212 | 0 | 17.2563 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 143.3 | 0.4435%
CZ 8 | 0.11436 | 0.033814 | 0.43145 | 0.28119 | 0 | 0.039617 | 0 | 0.17826 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.5132 | 0% | CZ 8 | 3.782 | 1.1183 | 14.2686 | 28.4031 | 0 | 1.3102 | 0 | 5.8952 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 69.1471 | 0% | CZ 8 | 1.1081 | 0.32766 | 4.1807 | 0 | 0 | 0.38388 | 0 | 1.7273 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.9379 | 0% | CZ 8 | 0 | 0 | 0 | 0.28403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28403 | 0% | CZ 8 | 11.6007 | 3.4302 | 43.7674 | 31.0445 | 0 | 4.0189 | 0 | 18.0829 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 156.0223 | 0%
Us Weighted | 0.11436 | 0.03408 | 0.32261 | 0.053639 | 0 | 0.14794 | 0 | 0.18395 | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0.32806 | 1.2911 | 100% | Us Weighted | 3.782 | 1.1271 | 10.6692 | 5.418 | 0 | 4.8927 | 0 | 6.0835 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8494 | 46.3422 | 100% | Us Weighted | 1.1081 | 0.33023 | 3.126 | 0 | 0 | 1.4336 | 0 | 1.7825 | 0 | 0 | 0 | 1.0315 | 0 | 0 | 0 | 3.1788 | 11.9907 | 100% | Us Weighted | 0 | 0 | 0 | 0.05418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05418 | 100% | Us Weighted | 11.6007 | 3.4572 | 32.7265 | 5.9219 | 0 | 15.0079 | 0 | 18.6605 | 0 | 0 | 0 | 10.7984 | 0 | 0 | 0 | 33.2792 | 131.4524 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.10283 | 0.062081 | 0.25554 | 0.00045608 | 0 | 0.35594 | 0 | 0.20627 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4229 | 3.509% | CZ 1A | 3.4007 | 2.0531 | 8.451 | 0.046069 | 0 | 11.7716 | 0 | 6.8216 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 47.0888 | 3.509% | CZ 1A | 0.99639 | 0.60155 | 2.4761 | 0 | 0 | 3.449 | 0 | 1.9987 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 13.7834 | 3.509% | CZ 1A | 0 | 0 | 0 | 0.00046069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00046069 | 3.509% | CZ 1A | 10.4312 | 6.2977 | 25.9224 | 0.050354 | 0 | 36.108 | 0 | 20.9244 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.3486 | 3.509%
CZ 1B | 0.10283 | 0.06203 | 0.24334 | 0.0013321 | 0 | 0.35218 | 0 | 0.29714 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4986 | 0% | CZ 1B | 3.4007 | 2.0514 | 8.0475 | 0.13456 | 0 | 11.6471 | 0 | 9.8269 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.6529 | 0% | CZ 1B | 0.99639 | 0.60106 | 2.3579 | 0 | 0 | 3.4126 | 0 | 2.8793 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 14.5088 | 0% | CZ 1B | 0 | 0 | 0 | 0.0013456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013456 | 0% | CZ 1B | 10.4312 | 6.2925 | 24.6848 | 0.14707 | 0 | 35.7262 | 0 | 30.143 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 152.0393 | 0%
CZ 2A | 0.10283 | 0.061971 | 0.28451 | 0.015718 | 0 | 0.24036 | 0 | 0.20033 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3455 | 14.94% | CZ 2A | 3.4007 | 2.0495 | 9.4091 | 1.5877 | 0 | 7.9491 | 0 | 6.6252 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 45.5661 | 14.94% | CZ 2A | 0.99639 | 0.60048 | 2.7568 | 0 | 0 | 2.3291 | 0 | 1.9412 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.8855 | 14.94% | CZ 2A | 0 | 0 | 0 | 0.015877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015877 | 14.94% | CZ 2A | 10.4312 | 6.2865 | 28.8614 | 1.7354 | 0 | 24.3831 | 0 | 20.322 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 136.6341 | 14.94%
CZ 2B | 0.10283 | 0.061928 | 0.26769 | 0.0032287 | 0 | 0.29594 | 0 | 0.26086 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4323 | 1.276% | CZ 2B | 3.4007 | 2.048 | 8.8528 | 0.32614 | 0 | 9.7873 | 0 | 8.6269 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 47.5866 | 1.276% | CZ 2B | 0.99639 | 0.60007 | 2.5938 | 0 | 0 | 2.8677 | 0 | 2.5276 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 13.8472 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0032614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032614 | 1.276% | CZ 2B | 10.4312 | 6.2822 | 27.1549 | 0.35647 | 0 | 30.0215 | 0 | 26.4619 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 145.3227 | 1.276%
CZ 3A | 0.10283 | 0.062013 | 0.30719 | 0.05146 | 0 | 0.18007 | 0 | 0.18762 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.331 | 11.27% | CZ 3A | 3.4007 | 2.0509 | 10.1593 | 5.198 | 0 | 5.955 | 0 | 6.2048 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 47.5135 | 11.27% | CZ 3A | 0.99639 | 0.6009 | 2.9767 | 0 | 0 | 1.7448 | 0 | 1.818 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.3983 | 11.27% | CZ 3A | 0 | 0 | 0 | 0.05198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05198 | 11.27% | CZ 3A | 10.4312 | 6.2908 | 31.1626 | 5.6814 | 0 | 18.2664 | 0 | 19.0326 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 135.4796 | 11.27%
CZ 3B | 0.10283 | 0.062013 | 0.29954 | 0.012693 | 0 | 0.16576 | 0 | 0.21762 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3002 | 11.78% | CZ 3B | 3.4007 | 2.0509 | 9.9062 | 1.2821 | 0 | 5.4819 | 0 | 7.197 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 43.8634 | 11.78% | CZ 3B | 0.99639 | 0.6009 | 2.9025 | 0 | 0 | 1.6062 | 0 | 2.1087 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.4762 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.012821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012821 | 11.78% | CZ 3B | 10.4312 | 6.2908 | 30.386 | 1.4013 | 0 | 16.815 | 0 | 22.0759 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 132.0148 | 11.78%
CZ 3C | 0.10283 | 0.061928 | 0.33165 | 0.012787 | 0 | 0.03175 | 0 | 0.15499 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.1357 | 3.558% | CZ 3C | 3.4007 | 2.048 | 10.9682 | 1.2916 | 0 | 1.05 | 0 | 5.1256 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 38.429 | 3.558% | CZ 3C | 0.99639 | 0.60007 | 3.2137 | 0 | 0 | 0.30765 | 0 | 1.5018 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 10.8812 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.012916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012916 | 3.558% | CZ 3C | 10.4312 | 6.2822 | 33.6439 | 1.4117 | 0 | 3.2208 | 0 | 15.7222 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 115.3266 | 3.558%
CZ 4A | 0.10283 | 0.061979 | 0.3349 | 0.084687 | 0 | 0.12748 | 0 | 0.19341 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3451 | 23.14% | CZ 4A | 3.4007 | 2.0497 | 11.0756 | 8.5543 | 0 | 4.2158 | 0 | 6.3965 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 50.2373 | 23.14% | CZ 4A | 0.99639 | 0.60057 | 3.2451 | 0 | 0 | 1.2352 | 0 | 1.8741 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.213 | 23.14% | CZ 4A | 0 | 0 | 0 | 0.085543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085543 | 23.14% | CZ 4A | 10.4312 | 6.2873 | 33.9731 | 9.3498 | 0 | 12.9315 | 0 | 19.6204 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 137.2079 | 23.14%
CZ 4B | 0.10283 | 0.061971 | 0.33043 | 0.033508 | 0 | 0.12878 | 0 | 0.22554 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3228 | 0.2995% | CZ 4B | 3.4007 | 2.0495 | 10.9278 | 3.3847 | 0 | 4.2588 | 0 | 7.4588 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 46.025 | 0.2995% | CZ 4B | 0.99639 | 0.60048 | 3.2018 | 0 | 0 | 1.2478 | 0 | 2.1854 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.4935 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.033847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033847 | 0.2995% | CZ 4B | 10.4312 | 6.2865 | 33.5198 | 3.6995 | 0 | 13.0633 | 0 | 22.8792 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 134.494 | 0.2995%
CZ 4C | 0.10283 | 0.061954 | 0.34662 | 0.061355 | 0 | 0.067578 | 0 | 0.19516 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.2753 | 5.067% | CZ 4C | 3.4007 | 2.0489 | 11.463 | 6.1974 | 0 | 2.2349 | 0 | 6.4543 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 46.3441 | 5.067% | CZ 4C | 0.99639 | 0.60032 | 3.3586 | 0 | 0 | 0.65482 | 0 | 1.8911 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.7629 | 5.067% | CZ 4C | 0 | 0 | 0 | 0.061974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061974 | 5.067% | CZ 4C | 10.4312 | 6.2847 | 35.1616 | 6.7738 | 0 | 6.8553 | 0 | 19.798 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 129.9192 | 5.067%
CZ 5A | 0.10283 | 0.061911 | 0.35424 | 0.15619 | 0 | 0.10188 | 0 | 0.19629 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4131 | 15.32% | CZ 5A | 3.4007 | 2.0475 | 11.7151 | 15.7767 | 0 | 3.3692 | 0 | 6.4917 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 57.3457 | 15.32% | CZ 5A | 0.99639 | 0.59991 | 3.4325 | 0 | 0 | 0.98717 | 0 | 1.9021 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.1796 | 15.32% | CZ 5A | 0 | 0 | 0 | 0.15777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15777 | 15.32% | CZ 5A | 10.4312 | 6.2804 | 35.9347 | 17.244 | 0 | 10.3347 | 0 | 19.9126 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.7522 | 15.32%
CZ 5B | 0.10283 | 0.061877 | 0.35065 | 0.073204 | 0 | 0.09282 | 0 | 0.2229 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3441 | 4.35% | CZ 5B | 3.4007 | 2.0464 | 11.5965 | 7.3944 | 0 | 3.0697 | 0 | 7.3717 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.4242 | 4.35% | CZ 5B | 0.99639 | 0.59958 | 3.3977 | 0 | 0 | 0.89941 | 0 | 2.1599 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.3146 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.073944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073944 | 4.35% | CZ 5B | 10.4312 | 6.277 | 35.571 | 8.0821 | 0 | 9.4159 | 0 | 22.612 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 137.0037 | 4.35%
CZ 5C | 0.10283 | 0.061843 | 0.3547 | 0.094949 | 0 | 0.037748 | 0 | 0.16412 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.256 | 0% | CZ 5C | 3.4007 | 2.0452 | 11.7305 | 9.5908 | 0 | 1.2484 | 0 | 5.4276 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 47.9881 | 0% | CZ 5C | 0.99639 | 0.59925 | 3.437 | 0 | 0 | 0.36577 | 0 | 1.5903 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.2503 | 0% | CZ 5C | 0 | 0 | 0 | 0.095908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095908 | 0% | CZ 5C | 10.4312 | 6.2735 | 35.9821 | 10.4828 | 0 | 3.8293 | 0 | 16.6487 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 128.2622 | 0%
CZ 6A | 0.10283 | 0.061911 | 0.37135 | 0.18417 | 0 | 0.067425 | 0 | 0.18322 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4107 | 4.28% | CZ 6A | 3.4007 | 2.0475 | 12.281 | 18.603 | 0 | 2.2298 | 0 | 6.0593 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 59.166 | 4.28% | CZ 6A | 0.99639 | 0.59991 | 3.5983 | 0 | 0 | 0.65334 | 0 | 1.7754 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.8849 | 4.28% | CZ 6A | 0 | 0 | 0 | 0.18603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18603 | 4.28% | CZ 6A | 10.4312 | 6.2804 | 37.6705 | 20.333 | 0 | 6.8398 | 0 | 18.5862 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.7558 | 4.28%
CZ 6B | 0.10283 | 0.06186 | 0.37375 | 0.11621 | 0 | 0.064358 | 0 | 0.22133 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3801 | 0.7689% | CZ 6B | 3.4007 | 2.0458 | 12.3605 | 11.7384 | 0 | 2.1284 | 0 | 7.3198 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 53.5383 | 0.7689% | CZ 6B | 0.99639 | 0.59941 | 3.6216 | 0 | 0 | 0.62362 | 0 | 2.1447 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.2473 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.11738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11738 | 0.7689% | CZ 6B | 10.4312 | 6.2753 | 37.9144 | 12.83 | 0 | 6.5287 | 0 | 22.4525 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 141.0467 | 0.7689%
CZ 7 | 0.10283 | 0.061869 | 0.39834 | 0.24872 | 0 | 0.045785 | 0 | 0.1778 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4751 | 0.4435% | CZ 7 | 3.4007 | 2.0461 | 13.1736 | 25.1234 | 0 | 1.5142 | 0 | 5.88 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 65.6828 | 0.4435% | CZ 7 | 0.99639 | 0.5995 | 3.8598 | 0 | 0 | 0.44365 | 0 | 1.7228 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.8838 | 0.4435% | CZ 7 | 0 | 0 | 0 | 0.25123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25123 | 0.4435% | CZ 7 | 10.4312 | 6.2761 | 40.4087 | 27.4599 | 0 | 4.6446 | 0 | 18.0363 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 151.8714 | 0.4435%
CZ 8 | 0.10283 | 0.061486 | 0.43153 | 0.31007 | 0 | 0.035318 | 0 | 0.18392 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.5649 | 0% | CZ 8 | 3.4007 | 2.0334 | 14.2711 | 31.32 | 0 | 1.168 | 0 | 6.0826 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 72.8207 | 0% | CZ 8 | 0.99639 | 0.59579 | 4.1814 | 0 | 0 | 0.34223 | 0 | 1.7822 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.1596 | 0% | CZ 8 | 0 | 0 | 0 | 0.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3132 | 0% | CZ 8 | 10.4312 | 6.2373 | 43.7751 | 34.2328 | 0 | 3.5828 | 0 | 18.6577 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 161.5316 | 0%
Us Weighted | 0.10283 | 0.061966 | 0.32269 | 0.069956 | 0 | 0.14966 | 0 | 0.19821 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3451 | 100% | Us Weighted | 3.4007 | 2.0493 | 10.672 | 7.0663 | 0 | 4.9494 | 0 | 6.555 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.2374 | 100% | Us Weighted | 0.99639 | 0.60044 | 3.1269 | 0 | 0 | 1.4502 | 0 | 1.9206 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.356 | 100% | Us Weighted | 0 | 0 | 0 | 0.070663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070663 | 100% | Us Weighted | 10.4312 | 6.286 | 32.7351 | 7.7235 | 0 | 15.1818 | 0 | 20.1066 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 137.0787 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.10283 | 0.062081 | 0.25555 | 0.00053673 | 0 | 0.43636 | 0 | 0.21092 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.5081 | 3.509% | CZ 1A | 3.4007 | 2.0531 | 8.4512 | 0.054216 | 0 | 14.431 | 0 | 6.9753 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.9103 | 3.509% | CZ 1A | 0.99639 | 0.60155 | 2.4762 | 0 | 0 | 4.2282 | 0 | 2.0437 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 14.6077 | 3.509% | CZ 1A | 0 | 0 | 0 | 0.00054216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00054216 | 3.509% | CZ 1A | 10.4312 | 6.2977 | 25.9233 | 0.059258 | 0 | 44.2655 | 0 | 21.3959 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 152.9874 | 3.509%
CZ 1B | 0.10283 | 0.06203 | 0.24335 | 0.0016046 | 0 | 0.43316 | 0 | 0.30395 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.5867 | 0% | CZ 1B | 3.4007 | 2.0514 | 8.048 | 0.16208 | 0 | 14.3251 | 0 | 10.052 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 52.5841 | 0% | CZ 1B | 0.99639 | 0.60106 | 2.3581 | 0 | 0 | 4.1972 | 0 | 2.9452 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 15.3595 | 0% | CZ 1B | 0 | 0 | 0 | 0.0016208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016208 | 0% | CZ 1B | 10.4312 | 6.2925 | 24.6865 | 0.17716 | 0 | 43.9406 | 0 | 30.8333 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 160.9759 | 0%
CZ 2A | 0.10283 | 0.061971 | 0.28459 | 0.024401 | 0 | 0.30697 | 0 | 0.22626 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4468 | 14.94% | CZ 2A | 3.4007 | 2.0495 | 9.4116 | 2.4647 | 0 | 10.152 | 0 | 7.4827 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.506 | 14.94% | CZ 2A | 0.99639 | 0.60048 | 2.7576 | 0 | 0 | 2.9745 | 0 | 2.1924 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 13.783 | 14.94% | CZ 2A | 0 | 0 | 0 | 0.024647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024647 | 14.94% | CZ 2A | 10.4312 | 6.2865 | 28.8691 | 2.6939 | 0 | 31.1402 | 0 | 22.9524 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 146.9879 | 14.94%
CZ 2B | 0.10283 | 0.061928 | 0.26776 | 0.0063073 | 0 | 0.39409 | 0 | 0.3004 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.5731 | 1.276% | CZ 2B | 3.4007 | 2.048 | 8.8553 | 0.6371 | 0 | 13.0332 | 0 | 9.9345 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 52.4536 | 1.276% | CZ 2B | 0.99639 | 0.60007 | 2.5946 | 0 | 0 | 3.8187 | 0 | 2.9108 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 15.1821 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.006371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006371 | 1.276% | CZ 2B | 10.4312 | 6.2822 | 27.1626 | 0.69635 | 0 | 39.9778 | 0 | 30.4731 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 159.6378 | 1.276%
CZ 3A | 0.10283 | 0.062013 | 0.30718 | 0.055097 | 0 | 0.23901 | 0 | 0.211 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4169 | 11.27% | CZ 3A | 3.4007 | 2.0509 | 10.1587 | 5.5654 | 0 | 7.9045 | 0 | 6.9781 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 50.603 | 11.27% | CZ 3A | 0.99639 | 0.6009 | 2.9765 | 0 | 0 | 2.316 | 0 | 2.0446 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 13.1959 | 11.27% | CZ 3A | 0 | 0 | 0 | 0.055654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055654 | 11.27% | CZ 3A | 10.4312 | 6.2908 | 31.1608 | 6.083 | 0 | 24.2461 | 0 | 21.4045 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.2309 | 11.27%
CZ 3B | 0.10283 | 0.062013 | 0.29952 | 0.01452 | 0 | 0.22685 | 0 | 0.2455 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.391 | 11.78% | CZ 3B | 3.4007 | 2.0509 | 9.9056 | 1.4666 | 0 | 7.5021 | 0 | 8.1191 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 46.9898 | 11.78% | CZ 3B | 0.99639 | 0.6009 | 2.9023 | 0 | 0 | 2.1981 | 0 | 2.3789 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 13.3382 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.014666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014666 | 11.78% | CZ 3B | 10.4312 | 6.2908 | 30.3843 | 1.603 | 0 | 23.0119 | 0 | 24.9045 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 141.2403 | 11.78%
CZ 3C | 0.10283 | 0.061928 | 0.33156 | 0.016575 | 0 | 0.070662 | 0 | 0.21751 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.2409 | 3.558% | CZ 3C | 3.4007 | 2.048 | 10.9652 | 1.6742 | 0 | 2.3369 | 0 | 7.1933 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 42.1631 | 3.558% | CZ 3C | 0.99639 | 0.60007 | 3.2128 | 0 | 0 | 0.6847 | 0 | 2.1076 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.8631 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.016742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016742 | 3.558% | CZ 3C | 10.4312 | 6.2822 | 33.6344 | 1.8299 | 0 | 7.1682 | 0 | 22.0647 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 126.0251 | 3.558%
CZ 4A | 0.10283 | 0.061979 | 0.33494 | 0.096078 | 0 | 0.15521 | 0 | 0.20074 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3916 | 23.14% | CZ 4A | 3.4007 | 2.0497 | 11.077 | 9.7049 | 0 | 5.1329 | 0 | 6.6387 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 52.5486 | 23.14% | CZ 4A | 0.99639 | 0.60057 | 3.2455 | 0 | 0 | 1.5039 | 0 | 1.9451 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.5531 | 23.14% | CZ 4A | 0 | 0 | 0 | 0.097049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097049 | 23.14% | CZ 4A | 10.4312 | 6.2873 | 33.9774 | 10.6074 | 0 | 15.7446 | 0 | 20.3634 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 142.0259 | 23.14%
CZ 4B | 0.10283 | 0.061971 | 0.33048 | 0.041576 | 0 | 0.15633 | 0 | 0.23416 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3671 | 0.2995% | CZ 4B | 3.4007 | 2.0495 | 10.9295 | 4.1996 | 0 | 5.17 | 0 | 7.744 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 48.038 | 0.2995% | CZ 4B | 0.99639 | 0.60048 | 3.2023 | 0 | 0 | 1.5148 | 0 | 2.269 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.8445 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.041996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041996 | 0.2995% | CZ 4B | 10.4312 | 6.2865 | 33.5249 | 4.5902 | 0 | 15.8584 | 0 | 23.7539 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 139.0597 | 0.2995%
CZ 4C | 0.10283 | 0.061954 | 0.34669 | 0.072067 | 0 | 0.080229 | 0 | 0.20071 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.3043 | 5.067% | CZ 4C | 3.4007 | 2.0489 | 11.4656 | 7.2795 | 0 | 2.6533 | 0 | 6.6378 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 48.0305 | 5.067% | CZ 4C | 0.99639 | 0.60032 | 3.3594 | 0 | 0 | 0.7774 | 0 | 1.9449 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.9399 | 5.067% | CZ 4C | 0 | 0 | 0 | 0.072795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072795 | 5.067% | CZ 4C | 10.4312 | 6.2847 | 35.1694 | 7.9565 | 0 | 8.1386 | 0 | 20.3608 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 132.9558 | 5.067%
CZ 5A | 0.10283 | 0.061911 | 0.35428 | 0.17306 | 0 | 0.12354 | 0 | 0.20319 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4586 | 15.32% | CZ 5A | 3.4007 | 2.0475 | 11.7165 | 17.481 | 0 | 4.0857 | 0 | 6.7199 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 59.996 | 15.32% | CZ 5A | 0.99639 | 0.59991 | 3.4329 | 0 | 0 | 1.1971 | 0 | 1.9689 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.4568 | 15.32% | CZ 5A | 0 | 0 | 0 | 0.17481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17481 | 15.32% | CZ 5A | 10.4312 | 6.2804 | 35.939 | 19.1067 | 0 | 12.5324 | 0 | 20.6124 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 149.5169 | 15.32%
CZ 5B | 0.10283 | 0.061877 | 0.35071 | 0.085577 | 0 | 0.1121 | 0 | 0.23115 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.384 | 4.35% | CZ 5B | 3.4007 | 2.0464 | 11.5985 | 8.6442 | 0 | 3.7072 | 0 | 7.6446 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 51.5863 | 4.35% | CZ 5B | 0.99639 | 0.59958 | 3.3983 | 0 | 0 | 1.0862 | 0 | 2.2398 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.5819 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.086442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086442 | 4.35% | CZ 5B | 10.4312 | 6.277 | 35.5771 | 9.4481 | 0 | 11.3715 | 0 | 23.4488 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 141.1682 | 4.35%
CZ 5C | 0.10283 | 0.061843 | 0.35477 | 0.11075 | 0 | 0.043364 | 0 | 0.16681 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.2802 | 0% | CZ 5C | 3.4007 | 2.0452 | 11.7328 | 11.1872 | 0 | 1.4341 | 0 | 5.5167 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 49.8616 | 0% | CZ 5C | 0.99639 | 0.59925 | 3.4377 | 0 | 0 | 0.42019 | 0 | 1.6164 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 11.3315 | 0% | CZ 5C | 0 | 0 | 0 | 0.11187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11187 | 0% | CZ 5C | 10.4312 | 6.2735 | 35.989 | 12.2276 | 0 | 4.399 | 0 | 16.9219 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 130.8569 | 0%
CZ 6A | 0.10283 | 0.061911 | 0.37139 | 0.20413 | 0 | 0.080849 | 0 | 0.18911 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.45 | 4.28% | CZ 6A | 3.4007 | 2.0475 | 12.2824 | 20.6196 | 0 | 2.6738 | 0 | 6.2543 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 61.823 | 4.28% | CZ 6A | 0.99639 | 0.59991 | 3.5987 | 0 | 0 | 0.78341 | 0 | 1.8325 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.0725 | 4.28% | CZ 6A | 0 | 0 | 0 | 0.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2062 | 4.28% | CZ 6A | 10.4312 | 6.2804 | 37.6748 | 22.5372 | 0 | 8.2015 | 0 | 19.1843 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 148.9242 | 4.28%
CZ 6B | 0.10283 | 0.06186 | 0.3738 | 0.13503 | 0 | 0.076592 | 0 | 0.2281 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.418 | 0.7689% | CZ 6B | 3.4007 | 2.0458 | 12.3622 | 13.6398 | 0 | 2.533 | 0 | 7.5437 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 56.07 | 0.7689% | CZ 6B | 0.99639 | 0.59941 | 3.6221 | 0 | 0 | 0.74217 | 0 | 2.2103 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.4319 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1364 | 0.7689% | CZ 6B | 10.4312 | 6.2753 | 37.9196 | 14.9084 | 0 | 7.7697 | 0 | 23.1394 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 145.0582 | 0.7689%
CZ 7 | 0.10283 | 0.061869 | 0.39836 | 0.28296 | 0 | 0.061223 | 0 | 0.20542 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.5525 | 0.4435% | CZ 7 | 3.4007 | 2.0461 | 13.1742 | 28.5817 | 0 | 2.0247 | 0 | 6.7935 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 70.5657 | 0.4435% | CZ 7 | 0.99639 | 0.5995 | 3.86 | 0 | 0 | 0.59324 | 0 | 1.9905 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.3012 | 0.4435% | CZ 7 | 0 | 0 | 0 | 0.28582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28582 | 0.4435% | CZ 7 | 10.4312 | 6.2761 | 40.4104 | 31.2398 | 0 | 6.2106 | 0 | 20.8382 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 160.021 | 0.4435%
CZ 8 | 0.10283 | 0.061486 | 0.43152 | 0.33467 | 0 | 0.048258 | 0 | 0.20595 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.6245 | 0% | CZ 8 | 3.4007 | 2.0334 | 14.2709 | 33.8052 | 0 | 1.596 | 0 | 6.8112 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 76.4621 | 0% | CZ 8 | 0.99639 | 0.59579 | 4.1813 | 0 | 0 | 0.46761 | 0 | 1.9957 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.4984 | 0% | CZ 8 | 0 | 0 | 0 | 0.33805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33805 | 0% | CZ 8 | 10.4312 | 6.2373 | 43.7743 | 36.9491 | 0 | 4.8954 | 0 | 20.8925 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 167.7945 | 0%
Us Weighted | 0.10283 | 0.061966 | 0.32273 | 0.079533 | 0 | 0.19094 | 0 | 0.21474 | 0 | 0 | 0 | 0.11009 | 0 | 0 | 0 | 0.32971 | 1.4125 | 100% | Us Weighted | 3.4007 | 2.0493 | 10.673 | 8.0336 | 0 | 6.3147 | 0 | 7.1016 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9039 | 52.1177 | 100% | Us Weighted | 0.99639 | 0.60044 | 3.1272 | 0 | 0 | 1.8502 | 0 | 2.0808 | 0 | 0 | 0 | 1.0668 | 0 | 0 | 0 | 3.1948 | 12.9165 | 100% | Us Weighted | 0 | 0 | 0 | 0.080336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080336 | 100% | Us Weighted | 10.4312 | 6.286 | 32.7382 | 8.7807 | 0 | 19.3696 | 0 | 21.7834 | 0 | 0 | 0 | 11.1682 | 0 | 0 | 0 | 33.4464 | 144.0037 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 33741 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 33741 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.0087765 | 0.027935 | 0.00034834 | 0.00038934 | 0 | 0.16132 | 0 | 0.043738 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.24808 | 3.509% | CZ 1A | 0.29025 | 0.92385 | 0.01152 | 0.039327 | 0 | 5.3349 | 0 | 1.4465 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.2307 | 3.509% | CZ 1A | 0.085042 | 0.27069 | 0.0033754 | 0 | 0 | 1.5631 | 0 | 0.42381 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 2.4 | 3.509% | CZ 1A | 0 | 0 | 0 | 0.00039327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039327 | 3.509% | CZ 1A | 0.89031 | 2.8338 | 0.035337 | 0.042985 | 0 | 16.3643 | 0 | 4.4369 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 25.169 | 3.509%
CZ 1B | 0.0087765 | 0.027918 | 0.00022939 | 0.0008927 | 0 | 0.15356 | 0 | 0.070178 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.26713 | 0% | CZ 1B | 0.29025 | 0.92329 | 0.0075864 | 0.090172 | 0 | 5.0784 | 0 | 2.3209 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.8949 | 0% | CZ 1B | 0.085042 | 0.27052 | 0.0022228 | 0 | 0 | 1.488 | 0 | 0.68001 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 2.5798 | 0% | CZ 1B | 0 | 0 | 0 | 0.00090172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00090172 | 0% | CZ 1B | 0.89031 | 2.8321 | 0.02327 | 0.098558 | 0 | 15.5774 | 0 | 7.119 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 27.1061 | 0%
CZ 2A | 0.0087765 | 0.027884 | 0.00034834 | 0.013574 | 0 | 0.12174 | 0 | 0.065479 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.24338 | 14.94% | CZ 2A | 0.29025 | 0.92217 | 0.01152 | 1.3711 | 0 | 4.0261 | 0 | 2.1655 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.971 | 14.94% | CZ 2A | 0.085042 | 0.27019 | 0.0033754 | 0 | 0 | 1.1796 | 0 | 0.63448 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 2.2267 | 14.94% | CZ 2A | 0 | 0 | 0 | 0.013711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013711 | 14.94% | CZ 2A | 0.89031 | 2.8287 | 0.035337 | 1.4986 | 0 | 12.3497 | 0 | 6.6424 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 24.8104 | 14.94%
CZ 2B | 0.0087765 | 0.027867 | 0.00028887 | 0.0040408 | 0 | 0.15954 | 0 | 0.094986 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.30107 | 1.276% | CZ 2B | 0.29025 | 0.92161 | 0.0095532 | 0.40816 | 0 | 5.2762 | 0 | 3.1413 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 10.2314 | 1.276% | CZ 2B | 0.085042 | 0.27003 | 0.0027991 | 0 | 0 | 1.5459 | 0 | 0.9204 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 2.8782 | 1.276% | CZ 2B | 0 | 0 | 0 | 0.0040816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040816 | 1.276% | CZ 2B | 0.89031 | 2.8269 | 0.029304 | 0.44612 | 0 | 16.1842 | 0 | 9.6357 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 30.5779 | 1.276%
CZ 3A | 0.0087765 | 0.02791 | 0.00018691 | 0.011894 | 0 | 0.0983 | 0 | 0.050807 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.20345 | 11.27% | CZ 3A | 0.29025 | 0.92301 | 0.0061815 | 1.2015 | 0 | 3.2509 | 0 | 1.6802 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 7.5364 | 11.27% | CZ 3A | 0.085042 | 0.27044 | 0.0018112 | 0 | 0 | 0.95251 | 0 | 0.49231 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.8561 | 11.27% | CZ 3A | 0 | 0 | 0 | 0.012015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012015 | 11.27% | CZ 3A | 0.89031 | 2.8312 | 0.018961 | 1.3132 | 0 | 9.9718 | 0 | 5.154 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 20.7449 | 11.27%
CZ 3B | 0.0087765 | 0.027901 | 0.00018691 | 0.003251 | 0 | 0.094935 | 0 | 0.060246 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.20087 | 11.78% | CZ 3B | 0.29025 | 0.92273 | 0.0061815 | 0.32838 | 0 | 3.1396 | 0 | 1.9924 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 6.8639 | 11.78% | CZ 3B | 0.085042 | 0.27036 | 0.0018112 | 0 | 0 | 0.91991 | 0 | 0.58377 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.9149 | 11.78% | CZ 3B | 0 | 0 | 0 | 0.0032838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032838 | 11.78% | CZ 3B | 0.89031 | 2.8304 | 0.018961 | 0.35892 | 0 | 9.6305 | 0 | 6.1115 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 20.406 | 11.78%
CZ 3C | 0.0087765 | 0.027867 | 0.00014443 | 0.0063935 | 0 | 0.049175 | 0 | 0.085454 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.18338 | 3.558% | CZ 3C | 0.29025 | 0.92161 | 0.0047766 | 0.64581 | 0 | 1.6263 | 0 | 2.8261 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 6.4991 | 3.558% | CZ 3C | 0.085042 | 0.27003 | 0.0013995 | 0 | 0 | 0.4765 | 0 | 0.82803 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.715 | 3.558% | CZ 3C | 0 | 0 | 0 | 0.0064581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064581 | 3.558% | CZ 3C | 0.89031 | 2.8269 | 0.014652 | 0.70587 | 0 | 4.9885 | 0 | 8.6687 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 18.6603 | 3.558%
CZ 4A | 0.0087765 | 0.027893 | 0.00041631 | 0.038667 | 0 | 0.047459 | 0 | 0.027714 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.1565 | 23.14% | CZ 4A | 0.29025 | 0.92245 | 0.013768 | 3.9058 | 0 | 1.5695 | 0 | 0.91655 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 7.8026 | 23.14% | CZ 4A | 0.085042 | 0.27028 | 0.004034 | 0 | 0 | 0.45987 | 0 | 0.26855 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.1418 | 23.14% | CZ 4A | 0 | 0 | 0 | 0.039058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039058 | 23.14% | CZ 4A | 0.89031 | 2.8295 | 0.042232 | 4.269 | 0 | 4.8144 | 0 | 2.8114 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 16.2223 | 23.14%
CZ 4B | 0.0087765 | 0.027893 | 0.00045879 | 0.021442 | 0 | 0.041648 | 0 | 0.030815 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.13661 | 0.2995% | CZ 4B | 0.29025 | 0.92245 | 0.015173 | 2.1658 | 0 | 1.3774 | 0 | 1.0191 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 5.9745 | 0.2995% | CZ 4B | 0.085042 | 0.27028 | 0.0044456 | 0 | 0 | 0.40356 | 0 | 0.2986 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.1159 | 0.2995% | CZ 4B | 0 | 0 | 0 | 0.021658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021658 | 0.2995% | CZ 4B | 0.89031 | 2.8295 | 0.046541 | 2.3672 | 0 | 4.2249 | 0 | 3.126 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 14.0499 | 0.2995%
CZ 4C | 0.0087765 | 0.027884 | 0.00045879 | 0.032368 | 0 | 0.020705 | 0 | 0.022846 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.11861 | 5.067% | CZ 4C | 0.29025 | 0.92217 | 0.015173 | 3.2695 | 0 | 0.68474 | 0 | 0.75555 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 6.1217 | 5.067% | CZ 4C | 0.085042 | 0.27019 | 0.0044456 | 0 | 0 | 0.20063 | 0 | 0.22137 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.83569 | 5.067% | CZ 4C | 0 | 0 | 0 | 0.032695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032695 | 5.067% | CZ 4C | 0.89031 | 2.8287 | 0.046541 | 3.5736 | 0 | 2.1004 | 0 | 2.3176 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 12.3224 | 5.067%
CZ 5A | 0.0087765 | 0.027867 | 0.00038232 | 0.065554 | 0 | 0.037893 | 0 | 0.028938 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.17498 | 15.32% | CZ 5A | 0.29025 | 0.92161 | 0.012644 | 6.6216 | 0 | 1.2532 | 0 | 0.95701 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 10.2406 | 15.32% | CZ 5A | 0.085042 | 0.27003 | 0.0037047 | 0 | 0 | 0.36717 | 0 | 0.2804 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.0604 | 15.32% | CZ 5A | 0 | 0 | 0 | 0.066216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066216 | 15.32% | CZ 5A | 0.89031 | 2.8269 | 0.038784 | 7.2374 | 0 | 3.8439 | 0 | 2.9355 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 18.3383 | 15.32%
CZ 5B | 0.0087765 | 0.027842 | 0.00041631 | 0.037321 | 0 | 0.029108 | 0 | 0.033492 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.14253 | 4.35% | CZ 5B | 0.29025 | 0.92076 | 0.013768 | 3.7698 | 0 | 0.96263 | 0 | 1.1076 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 7.2492 | 4.35% | CZ 5B | 0.085042 | 0.26978 | 0.004034 | 0 | 0 | 0.28205 | 0 | 0.32453 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.0194 | 4.35% | CZ 5B | 0 | 0 | 0 | 0.037698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037698 | 4.35% | CZ 5B | 0.89031 | 2.8243 | 0.042232 | 4.1204 | 0 | 2.9528 | 0 | 3.3975 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 14.7929 | 4.35%
CZ 5C | 0.0087765 | 0.027833 | 0.00045029 | 0.049427 | 0 | 0.0073491 | 0 | 0.011682 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.11109 | 0% | CZ 5C | 0.29025 | 0.92048 | 0.014892 | 4.9926 | 0 | 0.24305 | 0 | 0.38634 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 7.0319 | 0% | CZ 5C | 0.085042 | 0.2697 | 0.0043633 | 0 | 0 | 0.071212 | 0 | 0.1132 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.59752 | 0% | CZ 5C | 0 | 0 | 0 | 0.049926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049926 | 0% | CZ 5C | 0.89031 | 2.8235 | 0.045679 | 5.4569 | 0 | 0.74552 | 0 | 1.1851 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 11.7124 | 0%
CZ 6A | 0.0087765 | 0.027859 | 0.00040781 | 0.077701 | 0 | 0.023058 | 0 | 0.025335 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.16871 | 4.28% | CZ 6A | 0.29025 | 0.92133 | 0.013487 | 7.8486 | 0 | 0.76257 | 0 | 0.83788 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 10.8584 | 4.28% | CZ 6A | 0.085042 | 0.26995 | 0.0039516 | 0 | 0 | 0.22343 | 0 | 0.2455 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.88187 | 4.28% | CZ 6A | 0 | 0 | 0 | 0.078486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078486 | 4.28% | CZ 6A | 0.89031 | 2.8261 | 0.04137 | 8.5785 | 0 | 2.3391 | 0 | 2.5701 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 17.8109 | 4.28%
CZ 6B | 0.0087765 | 0.027833 | 0.00040781 | 0.056499 | 0 | 0.017961 | 0 | 0.030875 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.14793 | 0.7689% | CZ 6B | 0.29025 | 0.92048 | 0.013487 | 5.707 | 0 | 0.59399 | 0 | 1.0211 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.7306 | 0.7689% | CZ 6B | 0.085042 | 0.2697 | 0.0039516 | 0 | 0 | 0.17404 | 0 | 0.29917 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.88591 | 0.7689% | CZ 6B | 0 | 0 | 0 | 0.05707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05707 | 0.7689% | CZ 6B | 0.89031 | 2.8235 | 0.04137 | 6.2377 | 0 | 1.822 | 0 | 3.132 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 15.5123 | 0.7689%
CZ 7 | 0.0087765 | 0.027842 | 0.00038232 | 0.11235 | 0 | 0.015794 | 0 | 0.033135 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.20386 | 0.4435% | CZ 7 | 0.29025 | 0.92076 | 0.012644 | 11.3487 | 0 | 0.52234 | 0 | 1.0958 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 14.3749 | 0.4435% | CZ 7 | 0.085042 | 0.26978 | 0.0037047 | 0 | 0 | 0.15304 | 0 | 0.32107 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.88665 | 0.4435% | CZ 7 | 0 | 0 | 0 | 0.11349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11349 | 0.4435% | CZ 7 | 0.89031 | 2.8243 | 0.038784 | 12.4042 | 0 | 1.6022 | 0 | 3.3613 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 21.6865 | 0.4435%
CZ 8 | 0.0087765 | 0.027672 | 0.00028037 | 0.084768 | 0 | 0.01051 | 0 | 0.021826 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.15941 | 0% | CZ 8 | 0.29025 | 0.91514 | 0.0092723 | 8.5624 | 0 | 0.34757 | 0 | 0.72183 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 11.0308 | 0% | CZ 8 | 0.085042 | 0.26813 | 0.0027167 | 0 | 0 | 0.10184 | 0 | 0.21149 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 0.72323 | 0% | CZ 8 | 0 | 0 | 0 | 0.085624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085624 | 0% | CZ 8 | 0.89031 | 2.8071 | 0.028442 | 9.3587 | 0 | 1.0661 | 0 | 2.2141 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 16.9302 | 0%
Us Weighted | 0.0087765 | 0.027886 | 0.0003361 | 0.030622 | 0 | 0.070315 | 0 | 0.043413 | 0 | 0 | 0 | 0.0039252 | 0 | 0 | 0 | 0.0016482 | 0.18692 | 100% | Us Weighted | 0.29025 | 0.92223 | 0.011115 | 3.0932 | 0 | 2.3254 | 0 | 1.4357 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 8.2622 | 100% | Us Weighted | 0.085042 | 0.27021 | 0.0032567 | 0 | 0 | 0.68134 | 0 | 0.42066 | 0 | 0 | 0 | 0.038035 | 0 | 0 | 0 | 0.015971 | 1.5145 | 100% | Us Weighted | 0 | 0 | 0 | 0.030932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030932 | 100% | Us Weighted | 0.89031 | 2.8288 | 0.034095 | 3.3808 | 0 | 7.133 | 0 | 4.4039 | 0 | 0 | 0 | 0.39819 | 0 | 0 | 0 | 0.1672 | 19.2363 | 100%
Building Type: | Mid-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 33741 | [17 empty] | Prototype Floor Area: | 33741 | [17 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 8.535% | 45% | 0.1363% | 72.54% | 0% | 36.97% | 0% | 20.74% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.45% | 3.509% | CZ 1A | 8.535% | 45% | 0.1363% | 72.54% | 0% | 36.97% | 0% | 20.74% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.49% | 3.509% | CZ 1A | 8.535% | 45% | 0.1363% | 0% | 0% | 36.97% | 0% | 20.74% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.43% | 3.509% | CZ 1A | 0% | 0% | 0% | 72.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 72.54% | 3.509% | CZ 1A | 8.535% | 45% | 0.1363% | 72.54% | 0% | 36.97% | 0% | 20.74% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.45% | 3.509%
CZ 1B | 8.535% | 45.01% | 0.09426% | 55.63% | 0% | 35.45% | 0% | 23.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.84% | 0% | CZ 1B | 8.535% | 45.01% | 0.09426% | 55.63% | 0% | 35.45% | 0% | 23.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.92% | 0% | CZ 1B | 8.535% | 45.01% | 0.09426% | 0% | 0% | 35.45% | 0% | 23.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.8% | 0% | CZ 1B | 0% | 0% | 0% | 55.63% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.63% | 0% | CZ 1B | 8.535% | 45.01% | 0.09426% | 55.63% | 0% | 35.45% | 0% | 23.09% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.84% | 0%
CZ 2A | 8.535% | 45% | 0.1224% | 55.63% | 0% | 39.66% | 0% | 28.94% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.82% | 14.94% | CZ 2A | 8.535% | 45% | 0.1224% | 55.63% | 0% | 39.66% | 0% | 28.94% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 18.12% | 14.94% | CZ 2A | 8.535% | 45% | 0.1224% | 0% | 0% | 39.66% | 0% | 28.94% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.16% | 14.94% | CZ 2A | 0% | 0% | 0% | 55.63% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.63% | 14.94% | CZ 2A | 8.535% | 45% | 0.1224% | 55.63% | 0% | 39.66% | 0% | 28.94% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 16.88% | 14.94%
CZ 2B | 8.535% | 45% | 0.1079% | 64.07% | 0% | 40.48% | 0% | 31.62% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 19.14% | 1.276% | CZ 2B | 8.535% | 45% | 0.1079% | 64.07% | 0% | 40.48% | 0% | 31.62% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 19.51% | 1.276% | CZ 2B | 8.535% | 45% | 0.1079% | 0% | 0% | 40.48% | 0% | 31.62% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 18.96% | 1.276% | CZ 2B | 0% | 0% | 0% | 64.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 64.07% | 1.276% | CZ 2B | 8.535% | 45% | 0.1079% | 64.07% | 0% | 40.48% | 0% | 31.62% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 19.15% | 1.276%
CZ 3A | 8.535% | 45.01% | 0.06085% | 21.59% | 0% | 41.13% | 0% | 24.08% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.36% | 11.27% | CZ 3A | 8.535% | 45.01% | 0.06085% | 21.59% | 0% | 41.13% | 0% | 24.08% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.89% | 11.27% | CZ 3A | 8.535% | 45.01% | 0.06085% | 0% | 0% | 41.13% | 0% | 24.08% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.07% | 11.27% | CZ 3A | 0% | 0% | 0% | 21.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.59% | 11.27% | CZ 3A | 8.535% | 45.01% | 0.06085% | 21.59% | 0% | 41.13% | 0% | 24.08% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.38% | 11.27%
CZ 3B | 8.535% | 44.99% | 0.0624% | 22.39% | 0% | 41.85% | 0% | 24.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.44% | 11.78% | CZ 3B | 8.535% | 44.99% | 0.0624% | 22.39% | 0% | 41.85% | 0% | 24.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.61% | 11.78% | CZ 3B | 8.535% | 44.99% | 0.0624% | 0% | 0% | 41.85% | 0% | 24.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.36% | 11.78% | CZ 3B | 0% | 0% | 0% | 22.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.39% | 11.78% | CZ 3B | 8.535% | 44.99% | 0.0624% | 22.39% | 0% | 41.85% | 0% | 24.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.45% | 11.78%
CZ 3C | 8.535% | 45% | 0.04356% | 38.57% | 0% | 69.59% | 0% | 39.29% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.78% | 3.558% | CZ 3C | 8.535% | 45% | 0.04356% | 38.57% | 0% | 69.59% | 0% | 39.29% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 15.41% | 3.558% | CZ 3C | 8.535% | 45% | 0.04356% | 0% | 0% | 69.59% | 0% | 39.29% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.46% | 3.558% | CZ 3C | 0% | 0% | 0% | 38.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.57% | 3.558% | CZ 3C | 8.535% | 45% | 0.04356% | 38.57% | 0% | 69.59% | 0% | 39.29% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.81% | 3.558%
CZ 4A | 8.535% | 45% | 0.1243% | 40.25% | 0% | 30.58% | 0% | 13.81% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 11.25% | 23.14% | CZ 4A | 8.535% | 45% | 0.1243% | 40.25% | 0% | 30.58% | 0% | 13.81% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.85% | 23.14% | CZ 4A | 8.535% | 45% | 0.1243% | 0% | 0% | 30.58% | 0% | 13.81% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 9.096% | 23.14% | CZ 4A | 0% | 0% | 0% | 40.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.25% | 23.14% | CZ 4A | 8.535% | 45% | 0.1243% | 40.25% | 0% | 30.58% | 0% | 13.81% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 11.42% | 23.14%
CZ 4B | 8.535% | 45.01% | 0.1388% | 51.57% | 0% | 26.64% | 0% | 13.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 9.992% | 0.2995% | CZ 4B | 8.535% | 45.01% | 0.1388% | 51.57% | 0% | 26.64% | 0% | 13.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 12.44% | 0.2995% | CZ 4B | 8.535% | 45.01% | 0.1388% | 0% | 0% | 26.64% | 0% | 13.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 8.688% | 0.2995% | CZ 4B | 0% | 0% | 0% | 51.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.57% | 0.2995% | CZ 4B | 8.535% | 45.01% | 0.1388% | 51.57% | 0% | 26.64% | 0% | 13.16% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.1% | 0.2995%
CZ 4C | 8.535% | 45.01% | 0.1323% | 44.91% | 0% | 25.81% | 0% | 11.38% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 9.094% | 5.067% | CZ 4C | 8.535% | 45.01% | 0.1323% | 44.91% | 0% | 25.81% | 0% | 11.38% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 12.75% | 5.067% | CZ 4C | 8.535% | 45.01% | 0.1323% | 0% | 0% | 25.81% | 0% | 11.38% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 6.999% | 5.067% | CZ 4C | 0% | 0% | 0% | 44.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.91% | 5.067% | CZ 4C | 8.535% | 45.01% | 0.1323% | 44.91% | 0% | 25.81% | 0% | 11.38% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 9.268% | 5.067%
CZ 5A | 8.535% | 45.01% | 0.1079% | 37.88% | 0% | 30.67% | 0% | 14.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 12% | 15.32% | CZ 5A | 8.535% | 45.01% | 0.1079% | 37.88% | 0% | 30.67% | 0% | 14.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 17.07% | 15.32% | CZ 5A | 8.535% | 45.01% | 0.1079% | 0% | 0% | 30.67% | 0% | 14.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 8.512% | 15.32% | CZ 5A | 0% | 0% | 0% | 37.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.88% | 15.32% | CZ 5A | 8.535% | 45.01% | 0.1079% | 37.88% | 0% | 30.67% | 0% | 14.24% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 12.27% | 15.32%
CZ 5B | 8.535% | 45% | 0.1187% | 43.61% | 0% | 25.97% | 0% | 14.49% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.3% | 4.35% | CZ 5B | 8.535% | 45% | 0.1187% | 43.61% | 0% | 25.97% | 0% | 14.49% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.05% | 4.35% | CZ 5B | 8.535% | 45% | 0.1187% | 0% | 0% | 25.97% | 0% | 14.49% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 8.102% | 4.35% | CZ 5B | 0% | 0% | 0% | 43.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.61% | 4.35% | CZ 5B | 8.535% | 45% | 0.1187% | 43.61% | 0% | 25.97% | 0% | 14.49% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.48% | 4.35%
CZ 5C | 8.535% | 45.01% | 0.1269% | 44.63% | 0% | 16.95% | 0% | 7.003% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 8.678% | 0% | CZ 5C | 8.535% | 45.01% | 0.1269% | 44.63% | 0% | 16.95% | 0% | 7.003% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.1% | 0% | CZ 5C | 8.535% | 45.01% | 0.1269% | 0% | 0% | 16.95% | 0% | 7.003% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 5.273% | 0% | CZ 5C | 0% | 0% | 0% | 44.63% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.63% | 0% | CZ 5C | 8.535% | 45.01% | 0.1269% | 44.63% | 0% | 16.95% | 0% | 7.003% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 8.951% | 0%
CZ 6A | 8.535% | 45% | 0.1098% | 38.06% | 0% | 28.52% | 0% | 13.4% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 11.64% | 4.28% | CZ 6A | 8.535% | 45% | 0.1098% | 38.06% | 0% | 28.52% | 0% | 13.4% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 17.56% | 4.28% | CZ 6A | 8.535% | 45% | 0.1098% | 0% | 0% | 28.52% | 0% | 13.4% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 7.305% | 4.28% | CZ 6A | 0% | 0% | 0% | 38.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.06% | 4.28% | CZ 6A | 8.535% | 45% | 0.1098% | 38.06% | 0% | 28.52% | 0% | 13.4% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 11.96% | 4.28%
CZ 6B | 8.535% | 44.99% | 0.1091% | 41.84% | 0% | 23.45% | 0% | 13.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.43% | 0.7689% | CZ 6B | 8.535% | 44.99% | 0.1091% | 41.84% | 0% | 23.45% | 0% | 13.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 15.57% | 0.7689% | CZ 6B | 8.535% | 44.99% | 0.1091% | 0% | 0% | 23.45% | 0% | 13.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 7.126% | 0.7689% | CZ 6B | 0% | 0% | 0% | 41.84% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.84% | 0.7689% | CZ 6B | 8.535% | 44.99% | 0.1091% | 41.84% | 0% | 23.45% | 0% | 13.54% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.69% | 0.7689%
CZ 7 | 8.535% | 45% | 0.09598% | 39.71% | 0% | 25.8% | 0% | 16.13% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 13.13% | 0.4435% | CZ 7 | 8.535% | 45% | 0.09598% | 39.71% | 0% | 25.8% | 0% | 16.13% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 20.37% | 0.4435% | CZ 7 | 8.535% | 45% | 0.09598% | 0% | 0% | 25.8% | 0% | 16.13% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 7.208% | 0.4435% | CZ 7 | 0% | 0% | 0% | 39.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.71% | 0.4435% | CZ 7 | 8.535% | 45% | 0.09598% | 39.71% | 0% | 25.8% | 0% | 16.13% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 13.55% | 0.4435%
CZ 8 | 8.535% | 45% | 0.06497% | 25.33% | 0% | 21.78% | 0% | 10.6% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 9.813% | 0% | CZ 8 | 8.535% | 45% | 0.06497% | 25.33% | 0% | 21.78% | 0% | 10.6% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 14.43% | 0% | CZ 8 | 8.535% | 45% | 0.06497% | 0% | 0% | 21.78% | 0% | 10.6% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 5.787% | 0% | CZ 8 | 0% | 0% | 0% | 25.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.33% | 0% | CZ 8 | 8.535% | 45% | 0.06497% | 25.33% | 0% | 21.78% | 0% | 10.6% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 10.09% | 0%
Us Weighted | 8.535% | 45% | 0.1041% | 38.5% | 0% | 36.83% | 0% | 20.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 13.23% | 100% | Us Weighted | 8.535% | 45% | 0.1041% | 38.5% | 0% | 36.83% | 0% | 20.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 15.85% | 100% | Us Weighted | 8.535% | 45% | 0.1041% | 0% | 0% | 36.83% | 0% | 20.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 11.73% | 100% | Us Weighted | 0% | 0% | 0% | 38.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.5% | 100% | Us Weighted | 8.535% | 45% | 0.1041% | 38.5% | 0% | 36.83% | 0% | 20.22% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 13.36% | 100%

## Hospital
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Hospital |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Hospital | [14 empty] | Prototype Floor Area: | 241501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.41699 | 0.024405 | 0.048881 | 0.3056 | 0.082409 | 0.29901 | 0.058139 | 0.34464 | 0.028414 | 0.064223 | 0.024782 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 2.9302 |  | STD2013 | 13.7903 | 0.8071 | 4.724 | 26.3994 | 2.7254 | 9.8885 | 1.9227 | 11.3976 | 0.93968 | 2.1239 | 0.81958 | 9.843 | 0.40481 | 16.9886 | 0 | 20.9005 | 123.6752 |  | STD2013 | 4.0405 | 0.23648 | 0.03045 | 0.6374 | 0.79853 | 2.8973 | 0.56336 | 3.3395 | 0.27532 | 0.62231 | 0.24013 | 2.884 | 0.11861 | 1.7663 | 0 | 6.1246 | 24.5747 |  | STD2013 | 0 | 0 | 0.0462 | 0.24224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.39804 |  | STD2013 | 42.3004 | 2.4757 | 5.3685 | 33.1497 | 8.3598 | 30.332 | 5.8978 | 34.9608 | 2.8824 | 6.5149 | 2.514 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 300.779
STD2010 | 0.42577 | 0.024405 | 0.048878 | 0.38815 | 0.15368 | 0.31715 | 0.0672 | 0.35248 | 0.022623 | 0.071649 | 0.031664 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1392 |  | STD2010 | 14.0807 | 0.8071 | 4.7237 | 29.8027 | 5.0826 | 10.4885 | 2.2224 | 11.6571 | 0.74817 | 2.3695 | 1.0472 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 131.2603 |  | STD2010 | 4.1256 | 0.23648 | 0.030454 | 1.3413 | 1.4892 | 3.0731 | 0.65115 | 3.4155 | 0.21921 | 0.69427 | 0.30682 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 26.504 |  | STD2010 | 0 | 0 | 0.046198 | 0.25225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.40805 |  | STD2010 | 43.1909 | 2.4757 | 5.3682 | 41.6127 | 15.5902 | 32.1723 | 6.8169 | 35.7568 | 2.2949 | 7.2683 | 3.2121 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 322.0698
STD2007 | 0.49652 | 0.031021 | 0.049175 | 0.61872 | 0.21134 | 0.47328 | 0.080479 | 0.51116 | 0 | 0.1345 | 0.031754 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.9036 |  | STD2007 | 16.4205 | 1.0259 | 4.7353 | 54.7467 | 6.9891 | 15.6519 | 2.6615 | 16.9047 | 0 | 4.4481 | 1.0502 | 9.9723 | 0.68133 | 16.9886 | 0 | 21.5845 | 173.8606 |  | STD2007 | 4.8112 | 0.30059 | 0.033084 | 1.1055 | 2.0478 | 4.586 | 0.77982 | 4.953 | 0 | 1.3033 | 0.30769 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.4406 |  | STD2007 | 0 | 0 | 0.046223 | 0.50974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.66556 |  | STD2007 | 50.3681 | 3.1469 | 5.3986 | 67.2873 | 21.4384 | 48.0105 | 8.164 | 51.8533 | 0 | 13.6441 | 3.2212 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 401.8983
STD2004 | 0.49652 | 0.031021 | 0.049164 | 0.57701 | 0.21199 | 0.48871 | 0.077763 | 0.52691 | 0 | 0.13034 | 0.031717 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.8868 |  | STD2004 | 16.4205 | 1.0259 | 4.734 | 50.5168 | 7.0107 | 16.1624 | 2.5717 | 17.4257 | 0 | 4.3104 | 1.0489 | 9.9723 | 0.68134 | 16.9886 | 0 | 21.5845 | 170.4538 |  | STD2004 | 4.8112 | 0.30059 | 0.033094 | 1.1077 | 2.0541 | 4.7355 | 0.75351 | 5.1057 | 0 | 1.2629 | 0.30733 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.6845 |  | STD2004 | 0 | 0 | 0.04621 | 0.46736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.62318 |  | STD2004 | 50.3681 | 3.1469 | 5.3973 | 62.6794 | 21.5045 | 49.5763 | 7.8885 | 53.4515 | 0 | 13.2218 | 3.2175 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 399.8176
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | -1.1675e-05 | -0.041718 | 0.00065119 | 0.015435 | -0.0027159 | 0.015755 | 0 | -0.004163 | -3.7006e-05 | 0 | 4.0488e-07 | 0 | 0 | 0 | -0.016804 |  | 2004-2007 | 0 | 0 | -0.0012526 | -4.2298 | 0.021536 | 0.51044 | -0.089819 | 0.52103 | 0 | -0.13768 | -0.0012238 | 0 | 1.339e-05 | 0 | 0 | 0 | -3.4068 |  | 2004-2007 | 0 | 0 | 1.0458e-05 | 0.0022715 | 0.0063099 | 0.14956 | -0.026317 | 0.15266 | 0 | -0.040339 | -0.00035858 | 0 | 3.9232e-06 | 0 | 0 | 0 | 0.2438 |  | 2004-2007 | 0 | 0 | -1.2883e-05 | -0.042376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.042389 |  | 2004-2007 | 0 | 0 | -0.0012986 | -4.6079 | 0.066058 | 1.5657 | -0.27551 | 1.5982 | 0 | -0.4223 | -0.003754 | 0 | 4.1072e-05 | 0 | 0 | 0 | -2.0807
2007-2010 | 0.07075 | 0.006616 | 0.00029696 | 0.23058 | 0.057651 | 0.15613 | 0.013279 | 0.15868 | -0.022623 | 0.062851 | 9.0154e-05 | 0.0032607 | 0.0082832 | 0 | 0 | 0.018573 | 0.76441 |  | 2007-2010 | 2.3398 | 0.2188 | 0.011559 | 24.944 | 1.9066 | 5.1634 | 0.43915 | 5.2476 | -0.74817 | 2.0786 | 0.0029815 | 0.10784 | 0.27394 | 0 | 0 | 0.61425 | 42.6003 |  | 2007-2010 | 0.68556 | 0.064108 | 0.0026295 | -0.23582 | 0.55862 | 1.5129 | 0.12867 | 1.5375 | -0.21921 | 0.60902 | 0.00087358 | 0.031596 | 0.080263 | 0 | 0 | 0.17997 | 4.9367 |  | 2007-2010 | 0 | 0 | 2.5844e-05 | 0.25749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25751 |  | 2007-2010 | 7.1771 | 0.67115 | 0.030353 | 25.6747 | 5.8482 | 15.8382 | 1.347 | 16.0965 | -2.2949 | 6.3758 | 0.0091455 | 0.33078 | 0.84027 | 0 | 0 | 1.8841 | 79.8285
2010-2013 | 0.008779 | 0 | -2.4252e-06 | 0.08255 | 0.071275 | 0.018142 | 0.0090606 | 0.0078466 | -0.0057908 | 0.0074266 | 0.0068819 | 0.0006493 | 7.789e-05 | 0 | 0 | 0.0021093 | 0.20901 |  | 2010-2013 | 0.29033 | 0 | -0.00027788 | 3.4033 | 2.3572 | 0.59998 | 0.29965 | 0.2595 | -0.19151 | 0.24561 | 0.22759 | 0.021473 | 0.0025759 | 0 | 0 | 0.069758 | 7.5851 |  | 2010-2013 | 0.085067 | 0 | 4.6949e-06 | 0.70388 | 0.69064 | 0.17579 | 0.087795 | 0.076032 | -0.056112 | 0.071962 | 0.066684 | 0.0062916 | 0.00075474 | 0 | 0 | 0.020439 | 1.9292 |  | 2010-2013 | 0 | 0 | -2.9391e-06 | 0.01001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010007 |  | 2010-2013 | 0.89057 | 0 | -0.00027209 | 8.4629 | 7.2304 | 1.8404 | 0.91913 | 0.79598 | -0.58744 | 0.75337 | 0.69812 | 0.065867 | 0.0079014 | 0 | 0 | 0.21398 | 21.2909
2004-2013 | 0.079529 | 0.006616 | 0.00028286 | 0.27141 | 0.12958 | 0.18971 | 0.019623 | 0.18228 | -0.028414 | 0.066115 | 0.006935 | 0.00391 | 0.0083615 | 0 | 0 | 0.020683 | 0.95661 |  | 2004-2013 | 2.6301 | 0.2188 | 0.010029 | 24.1174 | 4.2853 | 6.2738 | 0.64898 | 6.0282 | -0.93968 | 2.1865 | 0.22935 | 0.12931 | 0.27653 | 0 | 0 | 0.684 | 46.7787 |  | 2004-2013 | 0.77063 | 0.064108 | 0.0026447 | 0.47033 | 1.2556 | 1.8382 | 0.19015 | 1.7662 | -0.27532 | 0.64064 | 0.067199 | 0.037888 | 0.081022 | 0 | 0 | 0.20041 | 7.1097 |  | 2004-2013 | 0 | 0 | 1.0022e-05 | 0.22512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22513 |  | 2004-2013 | 8.0677 | 0.67115 | 0.028783 | 29.5297 | 13.1447 | 19.2443 | 1.9907 | 18.4907 | -2.8824 | 6.7069 | 0.70351 | 0.39665 | 0.84822 | 0 | 0 | 2.0981 | 99.0387
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | -0.02375% | -7.23% | 0.3072% | 3.158% | -3.493% | 2.99% |  | -3.194% | -0.1167% | 0% | 0.001965% | 0% |  | 0% | -0.4323% |  | 2004-2007 | 0% | 0% | -0.02646% | -8.373% | 0.3072% | 3.158% | -3.493% | 2.99% |  | -3.194% | -0.1167% | 0% | 0.001965% | 0% |  | 0% | -1.999% |  | 2004-2007 | 0% | 0% | 0.0316% | 0.2051% | 0.3072% | 3.158% | -3.493% | 2.99% |  | -3.194% | -0.1167% | 0% | 0.001965% | 0% |  | 0% | 0.7695% |  | 2004-2007 |  |  | -0.02788% | -9.067% | [9 empty] | 0% |  |  | -6.802% |  | 2004-2007 | 0% | 0% | -0.02406% | -7.352% | 0.3072% | 3.158% | -3.493% | 2.99% |  | -3.194% | -0.1167% | 0% | 0.001965% | 0% |  | 0% | -0.5204%
2007-2010 | 14.25% | 21.33% | 0.6039% | 37.27% | 27.28% | 32.99% | 16.5% | 31.04% |  | 46.73% | 0.2839% | 1.081% | 40.21% | 0% |  | 2.846% | 19.58% |  | 2007-2010 | 14.25% | 21.33% | 0.2441% | 45.56% | 27.28% | 32.99% | 16.5% | 31.04% |  | 46.73% | 0.2839% | 1.081% | 40.21% | 0% |  | 2.846% | 24.5% |  | 2007-2010 | 14.25% | 21.33% | 7.948% | -21.33% | 27.28% | 32.99% | 16.5% | 31.04% |  | 46.73% | 0.2839% | 1.081% | 40.21% | 0% |  | 2.845% | 15.7% |  | 2007-2010 |  |  | 0.05591% | 50.51% | [9 empty] | 0% |  |  | 38.69% |  | 2007-2010 | 14.25% | 21.33% | 0.5623% | 38.16% | 27.28% | 32.99% | 16.5% | 31.04% |  | 46.73% | 0.2839% | 1.081% | 40.21% | 0% |  | 2.845% | 19.86%
2010-2013 | 2.062% | 0% | -0.004962% | 21.27% | 46.38% | 5.72% | 13.48% | 2.226% | -25.6% | 10.37% | 21.73% | 0.2177% | 0.6323% | 0% |  | 0.3326% | 6.658% |  | 2010-2013 | 2.062% | 0% | -0.005883% | 11.42% | 46.38% | 5.72% | 13.48% | 2.226% | -25.6% | 10.37% | 21.73% | 0.2177% | 0.6323% | 0% |  | 0.3327% | 5.779% |  | 2010-2013 | 2.062% | 0% | 0.01542% | 52.48% | 46.38% | 5.72% | 13.48% | 2.226% | -25.6% | 10.37% | 21.73% | 0.2177% | 0.6323% | 0% |  | 0.3326% | 7.279% |  | 2010-2013 |  |  | -0.006362% | 3.968% | [9 empty] | 0% |  |  | 2.452% |  | 2010-2013 | 2.062% | 0% | -0.005069% | 20.34% | 46.38% | 5.72% | 13.48% | 2.226% | -25.6% | 10.37% | 21.73% | 0.2177% | 0.6323% | 0% |  | 0.3326% | 6.611%
2004-2013 | 16.02% | 21.33% | 0.5753% | 47.04% | 61.13% | 38.82% | 25.24% | 34.59% |  | 50.73% | 21.87% | 1.297% | 40.59% | 0% |  | 3.169% | 24.61% |  | 2004-2013 | 16.02% | 21.33% | 0.2118% | 47.74% | 61.13% | 38.82% | 25.24% | 34.59% |  | 50.73% | 21.87% | 1.297% | 40.59% | 0% |  | 3.169% | 27.44% |  | 2004-2013 | 16.02% | 21.33% | 7.991% | 42.46% | 61.13% | 38.82% | 25.24% | 34.59% |  | 50.73% | 21.87% | 1.297% | 40.59% | 0% |  | 3.169% | 22.44% |  | 2004-2013 |  |  | 0.02169% | 48.17% | [9 empty] | 0% |  |  | 36.13% |  | 2004-2013 | 16.02% | 21.33% | 0.5333% | 47.11% | 61.13% | 38.82% | 25.24% | 34.59% |  | 50.73% | 21.87% | 1.297% | 40.59% | 0% |  | 3.169% | 24.77%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.41712 | 0.024455 | 0.039607 | 0.15941 | 0.001942 | 0.60787 | 0.17758 | 0.33475 | 0.032729 | 0.10132 | 0.026604 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 3.1561 | 1.17% | CZ 1A | 13.7948 | 0.80876 | 3.7873 | 16.0199 | 0.064224 | 20.1032 | 5.8729 | 11.0707 | 1.0824 | 3.3507 | 0.87982 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 124.9714 | 1.17% | CZ 1A | 4.0418 | 0.23696 | 0.030446 | 0.011709 | 0.018817 | 5.8902 | 1.7207 | 3.2437 | 0.31713 | 0.98174 | 0.25778 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 27.6445 | 1.17% | CZ 1A | 0 | 0 | 0.036834 | 0.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.30624 | 1.17% | CZ 1A | 42.314 | 2.4808 | 4.3447 | 17.5886 | 0.197 | 61.6643 | 18.0144 | 33.9581 | 3.3201 | 10.2779 | 2.6987 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 322.8814 | 1.17%
CZ 1B | 0.41734 | 0.024434 | 0.037977 | 0.18891 | 0.11639 | 0.41393 | 0.042072 | 0.35964 | 0.032729 | 0.078034 | 0.026135 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.9703 | 0% | CZ 1B | 13.8021 | 0.80805 | 3.6226 | 15.7936 | 3.8491 | 13.6893 | 1.3914 | 11.8937 | 1.0824 | 2.5807 | 0.86431 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 117.5139 | 0% | CZ 1B | 4.044 | 0.23676 | 0.030446 | 0.46903 | 1.1278 | 4.0109 | 0.40767 | 3.4848 | 0.31713 | 0.75613 | 0.25324 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 26.0313 | 0% | CZ 1B | 0 | 0 | 0.035186 | 0.14193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.28672 | 0% | CZ 1B | 42.3363 | 2.4786 | 4.1646 | 20.423 | 11.8067 | 41.9903 | 4.2679 | 36.4825 | 3.3201 | 7.9159 | 2.6512 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 303.8601 | 0%
CZ 2A | 0.41734 | 0.024412 | 0.043324 | 0.22247 | 0.021673 | 0.46559 | 0.11877 | 0.33026 | 0.029725 | 0.083832 | 0.025822 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 3.0159 | 13.88% | CZ 2A | 13.8021 | 0.80735 | 4.1627 | 21.1654 | 0.71674 | 15.3977 | 3.9278 | 10.9222 | 0.98306 | 2.7724 | 0.85399 | 9.843 | 0.40484 | 16.9886 | 0 | 20.9005 | 123.6483 | 13.88% | CZ 2A | 4.044 | 0.23655 | 0.030446 | 0.18625 | 0.21 | 4.5115 | 1.1508 | 3.2002 | 0.28803 | 0.81232 | 0.25022 | 2.884 | 0.11862 | 1.7663 | 0 | 6.1246 | 25.8137 | 13.88% | CZ 2A | 0 | 0 | 0.040588 | 0.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.35549 | 13.88% | CZ 2A | 42.3363 | 2.4765 | 4.755 | 24.3888 | 2.1985 | 47.2307 | 12.0482 | 33.5026 | 3.0154 | 8.5042 | 2.6195 | 30.1923 | 1.2418 | 30.4706 | 0 | 64.1183 | 309.0987 | 13.88%
CZ 2B | 0.41734 | 0.024396 | 0.041153 | 0.19078 | 0.066217 | 0.36598 | 0.059088 | 0.34372 | 0.028223 | 0.070127 | 0.025952 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.8657 | 2.777% | CZ 2B | 13.8021 | 0.8068 | 3.9434 | 17.6685 | 2.1899 | 12.1033 | 1.9541 | 11.3672 | 0.93336 | 2.3192 | 0.85827 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 116.083 | 2.777% | CZ 2B | 4.044 | 0.23639 | 0.030446 | 0.22846 | 0.64163 | 3.5462 | 0.57255 | 3.3306 | 0.27347 | 0.67952 | 0.25147 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 24.7281 | 2.777% | CZ 2B | 0 | 0 | 0.038395 | 0.16889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.31689 | 2.777% | CZ 2B | 42.3363 | 2.4748 | 4.5153 | 20.8512 | 6.7172 | 37.1257 | 5.994 | 34.8675 | 2.863 | 7.1139 | 2.6326 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 293.5144 | 2.777%
CZ 3A | 0.41739 | 0.024427 | 0.046237 | 0.27936 | 0.056713 | 0.36511 | 0.084226 | 0.33477 | 0.028883 | 0.07487 | 0.025217 | 0.29763 | 0.012243 | 0.29079 | 0 | 0.63204 | 2.9699 | 13.57% | CZ 3A | 13.8038 | 0.80782 | 4.457 | 25.0395 | 1.8756 | 12.0747 | 2.7855 | 11.0713 | 0.95519 | 2.4761 | 0.83397 | 9.843 | 0.40488 | 16.9886 | 0 | 20.9005 | 124.3174 | 13.57% | CZ 3A | 4.0445 | 0.23669 | 0.030446 | 0.45336 | 0.54954 | 3.5379 | 0.81614 | 3.2439 | 0.27987 | 0.72548 | 0.24435 | 2.884 | 0.11863 | 1.7663 | 0 | 6.1246 | 25.0555 | 13.57% | CZ 3A | 0 | 0 | 0.043531 | 0.23492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.38806 | 13.57% | CZ 3A | 42.3417 | 2.4779 | 5.0766 | 30.4232 | 5.7532 | 37.0379 | 8.5442 | 33.96 | 2.9299 | 7.595 | 2.5581 | 30.1923 | 1.2419 | 30.4706 | 0 | 64.1183 | 304.7209 | 13.57%
CZ 3B | 0.41732 | 0.02443 | 0.045265 | 0.21349 | 0.10625 | 0.27329 | 0.038236 | 0.36549 | 0.02709 | 0.056337 | 0.025132 | 0.29763 | 0.012239 | 0.29079 | 0 | 0.63204 | 2.825 | 7.904% | CZ 3B | 13.8014 | 0.80794 | 4.3587 | 18.5584 | 3.5138 | 9.0381 | 1.2645 | 12.0874 | 0.89591 | 1.8631 | 0.83114 | 9.843 | 0.40476 | 16.9886 | 0 | 20.9005 | 115.1573 | 7.904% | CZ 3B | 4.0438 | 0.23672 | 0.030446 | 0.4288 | 1.0295 | 2.6481 | 0.3705 | 3.5416 | 0.2625 | 0.5459 | 0.24352 | 2.884 | 0.11859 | 1.7663 | 0 | 6.1246 | 24.2748 | 7.904% | CZ 3B | 0 | 0 | 0.042548 | 0.17095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.3231 | 7.904% | CZ 3B | 42.3342 | 2.4783 | 4.9693 | 23.1738 | 10.7781 | 27.7233 | 3.8788 | 37.0767 | 2.7481 | 5.715 | 2.5494 | 30.1923 | 1.2416 | 30.4706 | 0 | 64.1183 | 289.4478 | 7.904%
CZ 3C | 0.41733 | 0.024393 | 0.04939 | 0.23448 | 0.0085715 | 0.14859 | 0.0093727 | 0.33363 | 0 | 0.036942 | 0.024639 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 2.52 | 1.133% | CZ 3C | 13.8017 | 0.80672 | 4.7754 | 22.9904 | 0.28347 | 4.914 | 0.30997 | 11.0335 | 0 | 1.2217 | 0.81485 | 9.843 | 0.40484 | 16.9886 | 0 | 20.9005 | 109.0887 | 1.133% | CZ 3C | 4.0439 | 0.23637 | 0.030446 | 0.099044 | 0.083056 | 1.4398 | 0.09082 | 3.2328 | 0 | 0.35797 | 0.23875 | 2.884 | 0.11862 | 1.7663 | 0 | 6.1246 | 20.7463 | 1.133% | CZ 3C | 0 | 0 | 0.046715 | 0.22652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.38284 | 1.133% | CZ 3C | 42.3353 | 2.4745 | 5.4247 | 25.7959 | 0.86952 | 15.0732 | 0.9508 | 33.8439 | 0 | 3.7475 | 2.4995 | 30.1923 | 1.2418 | 30.4706 | 0 | 64.1183 | 259.0379 | 1.133%
CZ 4A | 0.41667 | 0.024416 | 0.049807 | 0.32317 | 0.099534 | 0.283 | 0.055988 | 0.34308 | 0.029591 | 0.064401 | 0.024605 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.947 | 17.85% | CZ 4A | 13.7799 | 0.80747 | 4.8175 | 27.4171 | 3.2917 | 9.3591 | 1.8516 | 11.3462 | 0.97862 | 2.1298 | 0.81371 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 124.7296 | 17.85% | CZ 4A | 4.0375 | 0.23659 | 0.030446 | 0.74541 | 0.96447 | 2.7422 | 0.54252 | 3.3244 | 0.28673 | 0.62403 | 0.23841 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 24.6661 | 17.85% | CZ 4A | 0 | 0 | 0.047136 | 0.24873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.40547 | 17.85% | CZ 4A | 42.2682 | 2.4768 | 5.4707 | 34.9899 | 10.097 | 28.708 | 5.6796 | 34.8031 | 3.0018 | 6.533 | 2.496 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 302.5471 | 17.85%
CZ 4B | 0.41669 | 0.02441 | 0.049259 | 0.20043 | 0.13066 | 0.20029 | 0.017207 | 0.38114 | 0.027191 | 0.044791 | 0.024483 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.7492 | 0.6458% | CZ 4B | 13.7804 | 0.80727 | 4.7622 | 17.8586 | 4.3211 | 6.624 | 0.56906 | 12.6049 | 0.89925 | 1.4813 | 0.80971 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 112.6546 | 0.6458% | CZ 4B | 4.0376 | 0.23653 | 0.030446 | 0.34041 | 1.2661 | 1.9408 | 0.16673 | 3.6932 | 0.26348 | 0.43402 | 0.23724 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 23.54 | 0.6458% | CZ 4B | 0 | 0 | 0.046583 | 0.16697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.32315 | 0.6458% | CZ 4B | 42.2698 | 2.4762 | 5.4102 | 21.8134 | 13.2545 | 20.3184 | 1.7455 | 38.6641 | 2.7583 | 4.5437 | 2.4837 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 281.7609 | 0.6458%
CZ 4C | 0.41694 | 0.024403 | 0.051316 | 0.28482 | 0.025733 | 0.17161 | 0.015505 | 0.34319 | 0.028043 | 0.04267 | 0.024304 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 2.6612 | 3.07% | CZ 4C | 13.7889 | 0.80703 | 4.97 | 26.0762 | 0.85104 | 5.6753 | 0.51277 | 11.3499 | 0.92743 | 1.4112 | 0.80378 | 9.843 | 0.40484 | 16.9886 | 0 | 20.9005 | 115.3104 | 3.07% | CZ 4C | 4.0401 | 0.23646 | 0.030446 | 0.38418 | 0.24935 | 1.6629 | 0.15024 | 3.3255 | 0.27174 | 0.41346 | 0.2355 | 2.884 | 0.11862 | 1.7663 | 0 | 6.1246 | 21.8933 | 3.07% | CZ 4C | 0 | 0 | 0.048661 | 0.24765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.40591 | 3.07% | CZ 4C | 42.2959 | 2.4755 | 5.6374 | 31.0901 | 2.6105 | 17.4085 | 1.5729 | 34.8146 | 2.8448 | 4.3286 | 2.4655 | 30.1923 | 1.2418 | 30.4706 | 0 | 64.1183 | 273.5671 | 3.07%
CZ 5A | 0.4167 | 0.024386 | 0.052302 | 0.37534 | 0.10475 | 0.25528 | 0.043852 | 0.3475 | 0.02821 | 0.061361 | 0.024272 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.9666 | 23.55% | CZ 5A | 13.7808 | 0.80648 | 5.0695 | 31.4255 | 3.4643 | 8.4424 | 1.4503 | 11.4923 | 0.93293 | 2.0293 | 0.80272 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 127.8332 | 23.55% | CZ 5A | 4.0377 | 0.2363 | 0.030457 | 0.92529 | 1.015 | 2.4736 | 0.42492 | 3.3672 | 0.27335 | 0.59457 | 0.23519 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 24.5071 | 23.55% | CZ 5A | 0 | 0 | 0.049655 | 0.28267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.44193 | 23.55% | CZ 5A | 42.271 | 2.4738 | 5.7462 | 40.5832 | 10.6262 | 25.896 | 4.4485 | 35.2513 | 2.8617 | 6.2246 | 2.4622 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 304.8677 | 23.55%
CZ 5B | 0.41697 | 0.024375 | 0.051854 | 0.32145 | 0.094336 | 0.18221 | 0.0098831 | 0.35912 | 0.028313 | 0.044722 | 0.024094 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.79 | 6.333% | CZ 5B | 13.7898 | 0.80613 | 5.0243 | 26.6438 | 3.1198 | 6.0258 | 0.32685 | 11.8767 | 0.93634 | 1.479 | 0.79683 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 118.9623 | 6.333% | CZ 5B | 4.0404 | 0.23619 | 0.030446 | 0.83088 | 0.9141 | 1.7655 | 0.095766 | 3.4798 | 0.27435 | 0.43335 | 0.23347 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 23.2277 | 6.333% | CZ 5B | 0 | 0 | 0.049204 | 0.23808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.39689 | 6.333% | CZ 5B | 42.2986 | 2.4727 | 5.6968 | 34.7206 | 9.5697 | 18.4834 | 1.0026 | 36.4305 | 2.8721 | 4.5367 | 2.4442 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 286.5509 | 6.333%
CZ 5C | 0.41765 | 0.024361 | 0.05233 | 0.31764 | 0.037624 | 0.14226 | 0.0081786 | 0.34298 | 0.028201 | 0.03779 | 0.023999 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.6657 | 0% | CZ 5C | 13.8123 | 0.80566 | 5.0724 | 28.023 | 1.2443 | 4.7046 | 0.27048 | 11.3428 | 0.93265 | 1.2498 | 0.79369 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 116.3885 | 0% | CZ 5C | 4.047 | 0.23606 | 0.030446 | 0.5793 | 0.36457 | 1.3784 | 0.079249 | 3.3234 | 0.27327 | 0.36618 | 0.23255 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 21.8038 | 0% | CZ 5C | 0 | 0 | 0.049685 | 0.26046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.41975 | 0% | CZ 5C | 42.3678 | 2.4713 | 5.7493 | 34.5328 | 3.8167 | 14.4309 | 0.82966 | 34.7926 | 2.8608 | 3.8335 | 2.4346 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 274.1428 | 0%
CZ 6A | 0.41681 | 0.024387 | 0.054517 | 0.41185 | 0.13685 | 0.20196 | 0.025807 | 0.34672 | 0.028271 | 0.051631 | 0.023965 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.9555 | 6.413% | CZ 6A | 13.7843 | 0.80652 | 5.2932 | 33.9469 | 4.5258 | 6.6791 | 0.85347 | 11.4665 | 0.93497 | 1.7075 | 0.79255 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 128.9278 | 6.413% | CZ 6A | 4.0388 | 0.23631 | 0.030457 | 1.0917 | 1.326 | 1.957 | 0.25007 | 3.3597 | 0.27394 | 0.50029 | 0.23222 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 24.1899 | 6.413% | CZ 6A | 0 | 0 | 0.051893 | 0.30221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.46371 | 6.413% | CZ 6A | 42.282 | 2.4739 | 5.9907 | 44.4607 | 13.8824 | 20.4874 | 2.6179 | 35.1723 | 2.8679 | 5.2376 | 2.4311 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 303.9268 | 6.413%
CZ 6B | 0.41685 | 0.02437 | 0.054836 | 0.35961 | 0.13595 | 0.13989 | 0.0051042 | 0.37215 | 0.0289 | 0.038437 | 0.023696 | 0.29763 | 0.012239 | 0.29079 | 0 | 0.63204 | 2.8325 | 0.6868% | CZ 6B | 13.7859 | 0.80593 | 5.3254 | 28.8719 | 4.4962 | 4.6263 | 0.1688 | 12.3076 | 0.95578 | 1.2712 | 0.78368 | 9.843 | 0.40476 | 16.9886 | 0 | 20.9005 | 121.5355 | 0.6868% | CZ 6B | 4.0392 | 0.23614 | 0.030457 | 1.0628 | 1.3174 | 1.3555 | 0.049459 | 3.6061 | 0.28004 | 0.37245 | 0.22962 | 2.884 | 0.11859 | 1.7663 | 0 | 6.1246 | 23.4726 | 0.6868% | CZ 6B | 0 | 0 | 0.052214 | 0.25244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.41426 | 0.6868% | CZ 6B | 42.2867 | 2.4721 | 6.0259 | 38.719 | 13.7915 | 14.1908 | 0.51778 | 37.7522 | 2.9317 | 3.8992 | 2.4038 | 30.1923 | 1.2416 | 30.4706 | 0 | 64.1183 | 291.0134 | 0.6868%
CZ 7 | 0.41652 | 0.024371 | 0.058022 | 0.46122 | 0.15472 | 0.16139 | 0.015307 | 0.35693 | 0.02886 | 0.046564 | 0.023653 | 0.29763 | 0.01224 | 0.29079 | 0 | 0.63204 | 2.9803 | 0.9776% | CZ 7 | 13.775 | 0.80597 | 5.6473 | 37.3445 | 5.117 | 5.3374 | 0.50621 | 11.8042 | 0.95444 | 1.54 | 0.78223 | 9.843 | 0.4048 | 16.9886 | 0 | 20.9005 | 131.751 | 0.9776% | CZ 7 | 4.036 | 0.23615 | 0.030457 | 1.3183 | 1.4993 | 1.5638 | 0.14832 | 3.4586 | 0.27965 | 0.4512 | 0.22919 | 2.884 | 0.1186 | 1.7663 | 0 | 6.1246 | 24.1444 | 0.9776% | CZ 7 | 0 | 0 | 0.055433 | 0.32845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.49349 | 0.9776% | CZ 7 | 42.2532 | 2.4722 | 6.3777 | 49.7012 | 15.6957 | 16.3718 | 1.5527 | 36.2081 | 2.9276 | 4.7236 | 2.3994 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 306.7063 | 0.9776%
CZ 8 | 0.41736 | 0.024221 | 0.062348 | 0.6527 | 0.21693 | 0.11283 | 0.003567 | 0.35175 | 0.029557 | 0.035269 | 0.023307 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 3.1625 | 0.03822% | CZ 8 | 13.8028 | 0.80103 | 6.0843 | 52.0292 | 7.1742 | 3.7313 | 0.11797 | 11.6327 | 0.97749 | 1.1664 | 0.7708 | 9.843 | 0.40484 | 16.9886 | 0 | 20.9005 | 146.4252 | 0.03822% | CZ 8 | 4.0442 | 0.2347 | 0.030457 | 1.9825 | 2.102 | 1.0933 | 0.034564 | 3.4084 | 0.2864 | 0.34175 | 0.22584 | 2.884 | 0.11862 | 1.7663 | 0 | 6.1246 | 24.6775 | 0.03822% | CZ 8 | 0 | 0 | 0.059803 | 0.45263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.62204 | 0.03822% | CZ 8 | 42.3387 | 2.4571 | 6.8554 | 70.2275 | 22.006 | 11.4454 | 0.36185 | 35.6822 | 2.9983 | 3.5778 | 2.3644 | 30.1923 | 1.2418 | 30.4706 | 0 | 64.1183 | 326.3375 | 0.03822%
Us Weighted | 0.41699 | 0.024405 | 0.048881 | 0.3056 | 0.082409 | 0.29901 | 0.058139 | 0.34464 | 0.028414 | 0.064223 | 0.024782 | 0.29763 | 0.012241 | 0.29079 | 0 | 0.63204 | 2.9302 | 100% | Us Weighted | 13.7903 | 0.8071 | 4.724 | 26.3994 | 2.7254 | 9.8885 | 1.9227 | 11.3976 | 0.93968 | 2.1239 | 0.81958 | 9.843 | 0.40481 | 16.9886 | 0 | 20.9005 | 123.6752 | 100% | Us Weighted | 4.0405 | 0.23648 | 0.03045 | 0.6374 | 0.79853 | 2.8973 | 0.56336 | 3.3395 | 0.27532 | 0.62231 | 0.24013 | 2.884 | 0.11861 | 1.7663 | 0 | 6.1246 | 24.5747 | 100% | Us Weighted | 0 | 0 | 0.0462 | 0.24224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.39804 | 100% | Us Weighted | 42.3004 | 2.4757 | 5.3685 | 33.1497 | 8.3598 | 30.332 | 5.8978 | 34.9608 | 2.8824 | 6.5149 | 2.514 | 30.1923 | 1.2417 | 30.4706 | 0 | 64.1183 | 300.779 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.42583 | 0.024455 | 0.039605 | 0.16654 | 0.0052514 | 0.63507 | 0.18563 | 0.34968 | 0.032729 | 0.10465 | 0.033625 | 0.29828 | 0.01232 | 0.29079 | 0 | 0.63415 | 3.2386 | 1.17% | CZ 1A | 14.0829 | 0.80876 | 3.7871 | 16.414 | 0.17367 | 21.0026 | 6.1391 | 11.5645 | 1.0824 | 3.4608 | 1.112 | 9.8645 | 0.40743 | 16.9886 | 0 | 20.9702 | 127.8585 | 1.17% | CZ 1A | 4.1263 | 0.23696 | 0.030446 | 0.058246 | 0.050885 | 6.1537 | 1.7987 | 3.3884 | 0.31713 | 1.014 | 0.32582 | 2.8903 | 0.11938 | 1.7663 | 0 | 6.145 | 28.4215 | 1.17% | CZ 1A | 0 | 0 | 0.036832 | 0.16215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.30859 | 1.17% | CZ 1A | 43.1978 | 2.4808 | 4.3444 | 18.333 | 0.53272 | 64.4231 | 18.8311 | 35.4728 | 3.3201 | 10.6155 | 3.411 | 30.2582 | 1.2497 | 30.4706 | 0 | 64.3323 | 331.2732 | 1.17%
CZ 1B | 0.42591 | 0.024434 | 0.037975 | 0.25523 | 0.40405 | 0.46206 | 0.077762 | 0.3816 | 0 | 0.087741 | 0.033169 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.4255 | 0% | CZ 1B | 14.0853 | 0.80805 | 3.6224 | 16.7953 | 13.3625 | 15.2811 | 2.5717 | 12.6202 | 0 | 2.9017 | 1.0969 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 131.3759 | 0% | CZ 1B | 4.127 | 0.23676 | 0.030446 | 1.2816 | 3.9152 | 4.4773 | 0.7535 | 3.6977 | 0 | 0.8502 | 0.3214 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 30.612 | 0% | CZ 1B | 0 | 0 | 0.035184 | 0.12421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.269 | 0% | CZ 1B | 43.2052 | 2.4786 | 4.1644 | 26.9934 | 40.988 | 46.873 | 7.8884 | 38.7111 | 0 | 8.9007 | 3.3648 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 349.8783 | 0%
CZ 2A | 0.4259 | 0.024412 | 0.043322 | 0.25646 | 0.039279 | 0.48761 | 0.12845 | 0.34382 | 0.029704 | 0.08977 | 0.032778 | 0.29828 | 0.01232 | 0.29079 | 0 | 0.63415 | 3.137 | 13.88% | CZ 2A | 14.0851 | 0.80735 | 4.1625 | 22.7145 | 1.299 | 16.126 | 4.2479 | 11.3706 | 0.98235 | 2.9688 | 1.084 | 9.8645 | 0.40743 | 16.9886 | 0 | 20.9702 | 128.0789 | 13.88% | CZ 2A | 4.1269 | 0.23655 | 0.030446 | 0.455 | 0.3806 | 4.7249 | 1.2446 | 3.3316 | 0.28783 | 0.86985 | 0.31762 | 2.8903 | 0.11938 | 1.7663 | 0 | 6.145 | 26.9268 | 13.88% | CZ 2A | 0 | 0 | 0.040586 | 0.21162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.36181 | 13.88% | CZ 2A | 43.2046 | 2.4765 | 4.7547 | 27.893 | 3.9845 | 49.4647 | 13.03 | 34.8781 | 3.0133 | 9.1065 | 3.3251 | 30.2582 | 1.2497 | 30.4706 | 0 | 64.3323 | 321.4419 | 13.88%
CZ 2B | 0.42595 | 0.024396 | 0.041151 | 0.27821 | 0.21746 | 0.41595 | 0.078893 | 0.36131 | 0 | 0.077829 | 0.032943 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1896 | 2.777% | CZ 2B | 14.0866 | 0.8068 | 3.9432 | 20.3522 | 7.1918 | 13.7559 | 2.6091 | 11.949 | 0 | 2.5739 | 1.0895 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 126.5887 | 2.777% | CZ 2B | 4.1273 | 0.23639 | 0.030446 | 1.1054 | 2.1072 | 4.0304 | 0.76446 | 3.501 | 0 | 0.75415 | 0.31922 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 27.897 | 2.777% | CZ 2B | 0 | 0 | 0.038393 | 0.16579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.31379 | 2.777% | CZ 2B | 43.2092 | 2.4748 | 4.5151 | 29.6938 | 22.0601 | 42.1947 | 8.0031 | 36.6521 | 0 | 7.8952 | 3.3419 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 326.3506 | 2.777%
CZ 3A | 0.42577 | 0.024427 | 0.046237 | 0.33617 | 0.093104 | 0.37978 | 0.09349 | 0.34188 | 0.028779 | 0.082201 | 0.032137 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1195 | 13.57% | CZ 3A | 14.0809 | 0.80782 | 4.4568 | 27.3833 | 3.0791 | 12.5598 | 3.0918 | 11.3064 | 0.95177 | 2.7185 | 1.0628 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 129.7298 | 13.57% | CZ 3A | 4.1257 | 0.23669 | 0.030457 | 0.93747 | 0.90216 | 3.68 | 0.9059 | 3.3128 | 0.27887 | 0.79652 | 0.31141 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 26.4388 | 13.57% | CZ 3A | 0 | 0 | 0.043529 | 0.24184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.39497 | 13.57% | CZ 3A | 43.1916 | 2.4779 | 5.0766 | 36.2472 | 9.4447 | 38.5259 | 9.4839 | 34.6813 | 2.9195 | 8.3387 | 3.2601 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 319.958 | 13.57%
CZ 3B | 0.42575 | 0.02443 | 0.045262 | 0.30611 | 0.30341 | 0.29997 | 0.05199 | 0.3764 | 0 | 0.064408 | 0.032053 | 0.29828 | 0.012317 | 0.29079 | 0 | 0.63415 | 3.1653 | 7.904% | CZ 3B | 14.0801 | 0.80794 | 4.3584 | 21.1596 | 10.0342 | 9.9204 | 1.7194 | 12.4481 | 0 | 2.1301 | 1.06 | 9.8645 | 0.40735 | 16.9886 | 0 | 20.9702 | 125.9489 | 7.904% | CZ 3B | 4.1254 | 0.23672 | 0.030446 | 1.3921 | 2.94 | 2.9067 | 0.50378 | 3.6472 | 0 | 0.6241 | 0.31059 | 2.8903 | 0.11935 | 1.7663 | 0 | 6.145 | 27.638 | 7.904% | CZ 3B | 0 | 0 | 0.042545 | 0.16408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.31623 | 7.904% | CZ 3B | 43.1893 | 2.4783 | 4.9689 | 32.5081 | 30.7787 | 30.4298 | 5.274 | 38.183 | 0 | 6.5337 | 3.2516 | 30.2582 | 1.2495 | 30.4706 | 0 | 64.3323 | 323.9061 | 7.904%
CZ 3C | 0.42578 | 0.024393 | 0.049387 | 0.27162 | 0.02907 | 0.15669 | 0.01821 | 0.34825 | 0 | 0.044952 | 0.031486 | 0.29828 | 0.01232 | 0.29079 | 0 | 0.63415 | 2.6354 | 1.133% | CZ 3C | 14.0811 | 0.80672 | 4.7751 | 24.3542 | 0.96139 | 5.1819 | 0.60223 | 11.5171 | 0 | 1.4866 | 1.0413 | 9.8645 | 0.40743 | 16.9886 | 0 | 20.9702 | 113.0384 | 1.133% | CZ 3C | 4.1257 | 0.23637 | 0.030446 | 0.43956 | 0.28168 | 1.5183 | 0.17645 | 3.3745 | 0 | 0.43558 | 0.30509 | 2.8903 | 0.11938 | 1.7663 | 0 | 6.145 | 21.8446 | 1.133% | CZ 3C | 0 | 0 | 0.046712 | 0.22854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.38486 | 1.133% | CZ 3C | 43.1923 | 2.4745 | 5.4244 | 29.5812 | 2.949 | 15.8949 | 1.8473 | 35.3274 | 0 | 4.5601 | 3.194 | 30.2582 | 1.2497 | 30.4706 | 0 | 64.3323 | 270.7559 | 1.133%
CZ 4A | 0.42571 | 0.024416 | 0.049804 | 0.40097 | 0.14949 | 0.29812 | 0.063853 | 0.34948 | 0.029595 | 0.072037 | 0.031468 | 0.29828 | 0.012317 | 0.29079 | 0 | 0.63415 | 3.1305 | 17.85% | CZ 4A | 14.0787 | 0.80747 | 4.8171 | 30.5871 | 4.9438 | 9.8593 | 2.1117 | 11.5577 | 0.97874 | 2.3824 | 1.0407 | 9.8645 | 0.40735 | 16.9886 | 0 | 20.9702 | 131.3953 | 17.85% | CZ 4A | 4.125 | 0.23659 | 0.030457 | 1.4141 | 1.4485 | 2.8887 | 0.61873 | 3.3864 | 0.28677 | 0.69802 | 0.30492 | 2.8903 | 0.11935 | 1.7663 | 0 | 6.145 | 26.3591 | 17.85% | CZ 4A | 0 | 0 | 0.047132 | 0.25761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.41434 | 17.85% | CZ 4A | 43.1848 | 2.4768 | 5.4703 | 42.9607 | 15.1644 | 30.2422 | 6.4775 | 35.4519 | 3.0022 | 7.3076 | 3.1922 | 30.2582 | 1.2495 | 30.4706 | 0 | 64.3323 | 321.2412 | 17.85%
CZ 4B | 0.4257 | 0.02441 | 0.049255 | 0.34723 | 0.38505 | 0.21924 | 0.028453 | 0.39407 | 0 | 0.054185 | 0.031343 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1945 | 0.6458% | CZ 4B | 14.0784 | 0.80727 | 4.7618 | 22.3387 | 12.7341 | 7.2506 | 0.94098 | 13.0324 | 0 | 1.792 | 1.0366 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 127.0036 | 0.6458% | CZ 4B | 4.1249 | 0.23653 | 0.030446 | 1.8164 | 3.7311 | 2.1244 | 0.2757 | 3.8185 | 0 | 0.52504 | 0.30371 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 27.9076 | 0.6458% | CZ 4B | 0 | 0 | 0.046579 | 0.16139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.31758 | 0.6458% | CZ 4B | 43.184 | 2.4762 | 5.4098 | 36.6563 | 39.0604 | 22.2405 | 2.8863 | 39.9754 | 0 | 5.4967 | 3.1796 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 326.8759 | 0.6458%
CZ 4C | 0.42576 | 0.024403 | 0.051314 | 0.40122 | 0.082404 | 0.17541 | 0.023051 | 0.3501 | 0 | 0.050784 | 0.031131 | 0.29828 | 0.012317 | 0.29079 | 0 | 0.63415 | 2.8511 | 3.07% | CZ 4C | 14.0805 | 0.80703 | 4.9697 | 31.0228 | 2.7252 | 5.801 | 0.76232 | 11.5781 | 0 | 1.6795 | 1.0295 | 9.8645 | 0.40735 | 16.9886 | 0 | 20.9702 | 122.6864 | 3.07% | CZ 4C | 4.1256 | 0.23646 | 0.030457 | 1.3556 | 0.79848 | 1.6997 | 0.22336 | 3.3924 | 0 | 0.49209 | 0.30165 | 2.8903 | 0.11935 | 1.7663 | 0 | 6.145 | 23.5766 | 3.07% | CZ 4C | 0 | 0 | 0.048657 | 0.26396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.42222 | 3.07% | CZ 4C | 43.1905 | 2.4755 | 5.6371 | 43.0428 | 8.3593 | 17.7941 | 2.3383 | 35.5147 | 0 | 5.1517 | 3.158 | 30.2582 | 1.2495 | 30.4706 | 0 | 64.3323 | 292.9726 | 3.07%
CZ 5A | 0.42572 | 0.024386 | 0.052299 | 0.46063 | 0.16106 | 0.26956 | 0.051455 | 0.35209 | 0.028149 | 0.069237 | 0.031114 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1612 | 23.55% | CZ 5A | 14.079 | 0.80648 | 5.0692 | 34.9152 | 5.3266 | 8.9146 | 1.7017 | 11.6442 | 0.93093 | 2.2897 | 1.029 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 134.9374 | 23.55% | CZ 5A | 4.1251 | 0.2363 | 0.030457 | 1.6564 | 1.5607 | 2.612 | 0.49859 | 3.4117 | 0.27276 | 0.67089 | 0.30149 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 26.2973 | 23.55% | CZ 5A | 0 | 0 | 0.049652 | 0.29262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.45188 | 23.55% | CZ 5A | 43.1859 | 2.4738 | 5.7459 | 49.3241 | 16.3387 | 27.3446 | 5.2197 | 35.7172 | 2.8555 | 7.0236 | 3.1563 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 324.6961 | 23.55%
CZ 5B | 0.42577 | 0.024375 | 0.051853 | 0.49842 | 0.30088 | 0.19592 | 0.019047 | 0.3665 | 0 | 0.051342 | 0.03093 | 0.29828 | 0.01232 | 0.29079 | 0 | 0.63415 | 3.2006 | 6.333% | CZ 5B | 14.081 | 0.80613 | 5.0241 | 33.4561 | 9.9504 | 6.4794 | 0.62991 | 12.1207 | 0 | 1.698 | 1.0229 | 9.8645 | 0.40743 | 16.9886 | 0 | 20.9702 | 133.4992 | 6.333% | CZ 5B | 4.1257 | 0.23619 | 0.030457 | 2.4089 | 2.9154 | 1.8984 | 0.18456 | 3.5513 | 0 | 0.4975 | 0.29971 | 2.8903 | 0.11938 | 1.7663 | 0 | 6.145 | 27.0691 | 6.333% | CZ 5B | 0 | 0 | 0.049202 | 0.25235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.41115 | 6.333% | CZ 5B | 43.1918 | 2.4727 | 5.6966 | 52.8 | 30.5217 | 19.8748 | 1.9322 | 37.1789 | 0 | 5.2083 | 3.1377 | 30.2582 | 1.2497 | 30.4706 | 0 | 64.3323 | 328.3254 | 6.333%
CZ 5C | 0.42594 | 0.024361 | 0.052328 | 0.45146 | 0.10741 | 0.13959 | 0.013686 | 0.34974 | 0 | 0.044841 | 0.030802 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 2.8757 | 0% | CZ 5C | 14.0863 | 0.80566 | 5.0721 | 33.8889 | 3.5521 | 4.6163 | 0.45263 | 11.5662 | 0 | 1.483 | 1.0187 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 124.7726 | 0% | CZ 5C | 4.1273 | 0.23606 | 0.030457 | 1.6706 | 1.0408 | 1.3526 | 0.13262 | 3.3889 | 0 | 0.4345 | 0.29847 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 23.633 | 0% | CZ 5C | 0 | 0 | 0.049682 | 0.28187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.44116 | 0% | CZ 5C | 43.2082 | 2.4713 | 5.749 | 48.2979 | 10.8957 | 14.1599 | 1.3884 | 35.4782 | 0 | 4.5488 | 3.1247 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 295.6328 | 0%
CZ 6A | 0.42574 | 0.024387 | 0.054514 | 0.5386 | 0.19741 | 0.22575 | 0.032682 | 0.3511 | 0.028189 | 0.059941 | 0.030784 | 0.29828 | 0.01232 | 0.29079 | 0 | 0.63415 | 3.2046 | 6.413% | CZ 6A | 14.0799 | 0.80652 | 5.2929 | 40.9194 | 6.5286 | 7.4658 | 1.0808 | 11.6113 | 0.93226 | 1.9823 | 1.0181 | 9.8645 | 0.40743 | 16.9886 | 0 | 20.9702 | 139.9486 | 6.413% | CZ 6A | 4.1254 | 0.23631 | 0.030457 | 1.9233 | 1.9129 | 2.1875 | 0.31669 | 3.4021 | 0.27315 | 0.58082 | 0.29829 | 2.8903 | 0.11938 | 1.7663 | 0 | 6.145 | 26.2077 | 6.413% | CZ 6A | 0 | 0 | 0.05189 | 0.34355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.50505 | 6.413% | CZ 6A | 43.1886 | 2.4739 | 5.9904 | 57.6851 | 20.0257 | 22.9005 | 3.3154 | 35.6163 | 2.8596 | 6.0806 | 3.1228 | 30.2582 | 1.2497 | 30.4706 | 0 | 64.3323 | 329.5697 | 6.413%
CZ 6B | 0.42575 | 0.02437 | 0.054833 | 0.435 | 0.21936 | 0.17377 | 0.012045 | 0.37787 | 0.028885 | 0.047632 | 0.030505 | 0.29828 | 0.012317 | 0.29079 | 0 | 0.63415 | 3.0655 | 0.6868% | CZ 6B | 14.0801 | 0.80593 | 5.3251 | 33.2715 | 7.2546 | 5.7468 | 0.39834 | 12.4965 | 0.95527 | 1.5752 | 1.0089 | 9.8645 | 0.40735 | 16.9886 | 0 | 20.9702 | 131.149 | 0.6868% | CZ 6B | 4.1254 | 0.23614 | 0.030457 | 1.5216 | 2.1256 | 1.6838 | 0.11671 | 3.6615 | 0.27989 | 0.46154 | 0.29559 | 2.8903 | 0.11935 | 1.7663 | 0 | 6.145 | 25.4591 | 0.6868% | CZ 6B | 0 | 0 | 0.052212 | 0.28078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.4426 | 0.6868% | CZ 6B | 43.1893 | 2.4721 | 6.0256 | 46.6189 | 22.2528 | 17.6276 | 1.2218 | 38.3318 | 2.9302 | 4.8319 | 3.0945 | 30.2582 | 1.2495 | 30.4706 | 0 | 64.3323 | 314.9071 | 0.6868%
CZ 7 | 0.42574 | 0.024371 | 0.05802 | 0.60902 | 0.22751 | 0.18675 | 0.021363 | 0.35725 | 0.028854 | 0.054783 | 0.03044 | 0.29828 | 0.012317 | 0.29079 | 0 | 0.63415 | 3.2596 | 0.9776% | CZ 7 | 14.0798 | 0.80597 | 5.6471 | 46.3269 | 7.5242 | 6.1762 | 0.7065 | 11.8149 | 0.95425 | 1.8118 | 1.0067 | 9.8645 | 0.40735 | 16.9886 | 0 | 20.9702 | 145.0849 | 0.9776% | CZ 7 | 4.1253 | 0.23615 | 0.030457 | 2.1666 | 2.2046 | 1.8096 | 0.207 | 3.4617 | 0.27959 | 0.53084 | 0.29496 | 2.8903 | 0.11935 | 1.7663 | 0 | 6.145 | 26.2677 | 0.9776% | CZ 7 | 0 | 0 | 0.055431 | 0.38932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.55436 | 0.9776% | CZ 7 | 43.1881 | 2.4722 | 6.3775 | 65.2351 | 23.0797 | 18.9447 | 2.1671 | 36.2409 | 2.927 | 5.5574 | 3.0879 | 30.2582 | 1.2495 | 30.4706 | 0 | 64.3323 | 335.5883 | 0.9776%
CZ 8 | 0.42603 | 0.024221 | 0.062347 | 0.85158 | 0.29224 | 0.14221 | 0.0081572 | 0.35043 | 0.029551 | 0.042552 | 0.030065 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.4949 | 0.03822% | CZ 8 | 14.0893 | 0.80103 | 6.0842 | 64.9151 | 9.6649 | 4.7031 | 0.26977 | 11.5891 | 0.97729 | 1.4073 | 0.99429 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 163.7259 | 0.03822% | CZ 8 | 4.1281 | 0.2347 | 0.030457 | 3.0099 | 2.8318 | 1.378 | 0.079042 | 3.3956 | 0.28634 | 0.41232 | 0.29132 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 26.9985 | 0.03822% | CZ 8 | 0 | 0 | 0.059802 | 0.54642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.71583 | 0.03822% | CZ 8 | 43.2173 | 2.4571 | 6.8552 | 91.2348 | 29.6459 | 14.4262 | 0.82749 | 35.5481 | 2.9977 | 4.3166 | 3.0499 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 360.8871 | 0.03822%
Us Weighted | 0.42577 | 0.024405 | 0.048878 | 0.38815 | 0.15368 | 0.31715 | 0.0672 | 0.35248 | 0.022623 | 0.071649 | 0.031664 | 0.29828 | 0.012318 | 0.29079 | 0 | 0.63415 | 3.1392 | 100% | Us Weighted | 14.0807 | 0.8071 | 4.7237 | 29.8027 | 5.0826 | 10.4885 | 2.2224 | 11.6571 | 0.74817 | 2.3695 | 1.0472 | 9.8645 | 0.40739 | 16.9886 | 0 | 20.9702 | 131.2603 | 100% | Us Weighted | 4.1256 | 0.23648 | 0.030454 | 1.3413 | 1.4892 | 3.0731 | 0.65115 | 3.4155 | 0.21921 | 0.69427 | 0.30682 | 2.8903 | 0.11936 | 1.7663 | 0 | 6.145 | 26.504 | 100% | Us Weighted | 0 | 0 | 0.046198 | 0.25225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.40805 | 100% | Us Weighted | 43.1909 | 2.4757 | 5.3682 | 41.6127 | 15.5902 | 32.1723 | 6.8169 | 35.7568 | 2.2949 | 7.2683 | 3.2121 | 30.2582 | 1.2496 | 30.4706 | 0 | 64.3323 | 322.0698 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.49652 | 0.031085 | 0.039885 | 0.35835 | 0.0083364 | 0.94549 | 0.20564 | 0.51564 | 0 | 0.18715 | 0.033766 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 4.0875 | 1.17% | CZ 1A | 16.4205 | 1.028 | 3.7969 | 35.6132 | 0.2757 | 31.2686 | 6.8008 | 17.053 | 0 | 6.1893 | 1.1167 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 168.7894 | 1.17% | CZ 1A | 4.8112 | 0.3012 | 0.033068 | 0.083298 | 0.080779 | 9.1616 | 1.9926 | 4.9965 | 0 | 1.8134 | 0.32719 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 34.8136 | 1.17% | CZ 1A | 0 | 0 | 0.036841 | 0.35329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.49973 | 1.17% | CZ 1A | 50.3681 | 3.1533 | 4.3729 | 39.4865 | 0.84567 | 95.913 | 20.8608 | 52.3081 | 0 | 18.985 | 3.4253 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 419.0844 | 1.17%
CZ 1B | 0.49652 | 0.031057 | 0.038256 | 0.42784 | 0.41579 | 0.60476 | 0.095985 | 0.54874 | 0 | 0.15126 | 0.033251 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 4.1091 | 0% | CZ 1B | 16.4205 | 1.0271 | 3.6324 | 29.4732 | 13.7509 | 20.0003 | 3.1744 | 18.1475 | 0 | 5.0023 | 1.0997 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 160.9549 | 0% | CZ 1B | 4.8112 | 0.30094 | 0.033068 | 1.9601 | 4.029 | 5.86 | 0.93008 | 5.3172 | 0 | 1.4657 | 0.3222 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 36.2421 | 0% | CZ 1B | 0 | 0 | 0.035195 | 0.22783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.37263 | 0% | CZ 1B | 50.3681 | 3.1505 | 4.1931 | 45.4225 | 42.1793 | 61.3488 | 9.737 | 55.6653 | 0 | 15.344 | 3.3731 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 420.1476 | 0%
CZ 2A | 0.49652 | 0.031031 | 0.043606 | 0.4558 | 0.058928 | 0.73092 | 0.14806 | 0.51063 | 0 | 0.16653 | 0.032918 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.9406 | 13.88% | CZ 2A | 16.4205 | 1.0262 | 4.1727 | 42.973 | 1.9488 | 24.1724 | 4.8966 | 16.8874 | 0 | 5.5074 | 1.0887 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 168.3204 | 13.88% | CZ 2A | 4.8112 | 0.30069 | 0.03308 | 0.43746 | 0.57101 | 7.0825 | 1.4347 | 4.948 | 0 | 1.6136 | 0.31898 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 32.7639 | 13.88% | CZ 2A | 0 | 0 | 0.040598 | 0.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.565 | 13.88% | CZ 2A | 50.3681 | 3.1479 | 4.7837 | 49.9173 | 5.9779 | 74.1462 | 15.0198 | 51.8002 | 0 | 16.8932 | 3.3394 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 404.7594 | 13.88%
CZ 2B | 0.49652 | 0.03101 | 0.041438 | 0.47777 | 0.23033 | 0.60821 | 0.09499 | 0.52751 | 0 | 0.14326 | 0.03306 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.9497 | 2.777% | CZ 2B | 16.4205 | 1.0255 | 3.9538 | 38.3219 | 7.6174 | 20.1143 | 3.1415 | 17.4454 | 0 | 4.7377 | 1.0933 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 163.0982 | 2.777% | CZ 2B | 4.8112 | 0.30048 | 0.033068 | 1.4174 | 2.2319 | 5.8934 | 0.92044 | 5.1114 | 0 | 1.3881 | 0.32034 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 33.6406 | 2.777% | CZ 2B | 0 | 0 | 0.038409 | 0.33484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.48286 | 2.777% | CZ 2B | 50.3681 | 3.1457 | 4.5443 | 51.4374 | 23.3656 | 61.6985 | 9.6361 | 53.5117 | 0 | 14.5325 | 3.3537 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 404.9596 | 2.777%
CZ 3A | 0.49652 | 0.031049 | 0.046523 | 0.56082 | 0.13925 | 0.56312 | 0.11072 | 0.50771 | 0 | 0.15694 | 0.032266 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.9106 | 13.57% | CZ 3A | 16.4205 | 1.0268 | 4.4673 | 50.7608 | 4.6053 | 18.6231 | 3.6616 | 16.7906 | 0 | 5.1903 | 1.0671 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 171.8401 | 13.57% | CZ 3A | 4.8112 | 0.30086 | 0.03308 | 0.83981 | 1.3493 | 5.4565 | 1.0728 | 4.9196 | 0 | 1.5207 | 0.31265 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 31.8293 | 13.57% | CZ 3A | 0 | 0 | 0.043544 | 0.47895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.63209 | 13.57% | CZ 3A | 50.3681 | 3.1497 | 5.1057 | 61.1407 | 14.1262 | 57.1242 | 11.2316 | 51.5033 | 0 | 15.9206 | 3.2731 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 402.3092 | 13.57%
CZ 3B | 0.49652 | 0.031052 | 0.045557 | 0.44274 | 0.3234 | 0.40877 | 0.061546 | 0.5384 | 0 | 0.11445 | 0.032117 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.7602 | 7.904% | CZ 3B | 16.4205 | 1.0269 | 4.3697 | 35.4329 | 10.6952 | 13.5185 | 2.0354 | 17.8056 | 0 | 3.7851 | 1.0622 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 155.3787 | 7.904% | CZ 3B | 4.8112 | 0.30089 | 0.03308 | 1.3247 | 3.1337 | 3.9609 | 0.59637 | 5.217 | 0 | 1.109 | 0.31121 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 32.0107 | 7.904% | CZ 3B | 0 | 0 | 0.042568 | 0.30912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.46129 | 7.904% | CZ 3B | 50.3681 | 3.1501 | 4.999 | 47.6549 | 32.8064 | 41.4665 | 6.2434 | 54.6167 | 0 | 11.6104 | 3.2581 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 385.5393 | 7.904%
CZ 3C | 0.49652 | 0.031006 | 0.04969 | 0.48347 | 0.034005 | 0.25443 | 0.030141 | 0.50131 | 0 | 0.092249 | 0.031531 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.27 | 1.133% | CZ 3C | 16.4205 | 1.0254 | 4.7872 | 45.7575 | 1.1246 | 8.4144 | 0.9968 | 16.5791 | 0 | 3.0508 | 1.0428 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 148.4258 | 1.133% | CZ 3C | 4.8112 | 0.30044 | 0.03308 | 0.43895 | 0.3295 | 2.4654 | 0.29206 | 4.8576 | 0 | 0.89388 | 0.30553 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 25.9404 | 1.133% | CZ 3C | 0 | 0 | 0.046743 | 0.44259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.59894 | 1.133% | CZ 3C | 50.3681 | 3.1454 | 5.4554 | 52.9709 | 3.4495 | 25.8102 | 3.0576 | 50.8547 | 0 | 9.358 | 3.1986 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 337.034 | 1.133%
CZ 4A | 0.49652 | 0.031035 | 0.050104 | 0.65029 | 0.22555 | 0.4877 | 0.077349 | 0.50472 | 0 | 0.13979 | 0.031589 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.9603 | 17.85% | CZ 4A | 16.4205 | 1.0264 | 4.8291 | 57.4447 | 7.4591 | 16.1288 | 2.558 | 16.6918 | 0 | 4.6232 | 1.0447 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 177.4529 | 17.85% | CZ 4A | 4.8112 | 0.30072 | 0.03308 | 1.1754 | 2.1855 | 4.7257 | 0.7495 | 4.8906 | 0 | 1.3546 | 0.30609 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.7451 | 17.85% | CZ 4A | 0 | 0 | 0.047162 | 0.53433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.6911 | 17.85% | CZ 4A | 50.3681 | 3.1482 | 5.5011 | 70.7076 | 22.88 | 49.4733 | 7.8465 | 51.2001 | 0 | 14.1811 | 3.2045 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 407.8764 | 17.85%
CZ 4B | 0.49652 | 0.031028 | 0.049555 | 0.47389 | 0.41736 | 0.29684 | 0.035386 | 0.55318 | 0 | 0.098777 | 0.03138 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.7496 | 0.6458% | CZ 4B | 16.4205 | 1.0261 | 4.7736 | 37.5595 | 13.8028 | 9.817 | 1.1703 | 18.2946 | 0 | 3.2667 | 1.0378 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 156.3955 | 0.6458% | CZ 4B | 4.8112 | 0.30065 | 0.03308 | 1.4703 | 4.0442 | 2.8763 | 0.34289 | 5.3603 | 0 | 0.95713 | 0.30407 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 31.7128 | 0.6458% | CZ 4B | 0 | 0 | 0.046607 | 0.32541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.48162 | 0.6458% | CZ 4B | 50.3681 | 3.1475 | 5.4405 | 50.9601 | 42.3387 | 30.1125 | 3.5897 | 56.1167 | 0 | 10.0202 | 3.1833 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 384.643 | 0.6458%
CZ 4C | 0.49652 | 0.031018 | 0.051618 | 0.60246 | 0.095961 | 0.26536 | 0.032162 | 0.5029 | 0 | 0.0984 | 0.031197 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.4732 | 3.07% | CZ 4C | 16.4205 | 1.0258 | 4.982 | 53.9014 | 3.1736 | 8.7758 | 1.0637 | 16.6317 | 0 | 3.2542 | 1.0317 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 159.4872 | 3.07% | CZ 4C | 4.8112 | 0.30056 | 0.03308 | 0.99174 | 0.92985 | 2.5713 | 0.31165 | 4.873 | 0 | 0.95348 | 0.3023 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 27.2909 | 3.07% | CZ 4C | 0 | 0 | 0.048691 | 0.50517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.66346 | 3.07% | CZ 4C | 50.3681 | 3.1466 | 5.6683 | 65.5972 | 9.7346 | 26.9188 | 3.2626 | 51.0159 | 0 | 9.982 | 3.1647 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 358.2247 | 3.07%
CZ 5A | 0.49652 | 0.030997 | 0.052603 | 0.73034 | 0.24937 | 0.38601 | 0.062952 | 0.50674 | 0 | 0.12664 | 0.031166 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.939 | 23.55% | CZ 5A | 16.4205 | 1.0251 | 5.0814 | 65.1001 | 8.2471 | 12.7659 | 2.0819 | 16.7585 | 0 | 4.1883 | 1.0307 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 181.9262 | 23.55% | CZ 5A | 4.8112 | 0.30035 | 0.033091 | 1.2368 | 2.4164 | 3.7404 | 0.61 | 4.9102 | 0 | 1.2272 | 0.302 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 30.8002 | 23.55% | CZ 5A | 0 | 0 | 0.049685 | 0.60879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.76808 | 23.55% | CZ 5A | 50.3681 | 3.1444 | 5.777 | 79.4884 | 25.297 | 39.1579 | 6.3861 | 51.4048 | 0 | 12.8472 | 3.1616 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 406.3983 | 23.55%
CZ 5B | 0.49652 | 0.030982 | 0.052157 | 0.68123 | 0.33299 | 0.29882 | 0.026744 | 0.52039 | 0 | 0.099647 | 0.030978 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.8361 | 6.333% | CZ 5B | 16.4205 | 1.0246 | 5.0363 | 55.4855 | 11.0125 | 9.8824 | 0.88445 | 17.21 | 0 | 3.2955 | 1.0245 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 170.503 | 6.333% | CZ 5B | 4.8112 | 0.30021 | 0.033091 | 1.9005 | 3.2266 | 2.8955 | 0.25914 | 5.0425 | 0 | 0.96556 | 0.30017 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 30.9473 | 6.333% | CZ 5B | 0 | 0 | 0.049234 | 0.48999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.64883 | 6.333% | CZ 5B | 50.3681 | 3.1429 | 5.7277 | 73.4525 | 33.7797 | 30.3131 | 2.7129 | 52.7898 | 0 | 10.1085 | 3.1425 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 394.9037 | 6.333%
CZ 5C | 0.49652 | 0.030965 | 0.052635 | 0.65872 | 0.12398 | 0.22511 | 0.022221 | 0.49934 | 0 | 0.090187 | 0.030855 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.4962 | 0% | CZ 5C | 16.4205 | 1.024 | 5.0847 | 58.2823 | 4.1001 | 7.4447 | 0.73488 | 16.514 | 0 | 2.9826 | 1.0204 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 162.835 | 0% | CZ 5C | 4.8112 | 0.30004 | 0.03308 | 1.1774 | 1.2013 | 2.1813 | 0.21532 | 4.8386 | 0 | 0.8739 | 0.29898 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 27.1438 | 0% | CZ 5C | 0 | 0 | 0.049718 | 0.54264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.70196 | 0% | CZ 5C | 50.3681 | 3.1411 | 5.7805 | 71.6366 | 12.5765 | 22.8358 | 2.2542 | 50.6549 | 0 | 9.1489 | 3.1301 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 360.8926 | 0%
CZ 6A | 0.49652 | 0.030999 | 0.054821 | 0.84153 | 0.30587 | 0.32663 | 0.041978 | 0.50309 | 0 | 0.11515 | 0.030833 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 4.0131 | 6.413% | CZ 6A | 16.4205 | 1.0252 | 5.3055 | 74.9681 | 10.1155 | 10.8021 | 1.3883 | 16.6377 | 0 | 3.8081 | 1.0197 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 190.7174 | 6.413% | CZ 6A | 4.8112 | 0.30038 | 0.033091 | 1.4313 | 2.9638 | 3.165 | 0.40676 | 4.8748 | 0 | 1.1158 | 0.29877 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 30.6136 | 6.413% | CZ 6A | 0 | 0 | 0.051925 | 0.70083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.86236 | 6.413% | CZ 6A | 50.3681 | 3.1446 | 6.0219 | 91.5851 | 31.0281 | 33.1342 | 4.2583 | 51.0344 | 0 | 11.6811 | 3.1278 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 414.7496 | 6.413%
CZ 6B | 0.49652 | 0.030975 | 0.05514 | 0.73901 | 0.40317 | 0.24353 | 0.017529 | 0.53127 | 0 | 0.092533 | 0.030541 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.9059 | 0.6868% | CZ 6B | 16.4205 | 1.0244 | 5.3376 | 61.8708 | 13.3333 | 8.0539 | 0.5797 | 17.5698 | 0 | 3.0602 | 1.01 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 177.487 | 0.6868% | CZ 6B | 4.8112 | 0.30015 | 0.033091 | 1.8223 | 3.9066 | 2.3598 | 0.16985 | 5.1479 | 0 | 0.89663 | 0.29594 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 30.9561 | 0.6868% | CZ 6B | 0 | 0 | 0.052247 | 0.55651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.71837 | 0.6868% | CZ 6B | 50.3681 | 3.1422 | 6.057 | 79.9043 | 40.8983 | 24.7044 | 1.7782 | 53.8936 | 0 | 9.3868 | 3.0982 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 402.597 | 0.6868%
CZ 7 | 0.49652 | 0.030978 | 0.058329 | 0.9343 | 0.36155 | 0.26651 | 0.029747 | 0.50753 | 0 | 0.1051 | 0.030468 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 4.0867 | 0.9776% | CZ 7 | 16.4205 | 1.0245 | 5.6598 | 84.0693 | 11.9569 | 8.8137 | 0.98377 | 16.7849 | 0 | 3.4759 | 1.0076 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 199.4236 | 0.9776% | CZ 7 | 4.8112 | 0.30017 | 0.033091 | 1.4697 | 3.5033 | 2.5824 | 0.28824 | 4.9179 | 0 | 1.0184 | 0.29523 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 30.4324 | 0.9776% | CZ 7 | 0 | 0 | 0.055469 | 0.79053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.9556 | 0.9776% | CZ 7 | 50.3681 | 3.1425 | 6.4092 | 101.7913 | 36.6764 | 27.0352 | 3.0176 | 51.4858 | 0 | 10.662 | 3.0908 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 423.0446 | 0.9776%
CZ 8 | 0.49652 | 0.030788 | 0.062658 | 1.2367 | 0.48055 | 0.21005 | 0.013913 | 0.49947 | 0 | 0.084318 | 0.030097 | 0.30154 | 0.020604 | 0.29079 | 0 | 0.65272 | 4.4107 | 0.03822% | CZ 8 | 16.4205 | 1.0182 | 6.0971 | 111.6672 | 15.8924 | 6.9467 | 0.46012 | 16.5181 | 0 | 2.7885 | 0.99535 | 9.9723 | 0.6814 | 16.9886 | 0 | 21.5845 | 228.0308 | 0.03822% | CZ 8 | 4.8112 | 0.29833 | 0.033091 | 1.8907 | 4.6564 | 2.0354 | 0.13482 | 4.8397 | 0 | 0.81702 | 0.29163 | 2.9219 | 0.19965 | 1.7663 | 0 | 6.325 | 31.0211 | 0.03822% | CZ 8 | 0 | 0 | 0.059841 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 1.2216 | 0.03822% | CZ 8 | 50.3681 | 3.1232 | 6.8871 | 134.7931 | 48.7481 | 21.3081 | 1.4114 | 50.6673 | 0 | 8.5534 | 3.0531 | 30.589 | 2.0901 | 30.4706 | 0 | 66.2164 | 458.2791 | 0.03822%
Us Weighted | 0.49652 | 0.031021 | 0.049175 | 0.61872 | 0.21134 | 0.47328 | 0.080479 | 0.51116 | 0 | 0.1345 | 0.031754 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.9036 | 100% | Us Weighted | 16.4205 | 1.0259 | 4.7353 | 54.7467 | 6.9891 | 15.6519 | 2.6615 | 16.9047 | 0 | 4.4481 | 1.0502 | 9.9723 | 0.68133 | 16.9886 | 0 | 21.5845 | 173.8606 | 100% | Us Weighted | 4.8112 | 0.30059 | 0.033084 | 1.1055 | 2.0478 | 4.586 | 0.77982 | 4.953 | 0 | 1.3033 | 0.30769 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.4406 | 100% | Us Weighted | 0 | 0 | 0.046223 | 0.50974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.66556 | 100% | Us Weighted | 50.3681 | 3.1469 | 5.3986 | 67.2873 | 21.4384 | 48.0105 | 8.164 | 51.8533 | 0 | 13.6441 | 3.2212 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 401.8983 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.49652 | 0.031085 | 0.039869 | 0.35094 | 0.0084005 | 1.0094 | 0.19343 | 0.53181 | 0 | 0.17804 | 0.033754 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 4.1389 | 1.17% | CZ 1A | 16.4205 | 1.028 | 3.7953 | 34.8641 | 0.27782 | 33.381 | 6.397 | 17.5877 | 0 | 5.8881 | 1.1163 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 169.9825 | 1.17% | CZ 1A | 4.8112 | 0.3012 | 0.033068 | 0.083401 | 0.0814 | 9.7805 | 1.8743 | 5.1532 | 0 | 1.7252 | 0.32707 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 35.3833 | 1.17% | CZ 1A | 0 | 0 | 0.036825 | 0.34579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.49222 | 1.17% | CZ 1A | 50.3681 | 3.1533 | 4.3711 | 38.6684 | 0.85218 | 102.3925 | 19.6221 | 53.9485 | 0 | 18.061 | 3.4241 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 424.2272 | 1.17%
CZ 1B | 0.49652 | 0.031057 | 0.038241 | 0.42148 | 0.40458 | 0.60214 | 0.093861 | 0.56835 | 0 | 0.14631 | 0.033235 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 4.1014 | 0% | CZ 1B | 16.4205 | 1.0271 | 3.6308 | 28.8264 | 13.3799 | 19.9136 | 3.1041 | 18.7963 | 0 | 4.8387 | 1.0991 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 160.2633 | 0% | CZ 1B | 4.8112 | 0.30094 | 0.03308 | 1.9607 | 3.9203 | 5.8346 | 0.9095 | 5.5073 | 0 | 1.4177 | 0.32205 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 36.2301 | 0% | CZ 1B | 0 | 0 | 0.035179 | 0.22134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.36613 | 0% | CZ 1B | 50.3681 | 3.1505 | 4.1914 | 44.7198 | 41.0415 | 61.0827 | 9.5216 | 57.6554 | 0 | 14.8422 | 3.3715 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 419.3106 | 0%
CZ 2A | 0.49652 | 0.031031 | 0.043594 | 0.44233 | 0.059358 | 0.79489 | 0.14214 | 0.52977 | 0 | 0.16154 | 0.032867 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.9997 | 13.88% | CZ 2A | 16.4205 | 1.0262 | 4.1714 | 41.5946 | 1.9631 | 26.2881 | 4.7006 | 17.5201 | 0 | 5.3424 | 1.087 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 169.3408 | 13.88% | CZ 2A | 4.8112 | 0.30069 | 0.033091 | 0.44001 | 0.57517 | 7.7023 | 1.3773 | 5.1334 | 0 | 1.5653 | 0.31848 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 33.4696 | 13.88% | CZ 2A | 0 | 0 | 0.040585 | 0.40093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.55112 | 13.88% | CZ 2A | 50.3681 | 3.1479 | 4.7824 | 48.428 | 6.0215 | 80.6359 | 14.4186 | 53.7411 | 0 | 16.3872 | 3.3342 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 410.6307 | 13.88%
CZ 2B | 0.49652 | 0.03101 | 0.041427 | 0.46348 | 0.23779 | 0.61397 | 0.094553 | 0.55783 | 0 | 0.14208 | 0.033007 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.9773 | 2.777% | CZ 2B | 16.4205 | 1.0255 | 3.9526 | 36.7026 | 7.864 | 20.3047 | 3.127 | 18.4481 | 0 | 4.6989 | 1.0916 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 162.8624 | 2.777% | CZ 2B | 4.8112 | 0.30048 | 0.03308 | 1.4424 | 2.3041 | 5.9492 | 0.91621 | 5.4053 | 0 | 1.3768 | 0.31984 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 34.0714 | 2.777% | CZ 2B | 0 | 0 | 0.038397 | 0.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.4658 | 2.777% | CZ 2B | 50.3681 | 3.1457 | 4.5431 | 49.8359 | 24.1221 | 62.2825 | 9.5918 | 56.5876 | 0 | 14.4134 | 3.3484 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 407.6045 | 2.777%
CZ 3A | 0.49652 | 0.031049 | 0.04651 | 0.53084 | 0.13941 | 0.61779 | 0.10581 | 0.52242 | 0 | 0.15174 | 0.032239 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.94 | 13.57% | CZ 3A | 16.4205 | 1.0268 | 4.466 | 47.7275 | 4.6104 | 20.4312 | 3.4994 | 17.2773 | 0 | 5.0184 | 1.0662 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 170.7705 | 13.57% | CZ 3A | 4.8112 | 0.30086 | 0.033091 | 0.84044 | 1.3508 | 5.9863 | 1.0253 | 5.0622 | 0 | 1.4704 | 0.3124 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 32.4057 | 13.57% | CZ 3A | 0 | 0 | 0.043531 | 0.44859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.60173 | 13.57% | CZ 3A | 50.3681 | 3.1497 | 5.1043 | 57.8296 | 14.1419 | 62.6705 | 10.734 | 52.9962 | 0 | 15.3933 | 3.2705 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 405.0241 | 13.57%
CZ 3B | 0.49652 | 0.031052 | 0.045543 | 0.42742 | 0.32553 | 0.40519 | 0.060374 | 0.55504 | 0 | 0.11173 | 0.032091 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.7561 | 7.904% | CZ 3B | 16.4205 | 1.0269 | 4.3683 | 33.8688 | 10.7657 | 13.4001 | 1.9967 | 18.356 | 0 | 3.6952 | 1.0613 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 154.1863 | 7.904% | CZ 3B | 4.8112 | 0.30089 | 0.03308 | 1.3271 | 3.1543 | 3.9262 | 0.58502 | 5.3783 | 0 | 1.0827 | 0.31096 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 32.1224 | 7.904% | CZ 3B | 0 | 0 | 0.042554 | 0.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.44555 | 7.904% | CZ 3B | 50.3681 | 3.1501 | 4.9975 | 45.9611 | 33.0227 | 41.1035 | 6.1245 | 56.3051 | 0 | 11.3346 | 3.2554 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 384.9883 | 7.904%
CZ 3C | 0.49652 | 0.031006 | 0.049678 | 0.47707 | 0.034007 | 0.25548 | 0.030176 | 0.51472 | 0 | 0.092374 | 0.031507 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.2782 | 1.133% | CZ 3C | 16.4205 | 1.0254 | 4.786 | 45.1071 | 1.1247 | 8.4491 | 0.99798 | 17.0226 | 0 | 3.0549 | 1.042 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 148.257 | 1.133% | CZ 3C | 4.8112 | 0.30044 | 0.033091 | 0.43955 | 0.32952 | 2.4756 | 0.2924 | 4.9876 | 0 | 0.89509 | 0.3053 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 26.0825 | 1.133% | CZ 3C | 0 | 0 | 0.046731 | 0.43607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.5924 | 1.133% | CZ 3C | 50.3681 | 3.1454 | 5.4541 | 52.264 | 3.4498 | 25.9168 | 3.0612 | 52.215 | 0 | 9.3707 | 3.1962 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 337.807 | 1.133%
CZ 4A | 0.49652 | 0.031035 | 0.050093 | 0.60676 | 0.22569 | 0.48405 | 0.074578 | 0.51897 | 0 | 0.13545 | 0.031553 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.9203 | 17.85% | CZ 4A | 16.4205 | 1.0264 | 4.8279 | 53.0411 | 7.4638 | 16.0082 | 2.4664 | 17.1632 | 0 | 4.4795 | 1.0435 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 173.1672 | 17.85% | CZ 4A | 4.8112 | 0.30072 | 0.033091 | 1.1764 | 2.1869 | 4.6904 | 0.72265 | 5.0288 | 0 | 1.3125 | 0.30575 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.781 | 17.85% | CZ 4A | 0 | 0 | 0.047149 | 0.49026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.64701 | 17.85% | CZ 4A | 50.3681 | 3.1482 | 5.4999 | 65.9011 | 22.8945 | 49.1035 | 7.5654 | 52.6462 | 0 | 13.7404 | 3.2009 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 403.4339 | 17.85%
CZ 4B | 0.49652 | 0.031028 | 0.049543 | 0.44921 | 0.42054 | 0.29632 | 0.035122 | 0.5714 | 0 | 0.096812 | 0.031344 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.7435 | 0.6458% | CZ 4B | 16.4205 | 1.0261 | 4.7723 | 35.0169 | 13.908 | 9.7997 | 1.1615 | 18.8971 | 0 | 3.2017 | 1.0366 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 154.4672 | 0.6458% | CZ 4B | 4.8112 | 0.30065 | 0.033091 | 1.4772 | 4.075 | 2.8713 | 0.34032 | 5.5368 | 0 | 0.93809 | 0.30372 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 31.9001 | 0.6458% | CZ 4B | 0 | 0 | 0.046594 | 0.29975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.45595 | 0.6458% | CZ 4B | 50.3681 | 3.1475 | 5.4392 | 48.228 | 42.6613 | 30.0594 | 3.5628 | 57.9648 | 0 | 9.8209 | 3.1797 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 383.7973 | 0.6458%
CZ 4C | 0.49652 | 0.031018 | 0.051606 | 0.57265 | 0.096114 | 0.26445 | 0.031993 | 0.51609 | 0 | 0.096784 | 0.031164 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.454 | 3.07% | CZ 4C | 16.4205 | 1.0258 | 4.9807 | 50.8819 | 3.1786 | 8.7459 | 1.058 | 17.0677 | 0 | 3.2008 | 1.0306 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 156.8174 | 3.07% | CZ 4C | 4.8112 | 0.30056 | 0.033091 | 0.99291 | 0.93133 | 2.5625 | 0.31 | 5.0008 | 0 | 0.93782 | 0.30198 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 27.3949 | 3.07% | CZ 4C | 0 | 0 | 0.048678 | 0.47493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.63321 | 3.07% | CZ 4C | 50.3681 | 3.1466 | 5.6669 | 62.3048 | 9.7501 | 26.827 | 3.2454 | 52.3533 | 0 | 9.818 | 3.1614 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 356.0075 | 3.07%
CZ 5A | 0.49652 | 0.030997 | 0.052592 | 0.66184 | 0.24956 | 0.38099 | 0.060923 | 0.5211 | 0 | 0.12158 | 0.031127 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.8729 | 23.55% | CZ 5A | 16.4205 | 1.0251 | 5.0802 | 58.1748 | 8.2534 | 12.5999 | 2.0148 | 17.2335 | 0 | 4.0207 | 1.0294 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 175.0791 | 23.55% | CZ 5A | 4.8112 | 0.30035 | 0.033103 | 1.2377 | 2.4182 | 3.6917 | 0.59033 | 5.0494 | 0 | 1.1781 | 0.30162 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 30.8244 | 23.55% | CZ 5A | 0 | 0 | 0.049672 | 0.53951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.69878 | 23.55% | CZ 5A | 50.3681 | 3.1444 | 5.7758 | 71.9254 | 25.3164 | 38.6488 | 6.1802 | 52.862 | 0 | 12.3331 | 3.1576 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 399.0777 | 23.55%
CZ 5B | 0.49652 | 0.030982 | 0.052146 | 0.63925 | 0.33398 | 0.30338 | 0.027132 | 0.53587 | 0 | 0.097897 | 0.03094 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.8137 | 6.333% | CZ 5B | 16.4205 | 1.0246 | 5.0352 | 51.2165 | 11.0453 | 10.0332 | 0.89728 | 17.7219 | 0 | 3.2376 | 1.0232 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 166.882 | 6.333% | CZ 5B | 4.8112 | 0.30021 | 0.033103 | 1.9047 | 3.2362 | 2.9397 | 0.2629 | 5.1925 | 0 | 0.94861 | 0.2998 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 31.1416 | 6.333% | CZ 5B | 0 | 0 | 0.049222 | 0.44716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.60598 | 6.333% | CZ 5B | 50.3681 | 3.1429 | 5.7265 | 68.8146 | 33.8801 | 30.7756 | 2.7523 | 54.3599 | 0 | 9.931 | 3.1386 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 392.2557 | 6.333%
CZ 5C | 0.49652 | 0.030965 | 0.052623 | 0.62127 | 0.12403 | 0.22555 | 0.022204 | 0.51142 | 0 | 0.089333 | 0.030823 | 0.30154 | 0.020604 | 0.29079 | 0 | 0.65272 | 3.4704 | 0% | CZ 5C | 16.4205 | 1.024 | 5.0834 | 54.4998 | 4.1017 | 7.4592 | 0.73433 | 16.9132 | 0 | 2.9544 | 1.0194 | 9.9723 | 0.6814 | 16.9886 | 0 | 21.5845 | 159.4368 | 0% | CZ 5C | 4.8112 | 0.30004 | 0.033091 | 1.1774 | 1.2018 | 2.1855 | 0.21516 | 4.9555 | 0 | 0.86562 | 0.29867 | 2.9219 | 0.19965 | 1.7663 | 0 | 6.325 | 27.2567 | 0% | CZ 5C | 0 | 0 | 0.049705 | 0.50481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.66412 | 0% | CZ 5C | 50.3681 | 3.1411 | 5.7792 | 67.502 | 12.5815 | 22.8804 | 2.2525 | 51.8795 | 0 | 9.0622 | 3.1268 | 30.589 | 2.0901 | 30.4706 | 0 | 66.2164 | 357.9394 | 0%
CZ 6A | 0.49652 | 0.030999 | 0.054811 | 0.76438 | 0.30592 | 0.32661 | 0.041488 | 0.51684 | 0 | 0.11154 | 0.030794 | 0.30154 | 0.0206 | 0.29079 | 0 | 0.65272 | 3.9455 | 6.413% | CZ 6A | 16.4205 | 1.0252 | 5.3043 | 67.1716 | 10.1172 | 10.8014 | 1.3721 | 17.0926 | 0 | 3.6887 | 1.0184 | 9.9723 | 0.68128 | 16.9886 | 0 | 21.5845 | 183.2387 | 6.413% | CZ 6A | 4.8112 | 0.30038 | 0.033103 | 1.4317 | 2.9643 | 3.1648 | 0.40201 | 5.0081 | 0 | 1.0808 | 0.29839 | 2.9219 | 0.19961 | 1.7663 | 0 | 6.325 | 30.7074 | 6.413% | CZ 6A | 0 | 0 | 0.051913 | 0.62285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.78437 | 6.413% | CZ 6A | 50.3681 | 3.1446 | 6.0207 | 83.0662 | 31.0334 | 33.1322 | 4.2086 | 52.4298 | 0 | 11.3145 | 3.1238 | 30.589 | 2.0898 | 30.4706 | 0 | 66.2164 | 407.2078 | 6.413%
CZ 6B | 0.49652 | 0.030975 | 0.055129 | 0.677 | 0.40484 | 0.24713 | 0.017955 | 0.54759 | 0 | 0.09095 | 0.030499 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 3.8642 | 0.6868% | CZ 6B | 16.4205 | 1.0244 | 5.3365 | 55.5671 | 13.3886 | 8.173 | 0.59379 | 18.1097 | 0 | 3.0078 | 1.0087 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 171.8569 | 0.6868% | CZ 6B | 4.8112 | 0.30015 | 0.033103 | 1.8279 | 3.9228 | 2.3947 | 0.17398 | 5.3061 | 0 | 0.88129 | 0.29553 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 31.1595 | 0.6868% | CZ 6B | 0 | 0 | 0.052235 | 0.49328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.65512 | 0.6868% | CZ 6B | 50.3681 | 3.1422 | 6.0559 | 73.0527 | 41.0682 | 25.0696 | 1.8214 | 55.5495 | 0 | 9.2262 | 3.0939 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 397.8137 | 0.6868%
CZ 7 | 0.49652 | 0.030978 | 0.058319 | 0.83763 | 0.36366 | 0.2714 | 0.030027 | 0.52521 | 0 | 0.10233 | 0.030426 | 0.30154 | 0.020603 | 0.29079 | 0 | 0.65272 | 4.0121 | 0.9776% | CZ 7 | 16.4205 | 1.0245 | 5.6587 | 74.2076 | 12.0268 | 8.9755 | 0.99303 | 17.3696 | 0 | 3.3843 | 1.0062 | 9.9723 | 0.68136 | 16.9886 | 0 | 21.5845 | 190.2934 | 0.9776% | CZ 7 | 4.8112 | 0.30017 | 0.033103 | 1.4835 | 3.5238 | 2.6298 | 0.29096 | 5.0892 | 0 | 0.99159 | 0.29482 | 2.9219 | 0.19964 | 1.7663 | 0 | 6.325 | 30.6609 | 0.9776% | CZ 7 | 0 | 0 | 0.055457 | 0.69145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.85651 | 0.9776% | CZ 7 | 50.3681 | 3.1425 | 6.408 | 91.1053 | 36.8908 | 27.5314 | 3.046 | 53.2792 | 0 | 10.381 | 3.0865 | 30.589 | 2.09 | 30.4706 | 0 | 66.2164 | 414.6047 | 0.9776%
CZ 8 | 0.49652 | 0.030788 | 0.062649 | 1.0804 | 0.48139 | 0.21621 | 0.014594 | 0.51477 | 0 | 0.081785 | 0.030093 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 4.2749 | 0.03822% | CZ 8 | 16.4205 | 1.0182 | 6.0961 | 95.8181 | 15.9202 | 7.1503 | 0.48266 | 17.0242 | 0 | 2.7047 | 0.99523 | 9.9723 | 0.68132 | 16.9886 | 0 | 21.5845 | 212.857 | 0.03822% | CZ 8 | 4.8112 | 0.29833 | 0.033103 | 1.8995 | 4.6646 | 2.095 | 0.14142 | 4.988 | 0 | 0.79248 | 0.2916 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.228 | 0.03822% | CZ 8 | 0 | 0 | 0.059831 | 0.89335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 1.0628 | 0.03822% | CZ 8 | 50.3681 | 3.1232 | 6.8861 | 117.5291 | 48.8335 | 21.9328 | 1.4805 | 52.2198 | 0 | 8.2965 | 3.0528 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 443.0881 | 0.03822%
Us Weighted | 0.49652 | 0.031021 | 0.049164 | 0.57701 | 0.21199 | 0.48871 | 0.077763 | 0.52691 | 0 | 0.13034 | 0.031717 | 0.30154 | 0.020602 | 0.29079 | 0 | 0.65272 | 3.8868 | 100% | Us Weighted | 16.4205 | 1.0259 | 4.734 | 50.5168 | 7.0107 | 16.1624 | 2.5717 | 17.4257 | 0 | 4.3104 | 1.0489 | 9.9723 | 0.68134 | 16.9886 | 0 | 21.5845 | 170.4538 | 100% | Us Weighted | 4.8112 | 0.30059 | 0.033094 | 1.1077 | 2.0541 | 4.7355 | 0.75351 | 5.1057 | 0 | 1.2629 | 0.30733 | 2.9219 | 0.19963 | 1.7663 | 0 | 6.325 | 31.6845 | 100% | Us Weighted | 0 | 0 | 0.04621 | 0.46736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1096 | 0 | 0 | 0.62318 | 100% | Us Weighted | 50.3681 | 3.1469 | 5.3973 | 62.6794 | 21.5045 | 49.5763 | 7.8885 | 53.4515 | 0 | 13.2218 | 3.2175 | 30.589 | 2.0899 | 30.4706 | 0 | 66.2164 | 399.8176 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Hospital |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 241501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 241501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.079395 | 0.0066295 | 0.0002617 | 0.19153 | 0.0064586 | 0.40149 | 0.015848 | 0.19706 | -0.032729 | 0.076724 | 0.0071506 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 0.98278 | 1.17% | CZ 1A | 2.6257 | 0.21925 | 0.0080478 | 18.8442 | 0.21359 | 13.2778 | 0.52411 | 6.5171 | -1.0824 | 2.5374 | 0.23648 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 45.0111 | 1.17% | CZ 1A | 0.76933 | 0.064239 | 0.0026225 | 0.071692 | 0.062583 | 3.8904 | 0.15356 | 1.9095 | -0.31713 | 0.74345 | 0.069288 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 7.7388 | 1.17% | CZ 1A | 0 | 0 | -9.0268e-06 | 0.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18599 | 1.17% | CZ 1A | 8.0541 | 0.67252 | 0.026468 | 21.0798 | 0.65518 | 40.7283 | 1.6077 | 19.9904 | -3.3201 | 7.7831 | 0.72538 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 101.3458 | 1.17%
CZ 1B | 0.079175 | 0.0066236 | 0.00026483 | 0.23257 | 0.28819 | 0.18821 | 0.05179 | 0.20872 | -0.032729 | 0.068277 | 0.0071008 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 1.1311 | 0% | CZ 1B | 2.6184 | 0.21905 | 0.0082833 | 13.0328 | 9.5308 | 6.2243 | 1.7128 | 6.9026 | -1.0824 | 2.258 | 0.23483 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 42.7494 | 0% | CZ 1B | 0.7672 | 0.064181 | 0.002634 | 1.4917 | 2.7925 | 1.8237 | 0.50183 | 2.0224 | -0.31713 | 0.6616 | 0.068805 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 10.1988 | 0% | CZ 1B | 0 | 0 | -7.0644e-06 | 0.079416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079409 | 0% | CZ 1B | 8.0318 | 0.67191 | 0.026803 | 24.2968 | 29.2348 | 19.0924 | 5.2537 | 21.1729 | -3.3201 | 6.9263 | 0.72032 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 115.4505 | 0%
CZ 2A | 0.079175 | 0.0066188 | 0.00027029 | 0.21986 | 0.037686 | 0.3293 | 0.023367 | 0.19951 | -0.029725 | 0.077709 | 0.007045 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 0.98377 | 13.88% | CZ 2A | 2.6184 | 0.21889 | 0.0087543 | 20.4293 | 1.2463 | 10.8904 | 0.77276 | 6.5979 | -0.98306 | 2.57 | 0.23299 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 45.6925 | 13.88% | CZ 2A | 0.7672 | 0.064135 | 0.0026455 | 0.25376 | 0.36517 | 3.1909 | 0.22642 | 1.9332 | -0.28803 | 0.75299 | 0.068265 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 7.6559 | 13.88% | CZ 2A | 0 | 0 | -2.7473e-06 | 0.19563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19563 | 13.88% | CZ 2A | 8.0318 | 0.67143 | 0.027395 | 24.0391 | 3.8229 | 33.4052 | 2.3704 | 20.2385 | -3.0154 | 7.8831 | 0.71466 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 101.532 | 13.88%
CZ 2B | 0.079175 | 0.0066141 | 0.00027338 | 0.2727 | 0.17157 | 0.24799 | 0.035466 | 0.21411 | -0.028223 | 0.071957 | 0.0070557 | 0.00391 | 0.0083626 | 0 | 0 | 0.020683 | 1.1117 | 2.777% | CZ 2B | 2.6184 | 0.21874 | 0.0091467 | 19.0341 | 5.6742 | 8.2014 | 1.1729 | 7.081 | -0.93336 | 2.3797 | 0.23334 | 0.12931 | 0.27656 | 0 | 0 | 0.684 | 46.7794 | 2.777% | CZ 2B | 0.7672 | 0.064089 | 0.002634 | 1.214 | 1.6625 | 2.403 | 0.34366 | 2.0747 | -0.27347 | 0.69725 | 0.068368 | 0.037888 | 0.081032 | 0 | 0 | 0.20041 | 9.3432 | 2.777% | CZ 2B | 0 | 0 | 1.5699e-06 | 0.14891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14891 | 2.777% | CZ 2B | 8.0318 | 0.67095 | 0.027747 | 28.9847 | 17.4049 | 25.1568 | 3.5978 | 21.7201 | -2.863 | 7.2995 | 0.71575 | 0.39665 | 0.84832 | 0 | 0 | 2.0981 | 114.0901 | 2.777%
CZ 3A | 0.079122 | 0.0066224 | 0.00027301 | 0.25148 | 0.082694 | 0.25268 | 0.021587 | 0.18765 | -0.028883 | 0.076874 | 0.0070224 | 0.00391 | 0.0083602 | 0 | 0 | 0.020683 | 0.97008 | 13.57% | CZ 3A | 2.6167 | 0.21901 | 0.009029 | 22.688 | 2.7348 | 8.3565 | 0.71392 | 6.206 | -0.95519 | 2.5423 | 0.23224 | 0.12931 | 0.27648 | 0 | 0 | 0.684 | 46.4531 | 13.57% | CZ 3A | 0.76668 | 0.06417 | 0.0026455 | 0.38708 | 0.80129 | 2.4484 | 0.20918 | 1.8183 | -0.27987 | 0.74489 | 0.068046 | 0.037888 | 0.081009 | 0 | 0 | 0.20041 | 7.3502 | 13.57% | CZ 3A | 0 | 0 | 0 | 0.21367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21367 | 13.57% | CZ 3A | 8.0264 | 0.67179 | 0.027695 | 27.4063 | 8.3887 | 25.6326 | 2.1899 | 19.0363 | -2.9299 | 7.7983 | 0.71238 | 0.39665 | 0.84808 | 0 | 0 | 2.0981 | 100.3032 | 13.57%
CZ 3B | 0.079196 | 0.0066224 | 0.00027766 | 0.21392 | 0.21928 | 0.1319 | 0.022138 | 0.18955 | -0.02709 | 0.055397 | 0.0069595 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 0.93111 | 7.904% | CZ 3B | 2.6191 | 0.21901 | 0.0095784 | 15.3104 | 7.252 | 4.3621 | 0.73213 | 6.2687 | -0.89591 | 1.8321 | 0.23016 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 39.029 | 7.904% | CZ 3B | 0.76739 | 0.06417 | 0.002634 | 0.89826 | 2.1248 | 1.2781 | 0.21451 | 1.8367 | -0.2625 | 0.53679 | 0.067437 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 7.8476 | 7.904% | CZ 3B | 0 | 0 | 5.887e-06 | 0.12245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12245 | 7.904% | CZ 3B | 8.0338 | 0.67179 | 0.028218 | 22.7873 | 22.2446 | 13.3801 | 2.2457 | 19.2284 | -2.7481 | 5.6196 | 0.70599 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 95.5405 | 7.904%
CZ 3C | 0.079185 | 0.0066129 | 0.00028856 | 0.24259 | 0.025435 | 0.10689 | 0.020804 | 0.1811 | 0 | 0.055431 | 0.0068681 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 0.75816 | 1.133% | CZ 3C | 2.6188 | 0.2187 | 0.010599 | 22.1167 | 0.84119 | 3.5351 | 0.68801 | 5.9892 | 0 | 1.8332 | 0.22714 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 39.1684 | 1.133% | CZ 3C | 0.76729 | 0.064078 | 0.0026455 | 0.34051 | 0.24647 | 1.0358 | 0.20158 | 1.7548 | 0 | 0.53712 | 0.066551 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 5.3361 | 1.133% | CZ 3C | 0 | 0 | 1.5699e-05 | 0.20955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20956 | 1.133% | CZ 3C | 8.0328 | 0.67083 | 0.029411 | 26.4681 | 2.5802 | 10.8436 | 2.1104 | 18.3711 | 0 | 5.6231 | 0.69672 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 78.7692 | 1.133%
CZ 4A | 0.079846 | 0.0066188 | 0.00028584 | 0.28359 | 0.12615 | 0.20105 | 0.01859 | 0.17589 | -0.029591 | 0.071049 | 0.0069488 | 0.00391 | 0.0083614 | 0 | 0 | 0.020683 | 0.97339 | 17.85% | CZ 4A | 2.6406 | 0.21889 | 0.010324 | 25.624 | 4.1721 | 6.6491 | 0.6148 | 5.817 | -0.97862 | 2.3497 | 0.22981 | 0.12931 | 0.27652 | 0 | 0 | 0.684 | 48.4376 | 17.85% | CZ 4A | 0.7737 | 0.064135 | 0.0026455 | 0.43097 | 1.2224 | 1.9482 | 0.18013 | 1.7044 | -0.28673 | 0.68845 | 0.067333 | 0.037888 | 0.08102 | 0 | 0 | 0.20041 | 7.1149 | 17.85% | CZ 4A | 0 | 0 | 1.2951e-05 | 0.24153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24154 | 17.85% | CZ 4A | 8.0998 | 0.67143 | 0.029111 | 30.9112 | 12.7974 | 20.3955 | 1.8858 | 17.8431 | -3.0018 | 7.2074 | 0.70491 | 0.39665 | 0.8482 | 0 | 0 | 2.0981 | 100.8868 | 17.85%
CZ 4B | 0.079831 | 0.0066176 | 0.00028428 | 0.24878 | 0.28988 | 0.096024 | 0.017915 | 0.19026 | -0.027191 | 0.052021 | 0.006861 | 0.00391 | 0.0083602 | 0 | 0 | 0.020683 | 0.99424 | 0.6458% | CZ 4B | 2.6401 | 0.21885 | 0.010167 | 17.1583 | 9.5869 | 3.1756 | 0.59246 | 6.2922 | -0.89925 | 1.7204 | 0.2269 | 0.12931 | 0.27648 | 0 | 0 | 0.684 | 41.8125 | 0.6458% | CZ 4B | 0.77355 | 0.064124 | 0.0026455 | 1.1368 | 2.8089 | 0.93046 | 0.17359 | 1.8436 | -0.26348 | 0.50408 | 0.066482 | 0.037888 | 0.081009 | 0 | 0 | 0.20041 | 8.3601 | 0.6458% | CZ 4B | 0 | 0 | 1.1382e-05 | 0.13278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1328 | 0.6458% | CZ 4B | 8.0983 | 0.67131 | 0.028939 | 26.4146 | 29.4067 | 9.741 | 1.8173 | 19.3007 | -2.7583 | 5.2772 | 0.696 | 0.39665 | 0.84808 | 0 | 0 | 2.0981 | 102.0364 | 0.6458%
CZ 4C | 0.079573 | 0.0066153 | 0.00029011 | 0.28783 | 0.070381 | 0.092845 | 0.016488 | 0.17289 | -0.028043 | 0.054114 | 0.0068598 | 0.00391 | 0.0083602 | 0 | 0 | 0.020683 | 0.7928 | 3.07% | CZ 4C | 2.6316 | 0.21878 | 0.010756 | 24.8058 | 2.3276 | 3.0705 | 0.54527 | 5.7178 | -0.92743 | 1.7896 | 0.22686 | 0.12931 | 0.27648 | 0 | 0 | 0.684 | 41.507 | 3.07% | CZ 4C | 0.77105 | 0.064101 | 0.0026455 | 0.60873 | 0.68198 | 0.89965 | 0.15976 | 1.6753 | -0.27174 | 0.52435 | 0.06647 | 0.037888 | 0.081009 | 0 | 0 | 0.20041 | 5.5016 | 3.07% | CZ 4C | 0 | 0 | 1.7269e-05 | 0.22728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2273 | 3.07% | CZ 4C | 8.0721 | 0.67107 | 0.029583 | 31.2147 | 7.1396 | 9.4185 | 1.6726 | 17.5388 | -2.8448 | 5.4895 | 0.69588 | 0.39665 | 0.84808 | 0 | 0 | 2.0981 | 82.4403 | 3.07%
CZ 5A | 0.079819 | 0.0066105 | 0.00029011 | 0.2865 | 0.14481 | 0.12571 | 0.017071 | 0.1736 | -0.02821 | 0.060216 | 0.006855 | 0.00391 | 0.0083626 | 0 | 0 | 0.020683 | 0.90624 | 23.55% | CZ 5A | 2.6397 | 0.21862 | 0.010756 | 26.7493 | 4.7891 | 4.1575 | 0.56455 | 5.7413 | -0.93293 | 1.9914 | 0.22671 | 0.12931 | 0.27656 | 0 | 0 | 0.684 | 47.246 | 23.55% | CZ 5A | 0.77343 | 0.064055 | 0.0026455 | 0.31241 | 1.4032 | 1.2181 | 0.16541 | 1.6822 | -0.27335 | 0.58349 | 0.066424 | 0.037888 | 0.081032 | 0 | 0 | 0.20041 | 6.3174 | 23.55% | CZ 5A | 0 | 0 | 1.7269e-05 | 0.25683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25685 | 23.55% | CZ 5A | 8.0971 | 0.67059 | 0.029583 | 31.3422 | 14.6901 | 12.7528 | 1.7317 | 17.6107 | -2.8617 | 6.1085 | 0.6954 | 0.39665 | 0.84832 | 0 | 0 | 2.0981 | 94.21 | 23.55%
CZ 5B | 0.079547 | 0.006607 | 0.00029169 | 0.31781 | 0.23965 | 0.12117 | 0.017249 | 0.17674 | -0.028313 | 0.053175 | 0.0068455 | 0.00391 | 0.0083626 | 0 | 0 | 0.020683 | 1.0237 | 6.333% | CZ 5B | 2.6307 | 0.2185 | 0.010834 | 24.5727 | 7.9254 | 4.0074 | 0.57044 | 5.8452 | -0.93634 | 1.7586 | 0.22639 | 0.12931 | 0.27656 | 0 | 0 | 0.684 | 47.9197 | 6.333% | CZ 5B | 0.7708 | 0.06402 | 0.002657 | 1.0738 | 2.3221 | 1.1742 | 0.16714 | 1.7126 | -0.27435 | 0.51526 | 0.066332 | 0.037888 | 0.081032 | 0 | 0 | 0.20041 | 7.9139 | 6.333% | CZ 5B | 0 | 0 | 1.7661e-05 | 0.20908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2091 | 6.333% | CZ 5B | 8.0695 | 0.67023 | 0.029746 | 34.0939 | 24.3104 | 12.2922 | 1.7497 | 17.9294 | -2.8721 | 5.3942 | 0.69443 | 0.39665 | 0.84832 | 0 | 0 | 2.0981 | 105.7047 | 6.333%
CZ 5C | 0.078864 | 0.0066034 | 0.00029283 | 0.30363 | 0.086402 | 0.083293 | 0.014026 | 0.16844 | -0.028201 | 0.051543 | 0.0068242 | 0.00391 | 0.0083637 | 0 | 0 | 0.020683 | 0.80468 | 0% | CZ 5C | 2.6082 | 0.21838 | 0.011031 | 26.4768 | 2.8574 | 2.7546 | 0.46385 | 5.5705 | -0.93265 | 1.7046 | 0.22569 | 0.12931 | 0.2766 | 0 | 0 | 0.684 | 43.0483 | 0% | CZ 5C | 0.76418 | 0.063986 | 0.0026455 | 0.59806 | 0.83722 | 0.8071 | 0.13591 | 1.6321 | -0.27327 | 0.49944 | 0.066125 | 0.037888 | 0.081043 | 0 | 0 | 0.20041 | 5.4529 | 0% | CZ 5C | 0 | 0 | 2.0016e-05 | 0.24436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24438 | 0% | CZ 5C | 8.0002 | 0.66987 | 0.029883 | 32.9692 | 8.7649 | 8.4495 | 1.4228 | 17.0869 | -2.8608 | 5.2287 | 0.69227 | 0.39665 | 0.84844 | 0 | 0 | 2.0981 | 83.7965 | 0%
CZ 6A | 0.079711 | 0.0066117 | 0.00029361 | 0.35252 | 0.16907 | 0.12465 | 0.015681 | 0.17012 | -0.028271 | 0.059905 | 0.0068289 | 0.00391 | 0.0083602 | 0 | 0 | 0.020683 | 0.99008 | 6.413% | CZ 6A | 2.6361 | 0.21866 | 0.011109 | 33.2246 | 5.5914 | 4.1224 | 0.51858 | 5.6261 | -0.93497 | 1.9812 | 0.22584 | 0.12931 | 0.27648 | 0 | 0 | 0.684 | 54.3109 | 6.413% | CZ 6A | 0.77238 | 0.064066 | 0.0026455 | 0.33998 | 1.6383 | 1.2078 | 0.15194 | 1.6484 | -0.27394 | 0.58047 | 0.066171 | 0.037888 | 0.081009 | 0 | 0 | 0.20041 | 6.5176 | 6.413% | CZ 6A | 0 | 0 | 2.0801e-05 | 0.32064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32066 | 6.413% | CZ 6A | 8.0861 | 0.67071 | 0.029969 | 38.6055 | 17.151 | 12.6449 | 1.5907 | 17.2575 | -2.8679 | 6.077 | 0.69275 | 0.39665 | 0.84808 | 0 | 0 | 2.0981 | 103.281 | 6.413%
CZ 6B | 0.079665 | 0.0066058 | 0.00029361 | 0.31739 | 0.26889 | 0.10724 | 0.012851 | 0.17544 | -0.0289 | 0.052513 | 0.0068028 | 0.00391 | 0.0083637 | 0 | 0 | 0.020683 | 1.0317 | 0.6868% | CZ 6B | 2.6346 | 0.21846 | 0.011109 | 26.6953 | 8.8925 | 3.5466 | 0.42499 | 5.8021 | -0.95578 | 1.7367 | 0.22498 | 0.12931 | 0.2766 | 0 | 0 | 0.684 | 50.3214 | 0.6868% | CZ 6B | 0.77194 | 0.064009 | 0.0026455 | 0.76512 | 2.6055 | 1.0392 | 0.12452 | 1.7 | -0.28004 | 0.50884 | 0.065918 | 0.037888 | 0.081043 | 0 | 0 | 0.20041 | 7.6869 | 0.6868% | CZ 6B | 0 | 0 | 2.0801e-05 | 0.24084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24086 | 0.6868% | CZ 6B | 8.0814 | 0.67011 | 0.029969 | 34.3337 | 27.2767 | 10.8789 | 1.3036 | 17.7973 | -2.9317 | 5.327 | 0.6901 | 0.39665 | 0.84844 | 0 | 0 | 2.0981 | 106.8003 | 0.6868%
CZ 7 | 0.079995 | 0.006607 | 0.00029672 | 0.37641 | 0.20894 | 0.11001 | 0.01472 | 0.16828 | -0.02886 | 0.055769 | 0.0067731 | 0.00391 | 0.0083626 | 0 | 0 | 0.020683 | 1.0319 | 0.9776% | CZ 7 | 2.6455 | 0.2185 | 0.011423 | 36.8631 | 6.9098 | 3.6381 | 0.48682 | 5.5653 | -0.95444 | 1.8443 | 0.224 | 0.12931 | 0.27656 | 0 | 0 | 0.684 | 58.5425 | 0.9776% | CZ 7 | 0.77513 | 0.06402 | 0.0026455 | 0.16512 | 2.0246 | 1.066 | 0.14264 | 1.6306 | -0.27965 | 0.54039 | 0.065631 | 0.037888 | 0.081032 | 0 | 0 | 0.20041 | 6.5164 | 0.9776% | CZ 7 | 0 | 0 | 2.3941e-05 | 0.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36302 | 0.9776% | CZ 7 | 8.1149 | 0.67023 | 0.030312 | 41.4041 | 21.195 | 11.1596 | 1.4933 | 17.0711 | -2.9276 | 5.6573 | 0.68709 | 0.39665 | 0.84832 | 0 | 0 | 2.0981 | 107.8983 | 0.9776%
CZ 8 | 0.079152 | 0.0065666 | 0.0003006 | 0.42775 | 0.26446 | 0.10338 | 0.011027 | 0.16302 | -0.029557 | 0.046516 | 0.0067862 | 0.00391 | 0.0083602 | 0 | 0 | 0.020683 | 1.1124 | 0.03822% | CZ 8 | 2.6177 | 0.21717 | 0.011816 | 43.7889 | 8.746 | 3.419 | 0.36469 | 5.3914 | -0.97749 | 1.5383 | 0.22443 | 0.12931 | 0.27648 | 0 | 0 | 0.684 | 66.4318 | 0.03822% | CZ 8 | 0.76697 | 0.063629 | 0.0026455 | -0.083056 | 2.5626 | 1.0018 | 0.10685 | 1.5797 | -0.2864 | 0.45073 | 0.065757 | 0.037888 | 0.081009 | 0 | 0 | 0.20041 | 6.5504 | 0.03822% | CZ 8 | 0 | 0 | 2.7865e-05 | 0.44072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44075 | 0.03822% | CZ 8 | 8.0294 | 0.66613 | 0.030741 | 47.3016 | 26.8275 | 10.4874 | 1.1187 | 16.5376 | -2.9983 | 4.7187 | 0.68841 | 0.39665 | 0.84808 | 0 | 0 | 2.0981 | 116.7506 | 0.03822%
Us Weighted | 0.079529 | 0.006616 | 0.00028286 | 0.27141 | 0.12958 | 0.18971 | 0.019623 | 0.18228 | -0.028414 | 0.066115 | 0.006935 | 0.00391 | 0.0083615 | 0 | 0 | 0.020683 | 0.95661 | 100% | Us Weighted | 2.6301 | 0.2188 | 0.010029 | 24.1174 | 4.2853 | 6.2738 | 0.64898 | 6.0282 | -0.93968 | 2.1865 | 0.22935 | 0.12931 | 0.27653 | 0 | 0 | 0.684 | 46.7787 | 100% | Us Weighted | 0.77063 | 0.064108 | 0.0026447 | 0.47033 | 1.2556 | 1.8382 | 0.19015 | 1.7662 | -0.27532 | 0.64064 | 0.067199 | 0.037888 | 0.081022 | 0 | 0 | 0.20041 | 7.1097 | 100% | Us Weighted | 0 | 0 | 1.0022e-05 | 0.22512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22513 | 100% | Us Weighted | 8.0677 | 0.67115 | 0.028783 | 29.5297 | 13.1447 | 19.2443 | 1.9907 | 18.4907 | -2.8824 | 6.7069 | 0.70351 | 0.39665 | 0.84822 | 0 | 0 | 2.0981 | 99.0387 | 100%
Building Type: | Hospital |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 241501 | [17 empty] | Prototype Floor Area: | 241501 | [17 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 15.99% | 21.33% | 0.6564% | 54.58% | 76.88% | 39.78% | 8.193% | 37.05% | 0% | 43.09% | 21.18% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.75% | 1.17% | CZ 1A | 15.99% | 21.33% | 0.212% | 54.05% | 76.88% | 39.78% | 8.193% | 37.05% | 0% | 43.09% | 21.18% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.48% | 1.17% | CZ 1A | 15.99% | 21.33% | 7.93% | 85.96% | 76.88% | 39.78% | 8.193% | 37.05% | 0% | 43.09% | 21.18% | 1.297% | 40.59% | 0% | 0% | 3.169% | 21.87% | 1.17% | CZ 1A | 0% | 0% | -0.02451% | 53.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.78% | 1.17% | CZ 1A | 15.99% | 21.33% | 0.6055% | 54.51% | 76.88% | 39.78% | 8.193% | 37.05% | 0% | 43.09% | 21.18% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.89% | 1.17%
CZ 1B | 15.95% | 21.33% | 0.6925% | 55.18% | 71.23% | 31.26% | 55.18% | 36.72% | 0% | 46.67% | 21.37% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.58% | 0% | CZ 1B | 15.95% | 21.33% | 0.2281% | 45.21% | 71.23% | 31.26% | 55.18% | 36.72% | 0% | 46.67% | 21.37% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.67% | 0% | CZ 1B | 15.95% | 21.33% | 7.962% | 76.08% | 71.23% | 31.26% | 55.18% | 36.72% | 0% | 46.67% | 21.37% | 1.297% | 40.59% | 0% | 0% | 3.169% | 28.15% | 0% | CZ 1B | 0% | 0% | -0.02008% | 35.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.69% | 0% | CZ 1B | 15.95% | 21.33% | 0.6395% | 54.33% | 71.23% | 31.26% | 55.18% | 36.72% | 0% | 46.67% | 21.37% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.53% | 0%
CZ 2A | 15.95% | 21.33% | 0.62% | 49.71% | 63.49% | 41.43% | 16.44% | 37.66% | 0% | 48.1% | 21.43% | 1.297% | 40.58% | 0% | 0% | 3.169% | 24.6% | 13.88% | CZ 2A | 15.95% | 21.33% | 0.2099% | 49.12% | 63.49% | 41.43% | 16.44% | 37.66% | 0% | 48.1% | 21.43% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.98% | 13.88% | CZ 2A | 15.95% | 21.33% | 7.994% | 57.67% | 63.49% | 41.43% | 16.44% | 37.66% | 0% | 48.1% | 21.43% | 1.297% | 40.58% | 0% | 0% | 3.169% | 22.87% | 13.88% | CZ 2A | 0% | 0% | -0.006769% | 48.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.5% | 13.88% | CZ 2A | 15.95% | 21.33% | 0.5728% | 49.64% | 63.49% | 41.43% | 16.44% | 37.66% | 0% | 48.1% | 21.43% | 1.297% | 40.58% | 0% | 0% | 3.169% | 24.73% | 13.88%
CZ 2B | 15.95% | 21.33% | 0.6599% | 58.84% | 72.15% | 40.39% | 37.51% | 38.38% | 0% | 50.64% | 21.38% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.95% | 2.777% | CZ 2B | 15.95% | 21.33% | 0.2314% | 51.86% | 72.15% | 40.39% | 37.51% | 38.38% | 0% | 50.64% | 21.38% | 1.297% | 40.59% | 0% | 0% | 3.169% | 28.72% | 2.777% | CZ 2B | 15.95% | 21.33% | 7.962% | 84.16% | 72.15% | 40.39% | 37.51% | 38.38% | 0% | 50.64% | 21.38% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.42% | 2.777% | CZ 2B | 0% | 0% | 0.004089% | 46.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.97% | 2.777% | CZ 2B | 15.95% | 21.33% | 0.6107% | 58.16% | 72.15% | 40.39% | 37.51% | 38.38% | 0% | 50.64% | 21.38% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.99% | 2.777%
CZ 3A | 15.94% | 21.33% | 0.587% | 47.37% | 59.32% | 40.9% | 20.4% | 35.92% | 0% | 50.66% | 21.78% | 1.297% | 40.58% | 0% | 0% | 3.169% | 24.62% | 13.57% | CZ 3A | 15.94% | 21.33% | 0.2022% | 47.54% | 59.32% | 40.9% | 20.4% | 35.92% | 0% | 50.66% | 21.78% | 1.297% | 40.58% | 0% | 0% | 3.169% | 27.2% | 13.57% | CZ 3A | 15.94% | 21.33% | 7.994% | 46.06% | 59.32% | 40.9% | 20.4% | 35.92% | 0% | 50.66% | 21.78% | 1.297% | 40.58% | 0% | 0% | 3.169% | 22.68% | 13.57% | CZ 3A | 0% | 0% | 0% | 47.63% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.51% | 13.57% | CZ 3A | 15.94% | 21.33% | 0.5426% | 47.39% | 59.32% | 40.9% | 20.4% | 35.92% | 0% | 50.66% | 21.78% | 1.297% | 40.58% | 0% | 0% | 3.169% | 24.76% | 13.57%
CZ 3B | 15.95% | 21.33% | 0.6097% | 50.05% | 67.36% | 32.55% | 36.67% | 34.15% | 0% | 49.58% | 21.69% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.79% | 7.904% | CZ 3B | 15.95% | 21.33% | 0.2193% | 45.2% | 67.36% | 32.55% | 36.67% | 34.15% | 0% | 49.58% | 21.69% | 1.297% | 40.59% | 0% | 0% | 3.169% | 25.31% | 7.904% | CZ 3B | 15.95% | 21.33% | 7.962% | 67.69% | 67.36% | 32.55% | 36.67% | 34.15% | 0% | 49.58% | 21.69% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.43% | 7.904% | CZ 3B | 0% | 0% | 0.01383% | 41.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.48% | 7.904% | CZ 3B | 15.95% | 21.33% | 0.5647% | 49.58% | 67.36% | 32.55% | 36.67% | 34.15% | 0% | 49.58% | 21.69% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.82% | 7.904%
CZ 3C | 15.95% | 21.33% | 0.5809% | 50.85% | 74.79% | 41.84% | 68.94% | 35.18% | 0% | 60.01% | 21.8% | 1.297% | 40.58% | 0% | 0% | 3.169% | 23.13% | 1.133% | CZ 3C | 15.95% | 21.33% | 0.2215% | 49.03% | 74.79% | 41.84% | 68.94% | 35.18% | 0% | 60.01% | 21.8% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.42% | 1.133% | CZ 3C | 15.95% | 21.33% | 7.994% | 77.47% | 74.79% | 41.84% | 68.94% | 35.18% | 0% | 60.01% | 21.8% | 1.297% | 40.58% | 0% | 0% | 3.169% | 20.46% | 1.133% | CZ 3C | 0% | 0% | 0.03359% | 48.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.37% | 1.133% | CZ 3C | 15.95% | 21.33% | 0.5393% | 50.64% | 74.79% | 41.84% | 68.94% | 35.18% | 0% | 60.01% | 21.8% | 1.297% | 40.58% | 0% | 0% | 3.169% | 23.32% | 1.133%
CZ 4A | 16.08% | 21.33% | 0.5706% | 46.74% | 55.9% | 41.54% | 24.93% | 33.89% | 0% | 52.45% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.83% | 17.85% | CZ 4A | 16.08% | 21.33% | 0.2138% | 48.31% | 55.9% | 41.54% | 24.93% | 33.89% | 0% | 52.45% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.97% | 17.85% | CZ 4A | 16.08% | 21.33% | 7.994% | 36.64% | 55.9% | 41.54% | 24.93% | 33.89% | 0% | 52.45% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 22.39% | 17.85% | CZ 4A | 0% | 0% | 0.02747% | 49.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.33% | 17.85% | CZ 4A | 16.08% | 21.33% | 0.5293% | 46.91% | 55.9% | 41.54% | 24.93% | 33.89% | 0% | 52.45% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 25.01% | 17.85%
CZ 4B | 16.08% | 21.33% | 0.5738% | 55.38% | 68.93% | 32.41% | 51.01% | 33.3% | 0% | 53.73% | 21.89% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.56% | 0.6458% | CZ 4B | 16.08% | 21.33% | 0.213% | 49% | 68.93% | 32.41% | 51.01% | 33.3% | 0% | 53.73% | 21.89% | 1.297% | 40.58% | 0% | 0% | 3.169% | 27.07% | 0.6458% | CZ 4B | 16.08% | 21.33% | 7.994% | 76.96% | 68.93% | 32.41% | 51.01% | 33.3% | 0% | 53.73% | 21.89% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.21% | 0.6458% | CZ 4B | 0% | 0% | 0.02443% | 44.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.12% | 0.6458% | CZ 4B | 16.08% | 21.33% | 0.5321% | 54.77% | 68.93% | 32.41% | 51.01% | 33.3% | 0% | 53.73% | 21.89% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.59% | 0.6458%
CZ 4C | 16.03% | 21.33% | 0.5622% | 50.26% | 73.23% | 35.11% | 51.54% | 33.5% | 0% | 55.91% | 22.01% | 1.297% | 40.58% | 0% | 0% | 3.169% | 22.95% | 3.07% | CZ 4C | 16.03% | 21.33% | 0.2159% | 48.75% | 73.23% | 35.11% | 51.54% | 33.5% | 0% | 55.91% | 22.01% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.47% | 3.07% | CZ 4C | 16.03% | 21.33% | 7.994% | 61.31% | 73.23% | 35.11% | 51.54% | 33.5% | 0% | 55.91% | 22.01% | 1.297% | 40.58% | 0% | 0% | 3.169% | 20.08% | 3.07% | CZ 4C | 0% | 0% | 0.03548% | 47.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.9% | 3.07% | CZ 4C | 16.03% | 21.33% | 0.522% | 50.1% | 73.23% | 35.11% | 51.54% | 33.5% | 0% | 55.91% | 22.01% | 1.297% | 40.58% | 0% | 0% | 3.169% | 23.16% | 3.07%
CZ 5A | 16.08% | 21.33% | 0.5516% | 43.29% | 58.03% | 33% | 28.02% | 33.31% | 0% | 49.53% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.4% | 23.55% | CZ 5A | 16.08% | 21.33% | 0.2117% | 45.98% | 58.03% | 33% | 28.02% | 33.31% | 0% | 49.53% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.99% | 23.55% | CZ 5A | 16.08% | 21.33% | 7.992% | 25.24% | 58.03% | 33% | 28.02% | 33.31% | 0% | 49.53% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 20.49% | 23.55% | CZ 5A | 0% | 0% | 0.03477% | 47.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.76% | 23.55% | CZ 5A | 16.08% | 21.33% | 0.5122% | 43.58% | 58.03% | 33% | 28.02% | 33.31% | 0% | 49.53% | 22.02% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.61% | 23.55%
CZ 5B | 16.02% | 21.32% | 0.5594% | 49.72% | 71.75% | 39.94% | 63.57% | 32.98% | 0% | 54.32% | 22.13% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.84% | 6.333% | CZ 5B | 16.02% | 21.32% | 0.2152% | 47.98% | 71.75% | 39.94% | 63.57% | 32.98% | 0% | 54.32% | 22.13% | 1.297% | 40.59% | 0% | 0% | 3.169% | 28.71% | 6.333% | CZ 5B | 16.02% | 21.32% | 8.026% | 56.38% | 71.75% | 39.94% | 63.57% | 32.98% | 0% | 54.32% | 22.13% | 1.297% | 40.59% | 0% | 0% | 3.169% | 25.41% | 6.333% | CZ 5B | 0% | 0% | 0.03588% | 46.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.51% | 6.333% | CZ 5B | 16.02% | 21.32% | 0.5194% | 49.54% | 71.75% | 39.94% | 63.57% | 32.98% | 0% | 54.32% | 22.13% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.95% | 6.333%
CZ 5C | 15.88% | 21.33% | 0.5565% | 48.87% | 69.66% | 36.93% | 63.17% | 32.94% | 0% | 57.7% | 22.14% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.19% | 0% | CZ 5C | 15.88% | 21.33% | 0.217% | 48.58% | 69.66% | 36.93% | 63.17% | 32.94% | 0% | 57.7% | 22.14% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27% | 0% | CZ 5C | 15.88% | 21.33% | 7.994% | 50.8% | 69.66% | 36.93% | 63.17% | 32.94% | 0% | 57.7% | 22.14% | 1.297% | 40.59% | 0% | 0% | 3.169% | 20.01% | 0% | CZ 5C | 0% | 0% | 0.04027% | 48.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.8% | 0% | CZ 5C | 15.88% | 21.33% | 0.5171% | 48.84% | 69.66% | 36.93% | 63.17% | 32.94% | 0% | 57.7% | 22.14% | 1.297% | 40.59% | 0% | 0% | 3.169% | 23.41% | 0%
CZ 6A | 16.05% | 21.33% | 0.5357% | 46.12% | 55.27% | 38.16% | 37.8% | 32.92% | 0% | 53.71% | 22.18% | 1.297% | 40.58% | 0% | 0% | 3.169% | 25.09% | 6.413% | CZ 6A | 16.05% | 21.33% | 0.2094% | 49.46% | 55.27% | 38.16% | 37.8% | 32.92% | 0% | 53.71% | 22.18% | 1.297% | 40.58% | 0% | 0% | 3.169% | 29.64% | 6.413% | CZ 6A | 16.05% | 21.33% | 7.992% | 23.75% | 55.27% | 38.16% | 37.8% | 32.92% | 0% | 53.71% | 22.18% | 1.297% | 40.58% | 0% | 0% | 3.169% | 21.22% | 6.413% | CZ 6A | 0% | 0% | 0.04007% | 51.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.88% | 6.413% | CZ 6A | 16.05% | 21.33% | 0.4978% | 46.48% | 55.27% | 38.16% | 37.8% | 32.92% | 0% | 53.71% | 22.18% | 1.297% | 40.58% | 0% | 0% | 3.169% | 25.36% | 6.413%
CZ 6B | 16.04% | 21.33% | 0.5326% | 46.88% | 66.42% | 43.39% | 71.57% | 32.04% | 0% | 57.74% | 22.3% | 1.297% | 40.6% | 0% | 0% | 3.169% | 26.7% | 0.6868% | CZ 6B | 16.04% | 21.33% | 0.2082% | 48.04% | 66.42% | 43.39% | 71.57% | 32.04% | 0% | 57.74% | 22.3% | 1.297% | 40.6% | 0% | 0% | 3.169% | 29.28% | 0.6868% | CZ 6B | 16.04% | 21.33% | 7.992% | 41.86% | 66.42% | 43.39% | 71.57% | 32.04% | 0% | 57.74% | 22.3% | 1.297% | 40.6% | 0% | 0% | 3.169% | 24.67% | 0.6868% | CZ 6B | 0% | 0% | 0.03982% | 48.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.77% | 0.6868% | CZ 6B | 16.04% | 21.33% | 0.4949% | 47% | 66.42% | 43.39% | 71.57% | 32.04% | 0% | 57.74% | 22.3% | 1.297% | 40.6% | 0% | 0% | 3.169% | 26.85% | 0.6868%
CZ 7 | 16.11% | 21.33% | 0.5088% | 44.94% | 57.45% | 40.53% | 49.02% | 32.04% | 0% | 54.5% | 22.26% | 1.297% | 40.59% | 0% | 0% | 3.169% | 25.72% | 0.9776% | CZ 7 | 16.11% | 21.33% | 0.2019% | 49.68% | 57.45% | 40.53% | 49.02% | 32.04% | 0% | 54.5% | 22.26% | 1.297% | 40.59% | 0% | 0% | 3.169% | 30.76% | 0.9776% | CZ 7 | 16.11% | 21.33% | 7.992% | 11.13% | 57.45% | 40.53% | 49.02% | 32.04% | 0% | 54.5% | 22.26% | 1.297% | 40.59% | 0% | 0% | 3.169% | 21.25% | 0.9776% | CZ 7 | 0% | 0% | 0.04317% | 52.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.38% | 0.9776% | CZ 7 | 16.11% | 21.33% | 0.473% | 45.45% | 57.45% | 40.53% | 49.02% | 32.04% | 0% | 54.5% | 22.26% | 1.297% | 40.59% | 0% | 0% | 3.169% | 26.02% | 0.9776%
CZ 8 | 15.94% | 21.33% | 0.4798% | 39.59% | 54.94% | 47.82% | 75.56% | 31.67% | 0% | 56.88% | 22.55% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.02% | 0.03822% | CZ 8 | 15.94% | 21.33% | 0.1938% | 45.7% | 54.94% | 47.82% | 75.56% | 31.67% | 0% | 56.88% | 22.55% | 1.297% | 40.58% | 0% | 0% | 3.169% | 31.21% | 0.03822% | CZ 8 | 15.94% | 21.33% | 7.992% | -4.373% | 54.94% | 47.82% | 75.56% | 31.67% | 0% | 56.88% | 22.55% | 1.297% | 40.58% | 0% | 0% | 3.169% | 20.98% | 0.03822% | CZ 8 | 0% | 0% | 0.04657% | 49.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.47% | 0.03822% | CZ 8 | 15.94% | 21.33% | 0.4464% | 40.25% | 54.94% | 47.82% | 75.56% | 31.67% | 0% | 56.88% | 22.55% | 1.297% | 40.58% | 0% | 0% | 3.169% | 26.35% | 0.03822%
Us Weighted | 16.02% | 21.33% | 0.5753% | 47.04% | 61.13% | 38.82% | 25.24% | 34.59% | 0% | 50.73% | 21.87% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.61% | 100% | Us Weighted | 16.02% | 21.33% | 0.2118% | 47.74% | 61.13% | 38.82% | 25.24% | 34.59% | 0% | 50.73% | 21.87% | 1.297% | 40.59% | 0% | 0% | 3.169% | 27.44% | 100% | Us Weighted | 16.02% | 21.33% | 7.991% | 42.46% | 61.13% | 38.82% | 25.24% | 34.59% | 0% | 50.73% | 21.87% | 1.297% | 40.59% | 0% | 0% | 3.169% | 22.44% | 100% | Us Weighted | 0% | 0% | 0.02169% | 48.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.13% | 100% | Us Weighted | 16.02% | 21.33% | 0.5333% | 47.11% | 61.13% | 38.82% | 25.24% | 34.59% | 0% | 50.73% | 21.87% | 1.297% | 40.59% | 0% | 0% | 3.169% | 24.77% | 100%

## LgHotel
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Hotel |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Large Hotel | [14 empty] | Prototype Floor Area: | 122120 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.21495 | 0.055156 | 0.17906 | 0.093215 | 0 | 0.36727 | 0 | 0.15144 | 0.043581 | 0.017044 | 0.019929 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 1.8933 |  | STD2013 | 7.1086 | 1.8241 | 16.6398 | 9.4157 | 0 | 12.1462 | 0 | 5.0085 | 1.4413 | 0.56368 | 0.65907 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 89.0021 |  | STD2013 | 2.0828 | 0.53445 | 0.2064 | 0 | 0 | 3.5588 | 0 | 1.4675 | 0.42229 | 0.16516 | 0.19311 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 14.5817 |  | STD2013 | 0 | 0 | 0.15935 | 0.094157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39238 |  | STD2013 | 21.8048 | 5.5952 | 19.5781 | 10.2913 | 0 | 37.2571 | 0 | 15.363 | 4.4209 | 1.729 | 2.0216 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 195.543
STD2010 | 0.298 | 0.055156 | 0.17906 | 0.099608 | 0 | 0.44163 | 0 | 0.19578 | 0.033227 | 0.018712 | 0.024686 | 0.22358 | 0.0077171 | 0.31637 | 0 | 0.22382 | 2.1173 |  | STD2010 | 9.8552 | 1.8241 | 16.6395 | 10.0614 | 0 | 14.6054 | 0 | 6.4747 | 1.0988 | 0.61882 | 0.8164 | 7.3942 | 0.25521 | 19.8034 | 0 | 7.3996 | 96.8467 |  | STD2010 | 2.8876 | 0.53445 | 0.2064 | 0 | 0 | 4.2793 | 0 | 1.8971 | 0.32196 | 0.18131 | 0.2392 | 2.1665 | 0.074777 | 1.7334 | 0 | 2.1691 | 16.691 |  | STD2010 | 0 | 0 | 0.15935 | 0.10061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39884 |  | STD2010 | 30.2298 | 5.5952 | 19.5778 | 10.9971 | 0 | 44.8005 | 0 | 19.8605 | 3.3706 | 1.8982 | 2.5042 | 22.6808 | 0.78284 | 33.3255 | 0 | 22.708 | 218.331
STD2007 | 0.34095 | 0.071853 | 0.17967 | 0.30345 | 0 | 0.60205 | 0 | 0.21909 | 0 | 0.051216 | 0.023937 | 0.22962 | 0.013437 | 0.31637 | 0 | 0.22522 | 2.5769 |  | STD2007 | 11.2757 | 2.3763 | 16.6635 | 30.6513 | 0 | 19.9107 | 0 | 7.2456 | 0 | 1.6938 | 0.79163 | 7.5938 | 0.44439 | 19.8034 | 0 | 7.4458 | 125.8957 |  | STD2007 | 3.3038 | 0.69624 | 0.21178 | 0 | 0 | 5.8338 | 0 | 2.1229 | 0 | 0.49627 | 0.23195 | 2.225 | 0.1302 | 1.7334 | 0 | 2.1826 | 19.1678 |  | STD2007 | 0 | 0 | 0.15941 | 0.30651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.60479 |  | STD2007 | 34.587 | 7.289 | 19.6402 | 33.5019 | 0 | 61.0738 | 0 | 22.2249 | 0 | 5.1955 | 2.4282 | 23.293 | 1.3631 | 33.3255 | 0 | 22.85 | 266.7721
STD2004 | 0.34095 | 0.071853 | 0.17966 | 0.23295 | 0 | 0.57835 | 0 | 0.27035 | 0.10849 | 0.056928 | 0.024166 | 0.22962 | 0.013437 | 0.31637 | 0 | 0.22522 | 2.6483 |  | STD2004 | 11.2757 | 2.3763 | 16.6634 | 23.5302 | 0 | 19.1268 | 0 | 8.9407 | 3.588 | 1.8827 | 0.79922 | 7.5938 | 0.44437 | 19.8034 | 0 | 7.4458 | 123.4703 |  | STD2004 | 3.3038 | 0.69624 | 0.21168 | 0 | 0 | 5.6041 | 0 | 2.6196 | 1.0513 | 0.55162 | 0.23417 | 2.225 | 0.1302 | 1.7334 | 0 | 2.1826 | 20.5436 |  | STD2004 | 0 | 0 | 0.15941 | 0.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.53358 |  | STD2004 | 34.587 | 7.289 | 19.6395 | 25.7185 | 0 | 58.6693 | 0 | 27.4247 | 11.0059 | 5.7749 | 2.4515 | 23.293 | 1.3631 | 33.3255 | 0 | 22.85 | 273.3918
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | -7.8386e-06 | -0.070499 | 0 | -0.023703 | 0 | 0.051258 | 0.10849 | 0.0057122 | 0.0002293 | 0 | -5.1104e-07 | 0 | 0 | 0 | 0.071483 |  | 2004-2007 | 0 | 0 | -9.3017e-05 | -7.1211 | 0 | -0.78388 | 0 | 1.6952 | 3.588 | 0.18891 | 0.0075833 | 0 | -1.6901e-05 | 0 | 0 | 0 | -2.4254 |  | 2004-2007 | 0 | 0 | -9.9662e-05 | 0 | 0 | -0.22967 | 0 | 0.49668 | 1.0513 | 0.05535 | 0.0022219 | 0 | -4.9519e-06 | 0 | 0 | 0 | 1.3758 |  | 2004-2007 | 0 | 0 | 2.4713e-06 | -0.071211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.071209 |  | 2004-2007 | 0 | 0 | -0.00077325 | -7.7834 | 0 | -2.4045 | 0 | 5.1997 | 11.0059 | 0.57946 | 0.023261 | 0 | -5.1841e-05 | 0 | 0 | 0 | 6.6197
2007-2010 | 0.042952 | 0.016697 | 0.00061106 | 0.20384 | 0 | 0.16042 | 0 | 0.023308 | -0.033227 | 0.032504 | -0.00074883 | 0.0060352 | 0.0057201 | 0 | 0 | 0.0013991 | 0.45951 |  | 2007-2010 | 1.4205 | 0.55218 | 0.024011 | 20.5899 | 0 | 5.3053 | 0 | 0.77083 | -1.0988 | 1.075 | -0.024765 | 0.19959 | 0.18917 | 0 | 0 | 0.046269 | 29.049 |  | 2007-2010 | 0.4162 | 0.16179 | 0.0053787 | 0 | 0 | 1.5544 | 0 | 0.22585 | -0.32196 | 0.31496 | -0.007256 | 0.05848 | 0.055427 | 0 | 0 | 0.013557 | 2.4769 |  | 2007-2010 | 0 | 0 | 5.6536e-05 | 0.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20596 |  | 2007-2010 | 4.3572 | 1.6938 | 0.062489 | 22.5047 | 0 | 16.2733 | 0 | 2.3644 | -3.3706 | 3.2973 | -0.075963 | 0.61223 | 0.58027 | 0 | 0 | 0.14192 | 48.4411
2010-2013 | 0.083052 | 0 | -3.1853e-06 | 0.006393 | 0 | 0.074361 | 0 | 0.044335 | -0.010354 | 0.0016673 | 0.0047572 | 0.00047183 | 0.00040806 | 0 | 0 | 0.018986 | 0.22407 |  | 2010-2013 | 2.7466 | 0 | -0.00032175 | 0.64576 | 0 | 2.4592 | 0 | 1.4662 | -0.34242 | 0.055139 | 0.15733 | 0.015604 | 0.013495 | 0 | 0 | 0.62789 | 7.8446 |  | 2010-2013 | 0.80476 | 0 | 0 | 0 | 0 | 0.72055 | 0 | 0.4296 | -0.10033 | 0.016156 | 0.046096 | 0.004572 | 0.0039541 | 0 | 0 | 0.18397 | 2.1093 |  | 2010-2013 | 0 | 0 | -3.2175e-06 | 0.0064576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064544 |  | 2010-2013 | 8.425 | 0 | -0.00035168 | 0.70582 | 0 | 7.5434 | 0 | 4.4975 | -1.0503 | 0.16913 | 0.48258 | 0.047864 | 0.041395 | 0 | 0 | 1.926 | 22.788
2004-2013 | 0.126 | 0.016697 | 0.00060004 | 0.13973 | 0 | 0.21108 | 0 | 0.1189 | 0.064913 | 0.039884 | 0.0042377 | 0.006507 | 0.0061277 | 0 | 0 | 0.020385 | 0.75507 |  | 2004-2013 | 4.1671 | 0.55218 | 0.023596 | 14.1145 | 0 | 6.9806 | 0 | 3.9322 | 2.1468 | 1.319 | 0.14015 | 0.2152 | 0.20265 | 0 | 0 | 0.67416 | 34.4682 |  | 2004-2013 | 1.221 | 0.16179 | 0.0052791 | 0 | 0 | 2.0453 | 0 | 1.1521 | 0.629 | 0.38647 | 0.041062 | 0.063052 | 0.059376 | 0 | 0 | 0.19753 | 5.9619 |  | 2004-2013 | 0 | 0 | 5.579e-05 | 0.14115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1412 |  | 2004-2013 | 12.7823 | 1.6938 | 0.061364 | 15.4272 | 0 | 21.4122 | 0 | 12.0617 | 6.585 | 4.0459 | 0.42988 | 0.66009 | 0.62161 | 0 | 0 | 2.0679 | 77.8488
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | -0.004363% | -30.26% |  | -4.098% |  | 18.96% | 100% | 10.03% | 0.9488% | 0% | -0.003803% | 0% |  | 0% | 2.699% |  | 2004-2007 | 0% | 0% | -0.0005582% | -30.26% |  | -4.098% |  | 18.96% | 100% | 10.03% | 0.9488% | 0% | -0.003803% | 0% |  | 0% | -1.964% |  | 2004-2007 | 0% | 0% | -0.04708% |  |  | -4.098% |  | 18.96% | 100% | 10.03% | 0.9488% | 0% | -0.003803% | 0% |  | 0% | 6.697% |  | 2004-2007 |  |  | 0.00155% | -30.26% | [9 empty] | 0% |  |  | -13.35% |  | 2004-2007 | 0% | 0% | -0.003937% | -30.26% |  | -4.098% |  | 18.96% | 100% | 10.03% | 0.9488% | 0% | -0.003803% | 0% |  | 0% | 2.421%
2007-2010 | 12.6% | 23.24% | 0.3401% | 67.17% |  | 26.65% |  | 10.64% |  | 63.46% | -3.128% | 2.628% | 42.57% | 0% |  | 0.6212% | 17.83% |  | 2007-2010 | 12.6% | 23.24% | 0.1441% | 67.17% |  | 26.65% |  | 10.64% |  | 63.46% | -3.128% | 2.628% | 42.57% | 0% |  | 0.6214% | 23.07% |  | 2007-2010 | 12.6% | 23.24% | 2.54% |  |  | 26.65% |  | 10.64% |  | 63.46% | -3.128% | 2.628% | 42.57% | 0% |  | 0.6211% | 12.92% |  | 2007-2010 |  |  | 0.03547% | 67.17% | [9 empty] | 0% |  |  | 34.05% |  | 2007-2010 | 12.6% | 23.24% | 0.3182% | 67.17% |  | 26.65% |  | 10.64% |  | 63.46% | -3.128% | 2.628% | 42.57% | 0% |  | 0.6211% | 18.16%
2010-2013 | 27.87% | 0% | -0.001779% | 6.418% |  | 16.84% |  | 22.65% | -31.16% | 8.91% | 19.27% | 0.211% | 5.288% | 0% |  | 8.483% | 10.58% |  | 2010-2013 | 27.87% | 0% | -0.001934% | 6.418% |  | 16.84% |  | 22.65% | -31.16% | 8.91% | 19.27% | 0.211% | 5.288% | 0% |  | 8.486% | 8.1% |  | 2010-2013 | 27.87% | 0% | 0% |  |  | 16.84% |  | 22.65% | -31.16% | 8.91% | 19.27% | 0.211% | 5.288% | 0% |  | 8.482% | 12.64% |  | 2010-2013 |  |  | -0.002019% | 6.418% | [9 empty] | 0% |  |  | 1.618% |  | 2010-2013 | 27.87% | 0% | -0.001796% | 6.418% |  | 16.84% |  | 22.65% | -31.16% | 8.91% | 19.27% | 0.211% | 5.288% | 0% |  | 8.482% | 10.44%
2004-2013 | 36.96% | 23.24% | 0.334% | 59.98% |  | 36.5% |  | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% |  | 9.051% | 28.51% |  | 2004-2013 | 36.96% | 23.24% | 0.1416% | 59.98% |  | 36.5% |  | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% |  | 9.054% | 27.92% |  | 2004-2013 | 36.96% | 23.24% | 2.494% |  |  | 36.5% |  | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% |  | 9.05% | 29.02% |  | 2004-2013 |  |  | 0.035% | 59.98% | [9 empty] | 0% |  |  | 26.46% |  | 2004-2013 | 36.96% | 23.24% | 0.3125% | 59.98% |  | 36.5% |  | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% |  | 9.05% | 28.48%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.21512 | 0.055228 | 0.16079 | 0.015666 | 0 | 0.86204 | 0 | 0.14017 | 0.067174 | 0.024099 | 0.020042 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 2.3119 | 2.196% | CZ 1A | 7.1145 | 1.8265 | 14.7947 | 1.5824 | 0 | 28.5088 | 0 | 4.6355 | 2.2215 | 0.79697 | 0.66283 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 96.339 | 2.196% | CZ 1A | 2.0845 | 0.53515 | 0.2064 | 0 | 0 | 8.353 | 0 | 1.3582 | 0.6509 | 0.23351 | 0.19421 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 19.5671 | 2.196% | CZ 1A | 0 | 0 | 0.1409 | 0.015824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.2956 | 2.196% | CZ 1A | 21.8228 | 5.6025 | 17.5615 | 1.7295 | 0 | 87.4476 | 0 | 14.2189 | 6.8143 | 2.4446 | 2.0331 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 237.1568 | 2.196%
CZ 1B | 0.21511 | 0.055218 | 0.15738 | 0.030741 | 0 | 0.7746 | 0 | 0.16857 | 0.066049 | 0.020178 | 0.01988 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 2.2594 | 0% | CZ 1B | 7.1139 | 1.8261 | 14.4503 | 3.1052 | 0 | 25.6171 | 0 | 5.5749 | 2.1843 | 0.66733 | 0.65747 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 95.392 | 0% | CZ 1B | 2.0844 | 0.53506 | 0.2064 | 0 | 0 | 7.5058 | 0 | 1.6334 | 0.64001 | 0.19553 | 0.19264 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 18.9444 | 0% | CZ 1B | 0 | 0 | 0.13746 | 0.031052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.30738 | 0% | CZ 1B | 21.8212 | 5.6015 | 17.185 | 3.3939 | 0 | 78.5777 | 0 | 17.1005 | 6.7002 | 2.047 | 2.0167 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 231.9257 | 0%
CZ 2A | 0.21523 | 0.055204 | 0.16863 | 0.058928 | 0 | 0.61068 | 0 | 0.13847 | 0.050012 | 0.020951 | 0.019998 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 2.0897 | 12.54% | CZ 2A | 7.118 | 1.8257 | 15.586 | 5.9523 | 0 | 20.196 | 0 | 4.5793 | 1.654 | 0.69287 | 0.66135 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 92.4607 | 12.54% | CZ 2A | 2.0855 | 0.53492 | 0.2064 | 0 | 0 | 5.9174 | 0 | 1.3417 | 0.48461 | 0.20301 | 0.19377 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 16.9185 | 12.54% | CZ 2A | 0 | 0 | 0.14882 | 0.059523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.34721 | 12.54% | CZ 2A | 21.8336 | 5.6001 | 18.4263 | 6.5059 | 0 | 61.949 | 0 | 14.0465 | 5.0733 | 2.1253 | 2.0286 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 215.0703 | 12.54%
CZ 2B | 0.21521 | 0.05519 | 0.16407 | 0.029307 | 0 | 0.60256 | 0 | 0.15977 | 0.045934 | 0.019148 | 0.019904 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 2.0627 | 2.523% | CZ 2B | 7.1174 | 1.8252 | 15.1254 | 2.9603 | 0 | 19.9276 | 0 | 5.2839 | 1.5191 | 0.63325 | 0.65825 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 89.2457 | 2.523% | CZ 2B | 2.0854 | 0.53478 | 0.2064 | 0 | 0 | 5.8387 | 0 | 1.5482 | 0.4451 | 0.18554 | 0.19286 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 16.9881 | 2.523% | CZ 2B | 0 | 0 | 0.14421 | 0.029603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.31269 | 2.523% | CZ 2B | 21.8319 | 5.5986 | 17.9229 | 3.2356 | 0 | 61.1258 | 0 | 16.2078 | 4.6597 | 1.9424 | 2.0191 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 212.0255 | 2.523%
CZ 3A | 0.21532 | 0.055167 | 0.17475 | 0.10123 | 0 | 0.46397 | 0 | 0.13926 | 0.044474 | 0.019631 | 0.019953 | 0.22311 | 0.0073114 | 0.31637 | 0 | 0.20483 | 1.9854 | 12.83% | CZ 3A | 7.121 | 1.8244 | 16.2049 | 10.2257 | 0 | 15.3442 | 0 | 4.6054 | 1.4708 | 0.64924 | 0.65988 | 7.3786 | 0.2418 | 19.8034 | 0 | 6.7717 | 92.3009 | 12.83% | CZ 3A | 2.0864 | 0.53456 | 0.2064 | 0 | 0 | 4.4958 | 0 | 1.3494 | 0.43095 | 0.19023 | 0.19334 | 2.1619 | 0.070846 | 1.7334 | 0 | 1.9851 | 15.4383 | 12.83% | CZ 3A | 0 | 0 | 0.155 | 0.10226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39614 | 12.83% | CZ 3A | 21.8428 | 5.5963 | 19.1028 | 11.1767 | 0 | 47.0666 | 0 | 14.1265 | 4.5116 | 1.9915 | 2.0241 | 22.633 | 0.74169 | 33.3255 | 0 | 20.782 | 204.921 | 12.83%
CZ 3B | 0.21524 | 0.05519 | 0.17272 | 0.044297 | 0 | 0.37053 | 0 | 0.15892 | 0.041019 | 0.014516 | 0.019887 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 1.8439 | 16.01% | CZ 3B | 7.1183 | 1.8252 | 15.9992 | 4.4744 | 0 | 12.254 | 0 | 5.2556 | 1.3565 | 0.48008 | 0.6577 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 83.6164 | 16.01% | CZ 3B | 2.0857 | 0.53478 | 0.2064 | 0 | 0 | 3.5904 | 0 | 1.5399 | 0.39747 | 0.14066 | 0.19271 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 14.6391 | 16.01% | CZ 3B | 0 | 0 | 0.15295 | 0.044744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.33657 | 16.01% | CZ 3B | 21.8347 | 5.5986 | 18.878 | 4.8905 | 0 | 37.5877 | 0 | 16.1211 | 4.1611 | 1.4726 | 2.0174 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 190.0437 | 16.01%
CZ 3C | 0.2153 | 0.055164 | 0.18139 | 0.07816 | 0 | 0.11628 | 0 | 0.14288 | 0 | 0.010319 | 0.020021 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 1.5711 | 2.133% | CZ 3C | 7.1204 | 1.8244 | 16.8751 | 7.8949 | 0 | 3.8455 | 0 | 4.7253 | 0 | 0.34127 | 0.66213 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 77.4843 | 2.133% | CZ 3C | 2.0862 | 0.53453 | 0.2064 | 0 | 0 | 1.1267 | 0 | 1.3845 | 0 | 0.099992 | 0.194 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 11.5836 | 2.133% | CZ 3C | 0 | 0 | 0.16171 | 0.078949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.37953 | 2.133% | CZ 3C | 21.8409 | 5.596 | 19.8354 | 8.6292 | 0 | 11.7957 | 0 | 14.4944 | 0 | 1.0468 | 2.031 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 162.7511 | 2.133%
CZ 4A | 0.21465 | 0.055134 | 0.18227 | 0.09563 | 0 | 0.31833 | 0 | 0.15147 | 0.046153 | 0.017195 | 0.019927 | 0.22311 | 0.0073114 | 0.31637 | 0 | 0.20483 | 1.8524 | 19.36% | CZ 4A | 7.0988 | 1.8234 | 16.9636 | 9.6596 | 0 | 10.5277 | 0 | 5.0095 | 1.5263 | 0.56866 | 0.65902 | 7.3786 | 0.2418 | 19.8034 | 0 | 6.7717 | 88.0318 | 19.36% | CZ 4A | 2.0799 | 0.53424 | 0.2064 | 0 | 0 | 3.0846 | 0 | 1.4678 | 0.44721 | 0.16662 | 0.19309 | 2.1619 | 0.070846 | 1.7334 | 0 | 1.9851 | 14.131 | 19.36% | CZ 4A | 0 | 0 | 0.16259 | 0.096596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39806 | 19.36% | CZ 4A | 21.7747 | 5.5929 | 19.932 | 10.5579 | 0 | 32.2926 | 0 | 15.366 | 4.6819 | 1.7443 | 2.0215 | 22.633 | 0.74169 | 33.3255 | 0 | 20.782 | 191.446 | 19.36%
CZ 4B | 0.21465 | 0.05515 | 0.18112 | 0.058951 | 0 | 0.2725 | 0 | 0.18149 | 0.039319 | 0.013566 | 0.019857 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 1.7882 | 0.7475% | CZ 4B | 7.0988 | 1.8239 | 16.8478 | 5.9547 | 0 | 9.0118 | 0 | 6.0021 | 1.3003 | 0.44864 | 0.65669 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 83.34 | 0.7475% | CZ 4B | 2.0799 | 0.5344 | 0.2064 | 0 | 0 | 2.6404 | 0 | 1.7586 | 0.381 | 0.13145 | 0.19241 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 13.8758 | 0.7475% | CZ 4B | 0 | 0 | 0.16143 | 0.059547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.35985 | 0.7475% | CZ 4B | 21.7747 | 5.5946 | 19.8054 | 6.5085 | 0 | 27.6427 | 0 | 18.4109 | 3.9887 | 1.3761 | 2.0143 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 184.5977 | 0.7475%
CZ 4C | 0.21471 | 0.055108 | 0.18544 | 0.096393 | 0 | 0.16302 | 0 | 0.15401 | 0.037423 | 0.012624 | 0.019944 | 0.22311 | 0.0073043 | 0.31637 | 0 | 0.20483 | 1.6903 | 2.475% | CZ 4C | 7.1006 | 1.8225 | 17.2843 | 9.7366 | 0 | 5.3914 | 0 | 5.0935 | 1.2376 | 0.41751 | 0.65957 | 7.3786 | 0.24156 | 19.8034 | 0 | 6.7717 | 82.9388 | 2.475% | CZ 4C | 2.0805 | 0.53399 | 0.2064 | 0 | 0 | 1.5797 | 0 | 1.4924 | 0.36262 | 0.12233 | 0.19325 | 2.1619 | 0.070778 | 1.7334 | 0 | 1.9851 | 12.5222 | 2.475% | CZ 4C | 0 | 0 | 0.1658 | 0.097366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.40204 | 2.475% | CZ 4C | 21.7805 | 5.5903 | 20.2826 | 10.6421 | 0 | 16.5376 | 0 | 15.6236 | 3.7962 | 1.2807 | 2.0231 | 22.633 | 0.74097 | 33.3255 | 0 | 20.782 | 175.0382 | 2.475%
CZ 5A | 0.21467 | 0.055138 | 0.18751 | 0.1426 | 0 | 0.25966 | 0 | 0.15586 | 0.042214 | 0.016714 | 0.019918 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 1.8459 | 18.57% | CZ 5A | 7.0996 | 1.8235 | 17.4932 | 14.4045 | 0 | 8.5874 | 0 | 5.1545 | 1.3961 | 0.55274 | 0.65871 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 91.3655 | 18.57% | CZ 5A | 2.0802 | 0.53428 | 0.2064 | 0 | 0 | 2.5161 | 0 | 1.5102 | 0.40904 | 0.16195 | 0.193 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 13.5623 | 18.57% | CZ 5A | 0 | 0 | 0.16789 | 0.14405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.45081 | 18.57% | CZ 5A | 21.7771 | 5.5934 | 20.5109 | 15.7442 | 0 | 26.3409 | 0 | 15.8108 | 4.2823 | 1.6955 | 2.0205 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 191.2574 | 18.57%
CZ 5B | 0.21463 | 0.055092 | 0.18657 | 0.10065 | 0 | 0.2006 | 0 | 0.16385 | 0.041364 | 0.013615 | 0.019845 | 0.22311 | 0.0073043 | 0.31637 | 0 | 0.20483 | 1.7478 | 4.034% | CZ 5B | 7.098 | 1.822 | 17.3987 | 10.1671 | 0 | 6.6341 | 0 | 5.4189 | 1.368 | 0.45027 | 0.65631 | 7.3786 | 0.24156 | 19.8034 | 0 | 6.7717 | 85.2085 | 4.034% | CZ 5B | 2.0797 | 0.53383 | 0.2064 | 0 | 0 | 1.9438 | 0 | 1.5877 | 0.40081 | 0.13193 | 0.1923 | 2.1619 | 0.070778 | 1.7334 | 0 | 1.9851 | 13.0276 | 4.034% | CZ 5B | 0 | 0 | 0.16694 | 0.10167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.40749 | 4.034% | CZ 5B | 21.7724 | 5.5886 | 20.4076 | 11.1127 | 0 | 20.3493 | 0 | 16.6219 | 4.1961 | 1.3811 | 2.0131 | 22.633 | 0.74097 | 33.3255 | 0 | 20.782 | 180.9243 | 4.034%
CZ 5C | 0.21511 | 0.055052 | 0.18757 | 0.11544 | 0 | 0.10482 | 0 | 0.15387 | 0.037134 | 0.011101 | 0.019937 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 1.6516 | 0% | CZ 5C | 7.114 | 1.8206 | 17.4996 | 11.6602 | 0 | 3.4664 | 0 | 5.0886 | 1.2281 | 0.36712 | 0.65933 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 83.0992 | 0% | CZ 5C | 2.0844 | 0.53344 | 0.2064 | 0 | 0 | 1.0157 | 0 | 1.4909 | 0.35982 | 0.10757 | 0.19318 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 11.9426 | 0% | CZ 5C | 0 | 0 | 0.16795 | 0.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.42343 | 0% | CZ 5C | 21.8214 | 5.5846 | 20.5178 | 12.7446 | 0 | 10.6329 | 0 | 15.6086 | 3.767 | 1.1261 | 2.0224 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 171.3072 | 0%
CZ 6A | 0.21473 | 0.055108 | 0.19217 | 0.16717 | 0 | 0.18343 | 0 | 0.15652 | 0.041256 | 0.0147 | 0.019894 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 1.7966 | 4.577% | CZ 6A | 7.1016 | 1.8225 | 17.9636 | 16.8858 | 0 | 6.0662 | 0 | 5.1765 | 1.3644 | 0.48613 | 0.65794 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 91.7199 | 4.577% | CZ 6A | 2.0807 | 0.53399 | 0.2064 | 0 | 0 | 1.7774 | 0 | 1.5167 | 0.39976 | 0.14244 | 0.19277 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 12.8014 | 4.577% | CZ 6A | 0 | 0 | 0.17259 | 0.16886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.48032 | 4.577% | CZ 6A | 21.7833 | 5.5903 | 21.025 | 18.4562 | 0 | 18.6074 | 0 | 15.8782 | 4.1851 | 1.4912 | 2.0181 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 186.5168 | 4.577%
CZ 6B | 0.21457 | 0.055092 | 0.19284 | 0.14057 | 0 | 0.14182 | 0 | 0.17119 | 0.042643 | 0.012667 | 0.019836 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 1.7429 | 1.165% | CZ 6B | 7.0961 | 1.822 | 18.0317 | 14.1991 | 0 | 4.6903 | 0 | 5.6617 | 1.4103 | 0.4189 | 0.656 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 88.1812 | 1.165% | CZ 6B | 2.0792 | 0.53383 | 0.2064 | 0 | 0 | 1.3743 | 0 | 1.6588 | 0.41321 | 0.12274 | 0.1922 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 12.5318 | 1.165% | CZ 6B | 0 | 0 | 0.17327 | 0.14199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.45414 | 1.165% | CZ 6B | 21.7666 | 5.5886 | 21.0994 | 15.5196 | 0 | 14.387 | 0 | 17.3665 | 4.3258 | 1.2849 | 2.0122 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 180.8325 | 1.165%
CZ 7 | 0.21418 | 0.05507 | 0.19954 | 0.19968 | 0 | 0.14454 | 0 | 0.16666 | 0.041908 | 0.014972 | 0.019873 | 0.22311 | 0.0073067 | 0.31637 | 0 | 0.20483 | 1.808 | 0.7736% | CZ 7 | 7.0831 | 1.8213 | 18.7082 | 20.1698 | 0 | 4.78 | 0 | 5.5118 | 1.386 | 0.49514 | 0.65724 | 7.3786 | 0.24164 | 19.8034 | 0 | 6.7717 | 94.8078 | 0.7736% | CZ 7 | 2.0753 | 0.53362 | 0.2064 | 0 | 0 | 1.4005 | 0 | 1.6149 | 0.40609 | 0.14507 | 0.19257 | 2.1619 | 0.0708 | 1.7334 | 0 | 1.9851 | 12.5257 | 0.7736% | CZ 7 | 0 | 0 | 0.18004 | 0.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.52061 | 0.7736% | CZ 7 | 21.7266 | 5.5865 | 21.8389 | 22.0456 | 0 | 14.6621 | 0 | 16.9069 | 4.2513 | 1.5188 | 2.016 | 22.633 | 0.74121 | 33.3255 | 0 | 20.782 | 188.0344 | 0.7736%
CZ 8 | 0.21442 | 0.054723 | 0.20863 | 0.39795 | 0 | 0.098117 | 0 | 0.17916 | 0.044854 | 0.015643 | 0.019796 | 0.22311 | 0.0073043 | 0.31637 | 0 | 0.20483 | 1.9849 | 0.07229% | CZ 8 | 7.0912 | 1.8098 | 19.6266 | 40.1974 | 0 | 3.2449 | 0 | 5.9251 | 1.4834 | 0.51734 | 0.65468 | 7.3786 | 0.24156 | 19.8034 | 0 | 6.7717 | 114.7456 | 0.07229% | CZ 8 | 2.0777 | 0.53026 | 0.20642 | 0 | 0 | 0.95074 | 0 | 1.736 | 0.43463 | 0.15158 | 0.19182 | 2.1619 | 0.070778 | 1.7334 | 0 | 1.9851 | 12.2303 | 0.07229% | CZ 8 | 0 | 0 | 0.18922 | 0.40197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.73007 | 0.07229% | CZ 8 | 21.7514 | 5.5513 | 22.8429 | 43.9358 | 0 | 9.9533 | 0 | 18.1747 | 4.5502 | 1.5869 | 2.0081 | 22.633 | 0.74097 | 33.3255 | 0 | 20.782 | 207.836 | 0.07229%
Us Weighted | 0.21495 | 0.055156 | 0.17906 | 0.093215 | 0 | 0.36727 | 0 | 0.15144 | 0.043581 | 0.017044 | 0.019929 | 0.22311 | 0.007309 | 0.31637 | 0 | 0.20483 | 1.8933 | 100% | Us Weighted | 7.1086 | 1.8241 | 16.6398 | 9.4157 | 0 | 12.1462 | 0 | 5.0085 | 1.4413 | 0.56368 | 0.65907 | 7.3786 | 0.24172 | 19.8034 | 0 | 6.7717 | 89.0021 | 100% | Us Weighted | 2.0828 | 0.53445 | 0.2064 | 0 | 0 | 3.5588 | 0 | 1.4675 | 0.42229 | 0.16516 | 0.19311 | 2.1619 | 0.070823 | 1.7334 | 0 | 1.9851 | 14.5817 | 100% | Us Weighted | 0 | 0 | 0.15935 | 0.094157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39238 | 100% | Us Weighted | 21.8048 | 5.5952 | 19.5781 | 10.2913 | 0 | 37.2571 | 0 | 15.363 | 4.4209 | 1.729 | 2.0216 | 22.633 | 0.74145 | 33.3255 | 0 | 20.782 | 195.543 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29833 | 0.055228 | 0.16079 | 0.020476 | 0 | 1.0038 | 0 | 0.21925 | 0.067946 | 0.026674 | 0.024793 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.6488 | 2.196% | CZ 1A | 9.8663 | 1.8265 | 14.7946 | 2.0682 | 0 | 33.1986 | 0 | 7.2509 | 2.2471 | 0.88214 | 0.81996 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 107.8066 | 2.196% | CZ 1A | 2.8908 | 0.53515 | 0.2064 | 0 | 0 | 9.7271 | 0 | 2.1245 | 0.65839 | 0.25846 | 0.24024 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 22.7847 | 2.196% | CZ 1A | 0 | 0 | 0.1409 | 0.020682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.30046 | 2.196% | CZ 1A | 30.2638 | 5.6025 | 17.5613 | 2.2606 | 0 | 101.8332 | 0 | 22.2412 | 6.8926 | 2.7059 | 2.5151 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 271.3733 | 2.196%
CZ 1B | 0.29841 | 0.055218 | 0.15738 | 0.049419 | 0 | 0.98129 | 0 | 0.26169 | 0.0072981 | 0.022805 | 0.024613 | 0.22358 | 0.0077198 | 0.31637 | 0 | 0.22382 | 2.6296 | 0% | CZ 1B | 9.8689 | 1.8261 | 14.4503 | 4.9918 | 0 | 32.4526 | 0 | 8.6545 | 0.24136 | 0.7542 | 0.81398 | 7.3942 | 0.25531 | 19.8034 | 0 | 7.3996 | 108.9061 | 0% | CZ 1B | 2.8916 | 0.53506 | 0.2064 | 0 | 0 | 9.5085 | 0 | 2.5357 | 0.070718 | 0.22098 | 0.23849 | 2.1665 | 0.074804 | 1.7334 | 0 | 2.1691 | 22.3512 | 0% | CZ 1B | 0 | 0 | 0.13746 | 0.049918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.32625 | 0% | CZ 1B | 30.2717 | 5.6015 | 17.185 | 5.456 | 0 | 99.5448 | 0 | 26.5466 | 0.74034 | 2.3134 | 2.4968 | 22.6808 | 0.78312 | 33.3255 | 0 | 22.708 | 269.6535 | 0%
CZ 2A | 0.29849 | 0.055204 | 0.16863 | 0.063104 | 0 | 0.71013 | 0 | 0.18907 | 0.050246 | 0.022967 | 0.024751 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.3541 | 12.54% | CZ 2A | 9.8716 | 1.8257 | 15.5858 | 6.3741 | 0 | 23.485 | 0 | 6.2527 | 1.6617 | 0.75956 | 0.81856 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 101.487 | 12.54% | CZ 2A | 2.8923 | 0.53492 | 0.2064 | 0 | 0 | 6.881 | 0 | 1.832 | 0.48688 | 0.22255 | 0.23984 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 19.4397 | 12.54% | CZ 2A | 0 | 0 | 0.14881 | 0.063741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.35143 | 12.54% | CZ 2A | 30.28 | 5.6001 | 18.4261 | 6.9669 | 0 | 72.0375 | 0 | 19.1796 | 5.0971 | 2.3299 | 2.5108 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 241.9252 | 12.54%
CZ 2B | 0.29865 | 0.05519 | 0.16407 | 0.048211 | 0 | 0.80338 | 0 | 0.22761 | 0.0063474 | 0.023246 | 0.024676 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 2.4229 | 2.523% | CZ 2B | 9.8768 | 1.8252 | 15.1254 | 4.8698 | 0 | 26.5688 | 0 | 7.5272 | 0.20992 | 0.76879 | 0.81607 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 102.4403 | 2.523% | CZ 2B | 2.8939 | 0.53478 | 0.2064 | 0 | 0 | 7.7846 | 0 | 2.2055 | 0.061505 | 0.22525 | 0.23911 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 20.2946 | 2.523% | CZ 2B | 0 | 0 | 0.14421 | 0.048698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.33178 | 2.523% | CZ 2B | 30.2959 | 5.5986 | 17.9229 | 5.3227 | 0 | 81.497 | 0 | 23.089 | 0.6439 | 2.3582 | 2.5032 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 248.7284 | 2.523%
CZ 3A | 0.29809 | 0.055167 | 0.17475 | 0.093898 | 0 | 0.5386 | 0 | 0.18176 | 0.044599 | 0.021082 | 0.024709 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.2041 | 12.83% | CZ 3A | 9.8583 | 1.8244 | 16.2046 | 9.4847 | 0 | 17.8121 | 0 | 6.0111 | 1.4749 | 0.69722 | 0.81716 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 99.0369 | 12.83% | CZ 3A | 2.8885 | 0.53456 | 0.2064 | 0 | 0 | 5.2189 | 0 | 1.7612 | 0.43215 | 0.20428 | 0.23943 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 17.6291 | 12.83% | CZ 3A | 0 | 0 | 0.155 | 0.094847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.38872 | 12.83% | CZ 3A | 30.2393 | 5.5963 | 19.1025 | 10.3668 | 0 | 54.6368 | 0 | 18.4383 | 4.5242 | 2.1386 | 2.5066 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 227.0465 | 12.83%
CZ 3B | 0.29809 | 0.05519 | 0.17272 | 0.076106 | 0 | 0.46674 | 0 | 0.20504 | 0 | 0.016641 | 0.024657 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.0867 | 16.01% | CZ 3B | 9.8584 | 1.8252 | 15.999 | 7.6875 | 0 | 15.4358 | 0 | 6.7811 | 0 | 0.55034 | 0.81545 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 93.8051 | 16.01% | CZ 3B | 2.8885 | 0.53478 | 0.2064 | 0 | 0 | 4.5227 | 0 | 1.9868 | 0 | 0.16125 | 0.23893 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 16.683 | 16.01% | CZ 3B | 0 | 0 | 0.15295 | 0.076875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.36869 | 16.01% | CZ 3B | 30.2395 | 5.5986 | 18.8777 | 8.4024 | 0 | 47.3476 | 0 | 20.8003 | 0 | 1.6881 | 2.5013 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 214.9528 | 16.01%
CZ 3C | 0.29812 | 0.055164 | 0.18139 | 0.06737 | 0 | 0.16396 | 0 | 0.17309 | 0 | 0.011789 | 0.024775 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 1.7471 | 2.133% | CZ 3C | 9.8592 | 1.8244 | 16.8747 | 6.8051 | 0 | 5.4222 | 0 | 5.7243 | 0 | 0.38987 | 0.81933 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 82.5713 | 2.133% | CZ 3C | 2.8887 | 0.53453 | 0.2064 | 0 | 0 | 1.5887 | 0 | 1.6772 | 0 | 0.11423 | 0.24006 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 13.3935 | 2.133% | CZ 3C | 0 | 0 | 0.1617 | 0.068051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.36863 | 2.133% | CZ 3C | 30.2421 | 5.596 | 19.8349 | 7.438 | 0 | 16.6321 | 0 | 17.5587 | 0 | 1.1959 | 2.5132 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 180.5078 | 2.133%
CZ 4A | 0.29777 | 0.055134 | 0.18226 | 0.083297 | 0 | 0.37958 | 0 | 0.19193 | 0.046268 | 0.018575 | 0.024681 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.051 | 19.36% | CZ 4A | 9.8478 | 1.8234 | 16.9629 | 8.4139 | 0 | 12.5532 | 0 | 6.3475 | 1.5301 | 0.61431 | 0.81623 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 93.7615 | 19.36% | CZ 4A | 2.8854 | 0.53424 | 0.2064 | 0 | 0 | 3.678 | 0 | 1.8598 | 0.44833 | 0.17999 | 0.23915 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 16.175 | 19.36% | CZ 4A | 0 | 0 | 0.16258 | 0.084139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.3856 | 19.36% | CZ 4A | 30.2071 | 5.5929 | 19.9312 | 9.1963 | 0 | 38.5054 | 0 | 19.4701 | 4.6935 | 1.8843 | 2.5037 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 211.4819 | 19.36%
CZ 4B | 0.29782 | 0.05515 | 0.18112 | 0.13141 | 0 | 0.33847 | 0 | 0.25924 | 0 | 0.015908 | 0.024617 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 2.0752 | 0.7475% | CZ 4B | 9.8492 | 1.8239 | 16.8474 | 13.2738 | 0 | 11.1938 | 0 | 8.5736 | 0 | 0.52611 | 0.81413 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 97.7541 | 0.7475% | CZ 4B | 2.8858 | 0.5344 | 0.2064 | 0 | 0 | 3.2798 | 0 | 2.512 | 0 | 0.15415 | 0.23854 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 15.9547 | 0.7475% | CZ 4B | 0 | 0 | 0.16143 | 0.13274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.43304 | 0.7475% | CZ 4B | 30.2114 | 5.5946 | 19.805 | 14.5082 | 0 | 34.3358 | 0 | 26.2985 | 0 | 1.6138 | 2.4973 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 214.3615 | 0.7475%
CZ 4C | 0.2978 | 0.055108 | 0.18544 | 0.19613 | 0 | 0.20321 | 0 | 0.19089 | 0 | 0.014704 | 0.024714 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 1.9395 | 2.475% | CZ 4C | 9.8485 | 1.8225 | 17.2843 | 19.8107 | 0 | 6.7206 | 0 | 6.3131 | 0 | 0.48629 | 0.81732 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 97.9555 | 2.475% | CZ 4C | 2.8856 | 0.53399 | 0.2064 | 0 | 0 | 1.9691 | 0 | 1.8497 | 0 | 0.14248 | 0.23947 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 13.9704 | 2.475% | CZ 4C | 0 | 0 | 0.1658 | 0.19811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.50278 | 2.475% | CZ 4C | 30.2093 | 5.5903 | 20.2825 | 21.6531 | 0 | 20.6146 | 0 | 19.3649 | 0 | 1.4916 | 2.507 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 201.2103 | 2.475%
CZ 5A | 0.29777 | 0.055138 | 0.18751 | 0.1256 | 0 | 0.31179 | 0 | 0.1961 | 0.0423 | 0.017892 | 0.024671 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 2.0303 | 18.57% | CZ 5A | 9.8475 | 1.8235 | 17.4929 | 12.6871 | 0 | 10.3114 | 0 | 6.4853 | 1.3989 | 0.59171 | 0.81592 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 96.3066 | 18.57% | CZ 5A | 2.8853 | 0.53428 | 0.2064 | 0 | 0 | 3.0212 | 0 | 1.9002 | 0.40988 | 0.17337 | 0.23906 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 15.5134 | 18.57% | CZ 5A | 0 | 0 | 0.16788 | 0.12687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.43363 | 18.57% | CZ 5A | 30.2062 | 5.5934 | 20.5105 | 13.867 | 0 | 31.629 | 0 | 19.893 | 4.2911 | 1.815 | 2.5027 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 209.8052 | 18.57%
CZ 5B | 0.29778 | 0.055092 | 0.18658 | 0.22116 | 0 | 0.2499 | 0 | 0.20603 | 0 | 0.015559 | 0.024592 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 2.0282 | 4.034% | CZ 5B | 9.8481 | 1.822 | 17.3989 | 22.3398 | 0 | 8.2646 | 0 | 6.8138 | 0 | 0.51455 | 0.81328 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 102.6671 | 4.034% | CZ 5B | 2.8855 | 0.53383 | 0.2064 | 0 | 0 | 2.4215 | 0 | 1.9964 | 0 | 0.15076 | 0.23829 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 14.5763 | 4.034% | CZ 5B | 0 | 0 | 0.16694 | 0.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.52922 | 4.034% | CZ 5B | 30.2078 | 5.5886 | 20.4078 | 24.4173 | 0 | 25.3507 | 0 | 20.9006 | 0 | 1.5783 | 2.4946 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 210.4428 | 4.034%
CZ 5C | 0.29802 | 0.055052 | 0.18757 | 0.099731 | 0 | 0.14063 | 0 | 0.18681 | 0.036401 | 0.012268 | 0.02469 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 1.8127 | 0% | CZ 5C | 9.8559 | 1.8206 | 17.4992 | 10.0739 | 0 | 4.6509 | 0 | 6.1782 | 1.2038 | 0.40571 | 0.81654 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 87.3571 | 0% | CZ 5C | 2.8878 | 0.53344 | 0.2064 | 0 | 0 | 1.3627 | 0 | 1.8102 | 0.35272 | 0.11887 | 0.23924 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 13.655 | 0% | CZ 5C | 0 | 0 | 0.16795 | 0.10074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.40756 | 0% | CZ 5C | 30.2319 | 5.5846 | 20.5175 | 11.0107 | 0 | 14.2661 | 0 | 18.951 | 3.6927 | 1.2445 | 2.5046 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 187.5005 | 0%
CZ 6A | 0.29781 | 0.055108 | 0.19216 | 0.14845 | 0 | 0.22695 | 0 | 0.19489 | 0.041319 | 0.015709 | 0.02465 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 1.9685 | 4.577% | CZ 6A | 9.849 | 1.8225 | 17.9633 | 14.9946 | 0 | 7.5057 | 0 | 6.4453 | 1.3665 | 0.51952 | 0.81522 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 96.1337 | 4.577% | CZ 6A | 2.8857 | 0.53399 | 0.2064 | 0 | 0 | 2.1991 | 0 | 1.8884 | 0.40038 | 0.15222 | 0.23886 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 14.6488 | 4.577% | CZ 6A | 0 | 0 | 0.17259 | 0.14995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.46141 | 4.577% | CZ 6A | 30.2107 | 5.5903 | 21.0247 | 16.3891 | 0 | 23.0228 | 0 | 19.7702 | 4.1915 | 1.5936 | 2.5006 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 203.7904 | 4.577%
CZ 6B | 0.29776 | 0.055092 | 0.19284 | 0.12375 | 0 | 0.18305 | 0 | 0.20921 | 0.042519 | 0.013563 | 0.024589 | 0.22358 | 0.0077175 | 0.31637 | 0 | 0.22382 | 1.9138 | 1.165% | CZ 6B | 9.8472 | 1.822 | 18.0313 | 12.5002 | 0 | 6.0536 | 0 | 6.9188 | 1.4062 | 0.44856 | 0.8132 | 7.3942 | 0.25523 | 19.8034 | 0 | 7.3996 | 92.6933 | 1.165% | CZ 6B | 2.8852 | 0.53383 | 0.2064 | 0 | 0 | 1.7737 | 0 | 2.0272 | 0.412 | 0.13143 | 0.23827 | 2.1665 | 0.074781 | 1.7334 | 0 | 2.1691 | 14.3517 | 1.165% | CZ 6B | 0 | 0 | 0.17327 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.43714 | 1.165% | CZ 6B | 30.2052 | 5.5886 | 21.099 | 13.6627 | 0 | 18.5688 | 0 | 21.2225 | 4.3132 | 1.3759 | 2.4944 | 22.6808 | 0.78288 | 33.3255 | 0 | 22.708 | 198.0277 | 1.165%
CZ 7 | 0.29767 | 0.05507 | 0.19954 | 0.2083 | 0 | 0.17233 | 0 | 0.20819 | 0.041831 | 0.015751 | 0.024629 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 1.9948 | 0.7736% | CZ 7 | 9.8443 | 1.8213 | 18.708 | 21.0404 | 0 | 5.6992 | 0 | 6.8853 | 1.3834 | 0.52091 | 0.81452 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 101.5695 | 0.7736% | CZ 7 | 2.8844 | 0.53362 | 0.2064 | 0 | 0 | 1.6698 | 0 | 2.0174 | 0.40534 | 0.15263 | 0.23865 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 14.2519 | 0.7736% | CZ 7 | 0 | 0 | 0.18004 | 0.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.52931 | 0.7736% | CZ 7 | 30.1964 | 5.5865 | 21.8387 | 22.9972 | 0 | 17.4815 | 0 | 21.1199 | 4.2435 | 1.5978 | 2.4985 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 207.0569 | 0.7736%
CZ 8 | 0.29785 | 0.054723 | 0.20863 | 0.43121 | 0 | 0.12041 | 0 | 0.23562 | 0.044899 | 0.016756 | 0.024549 | 0.22358 | 0.0077151 | 0.31637 | 0 | 0.22382 | 2.2061 | 0.07229% | CZ 8 | 9.8503 | 1.8098 | 19.6265 | 43.5568 | 0 | 3.982 | 0 | 7.7922 | 1.4849 | 0.55414 | 0.81188 | 7.3942 | 0.25515 | 19.8034 | 0 | 7.3996 | 124.3207 | 0.07229% | CZ 8 | 2.8861 | 0.53026 | 0.20642 | 0 | 0 | 1.1667 | 0 | 2.2831 | 0.43506 | 0.16236 | 0.23788 | 2.1665 | 0.074758 | 1.7334 | 0 | 2.1691 | 14.0516 | 0.07229% | CZ 8 | 0 | 0 | 0.18922 | 0.43557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.76366 | 0.07229% | CZ 8 | 30.2147 | 5.5513 | 22.8427 | 47.6076 | 0 | 12.2143 | 0 | 23.9017 | 4.5547 | 1.6998 | 2.4904 | 22.6808 | 0.78264 | 33.3255 | 0 | 22.708 | 230.5741 | 0.07229%
Us Weighted | 0.298 | 0.055156 | 0.17906 | 0.099608 | 0 | 0.44163 | 0 | 0.19578 | 0.033227 | 0.018712 | 0.024686 | 0.22358 | 0.0077171 | 0.31637 | 0 | 0.22382 | 2.1173 | 100% | Us Weighted | 9.8552 | 1.8241 | 16.6395 | 10.0614 | 0 | 14.6054 | 0 | 6.4747 | 1.0988 | 0.61882 | 0.8164 | 7.3942 | 0.25521 | 19.8034 | 0 | 7.3996 | 96.8467 | 100% | Us Weighted | 2.8876 | 0.53445 | 0.2064 | 0 | 0 | 4.2793 | 0 | 1.8971 | 0.32196 | 0.18131 | 0.2392 | 2.1665 | 0.074777 | 1.7334 | 0 | 2.1691 | 16.691 | 100% | Us Weighted | 0 | 0 | 0.15935 | 0.10061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.39884 | 100% | Us Weighted | 30.2298 | 5.5952 | 19.5778 | 10.9971 | 0 | 44.8005 | 0 | 19.8605 | 3.3706 | 1.8982 | 2.5042 | 22.6808 | 0.78284 | 33.3255 | 0 | 22.708 | 218.331 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.34095 | 0.071946 | 0.16138 | 0.047594 | 0 | 1.5038 | 0 | 0.252 | 0 | 0.087305 | 0.024148 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 3.2738 | 2.196% | CZ 1A | 11.2757 | 2.3794 | 14.8159 | 4.8075 | 0 | 49.7336 | 0 | 8.3338 | 0 | 2.8873 | 0.79861 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 130.3191 | 2.196% | CZ 1A | 3.3038 | 0.69714 | 0.21179 | 0 | 0 | 14.5718 | 0 | 2.4418 | 0 | 0.84597 | 0.23399 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 28.5774 | 2.196% | CZ 1A | 0 | 0 | 0.14093 | 0.048075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.32788 | 2.196% | CZ 1A | 34.587 | 7.2984 | 17.6209 | 5.2546 | 0 | 152.5525 | 0 | 25.5631 | 0 | 8.8565 | 2.4496 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 335.0141 | 2.196%
CZ 1B | 0.34095 | 0.071934 | 0.15797 | 0.09212 | 0 | 1.1967 | 0 | 0.2973 | 0 | 0.07088 | 0.023843 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 3.0363 | 0% | CZ 1B | 11.2757 | 2.379 | 14.4718 | 9.305 | 0 | 39.5768 | 0 | 9.8322 | 0 | 2.3441 | 0.78851 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 125.2605 | 0% | CZ 1B | 3.3038 | 0.69703 | 0.21174 | 0 | 0 | 11.5959 | 0 | 2.8808 | 0 | 0.68682 | 0.23103 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 25.8782 | 0% | CZ 1B | 0 | 0 | 0.13749 | 0.09305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.36942 | 0% | CZ 1B | 34.587 | 7.2972 | 17.2446 | 10.1704 | 0 | 121.3976 | 0 | 30.1593 | 0 | 7.1903 | 2.4187 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 311.2965 | 0%
CZ 2A | 0.34095 | 0.071915 | 0.16922 | 0.1436 | 0 | 1.0757 | 0 | 0.22095 | 0 | 0.070554 | 0.024077 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.9016 | 12.54% | CZ 2A | 11.2757 | 2.3783 | 15.6076 | 14.5051 | 0 | 35.5751 | 0 | 7.307 | 0 | 2.3333 | 0.79628 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 125.0658 | 12.54% | CZ 2A | 3.3038 | 0.69685 | 0.21179 | 0 | 0 | 10.4234 | 0 | 2.1409 | 0 | 0.68366 | 0.23331 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 23.9648 | 12.54% | CZ 2A | 0 | 0 | 0.14885 | 0.14505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.43277 | 12.54% | CZ 2A | 34.587 | 7.2953 | 18.4862 | 15.8541 | 0 | 109.1228 | 0 | 22.4134 | 0 | 7.1572 | 2.4425 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 298.19 | 12.54%
CZ 2B | 0.34095 | 0.071897 | 0.16466 | 0.099212 | 0 | 1.0018 | 0 | 0.25807 | 0 | 0.06142 | 0.023934 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.8066 | 2.523% | CZ 2B | 11.2757 | 2.3777 | 15.1475 | 10.0214 | 0 | 33.1321 | 0 | 8.5347 | 0 | 2.0313 | 0.79154 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 118.5992 | 2.523% | CZ 2B | 3.3038 | 0.69667 | 0.21177 | 0 | 0 | 9.7076 | 0 | 2.5006 | 0 | 0.59515 | 0.23192 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 23.5187 | 2.523% | CZ 2B | 0 | 0 | 0.14425 | 0.10021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.38334 | 2.523% | CZ 2B | 34.587 | 7.2934 | 17.9832 | 10.9534 | 0 | 101.6291 | 0 | 26.1792 | 0 | 6.2306 | 2.428 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 288.1153 | 2.523%
CZ 3A | 0.34095 | 0.071866 | 0.17535 | 0.23701 | 0 | 0.78088 | 0 | 0.21299 | 0 | 0.061094 | 0.023984 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.6888 | 12.83% | CZ 3A | 11.2757 | 2.3767 | 16.2272 | 23.9408 | 0 | 25.8249 | 0 | 7.044 | 0 | 2.0205 | 0.79317 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 124.7903 | 12.83% | CZ 3A | 3.3038 | 0.69637 | 0.21179 | 0 | 0 | 7.5666 | 0 | 2.0639 | 0 | 0.59199 | 0.2324 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 20.9379 | 12.83% | CZ 3A | 0 | 0 | 0.15504 | 0.23941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.53333 | 12.83% | CZ 3A | 34.587 | 7.2903 | 19.1635 | 26.1673 | 0 | 79.215 | 0 | 21.6066 | 0 | 6.1975 | 2.433 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 277.4917 | 12.83%
CZ 3B | 0.34095 | 0.071897 | 0.17332 | 0.15177 | 0 | 0.54865 | 0 | 0.2281 | 0 | 0.04285 | 0.023958 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.3661 | 16.01% | CZ 3B | 11.2757 | 2.3777 | 16.0223 | 15.3302 | 0 | 18.1447 | 0 | 7.5435 | 0 | 1.4171 | 0.79232 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 108.191 | 16.01% | CZ 3B | 3.3038 | 0.69667 | 0.21172 | 0 | 0 | 5.3164 | 0 | 2.2102 | 0 | 0.41521 | 0.23215 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 18.6572 | 16.01% | CZ 3B | 0 | 0 | 0.153 | 0.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.44517 | 16.01% | CZ 3B | 34.587 | 7.2934 | 18.9391 | 16.7559 | 0 | 55.6569 | 0 | 23.139 | 0 | 4.3468 | 2.4303 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 243.9801 | 16.01%
CZ 3C | 0.34095 | 0.071864 | 0.18201 | 0.15576 | 0 | 0.21141 | 0 | 0.1858 | 0 | 0.030831 | 0.024016 | 0.22962 | 0.013433 | 0.31637 | 0 | 0.22522 | 1.9873 | 2.133% | CZ 3C | 11.2757 | 2.3766 | 16.8995 | 15.7336 | 0 | 6.9915 | 0 | 6.1448 | 0 | 1.0196 | 0.79426 | 7.5938 | 0.44426 | 19.8034 | 0 | 7.4458 | 96.5228 | 2.133% | CZ 3C | 3.3038 | 0.69635 | 0.21179 | 0 | 0 | 2.0485 | 0 | 1.8004 | 0 | 0.29875 | 0.23272 | 2.225 | 0.13017 | 1.7334 | 0 | 2.1826 | 14.8634 | 2.133% | CZ 3C | 0 | 0 | 0.16177 | 0.15734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.45798 | 2.133% | CZ 3C | 34.587 | 7.2901 | 19.8983 | 17.1968 | 0 | 21.4456 | 0 | 18.8484 | 0 | 3.1276 | 2.4363 | 23.293 | 1.3627 | 33.3255 | 0 | 22.85 | 205.6613 | 2.133%
CZ 4A | 0.34095 | 0.071824 | 0.18288 | 0.34804 | 0 | 0.52786 | 0 | 0.21202 | 0 | 0.051129 | 0.023899 | 0.22962 | 0.01344 | 0.31637 | 0 | 0.22522 | 2.5432 | 19.36% | CZ 4A | 11.2757 | 2.3753 | 16.9878 | 35.1554 | 0 | 17.4572 | 0 | 7.0118 | 0 | 1.6909 | 0.79038 | 7.5938 | 0.4445 | 19.8034 | 0 | 7.4458 | 128.0319 | 19.36% | CZ 4A | 3.3038 | 0.69596 | 0.21179 | 0 | 0 | 5.1149 | 0 | 2.0544 | 0 | 0.49543 | 0.23158 | 2.225 | 0.13024 | 1.7334 | 0 | 2.1826 | 18.379 | 19.36% | CZ 4A | 0 | 0 | 0.16265 | 0.35155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.65308 | 19.36% | CZ 4A | 34.587 | 7.286 | 19.9948 | 38.4248 | 0 | 53.548 | 0 | 21.5078 | 0 | 5.1867 | 2.4244 | 23.293 | 1.3634 | 33.3255 | 0 | 22.85 | 263.7915 | 19.36%
CZ 4B | 0.34095 | 0.071843 | 0.18172 | 0.22614 | 0 | 0.38413 | 0 | 0.27361 | 0 | 0.040702 | 0.024035 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.3278 | 0.7475% | CZ 4B | 11.2757 | 2.3759 | 16.8715 | 22.8428 | 0 | 12.7038 | 0 | 9.0487 | 0 | 1.3461 | 0.79488 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 112.5468 | 0.7475% | CZ 4B | 3.3038 | 0.69614 | 0.21165 | 0 | 0 | 3.7222 | 0 | 2.6512 | 0 | 0.39439 | 0.2329 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 17.4834 | 0.7475% | CZ 4B | 0 | 0 | 0.16149 | 0.22843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.52879 | 0.7475% | CZ 4B | 34.587 | 7.2879 | 19.8668 | 24.9671 | 0 | 38.9676 | 0 | 27.7558 | 0 | 4.1289 | 2.4382 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 240.8311 | 0.7475%
CZ 4C | 0.34095 | 0.071789 | 0.18607 | 0.32581 | 0 | 0.24219 | 0 | 0.20775 | 0 | 0.033378 | 0.023923 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.2165 | 2.475% | CZ 4C | 11.2757 | 2.3742 | 17.3095 | 32.9098 | 0 | 8.0094 | 0 | 6.8705 | 0 | 1.1039 | 0.79115 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 115.9315 | 2.475% | CZ 4C | 3.3038 | 0.69562 | 0.21181 | 0 | 0 | 2.3467 | 0 | 2.0131 | 0 | 0.32343 | 0.23181 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 15.3974 | 2.475% | CZ 4C | 0 | 0 | 0.16587 | 0.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.63384 | 2.475% | CZ 4C | 34.587 | 7.2825 | 20.3466 | 35.9704 | 0 | 24.568 | 0 | 21.0746 | 0 | 3.386 | 2.4268 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 230.4735 | 2.475%
CZ 5A | 0.34095 | 0.071831 | 0.18813 | 0.50004 | 0 | 0.41078 | 0 | 0.21535 | 0 | 0.046434 | 0.023873 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.582 | 18.57% | CZ 5A | 11.2757 | 2.3756 | 17.5183 | 50.5089 | 0 | 13.5851 | 0 | 7.1218 | 0 | 1.5356 | 0.78952 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 139.9979 | 18.57% | CZ 5A | 3.3038 | 0.69603 | 0.21179 | 0 | 0 | 3.9804 | 0 | 2.0867 | 0 | 0.44994 | 0.23133 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 17.2311 | 18.57% | CZ 5A | 0 | 0 | 0.16796 | 0.50509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.81192 | 18.57% | CZ 5A | 34.587 | 7.2867 | 20.5747 | 55.2062 | 0 | 41.6709 | 0 | 21.8455 | 0 | 4.7104 | 2.4218 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 269.1347 | 18.57%
CZ 5B | 0.34095 | 0.071768 | 0.18719 | 0.36812 | 0 | 0.29613 | 0 | 0.22318 | 0 | 0.035268 | 0.023803 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.3311 | 4.034% | CZ 5B | 11.2757 | 2.3735 | 17.4238 | 37.1843 | 0 | 9.7936 | 0 | 7.3809 | 0 | 1.1663 | 0.78719 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 122.6726 | 4.034% | CZ 5B | 3.3038 | 0.69542 | 0.21177 | 0 | 0 | 2.8695 | 0 | 2.1626 | 0 | 0.34174 | 0.23065 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 16.0866 | 4.034% | CZ 5B | 0 | 0 | 0.16701 | 0.37184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.67773 | 4.034% | CZ 5B | 34.587 | 7.2803 | 20.4712 | 40.6424 | 0 | 30.0407 | 0 | 22.6401 | 0 | 3.5776 | 2.4146 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 242.4857 | 4.034%
CZ 5C | 0.34095 | 0.071714 | 0.1882 | 0.38688 | 0 | 0.15616 | 0 | 0.20044 | 0 | 0.027589 | 0.023897 | 0.22962 | 0.01344 | 0.31637 | 0 | 0.22522 | 2.1805 | 0% | CZ 5C | 11.2757 | 2.3717 | 17.5254 | 39.0784 | 0 | 5.1644 | 0 | 6.6287 | 0 | 0.91241 | 0.7903 | 7.5938 | 0.4445 | 19.8034 | 0 | 7.4458 | 119.0345 | 0% | CZ 5C | 3.3038 | 0.69489 | 0.21181 | 0 | 0 | 1.5132 | 0 | 1.9422 | 0 | 0.26733 | 0.23156 | 2.225 | 0.13024 | 1.7334 | 0 | 2.1826 | 14.4359 | 0% | CZ 5C | 0 | 0 | 0.16802 | 0.39078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.69768 | 0% | CZ 5C | 34.587 | 7.2748 | 20.5826 | 42.7127 | 0 | 15.8413 | 0 | 20.3329 | 0 | 2.7987 | 2.4242 | 23.293 | 1.3634 | 33.3255 | 0 | 22.85 | 227.3861 | 0%
CZ 6A | 0.34095 | 0.071789 | 0.1928 | 0.58168 | 0 | 0.28366 | 0 | 0.21286 | 0 | 0.039066 | 0.02381 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.5312 | 4.577% | CZ 6A | 11.2757 | 2.3742 | 17.9893 | 58.7553 | 0 | 9.3809 | 0 | 7.0396 | 0 | 1.292 | 0.78743 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 144.1818 | 4.577% | CZ 6A | 3.3038 | 0.69562 | 0.21181 | 0 | 0 | 2.7486 | 0 | 2.0626 | 0 | 0.37854 | 0.23071 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 15.9028 | 4.577% | CZ 6A | 0 | 0 | 0.17266 | 0.58755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.89909 | 4.577% | CZ 6A | 34.587 | 7.2825 | 21.0896 | 64.2196 | 0 | 28.775 | 0 | 21.5933 | 0 | 3.9629 | 2.4153 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 264.7567 | 4.577%
CZ 6B | 0.34095 | 0.071768 | 0.19347 | 0.50462 | 0 | 0.20421 | 0 | 0.22606 | 0 | 0.031521 | 0.023786 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.381 | 1.165% | CZ 6B | 11.2757 | 2.3735 | 18.0574 | 50.9722 | 0 | 6.7536 | 0 | 7.476 | 0 | 1.0424 | 0.78665 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 134.0247 | 1.165% | CZ 6B | 3.3038 | 0.69542 | 0.21177 | 0 | 0 | 1.9788 | 0 | 2.1904 | 0 | 0.30543 | 0.23049 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 15.1872 | 1.165% | CZ 6B | 0 | 0 | 0.17335 | 0.50972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.82194 | 1.165% | CZ 6B | 34.587 | 7.2803 | 21.1638 | 55.7126 | 0 | 20.7158 | 0 | 22.9318 | 0 | 3.1976 | 2.413 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 248.8333 | 1.165%
CZ 7 | 0.34095 | 0.071739 | 0.20017 | 0.73992 | 0 | 0.20817 | 0 | 0.2261 | 0 | 0.037772 | 0.023786 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.6332 | 0.7736% | CZ 7 | 11.2757 | 2.3725 | 18.7346 | 74.7394 | 0 | 6.8846 | 0 | 7.4773 | 0 | 1.2492 | 0.78665 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 158.8073 | 0.7736% | CZ 7 | 3.3038 | 0.69514 | 0.21179 | 0 | 0 | 2.0172 | 0 | 2.1908 | 0 | 0.36601 | 0.23049 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 15.2863 | 0.7736% | CZ 7 | 0 | 0 | 0.18012 | 0.74739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 1.0664 | 0.7736% | CZ 7 | 34.587 | 7.2775 | 21.9041 | 81.6902 | 0 | 21.1177 | 0 | 22.9359 | 0 | 3.8317 | 2.413 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 276.5885 | 0.7736%
CZ 8 | 0.34095 | 0.071286 | 0.20927 | 1.1411 | 0 | 0.13122 | 0 | 0.26123 | 0 | 0.037207 | 0.023662 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 3.0005 | 0.07229% | CZ 8 | 11.2757 | 2.3575 | 19.6537 | 115.259 | 0 | 4.3397 | 0 | 8.6391 | 0 | 1.2305 | 0.78254 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 198.8251 | 0.07229% | CZ 8 | 3.3038 | 0.69075 | 0.21181 | 0 | 0 | 1.2715 | 0 | 2.5312 | 0 | 0.36053 | 0.22928 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 14.87 | 0.07229% | CZ 8 | 0 | 0 | 0.18931 | 1.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 1.4808 | 0.07229% | CZ 8 | 34.587 | 7.2315 | 22.9088 | 125.9781 | 0 | 13.3116 | 0 | 26.4995 | 0 | 3.7743 | 2.4003 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 317.5227 | 0.07229%
Us Weighted | 0.34095 | 0.071853 | 0.17967 | 0.30345 | 0 | 0.60205 | 0 | 0.21909 | 0 | 0.051216 | 0.023937 | 0.22962 | 0.013437 | 0.31637 | 0 | 0.22522 | 2.5769 | 100% | Us Weighted | 11.2757 | 2.3763 | 16.6635 | 30.6513 | 0 | 19.9107 | 0 | 7.2456 | 0 | 1.6938 | 0.79163 | 7.5938 | 0.44439 | 19.8034 | 0 | 7.4458 | 125.8957 | 100% | Us Weighted | 3.3038 | 0.69624 | 0.21178 | 0 | 0 | 5.8338 | 0 | 2.1229 | 0 | 0.49627 | 0.23195 | 2.225 | 0.1302 | 1.7334 | 0 | 2.1826 | 19.1678 | 100% | Us Weighted | 0 | 0 | 0.15941 | 0.30651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.60479 | 100% | Us Weighted | 34.587 | 7.289 | 19.6402 | 33.5019 | 0 | 61.0738 | 0 | 22.2249 | 0 | 5.1955 | 2.4282 | 23.293 | 1.3631 | 33.3255 | 0 | 22.85 | 266.7721 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.34095 | 0.071946 | 0.16136 | 0.057773 | 0 | 1.3055 | 0 | 0.25252 | 0.1278 | 0.099993 | 0.024465 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 3.2269 | 2.196% | CZ 1A | 11.2757 | 2.3794 | 14.8149 | 5.8356 | 0 | 43.1736 | 0 | 8.3512 | 4.2266 | 3.3069 | 0.80909 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 129.4603 | 2.196% | CZ 1A | 3.3038 | 0.69714 | 0.21163 | 0 | 0 | 12.6498 | 0 | 2.4469 | 1.2384 | 0.96892 | 0.23706 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 28.0247 | 2.196% | CZ 1A | 0 | 0 | 0.14093 | 0.058356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.33816 | 2.196% | CZ 1A | 34.587 | 7.2984 | 17.6188 | 6.3783 | 0 | 132.4303 | 0 | 25.6165 | 12.9647 | 10.1436 | 2.4818 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 330.3508 | 2.196%
CZ 1B | 0.34095 | 0.071934 | 0.15795 | 0.094193 | 0 | 1.1073 | 0 | 0.29968 | 0.12534 | 0.079653 | 0.024129 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 3.0858 | 0% | CZ 1B | 11.2757 | 2.379 | 14.4712 | 9.5145 | 0 | 36.6206 | 0 | 9.9107 | 4.1451 | 2.6342 | 0.79799 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 127.0364 | 0% | CZ 1B | 3.3038 | 0.69703 | 0.21163 | 0 | 0 | 10.7297 | 0 | 2.9038 | 1.2145 | 0.77182 | 0.23381 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 26.3373 | 0% | CZ 1B | 0 | 0 | 0.13749 | 0.095145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.37151 | 0% | CZ 1B | 34.587 | 7.2972 | 17.2431 | 10.3993 | 0 | 112.3297 | 0 | 30.4 | 12.7147 | 8.0802 | 2.4477 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 316.3306 | 0%
CZ 2A | 0.34095 | 0.071915 | 0.1692 | 0.15331 | 0 | 1.0061 | 0 | 0.24914 | 0.12305 | 0.082843 | 0.024282 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 3.0054 | 12.54% | CZ 2A | 11.2757 | 2.3783 | 15.6069 | 15.4862 | 0 | 33.2717 | 0 | 8.2394 | 4.0696 | 2.7397 | 0.80303 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 129.1578 | 12.54% | CZ 2A | 3.3038 | 0.69685 | 0.2117 | 0 | 0 | 9.7485 | 0 | 2.4141 | 1.1924 | 0.80273 | 0.23529 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 24.8765 | 12.54% | CZ 2A | 0 | 0 | 0.14884 | 0.15486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.44258 | 12.54% | CZ 2A | 34.587 | 7.2953 | 18.4849 | 16.9265 | 0 | 102.0573 | 0 | 25.2733 | 12.483 | 8.4038 | 2.4632 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 308.8056 | 12.54%
CZ 2B | 0.34095 | 0.071897 | 0.16466 | 0.13922 | 0 | 1.0262 | 0 | 0.31481 | 0.12037 | 0.074404 | 0.024157 | 0.22962 | 0.013433 | 0.31637 | 0 | 0.22522 | 3.0613 | 2.523% | CZ 2B | 11.2757 | 2.3777 | 15.1477 | 14.0626 | 0 | 33.9379 | 0 | 10.4112 | 3.9809 | 2.4606 | 0.79892 | 7.5938 | 0.44426 | 19.8034 | 0 | 7.4458 | 129.7405 | 2.523% | CZ 2B | 3.3038 | 0.69667 | 0.21168 | 0 | 0 | 9.9437 | 0 | 3.0505 | 1.1664 | 0.72096 | 0.23408 | 2.225 | 0.13017 | 1.7334 | 0 | 2.1826 | 25.5988 | 2.523% | CZ 2B | 0 | 0 | 0.14425 | 0.14063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.42375 | 2.523% | CZ 2B | 34.587 | 7.2934 | 17.9828 | 15.3704 | 0 | 104.1006 | 0 | 31.9352 | 12.211 | 7.5477 | 2.4506 | 23.293 | 1.3627 | 33.3255 | 0 | 22.85 | 314.31 | 2.523%
CZ 3A | 0.34095 | 0.071866 | 0.17533 | 0.16746 | 0 | 0.73058 | 0 | 0.22815 | 0.12062 | 0.069141 | 0.024289 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.713 | 12.83% | CZ 3A | 11.2757 | 2.3767 | 16.2261 | 16.9149 | 0 | 24.1611 | 0 | 7.5452 | 3.9892 | 2.2866 | 0.80326 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 120.8661 | 12.83% | CZ 3A | 3.3038 | 0.69637 | 0.21165 | 0 | 0 | 7.0792 | 0 | 2.2107 | 1.1688 | 0.66996 | 0.23535 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 21.8469 | 12.83% | CZ 3A | 0 | 0 | 0.15504 | 0.16915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.46306 | 12.83% | CZ 3A | 34.587 | 7.2903 | 19.1614 | 18.488 | 0 | 74.1116 | 0 | 23.144 | 12.2365 | 7.0138 | 2.4639 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 279.328 | 12.83%
CZ 3B | 0.34095 | 0.071897 | 0.17331 | 0.13368 | 0 | 0.52037 | 0 | 0.26329 | 0.082878 | 0.04658 | 0.024216 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.4418 | 16.01% | CZ 3B | 11.2757 | 2.3777 | 16.0228 | 13.5032 | 0 | 17.2092 | 0 | 8.7073 | 2.7409 | 1.5405 | 0.80086 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 109.4655 | 16.01% | CZ 3B | 3.3038 | 0.69667 | 0.21161 | 0 | 0 | 5.0423 | 0 | 2.5512 | 0.80307 | 0.45135 | 0.23465 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 19.5657 | 16.01% | CZ 3B | 0 | 0 | 0.15301 | 0.13503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.42691 | 16.01% | CZ 3B | 34.587 | 7.2934 | 18.9389 | 14.759 | 0 | 52.7874 | 0 | 26.7085 | 8.4074 | 4.7252 | 2.4565 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 251.495 | 16.01%
CZ 3C | 0.34095 | 0.071864 | 0.18199 | 0.20804 | 0 | 0.22035 | 0 | 0.21012 | 0 | 0.032425 | 0.024282 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.0747 | 2.133% | CZ 3C | 11.2757 | 2.3766 | 16.899 | 21.0146 | 0 | 7.2874 | 0 | 6.9491 | 0 | 1.0723 | 0.80303 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 102.965 | 2.133% | CZ 3C | 3.3038 | 0.69635 | 0.21168 | 0 | 0 | 2.1352 | 0 | 2.0361 | 0 | 0.31419 | 0.23529 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 15.2036 | 2.133% | CZ 3C | 0 | 0 | 0.16177 | 0.21015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.51079 | 2.133% | CZ 3C | 34.587 | 7.2901 | 19.897 | 22.9689 | 0 | 22.3532 | 0 | 21.3156 | 0 | 3.2893 | 2.4632 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 214.9957 | 2.133%
CZ 4A | 0.34095 | 0.071824 | 0.18286 | 0.23054 | 0 | 0.51978 | 0 | 0.23723 | 0.11852 | 0.055319 | 0.024174 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.5658 | 19.36% | CZ 4A | 11.2757 | 2.3753 | 16.9868 | 23.2871 | 0 | 17.1899 | 0 | 7.8455 | 3.9195 | 1.8295 | 0.79946 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 120.7962 | 19.36% | CZ 4A | 3.3038 | 0.69596 | 0.21168 | 0 | 0 | 5.0366 | 0 | 2.2987 | 1.1484 | 0.53603 | 0.23424 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 19.7365 | 19.36% | CZ 4A | 0 | 0 | 0.16264 | 0.23287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.53439 | 19.36% | CZ 4A | 34.587 | 7.286 | 19.993 | 25.4528 | 0 | 52.7282 | 0 | 24.0651 | 12.0226 | 5.6117 | 2.4523 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 265.0304 | 19.36%
CZ 4B | 0.34095 | 0.071843 | 0.18172 | 0.17879 | 0 | 0.37465 | 0 | 0.32221 | 0.079347 | 0.042343 | 0.024141 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.4006 | 0.7475% | CZ 4B | 11.2757 | 2.3759 | 16.8724 | 18.0593 | 0 | 12.3904 | 0 | 10.6558 | 2.6241 | 1.4003 | 0.79837 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 111.7397 | 0.7475% | CZ 4B | 3.3038 | 0.69614 | 0.21161 | 0 | 0 | 3.6303 | 0 | 3.1221 | 0.76886 | 0.41029 | 0.23392 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 18.6482 | 0.7475% | CZ 4B | 0 | 0 | 0.1615 | 0.18059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.48097 | 0.7475% | CZ 4B | 34.587 | 7.2879 | 19.8674 | 19.7388 | 0 | 38.0061 | 0 | 32.6856 | 8.0492 | 4.2954 | 2.4489 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 247.798 | 0.7475%
CZ 4C | 0.34095 | 0.071789 | 0.18607 | 0.30295 | 0 | 0.23031 | 0 | 0.30844 | 0.074953 | 0.033157 | 0.024087 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.3574 | 2.475% | CZ 4C | 11.2757 | 2.3742 | 17.3107 | 30.6015 | 0 | 7.6167 | 0 | 10.2006 | 2.4788 | 1.0966 | 0.79659 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 119.0387 | 2.475% | CZ 4C | 3.3038 | 0.69562 | 0.21172 | 0 | 0 | 2.2317 | 0 | 2.9887 | 0.72628 | 0.32129 | 0.2334 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 16.9836 | 2.475% | CZ 4C | 0 | 0 | 0.16588 | 0.30601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.61077 | 2.475% | CZ 4C | 34.587 | 7.2825 | 20.3473 | 33.4474 | 0 | 23.3633 | 0 | 31.2892 | 7.6035 | 3.3636 | 2.4434 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 244.5588 | 2.475%
CZ 5A | 0.34095 | 0.071831 | 0.18813 | 0.36713 | 0 | 0.411 | 0 | 0.32027 | 0.11406 | 0.050512 | 0.02404 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.6726 | 18.57% | CZ 5A | 11.2757 | 2.3756 | 17.519 | 37.0841 | 0 | 13.5923 | 0 | 10.5917 | 3.7722 | 1.6705 | 0.79504 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 133.9634 | 18.57% | CZ 5A | 3.3038 | 0.69603 | 0.21172 | 0 | 0 | 3.9825 | 0 | 3.1033 | 1.1052 | 0.48945 | 0.23294 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 19.3961 | 18.57% | CZ 5A | 0 | 0 | 0.16796 | 0.37084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.67768 | 18.57% | CZ 5A | 34.587 | 7.2867 | 20.575 | 40.5329 | 0 | 41.693 | 0 | 32.4889 | 11.5707 | 5.1241 | 2.4387 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 277.1284 | 18.57%
CZ 5B | 0.34095 | 0.071768 | 0.1872 | 0.29456 | 0 | 0.31007 | 0 | 0.30283 | 0.11196 | 0.03916 | 0.023974 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.4671 | 4.034% | CZ 5B | 11.2757 | 2.3735 | 17.4245 | 29.7538 | 0 | 10.2543 | 0 | 10.015 | 3.7028 | 1.2951 | 0.79286 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 122.1748 | 4.034% | CZ 5B | 3.3038 | 0.69542 | 0.2117 | 0 | 0 | 3.0045 | 0 | 2.9344 | 1.0849 | 0.37945 | 0.23231 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 18.1175 | 4.034% | CZ 5B | 0 | 0 | 0.16702 | 0.29754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.60343 | 4.034% | CZ 5B | 34.587 | 7.2803 | 20.4715 | 32.5209 | 0 | 31.454 | 0 | 30.72 | 11.3578 | 3.9725 | 2.432 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 255.6275 | 4.034%
CZ 5C | 0.34095 | 0.071714 | 0.18822 | 0.3503 | 0 | 0.1523 | 0 | 0.33156 | 0.072063 | 0.026364 | 0.024026 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.3421 | 0% | CZ 5C | 11.2757 | 2.3717 | 17.527 | 35.3836 | 0 | 5.0367 | 0 | 10.9651 | 2.3832 | 0.87189 | 0.79457 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 121.8969 | 0% | CZ 5C | 3.3038 | 0.69489 | 0.21174 | 0 | 0 | 1.4757 | 0 | 3.2127 | 0.69828 | 0.25546 | 0.23281 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 16.3566 | 0% | CZ 5C | 0 | 0 | 0.16804 | 0.35384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.66075 | 0% | CZ 5C | 34.587 | 7.2748 | 20.5839 | 38.6742 | 0 | 15.4496 | 0 | 33.6343 | 7.3103 | 2.6744 | 2.4373 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 243.4575 | 0%
CZ 6A | 0.34095 | 0.071789 | 0.1928 | 0.41909 | 0 | 0.29622 | 0 | 0.33714 | 0.11264 | 0.041728 | 0.023955 | 0.22962 | 0.013436 | 0.31637 | 0 | 0.22522 | 2.6209 | 4.577% | CZ 6A | 11.2757 | 2.3742 | 17.9904 | 42.332 | 0 | 9.7964 | 0 | 11.1497 | 3.7251 | 1.38 | 0.79224 | 7.5938 | 0.44434 | 19.8034 | 0 | 7.4458 | 136.103 | 4.577% | CZ 6A | 3.3038 | 0.69562 | 0.21174 | 0 | 0 | 2.8703 | 0 | 3.2668 | 1.0914 | 0.40433 | 0.23212 | 2.225 | 0.13019 | 1.7334 | 0 | 2.1826 | 18.3473 | 4.577% | CZ 6A | 0 | 0 | 0.17268 | 0.42332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.73487 | 4.577% | CZ 6A | 34.587 | 7.2825 | 21.0903 | 46.2689 | 0 | 30.0492 | 0 | 34.2005 | 11.4264 | 4.233 | 2.4301 | 23.293 | 1.363 | 33.3255 | 0 | 22.85 | 272.3994 | 4.577%
CZ 6B | 0.34095 | 0.071768 | 0.19347 | 0.35874 | 0 | 0.21792 | 0 | 0.31085 | 0.11131 | 0.033793 | 0.023923 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.4474 | 1.165% | CZ 6B | 11.2757 | 2.3735 | 18.0586 | 36.2361 | 0 | 7.2069 | 0 | 10.2804 | 3.6813 | 1.1176 | 0.79115 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 126.3086 | 1.165% | CZ 6B | 3.3038 | 0.69542 | 0.2117 | 0 | 0 | 2.1116 | 0 | 3.0121 | 1.0786 | 0.32745 | 0.23181 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 17.2436 | 1.165% | CZ 6B | 0 | 0 | 0.17336 | 0.36236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.6746 | 1.165% | CZ 6B | 34.587 | 7.2803 | 21.1646 | 39.606 | 0 | 22.1065 | 0 | 31.534 | 11.2921 | 3.4281 | 2.4268 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 254.257 | 1.165%
CZ 7 | 0.34095 | 0.071739 | 0.20018 | 0.52963 | 0 | 0.22718 | 0 | 0.3531 | 0.11113 | 0.040512 | 0.023887 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 2.6829 | 0.7736% | CZ 7 | 11.2757 | 2.3725 | 18.7357 | 53.4975 | 0 | 7.5131 | 0 | 11.6776 | 3.6752 | 1.3398 | 0.78999 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 146.1645 | 0.7736% | CZ 7 | 3.3038 | 0.69514 | 0.21174 | 0 | 0 | 2.2013 | 0 | 3.4215 | 1.0768 | 0.39255 | 0.23146 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 17.8055 | 0.7736% | CZ 7 | 0 | 0 | 0.18013 | 0.53497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.85398 | 0.7736% | CZ 7 | 34.587 | 7.2775 | 21.905 | 58.4728 | 0 | 23.0456 | 0 | 35.8198 | 11.2733 | 4.1096 | 2.4232 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 279.7454 | 0.7736%
CZ 8 | 0.34095 | 0.071286 | 0.20929 | 0.905 | 0 | 0.14503 | 0 | 0.39369 | 0.1107 | 0.037279 | 0.02373 | 0.22962 | 0.013438 | 0.31637 | 0 | 0.22522 | 3.0216 | 0.07229% | CZ 8 | 11.2757 | 2.3575 | 19.655 | 91.4138 | 0 | 4.7962 | 0 | 13.0198 | 3.6609 | 1.2329 | 0.78479 | 7.5938 | 0.44442 | 19.8034 | 0 | 7.4458 | 183.4841 | 0.07229% | CZ 8 | 3.3038 | 0.69075 | 0.21179 | 0 | 0 | 1.4053 | 0 | 3.8148 | 1.0726 | 0.36123 | 0.22994 | 2.225 | 0.13021 | 1.7334 | 0 | 2.1826 | 17.3613 | 0.07229% | CZ 8 | 0 | 0 | 0.18932 | 0.91414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 1.2423 | 0.07229% | CZ 8 | 34.587 | 7.2315 | 22.9101 | 99.9153 | 0 | 14.7118 | 0 | 39.9368 | 11.2294 | 3.7817 | 2.4073 | 23.293 | 1.3632 | 33.3255 | 0 | 22.85 | 317.5427 | 0.07229%
Us Weighted | 0.34095 | 0.071853 | 0.17966 | 0.23295 | 0 | 0.57835 | 0 | 0.27035 | 0.10849 | 0.056928 | 0.024166 | 0.22962 | 0.013437 | 0.31637 | 0 | 0.22522 | 2.6483 | 100% | Us Weighted | 11.2757 | 2.3763 | 16.6634 | 23.5302 | 0 | 19.1268 | 0 | 8.9407 | 3.588 | 1.8827 | 0.79922 | 7.5938 | 0.44437 | 19.8034 | 0 | 7.4458 | 123.4703 | 100% | Us Weighted | 3.3038 | 0.69624 | 0.21168 | 0 | 0 | 5.6041 | 0 | 2.6196 | 1.0513 | 0.55162 | 0.23417 | 2.225 | 0.1302 | 1.7334 | 0 | 2.1826 | 20.5436 | 100% | Us Weighted | 0 | 0 | 0.15941 | 0.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13887 | 0 | 0 | 0.53358 | 100% | Us Weighted | 34.587 | 7.289 | 19.6395 | 25.7185 | 0 | 58.6693 | 0 | 27.4247 | 11.0059 | 5.7749 | 2.4515 | 23.293 | 1.3631 | 33.3255 | 0 | 22.85 | 273.3918 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 122120 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 122120 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.12583 | 0.016718 | 0.00056296 | 0.042107 | 0 | 0.44343 | 0 | 0.11235 | 0.060629 | 0.075894 | 0.0044225 | 0.006507 | 0.0061268 | 0 | 0 | 0.020385 | 0.91496 | 2.196% | CZ 1A | 4.1613 | 0.5529 | 0.020184 | 4.2532 | 0 | 14.6648 | 0 | 3.7157 | 2.0051 | 2.5099 | 0.14626 | 0.2152 | 0.20262 | 0 | 0 | 0.67416 | 33.1214 | 2.196% | CZ 1A | 1.2192 | 0.162 | 0.0052316 | 0 | 0 | 4.2968 | 0 | 1.0887 | 0.58749 | 0.7354 | 0.042854 | 0.063052 | 0.059367 | 0 | 0 | 0.19753 | 8.4576 | 2.196% | CZ 1A | 0 | 0 | 2.3284e-05 | 0.042532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042556 | 2.196% | CZ 1A | 12.7642 | 1.696 | 0.057315 | 4.6488 | 0 | 44.9828 | 0 | 11.3976 | 6.1504 | 7.6989 | 0.44864 | 0.66009 | 0.62152 | 0 | 0 | 2.0679 | 93.194 | 2.196%
CZ 1B | 0.12584 | 0.016716 | 0.00057064 | 0.063452 | 0 | 0.33272 | 0 | 0.1311 | 0.059289 | 0.059474 | 0.0042488 | 0.006507 | 0.0061291 | 0 | 0 | 0.020385 | 0.82644 | 0% | CZ 1B | 4.1618 | 0.55282 | 0.02096 | 6.4093 | 0 | 11.0035 | 0 | 4.3358 | 1.9608 | 1.9669 | 0.14052 | 0.2152 | 0.2027 | 0 | 0 | 0.67416 | 31.6444 | 0% | CZ 1B | 1.2194 | 0.16197 | 0.0052316 | 0 | 0 | 3.224 | 0 | 1.2704 | 0.5745 | 0.57629 | 0.041171 | 0.063052 | 0.05939 | 0 | 0 | 0.19753 | 7.3929 | 0% | CZ 1B | 0 | 0 | 3.1045e-05 | 0.064093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064124 | 0% | CZ 1B | 12.7658 | 1.6957 | 0.058163 | 7.0054 | 0 | 33.7519 | 0 | 13.2995 | 6.0144 | 6.0332 | 0.43101 | 0.66009 | 0.62175 | 0 | 0 | 2.0679 | 84.4049 | 0%
CZ 2A | 0.12572 | 0.016711 | 0.00057461 | 0.094386 | 0 | 0.39538 | 0 | 0.11067 | 0.073042 | 0.061892 | 0.004284 | 0.006507 | 0.0061291 | 0 | 0 | 0.020385 | 0.91568 | 12.54% | CZ 2A | 4.1578 | 0.55267 | 0.020882 | 9.5339 | 0 | 13.0757 | 0 | 3.6601 | 2.4156 | 2.0469 | 0.14168 | 0.2152 | 0.2027 | 0 | 0 | 0.67416 | 36.6972 | 12.54% | CZ 2A | 1.2182 | 0.16193 | 0.0052998 | 0 | 0 | 3.8311 | 0 | 1.0724 | 0.70777 | 0.59972 | 0.041512 | 0.063052 | 0.05939 | 0 | 0 | 0.19753 | 7.9579 | 12.54% | CZ 2A | 0 | 0 | 2.7941e-05 | 0.095339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095367 | 12.54% | CZ 2A | 12.7535 | 1.6952 | 0.058538 | 10.4206 | 0 | 40.1083 | 0 | 11.2268 | 7.4096 | 6.2785 | 0.43459 | 0.66009 | 0.62175 | 0 | 0 | 2.0679 | 93.7354 | 12.54%
CZ 2B | 0.12574 | 0.016707 | 0.00058686 | 0.10991 | 0 | 0.42364 | 0 | 0.15504 | 0.074439 | 0.055256 | 0.0042535 | 0.006507 | 0.0061268 | 0 | 0 | 0.020385 | 0.99858 | 2.523% | CZ 2B | 4.1583 | 0.55251 | 0.022279 | 11.1022 | 0 | 14.0102 | 0 | 5.1273 | 2.4618 | 1.8274 | 0.14067 | 0.2152 | 0.20262 | 0 | 0 | 0.67416 | 40.4947 | 2.523% | CZ 2B | 1.2184 | 0.16188 | 0.0052771 | 0 | 0 | 4.105 | 0 | 1.5023 | 0.7213 | 0.53542 | 0.041216 | 0.063052 | 0.059367 | 0 | 0 | 0.19753 | 8.6107 | 2.523% | CZ 2B | 0 | 0 | 4.2687e-05 | 0.11102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11107 | 2.523% | CZ 2B | 12.7551 | 1.6948 | 0.059912 | 12.1347 | 0 | 42.9749 | 0 | 15.7275 | 7.5513 | 5.6053 | 0.43149 | 0.66009 | 0.62152 | 0 | 0 | 2.0679 | 102.2845 | 2.523%
CZ 3A | 0.12563 | 0.0167 | 0.00057529 | 0.066223 | 0 | 0.2666 | 0 | 0.088892 | 0.07615 | 0.049509 | 0.0043357 | 0.006507 | 0.0061244 | 0 | 0 | 0.020385 | 0.72763 | 12.83% | CZ 3A | 4.1547 | 0.55228 | 0.02127 | 6.6892 | 0 | 8.8169 | 0 | 2.9398 | 2.5184 | 1.6373 | 0.14339 | 0.2152 | 0.20254 | 0 | 0 | 0.67416 | 28.5652 | 12.83% | CZ 3A | 1.2173 | 0.16182 | 0.0052543 | 0 | 0 | 2.5833 | 0 | 0.86135 | 0.73788 | 0.47974 | 0.042012 | 0.063052 | 0.059345 | 0 | 0 | 0.19753 | 6.4086 | 12.83% | CZ 3A | 0 | 0 | 3.3374e-05 | 0.066892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066925 | 12.83% | CZ 3A | 12.7442 | 1.694 | 0.058656 | 7.3113 | 0 | 27.045 | 0 | 9.0175 | 7.7249 | 5.0224 | 0.43983 | 0.66009 | 0.62128 | 0 | 0 | 2.0679 | 74.407 | 12.83%
CZ 3B | 0.12571 | 0.016707 | 0.00059519 | 0.089385 | 0 | 0.14984 | 0 | 0.10437 | 0.041859 | 0.032063 | 0.0043286 | 0.006507 | 0.0061291 | 0 | 0 | 0.020385 | 0.59787 | 16.01% | CZ 3B | 4.1574 | 0.55251 | 0.023599 | 9.0288 | 0 | 4.9553 | 0 | 3.4516 | 1.3843 | 1.0604 | 0.14315 | 0.2152 | 0.2027 | 0 | 0 | 0.67416 | 25.8491 | 16.01% | CZ 3B | 1.2181 | 0.16188 | 0.0052089 | 0 | 0 | 1.4519 | 0 | 1.0113 | 0.40561 | 0.31069 | 0.041944 | 0.063052 | 0.05939 | 0 | 0 | 0.19753 | 4.9266 | 16.01% | CZ 3B | 0 | 0 | 5.821e-05 | 0.090288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090346 | 16.01% | CZ 3B | 12.7523 | 1.6948 | 0.060894 | 9.8685 | 0 | 15.1998 | 0 | 10.5874 | 4.2463 | 3.2526 | 0.43911 | 0.66009 | 0.62175 | 0 | 0 | 2.0679 | 61.4514 | 16.01%
CZ 3C | 0.12565 | 0.0167 | 0.00060223 | 0.12988 | 0 | 0.10407 | 0 | 0.067242 | 0 | 0.022106 | 0.0042606 | 0.006507 | 0.0061291 | 0 | 0 | 0.020385 | 0.50354 | 2.133% | CZ 3C | 4.1554 | 0.55228 | 0.023832 | 13.1196 | 0 | 3.4418 | 0 | 2.2238 | 0 | 0.73106 | 0.1409 | 0.2152 | 0.2027 | 0 | 0 | 0.67416 | 25.4807 | 2.133% | CZ 3C | 1.2175 | 0.16182 | 0.0052771 | 0 | 0 | 1.0084 | 0 | 0.65156 | 0 | 0.2142 | 0.041284 | 0.063052 | 0.05939 | 0 | 0 | 0.19753 | 3.6201 | 2.133% | CZ 3C | 0 | 0 | 5.821e-05 | 0.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13125 | 2.133% | CZ 3C | 12.7461 | 1.694 | 0.061608 | 14.3398 | 0 | 10.5574 | 0 | 6.8212 | 0 | 2.2425 | 0.43221 | 0.66009 | 0.62175 | 0 | 0 | 2.0679 | 52.2446 | 2.133%
CZ 4A | 0.1263 | 0.01669 | 0.00059685 | 0.13491 | 0 | 0.20145 | 0 | 0.085754 | 0.072364 | 0.038124 | 0.0042465 | 0.006507 | 0.0061268 | 0 | 0 | 0.020385 | 0.71346 | 19.36% | CZ 4A | 4.1769 | 0.55197 | 0.023288 | 13.6275 | 0 | 6.6622 | 0 | 2.836 | 2.3932 | 1.2608 | 0.14044 | 0.2152 | 0.20262 | 0 | 0 | 0.67416 | 32.7643 | 19.36% | CZ 4A | 1.2238 | 0.16172 | 0.0052771 | 0 | 0 | 1.952 | 0 | 0.83094 | 0.70119 | 0.36942 | 0.041148 | 0.063052 | 0.059367 | 0 | 0 | 0.19753 | 5.6055 | 19.36% | CZ 4A | 0 | 0 | 5.2777e-05 | 0.13628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13633 | 19.36% | CZ 4A | 12.8123 | 1.6931 | 0.061014 | 14.8949 | 0 | 20.4355 | 0 | 8.6991 | 7.3408 | 3.8675 | 0.43078 | 0.66009 | 0.62152 | 0 | 0 | 2.0679 | 73.5844 | 19.36%
CZ 4B | 0.1263 | 0.016692 | 0.00060518 | 0.11984 | 0 | 0.10216 | 0 | 0.14072 | 0.040028 | 0.028777 | 0.004284 | 0.006507 | 0.0061315 | 0 | 0 | 0.020385 | 0.61242 | 0.7475% | CZ 4B | 4.1769 | 0.55204 | 0.024608 | 12.1046 | 0 | 3.3786 | 0 | 4.6537 | 1.3238 | 0.9517 | 0.14168 | 0.2152 | 0.20278 | 0 | 0 | 0.67416 | 28.3997 | 0.7475% | CZ 4B | 1.2238 | 0.16175 | 0.0052089 | 0 | 0 | 0.98991 | 0 | 1.3635 | 0.38787 | 0.27884 | 0.041512 | 0.063052 | 0.059413 | 0 | 0 | 0.19753 | 4.7724 | 0.7475% | CZ 4B | 0 | 0 | 6.83e-05 | 0.12105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12111 | 0.7475% | CZ 4B | 12.8123 | 1.6933 | 0.061997 | 13.2303 | 0 | 10.3634 | 0 | 14.2746 | 4.0606 | 2.9192 | 0.43459 | 0.66009 | 0.62199 | 0 | 0 | 2.0679 | 63.2003 | 0.7475%
CZ 4C | 0.12624 | 0.016681 | 0.00063074 | 0.20656 | 0 | 0.067286 | 0 | 0.15443 | 0.037531 | 0.020533 | 0.0041432 | 0.006507 | 0.0061338 | 0 | 0 | 0.020385 | 0.66706 | 2.475% | CZ 4C | 4.1751 | 0.55166 | 0.026393 | 20.8649 | 0 | 2.2253 | 0 | 5.1071 | 1.2412 | 0.67905 | 0.13702 | 0.2152 | 0.20285 | 0 | 0 | 0.67416 | 36.0998 | 2.475% | CZ 4C | 1.2233 | 0.16163 | 0.0053226 | 0 | 0 | 0.65199 | 0 | 1.4964 | 0.36366 | 0.19896 | 0.040147 | 0.063052 | 0.059436 | 0 | 0 | 0.19753 | 4.4614 | 2.475% | CZ 4C | 0 | 0 | 8.227e-05 | 0.20865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20873 | 2.475% | CZ 4C | 12.8066 | 1.6921 | 0.064714 | 22.8053 | 0 | 6.8257 | 0 | 15.6655 | 3.8072 | 2.0829 | 0.4203 | 0.66009 | 0.62223 | 0 | 0 | 2.0679 | 69.5206 | 2.475%
CZ 5A | 0.12628 | 0.016692 | 0.00062536 | 0.22453 | 0 | 0.15134 | 0 | 0.16441 | 0.071847 | 0.033798 | 0.0041221 | 0.006507 | 0.0061268 | 0 | 0 | 0.020385 | 0.82666 | 18.57% | CZ 5A | 4.1762 | 0.55204 | 0.02585 | 22.6795 | 0 | 5.005 | 0 | 5.4372 | 2.3761 | 1.1178 | 0.13632 | 0.2152 | 0.20262 | 0 | 0 | 0.67416 | 42.5979 | 18.57% | CZ 5A | 1.2236 | 0.16175 | 0.0053226 | 0 | 0 | 1.4664 | 0 | 1.5931 | 0.69619 | 0.3275 | 0.039942 | 0.063052 | 0.059367 | 0 | 0 | 0.19753 | 5.8338 | 18.57% | CZ 5A | 0 | 0 | 7.6838e-05 | 0.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22687 | 18.57% | CZ 5A | 12.8099 | 1.6933 | 0.06412 | 24.7887 | 0 | 15.3522 | 0 | 16.6781 | 7.2884 | 3.4286 | 0.41816 | 0.66009 | 0.62152 | 0 | 0 | 2.0679 | 85.871 | 18.57%
CZ 5B | 0.12632 | 0.016676 | 0.00062302 | 0.19391 | 0 | 0.10947 | 0 | 0.13898 | 0.070599 | 0.025545 | 0.0041291 | 0.006507 | 0.0061315 | 0 | 0 | 0.020385 | 0.71927 | 4.034% | CZ 5B | 4.1777 | 0.5515 | 0.025772 | 19.5866 | 0 | 3.6202 | 0 | 4.5961 | 2.3348 | 0.8448 | 0.13656 | 0.2152 | 0.20278 | 0 | 0 | 0.67416 | 36.9663 | 4.034% | CZ 5B | 1.2241 | 0.16159 | 0.0052998 | 0 | 0 | 1.0607 | 0 | 1.3467 | 0.68409 | 0.24752 | 0.040011 | 0.063052 | 0.059413 | 0 | 0 | 0.19753 | 5.0899 | 4.034% | CZ 5B | 0 | 0 | 7.6837e-05 | 0.19587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19594 | 4.034% | CZ 5B | 12.8147 | 1.6917 | 0.063882 | 21.4082 | 0 | 11.1047 | 0 | 14.0982 | 7.1617 | 2.5913 | 0.41887 | 0.66009 | 0.62199 | 0 | 0 | 2.0679 | 74.7032 | 4.034%
CZ 5C | 0.12584 | 0.016662 | 0.00064308 | 0.23486 | 0 | 0.047481 | 0 | 0.17769 | 0.03493 | 0.015263 | 0.0040892 | 0.006507 | 0.0061315 | 0 | 0 | 0.020385 | 0.69049 | 0% | CZ 5C | 4.1617 | 0.55103 | 0.02748 | 23.7234 | 0 | 1.5703 | 0 | 5.8765 | 1.1552 | 0.50477 | 0.13524 | 0.2152 | 0.20278 | 0 | 0 | 0.67416 | 38.7977 | 0% | CZ 5C | 1.2194 | 0.16145 | 0.0053453 | 0 | 0 | 0.46009 | 0 | 1.7218 | 0.33846 | 0.1479 | 0.039624 | 0.063052 | 0.059413 | 0 | 0 | 0.19753 | 4.414 | 0% | CZ 5C | 0 | 0 | 9.236e-05 | 0.23723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23733 | 0% | CZ 5C | 12.7656 | 1.6902 | 0.066055 | 25.9296 | 0 | 4.8166 | 0 | 18.0256 | 3.5434 | 1.5483 | 0.41482 | 0.66009 | 0.62199 | 0 | 0 | 2.0679 | 72.1503 | 0%
CZ 6A | 0.12622 | 0.016681 | 0.00063616 | 0.25192 | 0 | 0.11279 | 0 | 0.18062 | 0.071383 | 0.027028 | 0.004061 | 0.006507 | 0.0061268 | 0 | 0 | 0.020385 | 0.82435 | 4.577% | CZ 6A | 4.1741 | 0.55166 | 0.026781 | 25.4462 | 0 | 3.7302 | 0 | 5.9733 | 2.3607 | 0.89386 | 0.1343 | 0.2152 | 0.20262 | 0 | 0 | 0.67416 | 44.383 | 4.577% | CZ 6A | 1.223 | 0.16163 | 0.0053453 | 0 | 0 | 1.0929 | 0 | 1.7502 | 0.69169 | 0.2619 | 0.039351 | 0.063052 | 0.059367 | 0 | 0 | 0.19753 | 5.546 | 4.577% | CZ 6A | 0 | 0 | 8.5375e-05 | 0.25446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25455 | 4.577% | CZ 6A | 12.8037 | 1.6921 | 0.065292 | 27.8127 | 0 | 11.4419 | 0 | 18.3223 | 7.2413 | 2.7418 | 0.41196 | 0.66009 | 0.62152 | 0 | 0 | 2.0679 | 85.8826 | 4.577%
CZ 6B | 0.12638 | 0.016676 | 0.00063454 | 0.21817 | 0 | 0.076096 | 0 | 0.13966 | 0.068671 | 0.021127 | 0.0040869 | 0.006507 | 0.0061315 | 0 | 0 | 0.020385 | 0.70452 | 1.165% | CZ 6B | 4.1796 | 0.5515 | 0.026936 | 22.037 | 0 | 2.5166 | 0 | 4.6187 | 2.2711 | 0.69869 | 0.13516 | 0.2152 | 0.20278 | 0 | 0 | 0.67416 | 38.1274 | 1.165% | CZ 6B | 1.2246 | 0.16159 | 0.0052998 | 0 | 0 | 0.73736 | 0 | 1.3533 | 0.66541 | 0.20471 | 0.039601 | 0.063052 | 0.059413 | 0 | 0 | 0.19753 | 4.7119 | 1.165% | CZ 6B | 0 | 0 | 8.8479e-05 | 0.22037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22046 | 1.165% | CZ 6B | 12.8204 | 1.6917 | 0.065155 | 24.0864 | 0 | 7.7194 | 0 | 14.1675 | 6.9662 | 2.1432 | 0.41458 | 0.66009 | 0.62199 | 0 | 0 | 2.0679 | 73.4245 | 1.165%
CZ 7 | 0.12677 | 0.016669 | 0.00064308 | 0.32994 | 0 | 0.082643 | 0 | 0.18644 | 0.069221 | 0.02554 | 0.0040141 | 0.006507 | 0.0061315 | 0 | 0 | 0.020385 | 0.87491 | 0.7736% | CZ 7 | 4.1926 | 0.55127 | 0.02748 | 33.3277 | 0 | 2.7331 | 0 | 6.1658 | 2.2892 | 0.84464 | 0.13275 | 0.2152 | 0.20278 | 0 | 0 | 0.67416 | 51.3567 | 0.7736% | CZ 7 | 1.2284 | 0.16152 | 0.0053453 | 0 | 0 | 0.8008 | 0 | 1.8066 | 0.67074 | 0.24748 | 0.038896 | 0.063052 | 0.059413 | 0 | 0 | 0.19753 | 5.2798 | 0.7736% | CZ 7 | 0 | 0 | 9.236e-05 | 0.33328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33337 | 0.7736% | CZ 7 | 12.8604 | 1.691 | 0.066055 | 36.4271 | 0 | 8.3836 | 0 | 18.9129 | 7.0219 | 2.5908 | 0.4072 | 0.66009 | 0.62199 | 0 | 0 | 2.0679 | 91.711 | 0.7736%
CZ 8 | 0.12653 | 0.016563 | 0.00065388 | 0.50704 | 0 | 0.046908 | 0 | 0.21453 | 0.065843 | 0.021636 | 0.0039343 | 0.006507 | 0.0061338 | 0 | 0 | 0.020385 | 1.0367 | 0.07229% | CZ 8 | 4.1845 | 0.54777 | 0.028411 | 51.2164 | 0 | 1.5513 | 0 | 7.0947 | 2.1775 | 0.71554 | 0.13011 | 0.2152 | 0.20285 | 0 | 0 | 0.67416 | 68.7385 | 0.07229% | CZ 8 | 1.2261 | 0.1605 | 0.0053681 | 0 | 0 | 0.45454 | 0 | 2.0787 | 0.63801 | 0.20965 | 0.038123 | 0.063052 | 0.059436 | 0 | 0 | 0.19753 | 5.131 | 0.07229% | CZ 8 | 0 | 0 | 0.0001009 | 0.51216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51227 | 0.07229% | CZ 8 | 12.8356 | 1.6802 | 0.067227 | 55.9796 | 0 | 4.7585 | 0 | 21.7621 | 6.6793 | 2.1948 | 0.39911 | 0.66009 | 0.62223 | 0 | 0 | 2.0679 | 109.7067 | 0.07229%
Us Weighted | 0.126 | 0.016697 | 0.00060004 | 0.13973 | 0 | 0.21108 | 0 | 0.1189 | 0.064913 | 0.039884 | 0.0042377 | 0.006507 | 0.0061277 | 0 | 0 | 0.020385 | 0.75507 | 100% | Us Weighted | 4.1671 | 0.55218 | 0.023596 | 14.1145 | 0 | 6.9806 | 0 | 3.9322 | 2.1468 | 1.319 | 0.14015 | 0.2152 | 0.20265 | 0 | 0 | 0.67416 | 34.4682 | 100% | Us Weighted | 1.221 | 0.16179 | 0.0052791 | 0 | 0 | 2.0453 | 0 | 1.1521 | 0.629 | 0.38647 | 0.041062 | 0.063052 | 0.059376 | 0 | 0 | 0.19753 | 5.9619 | 100% | Us Weighted | 0 | 0 | 5.579e-05 | 0.14115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1412 | 100% | Us Weighted | 12.7823 | 1.6938 | 0.061364 | 15.4272 | 0 | 21.4122 | 0 | 12.0617 | 6.585 | 4.0459 | 0.42988 | 0.66009 | 0.62161 | 0 | 0 | 2.0679 | 77.8488 | 100%
Building Type: | Large Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 122120 | [17 empty] | Prototype Floor Area: | 122120 | [17 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook.Dry | Data.Ctr | Equip | Total | Weight
CZ 1A | 36.9% | 23.24% | 0.3489% | 72.88% | 0% | 33.97% | 0% | 44.49% | 47.44% | 75.9% | 18.08% | 2.834% | 45.6% | 0% | 0% | 9.051% | 28.35% | 2.196% | CZ 1A | 36.9% | 23.24% | 0.1362% | 72.88% | 0% | 33.97% | 0% | 44.49% | 47.44% | 75.9% | 18.08% | 2.834% | 45.6% | 0% | 0% | 9.054% | 25.58% | 2.196% | CZ 1A | 36.9% | 23.24% | 2.472% | 0% | 0% | 33.97% | 0% | 44.49% | 47.44% | 75.9% | 18.08% | 2.834% | 45.6% | 0% | 0% | 9.05% | 30.18% | 2.196% | CZ 1A | 0% | 0% | 0.01652% | 72.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.58% | 2.196% | CZ 1A | 36.9% | 23.24% | 0.3253% | 72.88% | 0% | 33.97% | 0% | 44.49% | 47.44% | 75.9% | 18.08% | 2.834% | 45.6% | 0% | 0% | 9.05% | 28.21% | 2.196%
CZ 1B | 36.91% | 23.24% | 0.3613% | 67.36% | 0% | 30.05% | 0% | 43.75% | 47.3% | 74.67% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.051% | 26.78% | 0% | CZ 1B | 36.91% | 23.24% | 0.1448% | 67.36% | 0% | 30.05% | 0% | 43.75% | 47.3% | 74.67% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.054% | 24.91% | 0% | CZ 1B | 36.91% | 23.24% | 2.472% | 0% | 0% | 30.05% | 0% | 43.75% | 47.3% | 74.67% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.05% | 28.07% | 0% | CZ 1B | 0% | 0% | 0.02258% | 67.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.26% | 0% | CZ 1B | 36.91% | 23.24% | 0.3373% | 67.36% | 0% | 30.05% | 0% | 43.75% | 47.3% | 74.67% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.05% | 26.68% | 0%
CZ 2A | 36.87% | 23.24% | 0.3396% | 61.56% | 0% | 39.3% | 0% | 44.42% | 59.36% | 74.71% | 17.64% | 2.834% | 45.62% | 0% | 0% | 9.051% | 30.47% | 12.54% | CZ 2A | 36.87% | 23.24% | 0.1338% | 61.56% | 0% | 39.3% | 0% | 44.42% | 59.36% | 74.71% | 17.64% | 2.834% | 45.62% | 0% | 0% | 9.054% | 28.41% | 12.54% | CZ 2A | 36.87% | 23.24% | 2.503% | 0% | 0% | 39.3% | 0% | 44.42% | 59.36% | 74.71% | 17.64% | 2.834% | 45.62% | 0% | 0% | 9.05% | 31.99% | 12.54% | CZ 2A | 0% | 0% | 0.01877% | 61.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.55% | 12.54% | CZ 2A | 36.87% | 23.24% | 0.3167% | 61.56% | 0% | 39.3% | 0% | 44.42% | 59.36% | 74.71% | 17.64% | 2.834% | 45.62% | 0% | 0% | 9.05% | 30.35% | 12.54%
CZ 2B | 36.88% | 23.24% | 0.3564% | 78.95% | 0% | 41.28% | 0% | 49.25% | 61.84% | 74.26% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.051% | 32.62% | 2.523% | CZ 2B | 36.88% | 23.24% | 0.1471% | 78.95% | 0% | 41.28% | 0% | 49.25% | 61.84% | 74.26% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.054% | 31.21% | 2.523% | CZ 2B | 36.88% | 23.24% | 2.493% | 0% | 0% | 41.28% | 0% | 49.25% | 61.84% | 74.26% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.05% | 33.64% | 2.523% | CZ 2B | 0% | 0% | 0.02959% | 78.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.21% | 2.523% | CZ 2B | 36.88% | 23.24% | 0.3332% | 78.95% | 0% | 41.28% | 0% | 49.25% | 61.84% | 74.26% | 17.61% | 2.834% | 45.61% | 0% | 0% | 9.05% | 32.54% | 2.523%
CZ 3A | 36.85% | 23.24% | 0.3281% | 39.55% | 0% | 36.49% | 0% | 38.96% | 63.13% | 71.61% | 17.85% | 2.834% | 45.58% | 0% | 0% | 9.051% | 26.82% | 12.83% | CZ 3A | 36.85% | 23.24% | 0.1311% | 39.55% | 0% | 36.49% | 0% | 38.96% | 63.13% | 71.61% | 17.85% | 2.834% | 45.58% | 0% | 0% | 9.054% | 23.63% | 12.83% | CZ 3A | 36.85% | 23.24% | 2.483% | 0% | 0% | 36.49% | 0% | 38.96% | 63.13% | 71.61% | 17.85% | 2.834% | 45.58% | 0% | 0% | 9.05% | 29.33% | 12.83% | CZ 3A | 0% | 0% | 0.02153% | 39.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.45% | 12.83% | CZ 3A | 36.85% | 23.24% | 0.3061% | 39.55% | 0% | 36.49% | 0% | 38.96% | 63.13% | 71.61% | 17.85% | 2.834% | 45.58% | 0% | 0% | 9.05% | 26.64% | 12.83%
CZ 3B | 36.87% | 23.24% | 0.3434% | 66.86% | 0% | 28.79% | 0% | 39.64% | 50.51% | 68.84% | 17.88% | 2.834% | 45.61% | 0% | 0% | 9.051% | 24.48% | 16.01% | CZ 3B | 36.87% | 23.24% | 0.1473% | 66.86% | 0% | 28.79% | 0% | 39.64% | 50.51% | 68.84% | 17.88% | 2.834% | 45.61% | 0% | 0% | 9.054% | 23.61% | 16.01% | CZ 3B | 36.87% | 23.24% | 2.462% | 0% | 0% | 28.79% | 0% | 39.64% | 50.51% | 68.84% | 17.88% | 2.834% | 45.61% | 0% | 0% | 9.05% | 25.18% | 16.01% | CZ 3B | 0% | 0% | 0.03804% | 66.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.16% | 16.01% | CZ 3B | 36.87% | 23.24% | 0.3215% | 66.86% | 0% | 28.79% | 0% | 39.64% | 50.51% | 68.84% | 17.88% | 2.834% | 45.61% | 0% | 0% | 9.05% | 24.43% | 16.01%
CZ 3C | 36.85% | 23.24% | 0.3309% | 62.43% | 0% | 47.23% | 0% | 32% | 0% | 68.17% | 17.55% | 2.834% | 45.62% | 0% | 0% | 9.051% | 24.27% | 2.133% | CZ 3C | 36.85% | 23.24% | 0.141% | 62.43% | 0% | 47.23% | 0% | 32% | 0% | 68.17% | 17.55% | 2.834% | 45.62% | 0% | 0% | 9.054% | 24.75% | 2.133% | CZ 3C | 36.85% | 23.24% | 2.493% | 0% | 0% | 47.23% | 0% | 32% | 0% | 68.17% | 17.55% | 2.834% | 45.62% | 0% | 0% | 9.05% | 23.81% | 2.133% | CZ 3C | 0% | 0% | 0.03598% | 62.43% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.7% | 2.133% | CZ 3C | 36.85% | 23.24% | 0.3096% | 62.43% | 0% | 47.23% | 0% | 32% | 0% | 68.17% | 17.55% | 2.834% | 45.62% | 0% | 0% | 9.05% | 24.3% | 2.133%
CZ 4A | 37.04% | 23.24% | 0.3264% | 58.52% | 0% | 38.76% | 0% | 36.15% | 61.06% | 68.92% | 17.57% | 2.834% | 45.59% | 0% | 0% | 9.051% | 27.81% | 19.36% | CZ 4A | 37.04% | 23.24% | 0.1371% | 58.52% | 0% | 38.76% | 0% | 36.15% | 61.06% | 68.92% | 17.57% | 2.834% | 45.59% | 0% | 0% | 9.054% | 27.12% | 19.36% | CZ 4A | 37.04% | 23.24% | 2.493% | 0% | 0% | 38.76% | 0% | 36.15% | 61.06% | 68.92% | 17.57% | 2.834% | 45.59% | 0% | 0% | 9.05% | 28.4% | 19.36% | CZ 4A | 0% | 0% | 0.03245% | 58.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.51% | 19.36% | CZ 4A | 37.04% | 23.24% | 0.3052% | 58.52% | 0% | 38.76% | 0% | 36.15% | 61.06% | 68.92% | 17.57% | 2.834% | 45.59% | 0% | 0% | 9.05% | 27.76% | 19.36%
CZ 4B | 37.04% | 23.23% | 0.333% | 67.03% | 0% | 27.27% | 0% | 43.67% | 50.45% | 67.96% | 17.75% | 2.834% | 45.63% | 0% | 0% | 9.051% | 25.51% | 0.7475% | CZ 4B | 37.04% | 23.23% | 0.1458% | 67.03% | 0% | 27.27% | 0% | 43.67% | 50.45% | 67.96% | 17.75% | 2.834% | 45.63% | 0% | 0% | 9.054% | 25.42% | 0.7475% | CZ 4B | 37.04% | 23.23% | 2.462% | 0% | 0% | 27.27% | 0% | 43.67% | 50.45% | 67.96% | 17.75% | 2.834% | 45.63% | 0% | 0% | 9.05% | 25.59% | 0.7475% | CZ 4B | 0% | 0% | 0.04229% | 67.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.18% | 0.7475% | CZ 4B | 37.04% | 23.23% | 0.3121% | 67.03% | 0% | 27.27% | 0% | 43.67% | 50.45% | 67.96% | 17.75% | 2.834% | 45.63% | 0% | 0% | 9.05% | 25.5% | 0.7475%
CZ 4C | 37.03% | 23.24% | 0.339% | 68.18% | 0% | 29.22% | 0% | 50.07% | 50.07% | 61.93% | 17.2% | 2.834% | 45.64% | 0% | 0% | 9.051% | 28.3% | 2.475% | CZ 4C | 37.03% | 23.24% | 0.1525% | 68.18% | 0% | 29.22% | 0% | 50.07% | 50.07% | 61.93% | 17.2% | 2.834% | 45.64% | 0% | 0% | 9.054% | 30.33% | 2.475% | CZ 4C | 37.03% | 23.24% | 2.514% | 0% | 0% | 29.22% | 0% | 50.07% | 50.07% | 61.93% | 17.2% | 2.834% | 45.64% | 0% | 0% | 9.05% | 26.27% | 2.475% | CZ 4C | 0% | 0% | 0.0496% | 68.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.18% | 2.475% | CZ 4C | 37.03% | 23.24% | 0.318% | 68.18% | 0% | 29.22% | 0% | 50.07% | 50.07% | 61.93% | 17.2% | 2.834% | 45.64% | 0% | 0% | 9.05% | 28.43% | 2.475%
CZ 5A | 37.04% | 23.24% | 0.3324% | 61.16% | 0% | 36.82% | 0% | 51.33% | 62.99% | 66.91% | 17.15% | 2.834% | 45.6% | 0% | 0% | 9.051% | 30.93% | 18.57% | CZ 5A | 37.04% | 23.24% | 0.1476% | 61.16% | 0% | 36.82% | 0% | 51.33% | 62.99% | 66.91% | 17.15% | 2.834% | 45.6% | 0% | 0% | 9.054% | 31.8% | 18.57% | CZ 5A | 37.04% | 23.24% | 2.514% | 0% | 0% | 36.82% | 0% | 51.33% | 62.99% | 66.91% | 17.15% | 2.834% | 45.6% | 0% | 0% | 9.05% | 30.08% | 18.57% | CZ 5A | 0% | 0% | 0.04575% | 61.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.48% | 18.57% | CZ 5A | 37.04% | 23.24% | 0.3116% | 61.16% | 0% | 36.82% | 0% | 51.33% | 62.99% | 66.91% | 17.15% | 2.834% | 45.6% | 0% | 0% | 9.05% | 30.99% | 18.57%
CZ 5B | 37.05% | 23.24% | 0.3328% | 65.83% | 0% | 35.3% | 0% | 45.89% | 63.06% | 65.23% | 17.22% | 2.834% | 45.64% | 0% | 0% | 9.051% | 29.15% | 4.034% | CZ 5B | 37.05% | 23.24% | 0.1479% | 65.83% | 0% | 35.3% | 0% | 45.89% | 63.06% | 65.23% | 17.22% | 2.834% | 45.64% | 0% | 0% | 9.054% | 30.26% | 4.034% | CZ 5B | 37.05% | 23.24% | 2.503% | 0% | 0% | 35.3% | 0% | 45.89% | 63.06% | 65.23% | 17.22% | 2.834% | 45.64% | 0% | 0% | 9.05% | 28.09% | 4.034% | CZ 5B | 0% | 0% | 0.046% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.47% | 4.034% | CZ 5B | 37.05% | 23.24% | 0.3121% | 65.83% | 0% | 35.3% | 0% | 45.89% | 63.06% | 65.23% | 17.22% | 2.834% | 45.64% | 0% | 0% | 9.05% | 29.22% | 4.034%
CZ 5C | 36.91% | 23.23% | 0.3417% | 67.05% | 0% | 31.18% | 0% | 53.59% | 48.47% | 57.89% | 17.02% | 2.834% | 45.63% | 0% | 0% | 9.051% | 29.48% | 0% | CZ 5C | 36.91% | 23.23% | 0.1568% | 67.05% | 0% | 31.18% | 0% | 53.59% | 48.47% | 57.89% | 17.02% | 2.834% | 45.63% | 0% | 0% | 9.054% | 31.83% | 0% | CZ 5C | 36.91% | 23.23% | 2.524% | 0% | 0% | 31.18% | 0% | 53.59% | 48.47% | 57.89% | 17.02% | 2.834% | 45.63% | 0% | 0% | 9.05% | 26.99% | 0% | CZ 5C | 0% | 0% | 0.05496% | 67.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.92% | 0% | CZ 5C | 36.91% | 23.23% | 0.3209% | 67.05% | 0% | 31.18% | 0% | 53.59% | 48.47% | 57.89% | 17.02% | 2.834% | 45.63% | 0% | 0% | 9.05% | 29.64% | 0%
CZ 6A | 37.02% | 23.24% | 0.33% | 60.11% | 0% | 38.08% | 0% | 53.57% | 63.37% | 64.77% | 16.95% | 2.834% | 45.6% | 0% | 0% | 9.051% | 31.45% | 4.577% | CZ 6A | 37.02% | 23.24% | 0.1489% | 60.11% | 0% | 38.08% | 0% | 53.57% | 63.37% | 64.77% | 16.95% | 2.834% | 45.6% | 0% | 0% | 9.054% | 32.61% | 4.577% | CZ 6A | 37.02% | 23.24% | 2.524% | 0% | 0% | 38.08% | 0% | 53.57% | 63.37% | 64.77% | 16.95% | 2.834% | 45.6% | 0% | 0% | 9.05% | 30.23% | 4.577% | CZ 6A | 0% | 0% | 0.04944% | 60.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.64% | 4.577% | CZ 6A | 37.02% | 23.24% | 0.3096% | 60.11% | 0% | 38.08% | 0% | 53.57% | 63.37% | 64.77% | 16.95% | 2.834% | 45.6% | 0% | 0% | 9.05% | 31.53% | 4.577%
CZ 6B | 37.07% | 23.24% | 0.328% | 60.82% | 0% | 34.92% | 0% | 44.93% | 61.69% | 62.52% | 17.08% | 2.834% | 45.63% | 0% | 0% | 9.051% | 28.79% | 1.165% | CZ 6B | 37.07% | 23.24% | 0.1492% | 60.82% | 0% | 34.92% | 0% | 44.93% | 61.69% | 62.52% | 17.08% | 2.834% | 45.63% | 0% | 0% | 9.054% | 30.19% | 1.165% | CZ 6B | 37.07% | 23.24% | 2.503% | 0% | 0% | 34.92% | 0% | 44.93% | 61.69% | 62.52% | 17.08% | 2.834% | 45.63% | 0% | 0% | 9.05% | 27.33% | 1.165% | CZ 6B | 0% | 0% | 0.05104% | 60.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.68% | 1.165% | CZ 6B | 37.07% | 23.24% | 0.3078% | 60.82% | 0% | 34.92% | 0% | 44.93% | 61.69% | 62.52% | 17.08% | 2.834% | 45.63% | 0% | 0% | 9.05% | 28.88% | 1.165%
CZ 7 | 37.18% | 23.24% | 0.3212% | 62.3% | 0% | 36.38% | 0% | 52.8% | 62.29% | 63.04% | 16.8% | 2.834% | 45.63% | 0% | 0% | 9.051% | 32.61% | 0.7736% | CZ 7 | 37.18% | 23.24% | 0.1467% | 62.3% | 0% | 36.38% | 0% | 52.8% | 62.29% | 63.04% | 16.8% | 2.834% | 45.63% | 0% | 0% | 9.054% | 35.14% | 0.7736% | CZ 7 | 37.18% | 23.24% | 2.524% | 0% | 0% | 36.38% | 0% | 52.8% | 62.29% | 63.04% | 16.8% | 2.834% | 45.63% | 0% | 0% | 9.05% | 29.65% | 0.7736% | CZ 7 | 0% | 0% | 0.05127% | 62.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.04% | 0.7736% | CZ 7 | 37.18% | 23.24% | 0.3016% | 62.3% | 0% | 36.38% | 0% | 52.8% | 62.29% | 63.04% | 16.8% | 2.834% | 45.63% | 0% | 0% | 9.05% | 32.78% | 0.7736%
CZ 8 | 37.11% | 23.23% | 0.3124% | 56.03% | 0% | 32.34% | 0% | 54.49% | 59.48% | 58.04% | 16.58% | 2.834% | 45.64% | 0% | 0% | 9.051% | 34.31% | 0.07229% | CZ 8 | 37.11% | 23.23% | 0.1445% | 56.03% | 0% | 32.34% | 0% | 54.49% | 59.48% | 58.04% | 16.58% | 2.834% | 45.64% | 0% | 0% | 9.054% | 37.46% | 0.07229% | CZ 8 | 37.11% | 23.23% | 2.535% | 0% | 0% | 32.34% | 0% | 54.49% | 59.48% | 58.04% | 16.58% | 2.834% | 45.64% | 0% | 0% | 9.05% | 29.55% | 0.07229% | CZ 8 | 0% | 0% | 0.05329% | 56.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.23% | 0.07229% | CZ 8 | 37.11% | 23.23% | 0.2934% | 56.03% | 0% | 32.34% | 0% | 54.49% | 59.48% | 58.04% | 16.58% | 2.834% | 45.64% | 0% | 0% | 9.05% | 34.55% | 0.07229%
Us Weighted | 36.96% | 23.24% | 0.334% | 59.98% | 0% | 36.5% | 0% | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% | 0% | 9.051% | 28.51% | 100% | Us Weighted | 36.96% | 23.24% | 0.1416% | 59.98% | 0% | 36.5% | 0% | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% | 0% | 9.054% | 27.92% | 100% | Us Weighted | 36.96% | 23.24% | 2.494% | 0% | 0% | 36.5% | 0% | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% | 0% | 9.05% | 29.02% | 100% | Us Weighted | 0% | 0% | 0.035% | 59.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.46% | 100% | Us Weighted | 36.96% | 23.24% | 0.3125% | 59.98% | 0% | 36.5% | 0% | 43.98% | 59.83% | 70.06% | 17.54% | 2.834% | 45.6% | 0% | 0% | 9.05% | 28.48% | 100%

## SmHotel
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Hotel |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Small Hotel | [14 empty] | Prototype Floor Area: | 43202 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.21352 | 0.043656 | 0.12657 | 0.11578 | 0 | 0.19011 | 0 | 0.18497 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3364 |  | STD2013 | 7.0613 | 1.4437 | 12.785 | 4.8086 | 0 | 6.2872 | 0 | 6.1172 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 59.9937 |  | STD2013 | 2.069 | 0.42301 | 0 | 0.98218 | 0 | 1.8421 | 0 | 1.7923 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.6959 |  | STD2013 | 0 | 0 | 0.12785 | 0.014564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23489 |  | STD2013 | 21.6598 | 4.4285 | 13.974 | 11.8743 | 0 | 19.2853 | 0 | 18.7639 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 137.6486
STD2010 | 0.273 | 0.043656 | 0.12657 | 0.11273 | 0 | 0.2204 | 0 | 0.18676 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.447 |  | STD2010 | 9.0284 | 1.4437 | 12.7851 | 4.68 | 0 | 7.289 | 0 | 6.1764 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 63.6249 |  | STD2010 | 2.6453 | 0.42301 | 0 | 0.95665 | 0 | 2.1357 | 0 | 1.8097 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.772 |  | STD2010 | 0 | 0 | 0.12785 | 0.014149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23447 |  | STD2010 | 27.6935 | 4.4285 | 13.9741 | 11.5616 | 0 | 22.3583 | 0 | 18.9455 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 148.8684
STD2007 | 0.33043 | 0.063199 | 0.12661 | 0.1195 | 0 | 0.25525 | 0 | 0.19707 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5832 |  | STD2007 | 10.9277 | 2.0901 | 12.7886 | 4.8124 | 0 | 8.4415 | 0 | 6.5173 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 68.04 |  | STD2007 | 3.2018 | 0.61239 | 0 | 1.0352 | 0 | 2.4733 | 0 | 1.9096 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.1043 |  | STD2007 | 0 | 0 | 0.12789 | 0.012791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23315 |  | STD2007 | 33.5195 | 6.4111 | 13.978 | 12.236 | 0 | 25.8933 | 0 | 19.9912 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 162.6725
STD2004 | 0.33043 | 0.063199 | 0.12667 | 0.21257 | 0 | 0.27473 | 0 | 0.19829 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.697 |  | STD2004 | 10.9277 | 2.0901 | 12.7944 | 9.4237 | 0 | 9.0859 | 0 | 6.5577 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 73.3418 |  | STD2004 | 3.2018 | 0.61239 | 0 | 1.7184 | 0 | 2.6621 | 0 | 1.9214 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.9881 |  | STD2004 | 0 | 0 | 0.12794 | 0.035589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25601 |  | STD2004 | 33.5195 | 6.4111 | 13.9843 | 21.8795 | 0 | 27.8699 | 0 | 20.1149 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 174.4225
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 5.7429e-05 | 0.093069 | 0 | 0.019484 | 0 | 0.0012194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11383 |  | 2004-2007 | 0 | 0 | 0.005801 | 4.6113 | 0 | 0.64437 | 0 | 0.040326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3018 |  | 2004-2007 | 0 | 0 | 0 | 0.68313 | 0 | 0.1888 | 0 | 0.011815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88374 |  | 2004-2007 | 0 | 0 | 5.801e-05 | 0.022798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022856 |  | 2004-2007 | 0 | 0 | 0.0063404 | 9.6435 | 0 | 1.9765 | 0 | 0.1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7501
2007-2010 | 0.057432 | 0.019543 | 3.5627e-05 | 0.0067665 | 0 | 0.034848 | 0 | 0.010308 | 0 | 0 | 0 | 0.0056866 | 0 | 0 | 0 | 0.0015726 | 0.13619 |  | 2007-2010 | 1.8993 | 0.64632 | 0.0035987 | 0.13244 | 0 | 1.1525 | 0 | 0.34092 | 0 | 0 | 0 | 0.18807 | 0 | 0 | 0 | 0.052007 | 4.4152 |  | 2007-2010 | 0.5565 | 0.18937 | 0 | 0.078593 | 0 | 0.33767 | 0 | 0.099888 | 0 | 0 | 0 | 0.055103 | 0 | 0 | 0 | 0.015238 | 1.3324 |  | 2007-2010 | 0 | 0 | 3.5987e-05 | -0.001358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.001322 |  | 2007-2010 | 5.826 | 1.9825 | 0.0039334 | 0.67437 | 0 | 3.5351 | 0 | 1.0457 | 0 | 0 | 0 | 0.57687 | 0 | 0 | 0 | 0.15953 | 13.804
2010-2013 | 0.059479 | 0 | 3.885e-07 | -0.0030456 | 0 | 0.030293 | 0 | 0.0017903 | 0 | 0 | 0 | 0.00044458 | 0 | 0 | 0 | 0.021678 | 0.11064 |  | 2010-2013 | 1.967 | 0 | 3.9242e-05 | -0.12862 | 0 | 1.0018 | 0 | 0.059207 | 0 | 0 | 0 | 0.014703 | 0 | 0 | 0 | 0.71693 | 3.6311 |  | 2010-2013 | 0.57634 | 0 | 0 | -0.025531 | 0 | 0.29353 | 0 | 0.017348 | 0 | 0 | 0 | 0.0043079 | 0 | 0 | 0 | 0.21006 | 1.0761 |  | 2010-2013 | 0 | 0 | 3.9242e-07 | -0.00041486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00041447 |  | 2010-2013 | 6.0337 | 0 | 4.2891e-05 | -0.31263 | 0 | 3.073 | 0 | 0.18161 | 0 | 0 | 0 | 0.0451 | 0 | 0 | 0 | 2.1991 | 11.2199
2004-2013 | 0.11691 | 0.019543 | 9.3445e-05 | 0.09679 | 0 | 0.084625 | 0 | 0.013318 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.36066 |  | 2004-2013 | 3.8664 | 0.64632 | 0.0094389 | 4.6151 | 0 | 2.7987 | 0 | 0.44045 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 13.3481 |  | 2004-2013 | 1.1328 | 0.18937 | 0 | 0.73619 | 0 | 0.82 | 0 | 0.12905 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.2922 |  | 2004-2013 | 0 | 0 | 9.4389e-05 | 0.021025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02112 |  | 2004-2013 | 11.8597 | 1.9825 | 0.010317 | 10.0052 | 0 | 8.5846 | 0 | 1.351 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 36.774
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.04534% | 43.78% |  | 7.092% |  | 0.6149% |  | 0% |  | 0% |  |  |  | 0% | 6.708% |  | 2004-2007 | 0% | 0% | 0.04534% | 48.93% |  | 7.092% |  | 0.6149% |  | 0% |  | 0% |  |  |  | 0% | 7.229% |  | 2004-2007 | 0% | 0% |  | 39.75% |  | 7.092% |  | 0.6149% |  | 0% |  | 0% |  |  |  | 0% | 6.318% |  | 2004-2007 |  |  | 0.04534% | 64.06% | [11 empty] | 0% | 8.928% |  | 2004-2007 | 0% | 0% | 0.04534% | 44.08% |  | 7.092% |  | 0.6149% |  | 0% |  | 0% |  |  |  | 0% | 6.737%
2007-2010 | 17.38% | 30.92% | 0.02814% | 5.662% |  | 13.65% |  | 5.231% |  | 0% |  | 3.307% |  |  |  | 0.493% | 8.602% |  | 2007-2010 | 17.38% | 30.92% | 0.02814% | 2.752% |  | 13.65% |  | 5.231% |  | 0% |  | 3.307% |  |  |  | 0.3101% | 6.489% |  | 2007-2010 | 17.38% | 30.92% |  | 7.592% |  | 13.65% |  | 5.231% |  | 0% |  | 3.307% |  |  |  | 0.6913% | 10.17% |  | 2007-2010 |  |  | 0.02814% | -10.62% | [11 empty] | 0% | -0.567% |  | 2007-2010 | 17.38% | 30.92% | 0.02814% | 5.511% |  | 13.65% |  | 5.231% |  | 0% |  | 3.307% |  |  |  | 0.4808% | 8.486%
2010-2013 | 21.79% | 0% | 0.0003069% | -2.702% |  | 13.74% |  | 0.9586% |  | 0% |  | 0.2674% |  |  |  | 6.829% | 7.646% |  | 2010-2013 | 21.79% | 0% | 0.0003069% | -2.748% |  | 13.74% |  | 0.9586% |  | 0% |  | 0.2674% |  |  |  | 4.288% | 5.707% |  | 2010-2013 | 21.79% | 0% |  | -2.669% |  | 13.74% |  | 0.9586% |  | 0% |  | 0.2674% |  |  |  | 9.597% | 9.141% |  | 2010-2013 |  |  | 0.0003069% | -2.932% | [11 empty] | 0% | -0.1768% |  | 2010-2013 | 21.79% | 0% | 0.0003069% | -2.704% |  | 13.74% |  | 0.9586% |  | 0% |  | 0.2674% |  |  |  | 6.659% | 7.537%
2004-2013 | 35.38% | 30.92% | 0.07377% | 45.53% |  | 30.8% |  | 6.717% |  | 0% |  | 3.566% |  |  |  | 7.288% | 21.25% |  | 2004-2013 | 35.38% | 30.92% | 0.07377% | 48.97% |  | 30.8% |  | 6.717% |  | 0% |  | 3.566% |  |  |  | 4.585% | 18.2% |  | 2004-2013 | 35.38% | 30.92% |  | 42.84% |  | 30.8% |  | 6.717% |  | 0% |  | 3.566% |  |  |  | 10.22% | 23.54% |  | 2004-2013 |  |  | 0.07377% | 59.08% | [11 empty] | 0% | 8.25% |  | 2004-2013 | 35.38% | 30.92% | 0.07377% | 45.73% |  | 30.8% |  | 6.717% |  | 0% |  | 3.566% |  |  |  | 7.108% | 21.08%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.21439 | 0.043741 | 0.095372 | 0.00087421 | 0 | 0.40455 | 0 | 0.18438 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.4051 | 0.5926% | CZ 1A | 7.0901 | 1.4466 | 9.6335 | 0.035109 | 0 | 13.3789 | 0 | 6.0977 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 59.1725 | 0.5926% | CZ 1A | 2.0774 | 0.42384 | 0 | 0.007587 | 0 | 3.92 | 0 | 1.7866 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 11.8027 | 0.5926% | CZ 1A | 0 | 0 | 0.096335 | 9.2145e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.1889 | 0.5926% | CZ 1A | 21.748 | 4.4372 | 10.5294 | 0.0895 | 0 | 41.0383 | 0 | 18.7041 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 144.2093 | 0.5926%
CZ 1B | 0.2156 | 0.043708 | 0.089913 | 0.0042083 | 0 | 0.36393 | 0 | 0.19321 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3723 | 0% | CZ 1B | 7.1302 | 1.4455 | 9.0822 | 0.16677 | 0 | 12.0357 | 0 | 6.3896 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 57.7406 | 0% | CZ 1B | 2.0891 | 0.42352 | 0 | 0.036842 | 0 | 3.5264 | 0 | 1.8721 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 11.5354 | 0% | CZ 1B | 0 | 0 | 0.090822 | 0.00041026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.1837 | 0% | CZ 1B | 21.8711 | 4.4339 | 9.9268 | 0.43054 | 0 | 36.9181 | 0 | 19.5993 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 140.8426 | 0%
CZ 2A | 0.21544 | 0.043668 | 0.10796 | 0.023266 | 0 | 0.29923 | 0 | 0.18453 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3359 | 16.72% | CZ 2A | 7.1249 | 1.4442 | 10.9047 | 0.98413 | 0 | 9.8959 | 0 | 6.1028 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 57.9472 | 16.72% | CZ 2A | 2.0876 | 0.42314 | 0 | 0.19482 | 0 | 2.8995 | 0 | 1.7881 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.9804 | 16.72% | CZ 2A | 0 | 0 | 0.10905 | 0.0031922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.20471 | 16.72% | CZ 2A | 21.855 | 4.4298 | 11.9188 | 2.3885 | 0 | 30.3545 | 0 | 18.7196 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 137.3289 | 16.72%
CZ 2B | 0.2162 | 0.043642 | 0.10061 | 0.0089069 | 0 | 0.32307 | 0 | 0.18984 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.344 | 1.732% | CZ 2B | 7.1502 | 1.4433 | 10.1622 | 0.36864 | 0 | 10.6843 | 0 | 6.2783 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 57.5777 | 1.732% | CZ 2B | 2.095 | 0.42288 | 0 | 0.075742 | 0 | 3.1305 | 0 | 1.8395 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 11.1509 | 1.732% | CZ 2B | 0 | 0 | 0.10162 | 0.0011013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.1952 | 1.732% | CZ 2B | 21.9324 | 4.4271 | 11.1073 | 0.91332 | 0 | 32.773 | 0 | 19.2581 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 138.074 | 1.732%
CZ 3A | 0.21593 | 0.043695 | 0.11782 | 0.072386 | 0 | 0.22867 | 0 | 0.18469 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3249 | 15.56% | CZ 3A | 7.141 | 1.445 | 11.9014 | 3.0106 | 0 | 7.5623 | 0 | 6.1078 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 58.6587 | 15.56% | CZ 3A | 2.0923 | 0.42339 | 0 | 0.61346 | 0 | 2.2157 | 0 | 1.7896 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.7218 | 15.56% | CZ 3A | 0 | 0 | 0.11901 | 0.0091684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22065 | 15.56% | CZ 3A | 21.9041 | 4.4325 | 13.0082 | 7.4244 | 0 | 23.1965 | 0 | 18.7351 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 136.3635 | 15.56%
CZ 3B | 0.21606 | 0.043701 | 0.11456 | 0.026236 | 0 | 0.2134 | 0 | 0.19115 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.2669 | 6.609% | CZ 3B | 7.1454 | 1.4453 | 11.5714 | 1.0921 | 0 | 7.0576 | 0 | 6.3216 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 56.1239 | 6.609% | CZ 3B | 2.0936 | 0.42346 | 0 | 0.22221 | 0 | 2.0679 | 0 | 1.8522 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.2466 | 6.609% | CZ 3B | 0 | 0 | 0.11571 | 0.003337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21152 | 6.609% | CZ 3B | 21.9176 | 4.4332 | 12.6475 | 2.691 | 0 | 21.6483 | 0 | 19.3907 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 130.3911 | 6.609%
CZ 3C | 0.21595 | 0.043635 | 0.12852 | 0.016437 | 0 | 0.11603 | 0 | 0.18201 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.1644 | 1.264% | CZ 3C | 7.1418 | 1.4431 | 12.9821 | 0.76227 | 0 | 3.8374 | 0 | 6.0194 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 53.6767 | 1.264% | CZ 3C | 2.0925 | 0.42282 | 0 | 0.12808 | 0 | 1.1244 | 0 | 1.7637 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 9.1188 | 1.264% | CZ 3C | 0 | 0 | 0.12982 | 0.0032514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22554 | 1.264% | CZ 3C | 21.9068 | 4.4265 | 14.1894 | 1.6962 | 0 | 11.7709 | 0 | 18.4638 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 120.1164 | 1.264%
CZ 4A | 0.21168 | 0.043675 | 0.12991 | 0.11944 | 0 | 0.17028 | 0 | 0.18358 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3203 | 18.28% | CZ 4A | 7.0005 | 1.4444 | 13.1218 | 4.9946 | 0 | 5.6314 | 0 | 6.0712 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 59.7546 | 18.28% | CZ 4A | 2.0511 | 0.4232 | 0 | 1.0084 | 0 | 1.65 | 0 | 1.7788 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.4989 | 18.28% | CZ 4A | 0 | 0 | 0.13122 | 0.015529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23922 | 18.28% | CZ 4A | 21.4733 | 4.4305 | 14.3422 | 12.2545 | 0 | 17.2737 | 0 | 18.6226 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 136.0596 | 18.28%
CZ 4B | 0.21215 | 0.043662 | 0.12804 | 0.057356 | 0 | 0.16423 | 0 | 0.19216 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.2594 | 1.181% | CZ 4B | 7.0161 | 1.4439 | 12.9334 | 2.3755 | 0 | 5.4313 | 0 | 6.3551 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 57.046 | 1.181% | CZ 4B | 2.0557 | 0.42307 | 0 | 0.4875 | 0 | 1.5913 | 0 | 1.862 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.007 | 1.181% | CZ 4B | 0 | 0 | 0.12933 | 0.0071171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22892 | 1.181% | CZ 4B | 21.5211 | 4.4292 | 14.1362 | 5.8815 | 0 | 16.6598 | 0 | 19.4937 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 129.7842 | 1.181%
CZ 4C | 0.21263 | 0.043648 | 0.13501 | 0.079043 | 0 | 0.11607 | 0 | 0.18405 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.2322 | 2.281% | CZ 4C | 7.0319 | 1.4435 | 13.6372 | 3.3792 | 0 | 3.8385 | 0 | 6.0868 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 56.9077 | 2.281% | CZ 4C | 2.0603 | 0.42294 | 0 | 0.65679 | 0 | 1.1247 | 0 | 1.7834 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 9.6355 | 2.281% | CZ 4C | 0 | 0 | 0.13637 | 0.011375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24022 | 2.281% | CZ 4C | 21.5696 | 4.4278 | 14.9054 | 8.1193 | 0 | 11.7743 | 0 | 18.6704 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 127.1296 | 2.281%
CZ 5A | 0.21165 | 0.043622 | 0.13835 | 0.2108 | 0 | 0.13858 | 0 | 0.18401 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3888 | 21.19% | CZ 5A | 6.9996 | 1.4426 | 13.975 | 8.6956 | 0 | 4.5831 | 0 | 6.0854 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 63.2721 | 21.19% | CZ 5A | 2.0509 | 0.42269 | 0 | 1.7967 | 0 | 1.3428 | 0 | 1.783 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.9834 | 21.19% | CZ 5A | 0 | 0 | 0.13975 | 0.025634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25786 | 21.19% | CZ 5A | 21.4706 | 4.4251 | 15.2747 | 21.6115 | 0 | 14.0582 | 0 | 18.6664 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 143.1693 | 21.19%
CZ 5B | 0.21287 | 0.043602 | 0.13681 | 0.10868 | 0 | 0.12385 | 0 | 0.18775 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.2753 | 5.194% | CZ 5B | 7.04 | 1.442 | 13.8195 | 4.5567 | 0 | 4.0959 | 0 | 6.2092 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 58.6539 | 5.194% | CZ 5B | 2.0627 | 0.42249 | 0 | 0.91584 | 0 | 1.2001 | 0 | 1.8193 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.0077 | 5.194% | CZ 5B | 0 | 0 | 0.13819 | 0.014309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24498 | 5.194% | CZ 5B | 21.5945 | 4.4231 | 15.1047 | 11.1519 | 0 | 12.5639 | 0 | 19.046 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 131.5468 | 5.194%
CZ 5C | 0.2143 | 0.043575 | 0.13846 | 0.10578 | 0 | 0.087011 | 0 | 0.18139 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.2323 | 0% | CZ 5C | 7.0872 | 1.4411 | 13.9858 | 4.5156 | 0 | 2.8776 | 0 | 5.999 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 57.3969 | 0% | CZ 5C | 2.0765 | 0.42224 | 0 | 0.87997 | 0 | 0.84312 | 0 | 1.7577 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 9.5669 | 0% | CZ 5C | 0 | 0 | 0.13986 | 0.015123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24745 | 0% | CZ 5C | 21.7392 | 4.4204 | 15.2865 | 10.8653 | 0 | 8.8267 | 0 | 18.4012 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 127.202 | 0%
CZ 6A | 0.21219 | 0.043622 | 0.14584 | 0.24878 | 0 | 0.10564 | 0 | 0.18274 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.4006 | 6.195% | CZ 6A | 7.0174 | 1.4426 | 14.7309 | 10.302 | 0 | 3.4936 | 0 | 6.0435 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 64.5206 | 6.195% | CZ 6A | 2.0561 | 0.42269 | 0 | 2.1148 | 0 | 1.0236 | 0 | 1.7707 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.9752 | 6.195% | CZ 6A | 0 | 0 | 0.14731 | 0.030842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.27062 | 6.195% | CZ 6A | 21.5252 | 4.4251 | 16.1008 | 25.5108 | 0 | 10.7161 | 0 | 18.5378 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 144.4785 | 6.195%
CZ 6B | 0.21259 | 0.043589 | 0.1469 | 0.18054 | 0 | 0.096268 | 0 | 0.18926 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3309 | 1.79% | CZ 6B | 7.0308 | 1.4415 | 14.8381 | 7.4845 | 0 | 3.1837 | 0 | 6.2592 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 61.7286 | 1.79% | CZ 6B | 2.06 | 0.42237 | 0 | 1.5335 | 0 | 0.93282 | 0 | 1.8339 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.3699 | 1.79% | CZ 6B | 0 | 0 | 0.14838 | 0.022507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.26336 | 1.79% | CZ 6B | 21.5662 | 4.4217 | 16.2181 | 18.5141 | 0 | 9.7657 | 0 | 19.1995 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 137.348 | 1.79%
CZ 7 | 0.20963 | 0.043595 | 0.15767 | 0.33859 | 0 | 0.085764 | 0 | 0.18341 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.4804 | 1.191% | CZ 7 | 6.9327 | 1.4418 | 15.9265 | 14.0264 | 0 | 2.8363 | 0 | 6.0657 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 68.72 | 1.191% | CZ 7 | 2.0313 | 0.42243 | 0 | 2.8774 | 0 | 0.83104 | 0 | 1.7772 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 11.5267 | 1.191% | CZ 7 | 0 | 0 | 0.15927 | 0.042057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.29379 | 1.191% | CZ 7 | 21.2653 | 4.4224 | 17.4077 | 34.7205 | 0 | 8.7001 | 0 | 18.6058 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 152.7846 | 1.191%
CZ 8 | 0.21332 | 0.043323 | 0.17225 | 0.54676 | 0 | 0.062467 | 0 | 0.18263 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.6825 | 0.2253% | CZ 8 | 7.0549 | 1.4328 | 17.3989 | 22.6289 | 0 | 2.0659 | 0 | 6.0398 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 78.1117 | 0.2253% | CZ 8 | 2.0671 | 0.41979 | 0 | 4.6496 | 0 | 0.60529 | 0 | 1.7696 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 13.0987 | 0.2253% | CZ 8 | 0 | 0 | 0.17399 | 0.067599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.33406 | 0.2253% | CZ 8 | 21.6403 | 4.3948 | 19.017 | 56.0648 | 0 | 6.3368 | 0 | 18.5264 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 173.6428 | 0.2253%
Us Weighted | 0.21352 | 0.043656 | 0.12657 | 0.11578 | 0 | 0.19011 | 0 | 0.18497 | 0 | 0.00017252 | 0 | 0.16583 | 0 | 0 | 0 | 0.29576 | 1.3364 | 100% | Us Weighted | 7.0613 | 1.4437 | 12.785 | 4.8086 | 0 | 6.2872 | 0 | 6.1172 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 0 | 0 | 16.0007 | 59.9937 | 100% | Us Weighted | 2.069 | 0.42301 | 0 | 0.98218 | 0 | 1.8421 | 0 | 1.7923 | 0 | 0.0016717 | 0 | 1.6069 | 0 | 0 | 0 | 1.9788 | 10.6959 | 100% | Us Weighted | 0 | 0 | 0.12785 | 0.014564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23489 | 100% | Us Weighted | 21.6598 | 4.4285 | 13.974 | 11.8743 | 0 | 19.2853 | 0 | 18.7639 | 0 | 0.017501 | 0 | 16.8222 | 0 | 0 | 0 | 30.823 | 137.6486 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.27457 | 0.043741 | 0.095387 | 0.00091608 | 0 | 0.46178 | 0 | 0.1864 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.5467 | 0.5926% | CZ 1A | 9.0804 | 1.4466 | 9.635 | 0.037084 | 0 | 15.2716 | 0 | 6.1644 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 63.8575 | 0.5926% | CZ 1A | 2.6605 | 0.42384 | 0 | 0.0079085 | 0 | 4.4745 | 0 | 1.8062 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 13.1747 | 0.5926% | CZ 1A | 0 | 0 | 0.09635 | 0.00010092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.18892 | 0.5926% | CZ 1A | 27.8532 | 4.4372 | 10.5311 | 0.093825 | 0 | 46.844 | 0 | 18.9087 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 158.575 | 0.5926%
CZ 1B | 0.27457 | 0.043708 | 0.089911 | 0.0045267 | 0 | 0.40811 | 0 | 0.19654 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.5013 | 0% | CZ 1B | 9.0804 | 1.4455 | 9.0819 | 0.17774 | 0 | 13.4968 | 0 | 6.5 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 62.0046 | 0% | CZ 1B | 2.6605 | 0.42352 | 0 | 0.039864 | 0 | 3.9545 | 0 | 1.9045 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.7846 | 0% | CZ 1B | 0 | 0 | 0.090819 | 0.00041684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.18371 | 0% | CZ 1B | 27.8532 | 4.4339 | 9.9266 | 0.4629 | 0 | 41.3998 | 0 | 19.9379 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 153.9212 | 0%
CZ 2A | 0.27457 | 0.043668 | 0.10798 | 0.023255 | 0 | 0.34169 | 0 | 0.18717 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4622 | 16.72% | CZ 2A | 9.0804 | 1.4442 | 10.9075 | 0.99927 | 0 | 11.3003 | 0 | 6.1899 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 62.1439 | 16.72% | CZ 2A | 2.6605 | 0.42314 | 0 | 0.1925 | 0 | 3.311 | 0 | 1.8136 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.2024 | 16.72% | CZ 2A | 0 | 0 | 0.10908 | 0.0034225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.20497 | 16.72% | CZ 2A | 27.8532 | 4.4298 | 11.9219 | 2.3894 | 0 | 34.6625 | 0 | 18.9868 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 150.1506 | 16.72%
CZ 2B | 0.27457 | 0.043642 | 0.10062 | 0.0087822 | 0 | 0.3651 | 0 | 0.19402 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4706 | 1.732% | CZ 2B | 9.0804 | 1.4433 | 10.1633 | 0.36776 | 0 | 12.0743 | 0 | 6.4166 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 61.768 | 1.732% | CZ 2B | 2.6605 | 0.42288 | 0 | 0.07407 | 0 | 3.5377 | 0 | 1.88 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.377 | 1.732% | CZ 2B | 0 | 0 | 0.10163 | 0.0011496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.19525 | 1.732% | CZ 2B | 27.8532 | 4.4271 | 11.1085 | 0.90109 | 0 | 37.0366 | 0 | 19.6821 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 150.9156 | 1.732%
CZ 3A | 0.27305 | 0.043695 | 0.11781 | 0.064092 | 0 | 0.26417 | 0 | 0.18585 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4326 | 15.56% | CZ 3A | 9.0302 | 1.445 | 11.9003 | 2.6944 | 0 | 8.7366 | 0 | 6.1464 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 62.1751 | 15.56% | CZ 3A | 2.6458 | 0.42339 | 0 | 0.53906 | 0 | 2.5598 | 0 | 1.8009 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.7706 | 15.56% | CZ 3A | 0 | 0 | 0.119 | 0.0085453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22002 | 15.56% | CZ 3A | 27.699 | 4.4325 | 13.007 | 6.5775 | 0 | 26.7984 | 0 | 18.8535 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 147.2749 | 15.56%
CZ 3B | 0.27318 | 0.043701 | 0.11454 | 0.022387 | 0 | 0.24681 | 0 | 0.19293 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.3774 | 6.609% | CZ 3B | 9.0346 | 1.4453 | 11.5699 | 0.94222 | 0 | 8.1625 | 0 | 6.3804 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 59.757 | 6.609% | CZ 3B | 2.6471 | 0.42346 | 0 | 0.18813 | 0 | 2.3916 | 0 | 1.8694 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.3214 | 6.609% | CZ 3B | 0 | 0 | 0.1157 | 0.0030013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21117 | 6.609% | CZ 3B | 27.7125 | 4.4332 | 12.6459 | 2.2976 | 0 | 25.0375 | 0 | 19.5711 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 141.6047 | 6.609%
CZ 3C | 0.27457 | 0.043635 | 0.12851 | 0.01255 | 0 | 0.14465 | 0 | 0.18313 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.2709 | 1.264% | CZ 3C | 9.0804 | 1.4431 | 12.9803 | 0.60319 | 0 | 4.7837 | 0 | 6.0562 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 57.1692 | 1.264% | CZ 3C | 2.6605 | 0.42282 | 0 | 0.094774 | 0 | 1.4016 | 0 | 1.7745 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 10.1559 | 1.264% | CZ 3C | 0 | 0 | 0.1298 | 0.0027972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22507 | 1.264% | CZ 3C | 27.8532 | 4.4265 | 14.1875 | 1.2979 | 0 | 14.6734 | 0 | 18.5769 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 130.9223 | 1.264%
CZ 4A | 0.27236 | 0.043675 | 0.12989 | 0.11264 | 0 | 0.19899 | 0 | 0.18508 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4265 | 18.28% | CZ 4A | 9.0073 | 1.4444 | 13.1205 | 4.719 | 0 | 6.5809 | 0 | 6.121 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 63.2155 | 18.28% | CZ 4A | 2.6391 | 0.4232 | 0 | 0.94966 | 0 | 1.9282 | 0 | 1.7934 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.5353 | 18.28% | CZ 4A | 0 | 0 | 0.13121 | 0.014778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23845 | 18.28% | CZ 4A | 27.629 | 4.4305 | 14.3407 | 11.5573 | 0 | 20.1863 | 0 | 18.7754 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 146.8262 | 18.28%
CZ 4B | 0.27255 | 0.043662 | 0.12803 | 0.054311 | 0 | 0.1922 | 0 | 0.19392 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.3686 | 1.181% | CZ 4B | 9.0137 | 1.4439 | 12.9325 | 2.2402 | 0 | 6.3564 | 0 | 6.4131 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 60.6221 | 1.181% | CZ 4B | 2.641 | 0.42307 | 0 | 0.46294 | 0 | 1.8624 | 0 | 1.879 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.0701 | 1.181% | CZ 4B | 0 | 0 | 0.12932 | 0.0066015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.2284 | 1.181% | CZ 4B | 27.6486 | 4.4292 | 14.1352 | 5.568 | 0 | 19.4977 | 0 | 19.6714 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 140.857 | 1.181%
CZ 4C | 0.27253 | 0.043648 | 0.135 | 0.073212 | 0 | 0.13756 | 0 | 0.18538 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.3312 | 2.281% | CZ 4C | 9.0131 | 1.4435 | 13.6361 | 3.1499 | 0 | 4.5493 | 0 | 6.1306 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 60.1448 | 2.281% | CZ 4C | 2.6408 | 0.42294 | 0 | 0.60548 | 0 | 1.3329 | 0 | 1.7963 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 10.6001 | 2.281% | CZ 4C | 0 | 0 | 0.13636 | 0.010834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23967 | 2.281% | CZ 4C | 27.6465 | 4.4278 | 14.9042 | 7.5229 | 0 | 13.9545 | 0 | 18.8051 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 137.168 | 2.281%
CZ 5A | 0.27233 | 0.043622 | 0.13836 | 0.20873 | 0 | 0.16267 | 0 | 0.18571 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4953 | 21.19% | CZ 5A | 9.0062 | 1.4426 | 13.9753 | 8.5944 | 0 | 5.3797 | 0 | 6.1416 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 66.7621 | 21.19% | CZ 5A | 2.6388 | 0.42269 | 0 | 1.7813 | 0 | 1.5762 | 0 | 1.7995 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.0202 | 21.19% | CZ 5A | 0 | 0 | 0.13975 | 0.025147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25737 | 21.19% | CZ 5A | 27.6257 | 4.4251 | 15.275 | 21.3974 | 0 | 16.5016 | 0 | 18.8387 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 153.9704 | 21.19%
CZ 5B | 0.27269 | 0.043602 | 0.13681 | 0.10762 | 0 | 0.14481 | 0 | 0.18964 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.3791 | 5.194% | CZ 5B | 9.0183 | 1.442 | 13.8193 | 4.4915 | 0 | 4.7892 | 0 | 6.2715 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 62.054 | 5.194% | CZ 5B | 2.6423 | 0.42249 | 0 | 0.9098 | 0 | 1.4032 | 0 | 1.8375 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.0171 | 5.194% | CZ 5B | 0 | 0 | 0.13819 | 0.013863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24453 | 5.194% | CZ 5B | 27.6627 | 4.4231 | 15.1045 | 11.04 | 0 | 14.6903 | 0 | 19.2372 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 142.0646 | 5.194%
CZ 5C | 0.27283 | 0.043575 | 0.13846 | 0.10244 | 0 | 0.10536 | 0 | 0.18309 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.3296 | 0% | CZ 5C | 9.0229 | 1.4411 | 13.986 | 4.3666 | 0 | 3.4844 | 0 | 6.0552 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 60.5784 | 0% | CZ 5C | 2.6437 | 0.42224 | 0 | 0.85296 | 0 | 1.0209 | 0 | 1.7741 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 10.5156 | 0% | CZ 5C | 0 | 0 | 0.13986 | 0.014554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24689 | 0% | CZ 5C | 27.6768 | 4.4204 | 15.2867 | 10.5205 | 0 | 10.6879 | 0 | 18.5735 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 137.0727 | 0%
CZ 6A | 0.27241 | 0.043622 | 0.14584 | 0.25092 | 0 | 0.12585 | 0 | 0.18436 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.5069 | 6.195% | CZ 6A | 9.0091 | 1.4426 | 14.7313 | 10.3272 | 0 | 4.162 | 0 | 6.0971 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 67.9916 | 6.195% | CZ 6A | 2.6396 | 0.42269 | 0 | 2.1419 | 0 | 1.2195 | 0 | 1.7864 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.0118 | 6.195% | CZ 6A | 0 | 0 | 0.14731 | 0.030169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.26995 | 6.195% | CZ 6A | 27.6344 | 4.4251 | 16.1013 | 25.7212 | 0 | 12.7665 | 0 | 18.7021 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 155.2575 | 6.195%
CZ 6B | 0.27268 | 0.043589 | 0.1469 | 0.18505 | 0 | 0.11392 | 0 | 0.19118 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.4372 | 1.79% | CZ 6B | 9.0179 | 1.4415 | 14.8384 | 7.5894 | 0 | 3.7677 | 0 | 6.3227 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 65.1998 | 1.79% | CZ 6B | 2.6422 | 0.42237 | 0 | 1.5835 | 0 | 1.1039 | 0 | 1.8525 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.4062 | 1.79% | CZ 6B | 0 | 0 | 0.14838 | 0.021849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.2627 | 1.79% | CZ 6B | 27.6613 | 4.4217 | 16.2183 | 18.9658 | 0 | 11.5569 | 0 | 19.394 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 148.1251 | 1.79%
CZ 7 | 0.27224 | 0.043595 | 0.15769 | 0.35208 | 0 | 0.10061 | 0 | 0.18573 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.5958 | 1.191% | CZ 7 | 9.0034 | 1.4418 | 15.9287 | 14.4677 | 0 | 3.3274 | 0 | 6.1425 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 72.5338 | 1.191% | CZ 7 | 2.638 | 0.42243 | 0 | 3.0088 | 0 | 0.97493 | 0 | 1.7997 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 12.6455 | 1.191% | CZ 7 | 0 | 0 | 0.15929 | 0.041987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.29375 | 1.191% | CZ 7 | 27.6169 | 4.4224 | 17.4101 | 36.088 | 0 | 10.2066 | 0 | 18.8414 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 164.4924 | 1.191%
CZ 8 | 0.27286 | 0.043323 | 0.1723 | 0.58476 | 0 | 0.073521 | 0 | 0.1852 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.8159 | 0.2253% | CZ 8 | 9.024 | 1.4328 | 17.4044 | 24.0907 | 0 | 2.4315 | 0 | 6.1249 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 82.7305 | 0.2253% | CZ 8 | 2.644 | 0.41979 | 0 | 4.9885 | 0 | 0.71241 | 0 | 1.7946 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 14.361 | 0.2253% | CZ 8 | 0 | 0 | 0.17404 | 0.070651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.33717 | 0.2253% | CZ 8 | 27.6802 | 4.3948 | 19.023 | 59.9464 | 0 | 7.4582 | 0 | 18.7876 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 187.1971 | 0.2253%
Us Weighted | 0.273 | 0.043656 | 0.12657 | 0.11273 | 0 | 0.2204 | 0 | 0.18676 | 0 | 0.00017252 | 0 | 0.16627 | 0 | 0 | 0 | 0.31744 | 1.447 | 100% | Us Weighted | 9.0284 | 1.4437 | 12.7851 | 4.68 | 0 | 7.289 | 0 | 6.1764 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 0 | 0 | 16.7177 | 63.6249 | 100% | Us Weighted | 2.6453 | 0.42301 | 0 | 0.95665 | 0 | 2.1357 | 0 | 1.8097 | 0 | 0.0016717 | 0 | 1.6112 | 0 | 0 | 0 | 2.1888 | 11.772 | 100% | Us Weighted | 0 | 0 | 0.12785 | 0.014149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23447 | 100% | Us Weighted | 27.6935 | 4.4285 | 13.9741 | 11.5616 | 0 | 22.3583 | 0 | 18.9455 | 0 | 0.017501 | 0 | 16.8673 | 0 | 0 | 0 | 33.0221 | 148.8684 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.33043 | 0.063329 | 0.095391 | 0.0009589 | 0 | 0.52443 | 0 | 0.19798 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7037 | 0.5926% | CZ 1A | 10.9277 | 2.0944 | 9.6355 | 0.035549 | 0 | 17.3436 | 0 | 6.5474 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 69.0465 | 0.5926% | CZ 1A | 3.2018 | 0.61365 | 0 | 0.0087444 | 0 | 5.0816 | 0 | 1.9184 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.6962 | 0.5926% | CZ 1A | 0 | 0 | 0.096355 | 5.7042e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.18888 | 0.5926% | CZ 1A | 33.5195 | 6.4243 | 10.5316 | 0.09778 | 0 | 53.1997 | 0 | 20.0833 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 174.4995 | 0.5926%
CZ 1B | 0.33043 | 0.063276 | 0.089898 | 0.0041627 | 0 | 0.47072 | 0 | 0.20768 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6573 | 0% | CZ 1B | 10.9277 | 2.0926 | 9.0806 | 0.15404 | 0 | 15.5672 | 0 | 6.8684 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 67.153 | 0% | CZ 1B | 3.2018 | 0.61313 | 0 | 0.037999 | 0 | 4.5612 | 0 | 2.0124 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.2985 | 0% | CZ 1B | 0 | 0 | 0.090806 | 0.00024353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.18352 | 0% | CZ 1B | 33.5195 | 6.4189 | 9.9251 | 0.42443 | 0 | 47.7507 | 0 | 21.0681 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 169.7502 | 0%
CZ 2A | 0.33043 | 0.063216 | 0.108 | 0.022606 | 0 | 0.39521 | 0 | 0.19918 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6098 | 16.72% | CZ 2A | 10.9277 | 2.0907 | 10.9088 | 0.92512 | 0 | 13.0702 | 0 | 6.5873 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 66.9721 | 16.72% | CZ 2A | 3.2018 | 0.61256 | 0 | 0.19373 | 0 | 3.8295 | 0 | 1.9301 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.6397 | 16.72% | CZ 2A | 0 | 0 | 0.10909 | 0.0026393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.2042 | 16.72% | CZ 2A | 33.5195 | 6.4128 | 11.9233 | 2.3166 | 0 | 40.0912 | 0 | 20.2058 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 165.1127 | 16.72%
CZ 2B | 0.33043 | 0.063177 | 0.10061 | 0.0080631 | 0 | 0.42659 | 0 | 0.20643 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6264 | 1.732% | CZ 2B | 10.9277 | 2.0893 | 10.1629 | 0.31225 | 0 | 14.1079 | 0 | 6.8269 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 66.8894 | 1.732% | CZ 2B | 3.2018 | 0.61217 | 0 | 0.071627 | 0 | 4.1336 | 0 | 2.0003 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.8915 | 1.732% | CZ 2B | 0 | 0 | 0.10163 | 0.00067792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.19478 | 1.732% | CZ 2B | 33.5195 | 6.4088 | 11.108 | 0.82396 | 0 | 43.2745 | 0 | 20.9409 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 166.719 | 1.732%
CZ 3A | 0.33043 | 0.063256 | 0.11783 | 0.066781 | 0 | 0.30888 | 0 | 0.19553 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5739 | 15.56% | CZ 3A | 10.9277 | 2.092 | 11.9025 | 2.7095 | 0 | 10.215 | 0 | 6.4666 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 66.7756 | 15.56% | CZ 3A | 3.2018 | 0.61294 | 0 | 0.57565 | 0 | 2.993 | 0 | 1.8947 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.1501 | 15.56% | CZ 3A | 0 | 0 | 0.11902 | 0.0074484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21894 | 15.56% | CZ 3A | 33.5195 | 6.4169 | 13.0094 | 6.8406 | 0 | 31.3332 | 0 | 19.8356 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 161.5986 | 15.56%
CZ 3B | 0.33043 | 0.063263 | 0.11456 | 0.021195 | 0 | 0.2875 | 0 | 0.2033 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5114 | 6.609% | CZ 3B | 10.9277 | 2.0922 | 11.5714 | 0.85381 | 0 | 9.5079 | 0 | 6.7234 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 64.1387 | 6.609% | CZ 3B | 3.2018 | 0.61301 | 0 | 0.18357 | 0 | 2.7858 | 0 | 1.9699 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.6261 | 6.609% | CZ 3B | 0 | 0 | 0.11571 | 0.0022729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21046 | 6.609% | CZ 3B | 33.5195 | 6.4176 | 12.6475 | 2.1702 | 0 | 29.1644 | 0 | 20.6232 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 155.1857 | 6.609%
CZ 3C | 0.33043 | 0.06317 | 0.12854 | 0.012268 | 0 | 0.16802 | 0 | 0.19104 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.3846 | 1.264% | CZ 3C | 10.9277 | 2.0891 | 12.9843 | 0.53057 | 0 | 5.5568 | 0 | 6.3178 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 60.8686 | 1.264% | CZ 3C | 3.2018 | 0.61211 | 0 | 0.10107 | 0 | 1.6281 | 0 | 1.8511 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 11.2662 | 1.264% | CZ 3C | 0 | 0 | 0.12984 | 0.0018561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22417 | 1.264% | CZ 3C | 33.5195 | 6.4081 | 14.1918 | 1.261 | 0 | 17.0448 | 0 | 19.3792 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 142.4479 | 1.264%
CZ 4A | 0.33043 | 0.063223 | 0.12994 | 0.11987 | 0 | 0.228 | 0 | 0.19462 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5572 | 18.28% | CZ 4A | 10.9277 | 2.0909 | 13.1249 | 4.8547 | 0 | 7.5404 | 0 | 6.4363 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 67.4372 | 18.28% | CZ 4A | 3.2018 | 0.61262 | 0 | 1.0345 | 0 | 2.2093 | 0 | 1.8858 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.816 | 18.28% | CZ 4A | 0 | 0 | 0.13125 | 0.01324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23696 | 18.28% | CZ 4A | 33.5195 | 6.4135 | 14.3455 | 12.2771 | 0 | 23.1292 | 0 | 19.7427 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 160.0709 | 18.28%
CZ 4B | 0.33043 | 0.06321 | 0.12805 | 0.053074 | 0 | 0.22182 | 0 | 0.20652 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.4942 | 1.181% | CZ 4B | 10.9277 | 2.0904 | 12.9347 | 2.0949 | 0 | 7.3358 | 0 | 6.83 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 64.676 | 1.181% | CZ 4B | 3.2018 | 0.61249 | 0 | 0.46583 | 0 | 2.1494 | 0 | 2.0012 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.3027 | 1.181% | CZ 4B | 0 | 0 | 0.12935 | 0.0050504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.22687 | 1.181% | CZ 4B | 33.5195 | 6.4122 | 14.1376 | 5.4288 | 0 | 22.5019 | 0 | 20.9503 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 153.5936 | 1.181%
CZ 4C | 0.33043 | 0.063196 | 0.13504 | 0.07582 | 0 | 0.1583 | 0 | 0.19404 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.448 | 2.281% | CZ 4C | 10.9277 | 2.09 | 13.6403 | 3.1117 | 0 | 5.2353 | 0 | 6.4172 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 63.8846 | 2.281% | CZ 4C | 3.2018 | 0.61236 | 0 | 0.6485 | 0 | 1.5339 | 0 | 1.8802 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 11.7488 | 2.281% | CZ 4C | 0 | 0 | 0.1364 | 0.0089841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23786 | 2.281% | CZ 4C | 33.5195 | 6.4108 | 14.9088 | 7.7711 | 0 | 16.0587 | 0 | 19.6842 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 148.9965 | 2.281%
CZ 5A | 0.33043 | 0.06315 | 0.13841 | 0.22582 | 0 | 0.18774 | 0 | 0.19595 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6326 | 21.19% | CZ 5A | 10.9277 | 2.0885 | 13.981 | 9.0511 | 0 | 6.209 | 0 | 6.4804 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 71.2 | 21.19% | CZ 5A | 3.2018 | 0.61191 | 0 | 1.9623 | 0 | 1.8192 | 0 | 1.8988 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.366 | 21.19% | CZ 5A | 0 | 0 | 0.13981 | 0.023536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25582 | 21.19% | CZ 5A | 33.5195 | 6.4061 | 15.2812 | 23.1163 | 0 | 19.0454 | 0 | 19.878 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 167.8898 | 21.19%
CZ 5B | 0.33043 | 0.063123 | 0.13685 | 0.10886 | 0 | 0.16903 | 0 | 0.20037 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.4998 | 5.194% | CZ 5B | 10.9277 | 2.0876 | 13.823 | 4.3899 | 0 | 5.5901 | 0 | 6.6266 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 65.9073 | 5.194% | CZ 5B | 3.2018 | 0.61166 | 0 | 0.94214 | 0 | 1.6379 | 0 | 1.9416 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.2071 | 5.194% | CZ 5B | 0 | 0 | 0.13823 | 0.011744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24245 | 5.194% | CZ 5B | 33.5195 | 6.4034 | 15.1085 | 11.1469 | 0 | 17.1472 | 0 | 20.3263 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 154.2952 | 5.194%
CZ 5C | 0.33043 | 0.063084 | 0.1385 | 0.10445 | 0 | 0.12283 | 0 | 0.19057 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.441 | 0% | CZ 5C | 10.9277 | 2.0863 | 13.9902 | 4.2861 | 0 | 4.0621 | 0 | 6.3025 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 64.1173 | 0% | CZ 5C | 3.2018 | 0.61127 | 0 | 0.89347 | 0 | 1.1902 | 0 | 1.8466 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 11.6154 | 0% | CZ 5C | 0 | 0 | 0.1399 | 0.012367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24474 | 0% | CZ 5C | 33.5195 | 6.3994 | 15.2913 | 10.7055 | 0 | 12.4602 | 0 | 19.3321 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 148.3513 | 0%
CZ 6A | 0.33043 | 0.063157 | 0.1459 | 0.26821 | 0 | 0.14601 | 0 | 0.19342 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6383 | 6.195% | CZ 6A | 10.9277 | 2.0887 | 14.7374 | 10.776 | 0 | 4.8287 | 0 | 6.3968 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 72.2177 | 6.195% | CZ 6A | 3.2018 | 0.61198 | 0 | 2.327 | 0 | 1.4148 | 0 | 1.8743 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.3019 | 6.195% | CZ 6A | 0 | 0 | 0.14737 | 0.028339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.26818 | 6.195% | CZ 6A | 33.5195 | 6.4068 | 16.108 | 27.4591 | 0 | 14.8114 | 0 | 19.6216 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 168.5698 | 6.195%
CZ 6B | 0.33043 | 0.063104 | 0.14695 | 0.18539 | 0 | 0.13278 | 0 | 0.202 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5518 | 1.79% | CZ 6B | 10.9277 | 2.0869 | 14.843 | 7.4043 | 0 | 4.3913 | 0 | 6.6806 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 68.7961 | 1.79% | CZ 6B | 3.2018 | 0.61146 | 0 | 1.6148 | 0 | 1.2866 | 0 | 1.9574 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.5441 | 1.79% | CZ 6B | 0 | 0 | 0.14843 | 0.018931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25983 | 1.79% | CZ 6B | 33.5195 | 6.4014 | 16.2234 | 18.974 | 0 | 13.4699 | 0 | 20.4919 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 159.7234 | 1.79%
CZ 7 | 0.33043 | 0.06311 | 0.15777 | 0.38621 | 0 | 0.11883 | 0 | 0.1968 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7443 | 1.191% | CZ 7 | 10.9277 | 2.0871 | 15.936 | 15.4675 | 0 | 3.9298 | 0 | 6.5083 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 77.3188 | 1.191% | CZ 7 | 3.2018 | 0.61153 | 0 | 3.358 | 0 | 1.1514 | 0 | 1.9069 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.1016 | 1.191% | CZ 7 | 0 | 0 | 0.15936 | 0.040068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.2919 | 1.191% | CZ 7 | 33.5195 | 6.4021 | 17.418 | 39.5339 | 0 | 12.0543 | 0 | 19.9635 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 179.5347 | 1.191%
CZ 8 | 0.33043 | 0.062725 | 0.17237 | 0.59234 | 0 | 0.084364 | 0 | 0.19376 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.9271 | 0.2253% | CZ 8 | 10.9277 | 2.0744 | 17.4116 | 24.1463 | 0 | 2.79 | 0 | 6.4078 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 86.2202 | 0.2253% | CZ 8 | 3.2018 | 0.6078 | 0 | 5.0897 | 0 | 0.81747 | 0 | 1.8775 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 15.4663 | 0.2253% | CZ 8 | 0 | 0 | 0.17412 | 0.06775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.33434 | 0.2253% | CZ 8 | 33.5195 | 6.363 | 19.0309 | 60.6896 | 0 | 8.5581 | 0 | 19.6552 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 198.4597 | 0.2253%
Us Weighted | 0.33043 | 0.063199 | 0.12661 | 0.1195 | 0 | 0.25525 | 0 | 0.19707 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5832 | 100% | Us Weighted | 10.9277 | 2.0901 | 12.7886 | 4.8124 | 0 | 8.4415 | 0 | 6.5173 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 68.04 | 100% | Us Weighted | 3.2018 | 0.61239 | 0 | 1.0352 | 0 | 2.4733 | 0 | 1.9096 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.1043 | 100% | Us Weighted | 0 | 0 | 0.12789 | 0.012791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23315 | 100% | Us Weighted | 33.5195 | 6.4111 | 13.978 | 12.236 | 0 | 25.8933 | 0 | 19.9912 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 162.6725 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.33043 | 0.063329 | 0.095411 | 0.0020355 | 0 | 0.58925 | 0 | 0.198 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7696 | 0.5926% | CZ 1A | 10.9277 | 2.0944 | 9.6374 | 0.097862 | 0 | 19.4874 | 0 | 6.548 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 71.2552 | 0.5926% | CZ 1A | 3.2018 | 0.61365 | 0 | 0.015367 | 0 | 5.7098 | 0 | 1.9186 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 15.3311 | 0.5926% | CZ 1A | 0 | 0 | 0.096374 | 0.00045414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.1893 | 0.5926% | CZ 1A | 33.5195 | 6.4243 | 10.5337 | 0.21051 | 0 | 59.7754 | 0 | 20.0853 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 181.1921 | 0.5926%
CZ 1B | 0.33043 | 0.063276 | 0.089922 | 0.0094377 | 0 | 0.52041 | 0 | 0.20774 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7124 | 0% | CZ 1B | 10.9277 | 2.0926 | 9.083 | 0.43577 | 0 | 17.2106 | 0 | 6.8702 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 69.0823 | 0% | CZ 1B | 3.2018 | 0.61313 | 0 | 0.073813 | 0 | 5.0427 | 0 | 2.0129 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.8164 | 0% | CZ 1B | 0 | 0 | 0.09083 | 0.0018385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.18514 | 0% | CZ 1B | 33.5195 | 6.4189 | 9.9278 | 0.97369 | 0 | 52.7917 | 0 | 21.0735 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 175.3485 | 0%
CZ 2A | 0.33043 | 0.063216 | 0.10803 | 0.05371 | 0 | 0.44178 | 0 | 0.19877 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6871 | 16.72% | CZ 2A | 10.9277 | 2.0907 | 10.9119 | 2.4323 | 0 | 14.6102 | 0 | 6.5737 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 70.0089 | 16.72% | CZ 2A | 3.2018 | 0.61256 | 0 | 0.42687 | 0 | 4.2808 | 0 | 1.9261 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.3201 | 16.72% | CZ 2A | 0 | 0 | 0.10912 | 0.0097542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21134 | 16.72% | CZ 2A | 33.5195 | 6.4128 | 11.9267 | 5.535 | 0 | 44.8152 | 0 | 20.1641 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 173.0167 | 16.72%
CZ 2B | 0.33043 | 0.063177 | 0.10064 | 0.023668 | 0 | 0.48071 | 0 | 0.20637 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6961 | 1.732% | CZ 2B | 10.9277 | 2.0893 | 10.1657 | 1.087 | 0 | 15.8977 | 0 | 6.825 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 69.4548 | 1.732% | CZ 2B | 3.2018 | 0.61217 | 0 | 0.18595 | 0 | 4.658 | 0 | 1.9997 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.5296 | 1.732% | CZ 2B | 0 | 0 | 0.10166 | 0.0045239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.19865 | 1.732% | CZ 2B | 33.5195 | 6.4088 | 11.1112 | 2.4411 | 0 | 48.7644 | 0 | 20.9348 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 173.8232 | 1.732%
CZ 3A | 0.33043 | 0.063256 | 0.11789 | 0.12896 | 0 | 0.34323 | 0 | 0.19744 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6723 | 15.56% | CZ 3A | 10.9277 | 2.092 | 11.9077 | 5.7957 | 0 | 11.351 | 0 | 6.5296 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 71.066 | 15.56% | CZ 3A | 3.2018 | 0.61294 | 0 | 1.0313 | 0 | 3.3258 | 0 | 1.9132 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.957 | 15.56% | CZ 3A | 0 | 0 | 0.11908 | 0.022758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23431 | 15.56% | CZ 3A | 33.5195 | 6.4169 | 13.0151 | 13.2843 | 0 | 34.818 | 0 | 20.0288 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 171.726 | 15.56%
CZ 3B | 0.33043 | 0.063263 | 0.1146 | 0.053924 | 0 | 0.31417 | 0 | 0.20541 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.5729 | 6.609% | CZ 3B | 10.9277 | 2.0922 | 11.5758 | 2.5293 | 0 | 10.3901 | 0 | 6.7931 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 66.7705 | 6.609% | CZ 3B | 3.2018 | 0.61301 | 0 | 0.41613 | 0 | 3.0443 | 0 | 1.9904 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.1376 | 6.609% | CZ 3B | 0 | 0 | 0.11576 | 0.01109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.21932 | 6.609% | CZ 3B | 33.5195 | 6.4176 | 12.6523 | 5.5686 | 0 | 31.8704 | 0 | 20.8372 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 161.509 | 6.609%
CZ 3C | 0.33043 | 0.06317 | 0.12863 | 0.044826 | 0 | 0.16933 | 0 | 0.19579 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.4233 | 1.264% | CZ 3C | 10.9277 | 2.0891 | 12.993 | 2.2883 | 0 | 5.6 | 0 | 6.4749 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 62.8355 | 1.264% | CZ 3C | 3.2018 | 0.61211 | 0 | 0.31943 | 0 | 1.6408 | 0 | 1.8971 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 11.5433 | 1.264% | CZ 3C | 0 | 0 | 0.12993 | 0.011981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.23438 | 1.264% | CZ 3C | 33.5195 | 6.4081 | 14.2014 | 4.6536 | 0 | 17.1774 | 0 | 19.8612 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 146.4646 | 1.264%
CZ 4A | 0.33043 | 0.063223 | 0.13002 | 0.22264 | 0 | 0.23932 | 0 | 0.1969 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6737 | 18.28% | CZ 4A | 10.9277 | 2.0909 | 13.1337 | 9.9882 | 0 | 7.9145 | 0 | 6.5116 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 73.0289 | 18.28% | CZ 4A | 3.2018 | 0.61262 | 0 | 1.7829 | 0 | 2.3189 | 0 | 1.9079 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.6961 | 18.28% | CZ 4A | 0 | 0 | 0.13134 | 0.039032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.26284 | 18.28% | CZ 4A | 33.5195 | 6.4135 | 14.3551 | 22.9312 | 0 | 24.2769 | 0 | 19.9736 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 172.1132 | 18.28%
CZ 4B | 0.33043 | 0.06321 | 0.12814 | 0.11903 | 0 | 0.22667 | 0 | 0.20939 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.568 | 1.181% | CZ 4B | 10.9277 | 2.0904 | 12.9432 | 5.4768 | 0 | 7.4962 | 0 | 6.9248 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 68.3216 | 1.181% | CZ 4B | 3.2018 | 0.61249 | 0 | 0.93365 | 0 | 2.1964 | 0 | 2.029 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.8453 | 1.181% | CZ 4B | 0 | 0 | 0.12943 | 0.022902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.24481 | 1.181% | CZ 4B | 33.5195 | 6.4122 | 14.147 | 12.2777 | 0 | 22.9939 | 0 | 21.2411 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 161.2347 | 1.181%
CZ 4C | 0.33043 | 0.063196 | 0.13514 | 0.16464 | 0 | 0.15234 | 0 | 0.19609 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.533 | 2.281% | CZ 4C | 10.9277 | 2.09 | 13.6501 | 7.6839 | 0 | 5.0382 | 0 | 6.4848 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 68.3372 | 2.281% | CZ 4C | 3.2018 | 0.61236 | 0 | 1.276 | 0 | 1.4762 | 0 | 1.9 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.3384 | 2.281% | CZ 4C | 0 | 0 | 0.1365 | 0.033288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.26226 | 2.281% | CZ 4C | 33.5195 | 6.4108 | 14.9196 | 16.9972 | 0 | 15.4542 | 0 | 19.8915 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 157.8362 | 2.281%
CZ 5A | 0.33043 | 0.06315 | 0.13847 | 0.3732 | 0 | 0.19474 | 0 | 0.19678 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7879 | 21.19% | CZ 5A | 10.9277 | 2.0885 | 13.9865 | 16.3055 | 0 | 6.4403 | 0 | 6.5076 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 78.7184 | 21.19% | CZ 5A | 3.2018 | 0.61191 | 0 | 3.051 | 0 | 1.887 | 0 | 1.9067 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.5304 | 21.19% | CZ 5A | 0 | 0 | 0.13986 | 0.058924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.29126 | 21.19% | CZ 5A | 33.5195 | 6.4061 | 15.2872 | 38.3815 | 0 | 19.7548 | 0 | 19.9615 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 183.954 | 21.19%
CZ 5B | 0.33043 | 0.063123 | 0.13691 | 0.21305 | 0 | 0.16809 | 0 | 0.20137 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.6041 | 5.194% | CZ 5B | 10.9277 | 2.0876 | 13.8289 | 9.6382 | 0 | 5.559 | 0 | 6.6597 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 71.1635 | 5.194% | CZ 5B | 3.2018 | 0.61166 | 0 | 1.6947 | 0 | 1.6288 | 0 | 1.9513 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.9603 | 5.194% | CZ 5B | 0 | 0 | 0.13829 | 0.038541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.2693 | 5.194% | CZ 5B | 33.5195 | 6.4034 | 15.115 | 21.9547 | 0 | 17.0516 | 0 | 20.428 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 165.1155 | 5.194%
CZ 5C | 0.33043 | 0.063084 | 0.13857 | 0.21398 | 0 | 0.11168 | 0 | 0.19111 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.54 | 0% | CZ 5C | 10.9277 | 2.0863 | 13.9968 | 9.7909 | 0 | 3.6935 | 0 | 6.3202 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 69.2777 | 0% | CZ 5C | 3.2018 | 0.61127 | 0 | 1.6863 | 0 | 1.0822 | 0 | 1.8518 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 12.3054 | 0% | CZ 5C | 0 | 0 | 0.13997 | 0.040355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.27279 | 0% | CZ 5C | 33.5195 | 6.3994 | 15.2985 | 22.0648 | 0 | 11.3293 | 0 | 19.3866 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 158.6415 | 0%
CZ 6A | 0.33043 | 0.063157 | 0.14597 | 0.44264 | 0 | 0.14554 | 0 | 0.19417 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.813 | 6.195% | CZ 6A | 10.9277 | 2.0887 | 14.744 | 19.3635 | 0 | 4.8131 | 0 | 6.4214 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 80.8207 | 6.195% | CZ 6A | 3.2018 | 0.61198 | 0 | 3.6152 | 0 | 1.4102 | 0 | 1.8815 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 14.5927 | 6.195% | CZ 6A | 0 | 0 | 0.14744 | 0.070247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.31016 | 6.195% | CZ 6A | 33.5195 | 6.4068 | 16.1152 | 45.5257 | 0 | 14.7636 | 0 | 19.6969 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 186.6712 | 6.195%
CZ 6B | 0.33043 | 0.063104 | 0.14702 | 0.33892 | 0 | 0.12793 | 0 | 0.20301 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.7015 | 1.79% | CZ 6B | 10.9277 | 2.0869 | 14.8502 | 15.06 | 0 | 4.2307 | 0 | 6.7137 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 76.3316 | 1.79% | CZ 6B | 3.2018 | 0.61146 | 0 | 2.7347 | 0 | 1.2396 | 0 | 1.9671 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.6267 | 1.79% | CZ 6B | 0 | 0 | 0.1485 | 0.057263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.29824 | 1.79% | CZ 6B | 33.5195 | 6.4014 | 16.2313 | 34.8889 | 0 | 12.9772 | 0 | 20.5935 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 175.2551 | 1.79%
CZ 7 | 0.33043 | 0.06311 | 0.15782 | 0.62928 | 0 | 0.11529 | 0 | 0.19735 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.9844 | 1.191% | CZ 7 | 10.9277 | 2.0871 | 15.9412 | 27.0696 | 0 | 3.8126 | 0 | 6.5267 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 88.8274 | 1.191% | CZ 7 | 3.2018 | 0.61153 | 0 | 5.205 | 0 | 1.1171 | 0 | 1.9123 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 15.9198 | 1.191% | CZ 7 | 0 | 0 | 0.15941 | 0.093049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.34493 | 1.191% | CZ 7 | 33.5195 | 6.4021 | 17.4238 | 64.6616 | 0 | 11.6949 | 0 | 20.02 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 204.3652 | 1.191%
CZ 8 | 0.33043 | 0.062725 | 0.1724 | 0.88777 | 0 | 0.079155 | 0 | 0.19364 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 2.2173 | 0.2253% | CZ 8 | 10.9277 | 2.0744 | 17.4142 | 38.8294 | 0 | 2.6178 | 0 | 6.4038 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 100.7297 | 0.2253% | CZ 8 | 3.2018 | 0.6078 | 0 | 7.2517 | 0 | 0.767 | 0 | 1.8763 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 17.5766 | 0.2253% | CZ 8 | 0 | 0 | 0.17414 | 0.14079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.40741 | 0.2253% | CZ 8 | 33.5195 | 6.363 | 19.0338 | 91.3069 | 0 | 8.0297 | 0 | 19.6431 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 228.5393 | 0.2253%
Us Weighted | 0.33043 | 0.063199 | 0.12667 | 0.21257 | 0 | 0.27473 | 0 | 0.19829 | 0 | 0.00017252 | 0 | 0.17196 | 0 | 0 | 0 | 0.31901 | 1.697 | 100% | Us Weighted | 10.9277 | 2.0901 | 12.7944 | 9.4237 | 0 | 9.0859 | 0 | 6.5577 | 0 | 0.0057056 | 0 | 5.687 | 0 | 0 | 0 | 16.7697 | 73.3418 | 100% | Us Weighted | 3.2018 | 0.61239 | 0 | 1.7184 | 0 | 2.6621 | 0 | 1.9214 | 0 | 0.0016717 | 0 | 1.6663 | 0 | 0 | 0 | 2.2041 | 13.9881 | 100% | Us Weighted | 0 | 0 | 0.12794 | 0.035589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0.25601 | 100% | Us Weighted | 33.5195 | 6.4111 | 13.9843 | 21.8795 | 0 | 27.8699 | 0 | 20.1149 | 0 | 0.017501 | 0 | 17.4442 | 0 | 0 | 0 | 33.1817 | 174.4225 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 43202 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 43202 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.11604 | 0.019588 | 3.9096e-05 | 0.0011613 | 0 | 0.18471 | 0 | 0.013616 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.36453 | 0.5926% | CZ 1A | 3.8377 | 0.6478 | 0.0039491 | 0.062753 | 0 | 6.1085 | 0 | 0.4503 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 12.0826 | 0.5926% | CZ 1A | 1.1244 | 0.1898 | 0 | 0.0077799 | 0 | 1.7898 | 0 | 0.13194 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.5284 | 0.5926% | CZ 1A | 0 | 0 | 3.9491e-05 | 0.000362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00040149 | 0.5926% | CZ 1A | 11.7716 | 1.9871 | 0.0043163 | 0.12101 | 0 | 18.7371 | 0 | 1.3812 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 36.9829 | 0.5926%
CZ 1B | 0.11483 | 0.019568 | 8.6879e-06 | 0.0052294 | 0 | 0.15648 | 0 | 0.014532 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.34003 | 0% | CZ 1B | 3.7975 | 0.64714 | 0.00087757 | 0.26901 | 0 | 5.175 | 0 | 0.48058 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 11.3418 | 0% | CZ 1B | 1.1127 | 0.18961 | 0 | 0.036971 | 0 | 1.5162 | 0 | 0.14081 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.281 | 0% | CZ 1B | 0 | 0 | 8.7757e-06 | 0.0014282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001437 | 0% | CZ 1B | 11.6484 | 1.985 | 0.00095918 | 0.54315 | 0 | 15.8736 | 0 | 1.4741 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 34.5059 | 0%
CZ 2A | 0.11499 | 0.019548 | 7.1675e-05 | 0.030444 | 0 | 0.14255 | 0 | 0.01424 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.35122 | 16.72% | CZ 2A | 3.8028 | 0.64649 | 0.0072399 | 1.4482 | 0 | 4.7143 | 0 | 0.47093 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 12.0616 | 16.72% | CZ 2A | 1.1142 | 0.18942 | 0 | 0.23205 | 0 | 1.3813 | 0 | 0.13798 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.3396 | 16.72% | CZ 2A | 0 | 0 | 7.2399e-05 | 0.006562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066344 | 16.72% | CZ 2A | 11.6646 | 1.983 | 0.0079132 | 3.1465 | 0 | 14.4607 | 0 | 1.4445 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 35.6879 | 16.72%
CZ 2B | 0.11422 | 0.019535 | 3.4752e-05 | 0.014762 | 0 | 0.15764 | 0 | 0.016529 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.35211 | 1.732% | CZ 2B | 3.7775 | 0.64605 | 0.0035103 | 0.71838 | 0 | 5.2134 | 0 | 0.54664 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 11.8772 | 1.732% | CZ 2B | 1.1068 | 0.18929 | 0 | 0.1102 | 0 | 1.5275 | 0 | 0.16016 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.3787 | 1.732% | CZ 2B | 0 | 0 | 3.5103e-05 | 0.0034225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034576 | 1.732% | CZ 2B | 11.5872 | 1.9817 | 0.0038367 | 1.5278 | 0 | 15.9914 | 0 | 1.6768 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 35.7492 | 1.732%
CZ 3A | 0.1145 | 0.019561 | 6.2987e-05 | 0.056577 | 0 | 0.11456 | 0 | 0.012753 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.3474 | 15.56% | CZ 3A | 3.7867 | 0.64692 | 0.0063624 | 2.7851 | 0 | 3.7887 | 0 | 0.42177 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 12.4073 | 15.56% | CZ 3A | 1.1095 | 0.18955 | 0 | 0.41787 | 0 | 1.1101 | 0 | 0.12358 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.2353 | 15.56% | CZ 3A | 0 | 0 | 6.3624e-05 | 0.013589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013653 | 15.56% | CZ 3A | 11.6154 | 1.9844 | 0.0069541 | 5.8599 | 0 | 11.6215 | 0 | 1.2937 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 35.3625 | 15.56%
CZ 3B | 0.11437 | 0.019561 | 4.344e-05 | 0.027688 | 0 | 0.10077 | 0 | 0.01426 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.30607 | 6.609% | CZ 3B | 3.7824 | 0.64692 | 0.0043878 | 1.4372 | 0 | 3.3325 | 0 | 0.47159 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 10.6466 | 6.609% | CZ 3B | 1.1082 | 0.18955 | 0 | 0.19392 | 0 | 0.97641 | 0 | 0.13817 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.891 | 6.609% | CZ 3B | 0 | 0 | 4.3878e-05 | 0.0077533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077972 | 6.609% | CZ 3B | 11.602 | 1.9844 | 0.0047959 | 2.8776 | 0 | 10.2221 | 0 | 1.4465 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 31.1179 | 6.609%
CZ 3C | 0.11448 | 0.019535 | 0.0001086 | 0.02839 | 0 | 0.053296 | 0 | 0.013775 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.25896 | 1.264% | CZ 3C | 3.7859 | 0.64605 | 0.01097 | 1.526 | 0 | 1.7626 | 0 | 0.45557 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 9.1588 | 1.264% | CZ 3C | 1.1092 | 0.18929 | 0 | 0.19135 | 0 | 0.51643 | 0 | 0.13348 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.4245 | 1.264% | CZ 3C | 0 | 0 | 0.0001097 | 0.0087296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088393 | 1.264% | CZ 3C | 11.6127 | 1.9817 | 0.01199 | 2.9574 | 0 | 5.4065 | 0 | 1.3974 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 26.3483 | 1.264%
CZ 4A | 0.11875 | 0.019548 | 0.00011729 | 0.10319 | 0 | 0.069036 | 0 | 0.013317 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.35334 | 18.28% | CZ 4A | 3.9272 | 0.64649 | 0.011847 | 4.9936 | 0 | 2.2831 | 0 | 0.44043 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 13.2743 | 18.28% | CZ 4A | 1.1507 | 0.18942 | 0 | 0.77446 | 0 | 0.66894 | 0 | 0.12904 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.1972 | 18.28% | CZ 4A | 0 | 0 | 0.00011847 | 0.023503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023622 | 18.28% | CZ 4A | 12.0462 | 1.983 | 0.012949 | 10.6767 | 0 | 7.0032 | 0 | 1.351 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 36.0536 | 18.28%
CZ 4B | 0.11828 | 0.019548 | 9.7739e-05 | 0.061671 | 0 | 0.06244 | 0 | 0.017226 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.30864 | 1.181% | CZ 4B | 3.9116 | 0.64649 | 0.0098726 | 3.1013 | 0 | 2.065 | 0 | 0.56968 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 11.2756 | 1.181% | CZ 4B | 1.1461 | 0.18942 | 0 | 0.44616 | 0 | 0.60503 | 0 | 0.16691 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.8383 | 1.181% | CZ 4B | 0 | 0 | 9.8726e-05 | 0.015785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015884 | 1.181% | CZ 4B | 11.9984 | 1.983 | 0.010791 | 6.3961 | 0 | 6.3341 | 0 | 1.7474 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 31.4505 | 1.181%
CZ 4C | 0.1178 | 0.019548 | 0.00012815 | 0.0856 | 0 | 0.036276 | 0 | 0.012037 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.30077 | 2.281% | CZ 4C | 3.8958 | 0.64649 | 0.012944 | 4.3048 | 0 | 1.1997 | 0 | 0.39807 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 11.4295 | 2.281% | CZ 4C | 1.1415 | 0.18942 | 0 | 0.61924 | 0 | 0.35151 | 0 | 0.11663 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.703 | 2.281% | CZ 4C | 0 | 0 | 0.00012944 | 0.021913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022042 | 2.281% | CZ 4C | 11.95 | 1.983 | 0.014148 | 8.8779 | 0 | 3.68 | 0 | 1.221 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 30.7067 | 2.281%
CZ 5A | 0.11878 | 0.019528 | 0.00011294 | 0.1624 | 0 | 0.056156 | 0 | 0.012767 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.39912 | 21.19% | CZ 5A | 3.9281 | 0.64583 | 0.011408 | 7.61 | 0 | 1.8572 | 0 | 0.42221 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 15.4464 | 21.19% | CZ 5A | 1.1509 | 0.18923 | 0 | 1.2543 | 0 | 0.54414 | 0 | 0.12371 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.547 | 21.19% | CZ 5A | 0 | 0 | 0.00011408 | 0.033291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033405 | 21.19% | CZ 5A | 12.0489 | 1.981 | 0.012469 | 16.77 | 0 | 5.6966 | 0 | 1.2951 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 40.7847 | 21.19%
CZ 5B | 0.11755 | 0.019522 | 9.3395e-05 | 0.10437 | 0 | 0.044239 | 0 | 0.013623 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.32878 | 5.194% | CZ 5B | 3.8877 | 0.64561 | 0.0094339 | 5.0815 | 0 | 1.463 | 0 | 0.45052 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 12.5095 | 5.194% | CZ 5B | 1.1391 | 0.18916 | 0 | 0.77889 | 0 | 0.42867 | 0 | 0.132 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.9525 | 5.194% | CZ 5B | 0 | 0 | 9.4339e-05 | 0.024232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024326 | 5.194% | CZ 5B | 11.9251 | 1.9803 | 0.010311 | 10.8028 | 0 | 4.4877 | 0 | 1.3819 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 33.5687 | 5.194%
CZ 5C | 0.11613 | 0.019508 | 0.0001086 | 0.1082 | 0 | 0.024671 | 0 | 0.0097144 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.30771 | 0% | CZ 5C | 3.8405 | 0.64517 | 0.01097 | 5.2753 | 0 | 0.8159 | 0 | 0.32127 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 11.8808 | 0% | CZ 5C | 1.1253 | 0.18903 | 0 | 0.80635 | 0 | 0.23906 | 0 | 0.094131 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 2.7385 | 0% | CZ 5C | 0 | 0 | 0.0001097 | 0.025232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025342 | 0% | CZ 5C | 11.7803 | 1.979 | 0.01199 | 11.1995 | 0 | 2.5027 | 0 | 0.98545 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 31.4396 | 0%
CZ 6A | 0.11824 | 0.019535 | 0.00013032 | 0.19386 | 0 | 0.039899 | 0 | 0.011426 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.41247 | 6.195% | CZ 6A | 3.9103 | 0.64605 | 0.013164 | 9.0615 | 0 | 1.3195 | 0 | 0.37788 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 16.3001 | 6.195% | CZ 6A | 1.1457 | 0.18929 | 0 | 1.5004 | 0 | 0.38662 | 0 | 0.11072 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.6175 | 6.195% | CZ 6A | 0 | 0 | 0.00013164 | 0.039405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039537 | 6.195% | CZ 6A | 11.9944 | 1.9817 | 0.014388 | 20.015 | 0 | 4.0475 | 0 | 1.1591 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 42.1926 | 6.195%
CZ 6B | 0.11783 | 0.019515 | 0.00011946 | 0.15838 | 0 | 0.031658 | 0 | 0.013742 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.37063 | 1.79% | CZ 6B | 3.8969 | 0.64539 | 0.012067 | 7.5755 | 0 | 1.047 | 0 | 0.45447 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 14.603 | 1.79% | CZ 6B | 1.1418 | 0.1891 | 0 | 1.2013 | 0 | 0.30676 | 0 | 0.13316 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.2568 | 1.79% | CZ 6B | 0 | 0 | 0.00012067 | 0.034756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034877 | 1.79% | CZ 6B | 11.9533 | 1.9797 | 0.013189 | 16.3748 | 0 | 3.2115 | 0 | 1.394 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 37.9071 | 1.79%
CZ 7 | 0.1208 | 0.019515 | 0.00014552 | 0.29069 | 0 | 0.029521 | 0 | 0.013941 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.504 | 1.191% | CZ 7 | 3.995 | 0.64539 | 0.014699 | 13.0432 | 0 | 0.97631 | 0 | 0.46105 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 20.1074 | 1.191% | CZ 7 | 1.1705 | 0.1891 | 0 | 2.3276 | 0 | 0.28606 | 0 | 0.13509 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 4.3931 | 1.191% | CZ 7 | 0 | 0 | 0.00014699 | 0.050991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051138 | 1.191% | CZ 7 | 12.2542 | 1.9797 | 0.016066 | 29.9411 | 0 | 2.9947 | 0 | 1.4142 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 51.5806 | 1.191%
CZ 8 | 0.1171 | 0.019402 | 0.00015204 | 0.34101 | 0 | 0.016688 | 0 | 0.011008 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.53474 | 0.2253% | CZ 8 | 3.8728 | 0.64166 | 0.015357 | 16.2005 | 0 | 0.5519 | 0 | 0.36406 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 22.618 | 0.2253% | CZ 8 | 1.1347 | 0.188 | 0 | 2.6022 | 0 | 0.16171 | 0 | 0.10667 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 4.478 | 0.2253% | CZ 8 | 0 | 0 | 0.00015357 | 0.073194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073347 | 0.2253% | CZ 8 | 11.8793 | 1.9682 | 0.016786 | 35.242 | 0 | 1.6929 | 0 | 1.1167 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 54.8965 | 0.2253%
Us Weighted | 0.11691 | 0.019543 | 9.3445e-05 | 0.09679 | 0 | 0.084625 | 0 | 0.013318 | 0 | 0 | 0 | 0.0061312 | 0 | 0 | 0 | 0.023251 | 0.36066 | 100% | Us Weighted | 3.8664 | 0.64632 | 0.0094389 | 4.6151 | 0 | 2.7987 | 0 | 0.44045 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76893 | 13.3481 | 100% | Us Weighted | 1.1328 | 0.18937 | 0 | 0.73619 | 0 | 0.82 | 0 | 0.12905 | 0 | 0 | 0 | 0.059411 | 0 | 0 | 0 | 0.2253 | 3.2922 | 100% | Us Weighted | 0 | 0 | 9.4389e-05 | 0.021025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02112 | 100% | Us Weighted | 11.8597 | 1.9825 | 0.010317 | 10.0052 | 0 | 8.5846 | 0 | 1.351 | 0 | 0 | 0 | 0.62197 | 0 | 0 | 0 | 2.3586 | 36.774 | 100%
Building Type: | Small Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 43202 | [17 empty] | Prototype Floor Area: | 43202 | [17 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 35.12% | 30.93% | 0.04098% | 57.05% | 0% | 31.35% | 0% | 6.877% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 20.6% | 0.5926% | CZ 1A | 35.12% | 30.93% | 0.04098% | 64.12% | 0% | 31.35% | 0% | 6.877% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 16.96% | 0.5926% | CZ 1A | 35.12% | 30.93% | 0% | 50.63% | 0% | 31.35% | 0% | 6.877% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.01% | 0.5926% | CZ 1A | 0% | 0% | 0.04098% | 79.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2121% | 0.5926% | CZ 1A | 35.12% | 30.93% | 0.04098% | 57.49% | 0% | 31.35% | 0% | 6.877% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.41% | 0.5926%
CZ 1B | 34.75% | 30.92% | 0.009662% | 55.41% | 0% | 30.07% | 0% | 6.995% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 19.86% | 0% | CZ 1B | 34.75% | 30.92% | 0.009662% | 61.73% | 0% | 30.07% | 0% | 6.995% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 16.42% | 0% | CZ 1B | 34.75% | 30.92% | 0% | 50.09% | 0% | 30.07% | 0% | 6.995% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 22.14% | 0% | CZ 1B | 0% | 0% | 0.009662% | 77.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.7762% | 0% | CZ 1B | 34.75% | 30.92% | 0.009662% | 55.78% | 0% | 30.07% | 0% | 6.995% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 19.68% | 0%
CZ 2A | 34.8% | 30.92% | 0.06635% | 56.68% | 0% | 32.27% | 0% | 7.164% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 20.82% | 16.72% | CZ 2A | 34.8% | 30.92% | 0.06635% | 59.54% | 0% | 32.27% | 0% | 7.164% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 17.23% | 16.72% | CZ 2A | 34.8% | 30.92% | 0% | 54.36% | 0% | 32.27% | 0% | 7.164% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.32% | 16.72% | CZ 2A | 0% | 0% | 0.06635% | 67.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.139% | 16.72% | CZ 2A | 34.8% | 30.92% | 0.06635% | 56.85% | 0% | 32.27% | 0% | 7.164% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.63% | 16.72%
CZ 2B | 34.57% | 30.92% | 0.03453% | 62.37% | 0% | 32.79% | 0% | 8.009% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 20.76% | 1.732% | CZ 2B | 34.57% | 30.92% | 0.03453% | 66.09% | 0% | 32.79% | 0% | 8.009% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 17.1% | 1.732% | CZ 2B | 34.57% | 30.92% | 0% | 59.27% | 0% | 32.79% | 0% | 8.009% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.25% | 1.732% | CZ 2B | 0% | 0% | 0.03453% | 75.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.741% | 1.732% | CZ 2B | 34.57% | 30.92% | 0.03453% | 62.59% | 0% | 32.79% | 0% | 8.009% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.57% | 1.732%
CZ 3A | 34.65% | 30.92% | 0.05343% | 43.87% | 0% | 33.38% | 0% | 6.459% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 20.77% | 15.56% | CZ 3A | 34.65% | 30.92% | 0.05343% | 48.05% | 0% | 33.38% | 0% | 6.459% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 17.46% | 15.56% | CZ 3A | 34.65% | 30.92% | 0% | 40.52% | 0% | 33.38% | 0% | 6.459% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.18% | 15.56% | CZ 3A | 0% | 0% | 0.05343% | 59.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.827% | 15.56% | CZ 3A | 34.65% | 30.92% | 0.05343% | 44.11% | 0% | 33.38% | 0% | 6.459% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.59% | 15.56%
CZ 3B | 34.61% | 30.92% | 0.03791% | 51.35% | 0% | 32.07% | 0% | 6.942% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 19.46% | 6.609% | CZ 3B | 34.61% | 30.92% | 0.03791% | 56.82% | 0% | 32.07% | 0% | 6.942% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 15.95% | 6.609% | CZ 3B | 34.61% | 30.92% | 0% | 46.6% | 0% | 32.07% | 0% | 6.942% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 22.01% | 6.609% | CZ 3B | 0% | 0% | 0.03791% | 69.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.555% | 6.609% | CZ 3B | 34.61% | 30.92% | 0.03791% | 51.67% | 0% | 32.07% | 0% | 6.942% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 19.27% | 6.609%
CZ 3C | 34.64% | 30.92% | 0.08443% | 63.33% | 0% | 31.47% | 0% | 7.036% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 18.19% | 1.264% | CZ 3C | 34.64% | 30.92% | 0.08443% | 66.69% | 0% | 31.47% | 0% | 7.036% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 14.58% | 1.264% | CZ 3C | 34.64% | 30.92% | 0% | 59.9% | 0% | 31.47% | 0% | 7.036% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 21% | 1.264% | CZ 3C | 0% | 0% | 0.08443% | 72.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.771% | 1.264% | CZ 3C | 34.64% | 30.92% | 0.08443% | 63.55% | 0% | 31.47% | 0% | 7.036% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 17.99% | 1.264%
CZ 4A | 35.94% | 30.92% | 0.0902% | 46.35% | 0% | 28.85% | 0% | 6.764% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 21.11% | 18.28% | CZ 4A | 35.94% | 30.92% | 0.0902% | 49.99% | 0% | 28.85% | 0% | 6.764% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 18.18% | 18.28% | CZ 4A | 35.94% | 30.92% | 0% | 43.44% | 0% | 28.85% | 0% | 6.764% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.34% | 18.28% | CZ 4A | 0% | 0% | 0.0902% | 60.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.987% | 18.28% | CZ 4A | 35.94% | 30.92% | 0.0902% | 46.56% | 0% | 28.85% | 0% | 6.764% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.95% | 18.28%
CZ 4B | 35.8% | 30.93% | 0.07628% | 51.81% | 0% | 27.55% | 0% | 8.227% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 19.68% | 1.181% | CZ 4B | 35.8% | 30.93% | 0.07628% | 56.63% | 0% | 27.55% | 0% | 8.227% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 16.5% | 1.181% | CZ 4B | 35.8% | 30.93% | 0% | 47.79% | 0% | 27.55% | 0% | 8.227% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 22.1% | 1.181% | CZ 4B | 0% | 0% | 0.07628% | 68.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.488% | 1.181% | CZ 4B | 35.8% | 30.93% | 0.07628% | 52.1% | 0% | 27.55% | 0% | 8.227% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 19.51% | 1.181%
CZ 4C | 35.65% | 30.93% | 0.09483% | 51.99% | 0% | 23.81% | 0% | 6.139% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 19.62% | 2.281% | CZ 4C | 35.65% | 30.93% | 0.09483% | 56.02% | 0% | 23.81% | 0% | 6.139% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 16.73% | 2.281% | CZ 4C | 35.65% | 30.93% | 0% | 48.53% | 0% | 23.81% | 0% | 6.139% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 21.91% | 2.281% | CZ 4C | 0% | 0% | 0.09483% | 65.83% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.405% | 2.281% | CZ 4C | 35.65% | 30.93% | 0.09483% | 52.23% | 0% | 23.81% | 0% | 6.139% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 19.45% | 2.281%
CZ 5A | 35.95% | 30.92% | 0.08157% | 43.52% | 0% | 28.84% | 0% | 6.488% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 22.32% | 21.19% | CZ 5A | 35.95% | 30.92% | 0.08157% | 46.67% | 0% | 28.84% | 0% | 6.488% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 19.62% | 21.19% | CZ 5A | 35.95% | 30.92% | 0% | 41.11% | 0% | 28.84% | 0% | 6.488% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 24.41% | 21.19% | CZ 5A | 0% | 0% | 0.08157% | 56.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.47% | 21.19% | CZ 5A | 35.95% | 30.92% | 0.08157% | 43.69% | 0% | 28.84% | 0% | 6.488% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 22.17% | 21.19%
CZ 5B | 35.58% | 30.93% | 0.06822% | 48.99% | 0% | 26.32% | 0% | 6.765% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 20.5% | 5.194% | CZ 5B | 35.58% | 30.93% | 0.06822% | 52.72% | 0% | 26.32% | 0% | 6.765% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 17.58% | 5.194% | CZ 5B | 35.58% | 30.93% | 0% | 45.96% | 0% | 26.32% | 0% | 6.765% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 22.78% | 5.194% | CZ 5B | 0% | 0% | 0.06822% | 62.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.033% | 5.194% | CZ 5B | 35.58% | 30.93% | 0.06822% | 49.2% | 0% | 26.32% | 0% | 6.765% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 20.33% | 5.194%
CZ 5C | 35.14% | 30.92% | 0.07837% | 50.56% | 0% | 22.09% | 0% | 5.083% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 19.98% | 0% | CZ 5C | 35.14% | 30.92% | 0.07837% | 53.88% | 0% | 22.09% | 0% | 5.083% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 17.15% | 0% | CZ 5C | 35.14% | 30.92% | 0% | 47.82% | 0% | 22.09% | 0% | 5.083% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 22.25% | 0% | CZ 5C | 0% | 0% | 0.07837% | 62.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.29% | 0% | CZ 5C | 35.14% | 30.92% | 0.07837% | 50.76% | 0% | 22.09% | 0% | 5.083% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 19.82% | 0%
CZ 6A | 35.78% | 30.93% | 0.08928% | 43.8% | 0% | 27.42% | 0% | 5.885% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 22.75% | 6.195% | CZ 6A | 35.78% | 30.93% | 0.08928% | 46.8% | 0% | 27.42% | 0% | 5.885% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 20.17% | 6.195% | CZ 6A | 35.78% | 30.93% | 0% | 41.5% | 0% | 27.42% | 0% | 5.885% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 24.79% | 6.195% | CZ 6A | 0% | 0% | 0.08928% | 56.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.75% | 6.195% | CZ 6A | 35.78% | 30.93% | 0.08928% | 43.96% | 0% | 27.42% | 0% | 5.885% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 22.6% | 6.195%
CZ 6B | 35.66% | 30.93% | 0.08126% | 46.73% | 0% | 24.75% | 0% | 6.769% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 21.78% | 1.79% | CZ 6B | 35.66% | 30.93% | 0.08126% | 50.3% | 0% | 24.75% | 0% | 6.769% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 19.13% | 1.79% | CZ 6B | 35.66% | 30.93% | 0% | 43.93% | 0% | 24.75% | 0% | 6.769% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.9% | 1.79% | CZ 6B | 0% | 0% | 0.08126% | 60.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.69% | 1.79% | CZ 6B | 35.66% | 30.93% | 0.08126% | 46.93% | 0% | 24.75% | 0% | 6.769% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 21.63% | 1.79%
CZ 7 | 36.56% | 30.92% | 0.09221% | 46.19% | 0% | 25.61% | 0% | 7.064% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 25.4% | 1.191% | CZ 7 | 36.56% | 30.92% | 0.09221% | 48.18% | 0% | 25.61% | 0% | 7.064% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 22.64% | 1.191% | CZ 7 | 36.56% | 30.92% | 0% | 44.72% | 0% | 25.61% | 0% | 7.064% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 27.6% | 1.191% | CZ 7 | 0% | 0% | 0.09221% | 54.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.83% | 1.191% | CZ 7 | 36.56% | 30.92% | 0.09221% | 46.3% | 0% | 25.61% | 0% | 7.064% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 25.24% | 1.191%
CZ 8 | 35.44% | 30.93% | 0.08819% | 38.41% | 0% | 21.08% | 0% | 5.685% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 24.12% | 0.2253% | CZ 8 | 35.44% | 30.93% | 0.08819% | 41.72% | 0% | 21.08% | 0% | 5.685% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 22.45% | 0.2253% | CZ 8 | 35.44% | 30.93% | 0% | 35.88% | 0% | 21.08% | 0% | 5.685% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 25.48% | 0.2253% | CZ 8 | 0% | 0% | 0.08819% | 51.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18% | 0.2253% | CZ 8 | 35.44% | 30.93% | 0.08819% | 38.6% | 0% | 21.08% | 0% | 5.685% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 24.02% | 0.2253%
Us Weighted | 35.38% | 30.92% | 0.07377% | 45.53% | 0% | 30.8% | 0% | 6.717% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.288% | 21.25% | 100% | Us Weighted | 35.38% | 30.92% | 0.07377% | 48.97% | 0% | 30.8% | 0% | 6.717% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 4.585% | 18.2% | 100% | Us Weighted | 35.38% | 30.92% | 0% | 42.84% | 0% | 30.8% | 0% | 6.717% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 10.22% | 23.54% | 100% | Us Weighted | 0% | 0% | 0.07377% | 59.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.25% | 100% | Us Weighted | 35.38% | 30.92% | 0.07377% | 45.73% | 0% | 30.8% | 0% | 6.717% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 7.108% | 21.08% | 100%

## lgOffice
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Office |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Large Office | [14 empty] | Prototype Floor Area: | 498588 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.19606 | 0.039191 | 0.0097886 | 0.048275 | 0.036809 | 0.23004 | 0.022698 | 0.12572 | 0.0057228 | 0.030507 | 0 | 0.10929 | 0.0045904 | 0 | 0.85794 | 0.30673 | 2.0234 |  | STD2013 | 6.4841 | 1.2961 | 0.98874 | 4.8527 | 1.2173 | 7.6077 | 0.75066 | 4.1578 | 0.18926 | 1.0089 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 70.8369 |  | STD2013 | 1.8998 | 0.37976 | 0 | 0.0033596 | 0.35668 | 2.229 | 0.21994 | 1.2182 | 0.055453 | 0.29561 | 0 | 1.059 | 0.04448 | 0 | 8.3133 | 2.9721 | 19.0469 |  | STD2013 | 0 | 0 | 0.0098874 | 0.048412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0583 |  | STD2013 | 19.8893 | 3.9757 | 1.0807 | 5.3266 | 3.7341 | 23.3359 | 2.3026 | 12.7537 | 0.58054 | 3.0947 | 0 | 11.0871 | 0.46566 | 0 | 87.0323 | 31.1151 | 205.7739
STD2010 | 0.21908 | 0.039191 | 0.0097922 | 0.040169 | 0.036846 | 0.25274 | 0.028232 | 0.13225 | 0 | 0.034948 | 0 | 0.10953 | 0.0046198 | 0 | 0.85794 | 0.30783 | 2.0731 |  | STD2010 | 7.2453 | 1.2961 | 0.98911 | 3.9776 | 1.2186 | 8.3584 | 0.93366 | 4.3735 | 0 | 1.1558 | 0 | 3.6222 | 0.15278 | 0 | 28.3734 | 10.18 | 71.8764 |  | STD2010 | 2.1228 | 0.37976 | 0 | 0.011399 | 0.35703 | 2.449 | 0.27356 | 1.2814 | 0 | 0.33864 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9827 | 19.6158 |  | STD2010 | 0 | 0 | 0.0098911 | 0.039387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049278 |  | STD2010 | 22.2241 | 3.9757 | 1.0811 | 4.4243 | 3.7378 | 25.6384 | 2.8639 | 13.4154 | 0 | 3.5452 | 0 | 11.1106 | 0.46864 | 0 | 87.0323 | 31.2259 | 210.7434
STD2007 | 0.29548 | 0.056723 | 0.0098099 | 0.06088 | 0.0044346 | 0.32958 | 0.048336 | 0.14018 | 0 | 0.067933 | 0 | 0.11248 | 0.0082687 | 0 | 0.85794 | 0.33761 | 2.3296 |  | STD2007 | 9.772 | 1.8759 | 0.9909 | 6.0424 | 0.14666 | 10.8995 | 1.5985 | 4.6359 | 0 | 2.2467 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 81.7402 |  | STD2007 | 2.8632 | 0.54963 | 0 | 0.01528 | 0.04297 | 3.1935 | 0.46837 | 1.3583 | 0 | 0.65826 | 0 | 1.0899 | 0.080122 | 0 | 8.3133 | 3.2713 | 21.9042 |  | STD2007 | 0 | 0 | 0.009909 | 0.059902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069811 |  | STD2007 | 29.9746 | 5.7541 | 1.0831 | 6.7073 | 0.44986 | 33.4331 | 4.9034 | 14.2202 | 0 | 6.8914 | 0 | 11.4104 | 0.8388 | 0 | 87.0323 | 34.247 | 236.9456
STD2004 | 0.29548 | 0.056723 | 0.0098104 | 0.083457 | 0.0046833 | 0.33644 | 0.050271 | 0.14433 | 0 | 0.070475 | 0 | 0.11248 | 0.0082687 | 0 | 0.85794 | 0.33761 | 2.368 |  | STD2004 | 9.772 | 1.8759 | 0.99095 | 8.325 | 0.15488 | 11.1264 | 1.6625 | 4.7733 | 0 | 2.3307 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 84.5433 |  | STD2004 | 2.8632 | 0.54963 | 0 | 0.014977 | 0.04538 | 3.26 | 0.48712 | 1.3986 | 0 | 0.68289 | 0 | 1.0899 | 0.080123 | 0 | 8.3133 | 3.2713 | 22.0564 |  | STD2004 | 0 | 0 | 0.0099095 | 0.082739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092648 |  | STD2004 | 29.9746 | 5.7541 | 1.0831 | 9.2001 | 0.47509 | 34.129 | 5.0997 | 14.6415 | 0 | 7.1492 | 0 | 11.4104 | 0.8388 | 0 | 87.0323 | 34.247 | 241.0349
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 4.9087e-07 | 0.022577 | 0.0002487 | 0.0068597 | 0.0019351 | 0.0041526 | 0 | 0.0025414 | 0 | 0 | 6.6127e-08 | 0 | 0 | 0 | 0.038315 |  | 2004-2007 | 0 | 0 | 4.9583e-05 | 2.2826 | 0.0082247 | 0.22686 | 0.063998 | 0.13733 | 0 | 0.084047 | 0 | 0 | 2.1869e-06 | 0 | 0 | 0 | 2.8031 |  | 2004-2007 | 0 | 0 | 0 | -0.00030256 | 0.0024098 | 0.066469 | 0.018751 | 0.040238 | 0 | 0.024626 | 0 | 0 | 6.4076e-07 | 0 | 0 | 0 | 0.15219 |  | 2004-2007 | 0 | 0 | 4.9583e-07 | 0.022836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022837 |  | 2004-2007 | 0 | 0 | 5.4194e-05 | 2.4928 | 0.025228 | 0.69587 | 0.19631 | 0.42126 | 0 | 0.25781 | 0 | 0 | 6.7081e-06 | 0 | 0 | 0 | 4.0894
2007-2010 | 0.076402 | 0.017532 | 1.7723e-05 | 0.020711 | -0.032412 | 0.076838 | 0.020104 | 0.0079341 | 0 | 0.032985 | 0 | 0.0029559 | 0.0036489 | 0 | 0 | 0.029781 | 0.2565 |  | 2007-2010 | 2.5267 | 0.57979 | 0.0017902 | 2.0648 | -1.0719 | 2.5412 | 0.66488 | 0.26239 | 0 | 1.0909 | 0 | 0.097754 | 0.12067 | 0 | 0 | 0.9849 | 9.8638 |  | 2007-2010 | 0.74033 | 0.16988 | 0 | 0.003881 | -0.31406 | 0.74455 | 0.19481 | 0.07688 | 0 | 0.31962 | 0 | 0.028642 | 0.035357 | 0 | 0 | 0.28857 | 2.2885 |  | 2007-2010 | 0 | 0 | 1.7902e-05 | 0.020515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020533 |  | 2007-2010 | 7.7505 | 1.7784 | 0.0019567 | 2.283 | -3.2879 | 7.7947 | 2.0394 | 0.80486 | 0 | 3.3461 | 0 | 0.29985 | 0.37015 | 0 | 0 | 3.0211 | 26.2021
2010-2013 | 0.023016 | 0 | 3.6548e-06 | -0.0081053 | 3.6903e-05 | 0.022698 | 0.0055334 | 0.0065229 | -0.0057228 | 0.0044413 | 0 | 0.00023113 | 2.941e-05 | 0 | 0 | 0.001093 | 0.049778 |  | 2010-2013 | 0.76117 | 0 | 0.00036917 | -0.87508 | 0.0012204 | 0.75066 | 0.183 | 0.21572 | -0.18926 | 0.14688 | 0 | 0.0076439 | 0.00097263 | 0 | 0 | 0.036147 | 1.0394 |  | 2010-2013 | 0.22302 | 0 | 0 | 0.0080391 | 0.00035759 | 0.21994 | 0.053618 | 0.063206 | -0.055453 | 0.043036 | 0 | 0.0022396 | 0.00028498 | 0 | 0 | 0.010591 | 0.56888 |  | 2010-2013 | 0 | 0 | 3.6917e-06 | -0.0090252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0090215 |  | 2010-2013 | 2.3348 | 0 | 0.0004035 | -0.90229 | 0.0037436 | 2.3026 | 0.56133 | 0.6617 | -0.58054 | 0.45054 | 0 | 0.023447 | 0.0029834 | 0 | 0 | 0.11088 | 4.9696
2004-2013 | 0.099418 | 0.017532 | 2.1868e-05 | 0.035182 | -0.032126 | 0.1064 | 0.027573 | 0.01861 | -0.0057228 | 0.039968 | 0 | 0.003187 | 0.0036784 | 0 | 0 | 0.030874 | 0.34459 |  | 2004-2013 | 3.2879 | 0.57979 | 0.0022089 | 3.4723 | -1.0625 | 3.5187 | 0.91188 | 0.61545 | -0.18926 | 1.3218 | 0 | 0.1054 | 0.12165 | 0 | 0 | 1.021 | 13.7064 |  | 2004-2013 | 0.96335 | 0.16988 | 0 | 0.011618 | -0.3113 | 1.031 | 0.26718 | 0.18032 | -0.055453 | 0.38728 | 0 | 0.030881 | 0.035643 | 0 | 0 | 0.29916 | 3.0095 |  | 2004-2013 | 0 | 0 | 2.2089e-05 | 0.034326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034348 |  | 2004-2013 | 10.0853 | 1.7784 | 0.0024144 | 3.8735 | -3.259 | 10.7931 | 2.7971 | 1.8878 | -0.58054 | 4.0545 | 0 | 0.3233 | 0.37314 | 0 | 0 | 3.132 | 35.261
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.005004% | 27.05% | 5.31% | 2.039% | 3.849% | 2.877% |  | 3.606% |  | 0% | 0.0007997% |  | 0% | 0% | 1.618% |  | 2004-2007 | 0% | 0% | 0.005004% | 27.42% | 5.31% | 2.039% | 3.849% | 2.877% |  | 3.606% |  | 0% | 0.0007997% |  | 0% | 0% | 3.316% |  | 2004-2007 | 0% | 0% |  | -2.02% | 5.31% | 2.039% | 3.849% | 2.877% |  | 3.606% |  | 0% | 0.0007997% |  | 0% | 0% | 0.69% |  | 2004-2007 |  |  | 0.005004% | 27.6% | [12 empty] | 24.65% |  | 2004-2007 | 0% | 0% | 0.005004% | 27.1% | 5.31% | 2.039% | 3.849% | 2.877% |  | 3.606% |  | 0% | 0.0007997% |  | 0% | 0% | 1.697%
2007-2010 | 25.86% | 30.91% | 0.1807% | 34.02% | -730.9% | 23.31% | 41.59% | 5.66% |  | 48.56% |  | 2.628% | 44.13% |  | 0% | 8.821% | 11.01% |  | 2007-2010 | 25.86% | 30.91% | 0.1807% | 34.17% | -730.9% | 23.31% | 41.59% | 5.66% |  | 48.56% |  | 2.628% | 44.13% |  | 0% | 8.821% | 12.07% |  | 2007-2010 | 25.86% | 30.91% |  | 25.4% | -730.9% | 23.31% | 41.59% | 5.66% |  | 48.56% |  | 2.628% | 44.13% |  | 0% | 8.821% | 10.45% |  | 2007-2010 |  |  | 0.1807% | 34.25% | [12 empty] | 29.41% |  | 2007-2010 | 25.86% | 30.91% | 0.1807% | 34.04% | -730.9% | 23.31% | 41.59% | 5.66% |  | 48.56% |  | 2.628% | 44.13% |  | 0% | 8.821% | 11.06%
2010-2013 | 10.51% | 0% | 0.03732% | -20.18% | 0.1002% | 8.981% | 19.6% | 4.932% |  | 12.71% |  | 0.211% | 0.6366% |  | 0% | 0.3551% | 2.401% |  | 2010-2013 | 10.51% | 0% | 0.03732% | -22% | 0.1002% | 8.981% | 19.6% | 4.932% |  | 12.71% |  | 0.211% | 0.6366% |  | 0% | 0.3551% | 1.446% |  | 2010-2013 | 10.51% | 0% |  | 70.53% | 0.1002% | 8.981% | 19.6% | 4.932% |  | 12.71% |  | 0.211% | 0.6366% |  | 0% | 0.3551% | 2.9% |  | 2010-2013 |  |  | 0.03732% | -22.91% | [12 empty] | -18.31% |  | 2010-2013 | 10.51% | 0% | 0.03732% | -20.39% | 0.1002% | 8.981% | 19.6% | 4.932% |  | 12.71% |  | 0.211% | 0.6366% |  | 0% | 0.3551% | 2.358%
2004-2013 | 33.65% | 30.91% | 0.2229% | 42.16% | -686% | 31.62% | 54.85% | 12.89% |  | 56.71% |  | 2.833% | 44.49% |  | 0% | 9.145% | 14.55% |  | 2004-2013 | 33.65% | 30.91% | 0.2229% | 41.71% | -686% | 31.62% | 54.85% | 12.89% |  | 56.71% |  | 2.833% | 44.49% |  | 0% | 9.145% | 16.21% |  | 2004-2013 | 33.65% | 30.91% |  | 77.57% | -686% | 31.62% | 54.85% | 12.89% |  | 56.71% |  | 2.833% | 44.49% |  | 0% | 9.145% | 13.64% |  | 2004-2013 |  |  | 0.2229% | 41.49% | [12 empty] | 37.07% |  | 2004-2013 | 33.65% | 30.91% | 0.2229% | 42.1% | -686% | 31.62% | 54.85% | 12.89% |  | 56.71% |  | 2.833% | 44.49% |  | 0% | 9.145% | 14.63%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.19571 | 0.039167 | 0.0074489 | 0.00023487 | 0.00011442 | 0.41499 | 0.057919 | 0.12922 | 0.026856 | 0.05805 | 0 | 0.10929 | 0.0045902 | 0 | 0.85794 | 0.30673 | 2.2083 | 3.058% | CZ 1A | 6.4725 | 1.2953 | 0.75242 | 0.023725 | 0.0037839 | 13.7242 | 1.9155 | 4.2734 | 0.88815 | 1.9198 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 73.5523 | 3.058% | CZ 1A | 1.8964 | 0.37952 | 0 | 0 | 0.0011087 | 4.0211 | 0.56122 | 1.2521 | 0.26023 | 0.56249 | 0 | 1.059 | 0.044479 | 0 | 8.3133 | 2.9721 | 21.3232 | 3.058% | CZ 1A | 0 | 0 | 0.0075242 | 0.00023725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077614 | 3.058% | CZ 1A | 19.8536 | 3.9732 | 0.82239 | 0.025931 | 0.011607 | 42.0973 | 5.8755 | 13.1082 | 2.7243 | 5.8888 | 0 | 11.0871 | 0.46565 | 0 | 87.0323 | 31.1151 | 224.081 | 3.058%
CZ 1B | 0.19574 | 0.039124 | 0.0070215 | 0.0045818 | 0.010407 | 0.41836 | 0.030626 | 0.14877 | 0 | 0.050025 | 0 | 0.10929 | 0.0045897 | 0 | 0.85794 | 0.30673 | 2.1832 | 0% | CZ 1B | 6.4735 | 1.2939 | 0.70925 | 0.26601 | 0.34418 | 13.8357 | 1.0129 | 4.9201 | 0 | 1.6544 | 0 | 3.6145 | 0.15179 | 0 | 28.3734 | 10.1438 | 72.7935 | 0% | CZ 1B | 1.8967 | 0.3791 | 0 | 0.028068 | 0.10084 | 4.0538 | 0.29676 | 1.4416 | 0 | 0.48473 | 0 | 1.059 | 0.044473 | 0 | 8.3133 | 2.9721 | 21.0706 | 0% | CZ 1B | 0 | 0 | 0.0070925 | 0.0017022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087946 | 0% | CZ 1B | 19.8568 | 3.9688 | 0.7752 | 0.47989 | 1.0557 | 42.4396 | 3.1068 | 15.0919 | 0 | 5.0747 | 0 | 11.0871 | 0.46559 | 0 | 87.0323 | 31.1151 | 221.5495 | 0%
CZ 2A | 0.19597 | 0.03908 | 0.0084225 | 0.011926 | 0.00040304 | 0.32661 | 0.038722 | 0.12045 | 0.012274 | 0.043605 | 0 | 0.10929 | 0.0045908 | 0 | 0.85794 | 0.30673 | 2.076 | 9.789% | CZ 2A | 6.4809 | 1.2924 | 0.85076 | 1.2038 | 0.013329 | 10.8014 | 1.2806 | 3.9835 | 0.40591 | 1.4421 | 0 | 3.6145 | 0.15183 | 0 | 28.3734 | 10.1438 | 70.0382 | 9.789% | CZ 2A | 1.8989 | 0.37868 | 0 | 0.00012257 | 0.0039054 | 3.1648 | 0.37521 | 1.1672 | 0.11893 | 0.42253 | 0 | 1.059 | 0.044484 | 0 | 8.3133 | 2.9721 | 19.9192 | 9.789% | CZ 2A | 0 | 0 | 0.0085076 | 0.012033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020541 | 9.789% | CZ 2A | 19.8794 | 3.9644 | 0.92988 | 1.3165 | 0.040886 | 33.132 | 3.9281 | 12.219 | 1.2451 | 4.4234 | 0 | 11.0871 | 0.46571 | 0 | 87.0323 | 31.1151 | 210.7788 | 9.789%
CZ 2B | 0.19583 | 0.039045 | 0.0078528 | 0.0036999 | 0.079752 | 0.31169 | 0.040235 | 0.13752 | 0 | 0.040926 | 0 | 0.10929 | 0.0045897 | 0 | 0.85794 | 0.30673 | 2.1351 | 1.826% | CZ 2B | 6.4762 | 1.2913 | 0.79321 | 0.27611 | 2.6375 | 10.308 | 1.3306 | 4.5478 | 0 | 1.3535 | 0 | 3.6145 | 0.15179 | 0 | 28.3734 | 10.1438 | 71.2978 | 1.826% | CZ 2B | 1.8975 | 0.37834 | 0 | 0.013923 | 0.77279 | 3.0202 | 0.38987 | 1.3325 | 0 | 0.39657 | 0 | 1.059 | 0.044473 | 0 | 8.3133 | 2.9721 | 20.5907 | 1.826% | CZ 2B | 0 | 0 | 0.0079321 | 0.002286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010218 | 1.826% | CZ 2B | 19.8651 | 3.9608 | 0.86698 | 0.39561 | 8.0903 | 31.6186 | 4.0815 | 13.95 | 0 | 4.1517 | 0 | 11.0871 | 0.46559 | 0 | 87.0323 | 31.1151 | 216.6807 | 1.826%
CZ 3A | 0.19654 | 0.039187 | 0.0091879 | 0.042285 | 0.0010211 | 0.28076 | 0.028405 | 0.11944 | 0.0080948 | 0.036798 | 0 | 0.10929 | 0.0045908 | 0 | 0.85794 | 0.30673 | 2.0403 | 13.37% | CZ 3A | 6.5 | 1.296 | 0.92807 | 4.2708 | 0.03377 | 9.285 | 0.9394 | 3.95 | 0.26771 | 1.217 | 0 | 3.6145 | 0.15183 | 0 | 28.3734 | 10.1438 | 70.9712 | 13.37% | CZ 3A | 1.9045 | 0.37971 | 0 | 6.1284e-05 | 0.0098945 | 2.7205 | 0.27524 | 1.1574 | 0.078437 | 0.35657 | 0 | 1.059 | 0.044484 | 0 | 8.3133 | 2.9721 | 19.2712 | 13.37% | CZ 3A | 0 | 0 | 0.0092807 | 0.042706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051986 | 13.37% | CZ 3A | 19.9379 | 3.9752 | 1.0144 | 4.6684 | 0.10359 | 28.4806 | 2.8815 | 12.1163 | 0.82116 | 3.7329 | 0 | 11.0871 | 0.46571 | 0 | 87.0323 | 31.1151 | 207.4323 | 13.37%
CZ 3B | 0.19598 | 0.039115 | 0.0089348 | 0.0084333 | 0.10329 | 0.22718 | 0.022846 | 0.1405 | 0 | 0.028739 | 0 | 0.10929 | 0.0045897 | 0 | 0.85794 | 0.30673 | 2.0536 | 8.555% | CZ 3B | 6.4812 | 1.2936 | 0.9025 | 0.81759 | 3.4158 | 7.5133 | 0.75557 | 4.6465 | 0 | 0.95043 | 0 | 3.6145 | 0.15179 | 0 | 28.3734 | 10.1438 | 69.06 | 8.555% | CZ 3B | 1.899 | 0.37902 | 0 | 0.004886 | 1.0008 | 2.2014 | 0.22138 | 1.3614 | 0 | 0.27847 | 0 | 1.059 | 0.044473 | 0 | 8.3133 | 2.9721 | 19.7353 | 8.555% | CZ 3B | 0 | 0 | 0.009025 | 0.0080091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017034 | 8.555% | CZ 3B | 19.8804 | 3.9679 | 0.98643 | 0.92655 | 10.4777 | 23.0462 | 2.3176 | 14.2525 | 0 | 2.9153 | 0 | 11.0871 | 0.46559 | 0 | 87.0323 | 31.1151 | 208.4708 | 8.555%
CZ 3C | 0.19646 | 0.039102 | 0.010021 | 0.0038324 | 0.029277 | 0.07777 | 0.0057116 | 0.11326 | 0 | 0.015069 | 0 | 0.10929 | 0.0045902 | 0 | 0.85794 | 0.30673 | 1.7691 | 3.506% | CZ 3C | 6.4973 | 1.2932 | 1.0122 | 0.34703 | 0.96824 | 2.572 | 0.18889 | 3.7455 | 0 | 0.49835 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 59.4062 | 3.506% | CZ 3C | 1.9037 | 0.37889 | 0 | 0.0057161 | 0.28369 | 0.75358 | 0.055345 | 1.0974 | 0 | 0.14602 | 0 | 1.059 | 0.044479 | 0 | 8.3133 | 2.9721 | 17.0133 | 3.506% | CZ 3C | 0 | 0 | 0.010122 | 0.0032752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013397 | 3.506% | CZ 3C | 19.9299 | 3.9666 | 1.1063 | 0.41783 | 2.97 | 7.8892 | 0.5794 | 11.4889 | 0 | 1.5286 | 0 | 11.0871 | 0.46565 | 0 | 87.0323 | 31.1151 | 179.577 | 3.506%
CZ 4A | 0.1958 | 0.039189 | 0.010129 | 0.05712 | 0.0016128 | 0.24708 | 0.020772 | 0.12518 | 0.0063337 | 0.028938 | 0 | 0.10929 | 0.0045902 | 0 | 0.85794 | 0.30673 | 2.0107 | 34.02% | CZ 4A | 6.4755 | 1.296 | 1.0231 | 5.7495 | 0.053336 | 8.1713 | 0.68696 | 4.14 | 0.20947 | 0.95703 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 71.0459 | 34.02% | CZ 4A | 1.8973 | 0.37974 | 0 | 0.0028692 | 0.015627 | 2.3942 | 0.20128 | 1.213 | 0.061373 | 0.28041 | 0 | 1.059 | 0.044479 | 0 | 8.3133 | 2.9721 | 18.8348 | 34.02% | CZ 4A | 0 | 0 | 0.010231 | 0.057398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067629 | 34.02% | CZ 4A | 19.8629 | 3.9755 | 1.1182 | 6.3036 | 0.1636 | 25.0647 | 2.1072 | 12.6989 | 0.64251 | 2.9356 | 0 | 11.0871 | 0.46565 | 0 | 87.0323 | 31.1151 | 204.5729 | 34.02%
CZ 4B | 0.19553 | 0.03912 | 0.0099857 | 0.016047 | 0.12905 | 0.17414 | 0.012673 | 0.16163 | 0 | 0.023243 | 0 | 0.10929 | 0.0045897 | 0 | 0.85794 | 0.30673 | 2.04 | 0% | CZ 4B | 6.4664 | 1.2937 | 1.0087 | 1.4876 | 4.268 | 5.759 | 0.4191 | 5.3454 | 0 | 0.76867 | 0 | 3.6145 | 0.15179 | 0 | 28.3734 | 10.1438 | 69.1001 | 0% | CZ 4B | 1.8946 | 0.37906 | 0 | 0.01902 | 1.2505 | 1.6874 | 0.1228 | 1.5662 | 0 | 0.22522 | 0 | 1.059 | 0.044473 | 0 | 8.3133 | 2.9721 | 19.5338 | 0% | CZ 4B | 0 | 0 | 0.010087 | 0.014227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024313 | 0% | CZ 4B | 19.835 | 3.9684 | 1.1025 | 1.7541 | 13.0916 | 17.6652 | 1.2855 | 16.3964 | 0 | 2.3578 | 0 | 11.0871 | 0.46559 | 0 | 87.0323 | 31.1151 | 207.1566 | 0%
CZ 4C | 0.19644 | 0.03925 | 0.010527 | 0.02296 | 0.059069 | 0.10756 | 0.01018 | 0.12322 | 0 | 0.017284 | 0 | 0.10929 | 0.0045908 | 0 | 0.85794 | 0.30673 | 1.865 | 4.62% | CZ 4C | 6.4965 | 1.2981 | 1.0634 | 2.2721 | 1.9535 | 3.5572 | 0.33665 | 4.0751 | 0 | 0.57162 | 0 | 3.6145 | 0.15183 | 0 | 28.3734 | 10.1438 | 63.9077 | 4.62% | CZ 4C | 1.9035 | 0.38033 | 0 | 0.0067189 | 0.57237 | 1.0422 | 0.098639 | 1.194 | 0 | 0.16748 | 0 | 1.059 | 0.044484 | 0 | 8.3133 | 2.9721 | 17.7542 | 4.62% | CZ 4C | 0 | 0 | 0.010634 | 0.022492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033126 | 4.62% | CZ 4C | 19.9272 | 3.9816 | 1.1623 | 2.5287 | 5.9921 | 10.9112 | 1.0326 | 12.5 | 0 | 1.7534 | 0 | 11.0871 | 0.46571 | 0 | 87.0323 | 31.1151 | 189.4894 | 4.62%
CZ 5A | 0.19613 | 0.039343 | 0.010786 | 0.10085 | 0.091939 | 0.15802 | 0.014993 | 0.12604 | 0.0029944 | 0.026621 | 0 | 0.10929 | 0.0045902 | 0 | 0.85794 | 0.30673 | 2.0463 | 13.29% | CZ 5A | 6.4862 | 1.3011 | 1.0895 | 10.1449 | 3.0405 | 5.2259 | 0.49584 | 4.1682 | 0.099028 | 0.88038 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 75.2153 | 13.29% | CZ 5A | 1.9004 | 0.38123 | 0 | 0.0060169 | 0.89087 | 1.5312 | 0.14528 | 1.2213 | 0.029015 | 0.25795 | 0 | 1.059 | 0.044479 | 0 | 8.3133 | 2.9721 | 18.7522 | 13.29% | CZ 5A | 0 | 0 | 0.010895 | 0.10124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11214 | 13.29% | CZ 5A | 19.8956 | 3.9911 | 1.1909 | 11.1289 | 9.3265 | 16.0299 | 1.5209 | 12.7856 | 0.30376 | 2.7005 | 0 | 11.0871 | 0.46565 | 0 | 87.0323 | 31.1151 | 208.5738 | 13.29%
CZ 5B | 0.19618 | 0.039001 | 0.010668 | 0.034969 | 0.14358 | 0.13543 | 0.0081201 | 0.14001 | 0 | 0.019611 | 0 | 0.10929 | 0.0045902 | 0 | 0.85794 | 0.30673 | 2.0061 | 3.637% | CZ 5B | 6.488 | 1.2898 | 1.0776 | 3.5085 | 4.7485 | 4.4787 | 0.26854 | 4.6303 | 0 | 0.64857 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 69.4222 | 3.637% | CZ 5B | 1.901 | 0.37791 | 0 | 0.0033929 | 1.3913 | 1.3123 | 0.078683 | 1.3567 | 0 | 0.19003 | 0 | 1.059 | 0.044479 | 0 | 8.3133 | 2.9721 | 19.0002 | 3.637% | CZ 5B | 0 | 0 | 0.010776 | 0.034969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045745 | 3.637% | CZ 5B | 19.9013 | 3.9564 | 1.1778 | 3.8576 | 14.5656 | 13.7381 | 0.82373 | 14.2029 | 0 | 1.9894 | 0 | 11.0871 | 0.46565 | 0 | 87.0323 | 31.1151 | 203.913 | 3.637%
CZ 5C | 0.19846 | 0.039314 | 0.010795 | 0.033274 | 0.071349 | 0.067895 | 0.0049584 | 0.12386 | 0 | 0.013113 | 0 | 0.10929 | 0.0045925 | 0 | 0.85794 | 0.30673 | 1.8416 | 0% | CZ 5C | 6.5633 | 1.3002 | 1.0904 | 3.3162 | 2.3596 | 2.2454 | 0.16398 | 4.0961 | 0 | 0.43367 | 0 | 3.6145 | 0.15188 | 0 | 28.3734 | 10.1438 | 63.8524 | 0% | CZ 5C | 1.923 | 0.38095 | 0 | 0.0063902 | 0.69136 | 0.65789 | 0.048046 | 1.2002 | 0 | 0.12706 | 0 | 1.059 | 0.044501 | 0 | 8.3133 | 2.9721 | 17.4239 | 0% | CZ 5C | 0 | 0 | 0.010904 | 0.032944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043848 | 0% | CZ 5C | 20.1322 | 3.9882 | 1.1918 | 3.6677 | 7.2378 | 6.8875 | 0.503 | 12.5644 | 0 | 1.3302 | 0 | 11.0871 | 0.46588 | 0 | 87.0323 | 31.1151 | 187.2031 | 0%
CZ 6A | 0.19642 | 0.039416 | 0.01137 | 0.12089 | 0.10551 | 0.11802 | 0.014805 | 0.12386 | 0.001519 | 0.02126 | 0 | 0.10929 | 0.0045908 | 0 | 0.85794 | 0.30673 | 2.0316 | 4.001% | CZ 6A | 6.4957 | 1.3035 | 1.1485 | 12.1709 | 3.4892 | 3.9032 | 0.48963 | 4.0962 | 0.050237 | 0.70309 | 0 | 3.6145 | 0.15183 | 0 | 28.3734 | 10.1438 | 76.1338 | 4.001% | CZ 6A | 1.9032 | 0.38193 | 0 | 0.0057607 | 1.0223 | 1.1436 | 0.14346 | 1.2002 | 0.014719 | 0.206 | 0 | 1.059 | 0.044484 | 0 | 8.3133 | 2.9721 | 18.4102 | 4.001% | CZ 6A | 0 | 0 | 0.011485 | 0.12151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 4.001% | CZ 6A | 19.925 | 3.9984 | 1.2553 | 13.3416 | 10.7028 | 11.9727 | 1.5019 | 12.5645 | 0.1541 | 2.1566 | 0 | 11.0871 | 0.46571 | 0 | 87.0323 | 31.1151 | 207.2731 | 4.001%
CZ 6B | 0.19623 | 0.039122 | 0.011454 | 0.088988 | 0.15237 | 0.10363 | 0.0050769 | 0.14457 | 0.0014535 | 0.016329 | 0 | 0.10929 | 0.0045908 | 0 | 0.85794 | 0.30673 | 2.0378 | 0% | CZ 6B | 6.4896 | 1.2938 | 1.157 | 8.9637 | 5.039 | 3.4271 | 0.1679 | 4.781 | 0.048069 | 0.54002 | 0 | 3.6145 | 0.15183 | 0 | 28.3734 | 10.1438 | 74.1908 | 0% | CZ 6B | 1.9014 | 0.37909 | 0 | 0.0035656 | 1.4764 | 1.0041 | 0.049194 | 1.4008 | 0.014084 | 0.15822 | 0 | 1.059 | 0.044484 | 0 | 8.3133 | 2.9721 | 18.776 | 0% | CZ 6B | 0 | 0 | 0.01157 | 0.089515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10108 | 0% | CZ 6B | 19.9061 | 3.9687 | 1.2645 | 9.8214 | 15.4567 | 10.5123 | 0.51501 | 14.6653 | 0.14745 | 1.6564 | 0 | 11.0871 | 0.46571 | 0 | 87.0323 | 31.1151 | 207.6141 | 0%
CZ 7 | 0.19569 | 0.039285 | 0.01229 | 0.15918 | 0.11415 | 0.093264 | 0.0095719 | 0.13171 | 0.0012333 | 0.019271 | 0 | 0.10929 | 0.0045897 | 0 | 0.85794 | 0.30673 | 2.0542 | 0.3244% | CZ 7 | 6.4717 | 1.2992 | 1.2414 | 16.0215 | 3.7751 | 3.0844 | 0.31656 | 4.356 | 0.040786 | 0.63731 | 0 | 3.6145 | 0.15179 | 0 | 28.3734 | 10.1438 | 79.5275 | 0.3244% | CZ 7 | 1.8962 | 0.38067 | 0 | 0.0082343 | 1.1061 | 0.90372 | 0.09275 | 1.2763 | 0.01195 | 0.18673 | 0 | 1.059 | 0.044473 | 0 | 8.3133 | 2.9721 | 18.2516 | 0.3244% | CZ 7 | 0 | 0 | 0.012414 | 0.15993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17235 | 0.3244% | CZ 7 | 19.8512 | 3.9852 | 1.3569 | 17.567 | 11.5798 | 9.461 | 0.971 | 13.3615 | 0.12511 | 1.9549 | 0 | 11.0871 | 0.46559 | 0 | 87.0323 | 31.1151 | 209.9136 | 0.3244%
CZ 8 | 0.19984 | 0.039765 | 0.013429 | 0.248 | 0.14238 | 0.066527 | 0.002984 | 0.13019 | 0.00087106 | 0.016321 | 0 | 0.10929 | 0.0045925 | 0 | 0.85794 | 0.30673 | 2.1389 | 0% | CZ 8 | 6.6091 | 1.3151 | 1.3565 | 25.0236 | 4.7087 | 2.2001 | 0.098686 | 4.3055 | 0.028807 | 0.53977 | 0 | 3.6145 | 0.15188 | 0 | 28.3734 | 10.1438 | 88.4694 | 0% | CZ 8 | 1.9364 | 0.38532 | 0 | 0.0038107 | 1.3796 | 0.64463 | 0.028915 | 1.2615 | 0.0084404 | 0.15815 | 0 | 1.059 | 0.044501 | 0 | 8.3133 | 2.9721 | 18.1958 | 0% | CZ 8 | 0 | 0 | 0.013565 | 0.25011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26367 | 0% | CZ 8 | 20.2725 | 4.0339 | 1.4826 | 27.3764 | 14.4434 | 6.7486 | 0.30271 | 13.2067 | 0.088363 | 1.6557 | 0 | 11.0871 | 0.46588 | 0 | 87.0323 | 31.1151 | 219.3114 | 0%
Us Weighted | 0.19606 | 0.039191 | 0.0097886 | 0.048275 | 0.036809 | 0.23004 | 0.022698 | 0.12572 | 0.0057228 | 0.030507 | 0 | 0.10929 | 0.0045904 | 0 | 0.85794 | 0.30673 | 2.0234 | 100% | Us Weighted | 6.4841 | 1.2961 | 0.98874 | 4.8527 | 1.2173 | 7.6077 | 0.75066 | 4.1578 | 0.18926 | 1.0089 | 0 | 3.6145 | 0.15181 | 0 | 28.3734 | 10.1438 | 70.8369 | 100% | Us Weighted | 1.8998 | 0.37976 | 0 | 0.0033596 | 0.35668 | 2.229 | 0.21994 | 1.2182 | 0.055453 | 0.29561 | 0 | 1.059 | 0.04448 | 0 | 8.3133 | 2.9721 | 19.0469 | 100% | Us Weighted | 0 | 0 | 0.0098874 | 0.048412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0583 | 100% | Us Weighted | 19.8893 | 3.9757 | 1.0807 | 5.3266 | 3.7341 | 23.3359 | 2.3026 | 12.7537 | 0.58054 | 3.0947 | 0 | 11.0871 | 0.46566 | 0 | 87.0323 | 31.1151 | 205.7739 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.2208 | 0.039167 | 0.0074542 | 0.0010932 | 0.00011614 | 0.48754 | 0.068145 | 0.1419 | 0 | 0.067889 | 0 | 0.10953 | 0.0046207 | 0 | 0.85794 | 0.30783 | 2.314 | 3.058% | CZ 1A | 7.3021 | 1.2953 | 0.75295 | 0.10999 | 0.003841 | 16.1238 | 2.2537 | 4.6928 | 0 | 2.2452 | 0 | 3.6222 | 0.15281 | 0 | 28.3734 | 10.18 | 77.1079 | 3.058% | CZ 1A | 2.1395 | 0.37952 | 0 | 6.1284e-05 | 0.0011254 | 4.7242 | 0.66031 | 1.375 | 0 | 0.65784 | 0 | 1.0613 | 0.044774 | 0 | 8.3133 | 2.9827 | 22.3396 | 3.058% | CZ 1A | 0 | 0 | 0.0075295 | 0.0010978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086273 | 3.058% | CZ 1A | 22.3983 | 3.9732 | 0.82297 | 0.12063 | 0.011782 | 49.4579 | 6.9128 | 14.3945 | 0 | 6.8869 | 0 | 11.1106 | 0.46874 | 0 | 87.0323 | 31.2259 | 234.8165 | 3.058%
CZ 1B | 0.22141 | 0.039124 | 0.0070213 | 0.024387 | 0.010418 | 0.44912 | 0.031505 | 0.16044 | 0 | 0.056465 | 0 | 0.10953 | 0.0046207 | 0 | 0.85794 | 0.30783 | 2.2798 | 0% | CZ 1B | 7.3222 | 1.2939 | 0.70923 | 1.0603 | 0.34453 | 14.853 | 1.0419 | 5.3059 | 0 | 1.8674 | 0 | 3.6222 | 0.15281 | 0 | 28.3734 | 10.18 | 76.1267 | 0% | CZ 1B | 2.1454 | 0.3791 | 0 | 0.2001 | 0.10095 | 4.3519 | 0.30528 | 1.5546 | 0 | 0.54714 | 0 | 1.0613 | 0.044774 | 0 | 8.3133 | 2.9827 | 21.9865 | 0% | CZ 1B | 0 | 0 | 0.0070923 | 0.0037739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010866 | 0% | CZ 1B | 22.46 | 3.9688 | 0.77518 | 2.5074 | 1.0568 | 45.5598 | 3.196 | 16.2753 | 0 | 5.728 | 0 | 11.1106 | 0.46874 | 0 | 87.0323 | 31.2259 | 231.3647 | 0%
CZ 2A | 0.22247 | 0.03908 | 0.0084274 | 0.0099298 | 0.00038522 | 0.38373 | 0.048 | 0.13172 | 0 | 0.052684 | 0 | 0.10953 | 0.0046219 | 0 | 0.85794 | 0.30783 | 2.1763 | 9.789% | CZ 2A | 7.3575 | 1.2924 | 0.85125 | 1.0016 | 0.01274 | 12.6905 | 1.5874 | 4.3562 | 0 | 1.7423 | 0 | 3.6222 | 0.15285 | 0 | 28.3734 | 10.18 | 73.2203 | 9.789% | CZ 2A | 2.1557 | 0.37868 | 0 | 0.00020614 | 0.0037327 | 3.7183 | 0.46511 | 1.2763 | 0 | 0.5105 | 0 | 1.0613 | 0.044785 | 0 | 8.3133 | 2.9827 | 20.9107 | 9.789% | CZ 2A | 0 | 0 | 0.0085125 | 0.010009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018521 | 9.789% | CZ 2A | 22.5684 | 3.9644 | 0.93042 | 1.0961 | 0.039078 | 38.9267 | 4.8692 | 13.362 | 0 | 5.3445 | 0 | 11.1106 | 0.46886 | 0 | 87.0323 | 31.2259 | 220.9385 | 9.789%
CZ 2B | 0.22306 | 0.039045 | 0.0078528 | 0.012163 | 0.083642 | 0.33955 | 0.05064 | 0.15088 | 0 | 0.047468 | 0 | 0.10953 | 0.0046224 | 0 | 0.85794 | 0.30783 | 2.2342 | 1.826% | CZ 2B | 7.3769 | 1.2913 | 0.79321 | 0.64512 | 2.7662 | 11.2295 | 1.6748 | 4.9896 | 0 | 1.5698 | 0 | 3.6222 | 0.15287 | 0 | 28.3734 | 10.18 | 74.6648 | 1.826% | CZ 2B | 2.1614 | 0.37834 | 0 | 0.083223 | 0.81048 | 3.2902 | 0.4907 | 1.462 | 0 | 0.45996 | 0 | 1.0613 | 0.044791 | 0 | 8.3133 | 2.9827 | 21.5384 | 1.826% | CZ 2B | 0 | 0 | 0.0079321 | 0.0036108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011543 | 1.826% | CZ 2B | 22.6278 | 3.9608 | 0.86698 | 1.2659 | 8.4849 | 34.4451 | 5.1371 | 15.3052 | 0 | 4.8153 | 0 | 11.1106 | 0.46891 | 0 | 87.0323 | 31.2259 | 226.7469 | 1.826%
CZ 3A | 0.21974 | 0.039187 | 0.0091924 | 0.023356 | 0.0010056 | 0.31688 | 0.035056 | 0.12655 | 0 | 0.043759 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 2.0946 | 13.37% | CZ 3A | 7.267 | 1.296 | 0.92853 | 2.3587 | 0.033257 | 10.4798 | 1.1593 | 4.1853 | 0 | 1.4472 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 71.4834 | 13.37% | CZ 3A | 2.1292 | 0.37971 | 0 | 6.6855e-05 | 0.0097441 | 3.0706 | 0.33968 | 1.2263 | 0 | 0.42402 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 19.9814 | 13.37% | CZ 3A | 0 | 0 | 0.0092853 | 0.023585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03287 | 13.37% | CZ 3A | 22.2906 | 3.9752 | 1.0149 | 2.5785 | 0.10201 | 32.1456 | 3.5562 | 12.8379 | 0 | 4.439 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 212.7775 | 13.37%
CZ 3B | 0.21894 | 0.039115 | 0.0089346 | 0.01536 | 0.10424 | 0.24359 | 0.030787 | 0.15035 | 0 | 0.031846 | 0 | 0.10953 | 0.0046196 | 0 | 0.85794 | 0.30783 | 2.1231 | 8.555% | CZ 3B | 7.2405 | 1.2936 | 0.90248 | 0.95696 | 3.4475 | 8.056 | 1.0182 | 4.9724 | 0 | 1.0532 | 0 | 3.6222 | 0.15278 | 0 | 28.3734 | 10.18 | 71.2691 | 8.555% | CZ 3B | 2.1214 | 0.37902 | 0 | 0.084794 | 1.0101 | 2.3604 | 0.29832 | 1.4569 | 0 | 0.30859 | 0 | 1.0613 | 0.044763 | 0 | 8.3133 | 2.9827 | 20.4216 | 8.555% | CZ 3B | 0 | 0 | 0.0090248 | 0.0066756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0157 | 8.555% | CZ 3B | 22.2094 | 3.9679 | 0.98641 | 1.6173 | 10.5748 | 24.7109 | 3.1231 | 15.2524 | 0 | 3.2306 | 0 | 11.1106 | 0.46862 | 0 | 87.0323 | 31.2259 | 215.5103 | 8.555%
CZ 3C | 0.21953 | 0.039102 | 0.010025 | 0.0043157 | 0.029323 | 0.081615 | 0.0085444 | 0.12489 | 0 | 0.017913 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 1.8152 | 3.506% | CZ 3C | 7.2601 | 1.2932 | 1.0126 | 0.37397 | 0.96975 | 2.6991 | 0.28258 | 4.1304 | 0 | 0.59242 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 60.9425 | 3.506% | CZ 3C | 2.1272 | 0.37889 | 0 | 0.008836 | 0.28413 | 0.79083 | 0.082794 | 1.2102 | 0 | 0.17358 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 17.4586 | 3.506% | CZ 3C | 0 | 0 | 0.010126 | 0.0034382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013564 | 3.506% | CZ 3C | 22.2696 | 3.9666 | 1.1068 | 0.46829 | 2.9746 | 8.2792 | 0.86677 | 12.6695 | 0 | 1.8172 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 184.2562 | 3.506%
CZ 4A | 0.21792 | 0.039189 | 0.010133 | 0.044179 | 0.0015121 | 0.26522 | 0.0252 | 0.12988 | 0 | 0.032602 | 0 | 0.10953 | 0.004619 | 0 | 0.85794 | 0.30783 | 2.0457 | 34.02% | CZ 4A | 7.2068 | 1.296 | 1.0235 | 4.4608 | 0.050008 | 8.7711 | 0.83339 | 4.2955 | 0 | 1.0782 | 0 | 3.6222 | 0.15276 | 0 | 28.3734 | 10.18 | 71.3436 | 34.02% | CZ 4A | 2.1116 | 0.37974 | 0 | 0.00023956 | 0.014652 | 2.5699 | 0.24418 | 1.2586 | 0 | 0.31591 | 0 | 1.0613 | 0.044757 | 0 | 8.3133 | 2.9827 | 19.2968 | 34.02% | CZ 4A | 0 | 0 | 0.010235 | 0.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054835 | 34.02% | CZ 4A | 22.106 | 3.9755 | 1.1187 | 4.8773 | 0.1534 | 26.9042 | 2.5563 | 13.1759 | 0 | 3.3073 | 0 | 11.1106 | 0.46856 | 0 | 87.0323 | 31.2259 | 208.012 | 34.02%
CZ 4B | 0.21747 | 0.03912 | 0.0099896 | 0.027176 | 0.13209 | 0.19133 | 0.018661 | 0.16743 | 0 | 0.027385 | 0 | 0.10953 | 0.0046184 | 0 | 0.85794 | 0.30783 | 2.1106 | 0% | CZ 4B | 7.192 | 1.2937 | 1.0091 | 2.2059 | 4.3685 | 6.3275 | 0.61714 | 5.5371 | 0 | 0.90565 | 0 | 3.6222 | 0.15274 | 0 | 28.3734 | 10.18 | 71.785 | 0% | CZ 4B | 2.1072 | 0.37906 | 0 | 0.076883 | 1.28 | 1.854 | 0.18082 | 1.6223 | 0 | 0.26535 | 0 | 1.0613 | 0.044752 | 0 | 8.3133 | 2.9827 | 20.1677 | 0% | CZ 4B | 0 | 0 | 0.010091 | 0.019435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029526 | 0% | CZ 4B | 22.0608 | 3.9684 | 1.1029 | 2.9292 | 13.3999 | 19.409 | 1.893 | 16.9843 | 0 | 2.778 | 0 | 11.1106 | 0.46851 | 0 | 87.0323 | 31.2259 | 214.3629 | 0%
CZ 4C | 0.21894 | 0.03925 | 0.010531 | 0.028156 | 0.058777 | 0.10702 | 0.013471 | 0.12946 | 0 | 0.019575 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 1.9051 | 4.62% | CZ 4C | 7.2408 | 1.2981 | 1.0637 | 2.8063 | 1.9438 | 3.5394 | 0.44549 | 4.2816 | 0 | 0.64737 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 65.5949 | 4.62% | CZ 4C | 2.1215 | 0.38033 | 0 | 0.0053762 | 0.56954 | 1.037 | 0.13053 | 1.2545 | 0 | 0.18968 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 18.0906 | 4.62% | CZ 4C | 0 | 0 | 0.010637 | 0.02788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038517 | 4.62% | CZ 4C | 22.2103 | 3.9816 | 1.1627 | 3.1035 | 5.9625 | 10.8568 | 1.3665 | 13.1332 | 0 | 1.9857 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 193.6004 | 4.62%
CZ 5A | 0.21824 | 0.039343 | 0.01079 | 0.087837 | 0.091378 | 0.16965 | 0.018621 | 0.12947 | 0 | 0.029277 | 0 | 0.10953 | 0.004619 | 0 | 0.85794 | 0.30783 | 2.0745 | 13.29% | CZ 5A | 7.2174 | 1.3011 | 1.0899 | 8.8462 | 3.022 | 5.6104 | 0.61583 | 4.2817 | 0 | 0.96823 | 0 | 3.6222 | 0.15276 | 0 | 28.3734 | 10.18 | 75.281 | 13.29% | CZ 5A | 2.1147 | 0.38123 | 0 | 0.0037439 | 0.88544 | 1.6438 | 0.18044 | 1.2545 | 0 | 0.28369 | 0 | 1.0613 | 0.044757 | 0 | 8.3133 | 2.9827 | 19.1497 | 13.29% | CZ 5A | 0 | 0 | 0.010899 | 0.088334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099233 | 13.29% | CZ 5A | 22.1385 | 3.9911 | 1.1912 | 9.6941 | 9.2697 | 17.2093 | 1.889 | 13.1336 | 0 | 2.9699 | 0 | 11.1106 | 0.46856 | 0 | 87.0323 | 31.2259 | 211.3239 | 13.29%
CZ 5B | 0.21861 | 0.039001 | 0.010672 | 0.044601 | 0.14467 | 0.13632 | 0.012089 | 0.1435 | 0 | 0.021573 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 2.0509 | 3.637% | CZ 5B | 7.2299 | 1.2898 | 1.0779 | 4.2586 | 4.7844 | 4.5082 | 0.3998 | 4.7458 | 0 | 0.71345 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 71.3362 | 3.637% | CZ 5B | 2.1183 | 0.37791 | 0 | 0.035155 | 1.4018 | 1.3209 | 0.11714 | 1.3905 | 0 | 0.20904 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 19.3729 | 3.637% | CZ 5B | 0 | 0 | 0.010779 | 0.041387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052166 | 3.637% | CZ 5B | 22.1769 | 3.9564 | 1.1782 | 4.8916 | 14.6755 | 13.8283 | 1.2263 | 14.5572 | 0 | 2.1884 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 208.5163 | 3.637%
CZ 5C | 0.22204 | 0.039314 | 0.010798 | 0.039469 | 0.070791 | 0.06832 | 0.0070145 | 0.12744 | 0 | 0.014544 | 0 | 0.10953 | 0.0046224 | 0 | 0.85794 | 0.30783 | 1.8796 | 0% | CZ 5C | 7.3432 | 1.3002 | 1.0907 | 3.9625 | 2.3412 | 2.2594 | 0.23198 | 4.2146 | 0 | 0.48099 | 0 | 3.6222 | 0.15287 | 0 | 28.3734 | 10.18 | 65.5531 | 0% | CZ 5C | 2.1515 | 0.38095 | 0 | 0.0034597 | 0.68595 | 0.66201 | 0.067969 | 1.2349 | 0 | 0.14093 | 0 | 1.0613 | 0.044791 | 0 | 8.3133 | 2.9827 | 17.7298 | 0% | CZ 5C | 0 | 0 | 0.010907 | 0.039507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050414 | 0% | CZ 5C | 22.5244 | 3.9882 | 1.1921 | 4.3543 | 7.1812 | 6.9306 | 0.71157 | 12.9277 | 0 | 1.4754 | 0 | 11.1106 | 0.46891 | 0 | 87.0323 | 31.2259 | 191.1232 | 0%
CZ 6A | 0.21869 | 0.039416 | 0.011373 | 0.10532 | 0.1048 | 0.12501 | 0.018844 | 0.12677 | 0 | 0.022736 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 2.0529 | 4.001% | CZ 6A | 7.2323 | 1.3035 | 1.1488 | 10.6104 | 3.466 | 4.1343 | 0.6232 | 4.1925 | 0 | 0.7519 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 75.7912 | 4.001% | CZ 6A | 2.119 | 0.38193 | 0 | 0.0040559 | 1.0155 | 1.2113 | 0.1826 | 1.2284 | 0 | 0.2203 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 18.7653 | 4.001% | CZ 6A | 0 | 0 | 0.011488 | 0.10597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11745 | 4.001% | CZ 6A | 22.1842 | 3.9984 | 1.2556 | 11.6245 | 10.6317 | 12.6814 | 1.9116 | 12.8599 | 0 | 2.3064 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 209.2913 | 4.001%
CZ 6B | 0.21866 | 0.039122 | 0.011457 | 0.076878 | 0.15272 | 0.10881 | 0.0079683 | 0.14774 | 0 | 0.017681 | 0 | 0.10953 | 0.0046201 | 0 | 0.85794 | 0.30783 | 2.0609 | 0% | CZ 6B | 7.2312 | 1.2938 | 1.1573 | 7.6113 | 5.0508 | 3.5984 | 0.26352 | 4.8859 | 0 | 0.58472 | 0 | 3.6222 | 0.15279 | 0 | 28.3734 | 10.18 | 74.0054 | 0% | CZ 6B | 2.1187 | 0.37909 | 0 | 0.021973 | 1.4799 | 1.0543 | 0.077212 | 1.4316 | 0 | 0.17132 | 0 | 1.0613 | 0.044768 | 0 | 8.3133 | 2.9827 | 19.1362 | 0% | CZ 6B | 0 | 0 | 0.011573 | 0.075364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086936 | 0% | CZ 6B | 22.181 | 3.9687 | 1.2649 | 8.4673 | 15.4927 | 11.0376 | 0.80833 | 14.9871 | 0 | 1.7936 | 0 | 11.1106 | 0.46868 | 0 | 87.0323 | 31.2259 | 209.8386 | 0%
CZ 7 | 0.21864 | 0.039285 | 0.012297 | 0.15795 | 0.11323 | 0.095427 | 0.012034 | 0.13121 | 0 | 0.019257 | 0 | 0.10953 | 0.0046196 | 0 | 0.85794 | 0.30783 | 2.0792 | 0.3244% | CZ 7 | 7.2307 | 1.2992 | 1.2421 | 15.9197 | 3.7447 | 3.1559 | 0.398 | 4.3392 | 0 | 0.63686 | 0 | 3.6222 | 0.15278 | 0 | 28.3734 | 10.18 | 80.2947 | 0.3244% | CZ 7 | 2.1186 | 0.38067 | 0 | 0.0049083 | 1.0972 | 0.92468 | 0.11661 | 1.2714 | 0 | 0.1866 | 0 | 1.0613 | 0.044763 | 0 | 8.3133 | 2.9827 | 18.5027 | 0.3244% | CZ 7 | 0 | 0 | 0.012421 | 0.15903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17145 | 0.3244% | CZ 7 | 22.1792 | 3.9852 | 1.3577 | 17.4333 | 11.4866 | 9.6804 | 1.2208 | 13.3101 | 0 | 1.9535 | 0 | 11.1106 | 0.46862 | 0 | 87.0323 | 31.2259 | 212.4442 | 0.3244%
CZ 8 | 0.22449 | 0.039765 | 0.013437 | 0.27132 | 0.13968 | 0.068991 | 0.0043191 | 0.12875 | 0 | 0.015454 | 0 | 0.10953 | 0.0046247 | 0 | 0.85794 | 0.30783 | 2.1861 | 0% | CZ 8 | 7.4243 | 1.3151 | 1.3573 | 27.3447 | 4.6193 | 2.2816 | 0.14284 | 4.2579 | 0 | 0.51108 | 0 | 3.6222 | 0.15295 | 0 | 28.3734 | 10.18 | 91.5826 | 0% | CZ 8 | 2.1753 | 0.38532 | 0 | 0.0087858 | 1.3535 | 0.66852 | 0.041851 | 1.2475 | 0 | 0.14974 | 0 | 1.0613 | 0.044813 | 0 | 8.3133 | 2.9827 | 18.4327 | 0% | CZ 8 | 0 | 0 | 0.013573 | 0.27315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28672 | 0% | CZ 8 | 22.7733 | 4.0339 | 1.4835 | 29.9469 | 14.1693 | 6.9987 | 0.43814 | 13.0605 | 0 | 1.5677 | 0 | 11.1106 | 0.46915 | 0 | 87.0323 | 31.2259 | 224.3099 | 0%
Us Weighted | 0.21908 | 0.039191 | 0.0097922 | 0.040169 | 0.036846 | 0.25274 | 0.028232 | 0.13225 | 0 | 0.034948 | 0 | 0.10953 | 0.0046198 | 0 | 0.85794 | 0.30783 | 2.0731 | 100% | Us Weighted | 7.2453 | 1.2961 | 0.98911 | 3.9776 | 1.2186 | 8.3584 | 0.93366 | 4.3735 | 0 | 1.1558 | 0 | 3.6222 | 0.15278 | 0 | 28.3734 | 10.18 | 71.8764 | 100% | Us Weighted | 2.1228 | 0.37976 | 0 | 0.011399 | 0.35703 | 2.449 | 0.27356 | 1.2814 | 0 | 0.33864 | 0 | 1.0613 | 0.044765 | 0 | 8.3133 | 2.9827 | 19.6158 | 100% | Us Weighted | 0 | 0 | 0.0098911 | 0.039387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049278 | 100% | Us Weighted | 22.2241 | 3.9757 | 1.0811 | 4.4243 | 3.7378 | 25.6384 | 2.8639 | 13.4154 | 0 | 3.5452 | 0 | 11.1106 | 0.46864 | 0 | 87.0323 | 31.2259 | 210.7434 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29548 | 0.056825 | 0.0074685 | 0.0031778 | 0.00011212 | 0.56221 | 0.12745 | 0.15387 | 0 | 0.1126 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.6355 | 3.058% | CZ 1A | 9.772 | 1.8793 | 0.75439 | 0.32072 | 0.0037079 | 18.5929 | 4.2148 | 5.0888 | 0 | 3.7237 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 87.8821 | 3.058% | CZ 1A | 2.8632 | 0.55062 | 0 | 3.8999e-05 | 0.0010864 | 5.4477 | 1.2349 | 1.491 | 0 | 1.091 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 25.4342 | 3.058% | CZ 1A | 0 | 0 | 0.0075439 | 0.0032059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01075 | 3.058% | CZ 1A | 29.9746 | 5.7645 | 0.82455 | 0.35081 | 0.011373 | 57.0318 | 12.9286 | 15.6094 | 0 | 11.4221 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 267.4461 | 3.058%
CZ 1B | 0.29548 | 0.056776 | 0.0070364 | 0.031315 | 0.010343 | 0.49136 | 0.055636 | 0.17155 | 0 | 0.087504 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.5233 | 0% | CZ 1B | 9.772 | 1.8777 | 0.71075 | 1.7617 | 0.34207 | 16.2499 | 1.84 | 5.6735 | 0 | 2.8939 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 84.6531 | 0% | CZ 1B | 2.8632 | 0.55015 | 0 | 0.19988 | 0.10023 | 4.7612 | 0.5391 | 1.6623 | 0 | 0.8479 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 24.2786 | 0% | CZ 1B | 0 | 0 | 0.0071075 | 0.010795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017902 | 0% | CZ 1B | 29.9746 | 5.7595 | 0.77685 | 3.2725 | 1.0493 | 49.8449 | 5.6438 | 17.4028 | 0 | 8.8766 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 256.1294 | 0%
CZ 2A | 0.29548 | 0.056727 | 0.0084432 | 0.021258 | 0.00080896 | 0.45133 | 0.089395 | 0.14363 | 0 | 0.094252 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.4776 | 9.789% | CZ 2A | 9.772 | 1.876 | 0.85285 | 2.1443 | 0.026754 | 14.9263 | 2.9564 | 4.7499 | 0 | 3.1171 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 83.9533 | 9.789% | CZ 2A | 2.8632 | 0.54968 | 0 | 0.00042899 | 0.0078387 | 4.3734 | 0.86623 | 1.3917 | 0 | 0.91329 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 23.7204 | 9.789% | CZ 2A | 0 | 0 | 0.0085285 | 0.021428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029956 | 9.789% | CZ 2A | 29.9746 | 5.7545 | 0.93216 | 2.3466 | 0.082064 | 45.7847 | 9.0685 | 14.5699 | 0 | 9.5612 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 251.6028 | 9.789%
CZ 2B | 0.29548 | 0.056688 | 0.0078686 | 0.016272 | 0.001891 | 0.42143 | 0.055967 | 0.16406 | 0 | 0.077631 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.4136 | 1.826% | CZ 2B | 9.772 | 1.8748 | 0.79481 | 1.2882 | 0.062539 | 13.9374 | 1.8509 | 5.4257 | 0 | 2.5674 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 81.1053 | 1.826% | CZ 2B | 2.8632 | 0.5493 | 0 | 0.050704 | 0.018324 | 4.0836 | 0.54232 | 1.5897 | 0 | 0.75223 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 23.204 | 1.826% | CZ 2B | 0 | 0 | 0.0079481 | 0.011151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019099 | 1.826% | CZ 2B | 29.9746 | 5.7506 | 0.86873 | 1.7496 | 0.19183 | 42.7513 | 5.6775 | 16.6428 | 0 | 7.8751 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 245.0107 | 1.826%
CZ 3A | 0.29548 | 0.05676 | 0.0092086 | 0.050829 | 0.0018899 | 0.37048 | 0.064503 | 0.13712 | 0 | 0.08284 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.3854 | 13.37% | CZ 3A | 9.772 | 1.8771 | 0.93016 | 5.1309 | 0.062501 | 12.2524 | 2.1332 | 4.5348 | 0 | 2.7396 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 82.9644 | 13.37% | CZ 3A | 2.8632 | 0.54999 | 0 | 0.00047913 | 0.018313 | 3.5899 | 0.62503 | 1.3287 | 0 | 0.8027 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 22.533 | 13.37% | CZ 3A | 0 | 0 | 0.0093016 | 0.051293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060594 | 13.37% | CZ 3A | 29.9746 | 5.7579 | 1.0167 | 5.6113 | 0.19172 | 37.5828 | 6.5434 | 13.9101 | 0 | 8.4035 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 242.5205 | 13.37%
CZ 3B | 0.29548 | 0.056766 | 0.0089509 | 0.028064 | 0.030282 | 0.32997 | 0.035291 | 0.15741 | 0 | 0.050405 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.3089 | 8.555% | CZ 3B | 9.772 | 1.8773 | 0.90414 | 1.8091 | 1.0015 | 10.9124 | 1.1671 | 5.2056 | 0 | 1.667 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 77.8479 | 8.555% | CZ 3B | 2.8632 | 0.55005 | 0 | 0.14628 | 0.29343 | 3.1973 | 0.34196 | 1.5252 | 0 | 0.48841 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 22.1605 | 8.555% | CZ 3B | 0 | 0 | 0.0090414 | 0.013098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02214 | 8.555% | CZ 3B | 29.9746 | 5.7585 | 0.98822 | 2.9631 | 3.0719 | 33.4727 | 3.58 | 15.9677 | 0 | 5.1132 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 234.4185 | 8.555%
CZ 3C | 0.29548 | 0.056682 | 0.010043 | 0.013735 | 0.0002869 | 0.19717 | 0.014138 | 0.12825 | 0 | 0.033692 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.0658 | 3.506% | CZ 3C | 9.772 | 1.8745 | 1.0144 | 1.3815 | 0.0094883 | 6.5206 | 0.46757 | 4.2413 | 0 | 1.1143 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 69.9274 | 3.506% | CZ 3C | 2.8632 | 0.54923 | 0 | 0.00084126 | 0.00278 | 1.9105 | 0.137 | 1.2427 | 0 | 0.32647 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 19.7874 | 3.506% | CZ 3C | 0 | 0 | 0.010144 | 0.013786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023931 | 3.506% | CZ 3C | 29.9746 | 5.7499 | 1.1088 | 1.5157 | 0.029104 | 20.0013 | 1.4342 | 13.0097 | 0 | 3.4179 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 209.7697 | 3.506%
CZ 4A | 0.29548 | 0.056734 | 0.010151 | 0.065204 | 0.0014167 | 0.32521 | 0.045113 | 0.13644 | 0 | 0.077374 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.3294 | 34.02% | CZ 4A | 9.772 | 1.8763 | 1.0254 | 6.5812 | 0.046852 | 10.7553 | 1.4919 | 4.5121 | 0 | 2.5589 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 82.1515 | 34.02% | CZ 4A | 2.8632 | 0.54974 | 0 | 0.00071869 | 0.013728 | 3.1513 | 0.43714 | 1.322 | 0 | 0.74974 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 21.8422 | 34.02% | CZ 4A | 0 | 0 | 0.010254 | 0.065787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076041 | 34.02% | CZ 4A | 29.9746 | 5.7552 | 1.1207 | 7.1981 | 0.14371 | 32.9906 | 4.5764 | 13.8405 | 0 | 7.849 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 236.9773 | 34.02%
CZ 4B | 0.29548 | 0.056721 | 0.010008 | 0.05184 | 0.056403 | 0.29041 | 0.022495 | 0.17556 | 0 | 0.042267 | 0 | 0.11248 | 0.00827 | 0 | 0.85794 | 0.33761 | 2.3175 | 0% | CZ 4B | 9.772 | 1.8758 | 1.0109 | 3.6839 | 1.8653 | 9.6041 | 0.74395 | 5.806 | 0 | 1.3978 | 0 | 3.7199 | 0.2735 | 0 | 28.3734 | 11.1649 | 79.2916 | 0% | CZ 4B | 2.8632 | 0.54961 | 0 | 0.22142 | 0.54653 | 2.814 | 0.21797 | 1.7012 | 0 | 0.40956 | 0 | 1.0899 | 0.080135 | 0 | 8.3133 | 3.2713 | 22.0781 | 0% | CZ 4B | 0 | 0 | 0.010109 | 0.029282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039391 | 0% | CZ 4B | 29.9746 | 5.7539 | 1.1049 | 5.5186 | 5.7217 | 29.4596 | 2.282 | 17.8094 | 0 | 4.2877 | 0 | 11.4104 | 0.83893 | 0 | 87.0323 | 34.247 | 235.4411 | 0%
CZ 4C | 0.29548 | 0.056705 | 0.01055 | 0.050743 | 0.0006796 | 0.21648 | 0.017829 | 0.13518 | 0 | 0.032702 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.1326 | 4.62% | CZ 4C | 9.772 | 1.8753 | 1.0656 | 5.1186 | 0.022475 | 7.1592 | 0.58962 | 4.4706 | 0 | 1.0815 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 74.6867 | 4.62% | CZ 4C | 2.8632 | 0.54946 | 0 | 0.00099168 | 0.0065852 | 2.0976 | 0.17276 | 1.3099 | 0 | 0.31688 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.072 | 4.62% | CZ 4C | 0 | 0 | 0.010656 | 0.051152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061808 | 4.62% | CZ 4C | 29.9746 | 5.7523 | 1.1648 | 5.6013 | 0.06894 | 21.9602 | 1.8086 | 13.7132 | 0 | 3.3174 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 216.8898 | 4.62%
CZ 5A | 0.29548 | 0.056665 | 0.010809 | 0.11691 | 0.0014989 | 0.26977 | 0.035809 | 0.13724 | 0 | 0.048825 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.2893 | 13.29% | CZ 5A | 9.772 | 1.874 | 1.0918 | 11.797 | 0.049571 | 8.9216 | 1.1843 | 4.5388 | 0 | 1.6147 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 84.3755 | 13.29% | CZ 5A | 2.8632 | 0.54908 | 0 | 0.0017772 | 0.014524 | 2.614 | 0.34698 | 1.3299 | 0 | 0.47311 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 20.9472 | 13.29% | CZ 5A | 0 | 0 | 0.010918 | 0.11791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12883 | 13.29% | CZ 5A | 29.9746 | 5.7483 | 1.1934 | 12.9061 | 0.15205 | 27.3659 | 3.6326 | 13.9222 | 0 | 4.953 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 233.3768 | 13.29%
CZ 5B | 0.29548 | 0.05664 | 0.010691 | 0.066905 | 0.018357 | 0.25581 | 0.016603 | 0.14916 | 0 | 0.036776 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.2227 | 3.637% | CZ 5B | 9.772 | 1.8732 | 1.0799 | 6.54 | 0.60708 | 8.4599 | 0.54909 | 4.9331 | 0 | 1.2162 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 78.562 | 3.637% | CZ 5B | 2.8632 | 0.54883 | 0 | 0.031115 | 0.17787 | 2.4787 | 0.16088 | 1.4454 | 0 | 0.35635 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 20.817 | 3.637% | CZ 5B | 0 | 0 | 0.010799 | 0.064338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075136 | 3.637% | CZ 5B | 29.9746 | 5.7457 | 1.1803 | 7.3578 | 1.8622 | 25.9497 | 1.6843 | 15.1317 | 0 | 3.7307 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 226.1454 | 3.637%
CZ 5C | 0.29548 | 0.056607 | 0.010817 | 0.066391 | 0.00080839 | 0.183 | 0.011282 | 0.13068 | 0 | 0.024122 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.0955 | 0% | CZ 5C | 9.772 | 1.8721 | 1.0926 | 6.705 | 0.026735 | 6.0522 | 0.37311 | 4.3218 | 0 | 0.79774 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 74.545 | 0% | CZ 5C | 2.8632 | 0.54851 | 0 | 0.00016157 | 0.0078332 | 1.7733 | 0.10932 | 1.2663 | 0 | 0.23374 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 19.557 | 0% | CZ 5C | 0 | 0 | 0.010926 | 0.067045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077971 | 0% | CZ 5C | 29.9746 | 5.7424 | 1.1942 | 7.3297 | 0.082005 | 18.5645 | 1.1445 | 13.2566 | 0 | 2.447 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 213.264 | 0%
CZ 6A | 0.29548 | 0.056669 | 0.011394 | 0.13963 | 0.001914 | 0.2334 | 0.023392 | 0.13357 | 0 | 0.037798 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.2495 | 4.001% | CZ 6A | 9.772 | 1.8741 | 1.1509 | 14.0973 | 0.0633 | 7.719 | 0.77361 | 4.4172 | 0 | 1.25 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 84.6492 | 4.001% | CZ 6A | 2.8632 | 0.54911 | 0 | 0.00095825 | 0.018547 | 2.2616 | 0.22667 | 1.2942 | 0 | 0.36626 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.3353 | 4.001% | CZ 6A | 0 | 0 | 0.011509 | 0.14094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15245 | 4.001% | CZ 6A | 29.9746 | 5.7487 | 1.2579 | 15.4148 | 0.19416 | 23.6772 | 2.373 | 13.5494 | 0 | 3.8344 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 229.5526 | 4.001%
CZ 6B | 0.29548 | 0.056626 | 0.011478 | 0.10141 | 0.041337 | 0.23958 | 0.012028 | 0.15283 | 0 | 0.029612 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.2567 | 0% | CZ 6B | 9.772 | 1.8727 | 1.1594 | 9.8819 | 1.3671 | 7.9232 | 0.39779 | 5.0542 | 0 | 0.97931 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 81.9392 | 0% | CZ 6B | 2.8632 | 0.5487 | 0 | 0.051551 | 0.40054 | 2.3215 | 0.11655 | 1.4809 | 0 | 0.28694 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.8244 | 0% | CZ 6B | 0 | 0 | 0.011594 | 0.09706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10865 | 0% | CZ 6B | 29.9746 | 5.7443 | 1.2672 | 11.1483 | 4.1933 | 24.3034 | 1.2202 | 15.5031 | 0 | 3.0039 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 229.8869 | 0%
CZ 7 | 0.29548 | 0.05663 | 0.01232 | 0.19728 | 0.0022234 | 0.21145 | 0.016818 | 0.13836 | 0 | 0.031559 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.2784 | 0.3244% | CZ 7 | 9.772 | 1.8728 | 1.2444 | 19.9142 | 0.07353 | 6.9929 | 0.5562 | 4.5756 | 0 | 1.0437 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 89.577 | 0.3244% | CZ 7 | 2.8632 | 0.54873 | 0 | 0.0018441 | 0.021544 | 2.0489 | 0.16296 | 1.3406 | 0 | 0.30581 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.0483 | 0.3244% | CZ 7 | 0 | 0 | 0.012444 | 0.19908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21152 | 0.3244% | CZ 7 | 29.9746 | 5.7447 | 1.3601 | 21.7786 | 0.22554 | 21.4498 | 1.7061 | 14.0352 | 0 | 3.2015 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 233.0047 | 0.3244%
CZ 8 | 0.29548 | 0.056282 | 0.013461 | 0.30441 | 0.0042449 | 0.18861 | 0.0079476 | 0.13568 | 0 | 0.024131 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.3465 | 0% | CZ 8 | 9.772 | 1.8613 | 1.3597 | 30.7102 | 0.14039 | 6.2376 | 0.26284 | 4.4871 | 0 | 0.79804 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 99.1609 | 0% | CZ 8 | 2.8632 | 0.54536 | 0 | 0.0055267 | 0.041132 | 1.8276 | 0.077011 | 1.3147 | 0 | 0.23382 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 19.663 | 0% | CZ 8 | 0 | 0 | 0.013597 | 0.30691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32051 | 0% | CZ 8 | 29.9746 | 5.7094 | 1.4861 | 33.6035 | 0.43062 | 19.1331 | 0.80623 | 13.7638 | 0 | 2.4479 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 240.8838 | 0%
Us Weighted | 0.29548 | 0.056723 | 0.0098099 | 0.06088 | 0.0044346 | 0.32958 | 0.048336 | 0.14018 | 0 | 0.067933 | 0 | 0.11248 | 0.0082687 | 0 | 0.85794 | 0.33761 | 2.3296 | 100% | Us Weighted | 9.772 | 1.8759 | 0.9909 | 6.0424 | 0.14666 | 10.8995 | 1.5985 | 4.6359 | 0 | 2.2467 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 81.7402 | 100% | Us Weighted | 2.8632 | 0.54963 | 0 | 0.01528 | 0.04297 | 3.1935 | 0.46837 | 1.3583 | 0 | 0.65826 | 0 | 1.0899 | 0.080122 | 0 | 8.3133 | 3.2713 | 21.9042 | 100% | Us Weighted | 0 | 0 | 0.009909 | 0.059902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069811 | 100% | Us Weighted | 29.9746 | 5.7541 | 1.0831 | 6.7073 | 0.44986 | 33.4331 | 4.9034 | 14.2202 | 0 | 6.8914 | 0 | 11.4104 | 0.8388 | 0 | 87.0323 | 34.247 | 236.9456 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29548 | 0.056825 | 0.0074687 | 0.0032603 | 0.00013109 | 0.58747 | 0.13425 | 0.15667 | 0 | 0.11867 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.6765 | 3.058% | CZ 1A | 9.772 | 1.8793 | 0.75441 | 0.3283 | 0.0043353 | 19.4286 | 4.4399 | 5.1813 | 0 | 3.9246 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 89.2444 | 3.058% | CZ 1A | 2.8632 | 0.55062 | 0 | 0.00014485 | 0.0012702 | 5.6925 | 1.3009 | 1.5181 | 0 | 1.1499 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 25.8313 | 3.058% | CZ 1A | 0 | 0 | 0.0075441 | 0.0032781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010822 | 3.058% | CZ 1A | 29.9746 | 5.7645 | 0.82457 | 0.35981 | 0.013298 | 59.595 | 13.619 | 15.8929 | 0 | 12.0384 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 271.6106 | 3.058%
CZ 1B | 0.29548 | 0.056776 | 0.0070362 | 0.033437 | 0.011326 | 0.49621 | 0.057155 | 0.17762 | 0 | 0.095979 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.5473 | 0% | CZ 1B | 9.772 | 1.8777 | 0.71073 | 1.8728 | 0.37457 | 16.4103 | 1.8902 | 5.8742 | 0 | 3.1742 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 85.4883 | 0% | CZ 1B | 2.8632 | 0.55015 | 0 | 0.21461 | 0.10975 | 4.8082 | 0.55382 | 1.7211 | 0 | 0.93002 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 24.5055 | 0% | CZ 1B | 0 | 0 | 0.0071073 | 0.011403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01851 | 0% | CZ 1B | 29.9746 | 5.7595 | 0.77683 | 3.4931 | 1.1489 | 50.3368 | 5.7979 | 18.0185 | 0 | 9.7364 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 258.5713 | 0%
CZ 2A | 0.29548 | 0.056727 | 0.0084428 | 0.039724 | 0.00091706 | 0.47659 | 0.093794 | 0.14951 | 0 | 0.098799 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.5363 | 9.789% | CZ 2A | 9.772 | 1.876 | 0.85281 | 4.01 | 0.030328 | 15.7614 | 3.1019 | 4.9446 | 0 | 3.2674 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 87.1482 | 9.789% | CZ 2A | 2.8632 | 0.54968 | 0 | 0.00036213 | 0.0088861 | 4.6181 | 0.90885 | 1.4488 | 0 | 0.95734 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 24.1098 | 9.789% | CZ 2A | 0 | 0 | 0.0085281 | 0.040088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048616 | 9.789% | CZ 2A | 29.9746 | 5.7545 | 0.93212 | 4.3854 | 0.093029 | 48.3464 | 9.5147 | 15.1671 | 0 | 10.0224 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 257.7189 | 9.789%
CZ 2B | 0.29548 | 0.056688 | 0.0078684 | 0.026814 | 0.0022648 | 0.4478 | 0.061278 | 0.17017 | 0 | 0.086357 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.471 | 1.826% | CZ 2B | 9.772 | 1.8748 | 0.79479 | 2.3196 | 0.074899 | 14.8095 | 2.0266 | 5.6277 | 0 | 2.8559 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 83.6874 | 1.826% | CZ 2B | 2.8632 | 0.5493 | 0 | 0.055467 | 0.021945 | 4.3391 | 0.59378 | 1.6489 | 0 | 0.83678 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 23.6631 | 1.826% | CZ 2B | 0 | 0 | 0.0079479 | 0.021302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02925 | 1.826% | CZ 2B | 29.9746 | 5.7506 | 0.86871 | 2.909 | 0.22974 | 45.4265 | 6.2163 | 17.2622 | 0 | 8.7603 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 250.9266 | 1.826%
CZ 3A | 0.29548 | 0.05676 | 0.0092092 | 0.06639 | 0.0022193 | 0.37898 | 0.067881 | 0.14019 | 0 | 0.085313 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.4187 | 13.37% | CZ 3A | 9.772 | 1.8771 | 0.93022 | 6.703 | 0.073396 | 12.5334 | 2.2449 | 4.6362 | 0 | 2.8214 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 85.1233 | 13.37% | CZ 3A | 2.8632 | 0.54999 | 0 | 0.0004457 | 0.021505 | 3.6722 | 0.65775 | 1.3584 | 0 | 0.82667 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 22.7048 | 13.37% | CZ 3A | 0 | 0 | 0.0093022 | 0.067014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076317 | 13.37% | CZ 3A | 29.9746 | 5.7579 | 1.0167 | 7.3293 | 0.22514 | 38.4448 | 6.886 | 14.221 | 0 | 8.6544 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 246.0384 | 13.37%
CZ 3B | 0.29548 | 0.056766 | 0.0089509 | 0.032244 | 0.030846 | 0.33344 | 0.03621 | 0.15969 | 0 | 0.052156 | 0 | 0.11248 | 0.00827 | 0 | 0.85794 | 0.33761 | 2.3221 | 8.555% | CZ 3B | 9.772 | 1.8773 | 0.90414 | 2.2683 | 1.0201 | 11.0275 | 1.1975 | 5.2813 | 0 | 1.7249 | 0 | 3.7199 | 0.2735 | 0 | 28.3734 | 11.1649 | 78.6047 | 8.555% | CZ 3B | 2.8632 | 0.55005 | 0 | 0.14101 | 0.29889 | 3.231 | 0.35087 | 1.5474 | 0 | 0.50538 | 0 | 1.0899 | 0.080135 | 0 | 8.3133 | 3.2713 | 22.2425 | 8.555% | CZ 3B | 0 | 0 | 0.0090414 | 0.01787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026911 | 8.555% | CZ 3B | 29.9746 | 5.7585 | 0.98822 | 3.4294 | 3.1291 | 33.8256 | 3.6732 | 16.1998 | 0 | 5.2909 | 0 | 11.4104 | 0.83893 | 0 | 87.0323 | 34.247 | 235.798 | 8.555%
CZ 3C | 0.29548 | 0.056682 | 0.010043 | 0.029576 | 0.00034325 | 0.20115 | 0.014638 | 0.13489 | 0 | 0.03559 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.0947 | 3.506% | CZ 3C | 9.772 | 1.8745 | 1.0144 | 2.9805 | 0.011352 | 6.6524 | 0.48411 | 4.4611 | 0 | 1.177 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 71.9592 | 3.506% | CZ 3C | 2.8632 | 0.54923 | 0 | 0.00099168 | 0.003326 | 1.9491 | 0.14184 | 1.3071 | 0 | 0.34487 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 19.9143 | 3.506% | CZ 3C | 0 | 0 | 0.010144 | 0.029772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039916 | 3.506% | CZ 3C | 29.9746 | 5.7499 | 1.1088 | 3.2644 | 0.03482 | 20.4055 | 1.485 | 13.684 | 0 | 3.6104 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 212.846 | 3.506%
CZ 4A | 0.29548 | 0.056734 | 0.010152 | 0.091109 | 0.0016398 | 0.328 | 0.046545 | 0.14044 | 0 | 0.079831 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.3662 | 34.02% | CZ 4A | 9.772 | 1.8763 | 1.0254 | 9.1967 | 0.05423 | 10.8475 | 1.5393 | 4.6445 | 0 | 2.6401 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 85.1277 | 34.02% | CZ 4A | 2.8632 | 0.54974 | 0 | 0.00089697 | 0.015889 | 3.1783 | 0.45101 | 1.3608 | 0 | 0.77355 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 21.948 | 34.02% | CZ 4A | 0 | 0 | 0.010254 | 0.091936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10219 | 34.02% | CZ 4A | 29.9746 | 5.7552 | 1.1208 | 10.058 | 0.16634 | 33.2736 | 4.7217 | 14.2464 | 0 | 8.0983 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 240.9434 | 34.02%
CZ 4B | 0.29548 | 0.056721 | 0.010008 | 0.067515 | 0.056822 | 0.29258 | 0.022876 | 0.17829 | 0 | 0.043408 | 0 | 0.11248 | 0.00827 | 0 | 0.85794 | 0.33761 | 2.34 | 0% | CZ 4B | 9.772 | 1.8758 | 1.0109 | 5.2849 | 1.8792 | 9.6759 | 0.75654 | 5.8963 | 0 | 1.4356 | 0 | 3.7199 | 0.2735 | 0 | 28.3734 | 11.1649 | 81.1189 | 0% | CZ 4B | 2.8632 | 0.54961 | 0 | 0.2189 | 0.5506 | 2.835 | 0.22166 | 1.7276 | 0 | 0.42062 | 0 | 1.0899 | 0.080135 | 0 | 8.3133 | 3.2713 | 22.1418 | 0% | CZ 4B | 0 | 0 | 0.010109 | 0.045378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055487 | 0% | CZ 4B | 29.9746 | 5.7539 | 1.1049 | 7.2515 | 5.7642 | 29.6798 | 2.3206 | 18.0861 | 0 | 4.4034 | 0 | 11.4104 | 0.83893 | 0 | 87.0323 | 34.247 | 237.8678 | 0%
CZ 4C | 0.29548 | 0.056705 | 0.01055 | 0.071635 | 0.00077274 | 0.21742 | 0.01808 | 0.13848 | 0 | 0.033625 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.159 | 4.62% | CZ 4C | 9.772 | 1.8753 | 1.0657 | 7.228 | 0.025556 | 7.1903 | 0.59792 | 4.5798 | 0 | 1.112 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 76.9783 | 4.62% | CZ 4C | 2.8632 | 0.54946 | 0 | 0.0011198 | 0.0074877 | 2.1067 | 0.17519 | 1.3419 | 0 | 0.32582 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 20.1255 | 4.62% | CZ 4C | 0 | 0 | 0.010657 | 0.072242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082899 | 4.62% | CZ 4C | 29.9746 | 5.7523 | 1.1648 | 7.9078 | 0.078389 | 22.0554 | 1.834 | 14.0481 | 0 | 3.411 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 219.7551 | 4.62%
CZ 5A | 0.29548 | 0.056665 | 0.01081 | 0.15456 | 0.0017381 | 0.2734 | 0.036825 | 0.14219 | 0 | 0.050622 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.3386 | 13.29% | CZ 5A | 9.772 | 1.874 | 1.092 | 15.6008 | 0.057481 | 9.0416 | 1.2179 | 4.7023 | 0 | 1.6741 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 88.5638 | 13.29% | CZ 5A | 2.8632 | 0.54908 | 0 | 0.0015655 | 0.016842 | 2.6492 | 0.35683 | 1.3778 | 0 | 0.49051 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 21.0596 | 13.29% | CZ 5A | 0 | 0 | 0.01092 | 0.15595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16687 | 13.29% | CZ 5A | 29.9746 | 5.7483 | 1.1935 | 17.0622 | 0.17632 | 27.734 | 3.7357 | 14.4239 | 0 | 5.1352 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 238.7122 | 13.29%
CZ 5B | 0.29548 | 0.05664 | 0.010691 | 0.092955 | 0.01864 | 0.25698 | 0.016743 | 0.15299 | 0 | 0.037821 | 0 | 0.11248 | 0.0082682 | 0 | 0.85794 | 0.33761 | 2.2552 | 3.637% | CZ 5B | 9.772 | 1.8732 | 1.0799 | 9.1659 | 0.61645 | 8.4988 | 0.55371 | 5.0595 | 0 | 1.2508 | 0 | 3.7199 | 0.27344 | 0 | 28.3734 | 11.1649 | 81.4019 | 3.637% | CZ 5B | 2.8632 | 0.54883 | 0 | 0.031884 | 0.18062 | 2.4901 | 0.16223 | 1.4824 | 0 | 0.36648 | 0 | 1.0899 | 0.080118 | 0 | 8.3133 | 3.2713 | 20.8804 | 3.637% | CZ 5B | 0 | 0 | 0.010799 | 0.09057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10137 | 3.637% | CZ 5B | 29.9746 | 5.7457 | 1.1804 | 10.2331 | 1.8909 | 26.0692 | 1.6984 | 15.5195 | 0 | 3.8366 | 0 | 11.4104 | 0.83876 | 0 | 87.0323 | 34.247 | 229.677 | 3.637%
CZ 5C | 0.29548 | 0.056607 | 0.010818 | 0.09467 | 0.00089463 | 0.18263 | 0.011334 | 0.13461 | 0 | 0.024419 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.1278 | 0% | CZ 5C | 9.772 | 1.8721 | 1.0927 | 9.561 | 0.029587 | 6.0397 | 0.37484 | 4.4518 | 0 | 0.80757 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 77.533 | 0% | CZ 5C | 2.8632 | 0.54851 | 0 | 0.00023399 | 0.0086688 | 1.7696 | 0.10983 | 1.3044 | 0 | 0.23662 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 19.5957 | 0% | CZ 5C | 0 | 0 | 0.010927 | 0.095602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10653 | 0% | CZ 5C | 29.9746 | 5.7424 | 1.1944 | 10.4518 | 0.090754 | 18.526 | 1.1498 | 13.6555 | 0 | 2.4771 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 216.7908 | 0%
CZ 6A | 0.29548 | 0.056669 | 0.011395 | 0.18178 | 0.0022366 | 0.23416 | 0.023664 | 0.13851 | 0 | 0.038863 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.2991 | 4.001% | CZ 6A | 9.772 | 1.8741 | 1.151 | 18.3552 | 0.073967 | 7.7439 | 0.7826 | 4.5808 | 0 | 1.2853 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 89.1506 | 4.001% | CZ 6A | 2.8632 | 0.54911 | 0 | 0.00088026 | 0.021672 | 2.2689 | 0.2293 | 1.3422 | 0 | 0.37658 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.4065 | 4.001% | CZ 6A | 0 | 0 | 0.01151 | 0.18352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19503 | 4.001% | CZ 6A | 29.9746 | 5.7487 | 1.2581 | 20.0682 | 0.22689 | 23.7535 | 2.4006 | 14.0512 | 0 | 3.9424 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 234.9526 | 4.001%
CZ 6B | 0.29548 | 0.056626 | 0.011479 | 0.13953 | 0.042137 | 0.23261 | 0.011845 | 0.15684 | 0 | 0.02965 | 0 | 0.11248 | 0.0082694 | 0 | 0.85794 | 0.33761 | 2.2925 | 0% | CZ 6B | 9.772 | 1.8727 | 1.1595 | 13.7477 | 1.3935 | 7.6926 | 0.39174 | 5.1868 | 0 | 0.98057 | 0 | 3.7199 | 0.27348 | 0 | 28.3734 | 11.1649 | 85.7288 | 0% | CZ 6B | 2.8632 | 0.5487 | 0 | 0.049339 | 0.4083 | 2.2539 | 0.11478 | 1.5197 | 0 | 0.2873 | 0 | 1.0899 | 0.080129 | 0 | 8.3133 | 3.2713 | 20.7999 | 0% | CZ 6B | 0 | 0 | 0.011595 | 0.13579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14739 | 0% | CZ 6B | 29.9746 | 5.7443 | 1.2673 | 15.3587 | 4.2745 | 23.5963 | 1.2016 | 15.9098 | 0 | 3.0078 | 0 | 11.4104 | 0.83887 | 0 | 87.0323 | 34.247 | 233.8635 | 0%
CZ 7 | 0.29548 | 0.05663 | 0.012321 | 0.24814 | 0.0026166 | 0.21515 | 0.017364 | 0.14844 | 0 | 0.033465 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.3459 | 0.3244% | CZ 7 | 9.772 | 1.8728 | 1.2445 | 25.0509 | 0.086536 | 7.1153 | 0.57426 | 4.9092 | 0 | 1.1067 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 95.2639 | 0.3244% | CZ 7 | 2.8632 | 0.54873 | 0 | 0.0020279 | 0.025355 | 2.0848 | 0.16826 | 1.4384 | 0 | 0.32427 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 20.2096 | 0.3244% | CZ 7 | 0 | 0 | 0.012445 | 0.25044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26288 | 0.3244% | CZ 7 | 29.9746 | 5.7447 | 1.3602 | 27.3943 | 0.26544 | 21.8254 | 1.7615 | 15.0584 | 0 | 3.3948 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 240.3079 | 0.3244%
CZ 8 | 0.29548 | 0.056282 | 0.013462 | 0.35804 | 0.0048785 | 0.18978 | 0.0080776 | 0.14467 | 0 | 0.025427 | 0 | 0.11248 | 0.0082688 | 0 | 0.85794 | 0.33761 | 2.4124 | 0% | CZ 8 | 9.772 | 1.8613 | 1.3597 | 36.1535 | 0.16134 | 6.2764 | 0.26714 | 4.7844 | 0 | 0.8409 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 105.0084 | 0% | CZ 8 | 2.8632 | 0.54536 | 0 | 0.0018051 | 0.047272 | 1.839 | 0.07827 | 1.4018 | 0 | 0.24638 | 0 | 1.0899 | 0.080124 | 0 | 8.3133 | 3.2713 | 19.7777 | 0% | CZ 8 | 0 | 0 | 0.013597 | 0.36147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37507 | 0% | CZ 8 | 29.9746 | 5.7094 | 1.4862 | 39.5279 | 0.49489 | 19.2522 | 0.81941 | 14.6756 | 0 | 2.5794 | 0 | 11.4104 | 0.83881 | 0 | 87.0323 | 34.247 | 248.0482 | 0%
Us Weighted | 0.29548 | 0.056723 | 0.0098104 | 0.083457 | 0.0046833 | 0.33644 | 0.050271 | 0.14433 | 0 | 0.070475 | 0 | 0.11248 | 0.0082687 | 0 | 0.85794 | 0.33761 | 2.368 | 100% | Us Weighted | 9.772 | 1.8759 | 0.99095 | 8.325 | 0.15488 | 11.1264 | 1.6625 | 4.7733 | 0 | 2.3307 | 0 | 3.7199 | 0.27346 | 0 | 28.3734 | 11.1649 | 84.5433 | 100% | Us Weighted | 2.8632 | 0.54963 | 0 | 0.014977 | 0.04538 | 3.26 | 0.48712 | 1.3986 | 0 | 0.68289 | 0 | 1.0899 | 0.080123 | 0 | 8.3133 | 3.2713 | 22.0564 | 100% | Us Weighted | 0 | 0 | 0.0099095 | 0.082739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092648 | 100% | Us Weighted | 29.9746 | 5.7541 | 1.0831 | 9.2001 | 0.47509 | 34.129 | 5.0997 | 14.6415 | 0 | 7.1492 | 0 | 11.4104 | 0.8388 | 0 | 87.0323 | 34.247 | 241.0349 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 498588 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 498588 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.09977 | 0.017658 | 1.9761e-05 | 0.0030254 | 1.6674e-05 | 0.17249 | 0.076334 | 0.027451 | -0.026856 | 0.060622 | 0 | 0.003187 | 0.0036786 | 0 | 0 | 0.030874 | 0.46827 | 3.058% | CZ 1A | 3.2995 | 0.58396 | 0.0019961 | 0.30458 | 0.00055142 | 5.7044 | 2.5245 | 0.90785 | -0.88815 | 2.0048 | 0 | 0.1054 | 0.12166 | 0 | 0 | 1.021 | 15.6922 | 3.058% | CZ 1A | 0.96675 | 0.1711 | 0 | 0.00014485 | 0.00016157 | 1.6714 | 0.73967 | 0.266 | -0.26023 | 0.58741 | 0 | 0.030881 | 0.035645 | 0 | 0 | 0.29916 | 4.5081 | 3.058% | CZ 1A | 0 | 0 | 1.9961e-05 | 0.0030408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030608 | 3.058% | CZ 1A | 10.121 | 1.7912 | 0.0021817 | 0.33388 | 0.0016914 | 17.4976 | 7.7436 | 2.7847 | -2.7243 | 6.1496 | 0 | 0.3233 | 0.37317 | 0 | 0 | 3.132 | 47.5296 | 3.058%
CZ 1B | 0.099739 | 0.017652 | 1.468e-05 | 0.028855 | 0.00091878 | 0.077849 | 0.026529 | 0.02885 | 0 | 0.045954 | 0 | 0.003187 | 0.0036797 | 0 | 0 | 0.030874 | 0.3641 | 0% | CZ 1B | 3.2985 | 0.58379 | 0.0014828 | 1.6068 | 0.030385 | 2.5746 | 0.87734 | 0.95412 | 0 | 1.5198 | 0 | 0.1054 | 0.12169 | 0 | 0 | 1.021 | 12.6949 | 0% | CZ 1B | 0.96645 | 0.17105 | 0 | 0.18654 | 0.0089028 | 0.75435 | 0.25706 | 0.27955 | 0 | 0.44529 | 0 | 0.030881 | 0.035656 | 0 | 0 | 0.29916 | 3.4349 | 0% | CZ 1B | 0 | 0 | 1.4828e-05 | 0.009701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097158 | 0% | CZ 1B | 10.1178 | 1.7907 | 0.0016207 | 3.0132 | 0.093204 | 7.8972 | 2.6911 | 2.9266 | 0 | 4.6617 | 0 | 0.3233 | 0.37328 | 0 | 0 | 3.132 | 37.0218 | 0%
CZ 2A | 0.099516 | 0.017647 | 2.0326e-05 | 0.027798 | 0.00051401 | 0.14998 | 0.055072 | 0.029062 | -0.012274 | 0.055194 | 0 | 0.003187 | 0.0036786 | 0 | 0 | 0.030874 | 0.46027 | 9.789% | CZ 2A | 3.2911 | 0.58362 | 0.0020531 | 2.8062 | 0.016999 | 4.9601 | 1.8213 | 0.96111 | -0.40591 | 1.8253 | 0 | 0.1054 | 0.12166 | 0 | 0 | 1.021 | 17.1101 | 9.789% | CZ 2A | 0.9643 | 0.171 | 0 | 0.00023956 | 0.0049807 | 1.4533 | 0.53364 | 0.2816 | -0.11893 | 0.53482 | 0 | 0.030881 | 0.035645 | 0 | 0 | 0.29916 | 4.1906 | 9.789% | CZ 2A | 0 | 0 | 2.0531e-05 | 0.028054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028075 | 9.789% | CZ 2A | 10.0952 | 1.7902 | 0.002244 | 3.0688 | 0.052143 | 15.2144 | 5.5866 | 2.9481 | -1.2451 | 5.599 | 0 | 0.3233 | 0.37317 | 0 | 0 | 3.132 | 46.9402 | 9.789%
CZ 2B | 0.099657 | 0.017644 | 1.5621e-05 | 0.023114 | -0.077488 | 0.13612 | 0.021043 | 0.032651 | 0 | 0.045431 | 0 | 0.003187 | 0.0036786 | 0 | 0 | 0.030874 | 0.33592 | 1.826% | CZ 2B | 3.2958 | 0.5835 | 0.0015778 | 2.0434 | -2.5626 | 4.5015 | 0.69594 | 1.0798 | 0 | 1.5025 | 0 | 0.1054 | 0.12166 | 0 | 0 | 1.021 | 12.3895 | 1.826% | CZ 2B | 0.96566 | 0.17096 | 0 | 0.041545 | -0.75084 | 1.3189 | 0.20391 | 0.31639 | 0 | 0.44022 | 0 | 0.030881 | 0.035645 | 0 | 0 | 0.29916 | 3.0725 | 1.826% | CZ 2B | 0 | 0 | 1.5778e-05 | 0.019016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019032 | 1.826% | CZ 2B | 10.1095 | 1.7898 | 0.0017246 | 2.5134 | -7.8606 | 13.8079 | 2.1347 | 3.3122 | 0 | 4.6086 | 0 | 0.3233 | 0.37317 | 0 | 0 | 3.132 | 34.2458 | 1.826%
CZ 3A | 0.098939 | 0.017573 | 2.1267e-05 | 0.024105 | 0.0011982 | 0.098224 | 0.039475 | 0.020747 | -0.0080948 | 0.048514 | 0 | 0.003187 | 0.003678 | 0 | 0 | 0.030874 | 0.37844 | 13.37% | CZ 3A | 3.2721 | 0.58116 | 0.0021481 | 2.4322 | 0.039627 | 3.2484 | 1.3055 | 0.68614 | -0.26771 | 1.6044 | 0 | 0.1054 | 0.12164 | 0 | 0 | 1.021 | 14.152 | 13.37% | CZ 3A | 0.9587 | 0.17028 | 0 | 0.00038442 | 0.01161 | 0.95177 | 0.38251 | 0.20104 | -0.078437 | 0.4701 | 0 | 0.030881 | 0.035639 | 0 | 0 | 0.29916 | 3.4336 | 13.37% | CZ 3A | 0 | 0 | 2.1481e-05 | 0.024309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02433 | 13.37% | CZ 3A | 10.0367 | 1.7827 | 0.0023479 | 2.661 | 0.12155 | 9.9641 | 4.0045 | 2.1047 | -0.82116 | 4.9214 | 0 | 0.3233 | 0.37311 | 0 | 0 | 3.132 | 38.6061 | 13.37%
CZ 3B | 0.099507 | 0.017651 | 1.6185e-05 | 0.023811 | -0.072441 | 0.10626 | 0.013363 | 0.019196 | 0 | 0.023417 | 0 | 0.003187 | 0.0036803 | 0 | 0 | 0.030874 | 0.26852 | 8.555% | CZ 3B | 3.2908 | 0.58375 | 0.0016349 | 1.4507 | -2.3957 | 3.5142 | 0.44194 | 0.63484 | 0 | 0.77445 | 0 | 0.1054 | 0.12171 | 0 | 0 | 1.021 | 9.5447 | 8.555% | CZ 3B | 0.9642 | 0.17104 | 0 | 0.13613 | -0.70194 | 1.0296 | 0.12949 | 0.18601 | 0 | 0.22691 | 0 | 0.030881 | 0.035661 | 0 | 0 | 0.29916 | 2.5072 | 8.555% | CZ 3B | 0 | 0 | 1.6349e-05 | 0.0098607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009877 | 8.555% | CZ 3B | 10.0942 | 1.7906 | 0.0017869 | 2.5029 | -7.3486 | 10.7793 | 1.3556 | 1.9473 | 0 | 2.3755 | 0 | 0.3233 | 0.37334 | 0 | 0 | 3.132 | 27.3272 | 8.555%
CZ 3C | 0.099019 | 0.017579 | 2.2208e-05 | 0.025744 | -0.028934 | 0.12338 | 0.0089268 | 0.021639 | 0 | 0.020521 | 0 | 0.003187 | 0.0036791 | 0 | 0 | 0.030874 | 0.32564 | 3.506% | CZ 3C | 3.2747 | 0.58137 | 0.0022432 | 2.6335 | -0.95689 | 4.0804 | 0.29522 | 0.71563 | 0 | 0.67867 | 0 | 0.1054 | 0.12167 | 0 | 0 | 1.021 | 12.553 | 3.506% | CZ 3C | 0.95947 | 0.17034 | 0 | -0.0047244 | -0.28037 | 1.1956 | 0.086499 | 0.20968 | 0 | 0.19885 | 0 | 0.030881 | 0.03565 | 0 | 0 | 0.29916 | 2.901 | 3.506% | CZ 3C | 0 | 0 | 2.2432e-05 | 0.026496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026519 | 3.506% | CZ 3C | 10.0447 | 1.7833 | 0.0024518 | 2.8466 | -2.9352 | 12.5163 | 0.90556 | 2.1951 | 0 | 2.0817 | 0 | 0.3233 | 0.37322 | 0 | 0 | 3.132 | 33.2691 | 3.506%
CZ 4A | 0.099679 | 0.017545 | 2.296e-05 | 0.033989 | 2.7023e-05 | 0.080921 | 0.025773 | 0.015254 | -0.0063337 | 0.050893 | 0 | 0.003187 | 0.003678 | 0 | 0 | 0.030874 | 0.35551 | 34.02% | CZ 4A | 3.2965 | 0.58023 | 0.0023192 | 3.4471 | 0.00089369 | 2.6762 | 0.85235 | 0.50448 | -0.20947 | 1.6831 | 0 | 0.1054 | 0.12164 | 0 | 0 | 1.021 | 14.0818 | 34.02% | CZ 4A | 0.96587 | 0.17001 | 0 | -0.0019722 | 0.00026185 | 0.78411 | 0.24974 | 0.14781 | -0.061373 | 0.49314 | 0 | 0.030881 | 0.035639 | 0 | 0 | 0.29916 | 3.1133 | 34.02% | CZ 4A | 0 | 0 | 2.3192e-05 | 0.034538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034562 | 34.02% | CZ 4A | 10.1117 | 1.7798 | 0.0025349 | 3.7544 | 0.0027413 | 8.2089 | 2.6145 | 1.5474 | -0.64251 | 5.1627 | 0 | 0.3233 | 0.37311 | 0 | 0 | 3.132 | 36.3705 | 34.02%
CZ 4B | 0.099954 | 0.017601 | 2.2208e-05 | 0.051468 | -0.072232 | 0.11844 | 0.010203 | 0.016657 | 0 | 0.020165 | 0 | 0.003187 | 0.0036803 | 0 | 0 | 0.030874 | 0.30002 | 0% | CZ 4B | 3.3056 | 0.5821 | 0.0022432 | 3.7974 | -2.3888 | 3.9169 | 0.33743 | 0.55087 | 0 | 0.6669 | 0 | 0.1054 | 0.12171 | 0 | 0 | 1.021 | 12.0188 | 0% | CZ 4B | 0.96854 | 0.17055 | 0 | 0.19988 | -0.69991 | 1.1476 | 0.098867 | 0.1614 | 0 | 0.1954 | 0 | 0.030881 | 0.035661 | 0 | 0 | 0.29916 | 2.6081 | 0% | CZ 4B | 0 | 0 | 2.2432e-05 | 0.031152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031174 | 0% | CZ 4B | 10.1396 | 1.7855 | 0.0024518 | 5.4974 | -7.3274 | 12.0146 | 1.035 | 1.6897 | 0 | 2.0456 | 0 | 0.3233 | 0.37334 | 0 | 0 | 3.132 | 30.7112 | 0%
CZ 4C | 0.099044 | 0.017455 | 2.2772e-05 | 0.048675 | -0.058296 | 0.10986 | 0.0078999 | 0.015261 | 0 | 0.016341 | 0 | 0.003187 | 0.0036786 | 0 | 0 | 0.030874 | 0.294 | 4.62% | CZ 4C | 3.2755 | 0.57725 | 0.0023002 | 4.9559 | -1.9279 | 3.6331 | 0.26126 | 0.50469 | 0 | 0.54041 | 0 | 0.1054 | 0.12166 | 0 | 0 | 1.021 | 13.0707 | 4.62% | CZ 4C | 0.95972 | 0.16913 | 0 | -0.0055991 | -0.56488 | 1.0645 | 0.076549 | 0.14787 | 0 | 0.15834 | 0 | 0.030881 | 0.035645 | 0 | 0 | 0.29916 | 2.3713 | 4.62% | CZ 4C | 0 | 0 | 2.3002e-05 | 0.04975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049773 | 4.62% | CZ 4C | 10.0473 | 1.7706 | 0.0025141 | 5.3791 | -5.9137 | 11.1442 | 0.80139 | 1.5481 | 0 | 1.6577 | 0 | 0.3233 | 0.37317 | 0 | 0 | 3.132 | 30.2656 | 4.62%
CZ 5A | 0.099356 | 0.017322 | 2.3901e-05 | 0.053704 | -0.0902 | 0.11538 | 0.021832 | 0.01615 | -0.0029944 | 0.024001 | 0 | 0.003187 | 0.003678 | 0 | 0 | 0.030874 | 0.29231 | 13.29% | CZ 5A | 3.2858 | 0.57287 | 0.0024143 | 5.4559 | -2.9831 | 3.8157 | 0.72202 | 0.5341 | -0.099028 | 0.79375 | 0 | 0.1054 | 0.12164 | 0 | 0 | 1.021 | 13.3485 | 13.29% | CZ 5A | 0.96274 | 0.16785 | 0 | -0.0044514 | -0.87403 | 1.118 | 0.21155 | 0.15649 | -0.029015 | 0.23257 | 0 | 0.030881 | 0.035639 | 0 | 0 | 0.29916 | 2.3074 | 13.29% | CZ 5A | 0 | 0 | 2.4143e-05 | 0.054711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054735 | 13.29% | CZ 5A | 10.079 | 1.7572 | 0.0026388 | 5.9333 | -9.1502 | 11.7041 | 2.2147 | 1.6383 | -0.30376 | 2.4347 | 0 | 0.3233 | 0.37311 | 0 | 0 | 3.132 | 30.1384 | 13.29%
CZ 5B | 0.0993 | 0.017639 | 2.3149e-05 | 0.057986 | -0.12494 | 0.12156 | 0.0086226 | 0.012979 | 0 | 0.018209 | 0 | 0.003187 | 0.003678 | 0 | 0 | 0.030874 | 0.24911 | 3.637% | CZ 5B | 3.284 | 0.58333 | 0.0023382 | 5.6574 | -4.1321 | 4.0201 | 0.28516 | 0.42922 | 0 | 0.60221 | 0 | 0.1054 | 0.12164 | 0 | 0 | 1.021 | 11.9798 | 3.637% | CZ 5B | 0.9622 | 0.17091 | 0 | 0.028491 | -1.2107 | 1.1779 | 0.083552 | 0.12576 | 0 | 0.17645 | 0 | 0.030881 | 0.035639 | 0 | 0 | 0.29916 | 1.8802 | 3.637% | CZ 5B | 0 | 0 | 2.3382e-05 | 0.055602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055625 | 3.637% | CZ 5B | 10.0732 | 1.7893 | 0.0025557 | 6.3755 | -12.6747 | 12.3312 | 0.8747 | 1.3166 | 0 | 1.8472 | 0 | 0.3233 | 0.37311 | 0 | 0 | 3.132 | 25.764 | 3.637%
CZ 5C | 0.097024 | 0.017292 | 2.3525e-05 | 0.061396 | -0.070454 | 0.11473 | 0.0063757 | 0.010756 | 0 | 0.011306 | 0 | 0.003187 | 0.0036763 | 0 | 0 | 0.030874 | 0.28619 | 0% | CZ 5C | 3.2087 | 0.57188 | 0.0023763 | 6.2448 | -2.33 | 3.7943 | 0.21085 | 0.35571 | 0 | 0.3739 | 0 | 0.1054 | 0.12158 | 0 | 0 | 1.021 | 13.6806 | 0% | CZ 5C | 0.94015 | 0.16756 | 0 | -0.0061562 | -0.68269 | 1.1117 | 0.061779 | 0.10422 | 0 | 0.10955 | 0 | 0.030881 | 0.035622 | 0 | 0 | 0.29916 | 2.1718 | 0% | CZ 5C | 0 | 0 | 2.3763e-05 | 0.062658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062682 | 0% | CZ 5C | 9.8424 | 1.7542 | 0.0025972 | 6.7841 | -7.1471 | 11.6386 | 0.64677 | 1.0911 | 0 | 1.1469 | 0 | 0.3233 | 0.37293 | 0 | 0 | 3.132 | 29.5878 | 0%
CZ 6A | 0.099067 | 0.017253 | 2.5031e-05 | 0.060886 | -0.10327 | 0.11613 | 0.0088589 | 0.014656 | -0.001519 | 0.017603 | 0 | 0.003187 | 0.003678 | 0 | 0 | 0.030874 | 0.26743 | 4.001% | CZ 6A | 3.2763 | 0.57059 | 0.0025283 | 6.1843 | -3.4153 | 3.8407 | 0.29298 | 0.48468 | -0.050237 | 0.58217 | 0 | 0.1054 | 0.12164 | 0 | 0 | 1.021 | 13.0168 | 4.001% | CZ 6A | 0.95994 | 0.16718 | 0 | -0.0048804 | -1.0007 | 1.1253 | 0.085842 | 0.14201 | -0.014719 | 0.17057 | 0 | 0.030881 | 0.035639 | 0 | 0 | 0.29916 | 1.9963 | 4.001% | CZ 6A | 0 | 0 | 2.5283e-05 | 0.06201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062035 | 4.001% | CZ 6A | 10.0496 | 1.7502 | 0.0027635 | 6.7266 | -10.4759 | 11.7808 | 0.89868 | 1.4867 | -0.1541 | 1.7857 | 0 | 0.3233 | 0.37311 | 0 | 0 | 3.132 | 27.6794 | 4.001%
CZ 6B | 0.099253 | 0.017504 | 2.5031e-05 | 0.050539 | -0.11023 | 0.12898 | 0.0067684 | 0.012268 | -0.0014535 | 0.013321 | 0 | 0.003187 | 0.0036786 | 0 | 0 | 0.030874 | 0.25471 | 0% | CZ 6B | 3.2824 | 0.57888 | 0.0025283 | 4.784 | -3.6455 | 4.2655 | 0.22384 | 0.40572 | -0.048069 | 0.44055 | 0 | 0.1054 | 0.12166 | 0 | 0 | 1.021 | 11.5379 | 0% | CZ 6B | 0.96174 | 0.16961 | 0 | 0.045773 | -1.0681 | 1.2498 | 0.065585 | 0.11887 | -0.014084 | 0.12908 | 0 | 0.030881 | 0.035645 | 0 | 0 | 0.29916 | 2.0239 | 0% | CZ 6B | 0 | 0 | 2.5283e-05 | 0.046277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046303 | 0% | CZ 6B | 10.0685 | 1.7757 | 0.0027635 | 5.5373 | -11.1821 | 13.0839 | 0.68661 | 1.2445 | -0.14745 | 1.3513 | 0 | 0.3233 | 0.37317 | 0 | 0 | 3.132 | 26.2494 | 0%
CZ 7 | 0.099794 | 0.017345 | 3.0488e-05 | 0.08896 | -0.11153 | 0.12189 | 0.0077924 | 0.016727 | -0.0012333 | 0.014195 | 0 | 0.003187 | 0.0036791 | 0 | 0 | 0.030874 | 0.2917 | 0.3244% | CZ 7 | 3.3003 | 0.57361 | 0.0030796 | 9.0294 | -3.6886 | 4.0309 | 0.25771 | 0.55319 | -0.040786 | 0.46943 | 0 | 0.1054 | 0.12167 | 0 | 0 | 1.021 | 15.7364 | 0.3244% | CZ 7 | 0.96699 | 0.16807 | 0 | -0.0062064 | -1.0807 | 1.1811 | 0.075507 | 0.16208 | -0.01195 | 0.13754 | 0 | 0.030881 | 0.03565 | 0 | 0 | 0.29916 | 1.958 | 0.3244% | CZ 7 | 0 | 0 | 3.0796e-05 | 0.090506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090537 | 0.3244% | CZ 7 | 10.1234 | 1.7595 | 0.003366 | 9.8273 | -11.3143 | 12.3644 | 0.79048 | 1.6969 | -0.12511 | 1.4399 | 0 | 0.3233 | 0.37322 | 0 | 0 | 3.132 | 30.3943 | 0.3244%
CZ 8 | 0.095641 | 0.016517 | 3.2558e-05 | 0.11005 | -0.1375 | 0.12326 | 0.0050935 | 0.01448 | -0.00087106 | 0.0091056 | 0 | 0.003187 | 0.0036763 | 0 | 0 | 0.030874 | 0.27354 | 0% | CZ 8 | 3.163 | 0.54623 | 0.0032887 | 11.1299 | -4.5474 | 4.0763 | 0.16845 | 0.47888 | -0.028807 | 0.30113 | 0 | 0.1054 | 0.12158 | 0 | 0 | 1.021 | 16.539 | 0% | CZ 8 | 0.92674 | 0.16004 | 0 | -0.0020056 | -1.3324 | 1.1943 | 0.049356 | 0.14031 | -0.0084404 | 0.088232 | 0 | 0.030881 | 0.035622 | 0 | 0 | 0.29916 | 1.5819 | 0% | CZ 8 | 0 | 0 | 3.2887e-05 | 0.11137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1114 | 0% | CZ 8 | 9.7021 | 1.6755 | 0.0035946 | 12.1515 | -13.9486 | 12.5035 | 0.5167 | 1.4689 | -0.088363 | 0.9237 | 0 | 0.3233 | 0.37293 | 0 | 0 | 3.132 | 28.7368 | 0%
Us Weighted | 0.099418 | 0.017532 | 2.1868e-05 | 0.035182 | -0.032126 | 0.1064 | 0.027573 | 0.01861 | -0.0057228 | 0.039968 | 0 | 0.003187 | 0.0036784 | 0 | 0 | 0.030874 | 0.34459 | 100% | Us Weighted | 3.2879 | 0.57979 | 0.0022089 | 3.4723 | -1.0625 | 3.5187 | 0.91188 | 0.61545 | -0.18926 | 1.3218 | 0 | 0.1054 | 0.12165 | 0 | 0 | 1.021 | 13.7064 | 100% | Us Weighted | 0.96335 | 0.16988 | 0 | 0.011618 | -0.3113 | 1.031 | 0.26718 | 0.18032 | -0.055453 | 0.38728 | 0 | 0.030881 | 0.035643 | 0 | 0 | 0.29916 | 3.0095 | 100% | Us Weighted | 0 | 0 | 2.2089e-05 | 0.034326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034348 | 100% | Us Weighted | 10.0853 | 1.7784 | 0.0024144 | 3.8735 | -3.259 | 10.7931 | 2.7971 | 1.8878 | -0.58054 | 4.0545 | 0 | 0.3233 | 0.37314 | 0 | 0 | 3.132 | 35.261 | 100%
Building Type: | Large Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 498588 | [17 empty] | Prototype Floor Area: | 498588 | [17 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 33.77% | 31.07% | 0.2646% | 92.8% | 12.72% | 29.36% | 56.86% | 17.52% | 0% | 51.08% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 17.5% | 3.058% | CZ 1A | 33.77% | 31.07% | 0.2646% | 92.77% | 12.72% | 29.36% | 56.86% | 17.52% | 0% | 51.08% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 17.58% | 3.058% | CZ 1A | 33.77% | 31.07% | 0% | 100% | 12.72% | 29.36% | 56.86% | 17.52% | 0% | 51.08% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 17.45% | 3.058% | CZ 1A | 0% | 0% | 0.2646% | 92.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.28% | 3.058% | CZ 1A | 33.77% | 31.07% | 0.2646% | 92.79% | 12.72% | 29.36% | 56.86% | 17.52% | 0% | 51.08% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 17.5% | 3.058%
CZ 1B | 33.75% | 31.09% | 0.2086% | 86.3% | 8.112% | 15.69% | 46.42% | 16.24% | 0% | 47.88% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 14.29% | 0% | CZ 1B | 33.75% | 31.09% | 0.2086% | 85.8% | 8.112% | 15.69% | 46.42% | 16.24% | 0% | 47.88% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 14.85% | 0% | CZ 1B | 33.75% | 31.09% | 0% | 86.92% | 8.112% | 15.69% | 46.42% | 16.24% | 0% | 47.88% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 14.02% | 0% | CZ 1B | 0% | 0% | 0.2086% | 85.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 52.49% | 0% | CZ 1B | 33.75% | 31.09% | 0.2086% | 86.26% | 8.112% | 15.69% | 46.42% | 16.24% | 0% | 47.88% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 14.32% | 0%
CZ 2A | 33.68% | 31.11% | 0.2407% | 69.98% | 56.05% | 31.47% | 58.72% | 19.44% | 0% | 55.86% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 18.15% | 9.789% | CZ 2A | 33.68% | 31.11% | 0.2407% | 69.98% | 56.05% | 31.47% | 58.72% | 19.44% | 0% | 55.86% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 19.63% | 9.789% | CZ 2A | 33.68% | 31.11% | 0% | 66.15% | 56.05% | 31.47% | 58.72% | 19.44% | 0% | 55.86% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 17.38% | 9.789% | CZ 2A | 0% | 0% | 0.2407% | 69.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.75% | 9.789% | CZ 2A | 33.68% | 31.11% | 0.2407% | 69.98% | 56.05% | 31.47% | 58.72% | 19.44% | 0% | 55.86% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 18.21% | 9.789%
CZ 2B | 33.73% | 31.12% | 0.1985% | 86.2% | -3421% | 30.4% | 34.34% | 19.19% | 0% | 52.61% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 13.59% | 1.826% | CZ 2B | 33.73% | 31.12% | 0.1985% | 88.1% | -3421% | 30.4% | 34.34% | 19.19% | 0% | 52.61% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 14.8% | 1.826% | CZ 2B | 33.73% | 31.12% | 0% | 74.9% | -3421% | 30.4% | 34.34% | 19.19% | 0% | 52.61% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 12.98% | 1.826% | CZ 2B | 0% | 0% | 0.1985% | 89.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.07% | 1.826% | CZ 2B | 33.73% | 31.12% | 0.1985% | 86.4% | -3421% | 30.4% | 34.34% | 19.19% | 0% | 52.61% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 13.65% | 1.826%
CZ 3A | 33.48% | 30.96% | 0.2309% | 36.31% | 53.99% | 25.92% | 58.15% | 14.8% | 0% | 56.87% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.65% | 13.37% | CZ 3A | 33.48% | 30.96% | 0.2309% | 36.29% | 53.99% | 25.92% | 58.15% | 14.8% | 0% | 56.87% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 16.63% | 13.37% | CZ 3A | 33.48% | 30.96% | 0% | 86.25% | 53.99% | 25.92% | 58.15% | 14.8% | 0% | 56.87% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.12% | 13.37% | CZ 3A | 0% | 0% | 0.2309% | 36.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.88% | 13.37% | CZ 3A | 33.48% | 30.96% | 0.2309% | 36.31% | 53.99% | 25.92% | 58.15% | 14.8% | 0% | 56.87% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.69% | 13.37%
CZ 3B | 33.68% | 31.09% | 0.1808% | 73.85% | -234.8% | 31.87% | 36.9% | 12.02% | 0% | 44.9% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 11.56% | 8.555% | CZ 3B | 33.68% | 31.09% | 0.1808% | 63.96% | -234.8% | 31.87% | 36.9% | 12.02% | 0% | 44.9% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 12.14% | 8.555% | CZ 3B | 33.68% | 31.09% | 0% | 96.54% | -234.8% | 31.87% | 36.9% | 12.02% | 0% | 44.9% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 11.27% | 8.555% | CZ 3B | 0% | 0% | 0.1808% | 55.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.7% | 8.555% | CZ 3B | 33.68% | 31.09% | 0.1808% | 72.98% | -234.8% | 31.87% | 36.9% | 12.02% | 0% | 44.9% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 11.59% | 8.555%
CZ 3C | 33.51% | 31.01% | 0.2211% | 87.04% | -8429% | 61.34% | 60.98% | 16.04% | 0% | 57.66% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 15.55% | 3.506% | CZ 3C | 33.51% | 31.01% | 0.2211% | 88.36% | -8429% | 61.34% | 60.98% | 16.04% | 0% | 57.66% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 17.44% | 3.506% | CZ 3C | 33.51% | 31.01% | 0% | -476.4% | -8429% | 61.34% | 60.98% | 16.04% | 0% | 57.66% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 14.57% | 3.506% | CZ 3C | 0% | 0% | 0.2211% | 89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 66.44% | 3.506% | CZ 3C | 33.51% | 31.01% | 0.2211% | 87.2% | -8429% | 61.34% | 60.98% | 16.04% | 0% | 57.66% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 15.63% | 3.506%
CZ 4A | 33.73% | 30.92% | 0.2262% | 37.31% | 1.648% | 24.67% | 55.37% | 10.86% | 0% | 63.75% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.02% | 34.02% | CZ 4A | 33.73% | 30.92% | 0.2262% | 37.48% | 1.648% | 24.67% | 55.37% | 10.86% | 0% | 63.75% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 16.54% | 34.02% | CZ 4A | 33.73% | 30.92% | 0% | -219.9% | 1.648% | 24.67% | 55.37% | 10.86% | 0% | 63.75% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 14.18% | 34.02% | CZ 4A | 0% | 0% | 0.2262% | 37.57% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.82% | 34.02% | CZ 4A | 33.73% | 30.92% | 0.2262% | 37.33% | 1.648% | 24.67% | 55.37% | 10.86% | 0% | 63.75% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.1% | 34.02%
CZ 4B | 33.83% | 31.03% | 0.2219% | 76.23% | -127.1% | 40.48% | 44.6% | 9.343% | 0% | 46.46% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 12.82% | 0% | CZ 4B | 33.83% | 31.03% | 0.2219% | 71.85% | -127.1% | 40.48% | 44.6% | 9.343% | 0% | 46.46% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 14.82% | 0% | CZ 4B | 33.83% | 31.03% | 0% | 91.31% | -127.1% | 40.48% | 44.6% | 9.343% | 0% | 46.46% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 11.78% | 0% | CZ 4B | 0% | 0% | 0.2219% | 68.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 56.18% | 0% | CZ 4B | 33.83% | 31.03% | 0.2219% | 75.81% | -127.1% | 40.48% | 44.6% | 9.343% | 0% | 46.46% | 0% | 2.833% | 44.5% | 0% | 0% | 9.145% | 12.91% | 0%
CZ 4C | 33.52% | 30.78% | 0.2158% | 67.95% | -7544% | 50.53% | 43.7% | 11.02% | 0% | 48.6% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 13.62% | 4.62% | CZ 4C | 33.52% | 30.78% | 0.2158% | 68.57% | -7544% | 50.53% | 43.7% | 11.02% | 0% | 48.6% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 16.98% | 4.62% | CZ 4C | 33.52% | 30.78% | 0% | -500% | -7544% | 50.53% | 43.7% | 11.02% | 0% | 48.6% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.78% | 4.62% | CZ 4C | 0% | 0% | 0.2158% | 68.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.04% | 4.62% | CZ 4C | 33.52% | 30.78% | 0.2158% | 68.02% | -7544% | 50.53% | 43.7% | 11.02% | 0% | 48.6% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 13.77% | 4.62%
CZ 5A | 33.63% | 30.57% | 0.2211% | 34.75% | -5190% | 42.2% | 59.29% | 11.36% | 0% | 47.41% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 12.5% | 13.29% | CZ 5A | 33.63% | 30.57% | 0.2211% | 34.97% | -5190% | 42.2% | 59.29% | 11.36% | 0% | 47.41% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 15.07% | 13.29% | CZ 5A | 33.63% | 30.57% | 0% | -284.3% | -5190% | 42.2% | 59.29% | 11.36% | 0% | 47.41% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 10.96% | 13.29% | CZ 5A | 0% | 0% | 0.2211% | 35.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.8% | 13.29% | CZ 5A | 33.63% | 30.57% | 0.2211% | 34.77% | -5190% | 42.2% | 59.29% | 11.36% | 0% | 47.41% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 12.63% | 13.29%
CZ 5B | 33.61% | 31.14% | 0.2165% | 62.38% | -670.3% | 47.3% | 51.5% | 8.483% | 0% | 48.15% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.05% | 3.637% | CZ 5B | 33.61% | 31.14% | 0.2165% | 61.72% | -670.3% | 47.3% | 51.5% | 8.483% | 0% | 48.15% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 14.72% | 3.637% | CZ 5B | 33.61% | 31.14% | 0% | 89.36% | -670.3% | 47.3% | 51.5% | 8.483% | 0% | 48.15% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 9.005% | 3.637% | CZ 5B | 0% | 0% | 0.2165% | 61.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.87% | 3.637% | CZ 5B | 33.61% | 31.14% | 0.2165% | 62.3% | -670.3% | 47.3% | 51.5% | 8.483% | 0% | 48.15% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.22% | 3.637%
CZ 5C | 32.84% | 30.55% | 0.2175% | 64.85% | -7875% | 62.82% | 56.25% | 7.99% | 0% | 46.3% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 13.45% | 0% | CZ 5C | 32.84% | 30.55% | 0.2175% | 65.32% | -7875% | 62.82% | 56.25% | 7.99% | 0% | 46.3% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 17.64% | 0% | CZ 5C | 32.84% | 30.55% | 0% | -2631% | -7875% | 62.82% | 56.25% | 7.99% | 0% | 46.3% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 11.08% | 0% | CZ 5C | 0% | 0% | 0.2175% | 65.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.84% | 0% | CZ 5C | 32.84% | 30.55% | 0.2175% | 64.91% | -7875% | 62.82% | 56.25% | 7.99% | 0% | 46.3% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 13.65% | 0%
CZ 6A | 33.53% | 30.45% | 0.2197% | 33.49% | -4617% | 49.6% | 37.44% | 10.58% | 0% | 45.3% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.63% | 4.001% | CZ 6A | 33.53% | 30.45% | 0.2197% | 33.69% | -4617% | 49.6% | 37.44% | 10.58% | 0% | 45.3% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 14.6% | 4.001% | CZ 6A | 33.53% | 30.45% | 0% | -554.4% | -4617% | 49.6% | 37.44% | 10.58% | 0% | 45.3% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 9.783% | 4.001% | CZ 6A | 0% | 0% | 0.2197% | 33.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.81% | 4.001% | CZ 6A | 33.53% | 30.45% | 0.2197% | 33.52% | -4617% | 49.6% | 37.44% | 10.58% | 0% | 45.3% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.78% | 4.001%
CZ 6B | 33.59% | 30.91% | 0.2181% | 36.22% | -261.6% | 55.45% | 57.14% | 7.822% | 0% | 44.93% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.11% | 0% | CZ 6B | 33.59% | 30.91% | 0.2181% | 34.8% | -261.6% | 55.45% | 57.14% | 7.822% | 0% | 44.93% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 13.46% | 0% | CZ 6B | 33.59% | 30.91% | 0% | 92.77% | -261.6% | 55.45% | 57.14% | 7.822% | 0% | 44.93% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 9.73% | 0% | CZ 6B | 0% | 0% | 0.2181% | 34.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.42% | 0% | CZ 6B | 33.59% | 30.91% | 0.2181% | 36.05% | -261.6% | 55.45% | 57.14% | 7.822% | 0% | 44.93% | 0% | 2.833% | 44.48% | 0% | 0% | 9.145% | 11.22% | 0%
CZ 7 | 33.77% | 30.63% | 0.2475% | 35.85% | -4263% | 56.65% | 44.88% | 11.27% | 0% | 42.42% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 12.43% | 0.3244% | CZ 7 | 33.77% | 30.63% | 0.2475% | 36.04% | -4263% | 56.65% | 44.88% | 11.27% | 0% | 42.42% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 16.52% | 0.3244% | CZ 7 | 33.77% | 30.63% | 0% | -306% | -4263% | 56.65% | 44.88% | 11.27% | 0% | 42.42% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 9.689% | 0.3244% | CZ 7 | 0% | 0% | 0.2475% | 36.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.44% | 0.3244% | CZ 7 | 33.77% | 30.63% | 0.2475% | 35.87% | -4263% | 56.65% | 44.88% | 11.27% | 0% | 42.42% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 12.65% | 0.3244%
CZ 8 | 32.37% | 29.35% | 0.2419% | 30.74% | -2819% | 64.95% | 63.06% | 10.01% | 0% | 35.81% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 11.34% | 0% | CZ 8 | 32.37% | 29.35% | 0.2419% | 30.79% | -2819% | 64.95% | 63.06% | 10.01% | 0% | 35.81% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 15.75% | 0% | CZ 8 | 32.37% | 29.35% | 0% | -111.1% | -2819% | 64.95% | 63.06% | 10.01% | 0% | 35.81% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 7.998% | 0% | CZ 8 | 0% | 0% | 0.2419% | 30.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.7% | 0% | CZ 8 | 32.37% | 29.35% | 0.2419% | 30.74% | -2819% | 64.95% | 63.06% | 10.01% | 0% | 35.81% | 0% | 2.833% | 44.46% | 0% | 0% | 9.145% | 11.59% | 0%
Us Weighted | 33.65% | 30.91% | 0.2229% | 42.16% | -686% | 31.62% | 54.85% | 12.89% | 0% | 56.71% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 14.55% | 100% | Us Weighted | 33.65% | 30.91% | 0.2229% | 41.71% | -686% | 31.62% | 54.85% | 12.89% | 0% | 56.71% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 16.21% | 100% | Us Weighted | 33.65% | 30.91% | 0% | 77.57% | -686% | 31.62% | 54.85% | 12.89% | 0% | 56.71% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 13.64% | 100% | Us Weighted | 0% | 0% | 0.2229% | 41.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.07% | 100% | Us Weighted | 33.65% | 30.91% | 0.2229% | 42.1% | -686% | 31.62% | 54.85% | 12.89% | 0% | 56.71% | 0% | 2.833% | 44.49% | 0% | 0% | 9.145% | 14.63% | 100%

## MdOffice
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Medium Office |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Medium Office | [14 empty] | Prototype Floor Area: | 53628 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.17544 | 0.056061 | 0.01291 | 0.089351 | 0 | 0.17356 | 0 | 0.044594 | 8.9871e-05 | 8.0182e-05 | 0 | 0.088409 | 0.0091151 | 0 | 0 | 0.31254 | 0.96214 |  | STD2013 | 5.8019 | 1.854 | 1.304 | 4.3098 | 0 | 5.7398 | 0 | 1.4748 | 0.0029722 | 0.0026517 | 0 | 2.9238 | 0.30145 | 0 | 0 | 10.3361 | 34.0512 |  | STD2013 | 1.6999 | 0.54322 | 0 | 0.67257 | 0 | 1.6818 | 0 | 0.4321 | 0.00087084 | 0.00077695 | 0 | 0.85667 | 0.088324 | 0 | 0 | 3.0284 | 9.0047 |  | STD2013 | 0 | 0 | 0.01304 | 0.020143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033183 |  | STD2013 | 17.7967 | 5.687 | 1.4253 | 9.2427 | 0 | 17.6063 | 0 | 4.5237 | 0.0091168 | 0.0081339 | 0 | 8.9685 | 0.92467 | 0 | 0 | 31.7047 | 97.8968
STD2010 | 0.20344 | 0.056061 | 0.012914 | 0.10649 | 0 | 0.19737 | 0 | 0.04978 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092961 | 0 | 0 | 0.31637 | 1.0404 |  | STD2010 | 6.728 | 1.854 | 1.3045 | 5.0257 | 0 | 6.5273 | 0 | 1.6463 | 0 | 0.0026517 | 0 | 2.9318 | 0.30744 | 0 | 0 | 10.4626 | 36.7904 |  | STD2010 | 1.9713 | 0.54322 | 0 | 0.81733 | 0 | 1.9125 | 0 | 0.48236 | 0 | 0.00077695 | 0 | 0.859 | 0.090078 | 0 | 0 | 3.0655 | 9.7421 |  | STD2010 | 0 | 0 | 0.013045 | 0.022361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035406 |  | STD2010 | 20.6375 | 5.687 | 1.4258 | 11.0008 | 0 | 20.0219 | 0 | 5.0498 | 0 | 0.0081339 | 0 | 8.9929 | 0.94302 | 0 | 0 | 32.093 | 105.8598
STD2007 | 0.29548 | 0.12081 | 0.013103 | 0.13621 | 0 | 0.25789 | 0 | 0.054823 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018042 | 0 | 0 | 0.34279 | 1.3328 |  | STD2007 | 9.772 | 3.9953 | 1.3235 | 5.9311 | 0 | 8.5288 | 0 | 1.8131 | 0 | 0.0026517 | 0 | 3.093 | 0.59669 | 0 | 0 | 11.3367 | 46.3928 |  | STD2007 | 2.8632 | 1.1706 | 0 | 1.1164 | 0 | 2.4989 | 0 | 0.53123 | 0 | 0.00077695 | 0 | 0.90624 | 0.17483 | 0 | 0 | 3.3216 | 12.5838 |  | STD2007 | 0 | 0 | 0.013235 | 0.021207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034442 |  | STD2007 | 29.9745 | 12.255 | 1.4466 | 14.006 | 0 | 26.1613 | 0 | 5.5614 | 0 | 0.0081339 | 0 | 9.4875 | 1.8303 | 0 | 0 | 34.7739 | 135.5046
STD2004 | 0.29548 | 0.12081 | 0.013105 | 0.18599 | 0 | 0.2716 | 0 | 0.064549 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018041 | 0 | 0 | 0.34279 | 1.406 |  | STD2004 | 9.772 | 3.9953 | 1.3237 | 8.2552 | 0 | 8.9823 | 0 | 2.1347 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 49.4923 |  | STD2004 | 2.8632 | 1.1706 | 0 | 1.5021 | 0 | 2.6318 | 0 | 0.62547 | 0 | 0.00077695 | 0 | 0.90624 | 0.17481 | 0 | 0 | 3.3216 | 13.1966 |  | STD2004 | 0 | 0 | 0.013237 | 0.031285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044522 |  | STD2004 | 29.9745 | 12.255 | 1.4468 | 19.1452 | 0 | 27.5523 | 0 | 6.5481 | 0 | 0.0081339 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7739 | 143.0216
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 2.3005e-06 | 0.04978 | 0 | 0.013713 | 0 | 0.0097261 | 0 | 0 | 0 | 0 | -1.4076e-06 | 0 | 0 | 0 | 0.07322 |  | 2004-2007 | 0 | 0 | 0.00023237 | 2.3241 | 0 | 0.4535 | 0 | 0.32165 | 0 | 0 | 0 | 0 | -4.6552e-05 | 0 | 0 | 0 | 3.0995 |  | 2004-2007 | 0 | 0 | 0 | 0.38568 | 0 | 0.13288 | 0 | 0.094244 | 0 | 0 | 0 | 0 | -1.364e-05 | 0 | 0 | 0 | 0.61279 |  | 2004-2007 | 0 | 0 | 2.3237e-06 | 0.010078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01008 |  | 2004-2007 | 0 | 0 | 0.00025398 | 5.1392 | 0 | 1.3911 | 0 | 0.98664 | 0 | 0 | 0 | 0 | -0.00014279 | 0 | 0 | 0 | 7.517
2007-2010 | 0.092042 | 0.064746 | 0.00018819 | 0.029726 | 0 | 0.06052 | 0 | 0.0050436 | 0 | 0 | 0 | 0.0048751 | 0.0087462 | 0 | 0 | 0.026428 | 0.29232 |  | 2007-2010 | 3.044 | 2.1412 | 0.019009 | 0.90544 | 0 | 2.0015 | 0 | 0.1668 | 0 | 0 | 0 | 0.16123 | 0.28925 | 0 | 0 | 0.87401 | 9.6024 |  | 2007-2010 | 0.89187 | 0.62738 | 0 | 0.29911 | 0 | 0.58643 | 0 | 0.048872 | 0 | 0 | 0 | 0.047239 | 0.08475 | 0 | 0 | 0.25608 | 2.8417 |  | 2007-2010 | 0 | 0 | 0.00019009 | -0.0011542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00096415 |  | 2007-2010 | 9.337 | 6.568 | 0.020777 | 3.0052 | 0 | 6.1393 | 0 | 0.51164 | 0 | 0 | 0 | 0.49455 | 0.88724 | 0 | 0 | 2.6809 | 29.6448
2010-2013 | 0.028004 | 0 | 4.8804e-06 | 0.017136 | 0 | 0.023813 | 0 | 0.0051861 | -8.9871e-05 | 0 | 0 | 0.00024055 | 0.00018096 | 0 | 0 | 0.0038274 | 0.078303 |  | 2010-2013 | 0.92612 | 0 | 0.00049297 | 0.71593 | 0 | 0.78753 | 0 | 0.17151 | -0.0029722 | 0 | 0 | 0.0079553 | 0.0059844 | 0 | 0 | 0.12658 | 2.7391 |  | 2010-2013 | 0.27135 | 0 | 0 | 0.14476 | 0 | 0.23074 | 0 | 0.050253 | -0.00087084 | 0 | 0 | 0.0023309 | 0.0017534 | 0 | 0 | 0.037086 | 0.73741 |  | 2010-2013 | 0 | 0 | 4.9297e-06 | 0.0022185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022235 |  | 2010-2013 | 2.8408 | 0 | 0.00053881 | 1.758 | 0 | 2.4157 | 0 | 0.5261 | -0.0091168 | 0 | 0 | 0.024402 | 0.018357 | 0 | 0 | 0.38826 | 7.963
2004-2013 | 0.12005 | 0.064746 | 0.00019537 | 0.096642 | 0 | 0.098046 | 0 | 0.019956 | -8.9871e-05 | 0 | 0 | 0.0051156 | 0.0089258 | 0 | 0 | 0.030255 | 0.44384 |  | 2004-2013 | 3.9701 | 2.1412 | 0.019735 | 3.9455 | 0 | 3.2425 | 0 | 0.65997 | -0.0029722 | 0 | 0 | 0.16918 | 0.29519 | 0 | 0 | 1.0006 | 15.441 |  | 2004-2013 | 1.1632 | 0.62738 | 0 | 0.82956 | 0 | 0.95005 | 0 | 0.19337 | -0.00087084 | 0 | 0 | 0.04957 | 0.086489 | 0 | 0 | 0.29317 | 4.1919 |  | 2004-2013 | 0 | 0 | 0.00019735 | 0.011142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011339 |  | 2004-2013 | 12.1778 | 6.568 | 0.02157 | 9.9025 | 0 | 9.9461 | 0 | 2.0244 | -0.0091168 | 0 | 0 | 0.51895 | 0.90546 | 0 | 0 | 3.0692 | 45.1248
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.01755% | 26.76% |  | 5.049% |  | 15.07% |  | 0% |  | 0% | -0.007802% |  |  | 0% | 5.208% |  | 2004-2007 | 0% | 0% | 0.01755% | 28.15% |  | 5.049% |  | 15.07% |  | 0% |  | 0% | -0.007802% |  |  | 0% | 6.262% |  | 2004-2007 | 0% | 0% |  | 25.68% |  | 5.049% |  | 15.07% |  | 0% |  | 0% | -0.007802% |  |  | 0% | 4.644% |  | 2004-2007 |  |  | 0.01755% | 32.21% | [12 empty] | 22.64% |  | 2004-2007 | 0% | 0% | 0.01755% | 26.84% |  | 5.049% |  | 15.07% |  | 0% |  | 0% | -0.007802% |  |  | 0% | 5.256%
2007-2010 | 31.15% | 53.59% | 1.436% | 21.82% |  | 23.47% |  | 9.2% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 21.93% |  | 2007-2010 | 31.15% | 53.59% | 1.436% | 15.27% |  | 23.47% |  | 9.2% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 20.7% |  | 2007-2010 | 31.15% | 53.59% |  | 26.79% |  | 23.47% |  | 9.2% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 22.58% |  | 2007-2010 |  |  | 1.436% | -5.443% | [12 empty] | -2.799% |  | 2007-2010 | 31.15% | 53.59% | 1.436% | 21.46% |  | 23.47% |  | 9.2% |  | 0% |  | 5.213% | 48.48% |  |  | 7.71% | 21.88%
2010-2013 | 13.77% | 0% | 0.03779% | 16.09% |  | 12.07% |  | 10.42% |  | 0% |  | 0.2713% | 1.947% |  |  | 1.21% | 7.526% |  | 2010-2013 | 13.77% | 0% | 0.03779% | 14.25% |  | 12.07% |  | 10.42% |  | 0% |  | 0.2713% | 1.947% |  |  | 1.21% | 7.445% |  | 2010-2013 | 13.77% | 0% |  | 17.71% |  | 12.07% |  | 10.42% |  | 0% |  | 0.2713% | 1.947% |  |  | 1.21% | 7.569% |  | 2010-2013 |  |  | 0.03779% | 9.921% | [12 empty] | 6.28% |  | 2010-2013 | 13.77% | 0% | 0.03779% | 15.98% |  | 12.07% |  | 10.42% |  | 0% |  | 0.2713% | 1.947% |  |  | 1.21% | 7.522%
2004-2013 | 40.63% | 53.59% | 1.491% | 51.96% |  | 36.1% |  | 30.92% |  | 0% |  | 5.47% | 49.48% |  |  | 8.826% | 31.57% |  | 2004-2013 | 40.63% | 53.59% | 1.491% | 47.79% |  | 36.1% |  | 30.92% |  | 0% |  | 5.47% | 49.48% |  |  | 8.826% | 31.2% |  | 2004-2013 | 40.63% | 53.59% |  | 55.23% |  | 36.1% |  | 30.92% |  | 0% |  | 5.47% | 49.48% |  |  | 8.826% | 31.77% |  | 2004-2013 |  |  | 1.491% | 35.61% | [12 empty] | 25.47% |  | 2004-2013 | 40.63% | 53.59% | 1.491% | 51.72% |  | 36.1% |  | 30.92% |  | 0% |  | 5.47% | 49.48% |  |  | 8.826% | 31.55%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.17488 | 0.056074 | 0.010528 | 0.0036046 | 0 | 0.36227 | 0 | 0.048072 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 1.0656 | 2.141% | CZ 1A | 5.7834 | 1.8544 | 1.0634 | 0.11933 | 0 | 11.9807 | 0 | 1.5898 | 0 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 35.955 | 2.141% | CZ 1A | 1.6945 | 0.54335 | 0 | 0.034911 | 0 | 3.5103 | 0 | 0.46581 | 0 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 10.2231 | 2.141% | CZ 1A | 0 | 0 | 0.010634 | 1.7674e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010636 | 2.141% | CZ 1A | 17.74 | 5.6883 | 1.1623 | 0.36568 | 0 | 36.7495 | 0 | 4.8765 | 0 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 108.1881 | 2.141%
CZ 1B | 0.17484 | 0.056015 | 0.010131 | 0.010964 | 0 | 0.35926 | 0 | 0.062777 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091068 | 0 | 0 | 0.31254 | 1.0841 | 0% | CZ 1B | 5.7824 | 1.8525 | 1.0233 | 0.3746 | 0 | 11.8812 | 0 | 2.0761 | 0 | 0.0026517 | 0 | 2.9238 | 0.30117 | 0 | 0 | 10.3361 | 36.5538 | 0% | CZ 1B | 1.6942 | 0.54278 | 0 | 0.10453 | 0 | 3.4812 | 0 | 0.6083 | 0 | 0.00077695 | 0 | 0.85667 | 0.088243 | 0 | 0 | 3.0284 | 10.4051 | 0% | CZ 1B | 0 | 0 | 0.010233 | 0.00017851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010412 | 0% | CZ 1B | 17.7368 | 5.6823 | 1.1185 | 1.1138 | 0 | 36.4442 | 0 | 6.3683 | 0 | 0.0081339 | 0 | 8.9685 | 0.92381 | 0 | 0 | 31.7047 | 110.0691 | 0%
CZ 2A | 0.17537 | 0.055956 | 0.011548 | 0.043492 | 0 | 0.27015 | 0 | 0.042293 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 1.009 | 13.44% | CZ 2A | 5.7999 | 1.8506 | 1.1665 | 1.498 | 0 | 8.9344 | 0 | 1.3987 | 0 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 34.2119 | 13.44% | CZ 2A | 1.6993 | 0.54221 | 0 | 0.41292 | 0 | 2.6178 | 0 | 0.40982 | 0 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 9.6562 | 13.44% | CZ 2A | 0 | 0 | 0.011665 | 0.00088723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012552 | 13.44% | CZ 2A | 17.7904 | 5.6764 | 1.275 | 4.4199 | 0 | 27.4053 | 0 | 4.2904 | 0 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 102.463 | 13.44%
CZ 2B | 0.17518 | 0.055908 | 0.010969 | 0.018673 | 0 | 0.30865 | 0 | 0.055844 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 1.0354 | 4.829% | CZ 2B | 5.7933 | 1.849 | 1.108 | 0.67034 | 0 | 10.2074 | 0 | 1.8468 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 35.0389 | 4.829% | CZ 2B | 1.6974 | 0.54174 | 0 | 0.17342 | 0 | 2.9907 | 0 | 0.54112 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 9.9187 | 4.829% | CZ 2B | 0 | 0 | 0.01108 | 0.00078472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011865 | 4.829% | CZ 2B | 17.7704 | 5.6715 | 1.211 | 1.9013 | 0 | 31.3101 | 0 | 5.665 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 105.1355 | 4.829%
CZ 3A | 0.17624 | 0.056074 | 0.012353 | 0.10502 | 0 | 0.20165 | 0 | 0.040781 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 1.0023 | 12.66% | CZ 3A | 5.8285 | 1.8544 | 1.2478 | 3.9527 | 0 | 6.6689 | 0 | 1.3487 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 34.4651 | 12.66% | CZ 3A | 1.7077 | 0.54335 | 0 | 0.94923 | 0 | 1.954 | 0 | 0.39516 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 9.5237 | 12.66% | CZ 3A | 0 | 0 | 0.012478 | 0.0071297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019607 | 12.66% | CZ 3A | 17.8783 | 5.6883 | 1.3638 | 10.7167 | 0 | 20.4562 | 0 | 4.1369 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 101.8465 | 12.66%
CZ 3B | 0.17532 | 0.056004 | 0.012078 | 0.031981 | 0 | 0.17767 | 0 | 0.047024 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 0.91021 | 11.83% | CZ 3B | 5.7979 | 1.8521 | 1.22 | 1.3514 | 0 | 5.8757 | 0 | 1.5552 | 0 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 31.2162 | 11.83% | CZ 3B | 1.6988 | 0.54267 | 0 | 0.268 | 0 | 1.7216 | 0 | 0.45566 | 0 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 8.6609 | 11.83% | CZ 3B | 0 | 0 | 0.0122 | 0.0043672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016568 | 11.83% | CZ 3B | 17.7845 | 5.6813 | 1.3335 | 3.283 | 0 | 18.0231 | 0 | 4.7703 | 0 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 92.4813 | 11.83%
CZ 3C | 0.17606 | 0.055967 | 0.01323 | 0.02888 | 0 | 0.052049 | 0 | 0.032121 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.76846 | 2.246% | CZ 3C | 5.8227 | 1.8509 | 1.3363 | 1.0592 | 0 | 1.7213 | 0 | 1.0623 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 26.4168 | 2.246% | CZ 3C | 1.706 | 0.54231 | 0 | 0.26499 | 0 | 0.50434 | 0 | 0.31125 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 7.3032 | 2.246% | CZ 3C | 0 | 0 | 0.013363 | 0.0015482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014911 | 2.246% | CZ 3C | 17.8604 | 5.6775 | 1.4606 | 2.9434 | 0 | 5.28 | 0 | 3.2584 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 78.0866 | 2.246%
CZ 4A | 0.17493 | 0.056069 | 0.013347 | 0.087232 | 0 | 0.15113 | 0 | 0.043731 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.93659 | 19.67% | CZ 4A | 5.7852 | 1.8543 | 1.3482 | 4.5514 | 0 | 4.9982 | 0 | 1.4463 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 33.5475 | 19.67% | CZ 4A | 1.695 | 0.5433 | 0 | 0.60758 | 0 | 1.4644 | 0 | 0.42375 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 8.7084 | 19.67% | CZ 4A | 0 | 0 | 0.013482 | 0.024777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038259 | 19.67% | CZ 4A | 17.7454 | 5.6878 | 1.4735 | 9.0688 | 0 | 15.3313 | 0 | 4.4362 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 95.3494 | 19.67%
CZ 4B | 0.17449 | 0.055994 | 0.013191 | 0.039023 | 0 | 0.13911 | 0 | 0.056699 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.88864 | 0.602% | CZ 4B | 5.7705 | 1.8518 | 1.3324 | 1.8687 | 0 | 4.6004 | 0 | 1.8751 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 30.8631 | 0.602% | CZ 4B | 1.6907 | 0.54257 | 0 | 0.29566 | 0 | 1.3479 | 0 | 0.54941 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 8.4005 | 0.602% | CZ 4B | 0 | 0 | 0.013324 | 0.0085966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021921 | 0.602% | CZ 4B | 17.7004 | 5.6802 | 1.4564 | 4.0348 | 0 | 14.1112 | 0 | 5.7517 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 90.341 | 0.602%
CZ 4C | 0.17591 | 0.056127 | 0.01377 | 0.07915 | 0 | 0.084277 | 0 | 0.041128 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 0.8605 | 3.238% | CZ 4C | 5.8175 | 1.8562 | 1.3909 | 3.4823 | 0 | 2.7871 | 0 | 1.3602 | 0 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 30.2582 | 3.238% | CZ 4C | 1.7045 | 0.54387 | 0 | 0.64363 | 0 | 0.81663 | 0 | 0.39852 | 0 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 8.0814 | 3.238% | CZ 4C | 0 | 0 | 0.013909 | 0.012856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026765 | 3.238% | CZ 4C | 17.8447 | 5.6937 | 1.5203 | 8.1433 | 0 | 8.5493 | 0 | 4.1721 | 0 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 87.5291 | 3.238%
CZ 5A | 0.17539 | 0.056208 | 0.014047 | 0.16033 | 0 | 0.13074 | 0 | 0.045052 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 0.99191 | 17.52% | CZ 5A | 5.8004 | 1.8589 | 1.4189 | 8.616 | 0 | 4.3239 | 0 | 1.4899 | 0 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 37.0719 | 17.52% | CZ 5A | 1.6995 | 0.54464 | 0 | 1.0809 | 0 | 1.2669 | 0 | 0.43654 | 0 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 9.0027 | 17.52% | CZ 5A | 0 | 0 | 0.014189 | 0.049268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063456 | 17.52% | CZ 5A | 17.7921 | 5.7019 | 1.5508 | 16.7014 | 0 | 13.2631 | 0 | 4.5702 | 0 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 101.1852 | 17.52%
CZ 5B | 0.17554 | 0.055849 | 0.013921 | 0.092458 | 0 | 0.098132 | 0 | 0.050199 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091228 | 0 | 0 | 0.31254 | 0.89625 | 5.656% | CZ 5B | 5.8053 | 1.847 | 1.4061 | 4.4862 | 0 | 3.2454 | 0 | 1.6602 | 0 | 0.0026517 | 0 | 2.9238 | 0.3017 | 0 | 0 | 10.3361 | 32.0145 | 5.656% | CZ 5B | 1.701 | 0.54117 | 0 | 0.69216 | 0 | 0.95088 | 0 | 0.48642 | 0 | 0.00077695 | 0 | 0.85667 | 0.088398 | 0 | 0 | 3.0284 | 8.3459 | 5.656% | CZ 5B | 0 | 0 | 0.014061 | 0.021239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0353 | 5.656% | CZ 5B | 17.8073 | 5.6655 | 1.5369 | 9.5676 | 0 | 9.9548 | 0 | 5.0924 | 0 | 0.0081339 | 0 | 8.9685 | 0.92544 | 0 | 0 | 31.7047 | 91.2313 | 5.656%
CZ 5C | 0.17898 | 0.056165 | 0.014055 | 0.10814 | 0 | 0.045907 | 0 | 0.040695 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.85409 | 0% | CZ 5C | 5.919 | 1.8574 | 1.4197 | 4.7785 | 0 | 1.5182 | 0 | 1.3458 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 30.4028 | 0% | CZ 5C | 1.7343 | 0.54423 | 0 | 0.87645 | 0 | 0.44483 | 0 | 0.39433 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 7.9683 | 0% | CZ 5C | 0 | 0 | 0.014197 | 0.017872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032069 | 0% | CZ 5C | 18.1559 | 5.6975 | 1.5518 | 11.129 | 0 | 4.6569 | 0 | 4.1282 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 86.9256 | 0%
CZ 6A | 0.17583 | 0.056282 | 0.014673 | 0.18831 | 0 | 0.088061 | 0 | 0.04317 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.97648 | 4.935% | CZ 6A | 5.8151 | 1.8613 | 1.4821 | 10.301 | 0 | 2.9123 | 0 | 1.4277 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 37.3637 | 4.935% | CZ 6A | 1.7038 | 0.54537 | 0 | 1.2437 | 0 | 0.8533 | 0 | 0.41831 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 8.7388 | 4.935% | CZ 6A | 0 | 0 | 0.014821 | 0.060561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075383 | 4.935% | CZ 6A | 17.8371 | 5.7095 | 1.62 | 19.6401 | 0 | 8.9332 | 0 | 4.3793 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 99.7254 | 4.935%
CZ 6B | 0.17561 | 0.055972 | 0.014761 | 0.14553 | 0 | 0.067631 | 0 | 0.050285 | 0 | 8.0182e-05 | 0 | 0.088409 | 0.0091174 | 0 | 0 | 0.31254 | 0.91993 | 0.5759% | CZ 6B | 5.8078 | 1.8511 | 1.491 | 7.7037 | 0 | 2.2366 | 0 | 1.663 | 0 | 0.0026517 | 0 | 2.9238 | 0.30153 | 0 | 0 | 10.3361 | 34.3172 | 0.5759% | CZ 6B | 1.7017 | 0.54236 | 0 | 0.99781 | 0 | 0.65533 | 0 | 0.48725 | 0 | 0.00077695 | 0 | 0.85667 | 0.088346 | 0 | 0 | 3.0284 | 8.3587 | 0.5759% | CZ 6B | 0 | 0 | 0.01491 | 0.042981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057891 | 0.5759% | CZ 6B | 17.8149 | 5.678 | 1.6296 | 15.1439 | 0 | 6.8607 | 0 | 5.101 | 0 | 0.0081339 | 0 | 8.9685 | 0.9249 | 0 | 0 | 31.7047 | 93.8344 | 0.5759%
CZ 7 | 0.17468 | 0.056138 | 0.015665 | 0.18368 | 0 | 0.064905 | 0 | 0.0468 | 0.013524 | 8.0182e-05 | 0 | 0.088409 | 0.0091121 | 0 | 0 | 0.31254 | 0.96553 | 0.5453% | CZ 7 | 5.7769 | 1.8566 | 1.5823 | 6.7428 | 0 | 2.1465 | 0 | 1.5477 | 0.44726 | 0.0026517 | 0 | 2.9238 | 0.30135 | 0 | 0 | 10.3361 | 33.6639 | 0.5453% | CZ 7 | 1.6926 | 0.54397 | 0 | 1.6846 | 0 | 0.62892 | 0 | 0.45348 | 0.13105 | 0.00077695 | 0 | 0.85667 | 0.088295 | 0 | 0 | 3.0284 | 9.1088 | 0.5453% | CZ 7 | 0 | 0 | 0.015823 | 0.0099327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025756 | 0.5453% | CZ 7 | 17.72 | 5.6948 | 1.7295 | 18.7216 | 0 | 6.5841 | 0 | 4.7475 | 1.3719 | 0.0081339 | 0 | 8.9685 | 0.92436 | 0 | 0 | 31.7047 | 98.1751 | 0.5453%
CZ 8 | 0.18081 | 0.056534 | 0.016887 | 0.34202 | 0 | 0.035398 | 0 | 0.048264 | 0.014272 | 8.0182e-05 | 0 | 0.088409 | 0.0091228 | 0 | 0 | 0.31254 | 1.1043 | 0.113% | CZ 8 | 5.9797 | 1.8696 | 1.7057 | 15.1944 | 0 | 1.1707 | 0 | 1.5962 | 0.47201 | 0.0026517 | 0 | 2.9238 | 0.3017 | 0 | 0 | 10.3361 | 41.5525 | 0.113% | CZ 8 | 1.752 | 0.5478 | 0 | 2.7603 | 0 | 0.343 | 0 | 0.46767 | 0.1383 | 0.00077695 | 0 | 0.85667 | 0.088398 | 0 | 0 | 3.0284 | 9.9834 | 0.113% | CZ 8 | 0 | 0 | 0.017057 | 0.057735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074793 | 0.113% | CZ 8 | 18.3419 | 5.7349 | 1.8643 | 35.208 | 0 | 3.5908 | 0 | 4.8961 | 1.4478 | 0.0081339 | 0 | 8.9685 | 0.92544 | 0 | 0 | 31.7047 | 112.6908 | 0.113%
Us Weighted | 0.17544 | 0.056061 | 0.01291 | 0.089351 | 0 | 0.17356 | 0 | 0.044594 | 8.9871e-05 | 8.0182e-05 | 0 | 0.088409 | 0.0091151 | 0 | 0 | 0.31254 | 0.96214 | 100% | Us Weighted | 5.8019 | 1.854 | 1.304 | 4.3098 | 0 | 5.7398 | 0 | 1.4748 | 0.0029722 | 0.0026517 | 0 | 2.9238 | 0.30145 | 0 | 0 | 10.3361 | 34.0512 | 100% | Us Weighted | 1.6999 | 0.54322 | 0 | 0.67257 | 0 | 1.6818 | 0 | 0.4321 | 0.00087084 | 0.00077695 | 0 | 0.85667 | 0.088324 | 0 | 0 | 3.0284 | 9.0047 | 100% | Us Weighted | 0 | 0 | 0.01304 | 0.020143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033183 | 100% | Us Weighted | 17.7967 | 5.687 | 1.4253 | 9.2427 | 0 | 17.6063 | 0 | 4.5237 | 0.0091168 | 0.0081339 | 0 | 8.9685 | 0.92467 | 0 | 0 | 31.7047 | 97.8968 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.20594 | 0.056074 | 0.010535 | 0.0085973 | 0 | 0.44149 | 0 | 0.057966 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 1.195 | 2.141% | CZ 1A | 6.8109 | 1.8544 | 1.0641 | 0.28444 | 0 | 14.6008 | 0 | 1.917 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 40.2362 | 2.141% | CZ 1A | 1.9956 | 0.54335 | 0 | 0.083289 | 0 | 4.278 | 0 | 0.56168 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 11.4772 | 2.141% | CZ 1A | 0 | 0 | 0.010641 | 1.7674e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010643 | 2.141% | CZ 1A | 20.8916 | 5.6883 | 1.1631 | 0.87215 | 0 | 44.7863 | 0 | 5.8803 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 121.3186 | 2.141%
CZ 1B | 0.2077 | 0.056015 | 0.010131 | 0.020129 | 0 | 0.41707 | 0 | 0.079439 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092992 | 0 | 0 | 0.31637 | 1.2049 | 0% | CZ 1B | 6.869 | 1.8525 | 1.0233 | 0.6746 | 0 | 13.7931 | 0 | 2.6272 | 0 | 0.0026517 | 0 | 2.9318 | 0.30754 | 0 | 0 | 10.4626 | 40.5443 | 0% | CZ 1B | 2.0126 | 0.54278 | 0 | 0.19377 | 0 | 4.0413 | 0 | 0.76975 | 0 | 0.00077695 | 0 | 0.859 | 0.090108 | 0 | 0 | 3.0655 | 11.5757 | 0% | CZ 1B | 0 | 0 | 0.010233 | 0.00013255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010366 | 0% | CZ 1B | 21.07 | 5.6823 | 1.1185 | 2.0431 | 0 | 42.3087 | 0 | 8.0585 | 0 | 0.0081339 | 0 | 8.9929 | 0.94334 | 0 | 0 | 32.093 | 122.3186 | 0%
CZ 2A | 0.20867 | 0.055956 | 0.011553 | 0.06781 | 0 | 0.33084 | 0 | 0.052936 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092992 | 0 | 0 | 0.31637 | 1.1422 | 13.44% | CZ 2A | 6.901 | 1.8506 | 1.167 | 2.3034 | 0 | 10.9412 | 0 | 1.7507 | 0 | 0.0026517 | 0 | 2.9318 | 0.30754 | 0 | 0 | 10.4626 | 38.6186 | 13.44% | CZ 2A | 2.022 | 0.54221 | 0 | 0.64839 | 0 | 3.2057 | 0 | 0.51294 | 0 | 0.00077695 | 0 | 0.859 | 0.090108 | 0 | 0 | 3.0655 | 10.9467 | 13.44% | CZ 2A | 0 | 0 | 0.01167 | 0.0009049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012575 | 13.44% | CZ 2A | 21.1682 | 5.6764 | 1.2755 | 6.8869 | 0 | 33.561 | 0 | 5.37 | 0 | 0.0081339 | 0 | 8.9929 | 0.94334 | 0 | 0 | 32.093 | 115.9754 | 13.44%
CZ 2B | 0.20995 | 0.055908 | 0.010969 | 0.029599 | 0 | 0.36134 | 0 | 0.071768 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0093045 | 0 | 0 | 0.31637 | 1.1539 | 4.829% | CZ 2B | 6.9433 | 1.849 | 1.108 | 1.0197 | 0 | 11.9501 | 0 | 2.3735 | 0 | 0.0026517 | 0 | 2.9318 | 0.30771 | 0 | 0 | 10.4626 | 38.9483 | 4.829% | CZ 2B | 2.0344 | 0.54174 | 0 | 0.281 | 0 | 3.5014 | 0 | 0.69542 | 0 | 0.00077695 | 0 | 0.859 | 0.090159 | 0 | 0 | 3.0655 | 11.0693 | 4.829% | CZ 2B | 0 | 0 | 0.01108 | 0.00060622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011686 | 4.829% | CZ 2B | 21.2978 | 5.6715 | 1.211 | 3.008 | 0 | 36.6557 | 0 | 7.2804 | 0 | 0.0081339 | 0 | 8.9929 | 0.94388 | 0 | 0 | 32.093 | 117.1623 | 4.829%
CZ 3A | 0.20403 | 0.056074 | 0.01236 | 0.099775 | 0 | 0.23399 | 0 | 0.045704 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092992 | 0 | 0 | 0.31637 | 1.0663 | 12.66% | CZ 3A | 6.7474 | 1.8544 | 1.2485 | 3.728 | 0 | 7.7385 | 0 | 1.5115 | 0 | 0.0026517 | 0 | 2.9318 | 0.30754 | 0 | 0 | 10.4626 | 36.5329 | 12.66% | CZ 3A | 1.977 | 0.54335 | 0 | 0.90572 | 0 | 2.2673 | 0 | 0.44286 | 0 | 0.00077695 | 0 | 0.859 | 0.090108 | 0 | 0 | 3.0655 | 10.1517 | 12.66% | CZ 3A | 0 | 0 | 0.012485 | 0.0063679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018853 | 12.66% | CZ 3A | 20.697 | 5.6883 | 1.3646 | 10.178 | 0 | 23.7369 | 0 | 4.6363 | 0 | 0.0081339 | 0 | 8.9929 | 0.94334 | 0 | 0 | 32.093 | 108.3384 | 12.66%
CZ 3B | 0.20308 | 0.056004 | 0.012075 | 0.027796 | 0 | 0.1942 | 0 | 0.055497 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 0.96304 | 11.83% | CZ 3B | 6.7163 | 1.8521 | 1.2197 | 1.1796 | 0 | 6.4223 | 0 | 1.8354 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 32.9298 | 11.83% | CZ 3B | 1.9679 | 0.54267 | 0 | 0.2322 | 0 | 1.8817 | 0 | 0.53775 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 9.1776 | 11.83% | CZ 3B | 0 | 0 | 0.012197 | 0.0038706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016067 | 11.83% | CZ 3B | 20.6015 | 5.6813 | 1.3331 | 2.854 | 0 | 19.6997 | 0 | 5.6297 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 97.8362 | 11.83%
CZ 3C | 0.20384 | 0.055967 | 0.013231 | 0.034494 | 0 | 0.061868 | 0 | 0.03953 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 0.82332 | 2.246% | CZ 3C | 6.7412 | 1.8509 | 1.3365 | 1.2334 | 0 | 2.0461 | 0 | 1.3073 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 28.2198 | 2.246% | CZ 3C | 1.9752 | 0.54231 | 0 | 0.32104 | 0 | 0.59949 | 0 | 0.38304 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 7.8364 | 2.246% | CZ 3C | 0 | 0 | 0.013365 | 0.0013768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014742 | 2.246% | CZ 3C | 20.678 | 5.6775 | 1.4608 | 3.5114 | 0 | 6.2761 | 0 | 4.01 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 83.6506 | 2.246%
CZ 4A | 0.20086 | 0.056069 | 0.013354 | 0.10501 | 0 | 0.16433 | 0 | 0.046094 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 1.0001 | 19.67% | CZ 4A | 6.6428 | 1.8543 | 1.3489 | 5.2705 | 0 | 5.4346 | 0 | 1.5244 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 35.7798 | 19.67% | CZ 4A | 1.9463 | 0.5433 | 0 | 0.76115 | 0 | 1.5923 | 0 | 0.44664 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 9.3051 | 19.67% | CZ 4A | 0 | 0 | 0.013489 | 0.026727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040215 | 19.67% | CZ 4A | 20.3759 | 5.6878 | 1.4743 | 10.8897 | 0 | 16.6701 | 0 | 4.6759 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 101.8106 | 19.67%
CZ 4B | 0.20032 | 0.055994 | 0.0132 | 0.05134 | 0 | 0.14911 | 0 | 0.060452 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092885 | 0 | 0 | 0.31637 | 0.9448 | 0.602% | CZ 4B | 6.6249 | 1.8518 | 1.3333 | 2.3306 | 0 | 4.9312 | 0 | 1.9992 | 0 | 0.0026517 | 0 | 2.9318 | 0.30718 | 0 | 0 | 10.4626 | 32.7753 | 0.602% | CZ 4B | 1.9411 | 0.54257 | 0 | 0.40723 | 0 | 1.4448 | 0 | 0.58577 | 0 | 0.00077695 | 0 | 0.859 | 0.090004 | 0 | 0 | 3.0655 | 8.9368 | 0.602% | CZ 4B | 0 | 0 | 0.013333 | 0.0094078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022741 | 0.602% | CZ 4B | 20.3212 | 5.6802 | 1.4573 | 5.2915 | 0 | 15.1258 | 0 | 6.1324 | 0 | 0.0081339 | 0 | 8.9929 | 0.94225 | 0 | 0 | 32.093 | 96.0447 | 0.602%
CZ 4C | 0.20236 | 0.056127 | 0.013772 | 0.094015 | 0 | 0.087986 | 0 | 0.04464 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092885 | 0 | 0 | 0.31637 | 0.91328 | 3.238% | CZ 4C | 6.6923 | 1.8562 | 1.3911 | 4.0494 | 0 | 2.9098 | 0 | 1.4763 | 0 | 0.0026517 | 0 | 2.9318 | 0.30718 | 0 | 0 | 10.4626 | 32.0794 | 3.238% | CZ 4C | 1.9608 | 0.54387 | 0 | 0.7769 | 0 | 0.85257 | 0 | 0.43255 | 0 | 0.00077695 | 0 | 0.859 | 0.090004 | 0 | 0 | 3.0655 | 8.582 | 3.238% | CZ 4C | 0 | 0 | 0.013911 | 0.013978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027889 | 3.238% | CZ 4C | 20.5278 | 5.6937 | 1.5205 | 9.6612 | 0 | 8.9256 | 0 | 4.5284 | 0 | 0.0081339 | 0 | 8.9929 | 0.94225 | 0 | 0 | 32.093 | 92.8935 | 3.238%
CZ 5A | 0.20123 | 0.056208 | 0.014054 | 0.19287 | 0 | 0.14038 | 0 | 0.046335 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 1.0655 | 17.52% | CZ 5A | 6.655 | 1.8589 | 1.4196 | 10.0192 | 0 | 4.6427 | 0 | 1.5323 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 39.8321 | 17.52% | CZ 5A | 1.9499 | 0.54464 | 0 | 1.3497 | 0 | 1.3603 | 0 | 0.44897 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 9.6688 | 17.52% | CZ 5A | 0 | 0 | 0.014196 | 0.054128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068324 | 17.52% | CZ 5A | 20.4134 | 5.7019 | 1.5516 | 20.0459 | 0 | 14.2408 | 0 | 4.7003 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 108.6906 | 17.52%
CZ 5B | 0.20199 | 0.055849 | 0.013928 | 0.11634 | 0 | 0.1041 | 0 | 0.051985 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092992 | 0 | 0 | 0.31637 | 0.95859 | 5.656% | CZ 5B | 6.6802 | 1.847 | 1.4068 | 5.4503 | 0 | 3.4428 | 0 | 1.7192 | 0 | 0.0026517 | 0 | 2.9318 | 0.30754 | 0 | 0 | 10.4626 | 34.2511 | 5.656% | CZ 5B | 1.9573 | 0.54117 | 0 | 0.89872 | 0 | 1.0087 | 0 | 0.50372 | 0 | 0.00077695 | 0 | 0.859 | 0.090108 | 0 | 0 | 3.0655 | 8.9251 | 5.656% | CZ 5B | 0 | 0 | 0.014068 | 0.02383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037898 | 5.656% | CZ 5B | 20.4909 | 5.6655 | 1.5377 | 12.0133 | 0 | 10.5605 | 0 | 5.2735 | 0 | 0.0081339 | 0 | 8.9929 | 0.94334 | 0 | 0 | 32.093 | 97.5788 | 5.656%
CZ 5C | 0.20693 | 0.056165 | 0.014062 | 0.13098 | 0 | 0.04719 | 0 | 0.043582 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0093099 | 0 | 0 | 0.31637 | 0.91332 | 0% | CZ 5C | 6.8436 | 1.8574 | 1.4205 | 5.6748 | 0 | 1.5606 | 0 | 1.4413 | 0 | 0.0026517 | 0 | 2.9318 | 0.30789 | 0 | 0 | 10.4626 | 32.5031 | 0% | CZ 5C | 2.0052 | 0.54423 | 0 | 1.0776 | 0 | 0.45726 | 0 | 0.4223 | 0 | 0.00077695 | 0 | 0.859 | 0.090211 | 0 | 0 | 3.0655 | 8.5221 | 0% | CZ 5C | 0 | 0 | 0.014205 | 0.019968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034173 | 0% | CZ 5C | 20.9919 | 5.6975 | 1.5526 | 13.4642 | 0 | 4.7871 | 0 | 4.421 | 0 | 0.0081339 | 0 | 8.9929 | 0.94442 | 0 | 0 | 32.093 | 92.9528 | 0%
CZ 6A | 0.20193 | 0.056282 | 0.01468 | 0.2269 | 0 | 0.094604 | 0 | 0.044223 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092992 | 0 | 0 | 0.31637 | 1.053 | 4.935% | CZ 6A | 6.6781 | 1.8613 | 1.4828 | 11.9586 | 0 | 3.1287 | 0 | 1.4625 | 0 | 0.0026517 | 0 | 2.9318 | 0.30754 | 0 | 0 | 10.4626 | 40.2767 | 4.935% | CZ 6A | 1.9567 | 0.54537 | 0 | 1.5633 | 0 | 0.9167 | 0 | 0.42851 | 0 | 0.00077695 | 0 | 0.859 | 0.090108 | 0 | 0 | 3.0655 | 9.4259 | 4.935% | CZ 6A | 0 | 0 | 0.014828 | 0.066231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08106 | 4.935% | CZ 6A | 20.4844 | 5.7095 | 1.6207 | 23.605 | 0 | 9.5969 | 0 | 4.4861 | 0 | 0.0081339 | 0 | 8.9929 | 0.94334 | 0 | 0 | 32.093 | 107.54 | 4.935%
CZ 6B | 0.20208 | 0.055972 | 0.014768 | 0.18362 | 0 | 0.070742 | 0 | 0.051659 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092885 | 0 | 0 | 0.31637 | 0.99322 | 0.5759% | CZ 6B | 6.6831 | 1.8511 | 1.4917 | 9.3156 | 0 | 2.3395 | 0 | 1.7084 | 0 | 0.0026517 | 0 | 2.9318 | 0.30718 | 0 | 0 | 10.4626 | 37.0937 | 0.5759% | CZ 6B | 1.9581 | 0.54236 | 0 | 1.3167 | 0 | 0.68548 | 0 | 0.50056 | 0 | 0.00077695 | 0 | 0.859 | 0.090004 | 0 | 0 | 3.0655 | 9.0185 | 0.5759% | CZ 6B | 0 | 0 | 0.014917 | 0.048218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063135 | 0.5759% | CZ 6B | 20.4996 | 5.678 | 1.6304 | 19.0545 | 0 | 7.1763 | 0 | 5.2404 | 0 | 0.0081339 | 0 | 8.9929 | 0.94225 | 0 | 0 | 32.093 | 101.3154 | 0.5759%
CZ 7 | 0.20192 | 0.056138 | 0.015667 | 0.32972 | 0 | 0.06584 | 0 | 0.046233 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092938 | 0 | 0 | 0.31637 | 1.1299 | 0.5453% | CZ 7 | 6.6778 | 1.8566 | 1.5825 | 17.8191 | 0 | 2.1774 | 0 | 1.529 | 0 | 0.0026517 | 0 | 2.9318 | 0.30736 | 0 | 0 | 10.4626 | 45.3468 | 0.5453% | CZ 7 | 1.9566 | 0.54397 | 0 | 2.2087 | 0 | 0.63798 | 0 | 0.44799 | 0 | 0.00077695 | 0 | 0.859 | 0.090056 | 0 | 0 | 3.0655 | 9.8105 | 0.5453% | CZ 7 | 0 | 0 | 0.015825 | 0.10281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11863 | 0.5453% | CZ 7 | 20.4833 | 5.6948 | 1.7297 | 34.3595 | 0 | 6.679 | 0 | 4.69 | 0 | 0.0081339 | 0 | 8.9929 | 0.94279 | 0 | 0 | 32.093 | 115.6732 | 0.5453%
CZ 8 | 0.21048 | 0.056534 | 0.016895 | 0.55498 | 0 | 0.035211 | 0 | 0.048221 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0093099 | 0 | 0 | 0.31637 | 1.3367 | 0.113% | CZ 8 | 6.961 | 1.8696 | 1.7066 | 30.841 | 0 | 1.1645 | 0 | 1.5948 | 0 | 0.0026517 | 0 | 2.9318 | 0.30789 | 0 | 0 | 10.4626 | 57.8424 | 0.113% | CZ 8 | 2.0395 | 0.5478 | 0 | 3.5968 | 0 | 0.34118 | 0 | 0.46726 | 0 | 0.00077695 | 0 | 0.859 | 0.090211 | 0 | 0 | 3.0655 | 11.0081 | 0.113% | CZ 8 | 0 | 0 | 0.017066 | 0.18565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20272 | 0.113% | CZ 8 | 21.352 | 5.7349 | 1.8653 | 57.9463 | 0 | 3.5719 | 0 | 4.8917 | 0 | 0.0081339 | 0 | 8.9929 | 0.94442 | 0 | 0 | 32.093 | 137.4006 | 0.113%
Us Weighted | 0.20344 | 0.056061 | 0.012914 | 0.10649 | 0 | 0.19737 | 0 | 0.04978 | 0 | 8.0182e-05 | 0 | 0.088649 | 0.0092961 | 0 | 0 | 0.31637 | 1.0404 | 100% | Us Weighted | 6.728 | 1.854 | 1.3045 | 5.0257 | 0 | 6.5273 | 0 | 1.6463 | 0 | 0.0026517 | 0 | 2.9318 | 0.30744 | 0 | 0 | 10.4626 | 36.7904 | 100% | Us Weighted | 1.9713 | 0.54322 | 0 | 0.81733 | 0 | 1.9125 | 0 | 0.48236 | 0 | 0.00077695 | 0 | 0.859 | 0.090078 | 0 | 0 | 3.0655 | 9.7421 | 100% | Us Weighted | 0 | 0 | 0.013045 | 0.022361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035406 | 100% | Us Weighted | 20.6375 | 5.687 | 1.4258 | 11.0008 | 0 | 20.0219 | 0 | 5.0498 | 0 | 0.0081339 | 0 | 8.9929 | 0.94302 | 0 | 0 | 32.093 | 105.8598 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29548 | 0.12104 | 0.010761 | 0.0076671 | 0 | 0.55085 | 0 | 0.066225 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.01805 | 0 | 0 | 0.34279 | 1.5065 | 2.141% | CZ 1A | 9.772 | 4.0029 | 1.0869 | 0.25404 | 0 | 18.2174 | 0 | 2.1902 | 0 | 0.0026517 | 0 | 3.093 | 0.59693 | 0 | 0 | 11.3367 | 50.5526 | 2.141% | CZ 1A | 2.8632 | 1.1728 | 0 | 0.074225 | 0 | 5.3376 | 0 | 0.64171 | 0 | 0.00077695 | 0 | 0.90624 | 0.1749 | 0 | 0 | 3.3216 | 14.4931 | 2.141% | CZ 1A | 0 | 0 | 0.010869 | 7.0696e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010877 | 2.141% | CZ 1A | 29.9745 | 12.2784 | 1.188 | 0.77783 | 0 | 55.8798 | 0 | 6.7181 | 0 | 0.0081339 | 0 | 9.4875 | 1.831 | 0 | 0 | 34.7739 | 152.9172 | 2.141%
CZ 1B | 0.29548 | 0.12094 | 0.01036 | 0.029272 | 0 | 0.50237 | 0 | 0.098693 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.5115 | 0% | CZ 1B | 9.772 | 3.9995 | 1.0465 | 0.96877 | 0 | 16.614 | 0 | 3.2639 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 50.6935 | 0% | CZ 1B | 2.8632 | 1.1718 | 0 | 0.28354 | 0 | 4.8679 | 0 | 0.95632 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 14.5461 | 0% | CZ 1B | 0 | 0 | 0.010465 | 1.0604e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010475 | 0% | CZ 1B | 29.9745 | 12.2681 | 1.1438 | 2.9695 | 0 | 50.9615 | 0 | 10.0117 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 153.4286 | 0%
CZ 2A | 0.29548 | 0.12083 | 0.011751 | 0.062755 | 0 | 0.4259 | 0 | 0.059698 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4309 | 13.44% | CZ 2A | 9.772 | 3.9962 | 1.187 | 2.29 | 0 | 14.0851 | 0 | 1.9743 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 48.3334 | 13.44% | CZ 2A | 2.8632 | 1.1709 | 0 | 0.57748 | 0 | 4.1269 | 0 | 0.57847 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 13.7203 | 13.44% | CZ 2A | 0 | 0 | 0.01187 | 0.0031901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01506 | 13.44% | CZ 2A | 29.9745 | 12.2578 | 1.2974 | 6.3943 | 0 | 43.2045 | 0 | 6.056 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 145.2839 | 13.44%
CZ 2B | 0.29548 | 0.12075 | 0.011181 | 0.044713 | 0 | 0.43616 | 0 | 0.0827 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4454 | 4.829% | CZ 2B | 9.772 | 3.9933 | 1.1294 | 1.4859 | 0 | 14.4245 | 0 | 2.735 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 48.5689 | 4.829% | CZ 2B | 2.8632 | 1.17 | 0 | 0.43224 | 0 | 4.2264 | 0 | 0.80135 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 13.8966 | 4.829% | CZ 2B | 0 | 0 | 0.011294 | 0.00010604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0114 | 4.829% | CZ 2B | 29.9745 | 12.2491 | 1.2344 | 4.5367 | 0 | 44.2457 | 0 | 8.3893 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 146.7291 | 4.829%
CZ 3A | 0.29548 | 0.1209 | 0.012544 | 0.1104 | 0 | 0.30824 | 0 | 0.052134 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.3541 | 12.66% | CZ 3A | 9.772 | 3.9985 | 1.267 | 4.9415 | 0 | 10.1938 | 0 | 1.7242 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 46.9258 | 12.66% | CZ 3A | 2.8632 | 1.1715 | 0 | 0.88567 | 0 | 2.9868 | 0 | 0.50517 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 12.8157 | 12.66% | CZ 3A | 0 | 0 | 0.01267 | 0.019187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031857 | 12.66% | CZ 3A | 29.9745 | 12.2648 | 1.3849 | 11.3692 | 0 | 31.2683 | 0 | 5.2887 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 137.6498 | 12.66%
CZ 3B | 0.29548 | 0.12091 | 0.012278 | 0.041263 | 0 | 0.24903 | 0 | 0.06166 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.2351 | 11.83% | CZ 3B | 9.772 | 3.9988 | 1.2402 | 1.4901 | 0 | 8.2359 | 0 | 2.0392 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 41.8052 | 11.83% | CZ 3B | 2.8632 | 1.1716 | 0 | 0.38195 | 0 | 2.4131 | 0 | 0.59747 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 11.8308 | 11.83% | CZ 3B | 0 | 0 | 0.012402 | 0.0018646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014266 | 11.83% | CZ 3B | 29.9745 | 12.2659 | 1.3555 | 4.2024 | 0 | 25.2628 | 0 | 6.255 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 125.4161 | 11.83%
CZ 3C | 0.29548 | 0.12073 | 0.013412 | 0.048908 | 0 | 0.13039 | 0 | 0.040668 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.01805 | 0 | 0 | 0.34279 | 1.104 | 2.246% | CZ 3C | 9.772 | 3.9928 | 1.3547 | 1.6619 | 0 | 4.3122 | 0 | 1.345 | 0 | 0.0026517 | 0 | 3.093 | 0.59693 | 0 | 0 | 11.3367 | 37.4678 | 2.246% | CZ 3C | 2.8632 | 1.1699 | 0 | 0.46757 | 0 | 1.2635 | 0 | 0.39407 | 0 | 0.00077695 | 0 | 0.90624 | 0.1749 | 0 | 0 | 3.3216 | 10.5617 | 2.246% | CZ 3C | 0 | 0 | 0.013547 | 0.000661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014208 | 2.246% | CZ 3C | 29.9745 | 12.2475 | 1.4807 | 4.9672 | 0 | 13.2273 | 0 | 4.1255 | 0 | 0.0081339 | 0 | 9.4875 | 1.831 | 0 | 0 | 34.7739 | 112.1233 | 2.246%
CZ 4A | 0.29548 | 0.12084 | 0.013534 | 0.14493 | 0 | 0.22576 | 0 | 0.049836 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.3048 | 19.67% | CZ 4A | 9.772 | 3.9965 | 1.3671 | 6.3873 | 0 | 7.4662 | 0 | 1.6481 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 45.6663 | 19.67% | CZ 4A | 2.8632 | 1.171 | 0 | 1.177 | 0 | 2.1876 | 0 | 0.4829 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 12.2851 | 19.67% | CZ 4A | 0 | 0 | 0.013671 | 0.023701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037372 | 19.67% | CZ 4A | 29.9745 | 12.2589 | 1.4942 | 14.9128 | 0 | 22.9018 | 0 | 5.0555 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 132.6976 | 19.67%
CZ 4B | 0.29548 | 0.12082 | 0.013377 | 0.074689 | 0 | 0.19778 | 0 | 0.063665 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018034 | 0 | 0 | 0.34279 | 1.2202 | 0.602% | CZ 4B | 9.772 | 3.9956 | 1.3512 | 2.813 | 0 | 6.5409 | 0 | 2.1055 | 0 | 0.0026517 | 0 | 3.093 | 0.5964 | 0 | 0 | 11.3367 | 41.6069 | 0.602% | CZ 4B | 2.8632 | 1.1707 | 0 | 0.67481 | 0 | 1.9165 | 0 | 0.6169 | 0 | 0.00077695 | 0 | 0.90624 | 0.17474 | 0 | 0 | 3.3216 | 11.6454 | 0.602% | CZ 4B | 0 | 0 | 0.013512 | 0.0050989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018611 | 0.602% | CZ 4B | 29.9745 | 12.2561 | 1.4768 | 7.6219 | 0 | 20.0636 | 0 | 6.4583 | 0 | 0.0081339 | 0 | 9.4875 | 1.8294 | 0 | 0 | 34.7739 | 123.9501 | 0.602%
CZ 4C | 0.29548 | 0.12079 | 0.013956 | 0.13769 | 0 | 0.13233 | 0 | 0.046896 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.2016 | 3.238% | CZ 4C | 9.772 | 3.9946 | 1.4097 | 5.3216 | 0 | 4.3764 | 0 | 1.5509 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 41.454 | 3.238% | CZ 4C | 2.8632 | 1.1704 | 0 | 1.2247 | 0 | 1.2823 | 0 | 0.45441 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.3984 | 3.238% | CZ 4C | 0 | 0 | 0.014097 | 0.011417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025514 | 3.238% | CZ 4C | 29.9745 | 12.2529 | 1.5408 | 14.0691 | 0 | 13.4242 | 0 | 4.7572 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 122.1181 | 3.238%
CZ 5A | 0.29548 | 0.1207 | 0.014234 | 0.25205 | 0 | 0.17548 | 0 | 0.050344 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.3627 | 17.52% | CZ 5A | 9.772 | 3.9917 | 1.4378 | 11.4517 | 0 | 5.8034 | 0 | 1.6649 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 49.1506 | 17.52% | CZ 5A | 2.8632 | 1.1696 | 0 | 1.9978 | 0 | 1.7004 | 0 | 0.48782 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 12.6223 | 17.52% | CZ 5A | 0 | 0 | 0.014378 | 0.04633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060708 | 17.52% | CZ 5A | 29.9745 | 12.2442 | 1.5715 | 25.9794 | 0 | 17.8013 | 0 | 5.107 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 138.7779 | 17.52%
CZ 5B | 0.29548 | 0.12065 | 0.014108 | 0.15789 | 0 | 0.14745 | 0 | 0.05455 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.2446 | 5.656% | CZ 5B | 9.772 | 3.99 | 1.425 | 6.4343 | 0 | 4.8765 | 0 | 1.8041 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 43.3307 | 5.656% | CZ 5B | 2.8632 | 1.1691 | 0 | 1.357 | 0 | 1.4288 | 0 | 0.52859 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.7501 | 5.656% | CZ 5B | 0 | 0 | 0.01425 | 0.018027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032278 | 5.656% | CZ 5B | 29.9745 | 12.2388 | 1.5576 | 16.1771 | 0 | 14.9582 | 0 | 5.5338 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 126.5393 | 5.656%
CZ 5C | 0.29548 | 0.12058 | 0.014244 | 0.18888 | 0 | 0.090296 | 0 | 0.044116 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.208 | 0% | CZ 5C | 9.772 | 3.9877 | 1.4388 | 7.4189 | 0 | 2.9862 | 0 | 1.459 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 42.0915 | 0% | CZ 5C | 2.8632 | 1.1684 | 0 | 1.663 | 0 | 0.87495 | 0 | 0.42748 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.4004 | 0% | CZ 5C | 0 | 0 | 0.014388 | 0.017432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03182 | 0% | CZ 5C | 29.9745 | 12.2317 | 1.5726 | 19.3151 | 0 | 9.1598 | 0 | 4.4753 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 122.8285 | 0%
CZ 6A | 0.29548 | 0.12071 | 0.014859 | 0.29824 | 0 | 0.12574 | 0 | 0.047484 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.357 | 4.935% | CZ 6A | 9.772 | 3.9919 | 1.5009 | 13.9899 | 0 | 4.1583 | 0 | 1.5704 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 50.0124 | 4.935% | CZ 6A | 2.8632 | 1.1696 | 0 | 2.3014 | 0 | 1.2184 | 0 | 0.46011 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 12.4161 | 4.935% | CZ 6A | 0 | 0 | 0.015009 | 0.061353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076362 | 4.935% | CZ 6A | 29.9745 | 12.2448 | 1.6405 | 30.799 | 0 | 12.755 | 0 | 4.8169 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 138.3306 | 4.935%
CZ 6B | 0.29548 | 0.12062 | 0.014944 | 0.22727 | 0 | 0.10857 | 0 | 0.053583 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.2749 | 0.5759% | CZ 6B | 9.772 | 3.9889 | 1.5095 | 9.865 | 0 | 3.5906 | 0 | 1.7721 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 45.527 | 0.5759% | CZ 6B | 2.8632 | 1.1687 | 0 | 1.8673 | 0 | 1.052 | 0 | 0.51921 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.8739 | 0.5759% | CZ 6B | 0 | 0 | 0.015095 | 0.03492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050015 | 0.5759% | CZ 6B | 29.9745 | 12.2355 | 1.6499 | 23.3652 | 0 | 11.0138 | 0 | 5.4356 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 129.7741 | 0.5759%
CZ 7 | 0.29548 | 0.12063 | 0.015847 | 0.41127 | 0 | 0.095989 | 0 | 0.048494 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4421 | 0.5453% | CZ 7 | 9.772 | 3.9893 | 1.6007 | 19.6929 | 0 | 3.1745 | 0 | 1.6038 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 54.862 | 0.5453% | CZ 7 | 2.8632 | 1.1688 | 0 | 3.1163 | 0 | 0.93011 | 0 | 0.4699 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 12.9517 | 0.5453% | CZ 7 | 0 | 0 | 0.016007 | 0.09057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10658 | 0.5453% | CZ 7 | 29.9745 | 12.2366 | 1.7496 | 42.5238 | 0 | 9.7374 | 0 | 4.9194 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 147.2407 | 0.5453%
CZ 8 | 0.29548 | 0.11988 | 0.017083 | 0.6344 | 0 | 0.064434 | 0 | 0.049344 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.6351 | 0.113% | CZ 8 | 9.772 | 3.9647 | 1.7255 | 32.007 | 0 | 2.1309 | 0 | 1.6319 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 66.2609 | 0.113% | CZ 8 | 2.8632 | 1.1616 | 0 | 4.5746 | 0 | 0.62436 | 0 | 0.47814 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 14.1053 | 0.113% | CZ 8 | 0 | 0 | 0.017255 | 0.16394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18119 | 0.113% | CZ 8 | 29.9745 | 12.1613 | 1.886 | 65.8099 | 0 | 6.5364 | 0 | 5.0056 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 167.473 | 0.113%
Us Weighted | 0.29548 | 0.12081 | 0.013103 | 0.13621 | 0 | 0.25789 | 0 | 0.054823 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018042 | 0 | 0 | 0.34279 | 1.3328 | 100% | Us Weighted | 9.772 | 3.9953 | 1.3235 | 5.9311 | 0 | 8.5288 | 0 | 1.8131 | 0 | 0.0026517 | 0 | 3.093 | 0.59669 | 0 | 0 | 11.3367 | 46.3928 | 100% | Us Weighted | 2.8632 | 1.1706 | 0 | 1.1164 | 0 | 2.4989 | 0 | 0.53123 | 0 | 0.00077695 | 0 | 0.90624 | 0.17483 | 0 | 0 | 3.3216 | 12.5838 | 100% | Us Weighted | 0 | 0 | 0.013235 | 0.021207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034442 | 100% | Us Weighted | 29.9745 | 12.255 | 1.4466 | 14.006 | 0 | 26.1613 | 0 | 5.5614 | 0 | 0.0081339 | 0 | 9.4875 | 1.8303 | 0 | 0 | 34.7739 | 135.5046 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29548 | 0.12104 | 0.010763 | 0.0080671 | 0 | 0.5876 | 0 | 0.07528 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.01805 | 0 | 0 | 0.34279 | 1.5527 | 2.141% | CZ 1A | 9.772 | 4.0029 | 1.0871 | 0.27048 | 0 | 19.4328 | 0 | 2.4896 | 0 | 0.0026517 | 0 | 3.093 | 0.59693 | 0 | 0 | 11.3367 | 52.0841 | 2.141% | CZ 1A | 2.8632 | 1.1728 | 0 | 0.077643 | 0 | 5.6938 | 0 | 0.72945 | 0 | 0.00077695 | 0 | 0.90624 | 0.1749 | 0 | 0 | 3.3216 | 14.9404 | 2.141% | CZ 1A | 0 | 0 | 0.010871 | 5.4789e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010926 | 2.141% | CZ 1A | 29.9745 | 12.2784 | 1.1882 | 0.81884 | 0 | 59.6079 | 0 | 7.6366 | 0 | 0.0081339 | 0 | 9.4875 | 1.831 | 0 | 0 | 34.7739 | 157.605 | 2.141%
CZ 1B | 0.29548 | 0.12094 | 0.010358 | 0.030048 | 0 | 0.5238 | 0 | 0.12055 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.5556 | 0% | CZ 1B | 9.772 | 3.9995 | 1.0463 | 1.0022 | 0 | 17.3229 | 0 | 3.9866 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 52.1585 | 0% | CZ 1B | 2.8632 | 1.1718 | 0 | 0.28996 | 0 | 5.0756 | 0 | 1.1681 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 14.9721 | 0% | CZ 1B | 0 | 0 | 0.010463 | 0.00012548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010588 | 0% | CZ 1B | 29.9745 | 12.2681 | 1.1436 | 3.0493 | 0 | 53.136 | 0 | 12.2285 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 157.8999 | 0%
CZ 2A | 0.29548 | 0.12083 | 0.011751 | 0.081645 | 0 | 0.45348 | 0 | 0.068727 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4864 | 13.44% | CZ 2A | 9.772 | 3.9962 | 1.187 | 3.1499 | 0 | 14.9973 | 0 | 2.2729 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 50.4041 | 13.44% | CZ 2A | 2.8632 | 1.1709 | 0 | 0.72697 | 0 | 4.3942 | 0 | 0.66595 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 14.2245 | 13.44% | CZ 2A | 0 | 0 | 0.01187 | 0.0066878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018558 | 13.44% | CZ 2A | 29.9745 | 12.2578 | 1.2974 | 8.3416 | 0 | 46.0026 | 0 | 6.9718 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 150.9451 | 13.44%
CZ 2B | 0.29548 | 0.12075 | 0.011184 | 0.057743 | 0 | 0.46215 | 0 | 0.097282 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.499 | 4.829% | CZ 2B | 9.772 | 3.9933 | 1.1297 | 1.9391 | 0 | 15.2839 | 0 | 3.2173 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 50.3643 | 4.829% | CZ 2B | 2.8632 | 1.17 | 0 | 0.55531 | 0 | 4.4781 | 0 | 0.94265 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 14.4128 | 4.829% | CZ 2B | 0 | 0 | 0.011297 | 0.00043831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011735 | 4.829% | CZ 2B | 29.9745 | 12.2491 | 1.2348 | 5.8615 | 0 | 46.8816 | 0 | 9.8686 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 152.17 | 4.829%
CZ 3A | 0.29548 | 0.1209 | 0.012544 | 0.14202 | 0 | 0.32759 | 0 | 0.061211 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4142 | 12.66% | CZ 3A | 9.772 | 3.9985 | 1.267 | 6.6786 | 0 | 10.8337 | 0 | 2.0243 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 49.6031 | 12.66% | CZ 3A | 2.8632 | 1.1715 | 0 | 1.0934 | 0 | 3.1743 | 0 | 0.59312 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 13.2989 | 12.66% | CZ 3A | 0 | 0 | 0.01267 | 0.029468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042138 | 12.66% | CZ 3A | 29.9745 | 12.2648 | 1.3849 | 14.6679 | 0 | 33.2313 | 0 | 6.2094 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 143.8323 | 12.66%
CZ 3B | 0.29548 | 0.12091 | 0.01228 | 0.057823 | 0 | 0.26148 | 0 | 0.071357 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.2738 | 11.83% | CZ 3B | 9.772 | 3.9988 | 1.2404 | 2.1971 | 0 | 8.6475 | 0 | 2.3599 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 43.2447 | 11.83% | CZ 3B | 2.8632 | 1.1716 | 0 | 0.51968 | 0 | 2.5337 | 0 | 0.69143 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 12.1831 | 11.83% | CZ 3B | 0 | 0 | 0.012404 | 0.0042347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016638 | 11.83% | CZ 3B | 29.9745 | 12.2659 | 1.3557 | 5.9033 | 0 | 26.5252 | 0 | 7.2386 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 129.3632 | 11.83%
CZ 3C | 0.29548 | 0.12073 | 0.013413 | 0.1043 | 0 | 0.14403 | 0 | 0.052717 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.1851 | 2.246% | CZ 3C | 9.772 | 3.9928 | 1.3549 | 3.5151 | 0 | 4.7632 | 0 | 1.7434 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 40.1703 | 2.246% | CZ 3C | 2.8632 | 1.1699 | 0 | 1.0012 | 0 | 1.3956 | 0 | 0.51082 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.3441 | 2.246% | CZ 3C | 0 | 0 | 0.013549 | 0.00097914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014528 | 2.246% | CZ 3C | 29.9745 | 12.2475 | 1.4809 | 10.5889 | 0 | 14.6106 | 0 | 5.3478 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 120.3496 | 2.246%
CZ 4A | 0.29548 | 0.12084 | 0.013538 | 0.2165 | 0 | 0.23588 | 0 | 0.059543 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.3962 | 19.67% | CZ 4A | 9.772 | 3.9965 | 1.3674 | 9.547 | 0 | 7.801 | 0 | 1.9692 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 49.482 | 19.67% | CZ 4A | 2.8632 | 1.171 | 0 | 1.7575 | 0 | 2.2857 | 0 | 0.57696 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 13.0577 | 19.67% | CZ 4A | 0 | 0 | 0.013674 | 0.035487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049162 | 19.67% | CZ 4A | 29.9745 | 12.2589 | 1.4946 | 22.2776 | 0 | 23.9288 | 0 | 6.0402 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 142.0741 | 19.67%
CZ 4B | 0.29548 | 0.12082 | 0.01338 | 0.12224 | 0 | 0.20596 | 0 | 0.073965 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.2863 | 0.602% | CZ 4B | 9.772 | 3.9956 | 1.3515 | 4.8043 | 0 | 6.8112 | 0 | 2.4461 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 44.2097 | 0.602% | CZ 4B | 2.8632 | 1.1707 | 0 | 1.0759 | 0 | 1.9957 | 0 | 0.71671 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 12.2256 | 0.602% | CZ 4B | 0 | 0 | 0.013515 | 0.011322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024837 | 0.602% | CZ 4B | 29.9745 | 12.2561 | 1.4772 | 12.5013 | 0 | 20.8927 | 0 | 7.5032 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 130.7046 | 0.602%
CZ 4C | 0.29548 | 0.12079 | 0.013961 | 0.20566 | 0 | 0.13488 | 0 | 0.055646 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018034 | 0 | 0 | 0.34279 | 1.2808 | 3.238% | CZ 4C | 9.772 | 3.9946 | 1.4102 | 8.0866 | 0 | 4.4607 | 0 | 1.8403 | 0 | 0.0026517 | 0 | 3.093 | 0.5964 | 0 | 0 | 11.3367 | 44.5931 | 3.238% | CZ 4C | 2.8632 | 1.1704 | 0 | 1.8095 | 0 | 1.307 | 0 | 0.5392 | 0 | 0.00077695 | 0 | 0.90624 | 0.17474 | 0 | 0 | 3.3216 | 12.0926 | 3.238% | CZ 4C | 0 | 0 | 0.014102 | 0.019107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033209 | 3.238% | CZ 4C | 29.9745 | 12.2529 | 1.5414 | 21.0323 | 0 | 13.6828 | 0 | 5.6449 | 0 | 0.0081339 | 0 | 9.4875 | 1.8294 | 0 | 0 | 34.7739 | 130.2276 | 3.238%
CZ 5A | 0.29548 | 0.1207 | 0.014237 | 0.3312 | 0 | 0.18261 | 0 | 0.059939 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.4586 | 17.52% | CZ 5A | 9.772 | 3.9917 | 1.4381 | 15.3155 | 0 | 6.0392 | 0 | 1.9823 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 53.5679 | 17.52% | CZ 5A | 2.8632 | 1.1696 | 0 | 2.587 | 0 | 1.7695 | 0 | 0.5808 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 13.3735 | 17.52% | CZ 5A | 0 | 0 | 0.014381 | 0.06486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079241 | 17.52% | CZ 5A | 29.9745 | 12.2442 | 1.5719 | 34.1729 | 0 | 18.5247 | 0 | 6.0804 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 148.6685 | 17.52%
CZ 5B | 0.29548 | 0.12065 | 0.014111 | 0.21827 | 0 | 0.15083 | 0 | 0.064017 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.3178 | 5.656% | CZ 5B | 9.772 | 3.99 | 1.4254 | 9.359 | 0 | 4.9883 | 0 | 2.1171 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 46.6806 | 5.656% | CZ 5B | 2.8632 | 1.1691 | 0 | 1.8098 | 0 | 1.4615 | 0 | 0.62032 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 12.3273 | 5.656% | CZ 5B | 0 | 0 | 0.014254 | 0.031822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046076 | 5.656% | CZ 5B | 29.9745 | 12.2388 | 1.558 | 22.4247 | 0 | 15.3009 | 0 | 6.4941 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 134.0904 | 5.656%
CZ 5C | 0.29548 | 0.12058 | 0.014246 | 0.25546 | 0 | 0.088783 | 0 | 0.052156 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.2811 | 0% | CZ 5C | 9.772 | 3.9877 | 1.439 | 10.4208 | 0 | 2.9362 | 0 | 1.7249 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 45.3094 | 0% | CZ 5C | 2.8632 | 1.1684 | 0 | 2.1941 | 0 | 0.86029 | 0 | 0.50538 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 11.9947 | 0% | CZ 5C | 0 | 0 | 0.01439 | 0.029325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043715 | 0% | CZ 5C | 29.9745 | 12.2317 | 1.5728 | 26.1747 | 0 | 9.0064 | 0 | 5.2908 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 130.3505 | 0%
CZ 6A | 0.29548 | 0.12071 | 0.01486 | 0.38655 | 0 | 0.12808 | 0 | 0.056288 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.4564 | 4.935% | CZ 6A | 9.772 | 3.9919 | 1.501 | 18.3835 | 0 | 4.2357 | 0 | 1.8615 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 54.7745 | 4.935% | CZ 6A | 2.8632 | 1.1696 | 0 | 2.9469 | 0 | 1.241 | 0 | 0.54542 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 13.1695 | 4.935% | CZ 6A | 0 | 0 | 0.01501 | 0.083258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098269 | 4.935% | CZ 6A | 29.9745 | 12.2448 | 1.6406 | 39.9509 | 0 | 12.9925 | 0 | 5.71 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 148.6128 | 4.935%
CZ 6B | 0.29548 | 0.12062 | 0.014951 | 0.315 | 0 | 0.10901 | 0 | 0.062237 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018044 | 0 | 0 | 0.34279 | 1.3717 | 0.5759% | CZ 6B | 9.772 | 3.9889 | 1.5102 | 14.283 | 0 | 3.6051 | 0 | 2.0583 | 0 | 0.0026517 | 0 | 3.093 | 0.59675 | 0 | 0 | 11.3367 | 50.2465 | 0.5759% | CZ 6B | 2.8632 | 1.1687 | 0 | 2.501 | 0 | 1.0563 | 0 | 0.60307 | 0 | 0.00077695 | 0 | 0.90624 | 0.17485 | 0 | 0 | 3.3216 | 12.5957 | 0.5759% | CZ 6B | 0 | 0 | 0.015102 | 0.05747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072573 | 0.5759% | CZ 6B | 29.9745 | 12.2355 | 1.6507 | 32.4645 | 0 | 11.0583 | 0 | 6.3135 | 0 | 0.0081339 | 0 | 9.4875 | 1.8305 | 0 | 0 | 34.7739 | 139.797 | 0.5759%
CZ 7 | 0.29548 | 0.12063 | 0.015852 | 0.5179 | 0 | 0.10516 | 0 | 0.062617 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.5721 | 0.5453% | CZ 7 | 9.772 | 3.9893 | 1.6013 | 24.6835 | 0 | 3.4778 | 0 | 2.0708 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 60.6235 | 0.5453% | CZ 7 | 2.8632 | 1.1688 | 0 | 3.9407 | 0 | 1.019 | 0 | 0.60675 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 14.0019 | 0.5453% | CZ 7 | 0 | 0 | 0.016013 | 0.11234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12835 | 0.5453% | CZ 7 | 29.9745 | 12.2366 | 1.7502 | 53.5338 | 0 | 10.6679 | 0 | 6.352 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 160.6144 | 0.5453%
CZ 8 | 0.29548 | 0.11988 | 0.017084 | 0.72546 | 0 | 0.06886 | 0 | 0.062841 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018039 | 0 | 0 | 0.34279 | 1.744 | 0.113% | CZ 8 | 9.772 | 3.9647 | 1.7257 | 37.383 | 0 | 2.2773 | 0 | 2.0783 | 0 | 0.0026517 | 0 | 3.093 | 0.59658 | 0 | 0 | 11.3367 | 72.2298 | 0.113% | CZ 8 | 2.8632 | 1.1616 | 0 | 5.1197 | 0 | 0.66724 | 0 | 0.60892 | 0 | 0.00077695 | 0 | 0.90624 | 0.1748 | 0 | 0 | 3.3216 | 14.8241 | 0.113% | CZ 8 | 0 | 0 | 0.017257 | 0.19909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21635 | 0.113% | CZ 8 | 29.9745 | 12.1613 | 1.8862 | 75.3591 | 0 | 6.9854 | 0 | 6.3748 | 0 | 0.0081339 | 0 | 9.4875 | 1.8299 | 0 | 0 | 34.7739 | 178.8406 | 0.113%
Us Weighted | 0.29548 | 0.12081 | 0.013105 | 0.18599 | 0 | 0.2716 | 0 | 0.064549 | 0 | 8.0182e-05 | 0 | 0.093524 | 0.018041 | 0 | 0 | 0.34279 | 1.406 | 100% | Us Weighted | 9.772 | 3.9953 | 1.3237 | 8.2552 | 0 | 8.9823 | 0 | 2.1347 | 0 | 0.0026517 | 0 | 3.093 | 0.59664 | 0 | 0 | 11.3367 | 49.4923 | 100% | Us Weighted | 2.8632 | 1.1706 | 0 | 1.5021 | 0 | 2.6318 | 0 | 0.62547 | 0 | 0.00077695 | 0 | 0.90624 | 0.17481 | 0 | 0 | 3.3216 | 13.1966 | 100% | Us Weighted | 0 | 0 | 0.013237 | 0.031285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044522 | 100% | Us Weighted | 29.9745 | 12.255 | 1.4468 | 19.1452 | 0 | 27.5523 | 0 | 6.5481 | 0 | 0.0081339 | 0 | 9.4875 | 1.8301 | 0 | 0 | 34.7739 | 143.0216 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Medium Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 53628 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 53628 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.1206 | 0.064963 | 0.00023446 | 0.0044625 | 0 | 0.22533 | 0 | 0.027208 | 0 | 0 | 0 | 0.0051156 | 0.0089376 | 0 | 0 | 0.030255 | 0.48711 | 2.141% | CZ 1A | 3.9886 | 2.1484 | 0.023683 | 0.15115 | 0 | 7.4521 | 0 | 0.89982 | 0 | 0 | 0 | 0.16918 | 0.29558 | 0 | 0 | 1.0006 | 16.1291 | 2.141% | CZ 1A | 1.1686 | 0.62949 | 0 | 0.042732 | 0 | 2.1834 | 0 | 0.26365 | 0 | 0 | 0 | 0.04957 | 0.086604 | 0 | 0 | 0.29317 | 4.7173 | 2.141% | CZ 1A | 0 | 0 | 0.00023683 | 5.3022e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00028985 | 2.141% | CZ 1A | 12.2345 | 6.5901 | 0.025886 | 0.45316 | 0 | 22.8584 | 0 | 2.7601 | 0 | 0 | 0 | 0.51895 | 0.90666 | 0 | 0 | 3.0692 | 49.4169 | 2.141%
CZ 1B | 0.12064 | 0.064921 | 0.00022746 | 0.019084 | 0 | 0.16454 | 0 | 0.057768 | 0 | 0 | 0 | 0.0051156 | 0.0089376 | 0 | 0 | 0.030255 | 0.47149 | 0% | CZ 1B | 3.9896 | 2.147 | 0.022976 | 0.62758 | 0 | 5.4417 | 0 | 1.9105 | 0 | 0 | 0 | 0.16918 | 0.29558 | 0 | 0 | 1.0006 | 15.6047 | 0% | CZ 1B | 1.1689 | 0.62907 | 0 | 0.18543 | 0 | 1.5944 | 0 | 0.55977 | 0 | 0 | 0 | 0.04957 | 0.086604 | 0 | 0 | 0.29317 | 4.567 | 0% | CZ 1B | 0 | 0 | 0.00022976 | -5.3022e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00017674 | 0% | CZ 1B | 12.2377 | 6.5857 | 0.025113 | 1.9355 | 0 | 16.6918 | 0 | 5.8602 | 0 | 0 | 0 | 0.51895 | 0.90666 | 0 | 0 | 3.0692 | 47.8309 | 0%
CZ 2A | 0.12011 | 0.064878 | 0.00020297 | 0.038152 | 0 | 0.18333 | 0 | 0.026433 | 0 | 0 | 0 | 0.0051156 | 0.0089269 | 0 | 0 | 0.030255 | 0.4774 | 13.44% | CZ 2A | 3.9721 | 2.1456 | 0.020502 | 1.6519 | 0 | 6.0629 | 0 | 0.87419 | 0 | 0 | 0 | 0.16918 | 0.29523 | 0 | 0 | 1.0006 | 16.1922 | 13.44% | CZ 2A | 1.1638 | 0.62866 | 0 | 0.31404 | 0 | 1.7764 | 0 | 0.25613 | 0 | 0 | 0 | 0.04957 | 0.0865 | 0 | 0 | 0.29317 | 4.5683 | 13.44% | CZ 2A | 0 | 0 | 0.00020502 | 0.0058006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060056 | 13.44% | CZ 2A | 12.184 | 6.5814 | 0.022408 | 3.9217 | 0 | 18.5973 | 0 | 2.6815 | 0 | 0 | 0 | 0.51895 | 0.90557 | 0 | 0 | 3.0692 | 48.4821 | 13.44%
CZ 2B | 0.12031 | 0.064841 | 0.00021522 | 0.039069 | 0 | 0.1535 | 0 | 0.041438 | 0 | 0 | 0 | 0.0051156 | 0.0089269 | 0 | 0 | 0.030255 | 0.46367 | 4.829% | CZ 2B | 3.9787 | 2.1444 | 0.021739 | 1.2688 | 0 | 5.0765 | 0 | 1.3704 | 0 | 0 | 0 | 0.16918 | 0.29523 | 0 | 0 | 1.0006 | 15.3254 | 4.829% | CZ 2B | 1.1657 | 0.62829 | 0 | 0.3819 | 0 | 1.4874 | 0 | 0.40153 | 0 | 0 | 0 | 0.04957 | 0.0865 | 0 | 0 | 0.29317 | 4.4941 | 4.829% | CZ 2B | 0 | 0 | 0.00021739 | -0.00034641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00012902 | 4.829% | CZ 2B | 12.2041 | 6.5776 | 0.023761 | 3.9602 | 0 | 15.5715 | 0 | 4.2036 | 0 | 0 | 0 | 0.51895 | 0.90557 | 0 | 0 | 3.0692 | 47.0345 | 4.829%
CZ 3A | 0.11924 | 0.06483 | 0.00019072 | 0.036996 | 0 | 0.12593 | 0 | 0.02043 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.41192 | 12.66% | CZ 3A | 3.9435 | 2.144 | 0.019265 | 2.726 | 0 | 4.1648 | 0 | 0.67566 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 15.138 | 12.66% | CZ 3A | 1.1554 | 0.62819 | 0 | 0.1442 | 0 | 1.2203 | 0 | 0.19797 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 3.7753 | 12.66% | CZ 3A | 0 | 0 | 0.00019265 | 0.022338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022531 | 12.66% | CZ 3A | 12.0962 | 6.5765 | 0.021056 | 3.9512 | 0 | 12.7751 | 0 | 2.0725 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 41.9857 | 12.66%
CZ 3B | 0.12017 | 0.06491 | 0.00020122 | 0.025842 | 0 | 0.083812 | 0 | 0.024333 | 0 | 0 | 0 | 0.0051156 | 0.0089323 | 0 | 0 | 0.030255 | 0.36357 | 11.83% | CZ 3B | 3.9741 | 2.1467 | 0.020325 | 0.84573 | 0 | 2.7718 | 0 | 0.80471 | 0 | 0 | 0 | 0.16918 | 0.2954 | 0 | 0 | 1.0006 | 12.0284 | 11.83% | CZ 3B | 1.1644 | 0.62897 | 0 | 0.25168 | 0 | 0.81212 | 0 | 0.23578 | 0 | 0 | 0 | 0.04957 | 0.086552 | 0 | 0 | 0.29317 | 3.5222 | 11.83% | CZ 3B | 0 | 0 | 0.00020325 | -0.00013255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0696e-05 | 11.83% | CZ 3B | 12.19 | 6.5847 | 0.022215 | 2.6204 | 0 | 8.5021 | 0 | 2.4684 | 0 | 0 | 0 | 0.51895 | 0.90612 | 0 | 0 | 3.0692 | 36.8819 | 11.83%
CZ 3C | 0.11942 | 0.064766 | 0.00018372 | 0.075417 | 0 | 0.091979 | 0 | 0.020596 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.41665 | 2.246% | CZ 3C | 3.9493 | 2.1419 | 0.018558 | 2.4559 | 0 | 3.0419 | 0 | 0.68114 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 13.7535 | 2.246% | CZ 3C | 1.1571 | 0.62757 | 0 | 0.73624 | 0 | 0.89127 | 0 | 0.19957 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 4.041 | 2.246% | CZ 3C | 0 | 0 | 0.00018558 | -0.0005691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00038352 | 2.246% | CZ 3C | 12.1141 | 6.57 | 0.020283 | 7.6455 | 0 | 9.3307 | 0 | 2.0893 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 42.263 | 2.246%
CZ 4A | 0.12055 | 0.064776 | 0.00019072 | 0.12927 | 0 | 0.084752 | 0 | 0.015812 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.45965 | 19.67% | CZ 4A | 3.9868 | 2.1422 | 0.019265 | 4.9956 | 0 | 2.8029 | 0 | 0.52292 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 15.9345 | 19.67% | CZ 4A | 1.1681 | 0.62767 | 0 | 1.1499 | 0 | 0.82124 | 0 | 0.15321 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 4.3493 | 19.67% | CZ 4A | 0 | 0 | 0.00019265 | 0.01071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010903 | 19.67% | CZ 4A | 12.229 | 6.5711 | 0.021056 | 13.2088 | 0 | 8.5975 | 0 | 1.604 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 46.7247 | 19.67%
CZ 4B | 0.12099 | 0.064824 | 0.00018897 | 0.083222 | 0 | 0.06685 | 0 | 0.017266 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.39764 | 0.602% | CZ 4B | 4.0015 | 2.1438 | 0.019088 | 2.9356 | 0 | 2.2108 | 0 | 0.57101 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 13.3466 | 0.602% | CZ 4B | 1.1724 | 0.62814 | 0 | 0.78027 | 0 | 0.64777 | 0 | 0.1673 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 3.8251 | 0.602% | CZ 4B | 0 | 0 | 0.00019088 | 0.0027253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029162 | 0.602% | CZ 4B | 12.274 | 6.576 | 0.020863 | 8.4665 | 0 | 6.7815 | 0 | 1.7515 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 40.3635 | 0.602%
CZ 4C | 0.11957 | 0.064659 | 0.00019072 | 0.12651 | 0 | 0.050606 | 0 | 0.014518 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.42035 | 3.238% | CZ 4C | 3.9544 | 2.1384 | 0.019265 | 4.6043 | 0 | 1.6736 | 0 | 0.48014 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 14.3349 | 3.238% | CZ 4C | 1.1586 | 0.62653 | 0 | 1.1659 | 0 | 0.49036 | 0 | 0.14068 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 4.0113 | 3.238% | CZ 4C | 0 | 0 | 0.00019265 | 0.0062513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064439 | 3.238% | CZ 4C | 12.1298 | 6.5592 | 0.021056 | 12.889 | 0 | 5.1336 | 0 | 1.4728 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 42.6985 | 3.238%
CZ 5A | 0.12009 | 0.064493 | 0.00019072 | 0.17087 | 0 | 0.051867 | 0 | 0.014887 | 0 | 0 | 0 | 0.0051156 | 0.0089323 | 0 | 0 | 0.030255 | 0.4667 | 17.52% | CZ 5A | 3.9716 | 2.1329 | 0.019265 | 6.6995 | 0 | 1.7153 | 0 | 0.49234 | 0 | 0 | 0 | 0.16918 | 0.2954 | 0 | 0 | 1.0006 | 16.496 | 17.52% | CZ 5A | 1.1637 | 0.62493 | 0 | 1.5061 | 0 | 0.50258 | 0 | 0.14425 | 0 | 0 | 0 | 0.04957 | 0.086552 | 0 | 0 | 0.29317 | 4.3708 | 17.52% | CZ 5A | 0 | 0 | 0.00019265 | 0.015592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015785 | 17.52% | CZ 5A | 12.1824 | 6.5424 | 0.021056 | 17.4715 | 0 | 5.2615 | 0 | 1.5102 | 0 | 0 | 0 | 0.51895 | 0.90612 | 0 | 0 | 3.0692 | 47.4833 | 17.52%
CZ 5B | 0.11994 | 0.064798 | 0.00019072 | 0.12582 | 0 | 0.052701 | 0 | 0.013818 | 0 | 0 | 0 | 0.0051156 | 0.0089162 | 0 | 0 | 0.030255 | 0.42155 | 5.656% | CZ 5B | 3.9666 | 2.143 | 0.019265 | 4.8727 | 0 | 1.7429 | 0 | 0.45698 | 0 | 0 | 0 | 0.16918 | 0.29487 | 0 | 0 | 1.0006 | 14.6661 | 5.656% | CZ 5B | 1.1622 | 0.62788 | 0 | 1.1176 | 0 | 0.51066 | 0 | 0.13389 | 0 | 0 | 0 | 0.04957 | 0.086397 | 0 | 0 | 0.29317 | 3.9814 | 5.656% | CZ 5B | 0 | 0 | 0.00019265 | 0.010583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010776 | 5.656% | CZ 5B | 12.1672 | 6.5733 | 0.021056 | 12.8571 | 0 | 5.3461 | 0 | 1.4017 | 0 | 0 | 0 | 0.51895 | 0.90449 | 0 | 0 | 3.0692 | 42.8591 | 5.656%
CZ 5C | 0.1165 | 0.064413 | 0.00019072 | 0.14732 | 0 | 0.042876 | 0 | 0.011461 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.42705 | 0% | CZ 5C | 3.853 | 2.1302 | 0.019265 | 5.6423 | 0 | 1.418 | 0 | 0.37902 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 14.9065 | 0% | CZ 5C | 1.1289 | 0.62415 | 0 | 1.3176 | 0 | 0.41546 | 0 | 0.11105 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 4.0264 | 0% | CZ 5C | 0 | 0 | 0.00019265 | 0.011453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011645 | 0% | CZ 5C | 11.8185 | 6.5342 | 0.021056 | 15.0458 | 0 | 4.3495 | 0 | 1.1626 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 43.4248 | 0%
CZ 6A | 0.11965 | 0.064424 | 0.00018722 | 0.19823 | 0 | 0.040016 | 0 | 0.013118 | 0 | 0 | 0 | 0.0051156 | 0.0089216 | 0 | 0 | 0.030255 | 0.47992 | 4.935% | CZ 6A | 3.9569 | 2.1306 | 0.018911 | 8.0825 | 0 | 1.3234 | 0 | 0.43382 | 0 | 0 | 0 | 0.16918 | 0.29505 | 0 | 0 | 1.0006 | 17.4109 | 4.935% | CZ 6A | 1.1594 | 0.62425 | 0 | 1.7031 | 0 | 0.38775 | 0 | 0.12711 | 0 | 0 | 0 | 0.04957 | 0.086449 | 0 | 0 | 0.29317 | 4.4308 | 4.935% | CZ 6A | 0 | 0 | 0.00018911 | 0.022697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022886 | 4.935% | CZ 6A | 12.1374 | 6.5353 | 0.02067 | 20.3108 | 0 | 4.0594 | 0 | 1.3307 | 0 | 0 | 0 | 0.51895 | 0.90503 | 0 | 0 | 3.0692 | 48.8874 | 4.935%
CZ 6B | 0.11987 | 0.064643 | 0.00019072 | 0.16947 | 0 | 0.041379 | 0 | 0.011952 | 0 | 0 | 0 | 0.0051156 | 0.0089269 | 0 | 0 | 0.030255 | 0.4518 | 0.5759% | CZ 6B | 3.9642 | 2.1378 | 0.019265 | 6.5793 | 0 | 1.3685 | 0 | 0.39528 | 0 | 0 | 0 | 0.16918 | 0.29523 | 0 | 0 | 1.0006 | 15.9293 | 0.5759% | CZ 6B | 1.1615 | 0.62638 | 0 | 1.5032 | 0 | 0.40096 | 0 | 0.11582 | 0 | 0 | 0 | 0.04957 | 0.0865 | 0 | 0 | 0.29317 | 4.2371 | 0.5759% | CZ 6B | 0 | 0 | 0.00019265 | 0.014489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014682 | 0.5759% | CZ 6B | 12.1596 | 6.5575 | 0.021056 | 17.3206 | 0 | 4.1976 | 0 | 1.2125 | 0 | 0 | 0 | 0.51895 | 0.90557 | 0 | 0 | 3.0692 | 45.9626 | 0.5759%
CZ 7 | 0.1208 | 0.064488 | 0.00018722 | 0.33421 | 0 | 0.040257 | 0 | 0.015817 | -0.013524 | 0 | 0 | 0.0051156 | 0.0089269 | 0 | 0 | 0.030255 | 0.60654 | 0.5453% | CZ 7 | 3.9951 | 2.1327 | 0.018911 | 17.9407 | 0 | 1.3313 | 0 | 0.5231 | -0.44726 | 0 | 0 | 0.16918 | 0.29523 | 0 | 0 | 1.0006 | 26.9596 | 0.5453% | CZ 7 | 1.1706 | 0.62488 | 0 | 2.2561 | 0 | 0.39008 | 0 | 0.15327 | -0.13105 | 0 | 0 | 0.04957 | 0.0865 | 0 | 0 | 0.29317 | 4.8931 | 0.5453% | CZ 7 | 0 | 0 | 0.00018911 | 0.10241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1026 | 0.5453% | CZ 7 | 12.2545 | 6.5418 | 0.02067 | 34.8122 | 0 | 4.0838 | 0 | 1.6045 | -1.3719 | 0 | 0 | 0.51895 | 0.90557 | 0 | 0 | 3.0692 | 62.4393 | 0.5453%
CZ 8 | 0.11467 | 0.063349 | 0.00019772 | 0.38344 | 0 | 0.033463 | 0 | 0.014577 | -0.014272 | 0 | 0 | 0.0051156 | 0.0089162 | 0 | 0 | 0.030255 | 0.63971 | 0.113% | CZ 8 | 3.7923 | 2.095 | 0.019972 | 22.1886 | 0 | 1.1067 | 0 | 0.48208 | -0.47201 | 0 | 0 | 0.16918 | 0.29487 | 0 | 0 | 1.0006 | 30.6773 | 0.113% | CZ 8 | 1.1111 | 0.61384 | 0 | 2.3594 | 0 | 0.32425 | 0 | 0.14125 | -0.1383 | 0 | 0 | 0.04957 | 0.086397 | 0 | 0 | 0.29317 | 4.8407 | 0.113% | CZ 8 | 0 | 0 | 0.00019972 | 0.14136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14156 | 0.113% | CZ 8 | 11.6326 | 6.4263 | 0.021829 | 40.1511 | 0 | 3.3945 | 0 | 1.4787 | -1.4478 | 0 | 0 | 0.51895 | 0.90449 | 0 | 0 | 3.0692 | 66.1498 | 0.113%
Us Weighted | 0.12005 | 0.064746 | 0.00019537 | 0.096642 | 0 | 0.098046 | 0 | 0.019956 | -8.9871e-05 | 0 | 0 | 0.0051156 | 0.0089258 | 0 | 0 | 0.030255 | 0.44384 | 100% | Us Weighted | 3.9701 | 2.1412 | 0.019735 | 3.9455 | 0 | 3.2425 | 0 | 0.65997 | -0.0029722 | 0 | 0 | 0.16918 | 0.29519 | 0 | 0 | 1.0006 | 15.441 | 100% | Us Weighted | 1.1632 | 0.62738 | 0 | 0.82956 | 0 | 0.95005 | 0 | 0.19337 | -0.00087084 | 0 | 0 | 0.04957 | 0.086489 | 0 | 0 | 0.29317 | 4.1919 | 100% | Us Weighted | 0 | 0 | 0.00019735 | 0.011142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011339 | 100% | Us Weighted | 12.1778 | 6.568 | 0.02157 | 9.9025 | 0 | 9.9461 | 0 | 2.0244 | -0.0091168 | 0 | 0 | 0.51895 | 0.90546 | 0 | 0 | 3.0692 | 45.1248 | 100%
Building Type: | Medium Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 53628 | [17 empty] | Prototype Floor Area: | 53628 | [17 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 40.82% | 53.67% | 2.179% | 55.32% | 0% | 38.35% | 0% | 36.14% | 0% | 0% | 0% | 5.47% | 49.52% | 0% | 0% | 8.826% | 31.37% | 2.141% | CZ 1A | 40.82% | 53.67% | 2.179% | 55.88% | 0% | 38.35% | 0% | 36.14% | 0% | 0% | 0% | 5.47% | 49.52% | 0% | 0% | 8.826% | 30.97% | 2.141% | CZ 1A | 40.82% | 53.67% | 0% | 55.04% | 0% | 38.35% | 0% | 36.14% | 0% | 0% | 0% | 5.47% | 49.52% | 0% | 0% | 8.826% | 31.57% | 2.141% | CZ 1A | 0% | 0% | 2.179% | 96.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.653% | 2.141% | CZ 1A | 40.82% | 53.67% | 2.179% | 55.34% | 0% | 38.35% | 0% | 36.14% | 0% | 0% | 0% | 5.47% | 49.52% | 0% | 0% | 8.826% | 31.35% | 2.141%
CZ 1B | 40.83% | 53.68% | 2.196% | 63.51% | 0% | 31.41% | 0% | 47.92% | 0% | 0% | 0% | 5.47% | 49.53% | 0% | 0% | 8.826% | 30.31% | 0% | CZ 1B | 40.83% | 53.68% | 2.196% | 62.62% | 0% | 31.41% | 0% | 47.92% | 0% | 0% | 0% | 5.47% | 49.53% | 0% | 0% | 8.826% | 29.92% | 0% | CZ 1B | 40.83% | 53.68% | 0% | 63.95% | 0% | 31.41% | 0% | 47.92% | 0% | 0% | 0% | 5.47% | 49.53% | 0% | 0% | 8.826% | 30.5% | 0% | CZ 1B | 0% | 0% | 2.196% | -42.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.669% | 0% | CZ 1B | 40.83% | 53.68% | 2.196% | 63.47% | 0% | 31.41% | 0% | 47.92% | 0% | 0% | 0% | 5.47% | 49.53% | 0% | 0% | 8.826% | 30.29% | 0%
CZ 2A | 40.65% | 53.69% | 1.727% | 46.73% | 0% | 40.43% | 0% | 38.46% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 32.12% | 13.44% | CZ 2A | 40.65% | 53.69% | 1.727% | 52.44% | 0% | 40.43% | 0% | 38.46% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 32.12% | 13.44% | CZ 2A | 40.65% | 53.69% | 0% | 43.2% | 0% | 40.43% | 0% | 38.46% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 32.12% | 13.44% | CZ 2A | 0% | 0% | 1.727% | 86.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.36% | 13.44% | CZ 2A | 40.65% | 53.69% | 1.727% | 47.01% | 0% | 40.43% | 0% | 38.46% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 32.12% | 13.44%
CZ 2B | 40.71% | 53.7% | 1.924% | 67.66% | 0% | 33.21% | 0% | 42.6% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 30.93% | 4.829% | CZ 2B | 40.71% | 53.7% | 1.924% | 65.43% | 0% | 33.21% | 0% | 42.6% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 30.43% | 4.829% | CZ 2B | 40.71% | 53.7% | 0% | 68.77% | 0% | 33.21% | 0% | 42.6% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 31.18% | 4.829% | CZ 2B | 0% | 0% | 1.924% | -79.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -1.099% | 4.829% | CZ 2B | 40.71% | 53.7% | 1.924% | 67.56% | 0% | 33.21% | 0% | 42.6% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 30.91% | 4.829%
CZ 3A | 40.35% | 53.62% | 1.52% | 26.05% | 0% | 38.44% | 0% | 33.38% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 29.13% | 12.66% | CZ 3A | 40.35% | 53.62% | 1.52% | 40.82% | 0% | 38.44% | 0% | 33.38% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 30.52% | 12.66% | CZ 3A | 40.35% | 53.62% | 0% | 13.19% | 0% | 38.44% | 0% | 33.38% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 28.39% | 12.66% | CZ 3A | 0% | 0% | 1.52% | 75.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 53.47% | 12.66% | CZ 3A | 40.35% | 53.62% | 1.52% | 26.94% | 0% | 38.44% | 0% | 33.38% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 29.19% | 12.66%
CZ 3B | 40.67% | 53.68% | 1.639% | 44.69% | 0% | 32.05% | 0% | 34.1% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 28.54% | 11.83% | CZ 3B | 40.67% | 53.68% | 1.639% | 38.49% | 0% | 32.05% | 0% | 34.1% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 27.81% | 11.83% | CZ 3B | 40.67% | 53.68% | 0% | 48.43% | 0% | 32.05% | 0% | 34.1% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 28.91% | 11.83% | CZ 3B | 0% | 0% | 1.639% | -3.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4249% | 11.83% | CZ 3B | 40.67% | 53.68% | 1.639% | 44.39% | 0% | 32.05% | 0% | 34.1% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 28.51% | 11.83%
CZ 3C | 40.41% | 53.64% | 1.37% | 72.31% | 0% | 63.86% | 0% | 39.07% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 35.16% | 2.246% | CZ 3C | 40.41% | 53.64% | 1.37% | 69.87% | 0% | 63.86% | 0% | 39.07% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 34.24% | 2.246% | CZ 3C | 40.41% | 53.64% | 0% | 73.53% | 0% | 63.86% | 0% | 39.07% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 35.62% | 2.246% | CZ 3C | 0% | 0% | 1.37% | -58.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.64% | 2.246% | CZ 3C | 40.41% | 53.64% | 1.37% | 72.2% | 0% | 63.86% | 0% | 39.07% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 35.12% | 2.246%
CZ 4A | 40.8% | 53.6% | 1.409% | 59.71% | 0% | 35.93% | 0% | 26.56% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.92% | 19.67% | CZ 4A | 40.8% | 53.6% | 1.409% | 52.33% | 0% | 35.93% | 0% | 26.56% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.2% | 19.67% | CZ 4A | 40.8% | 53.6% | 0% | 65.43% | 0% | 35.93% | 0% | 26.56% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 33.31% | 19.67% | CZ 4A | 0% | 0% | 1.409% | 30.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.18% | 19.67% | CZ 4A | 40.8% | 53.6% | 1.409% | 59.29% | 0% | 35.93% | 0% | 26.56% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.89% | 19.67%
CZ 4B | 40.95% | 53.65% | 1.412% | 68.08% | 0% | 32.46% | 0% | 23.34% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 30.91% | 0.602% | CZ 4B | 40.95% | 53.65% | 1.412% | 61.1% | 0% | 32.46% | 0% | 23.34% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 30.19% | 0.602% | CZ 4B | 40.95% | 53.65% | 0% | 72.52% | 0% | 32.46% | 0% | 23.34% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 31.29% | 0.602% | CZ 4B | 0% | 0% | 1.412% | 24.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.74% | 0.602% | CZ 4B | 40.95% | 53.65% | 1.412% | 67.72% | 0% | 32.46% | 0% | 23.34% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 30.88% | 0.602%
CZ 4C | 40.47% | 53.53% | 1.366% | 61.51% | 0% | 37.52% | 0% | 26.09% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 32.82% | 3.238% | CZ 4C | 40.47% | 53.53% | 1.366% | 56.94% | 0% | 37.52% | 0% | 26.09% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 32.15% | 3.238% | CZ 4C | 40.47% | 53.53% | 0% | 64.43% | 0% | 37.52% | 0% | 26.09% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 33.17% | 3.238% | CZ 4C | 0% | 0% | 1.366% | 32.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.4% | 3.238% | CZ 4C | 40.47% | 53.53% | 1.366% | 61.28% | 0% | 37.52% | 0% | 26.09% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 32.79% | 3.238%
CZ 5A | 40.64% | 53.43% | 1.34% | 51.59% | 0% | 28.4% | 0% | 24.84% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 32% | 17.52% | CZ 5A | 40.64% | 53.43% | 1.34% | 43.74% | 0% | 28.4% | 0% | 24.84% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 30.79% | 17.52% | CZ 5A | 40.64% | 53.43% | 0% | 58.22% | 0% | 28.4% | 0% | 24.84% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 32.68% | 17.52% | CZ 5A | 0% | 0% | 1.34% | 24.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.92% | 17.52% | CZ 5A | 40.64% | 53.43% | 1.34% | 51.13% | 0% | 28.4% | 0% | 24.84% | 0% | 0% | 0% | 5.47% | 49.5% | 0% | 0% | 8.826% | 31.94% | 17.52%
CZ 5B | 40.59% | 53.71% | 1.352% | 57.64% | 0% | 34.94% | 0% | 21.58% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 31.99% | 5.656% | CZ 5B | 40.59% | 53.71% | 1.352% | 52.07% | 0% | 34.94% | 0% | 21.58% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 31.42% | 5.656% | CZ 5B | 40.59% | 53.71% | 0% | 61.75% | 0% | 34.94% | 0% | 21.58% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 32.3% | 5.656% | CZ 5B | 0% | 0% | 1.352% | 33.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 23.39% | 5.656% | CZ 5B | 40.59% | 53.71% | 1.352% | 57.33% | 0% | 34.94% | 0% | 21.58% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 31.96% | 5.656%
CZ 5C | 39.43% | 53.42% | 1.339% | 57.67% | 0% | 48.29% | 0% | 21.97% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 33.33% | 0% | CZ 5C | 39.43% | 53.42% | 1.339% | 54.14% | 0% | 48.29% | 0% | 21.97% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.9% | 0% | CZ 5C | 39.43% | 53.42% | 0% | 60.05% | 0% | 48.29% | 0% | 21.97% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 33.57% | 0% | CZ 5C | 0% | 0% | 1.339% | 39.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.64% | 0% | CZ 5C | 39.43% | 53.42% | 1.339% | 57.48% | 0% | 48.29% | 0% | 21.97% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 33.31% | 0%
CZ 6A | 40.49% | 53.37% | 1.26% | 51.28% | 0% | 31.24% | 0% | 23.3% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.95% | 4.935% | CZ 6A | 40.49% | 53.37% | 1.26% | 43.97% | 0% | 31.24% | 0% | 23.3% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 31.79% | 4.935% | CZ 6A | 40.49% | 53.37% | 0% | 57.79% | 0% | 31.24% | 0% | 23.3% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 33.64% | 4.935% | CZ 6A | 0% | 0% | 1.26% | 27.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 23.29% | 4.935% | CZ 6A | 40.49% | 53.37% | 1.26% | 50.84% | 0% | 31.24% | 0% | 23.3% | 0% | 0% | 0% | 5.47% | 49.46% | 0% | 0% | 8.826% | 32.9% | 4.935%
CZ 6B | 40.57% | 53.59% | 1.276% | 53.8% | 0% | 37.96% | 0% | 19.2% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 32.94% | 0.5759% | CZ 6B | 40.57% | 53.59% | 1.276% | 46.06% | 0% | 37.96% | 0% | 19.2% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 31.7% | 0.5759% | CZ 6B | 40.57% | 53.59% | 0% | 60.1% | 0% | 37.96% | 0% | 19.2% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 33.64% | 0.5759% | CZ 6B | 0% | 0% | 1.276% | 25.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.23% | 0.5759% | CZ 6B | 40.57% | 53.59% | 1.276% | 53.35% | 0% | 37.96% | 0% | 19.2% | 0% | 0% | 0% | 5.47% | 49.47% | 0% | 0% | 8.826% | 32.88% | 0.5759%
CZ 7 | 40.88% | 53.46% | 1.181% | 64.53% | 0% | 38.28% | 0% | 25.26% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 38.58% | 0.5453% | CZ 7 | 40.88% | 53.46% | 1.181% | 72.68% | 0% | 38.28% | 0% | 25.26% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 44.47% | 0.5453% | CZ 7 | 40.88% | 53.46% | 0% | 57.25% | 0% | 38.28% | 0% | 25.26% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 34.95% | 0.5453% | CZ 7 | 0% | 0% | 1.181% | 91.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.93% | 0.5453% | CZ 7 | 40.88% | 53.46% | 1.181% | 65.03% | 0% | 38.28% | 0% | 25.26% | 0% | 0% | 0% | 5.47% | 49.49% | 0% | 0% | 8.826% | 38.88% | 0.5453%
CZ 8 | 38.81% | 52.84% | 1.157% | 52.85% | 0% | 48.59% | 0% | 23.2% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 36.68% | 0.113% | CZ 8 | 38.81% | 52.84% | 1.157% | 59.35% | 0% | 48.59% | 0% | 23.2% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 42.47% | 0.113% | CZ 8 | 38.81% | 52.84% | 0% | 46.08% | 0% | 48.59% | 0% | 23.2% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 32.65% | 0.113% | CZ 8 | 0% | 0% | 1.157% | 71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.43% | 0.113% | CZ 8 | 38.81% | 52.84% | 1.157% | 53.28% | 0% | 48.59% | 0% | 23.2% | 0% | 0% | 0% | 5.47% | 49.43% | 0% | 0% | 8.826% | 36.99% | 0.113%
Us Weighted | 40.63% | 53.59% | 1.491% | 51.96% | 0% | 36.1% | 0% | 30.92% | 0% | 0% | 0% | 5.47% | 49.48% | 0% | 0% | 8.826% | 31.57% | 100% | Us Weighted | 40.63% | 53.59% | 1.491% | 47.79% | 0% | 36.1% | 0% | 30.92% | 0% | 0% | 0% | 5.47% | 49.48% | 0% | 0% | 8.826% | 31.2% | 100% | Us Weighted | 40.63% | 53.59% | 0% | 55.23% | 0% | 36.1% | 0% | 30.92% | 0% | 0% | 0% | 5.47% | 49.48% | 0% | 0% | 8.826% | 31.77% | 100% | Us Weighted | 0% | 0% | 1.491% | 35.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.47% | 100% | Us Weighted | 40.63% | 53.59% | 1.491% | 51.72% | 0% | 36.1% | 0% | 30.92% | 0% | 0% | 0% | 5.47% | 49.48% | 0% | 0% | 8.826% | 31.55% | 100%

## SmOffice
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Office |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Small Office | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.23798 | 0.064081 | 0.093836 | 0.028798 | 0 | 0.09972 | 0 | 0.10441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.88042 |  | STD2013 | 7.8703 | 2.1193 | 3.1033 | 1.2146 | 0 | 3.2979 | 0 | 3.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.379 |  | STD2013 | 2.306 | 0.62094 | 0.90926 | 0.24166 | 0 | 0.96627 | 0 | 1.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.4938 |  | STD2013 | 0 | 0 | 0 | 0.003898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003898 |  | STD2013 | 24.1412 | 6.5006 | 9.519 | 2.9559 | 0 | 10.1159 | 0 | 10.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 89.3472
STD2010 | 0.27937 | 0.064081 | 0.093836 | 0.032685 | 0 | 0.14113 | 0 | 0.12161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.98901 |  | STD2010 | 9.2391 | 2.1193 | 3.1033 | 1.3928 | 0 | 4.6675 | 0 | 4.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.0199 |  | STD2010 | 2.707 | 0.62094 | 0.90926 | 0.27222 | 0 | 1.3676 | 0 | 1.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.5389 |  | STD2010 | 0 | 0 | 0 | 0.0046374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046374 |  | STD2010 | 28.3401 | 6.5006 | 9.519 | 3.3568 | 0 | 14.3171 | 0 | 12.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 100.3693
STD2007 | 0.36972 | 0.13379 | 0.093993 | 0.03564 | 0 | 0.15702 | 0 | 0.13251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1978 |  | STD2007 | 12.2271 | 4.4247 | 3.1085 | 1.6177 | 0 | 5.1929 | 0 | 4.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0509 |  | STD2007 | 3.5825 | 1.2964 | 0.91078 | 0.28273 | 0 | 1.5215 | 0 | 1.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5436 |  | STD2007 | 0 | 0 | 0 | 0.0065272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065272 |  | STD2007 | 37.5052 | 13.5722 | 9.5349 | 3.6733 | 0 | 15.9287 | 0 | 13.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 121.563
STD2004 | 0.36972 | 0.13379 | 0.093993 | 0.050787 | 0 | 0.20014 | 0 | 0.13776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2613 |  | STD2004 | 12.2271 | 4.4247 | 3.1085 | 2.3354 | 0 | 6.6191 | 0 | 4.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.3685 |  | STD2004 | 3.5825 | 1.2964 | 0.91078 | 0.39858 | 0 | 1.9394 | 0 | 1.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.1282 |  | STD2004 | 0 | 0 | 0 | 0.0097506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097506 |  | STD2004 | 37.5052 | 13.5722 | 9.5349 | 5.2384 | 0 | 20.3033 | 0 | 13.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 128.0356
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 4.3535e-08 | 0.015147 | 0 | 0.043124 | 0 | 0.0052527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063523 |  | 2004-2007 | 0 | 0 | 1.4397e-06 | 0.71772 | 0 | 1.4262 | 0 | 0.17371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3176 |  | 2004-2007 | 0 | 0 | 4.2184e-07 | 0.11585 | 0 | 0.41786 | 0 | 0.050898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58461 |  | 2004-2007 | 0 | 0 | 0 | 0.0032234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032234 |  | 2004-2007 | 0 | 0 | 4.4163e-06 | 1.5651 | 0 | 4.3746 | 0 | 0.53285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4726
2007-2010 | 0.090348 | 0.06971 | 0.0001567 | 0.0029554 | 0 | 0.015886 | 0 | 0.010892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018809 | 0.20876 |  | 2007-2010 | 2.9879 | 2.3054 | 0.0051822 | 0.22485 | 0 | 0.52537 | 0 | 0.36022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62204 | 7.031 |  | 2007-2010 | 0.87546 | 0.67548 | 0.0015184 | 0.010509 | 0 | 0.15393 | 0 | 0.10554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18226 | 2.0047 |  | 2007-2010 | 0 | 0 | 0 | 0.0018898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018898 |  | 2007-2010 | 9.1652 | 7.0716 | 0.015896 | 0.31657 | 0 | 1.6115 | 0 | 1.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.908 | 21.1937
2010-2013 | 0.041392 | 0 | 0 | 0.0038865 | 0 | 0.041415 | 0 | 0.017207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046892 | 0.10859 |  | 2010-2013 | 1.3689 | 0 | 0 | 0.17826 | 0 | 1.3697 | 0 | 0.56906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 | 3.6409 |  | 2010-2013 | 0.40108 | 0 | 0 | 0.030567 | 0 | 0.40131 | 0 | 0.16673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045438 | 1.0451 |  | 2010-2013 | 0 | 0 | 0 | 0.00073939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00073939 |  | 2010-2013 | 4.1989 | 0 | 0 | 0.40082 | 0 | 4.2013 | 0 | 1.7455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47569 | 11.0222
2004-2013 | 0.13174 | 0.06971 | 0.00015674 | 0.021989 | 0 | 0.10042 | 0 | 0.033352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.38087 |  | 2004-2013 | 4.3568 | 2.3054 | 0.0051837 | 1.1208 | 0 | 3.3212 | 0 | 1.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.9895 |  | 2004-2013 | 1.2765 | 0.67548 | 0.0015188 | 0.15692 | 0 | 0.9731 | 0 | 0.32317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.6344 |  | 2004-2013 | 0 | 0 | 0 | 0.0058526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058526 |  | 2004-2013 | 13.364 | 7.0716 | 0.0159 | 2.2825 | 0 | 10.1874 | 0 | 3.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 38.6884
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 4.632e-05% | 29.82% |  | 21.55% |  | 3.813% | [7 empty] | 0% | 5.036% |  | 2004-2007 | 0% | 0% | 4.632e-05% | 30.73% |  | 21.55% |  | 3.813% | [7 empty] | 0% | 5.47% |  | 2004-2007 | 0% | 0% | 4.632e-05% | 29.06% |  | 21.55% |  | 3.813% | [7 empty] | 0% | 4.82% |  | 2004-2007 |  |  |  | 33.06% | [12 empty] | 33.06% |  | 2004-2007 | 0% | 0% | 4.632e-05% | 29.88% |  | 21.55% |  | 3.813% | [7 empty] | 0% | 5.055%
2007-2010 | 24.44% | 52.1% | 0.1667% | 8.292% |  | 10.12% |  | 8.22% | [7 empty] | 6.837% | 17.43% |  | 2007-2010 | 24.44% | 52.1% | 0.1667% | 13.9% |  | 10.12% |  | 8.22% | [7 empty] | 6.837% | 17.56% |  | 2007-2010 | 24.44% | 52.1% | 0.1667% | 3.717% |  | 10.12% |  | 8.22% | [7 empty] | 6.837% | 17.37% |  | 2007-2010 |  |  |  | 28.95% | [12 empty] | 28.95% |  | 2007-2010 | 24.44% | 52.1% | 0.1667% | 8.618% |  | 10.12% |  | 8.22% | [7 empty] | 6.837% | 17.43%
2010-2013 | 14.82% | 0% | 0% | 11.89% |  | 29.34% |  | 14.15% | [7 empty] | 1.83% | 10.98% |  | 2010-2013 | 14.82% | 0% | 0% | 12.8% |  | 29.34% |  | 14.15% | [7 empty] | 1.83% | 11.03% |  | 2010-2013 | 14.82% | 0% | 0% | 11.23% |  | 29.34% |  | 14.15% | [7 empty] | 1.83% | 10.96% |  | 2010-2013 |  |  |  | 15.94% | [12 empty] | 15.94% |  | 2010-2013 | 14.82% | 0% | 0% | 11.94% |  | 29.34% |  | 14.15% | [7 empty] | 1.83% | 10.98%
2004-2013 | 35.63% | 52.1% | 0.1668% | 43.3% |  | 50.18% |  | 24.21% | [7 empty] | 8.542% | 30.2% |  | 2004-2013 | 35.63% | 52.1% | 0.1668% | 47.99% |  | 50.18% |  | 24.21% | [7 empty] | 8.542% | 30.66% |  | 2004-2013 | 35.63% | 52.1% | 0.1668% | 39.37% |  | 50.18% |  | 24.21% | [7 empty] | 8.542% | 29.97% |  | 2004-2013 |  |  |  | 60.02% | [12 empty] | 60.02% |  | 2004-2013 | 35.63% | 52.1% | 0.1668% | 43.57% |  | 50.18% |  | 24.21% | [7 empty] | 8.542% | 30.22%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.23894 | 0.064086 | 0.093836 | 0.00026051 | 0 | 0.18955 | 0 | 0.099307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.93758 | 1.497% | CZ 1A | 7.9021 | 2.1194 | 3.1033 | 0.0086155 | 0 | 6.2686 | 0 | 3.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.0071 | 1.497% | CZ 1A | 2.3153 | 0.62098 | 0.90926 | 0.0025243 | 0 | 1.8367 | 0 | 0.96227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 9.085 | 1.497% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.497% | CZ 1A | 24.2389 | 6.501 | 9.519 | 0.026427 | 0 | 19.2283 | 0 | 10.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 95.1108 | 1.497%
CZ 1B | 0.23967 | 0.064086 | 0.093836 | 0.001042 | 0 | 0.19346 | 0 | 0.12718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.97087 | 0% | CZ 1B | 7.9262 | 2.1194 | 3.1033 | 0.034462 | 0 | 6.3979 | 0 | 4.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.1082 | 0% | CZ 1B | 2.3224 | 0.62098 | 0.90926 | 0.010097 | 0 | 1.8746 | 0 | 1.2324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 9.4076 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 24.3129 | 6.501 | 9.519 | 0.10571 | 0 | 19.6247 | 0 | 12.9017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 98.4882 | 0%
CZ 2A | 0.24004 | 0.064034 | 0.093836 | 0.0087646 | 0 | 0.14187 | 0 | 0.10259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.90274 | 18.97% | CZ 2A | 7.9383 | 2.1177 | 3.1033 | 0.31187 | 0 | 4.692 | 0 | 3.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.8767 | 18.97% | CZ 2A | 2.3259 | 0.62048 | 0.90926 | 0.081788 | 0 | 1.3747 | 0 | 0.99407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.7442 | 18.97% | CZ 2A | 0 | 0 | 0 | 0.00032731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00032731 | 18.97% | CZ 2A | 24.3499 | 6.4958 | 9.519 | 0.89201 | 0 | 14.3922 | 0 | 10.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 91.579 | 18.97%
CZ 2B | 0.23936 | 0.064034 | 0.093836 | 0.0033516 | 0 | 0.17037 | 0 | 0.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.94526 | 5.157% | CZ 2B | 7.9159 | 2.1177 | 3.1033 | 0.112 | 0 | 5.6345 | 0 | 4.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.2621 | 5.157% | CZ 2B | 2.3193 | 0.62048 | 0.90926 | 0.032311 | 0 | 1.6509 | 0 | 1.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 9.1592 | 5.157% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 5.157% | CZ 2B | 24.2811 | 6.4958 | 9.519 | 0.34015 | 0 | 17.2833 | 0 | 12.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 95.8897 | 5.157%
CZ 3A | 0.2403 | 0.064086 | 0.093836 | 0.029639 | 0 | 0.10738 | 0 | 0.10191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.88875 | 17.17% | CZ 3A | 7.9469 | 2.1194 | 3.1033 | 1.1355 | 0 | 3.5513 | 0 | 3.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.5476 | 17.17% | CZ 3A | 2.3284 | 0.62098 | 0.90926 | 0.26505 | 0 | 1.0405 | 0 | 0.98751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.5897 | 17.17% | CZ 3A | 0 | 0 | 0 | 0.0023084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023084 | 17.17% | CZ 3A | 24.3763 | 6.501 | 9.519 | 3.0271 | 0 | 10.8932 | 0 | 10.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 90.1782 | 17.17%
CZ 3B | 0.23941 | 0.064034 | 0.093836 | 0.012946 | 0 | 0.10478 | 0 | 0.11812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.88472 | 8.466% | CZ 3B | 7.9176 | 2.1177 | 3.1033 | 0.46522 | 0 | 3.4651 | 0 | 3.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.2961 | 8.466% | CZ 3B | 2.3198 | 0.62048 | 0.90926 | 0.12016 | 0 | 1.0153 | 0 | 1.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.5675 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00055126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00055126 | 8.466% | CZ 3B | 24.2864 | 6.4958 | 9.519 | 1.3182 | 0 | 10.6289 | 0 | 11.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 89.7536 | 8.466%
CZ 3C | 0.23988 | 0.064034 | 0.093836 | 0.0072242 | 0 | 0.038399 | 0 | 0.089199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.78417 | 1.386% | CZ 3C | 7.9331 | 2.1177 | 3.1033 | 0.24123 | 0 | 1.2699 | 0 | 2.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.936 | 1.386% | CZ 3C | 2.3244 | 0.62048 | 0.90926 | 0.069671 | 0 | 0.37208 | 0 | 0.86432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.5982 | 1.386% | CZ 3C | 0 | 0 | 0 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4454e-05 | 1.386% | CZ 3C | 24.334 | 6.4958 | 9.519 | 0.73315 | 0 | 3.8953 | 0 | 9.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 79.5491 | 1.386%
CZ 4A | 0.23561 | 0.064034 | 0.093836 | 0.030901 | 0 | 0.082895 | 0 | 0.098682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.85756 | 16.69% | CZ 4A | 7.7918 | 2.1177 | 3.1033 | 1.1992 | 0 | 2.7414 | 0 | 3.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.5378 | 16.69% | CZ 4A | 2.283 | 0.62048 | 0.90926 | 0.27414 | 0 | 0.80324 | 0 | 0.95621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2843 | 16.69% | CZ 4A | 0 | 0 | 0 | 0.0026357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026357 | 16.69% | CZ 4A | 23.9006 | 6.4958 | 9.519 | 3.1581 | 0 | 8.4091 | 0 | 10.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 87.0163 | 16.69%
CZ 4B | 0.23509 | 0.063982 | 0.093836 | 0.017829 | 0 | 0.08748 | 0 | 0.12124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.87106 | 0.844% | CZ 4B | 7.7746 | 2.116 | 3.1033 | 0.61858 | 0 | 2.8931 | 0 | 4.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.836 | 0.844% | CZ 4B | 2.2779 | 0.61997 | 0.90926 | 0.16862 | 0 | 0.84766 | 0 | 1.1748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.4362 | 0.844% | CZ 4B | 0 | 0 | 0 | 0.00043067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00043067 | 0.844% | CZ 4B | 23.8477 | 6.4905 | 9.519 | 1.8124 | 0 | 8.8742 | 0 | 12.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 88.3662 | 0.844%
CZ 4C | 0.23691 | 0.064086 | 0.093836 | 0.019409 | 0 | 0.051217 | 0 | 0.10743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.82449 | 2.185% | CZ 4C | 7.8349 | 2.1194 | 3.1033 | 0.672 | 0 | 1.6938 | 0 | 3.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.2973 | 2.185% | CZ 4C | 2.2956 | 0.62098 | 0.90926 | 0.18377 | 0 | 0.49628 | 0 | 1.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.9849 | 2.185% | CZ 4C | 0 | 0 | 0 | 0.0004479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0004479 | 2.185% | CZ 4C | 24.0327 | 6.501 | 9.519 | 1.9728 | 0 | 5.1956 | 0 | 10.8985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 83.6429 | 2.185%
CZ 5A | 0.23576 | 0.064242 | 0.093836 | 0.055198 | 0 | 0.070078 | 0 | 0.10108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.8718 | 16.4% | CZ 5A | 7.797 | 2.1246 | 3.1033 | 2.5172 | 0 | 2.3176 | 0 | 3.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.5233 | 16.4% | CZ 5A | 2.2845 | 0.6225 | 0.90926 | 0.4362 | 0 | 0.67904 | 0 | 0.97943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.3489 | 16.4% | CZ 5A | 0 | 0 | 0 | 0.010284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010284 | 16.4% | CZ 5A | 23.9165 | 6.5169 | 9.519 | 5.6907 | 0 | 7.1089 | 0 | 10.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 88.5288 | 16.4%
CZ 5B | 0.23644 | 0.063877 | 0.093836 | 0.03111 | 0 | 0.060491 | 0 | 0.11311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.85047 | 5.738% | CZ 5B | 7.8194 | 2.1125 | 3.1033 | 1.1389 | 0 | 2.0005 | 0 | 3.7408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.2363 | 5.738% | CZ 5B | 2.2911 | 0.61896 | 0.90926 | 0.28575 | 0 | 0.58615 | 0 | 1.0961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2252 | 5.738% | CZ 5B | 0 | 0 | 0 | 0.0016365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016365 | 5.738% | CZ 5B | 23.9852 | 6.4799 | 9.519 | 3.1704 | 0 | 6.1364 | 0 | 11.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 86.2887 | 5.738%
CZ 5C | 0.23878 | 0.06419 | 0.093836 | 0.027415 | 0 | 0.036732 | 0 | 0.099672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.81223 | 0% | CZ 5C | 7.8969 | 2.1229 | 3.1033 | 0.93563 | 0 | 1.2148 | 0 | 3.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.8906 | 0% | CZ 5C | 2.3138 | 0.62199 | 0.90926 | 0.26152 | 0 | 0.35593 | 0 | 0.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 7.8663 | 0% | CZ 5C | 0 | 0 | 0 | 0.00043067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00043067 | 0% | CZ 5C | 24.223 | 6.5116 | 9.519 | 2.7849 | 0 | 3.7262 | 0 | 10.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 82.3989 | 0%
CZ 6A | 0.23618 | 0.064294 | 0.093836 | 0.071383 | 0 | 0.050748 | 0 | 0.096858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.8649 | 4.301% | CZ 6A | 7.8108 | 2.1263 | 3.1033 | 3.5715 | 0 | 1.6783 | 0 | 3.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.8143 | 4.301% | CZ 6A | 2.2885 | 0.623 | 0.90926 | 0.519 | 0 | 0.49174 | 0 | 0.93854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2081 | 4.301% | CZ 6A | 0 | 0 | 0 | 0.018002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018002 | 4.301% | CZ 6A | 23.9587 | 6.5222 | 9.519 | 7.401 | 0 | 5.148 | 0 | 9.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 87.8977 | 4.301%
CZ 6B | 0.23608 | 0.063982 | 0.093836 | 0.056191 | 0 | 0.046163 | 0 | 0.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.86425 | 0.5387% | CZ 6B | 7.8073 | 2.116 | 3.1033 | 2.4724 | 0 | 1.5267 | 0 | 3.8494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.1959 | 0.5387% | CZ 6B | 2.2875 | 0.61997 | 0.90926 | 0.4569 | 0 | 0.44731 | 0 | 1.1279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2868 | 0.5387% | CZ 6B | 0 | 0 | 0 | 0.0091302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0091302 | 0.5387% | CZ 6B | 23.9482 | 6.4905 | 9.519 | 5.7812 | 0 | 4.6829 | 0 | 11.8076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 87.7525 | 0.5387%
CZ 7 | 0.23165 | 0.064138 | 0.093836 | 0.10183 | 0 | 0.040431 | 0 | 0.10488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.88836 | 0.5766% | CZ 7 | 7.6609 | 2.1211 | 3.1033 | 6.1263 | 0 | 1.3371 | 0 | 3.4686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.1382 | 0.5766% | CZ 7 | 2.2446 | 0.62149 | 0.90926 | 0.59321 | 0 | 0.39177 | 0 | 1.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.2146 | 0.5766% | CZ 7 | 0 | 0 | 0 | 0.041017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041017 | 0.5766% | CZ 7 | 23.4989 | 6.5063 | 9.519 | 10.6935 | 0 | 4.1015 | 0 | 10.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 90.482 | 0.5766%
CZ 8 | 0.23561 | 0.064503 | 0.093836 | 0.17277 | 0 | 0.029073 | 0 | 0.11285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.96024 | 0.08356% | CZ 8 | 7.7918 | 2.1332 | 3.1033 | 13.5648 | 0 | 0.96149 | 0 | 3.7322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 39.6077 | 0.08356% | CZ 8 | 2.283 | 0.62502 | 0.90926 | 0.55434 | 0 | 0.28171 | 0 | 1.0935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.1848 | 0.08356% | CZ 8 | 0 | 0 | 0 | 0.11673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11673 | 0.08356% | CZ 8 | 23.9006 | 6.5433 | 9.519 | 18.5618 | 0 | 2.9493 | 0 | 11.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 98.4454 | 0.08356%
Us Weighted | 0.23798 | 0.064081 | 0.093836 | 0.028798 | 0 | 0.09972 | 0 | 0.10441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2516 | 0.88042 | 100% | Us Weighted | 7.8703 | 2.1193 | 3.1033 | 1.2146 | 0 | 3.2979 | 0 | 3.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.379 | 100% | Us Weighted | 2.306 | 0.62094 | 0.90926 | 0.24166 | 0 | 0.96627 | 0 | 1.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.438 | 8.4938 | 100% | Us Weighted | 0 | 0 | 0 | 0.003898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003898 | 100% | Us Weighted | 24.1412 | 6.5006 | 9.519 | 2.9559 | 0 | 10.1159 | 0 | 10.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5232 | 89.3472 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.28151 | 0.064086 | 0.093836 | 0.00036472 | 0 | 0.29182 | 0 | 0.13411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.122 | 1.497% | CZ 1A | 9.3099 | 2.1194 | 3.1033 | 0.012062 | 0 | 9.6511 | 0 | 4.4352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 37.1069 | 1.497% | CZ 1A | 2.7278 | 0.62098 | 0.90926 | 0.003534 | 0 | 2.8277 | 0 | 1.2995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.8722 | 1.497% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.497% | CZ 1A | 28.557 | 6.501 | 9.519 | 0.036998 | 0 | 29.6035 | 0 | 13.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 113.8212 | 1.497%
CZ 1B | 0.28193 | 0.064086 | 0.093836 | 0.0013026 | 0 | 0.23785 | 0 | 0.15094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.0862 | 0% | CZ 1B | 9.3237 | 2.1194 | 3.1033 | 0.043077 | 0 | 7.8659 | 0 | 4.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 35.9231 | 0% | CZ 1B | 2.7318 | 0.62098 | 0.90926 | 0.012622 | 0 | 2.3047 | 0 | 1.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.5254 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 28.5993 | 6.501 | 9.519 | 0.13214 | 0 | 24.1279 | 0 | 15.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 110.1901 | 0%
CZ 2A | 0.28213 | 0.064034 | 0.093836 | 0.008956 | 0 | 0.21753 | 0 | 0.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.053 | 18.97% | CZ 2A | 9.3306 | 2.1177 | 3.1033 | 0.31704 | 0 | 7.1939 | 0 | 4.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.8444 | 18.97% | CZ 2A | 2.7338 | 0.62048 | 0.90926 | 0.083807 | 0 | 2.1078 | 0 | 1.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.2002 | 18.97% | CZ 2A | 0 | 0 | 0 | 0.00031008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00031008 | 18.97% | CZ 2A | 28.6205 | 6.4958 | 9.519 | 0.91127 | 0 | 22.0666 | 0 | 13.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 106.8202 | 18.97%
CZ 2B | 0.28177 | 0.064034 | 0.093836 | 0.0034558 | 0 | 0.20534 | 0 | 0.14005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.0448 | 5.157% | CZ 2B | 9.3185 | 2.1177 | 3.1033 | 0.11545 | 0 | 6.7907 | 0 | 4.6317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.5532 | 5.157% | CZ 2B | 2.7303 | 0.62048 | 0.90926 | 0.033321 | 0 | 1.9897 | 0 | 1.3571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 10.1235 | 5.157% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 5.157% | CZ 2B | 28.5835 | 6.4958 | 9.519 | 0.35072 | 0 | 20.8298 | 0 | 14.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 105.9848 | 5.157%
CZ 3A | 0.28015 | 0.064086 | 0.093836 | 0.026573 | 0 | 0.16251 | 0 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.0024 | 17.17% | CZ 3A | 9.2651 | 2.1194 | 3.1033 | 1.0028 | 0 | 5.3743 | 0 | 3.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.2764 | 17.17% | CZ 3A | 2.7146 | 0.62098 | 0.90926 | 0.23981 | 0 | 1.5747 | 0 | 1.1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.6959 | 17.17% | CZ 3A | 0 | 0 | 0 | 0.0018433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018433 | 17.17% | CZ 3A | 28.4196 | 6.501 | 9.519 | 2.712 | 0 | 16.4852 | 0 | 12.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 101.7076 | 17.17%
CZ 3B | 0.27979 | 0.064034 | 0.093836 | 0.011612 | 0 | 0.12208 | 0 | 0.12604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.95367 | 8.466% | CZ 3B | 9.253 | 2.1177 | 3.1033 | 0.40836 | 0 | 4.0372 | 0 | 4.1682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 31.5636 | 8.466% | CZ 3B | 2.7111 | 0.62048 | 0.90926 | 0.10905 | 0 | 1.1829 | 0 | 1.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.2375 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00036176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00036176 | 8.466% | CZ 3B | 28.3826 | 6.4958 | 9.519 | 1.1812 | 0 | 12.3837 | 0 | 12.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 96.7466 | 8.466%
CZ 3C | 0.27995 | 0.064034 | 0.093836 | 0.0059567 | 0 | 0.056375 | 0 | 0.098994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.85543 | 1.386% | CZ 3C | 9.2582 | 2.1177 | 3.1033 | 0.19816 | 0 | 1.8644 | 0 | 3.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 28.2915 | 1.386% | CZ 3C | 2.7126 | 0.62048 | 0.90926 | 0.057554 | 0 | 0.54626 | 0 | 0.95924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.2888 | 1.386% | CZ 3C | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 1.386% | CZ 3C | 28.3985 | 6.4958 | 9.519 | 0.60442 | 0 | 5.7188 | 0 | 10.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 86.7776 | 1.386%
CZ 4A | 0.27744 | 0.064034 | 0.093836 | 0.0392 | 0 | 0.11499 | 0 | 0.11494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.96073 | 16.69% | CZ 4A | 9.1755 | 2.1177 | 3.1033 | 1.5455 | 0 | 3.8029 | 0 | 3.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.0219 | 16.69% | CZ 4A | 2.6884 | 0.62048 | 0.90926 | 0.34432 | 0 | 1.1142 | 0 | 1.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.2738 | 16.69% | CZ 4A | 0 | 0 | 0 | 0.0037038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037038 | 16.69% | CZ 4A | 28.1448 | 6.4958 | 9.519 | 4.0095 | 0 | 11.6649 | 0 | 11.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 97.4924 | 16.69%
CZ 4B | 0.27713 | 0.063982 | 0.093836 | 0.023016 | 0 | 0.12426 | 0 | 0.14135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.97987 | 0.844% | CZ 4B | 9.1651 | 2.116 | 3.1033 | 0.80984 | 0 | 4.1096 | 0 | 4.6748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.4545 | 0.844% | CZ 4B | 2.6854 | 0.61997 | 0.90926 | 0.21608 | 0 | 1.2041 | 0 | 1.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.4879 | 0.844% | CZ 4B | 0 | 0 | 0 | 0.00072352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072352 | 0.844% | CZ 4B | 28.1131 | 6.4905 | 9.519 | 2.3412 | 0 | 12.6057 | 0 | 14.3393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 99.4077 | 0.844%
CZ 4C | 0.27807 | 0.064086 | 0.093836 | 0.025759 | 0 | 0.070546 | 0 | 0.11963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.90822 | 2.185% | CZ 4C | 9.1962 | 2.1194 | 3.1033 | 0.90288 | 0 | 2.3331 | 0 | 3.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 30.0869 | 2.185% | CZ 4C | 2.6945 | 0.62098 | 0.90926 | 0.24233 | 0 | 0.68358 | 0 | 1.1592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.7932 | 2.185% | CZ 4C | 0 | 0 | 0 | 0.00075798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00075798 | 2.185% | CZ 4C | 28.2082 | 6.501 | 9.519 | 2.6198 | 0 | 7.1564 | 0 | 12.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 92.1387 | 2.185%
CZ 5A | 0.2775 | 0.064242 | 0.093836 | 0.068065 | 0 | 0.094201 | 0 | 0.11483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.96897 | 16.4% | CZ 5A | 9.1772 | 2.1246 | 3.1033 | 3.1443 | 0 | 3.1154 | 0 | 3.7977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.9384 | 16.4% | CZ 5A | 2.6889 | 0.6225 | 0.90926 | 0.53212 | 0 | 0.91279 | 0 | 1.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.2617 | 16.4% | CZ 5A | 0 | 0 | 0 | 0.013282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013282 | 16.4% | CZ 5A | 28.1501 | 6.5169 | 9.519 | 7.0225 | 0 | 9.556 | 0 | 11.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 98.4124 | 16.4%
CZ 5B | 0.27776 | 0.063877 | 0.093836 | 0.038793 | 0 | 0.088313 | 0 | 0.12864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.94751 | 5.738% | CZ 5B | 9.1858 | 2.1125 | 3.1033 | 1.4336 | 0 | 2.9206 | 0 | 4.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 31.4861 | 5.738% | CZ 5B | 2.6914 | 0.61896 | 0.90926 | 0.35441 | 0 | 0.85574 | 0 | 1.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.1597 | 5.738% | CZ 5B | 0 | 0 | 0 | 0.0022395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022395 | 5.738% | CZ 5B | 28.1765 | 6.4799 | 9.519 | 3.9551 | 0 | 8.9588 | 0 | 13.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 96.1379 | 5.738%
CZ 5C | 0.27896 | 0.06419 | 0.093836 | 0.035103 | 0 | 0.048403 | 0 | 0.10702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.8838 | 0% | CZ 5C | 9.2255 | 2.1229 | 3.1033 | 1.213 | 0 | 1.6008 | 0 | 3.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 29.2805 | 0% | CZ 5C | 2.703 | 0.62199 | 0.90926 | 0.3327 | 0 | 0.46902 | 0 | 1.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.5564 | 0% | CZ 5C | 0 | 0 | 0 | 0.0007752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007752 | 0% | CZ 5C | 28.2981 | 6.5116 | 9.519 | 3.5678 | 0 | 4.9101 | 0 | 10.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 89.6618 | 0%
CZ 6A | 0.27771 | 0.064294 | 0.093836 | 0.077431 | 0 | 0.067941 | 0 | 0.10639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.94389 | 4.301% | CZ 6A | 9.1841 | 2.1263 | 3.1033 | 3.8851 | 0 | 2.2469 | 0 | 3.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.5402 | 4.301% | CZ 6A | 2.6909 | 0.623 | 0.90926 | 0.56141 | 0 | 0.65834 | 0 | 1.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.9573 | 4.301% | CZ 6A | 0 | 0 | 0 | 0.01969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01969 | 4.301% | CZ 6A | 28.1712 | 6.5222 | 9.519 | 8.0295 | 0 | 6.8922 | 0 | 10.7928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 95.9258 | 4.301%
CZ 6B | 0.2776 | 0.063982 | 0.093836 | 0.061796 | 0 | 0.064555 | 0 | 0.12755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.94561 | 0.5387% | CZ 6B | 9.1807 | 2.116 | 3.1033 | 2.7412 | 0 | 2.1349 | 0 | 4.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 31.9701 | 0.5387% | CZ 6B | 2.6899 | 0.61997 | 0.90926 | 0.49931 | 0 | 0.62552 | 0 | 1.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.0633 | 0.5387% | CZ 6B | 0 | 0 | 0 | 0.010371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010371 | 0.5387% | CZ 6B | 28.1606 | 6.4905 | 9.519 | 6.3608 | 0 | 6.5486 | 0 | 12.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 96.0171 | 0.5387%
CZ 7 | 0.27786 | 0.064138 | 0.093836 | 0.11552 | 0 | 0.051842 | 0 | 0.11228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.97177 | 0.5766% | CZ 7 | 9.1893 | 2.1211 | 3.1033 | 7.0067 | 0 | 1.7145 | 0 | 3.7133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 35.324 | 0.5766% | CZ 7 | 2.6924 | 0.62149 | 0.90926 | 0.6649 | 0 | 0.50234 | 0 | 1.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.9618 | 0.5766% | CZ 7 | 0 | 0 | 0 | 0.047374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047374 | 0.5766% | CZ 7 | 28.1871 | 6.5063 | 9.519 | 12.1388 | 0 | 5.259 | 0 | 11.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 98.9991 | 0.5766%
CZ 8 | 0.27922 | 0.064503 | 0.093836 | 0.18716 | 0 | 0.036367 | 0 | 0.11749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 1.0349 | 0.08356% | CZ 8 | 9.2341 | 2.1332 | 3.1033 | 14.7742 | 0 | 1.2027 | 0 | 3.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 42.8089 | 0.08356% | CZ 8 | 2.7056 | 0.62502 | 0.90926 | 0.58917 | 0 | 0.35239 | 0 | 1.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 8.8033 | 0.08356% | CZ 8 | 0 | 0 | 0 | 0.12763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12763 | 0.08356% | CZ 8 | 28.3245 | 6.5433 | 9.519 | 20.1184 | 0 | 3.6892 | 0 | 11.9186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 106.1119 | 0.08356%
Us Weighted | 0.27937 | 0.064081 | 0.093836 | 0.032685 | 0 | 0.14113 | 0 | 0.12161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25629 | 0.98901 | 100% | Us Weighted | 9.2391 | 2.1193 | 3.1033 | 1.3928 | 0 | 4.6675 | 0 | 4.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.0199 | 100% | Us Weighted | 2.707 | 0.62094 | 0.90926 | 0.27222 | 0 | 1.3676 | 0 | 1.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4834 | 9.5389 | 100% | Us Weighted | 0 | 0 | 0 | 0.0046374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046374 | 100% | Us Weighted | 28.3401 | 6.5006 | 9.519 | 3.3568 | 0 | 14.3171 | 0 | 12.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9989 | 100.3693 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.36972 | 0.13395 | 0.093992 | 0.00036472 | 0 | 0.31954 | 0 | 0.14583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.3385 | 1.497% | CZ 1A | 12.2271 | 4.4301 | 3.1085 | 0.012062 | 0 | 10.5677 | 0 | 4.8229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.2663 | 1.497% | CZ 1A | 3.5825 | 1.298 | 0.91077 | 0.003534 | 0 | 3.0963 | 0 | 1.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.9699 | 1.497% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.497% | CZ 1A | 37.5052 | 13.5888 | 9.5349 | 0.036998 | 0 | 32.4154 | 0 | 14.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 135.782 | 1.497%
CZ 1B | 0.36972 | 0.13395 | 0.093992 | 0.0011462 | 0 | 0.25712 | 0 | 0.16209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2931 | 0% | CZ 1B | 12.2271 | 4.4301 | 3.1085 | 0.037908 | 0 | 8.5035 | 0 | 5.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.7655 | 0% | CZ 1B | 3.5825 | 1.298 | 0.91077 | 0.011107 | 0 | 2.4915 | 0 | 1.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.5302 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5052 | 13.5888 | 9.5349 | 0.11628 | 0 | 26.0835 | 0 | 16.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 131.1784 | 0%
CZ 2A | 0.36972 | 0.1339 | 0.093992 | 0.0084529 | 0 | 0.2392 | 0 | 0.14088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2613 | 18.97% | CZ 2A | 12.2271 | 4.4284 | 3.1085 | 0.29809 | 0 | 7.9107 | 0 | 4.6592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.7299 | 18.97% | CZ 2A | 3.5825 | 1.2975 | 0.91077 | 0.079263 | 0 | 2.3178 | 0 | 1.3651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.2187 | 18.97% | CZ 2A | 0 | 0 | 0 | 0.00027563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00027563 | 18.97% | CZ 2A | 37.5052 | 13.5835 | 9.5349 | 0.85993 | 0 | 24.2653 | 0 | 14.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 127.9475 | 18.97%
CZ 2B | 0.36972 | 0.13385 | 0.093992 | 0.0030911 | 0 | 0.22248 | 0 | 0.15016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2484 | 5.157% | CZ 2B | 12.2271 | 4.4266 | 3.1085 | 0.10339 | 0 | 7.3576 | 0 | 4.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.2871 | 5.157% | CZ 2B | 3.5825 | 1.297 | 0.91077 | 0.029787 | 0 | 2.1558 | 0 | 1.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.0965 | 5.157% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 5.157% | CZ 2B | 37.5052 | 13.5782 | 9.5349 | 0.31372 | 0 | 22.5687 | 0 | 15.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 126.6402 | 5.157%
CZ 3A | 0.36972 | 0.1338 | 0.093992 | 0.025964 | 0 | 0.18012 | 0 | 0.12953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2082 | 17.17% | CZ 3A | 12.2271 | 4.4249 | 3.1085 | 0.98729 | 0 | 5.9567 | 0 | 4.2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.086 | 17.17% | CZ 3A | 3.5825 | 1.2965 | 0.91077 | 0.23325 | 0 | 1.7453 | 0 | 1.2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.6891 | 17.17% | CZ 3A | 0 | 0 | 0 | 0.0019122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019122 | 17.17% | CZ 3A | 37.5052 | 13.5729 | 9.5349 | 2.6509 | 0 | 18.2716 | 0 | 13.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 122.582 | 17.17%
CZ 3B | 0.36972 | 0.13385 | 0.093992 | 0.011092 | 0 | 0.13583 | 0 | 0.13609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1557 | 8.466% | CZ 3B | 12.2271 | 4.4266 | 3.1085 | 0.38769 | 0 | 4.4921 | 0 | 4.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.2406 | 8.466% | CZ 3B | 3.5825 | 1.297 | 0.91077 | 0.10451 | 0 | 1.3162 | 0 | 1.3187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.1953 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00031008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00031008 | 8.466% | CZ 3B | 37.5052 | 13.5782 | 9.5349 | 1.128 | 0 | 13.779 | 0 | 13.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 117.2377 | 8.466%
CZ 3C | 0.36972 | 0.1338 | 0.093992 | 0.0054878 | 0 | 0.067004 | 0 | 0.10702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.0521 | 1.386% | CZ 3C | 12.2271 | 4.4249 | 3.1085 | 0.18265 | 0 | 2.2159 | 0 | 3.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 34.7962 | 1.386% | CZ 3C | 3.5825 | 1.2965 | 0.91077 | 0.053011 | 0 | 0.64925 | 0 | 1.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.1947 | 1.386% | CZ 3C | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 1.386% | CZ 3C | 37.5052 | 13.5729 | 9.5349 | 0.55685 | 0 | 6.797 | 0 | 10.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 106.73 | 1.386%
CZ 4A | 0.36972 | 0.13375 | 0.093992 | 0.045757 | 0 | 0.13109 | 0 | 0.12619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1756 | 16.69% | CZ 4A | 12.2271 | 4.4232 | 3.1085 | 1.9211 | 0 | 4.3353 | 0 | 4.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.2864 | 16.69% | CZ 4A | 3.5825 | 1.296 | 0.91077 | 0.38521 | 0 | 1.2702 | 0 | 1.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.3331 | 16.69% | CZ 4A | 0 | 0 | 0 | 0.0060638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060638 | 16.69% | CZ 4A | 37.5052 | 13.5676 | 9.5349 | 4.6955 | 0 | 13.2981 | 0 | 12.8012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 119.3095 | 16.69%
CZ 4B | 0.36972 | 0.13375 | 0.093992 | 0.026963 | 0 | 0.13818 | 0 | 0.15355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1912 | 0.844% | CZ 4B | 12.2271 | 4.4232 | 3.1085 | 0.98902 | 0 | 4.5696 | 0 | 5.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.4933 | 0.844% | CZ 4B | 3.5825 | 1.296 | 0.91077 | 0.24738 | 0 | 1.3389 | 0 | 1.4878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.529 | 0.844% | CZ 4B | 0 | 0 | 0 | 0.001447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001447 | 0.844% | CZ 4B | 37.5052 | 13.5676 | 9.5349 | 2.748 | 0 | 14.0169 | 0 | 15.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 120.8556 | 0.844%
CZ 4C | 0.36972 | 0.13369 | 0.093992 | 0.029865 | 0 | 0.078987 | 0 | 0.12958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1109 | 2.185% | CZ 4C | 12.2271 | 4.4215 | 3.1085 | 1.0769 | 0 | 2.6122 | 0 | 4.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.8294 | 2.185% | CZ 4C | 3.5825 | 1.2955 | 0.91077 | 0.27666 | 0 | 0.76537 | 0 | 1.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.7521 | 2.185% | CZ 4C | 0 | 0 | 0 | 0.0013265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013265 | 2.185% | CZ 4C | 37.5052 | 13.5623 | 9.5349 | 3.0414 | 0 | 8.0127 | 0 | 13.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 112.7082 | 2.185%
CZ 5A | 0.36972 | 0.13375 | 0.093992 | 0.076894 | 0 | 0.10686 | 0 | 0.12676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1831 | 16.4% | CZ 5A | 12.2271 | 4.4232 | 3.1085 | 3.8627 | 0 | 3.5341 | 0 | 4.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.4457 | 16.4% | CZ 5A | 3.5825 | 1.296 | 0.91077 | 0.55686 | 0 | 1.0355 | 0 | 1.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.2756 | 16.4% | CZ 5A | 0 | 0 | 0 | 0.019621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019621 | 16.4% | CZ 5A | 37.5052 | 13.5676 | 9.5349 | 7.9744 | 0 | 10.8404 | 0 | 12.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 120.1888 | 16.4%
CZ 5B | 0.36972 | 0.13364 | 0.093992 | 0.040085 | 0 | 0.09863 | 0 | 0.13963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1508 | 5.738% | CZ 5B | 12.2271 | 4.4197 | 3.1085 | 1.5145 | 0 | 3.2618 | 0 | 4.6179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.2475 | 5.738% | CZ 5B | 3.5825 | 1.295 | 0.91077 | 0.36148 | 0 | 0.9557 | 0 | 1.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.1241 | 5.738% | CZ 5B | 0 | 0 | 0 | 0.002808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002808 | 5.738% | CZ 5B | 37.5052 | 13.5571 | 9.5349 | 4.0913 | 0 | 10.0053 | 0 | 14.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 116.7655 | 5.738%
CZ 5C | 0.36972 | 0.13354 | 0.093992 | 0.035427 | 0 | 0.055072 | 0 | 0.11582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.0787 | 0% | CZ 5C | 12.2271 | 4.4163 | 3.1085 | 1.2458 | 0 | 1.8213 | 0 | 3.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 35.7473 | 0% | CZ 5C | 3.5825 | 1.294 | 0.91077 | 0.3327 | 0 | 0.53364 | 0 | 1.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.4416 | 0% | CZ 5C | 0 | 0 | 0 | 0.0011025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011025 | 0% | CZ 5C | 37.5052 | 13.5465 | 9.5349 | 3.6036 | 0 | 5.5867 | 0 | 11.7495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 109.4332 | 0%
CZ 6A | 0.36972 | 0.13369 | 0.093992 | 0.084863 | 0 | 0.077163 | 0 | 0.11728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1518 | 4.301% | CZ 6A | 12.2271 | 4.4215 | 3.1085 | 4.5225 | 0 | 2.5519 | 0 | 3.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.808 | 4.301% | CZ 6A | 3.5825 | 1.2955 | 0.91077 | 0.57756 | 0 | 0.7477 | 0 | 1.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.9161 | 4.301% | CZ 6A | 0 | 0 | 0 | 0.025513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025513 | 4.301% | CZ 6A | 37.5052 | 13.5623 | 9.5349 | 8.8351 | 0 | 7.8277 | 0 | 11.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 117.0696 | 4.301%
CZ 6B | 0.36972 | 0.13364 | 0.093992 | 0.064899 | 0 | 0.072474 | 0 | 0.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1486 | 0.5387% | CZ 6B | 12.2271 | 4.4197 | 3.1085 | 3.0582 | 0 | 2.3968 | 0 | 4.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 38.8985 | 0.5387% | CZ 6B | 3.5825 | 1.295 | 0.91077 | 0.4988 | 0 | 0.70226 | 0 | 1.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.9999 | 0.5387% | CZ 6B | 0 | 0 | 0 | 0.013557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013557 | 0.5387% | CZ 6B | 37.5052 | 13.5571 | 9.5349 | 6.7038 | 0 | 7.352 | 0 | 14.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 116.6402 | 0.5387%
CZ 7 | 0.36972 | 0.13359 | 0.093992 | 0.13816 | 0 | 0.058719 | 0 | 0.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1945 | 0.5766% | CZ 7 | 12.2271 | 4.418 | 3.1085 | 9.1273 | 0 | 1.9419 | 0 | 4.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.0613 | 0.5766% | CZ 7 | 3.5825 | 1.2945 | 0.91077 | 0.68863 | 0 | 0.56898 | 0 | 1.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.9242 | 0.5766% | CZ 7 | 0 | 0 | 0 | 0.06777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06777 | 0.5766% | CZ 7 | 37.5052 | 13.5518 | 9.5349 | 14.6166 | 0 | 5.9567 | 0 | 12.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 121.7728 | 0.5766%
CZ 8 | 0.36972 | 0.13276 | 0.094461 | 0.20922 | 0 | 0.041421 | 0 | 0.12958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2523 | 0.08356% | CZ 8 | 12.2271 | 4.3904 | 3.124 | 17.024 | 0 | 1.3699 | 0 | 4.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 51.5186 | 0.08356% | CZ 8 | 3.5825 | 1.2864 | 0.91532 | 0.58615 | 0 | 0.40137 | 0 | 1.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.693 | 0.08356% | CZ 8 | 0 | 0 | 0 | 0.15023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15023 | 0.08356% | CZ 8 | 37.5052 | 13.4672 | 9.5824 | 22.557 | 0 | 4.2019 | 0 | 13.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 128.3655 | 0.08356%
Us Weighted | 0.36972 | 0.13379 | 0.093993 | 0.03564 | 0 | 0.15702 | 0 | 0.13251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1978 | 100% | Us Weighted | 12.2271 | 4.4247 | 3.1085 | 1.6177 | 0 | 5.1929 | 0 | 4.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0509 | 100% | Us Weighted | 3.5825 | 1.2964 | 0.91078 | 0.28273 | 0 | 1.5215 | 0 | 1.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5436 | 100% | Us Weighted | 0 | 0 | 0 | 0.0065272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065272 | 100% | Us Weighted | 37.5052 | 13.5722 | 9.5349 | 3.6733 | 0 | 15.9287 | 0 | 13.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 121.563 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.36972 | 0.13395 | 0.093992 | 0.00046892 | 0 | 0.40864 | 0 | 0.14563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.4275 | 1.497% | CZ 1A | 12.2271 | 4.4301 | 3.1085 | 0.015508 | 0 | 13.5142 | 0 | 4.8161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 47.2094 | 1.497% | CZ 1A | 3.5825 | 1.298 | 0.91077 | 0.0045438 | 0 | 3.9596 | 0 | 1.4111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 13.8322 | 1.497% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.497% | CZ 1A | 37.5052 | 13.5888 | 9.5349 | 0.047569 | 0 | 41.4534 | 0 | 14.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 144.8095 | 1.497%
CZ 1B | 0.36972 | 0.13395 | 0.093992 | 0.0014589 | 0 | 0.32324 | 0 | 0.16209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.3596 | 0% | CZ 1B | 12.2271 | 4.4301 | 3.1085 | 0.048247 | 0 | 10.6901 | 0 | 5.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.9624 | 0% | CZ 1B | 3.5825 | 1.298 | 0.91077 | 0.014136 | 0 | 3.1322 | 0 | 1.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 13.1739 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5052 | 13.5888 | 9.5349 | 0.14799 | 0 | 32.7906 | 0 | 16.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 137.9173 | 0%
CZ 2A | 0.36972 | 0.1339 | 0.093992 | 0.011577 | 0 | 0.30808 | 0 | 0.14479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.3372 | 18.97% | CZ 2A | 12.2271 | 4.4284 | 3.1085 | 0.40836 | 0 | 10.1887 | 0 | 4.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.2474 | 18.97% | CZ 2A | 3.5825 | 1.2975 | 0.91077 | 0.10855 | 0 | 2.9853 | 0 | 1.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.9533 | 18.97% | CZ 2A | 0 | 0 | 0 | 0.00037899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037899 | 18.97% | CZ 2A | 37.5052 | 13.5835 | 9.5349 | 1.1778 | 0 | 31.2526 | 0 | 14.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 135.649 | 18.97%
CZ 2B | 0.36972 | 0.13385 | 0.093992 | 0.0047584 | 0 | 0.28562 | 0 | 0.15631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.3194 | 5.157% | CZ 2B | 12.2271 | 4.4266 | 3.1085 | 0.15852 | 0 | 9.446 | 0 | 5.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 43.6339 | 5.157% | CZ 2B | 3.5825 | 1.297 | 0.91077 | 0.045942 | 0 | 2.7677 | 0 | 1.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.7841 | 5.157% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 5.157% | CZ 2B | 37.5052 | 13.5782 | 9.5349 | 0.48285 | 0 | 28.9746 | 0 | 15.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 133.8389 | 5.157%
CZ 3A | 0.36972 | 0.1338 | 0.093992 | 0.03249 | 0 | 0.23113 | 0 | 0.13255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2688 | 17.17% | CZ 3A | 12.2271 | 4.4249 | 3.1085 | 1.2182 | 0 | 7.6437 | 0 | 4.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.1038 | 17.17% | CZ 3A | 3.5825 | 1.2965 | 0.91077 | 0.29433 | 0 | 2.2396 | 0 | 1.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.2737 | 17.17% | CZ 3A | 0 | 0 | 0 | 0.0021361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021361 | 17.17% | CZ 3A | 37.5052 | 13.5729 | 9.5349 | 3.3149 | 0 | 23.4461 | 0 | 13.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 128.7269 | 17.17%
CZ 3B | 0.36972 | 0.13385 | 0.093992 | 0.013678 | 0 | 0.17043 | 0 | 0.13943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1962 | 8.466% | CZ 3B | 12.2271 | 4.4266 | 3.1085 | 0.47901 | 0 | 5.6362 | 0 | 4.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.5864 | 8.466% | CZ 3B | 3.5825 | 1.297 | 0.91077 | 0.12874 | 0 | 1.6514 | 0 | 1.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.5871 | 8.466% | CZ 3B | 0 | 0 | 0 | 0.00039622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039622 | 8.466% | CZ 3B | 37.5052 | 13.5782 | 9.5349 | 1.3911 | 0 | 17.2886 | 0 | 14.1437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 121.3486 | 8.466%
CZ 3C | 0.36972 | 0.1338 | 0.093992 | 0.009152 | 0 | 0.089199 | 0 | 0.12301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.094 | 1.386% | CZ 3C | 12.2271 | 4.4249 | 3.1085 | 0.30499 | 0 | 2.9499 | 0 | 4.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.1816 | 1.386% | CZ 3C | 3.5825 | 1.2965 | 0.91077 | 0.088351 | 0 | 0.86432 | 0 | 1.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.6001 | 1.386% | CZ 3C | 0 | 0 | 0 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4454e-05 | 1.386% | CZ 3C | 37.5052 | 13.5729 | 9.5349 | 0.92871 | 0 | 9.0486 | 0 | 12.4788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 110.9761 | 1.386%
CZ 4A | 0.36972 | 0.13375 | 0.093992 | 0.059452 | 0 | 0.166 | 0 | 0.12989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2279 | 16.69% | CZ 4A | 12.2271 | 4.4232 | 3.1085 | 2.469 | 0 | 5.4898 | 0 | 4.2957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.1111 | 16.69% | CZ 4A | 3.5825 | 1.296 | 0.91077 | 0.50436 | 0 | 1.6085 | 0 | 1.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.8264 | 16.69% | CZ 4A | 0 | 0 | 0 | 0.0074764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074764 | 16.69% | CZ 4A | 37.5052 | 13.5676 | 9.5349 | 6.0973 | 0 | 16.8393 | 0 | 13.1765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 124.6278 | 16.69%
CZ 4B | 0.36972 | 0.13375 | 0.093992 | 0.034039 | 0 | 0.17204 | 0 | 0.15792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2366 | 0.844% | CZ 4B | 12.2271 | 4.4232 | 3.1085 | 1.2578 | 0 | 5.6897 | 0 | 5.2227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.0268 | 0.844% | CZ 4B | 3.5825 | 1.296 | 0.91077 | 0.311 | 0 | 1.6671 | 0 | 1.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.9632 | 0.844% | CZ 4B | 0 | 0 | 0 | 0.0019639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019639 | 0.844% | CZ 4B | 37.5052 | 13.5676 | 9.5349 | 3.4705 | 0 | 17.4524 | 0 | 16.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 125.4576 | 0.844%
CZ 4C | 0.36972 | 0.13369 | 0.093992 | 0.039895 | 0 | 0.095764 | 0 | 0.13244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1406 | 2.185% | CZ 4C | 12.2271 | 4.4215 | 3.1085 | 1.4422 | 0 | 3.167 | 0 | 4.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 37.8443 | 2.185% | CZ 4C | 3.5825 | 1.2955 | 0.91077 | 0.36905 | 0 | 0.92794 | 0 | 1.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.0348 | 2.185% | CZ 4C | 0 | 0 | 0 | 0.001826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001826 | 2.185% | CZ 4C | 37.5052 | 13.5623 | 9.5349 | 4.0632 | 0 | 9.7146 | 0 | 13.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 115.7227 | 2.185%
CZ 5A | 0.36972 | 0.13375 | 0.093992 | 0.11523 | 0 | 0.13573 | 0 | 0.13547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.259 | 16.4% | CZ 5A | 12.2271 | 4.4232 | 3.1085 | 5.813 | 0 | 4.4887 | 0 | 4.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 43.6384 | 16.4% | CZ 5A | 3.5825 | 1.296 | 0.91077 | 0.831 | 0 | 1.3152 | 0 | 1.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.9137 | 16.4% | CZ 5A | 0 | 0 | 0 | 0.029768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029768 | 16.4% | CZ 5A | 37.5052 | 13.5676 | 9.5349 | 11.9534 | 0 | 13.7685 | 0 | 13.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 127.9786 | 16.4%
CZ 5B | 0.36972 | 0.13364 | 0.093992 | 0.061034 | 0 | 0.12291 | 0 | 0.14792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2043 | 5.738% | CZ 5B | 12.2271 | 4.4197 | 3.1085 | 2.3881 | 0 | 4.0648 | 0 | 4.8919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.198 | 5.738% | CZ 5B | 3.5825 | 1.295 | 0.91077 | 0.53869 | 0 | 1.191 | 0 | 1.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.6169 | 5.738% | CZ 5B | 0 | 0 | 0 | 0.0054953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054953 | 5.738% | CZ 5B | 37.5052 | 13.5571 | 9.5349 | 6.2402 | 0 | 12.4683 | 0 | 15.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 122.2178 | 5.738%
CZ 5C | 0.36972 | 0.13354 | 0.093992 | 0.057041 | 0 | 0.062679 | 0 | 0.11973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.1118 | 0% | CZ 5C | 12.2271 | 4.4163 | 3.1085 | 2.0556 | 0 | 2.0729 | 0 | 3.9597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.9379 | 0% | CZ 5C | 3.5825 | 1.294 | 0.91077 | 0.52859 | 0 | 0.60735 | 0 | 1.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 10.749 | 0% | CZ 5C | 0 | 0 | 0 | 0.0025151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025151 | 0% | CZ 5C | 37.5052 | 13.5465 | 9.5349 | 5.8087 | 0 | 6.3583 | 0 | 12.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 112.8064 | 0%
CZ 6A | 0.36972 | 0.13369 | 0.093992 | 0.13796 | 0 | 0.093263 | 0 | 0.12562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2293 | 4.301% | CZ 6A | 12.2271 | 4.4215 | 3.1085 | 7.4686 | 0 | 3.0843 | 0 | 4.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 43.5622 | 4.301% | CZ 6A | 3.5825 | 1.2955 | 0.91077 | 0.92238 | 0 | 0.9037 | 0 | 1.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.4977 | 4.301% | CZ 6A | 0 | 0 | 0 | 0.043205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043205 | 4.301% | CZ 6A | 37.5052 | 13.5623 | 9.5349 | 14.3787 | 0 | 9.4609 | 0 | 12.7431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 125.0921 | 4.301%
CZ 6B | 0.36972 | 0.13364 | 0.093992 | 0.10679 | 0 | 0.0855 | 0 | 0.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2121 | 0.5387% | CZ 6B | 12.2271 | 4.4197 | 3.1085 | 5.2789 | 0 | 2.8276 | 0 | 4.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.8344 | 0.5387% | CZ 6B | 3.5825 | 1.295 | 0.91077 | 0.78557 | 0 | 0.82848 | 0 | 1.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.4962 | 0.5387% | CZ 6B | 0 | 0 | 0 | 0.025978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025978 | 0.5387% | CZ 6B | 37.5052 | 13.5571 | 9.5349 | 11.0635 | 0 | 8.6733 | 0 | 14.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 123.1933 | 0.5387%
CZ 7 | 0.36972 | 0.13359 | 0.093992 | 0.21542 | 0 | 0.075288 | 0 | 0.14792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.311 | 0.5766% | CZ 7 | 12.2271 | 4.418 | 3.1085 | 14.1389 | 0 | 2.4899 | 0 | 4.8919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 50.3722 | 0.5766% | CZ 7 | 3.5825 | 1.2945 | 0.91077 | 1.087 | 0 | 0.72953 | 0 | 1.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.7032 | 0.5766% | CZ 7 | 0 | 0 | 0 | 0.10429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10429 | 0.5766% | CZ 7 | 37.5052 | 13.5518 | 9.5349 | 22.7785 | 0 | 7.6374 | 0 | 15.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 133.9199 | 0.5766%
CZ 8 | 0.36972 | 0.13276 | 0.094514 | 0.2893 | 0 | 0.053353 | 0 | 0.15282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.3676 | 0.08356% | CZ 8 | 12.2271 | 4.3904 | 3.1257 | 23.6892 | 0 | 1.7644 | 0 | 5.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 59.3486 | 0.08356% | CZ 8 | 3.5825 | 1.2864 | 0.91582 | 0.7891 | 0 | 0.51698 | 0 | 1.4808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 11.2372 | 0.08356% | CZ 8 | 0 | 0 | 0 | 0.20996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20996 | 0.08356% | CZ 8 | 37.5052 | 13.4672 | 9.5877 | 31.2097 | 0 | 5.4123 | 0 | 15.5021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 140.5911 | 0.08356%
Us Weighted | 0.36972 | 0.13379 | 0.093993 | 0.050787 | 0 | 0.20014 | 0 | 0.13776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2751 | 1.2613 | 100% | Us Weighted | 12.2271 | 4.4247 | 3.1085 | 2.3354 | 0 | 6.6191 | 0 | 4.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.3685 | 100% | Us Weighted | 3.5825 | 1.2964 | 0.91078 | 0.39858 | 0 | 1.9394 | 0 | 1.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6657 | 12.1282 | 100% | Us Weighted | 0 | 0 | 0 | 0.0097506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097506 | 100% | Us Weighted | 37.5052 | 13.5722 | 9.5349 | 5.2384 | 0 | 20.3033 | 0 | 13.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9069 | 128.0356 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.13078 | 0.069869 | 0.00015631 | 0.00020841 | 0 | 0.21909 | 0 | 0.046319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.48992 | 1.497% | CZ 1A | 4.325 | 2.3107 | 0.0051693 | 0.0068924 | 0 | 7.2456 | 0 | 1.5318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.2023 | 1.497% | CZ 1A | 1.2672 | 0.67702 | 0.0015146 | 0.0020194 | 0 | 2.1229 | 0 | 0.44882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.7472 | 1.497% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.497% | CZ 1A | 13.2664 | 7.0877 | 0.015856 | 0.021142 | 0 | 22.2251 | 0 | 4.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 49.6987 | 1.497%
CZ 1B | 0.13005 | 0.069869 | 0.00015631 | 0.00041682 | 0 | 0.12979 | 0 | 0.034909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.38868 | 0% | CZ 1B | 4.3008 | 2.3107 | 0.0051693 | 0.013785 | 0 | 4.2922 | 0 | 1.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.8543 | 0% | CZ 1B | 1.2601 | 0.67702 | 0.0015146 | 0.0040389 | 0 | 1.2576 | 0 | 0.33826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.7663 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 13.1924 | 7.0877 | 0.015856 | 0.042283 | 0 | 13.1659 | 0 | 3.5412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 39.4291 | 0%
CZ 2A | 0.12968 | 0.069869 | 0.00015631 | 0.0028126 | 0 | 0.16621 | 0 | 0.042203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.43443 | 18.97% | CZ 2A | 4.2888 | 2.3107 | 0.0051693 | 0.096492 | 0 | 5.4967 | 0 | 1.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 14.3706 | 18.97% | CZ 2A | 1.2566 | 0.67702 | 0.0015146 | 0.026758 | 0 | 1.6105 | 0 | 0.40894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 4.209 | 18.97% | CZ 2A | 0 | 0 | 0 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.168e-05 | 18.97% | CZ 2A | 13.1554 | 7.0877 | 0.015856 | 0.28578 | 0 | 16.8604 | 0 | 4.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 44.0701 | 18.97%
CZ 2B | 0.13036 | 0.069817 | 0.00015631 | 0.0014068 | 0 | 0.11525 | 0 | 0.033606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.37409 | 5.157% | CZ 2B | 4.3112 | 2.3089 | 0.0051693 | 0.046524 | 0 | 3.8115 | 0 | 1.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.3718 | 5.157% | CZ 2B | 1.2632 | 0.67652 | 0.0015146 | 0.013631 | 0 | 1.1168 | 0 | 0.32564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.6249 | 5.157% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.157% | CZ 2B | 13.2241 | 7.0824 | 0.015856 | 0.14271 | 0 | 11.6913 | 0 | 3.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 37.9492 | 5.157%
CZ 3A | 0.12942 | 0.069713 | 0.00015631 | 0.0028514 | 0 | 0.12374 | 0 | 0.030636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.38002 | 17.17% | CZ 3A | 4.2802 | 2.3055 | 0.0051693 | 0.082713 | 0 | 4.0924 | 0 | 1.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.5562 | 17.17% | CZ 3A | 1.2541 | 0.67551 | 0.0015146 | 0.029282 | 0 | 1.199 | 0 | 0.29686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.684 | 17.17% | CZ 3A | 0 | 0 | 0 | -0.00017227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00017227 | 17.17% | CZ 3A | 13.1289 | 7.0719 | 0.015856 | 0.28772 | 0 | 12.5528 | 0 | 3.1078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 38.5488 | 17.17%
CZ 3B | 0.13031 | 0.069817 | 0.00015631 | 0.00073225 | 0 | 0.065649 | 0 | 0.02131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.31147 | 8.466% | CZ 3B | 4.3095 | 2.3089 | 0.0051693 | 0.013789 | 0 | 2.1711 | 0 | 0.70475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 10.2903 | 8.466% | CZ 3B | 1.2627 | 0.67652 | 0.0015146 | 0.0085827 | 0 | 0.63613 | 0 | 0.20649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.0196 | 8.466% | CZ 3B | 0 | 0 | 0 | -0.00015504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00015504 | 8.466% | CZ 3B | 13.2188 | 7.0824 | 0.015856 | 0.072906 | 0 | 6.6596 | 0 | 2.1617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 31.5951 | 8.466%
CZ 3C | 0.12984 | 0.069765 | 0.00015631 | 0.0019278 | 0 | 0.0508 | 0 | 0.033814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.3098 | 1.386% | CZ 3C | 4.294 | 2.3072 | 0.0051693 | 0.063755 | 0 | 1.68 | 0 | 1.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 10.2455 | 1.386% | CZ 3C | 1.2581 | 0.67601 | 0.0015146 | 0.01868 | 0 | 0.49224 | 0 | 0.32766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.0019 | 1.386% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386% | CZ 3C | 13.1712 | 7.0772 | 0.015856 | 0.19556 | 0 | 5.1533 | 0 | 3.4302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 31.427 | 1.386%
CZ 4A | 0.13411 | 0.069713 | 0.00015631 | 0.028551 | 0 | 0.083103 | 0 | 0.031209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.37034 | 16.69% | CZ 4A | 4.4352 | 2.3055 | 0.0051693 | 1.2698 | 0 | 2.7483 | 0 | 1.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.5733 | 16.69% | CZ 4A | 1.2995 | 0.67551 | 0.0015146 | 0.23022 | 0 | 0.80526 | 0 | 0.30241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.5421 | 16.69% | CZ 4A | 0 | 0 | 0 | 0.0048407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048407 | 16.69% | CZ 4A | 13.6046 | 7.0719 | 0.015856 | 2.9392 | 0 | 8.4302 | 0 | 3.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 37.6115 | 16.69%
CZ 4B | 0.13463 | 0.069765 | 0.00015631 | 0.016211 | 0 | 0.084562 | 0 | 0.03668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.3655 | 0.844% | CZ 4B | 4.4525 | 2.3072 | 0.0051693 | 0.63923 | 0 | 2.7966 | 0 | 1.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.1909 | 0.844% | CZ 4B | 1.3046 | 0.67601 | 0.0015146 | 0.14237 | 0 | 0.81939 | 0 | 0.35542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.527 | 0.844% | CZ 4B | 0 | 0 | 0 | 0.0015332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015332 | 0.844% | CZ 4B | 13.6575 | 7.0772 | 0.015856 | 1.6581 | 0 | 8.5782 | 0 | 3.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 37.0914 | 0.844%
CZ 4C | 0.13281 | 0.069609 | 0.00015631 | 0.020486 | 0 | 0.044547 | 0 | 0.025009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.31611 | 2.185% | CZ 4C | 4.3922 | 2.3021 | 0.0051693 | 0.77019 | 0 | 1.4732 | 0 | 0.82709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 10.547 | 2.185% | CZ 4C | 1.2869 | 0.6745 | 0.0015146 | 0.18528 | 0 | 0.43166 | 0 | 0.24233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.0499 | 2.185% | CZ 4C | 0 | 0 | 0 | 0.0013781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013781 | 2.185% | CZ 4C | 13.4725 | 7.0613 | 0.015856 | 2.0904 | 0 | 4.519 | 0 | 2.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 32.0798 | 2.185%
CZ 5A | 0.13395 | 0.069504 | 0.00015631 | 0.060033 | 0 | 0.065649 | 0 | 0.034387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.38718 | 16.4% | CZ 5A | 4.4301 | 2.2986 | 0.0051693 | 3.2958 | 0 | 2.1711 | 0 | 1.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 14.1151 | 16.4% | CZ 5A | 1.298 | 0.67349 | 0.0015146 | 0.3948 | 0 | 0.63613 | 0 | 0.33321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.5648 | 16.4% | CZ 5A | 0 | 0 | 0 | 0.019483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019483 | 16.4% | CZ 5A | 13.5888 | 7.0507 | 0.015856 | 6.2627 | 0 | 6.6596 | 0 | 3.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 39.4498 | 16.4%
CZ 5B | 0.13328 | 0.069765 | 0.00015631 | 0.029923 | 0 | 0.062419 | 0 | 0.034804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.35384 | 5.738% | CZ 5B | 4.4077 | 2.3072 | 0.0051693 | 1.2492 | 0 | 2.0643 | 0 | 1.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 11.9616 | 5.738% | CZ 5B | 1.2914 | 0.67601 | 0.0015146 | 0.25294 | 0 | 0.60483 | 0 | 0.33725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.3917 | 5.738% | CZ 5B | 0 | 0 | 0 | 0.0038588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038588 | 5.738% | CZ 5B | 13.5201 | 7.0772 | 0.015856 | 3.0698 | 0 | 6.3319 | 0 | 3.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 35.9291 | 5.738%
CZ 5C | 0.13093 | 0.069348 | 0.00015631 | 0.029626 | 0 | 0.025947 | 0 | 0.020059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.29957 | 0% | CZ 5C | 4.3301 | 2.2934 | 0.0051693 | 1.12 | 0 | 0.8581 | 0 | 0.66339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 10.0473 | 0% | CZ 5C | 1.2687 | 0.67197 | 0.0015146 | 0.26707 | 0 | 0.25142 | 0 | 0.19437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 2.8828 | 0% | CZ 5C | 0 | 0 | 0 | 0.0020844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020844 | 0% | CZ 5C | 13.2822 | 7.0349 | 0.015856 | 3.0238 | 0 | 2.6321 | 0 | 2.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 30.4075 | 0%
CZ 6A | 0.13354 | 0.0694 | 0.00015631 | 0.06658 | 0 | 0.042515 | 0 | 0.02876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.36445 | 4.301% | CZ 6A | 4.4163 | 2.2952 | 0.0051693 | 3.897 | 0 | 1.406 | 0 | 0.95115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 13.748 | 4.301% | CZ 6A | 1.294 | 0.67248 | 0.0015146 | 0.40339 | 0 | 0.41197 | 0 | 0.27868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.2897 | 4.301% | CZ 6A | 0 | 0 | 0 | 0.025203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025203 | 4.301% | CZ 6A | 13.5465 | 7.0402 | 0.015856 | 6.9777 | 0 | 4.3129 | 0 | 2.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 37.1944 | 4.301%
CZ 6B | 0.13364 | 0.069661 | 0.00015631 | 0.050598 | 0 | 0.039337 | 0 | 0.031001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.34789 | 0.5387% | CZ 6B | 4.4197 | 2.3038 | 0.0051693 | 2.8065 | 0 | 1.3009 | 0 | 1.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.6385 | 0.5387% | CZ 6B | 1.295 | 0.675 | 0.0015146 | 0.32867 | 0 | 0.38117 | 0 | 0.30039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.2094 | 0.5387% | CZ 6B | 0 | 0 | 0 | 0.016848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016848 | 0.5387% | CZ 6B | 13.5571 | 7.0666 | 0.015856 | 5.2823 | 0 | 3.9905 | 0 | 3.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 35.4408 | 0.5387%
CZ 7 | 0.13807 | 0.069452 | 0.00015631 | 0.1136 | 0 | 0.034856 | 0 | 0.043036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.42267 | 0.5766% | CZ 7 | 4.5662 | 2.2969 | 0.0051693 | 8.0126 | 0 | 1.1528 | 0 | 1.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.234 | 0.5766% | CZ 7 | 1.3379 | 0.67298 | 0.0015146 | 0.49376 | 0 | 0.33775 | 0 | 0.41702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.4886 | 0.5766% | CZ 7 | 0 | 0 | 0 | 0.063274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063274 | 0.5766% | CZ 7 | 14.0063 | 7.0454 | 0.015856 | 12.085 | 0 | 3.5359 | 0 | 4.3657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 43.438 | 0.5766%
CZ 8 | 0.13411 | 0.068254 | 0.00067733 | 0.11653 | 0 | 0.02428 | 0 | 0.039962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.40731 | 0.08356% | CZ 8 | 4.4352 | 2.2573 | 0.0224 | 10.1244 | 0 | 0.80296 | 0 | 1.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 19.741 | 0.08356% | CZ 8 | 1.2995 | 0.66137 | 0.0065632 | 0.23476 | 0 | 0.23527 | 0 | 0.38723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.0524 | 0.08356% | CZ 8 | 0 | 0 | 0 | 0.093231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093231 | 0.08356% | CZ 8 | 13.6046 | 6.9239 | 0.06871 | 12.6479 | 0 | 2.463 | 0 | 4.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 42.1457 | 0.08356%
Us Weighted | 0.13174 | 0.06971 | 0.00015674 | 0.021989 | 0 | 0.10042 | 0 | 0.033352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023498 | 0.38087 | 100% | Us Weighted | 4.3568 | 2.3054 | 0.0051837 | 1.1208 | 0 | 3.3212 | 0 | 1.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 12.9895 | 100% | Us Weighted | 1.2765 | 0.67548 | 0.0015188 | 0.15692 | 0 | 0.9731 | 0 | 0.32317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22769 | 3.6344 | 100% | Us Weighted | 0 | 0 | 0 | 0.0058526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058526 | 100% | Us Weighted | 13.364 | 7.0716 | 0.0159 | 2.2825 | 0 | 10.1874 | 0 | 3.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3837 | 38.6884 | 100%
Building Type: | Small Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 35.37% | 52.16% | 0.1663% | 44.44% | 0% | 53.61% | 0% | 31.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.32% | 1.497% | CZ 1A | 35.37% | 52.16% | 0.1663% | 44.44% | 0% | 53.61% | 0% | 31.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.32% | 1.497% | CZ 1A | 35.37% | 52.16% | 0.1663% | 44.44% | 0% | 53.61% | 0% | 31.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.32% | 1.497% | CZ 1A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.497% | CZ 1A | 35.37% | 52.16% | 0.1663% | 44.44% | 0% | 53.61% | 0% | 31.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 34.32% | 1.497%
CZ 1B | 35.17% | 52.16% | 0.1663% | 28.57% | 0% | 40.15% | 0% | 21.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.59% | 0% | CZ 1B | 35.17% | 52.16% | 0.1663% | 28.57% | 0% | 40.15% | 0% | 21.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.59% | 0% | CZ 1B | 35.17% | 52.16% | 0.1663% | 28.57% | 0% | 40.15% | 0% | 21.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.59% | 0% | CZ 1B | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | CZ 1B | 35.17% | 52.16% | 0.1663% | 28.57% | 0% | 40.15% | 0% | 21.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.59% | 0%
CZ 2A | 35.08% | 52.18% | 0.1663% | 24.29% | 0% | 53.95% | 0% | 29.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.49% | 18.97% | CZ 2A | 35.08% | 52.18% | 0.1663% | 23.63% | 0% | 53.95% | 0% | 29.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.48% | 18.97% | CZ 2A | 35.08% | 52.18% | 0.1663% | 24.65% | 0% | 53.95% | 0% | 29.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.49% | 18.97% | CZ 2A | 0% | 0% | 0% | 13.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.64% | 18.97% | CZ 2A | 35.08% | 52.18% | 0.1663% | 24.26% | 0% | 53.95% | 0% | 29.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.49% | 18.97%
CZ 2B | 35.26% | 52.16% | 0.1663% | 29.56% | 0% | 40.35% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.35% | 5.157% | CZ 2B | 35.26% | 52.16% | 0.1663% | 29.35% | 0% | 40.35% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.35% | 5.157% | CZ 2B | 35.26% | 52.16% | 0.1663% | 29.67% | 0% | 40.35% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.35% | 5.157% | CZ 2B | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.157% | CZ 2B | 35.26% | 52.16% | 0.1663% | 29.55% | 0% | 40.35% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.35% | 5.157%
CZ 3A | 35.01% | 52.1% | 0.1663% | 8.776% | 0% | 53.54% | 0% | 23.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.95% | 17.17% | CZ 3A | 35.01% | 52.1% | 0.1663% | 6.79% | 0% | 53.54% | 0% | 23.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.82% | 17.17% | CZ 3A | 35.01% | 52.1% | 0.1663% | 9.949% | 0% | 53.54% | 0% | 23.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.02% | 17.17% | CZ 3A | 0% | 0% | 0% | -8.065% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -8.065% | 17.17% | CZ 3A | 35.01% | 52.1% | 0.1663% | 8.68% | 0% | 53.54% | 0% | 23.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.95% | 17.17%
CZ 3B | 35.25% | 52.16% | 0.1663% | 5.353% | 0% | 38.52% | 0% | 15.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.04% | 8.466% | CZ 3B | 35.25% | 52.16% | 0.1663% | 2.879% | 0% | 38.52% | 0% | 15.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 25.99% | 8.466% | CZ 3B | 35.25% | 52.16% | 0.1663% | 6.667% | 0% | 38.52% | 0% | 15.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.06% | 8.466% | CZ 3B | 0% | 0% | 0% | -39.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -39.13% | 8.466% | CZ 3B | 35.25% | 52.16% | 0.1663% | 5.241% | 0% | 38.52% | 0% | 15.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.04% | 8.466%
CZ 3C | 35.12% | 52.14% | 0.1663% | 21.06% | 0% | 56.95% | 0% | 27.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.32% | 1.386% | CZ 3C | 35.12% | 52.14% | 0.1663% | 20.9% | 0% | 56.95% | 0% | 27.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.32% | 1.386% | CZ 3C | 35.12% | 52.14% | 0.1663% | 21.14% | 0% | 56.95% | 0% | 27.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.32% | 1.386% | CZ 3C | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.386% | CZ 3C | 35.12% | 52.14% | 0.1663% | 21.06% | 0% | 56.95% | 0% | 27.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.32% | 1.386%
CZ 4A | 36.27% | 52.12% | 0.1663% | 48.02% | 0% | 50.06% | 0% | 24.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.16% | 16.69% | CZ 4A | 36.27% | 52.12% | 0.1663% | 51.43% | 0% | 50.06% | 0% | 24.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.58% | 16.69% | CZ 4A | 36.27% | 52.12% | 0.1663% | 45.65% | 0% | 50.06% | 0% | 24.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.95% | 16.69% | CZ 4A | 0% | 0% | 0% | 64.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 64.75% | 16.69% | CZ 4A | 36.27% | 52.12% | 0.1663% | 48.21% | 0% | 50.06% | 0% | 24.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.18% | 16.69%
CZ 4B | 36.41% | 52.16% | 0.1663% | 47.62% | 0% | 49.15% | 0% | 23.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.56% | 0.844% | CZ 4B | 36.41% | 52.16% | 0.1663% | 50.82% | 0% | 49.15% | 0% | 23.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.71% | 0.844% | CZ 4B | 36.41% | 52.16% | 0.1663% | 45.78% | 0% | 49.15% | 0% | 23.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.48% | 0.844% | CZ 4B | 0% | 0% | 0% | 78.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 78.07% | 0.844% | CZ 4B | 36.41% | 52.16% | 0.1663% | 47.78% | 0% | 49.15% | 0% | 23.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.56% | 0.844%
CZ 4C | 35.92% | 52.07% | 0.1663% | 51.35% | 0% | 46.52% | 0% | 18.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.71% | 2.185% | CZ 4C | 35.92% | 52.07% | 0.1663% | 53.4% | 0% | 46.52% | 0% | 18.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.87% | 2.185% | CZ 4C | 35.92% | 52.07% | 0.1663% | 50.21% | 0% | 46.52% | 0% | 18.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.64% | 2.185% | CZ 4C | 0% | 0% | 0% | 75.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 75.47% | 2.185% | CZ 4C | 35.92% | 52.07% | 0.1663% | 51.45% | 0% | 46.52% | 0% | 18.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.72% | 2.185%
CZ 5A | 36.23% | 51.97% | 0.1663% | 52.1% | 0% | 48.37% | 0% | 25.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.75% | 16.4% | CZ 5A | 36.23% | 51.97% | 0.1663% | 56.7% | 0% | 48.37% | 0% | 25.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.35% | 16.4% | CZ 5A | 36.23% | 51.97% | 0.1663% | 47.51% | 0% | 48.37% | 0% | 25.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.92% | 16.4% | CZ 5A | 0% | 0% | 0% | 65.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 65.45% | 16.4% | CZ 5A | 36.23% | 51.97% | 0.1663% | 52.39% | 0% | 48.37% | 0% | 25.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.83% | 16.4%
CZ 5B | 36.05% | 52.2% | 0.1663% | 49.03% | 0% | 50.78% | 0% | 23.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.38% | 5.738% | CZ 5B | 36.05% | 52.2% | 0.1663% | 52.31% | 0% | 50.78% | 0% | 23.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.76% | 5.738% | CZ 5B | 36.05% | 52.2% | 0.1663% | 46.95% | 0% | 50.78% | 0% | 23.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.2% | 5.738% | CZ 5B | 0% | 0% | 0% | 70.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 70.22% | 5.738% | CZ 5B | 36.05% | 52.2% | 0.1663% | 49.19% | 0% | 50.78% | 0% | 23.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.4% | 5.738%
CZ 5C | 35.41% | 51.93% | 0.1663% | 51.94% | 0% | 41.4% | 0% | 16.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.94% | 0% | CZ 5C | 35.41% | 51.93% | 0.1663% | 54.48% | 0% | 41.4% | 0% | 16.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.2% | 0% | CZ 5C | 35.41% | 51.93% | 0.1663% | 50.53% | 0% | 41.4% | 0% | 16.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.82% | 0% | CZ 5C | 0% | 0% | 0% | 82.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 82.88% | 0% | CZ 5C | 35.41% | 51.93% | 0.1663% | 52.06% | 0% | 41.4% | 0% | 16.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 26.96% | 0%
CZ 6A | 36.12% | 51.91% | 0.1663% | 48.26% | 0% | 45.59% | 0% | 22.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.65% | 4.301% | CZ 6A | 36.12% | 51.91% | 0.1663% | 52.18% | 0% | 45.59% | 0% | 22.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 31.56% | 4.301% | CZ 6A | 36.12% | 51.91% | 0.1663% | 43.73% | 0% | 45.59% | 0% | 22.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.61% | 4.301% | CZ 6A | 0% | 0% | 0% | 58.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.33% | 4.301% | CZ 6A | 36.12% | 51.91% | 0.1663% | 48.53% | 0% | 45.59% | 0% | 22.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.73% | 4.301%
CZ 6B | 36.15% | 52.12% | 0.1663% | 47.38% | 0% | 46.01% | 0% | 21.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.7% | 0.5387% | CZ 6B | 36.15% | 52.12% | 0.1663% | 53.16% | 0% | 46.01% | 0% | 21.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.21% | 0.5387% | CZ 6B | 36.15% | 52.12% | 0.1663% | 41.84% | 0% | 46.01% | 0% | 21.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.92% | 0.5387% | CZ 6B | 0% | 0% | 0% | 64.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 64.85% | 0.5387% | CZ 6B | 36.15% | 52.12% | 0.1663% | 47.75% | 0% | 46.01% | 0% | 21.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 28.77% | 0.5387%
CZ 7 | 37.34% | 51.99% | 0.1663% | 52.73% | 0% | 46.3% | 0% | 29.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.24% | 0.5766% | CZ 7 | 37.34% | 51.99% | 0.1663% | 56.67% | 0% | 46.3% | 0% | 29.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 36.2% | 0.5766% | CZ 7 | 37.34% | 51.99% | 0.1663% | 45.42% | 0% | 46.3% | 0% | 29.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.81% | 0.5766% | CZ 7 | 0% | 0% | 0% | 60.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.67% | 0.5766% | CZ 7 | 37.34% | 51.99% | 0.1663% | 53.05% | 0% | 46.3% | 0% | 29.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 32.44% | 0.5766%
CZ 8 | 36.27% | 51.41% | 0.7166% | 40.28% | 0% | 45.51% | 0% | 26.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.78% | 0.08356% | CZ 8 | 36.27% | 51.41% | 0.7166% | 42.74% | 0% | 45.51% | 0% | 26.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 33.26% | 0.08356% | CZ 8 | 36.27% | 51.41% | 0.7166% | 29.75% | 0% | 45.51% | 0% | 26.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 27.16% | 0.08356% | CZ 8 | 0% | 0% | 0% | 44.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.4% | 0.08356% | CZ 8 | 36.27% | 51.41% | 0.7166% | 40.53% | 0% | 45.51% | 0% | 26.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.98% | 0.08356%
Us Weighted | 35.63% | 52.1% | 0.1668% | 43.3% | 0% | 50.18% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.2% | 100% | Us Weighted | 35.63% | 52.1% | 0.1668% | 47.99% | 0% | 50.18% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.66% | 100% | Us Weighted | 35.63% | 52.1% | 0.1668% | 39.37% | 0% | 50.18% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 29.97% | 100% | Us Weighted | 0% | 0% | 0% | 60.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 60.02% | 100% | Us Weighted | 35.63% | 52.1% | 0.1668% | 43.57% | 0% | 50.18% | 0% | 24.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 30.22% | 100%

## Clinic
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Outpatient Healthcare | [14 empty] | Prototype Floor Area: | 40946 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.35314 | 0.077889 | 0.028459 | 0.33999 | 0.076218 | 0.57012 | 0 | 0.26101 | 0.012804 | 0.011024 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.0546 |  | STD2013 | 11.6788 | 2.5759 | 2.8746 | 21.1247 | 2.5206 | 18.8548 | 0 | 8.632 | 0.42346 | 0.36456 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 115.767 |  | STD2013 | 3.4218 | 0.75473 | 0 | 1.8852 | 0.73854 | 5.5244 | 0 | 2.5292 | 0.12407 | 0.10682 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 27.4953 |  | STD2013 | 0 | 0 | 0.028746 | 0.14691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21926 |  | STD2013 | 35.8233 | 7.9013 | 3.1419 | 35.7928 | 7.7318 | 57.8351 | 0 | 26.4778 | 1.2989 | 1.1183 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 311.813
STD2010 | 0.37912 | 0.077889 | 0.028491 | 0.3936 | 0.096822 | 0.58215 | 0 | 0.28416 | 0 | 0.010721 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.1799 |  | STD2010 | 12.538 | 2.5759 | 2.8779 | 23.2133 | 3.202 | 19.2524 | 0 | 9.3975 | 0 | 0.35456 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 120.2299 |  | STD2010 | 3.6736 | 0.75473 | 0 | 2.3597 | 0.93819 | 5.6409 | 0 | 2.7534 | 0 | 0.10389 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 28.6645 |  | STD2010 | 0 | 0 | 0.028779 | 0.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22398 |  | STD2010 | 38.4591 | 7.9013 | 3.1455 | 41.273 | 9.8219 | 59.0546 | 0 | 28.8258 | 0 | 1.0876 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 324.5695
STD2007 | 0.42796 | 0.15887 | 0.028801 | 0.69202 | 0.12365 | 0.78866 | 0 | 0.37295 | 0 | 0.011653 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9455 |  | STD2007 | 14.1533 | 5.254 | 2.9092 | 35.5485 | 4.0892 | 26.0821 | 0 | 12.334 | 0 | 0.38539 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 148.0338 |  | STD2007 | 4.1469 | 1.5394 | 0 | 4.8995 | 1.1981 | 7.642 | 0 | 3.6138 | 0 | 0.11292 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 35.7274 |  | STD2007 | 0 | 0 | 0.029092 | 0.18826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26096 |  | STD2007 | 43.4138 | 16.1161 | 3.1798 | 71.8704 | 12.5432 | 80.0038 | 0 | 37.833 | 0 | 1.1822 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 402.5535
STD2004 | 0.42796 | 0.15887 | 0.028807 | 0.8212 | 0.15282 | 0.82577 | 0 | 0.41363 | 0 | 0.013393 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1833 |  | STD2004 | 14.1533 | 5.254 | 2.9098 | 41.3493 | 5.054 | 27.3092 | 0 | 13.6793 | 0 | 0.44293 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 157.4301 |  | STD2004 | 4.1469 | 1.5394 | 0 | 5.9333 | 1.4808 | 8.0015 | 0 | 4.008 | 0 | 0.12978 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.8145 |  | STD2004 | 0 | 0 | 0.029098 | 0.21099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28369 |  | STD2004 | 43.4138 | 16.1161 | 3.1804 | 85.1771 | 15.5026 | 83.768 | 0 | 41.9597 | 0 | 1.3586 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 426.8876
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 5.8616e-06 | 0.12919 | 0.029174 | 0.037106 | 0 | 0.04068 | 0 | 0.0017396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23789 |  | 2004-2007 | 0 | 0 | 0.00059208 | 5.8009 | 0.96482 | 1.2272 | 0 | 1.3453 | 0 | 0.057532 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3963 |  | 2004-2007 | 0 | 0 | 0 | 1.0338 | 0.28269 | 0.35955 | 0 | 0.39418 | 0 | 0.016857 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0871 |  | 2004-2007 | 0 | 0 | 5.9208e-06 | 0.022725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022731 |  | 2004-2007 | 0 | 0 | 0.00064715 | 13.3067 | 2.9595 | 3.7642 | 0 | 4.1267 | 0 | 0.17647 | 0 | 0 | 0 | 0 | 0 | 0 | 24.3341
2007-2010 | 0.048842 | 0.08098 | 0.0003102 | 0.29842 | 0.026826 | 0.20651 | 0 | 0.088791 | 0 | 0.00093225 | 0 | 0.0076872 | 0 | 0 | 0 | 0.006217 | 0.76551 |  | 2007-2010 | 1.6153 | 2.6781 | 0.031333 | 12.3352 | 0.88716 | 6.8297 | 0 | 2.9364 | 0 | 0.030831 | 0 | 0.25423 | 0 | 0 | 0 | 0.2056 | 27.8039 |  | 2007-2010 | 0.47327 | 0.78468 | 0 | 2.5399 | 0.25993 | 2.0011 | 0 | 0.86037 | 0 | 0.0090334 | 0 | 0.074488 | 0 | 0 | 0 | 0.060241 | 7.063 |  | 2007-2010 | 0 | 0 | 0.00031333 | 0.036667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03698 |  | 2007-2010 | 4.9547 | 8.2148 | 0.034247 | 30.5974 | 2.7213 | 20.9493 | 0 | 9.0072 | 0 | 0.09457 | 0 | 0.77982 | 0 | 0 | 0 | 0.63066 | 77.984
2010-2013 | 0.025982 | 0 | 3.2679e-05 | 0.053612 | 0.020604 | 0.012021 | 0 | 0.023147 | -0.012804 | -0.00030243 | 0 | 0.0012392 | 0 | 0 | 0 | 0.0018063 | 0.12534 |  | 2010-2013 | 0.85927 | 0 | 0.0033009 | 2.0886 | 0.6814 | 0.39756 | 0 | 0.7655 | -0.42346 | -0.010002 | 0 | 0.040982 | 0 | 0 | 0 | 0.059736 | 4.4628 |  | 2010-2013 | 0.25176 | 0 | 0 | 0.47449 | 0.19965 | 0.11648 | 0 | 0.22429 | -0.12407 | -0.0029305 | 0 | 0.012008 | 0 | 0 | 0 | 0.017502 | 1.1692 |  | 2010-2013 | 0 | 0 | 3.3009e-05 | 0.0046913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047243 |  | 2010-2013 | 2.6357 | 0 | 0.0036078 | 5.4802 | 2.0901 | 1.2195 | 0 | 2.3481 | -1.2989 | -0.03068 | 0 | 0.12571 | 0 | 0 | 0 | 0.18323 | 12.7565
2004-2013 | 0.074825 | 0.08098 | 0.00034874 | 0.48121 | 0.076603 | 0.25564 | 0 | 0.15262 | -0.012804 | 0.0023694 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1287 |  | 2004-2013 | 2.4746 | 2.6781 | 0.035226 | 20.2246 | 2.5334 | 8.4544 | 0 | 5.0473 | -0.42346 | 0.078361 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.663 |  | 2004-2013 | 0.72504 | 0.78468 | 0 | 4.0481 | 0.74227 | 2.4771 | 0 | 1.4788 | -0.12407 | 0.022959 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 10.3192 |  | 2004-2013 | 0 | 0 | 0.00035226 | 0.064083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064436 |  | 2004-2013 | 7.5904 | 8.2148 | 0.038502 | 49.3843 | 7.7709 | 25.9329 | 0 | 15.482 | -1.2989 | 0.24036 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 115.0746
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.02035% | 15.73% | 19.09% | 4.494% |  | 9.835% |  | 12.99% |  | 0% |  |  |  | 0% | 5.687% |  | 2004-2007 | 0% | 0% | 0.02035% | 14.03% | 19.09% | 4.494% |  | 9.835% |  | 12.99% |  | 0% |  |  |  | 0% | 5.969% |  | 2004-2007 | 0% | 0% |  | 17.42% | 19.09% | 4.494% |  | 9.835% |  | 12.99% |  | 0% |  |  |  | 0% | 5.519% |  | 2004-2007 |  |  | 0.02035% | 10.77% | [11 empty] | 0% | 8.013% |  | 2004-2007 | 0% | 0% | 0.02035% | 15.62% | 19.09% | 4.494% |  | 9.835% |  | 12.99% |  | 0% |  |  |  | 0% | 5.7%
2007-2010 | 11.41% | 50.97% | 1.077% | 43.12% | 21.7% | 26.19% |  | 23.81% |  | 8% |  | 1.684% |  |  |  | 0.7029% | 19.4% |  | 2007-2010 | 11.41% | 50.97% | 1.077% | 34.7% | 21.7% | 26.19% |  | 23.81% |  | 8% |  | 1.684% |  |  |  | 0.6389% | 18.78% |  | 2007-2010 | 11.41% | 50.97% |  | 51.84% | 21.7% | 26.19% |  | 23.81% |  | 8% |  | 1.684% |  |  |  | 0.739% | 19.77% |  | 2007-2010 |  |  | 1.077% | 19.48% | [11 empty] | 0% | 14.17% |  | 2007-2010 | 11.41% | 50.97% | 1.077% | 42.57% | 21.7% | 26.19% |  | 23.81% |  | 8% |  | 1.684% |  |  |  | 0.6999% | 19.37%
2010-2013 | 6.853% | 0% | 0.1147% | 13.62% | 21.28% | 2.065% |  | 8.146% |  | -2.821% |  | 0.2761% |  |  |  | 0.2057% | 3.942% |  | 2010-2013 | 6.853% | 0% | 0.1147% | 8.997% | 21.28% | 2.065% |  | 8.146% |  | -2.821% |  | 0.2761% |  |  |  | 0.1868% | 3.712% |  | 2010-2013 | 6.853% | 0% |  | 20.11% | 21.28% | 2.065% |  | 8.146% |  | -2.821% |  | 0.2761% |  |  |  | 0.2163% | 4.079% |  | 2010-2013 |  |  | 0.1147% | 3.095% | [11 empty] | 0% | 2.109% |  | 2010-2013 | 6.853% | 0% | 0.1147% | 13.28% | 21.28% | 2.065% |  | 8.146% |  | -2.821% |  | 0.2761% |  |  |  | 0.2048% | 3.93%
2004-2013 | 17.48% | 50.97% | 1.211% | 58.6% | 50.13% | 30.96% |  | 36.9% |  | 17.69% |  | 1.955% |  |  |  | 0.9072% | 26.98% |  | 2004-2013 | 17.48% | 50.97% | 1.211% | 48.91% | 50.13% | 30.96% |  | 36.9% |  | 17.69% |  | 1.955% |  |  |  | 0.8245% | 26.46% |  | 2004-2013 | 17.48% | 50.97% |  | 68.23% | 50.13% | 30.96% |  | 36.9% |  | 17.69% |  | 1.955% |  |  |  | 0.9537% | 27.29% |  | 2004-2013 |  |  | 1.211% | 30.37% | [11 empty] | 0% | 22.71% |  | 2004-2013 | 17.48% | 50.97% | 1.211% | 57.98% | 50.13% | 30.96% |  | 36.9% |  | 17.69% |  | 1.955% |  |  |  | 0.9033% | 26.96%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.35339 | 0.077852 | 0.022176 | 0.23271 | 0.0012182 | 1.1588 | 0 | 0.26581 | 0.02115 | 0.0074772 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.4646 | 0.8522% | CZ 1A | 11.6872 | 2.5747 | 2.24 | 14.7671 | 0.040287 | 38.3241 | 0 | 8.7907 | 0.69947 | 0.24728 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 126.0885 | 0.8522% | CZ 1A | 3.4243 | 0.75437 | 0 | 1.2464 | 0.011804 | 11.2288 | 0 | 2.5757 | 0.20494 | 0.072452 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 31.9294 | 0.8522% | CZ 1A | 0 | 0 | 0.0224 | 0.10513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17114 | 0.8522% | CZ 1A | 35.8493 | 7.8975 | 2.4484 | 24.5395 | 0.12358 | 117.5548 | 0 | 26.9646 | 2.1455 | 0.75851 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 352.9736 | 0.8522%
CZ 1B | 0.35358 | 0.077838 | 0.021136 | 0.23562 | 0.088858 | 0.93687 | 0 | 0.28975 | 0 | 0.0074352 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.335 | 0% | CZ 1B | 11.6935 | 2.5742 | 2.1349 | 13.3581 | 2.9387 | 30.9837 | 0 | 9.5823 | 0 | 0.24589 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 120.2289 | 0% | CZ 1B | 3.4262 | 0.75424 | 0 | 1.4893 | 0.86102 | 9.0781 | 0 | 2.8076 | 0 | 0.072045 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 30.8991 | 0% | CZ 1B | 0 | 0 | 0.021349 | 0.082749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1477 | 0% | CZ 1B | 35.8685 | 7.8961 | 2.3335 | 24.6365 | 9.014 | 95.039 | 0 | 29.3928 | 0 | 0.75424 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 339.6265 | 0%
CZ 2A | 0.35395 | 0.077817 | 0.024631 | 0.31654 | 0.015451 | 0.90949 | 0 | 0.25135 | 0.016733 | 0.0086113 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.2985 | 12.98% | CZ 2A | 11.7055 | 2.5735 | 2.4879 | 18.3012 | 0.511 | 30.0781 | 0 | 8.3124 | 0.55337 | 0.28479 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 121.5255 | 12.98% | CZ 2A | 3.4297 | 0.75404 | 0 | 1.9501 | 0.14972 | 8.8128 | 0 | 2.4355 | 0.16214 | 0.083442 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 30.188 | 12.98% | CZ 2A | 0 | 0 | 0.024879 | 0.11646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18494 | 12.98% | CZ 2A | 35.9054 | 7.894 | 2.7193 | 33.1443 | 1.5674 | 92.2614 | 0 | 25.4973 | 1.6974 | 0.87356 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 336.2519 | 12.98%
CZ 2B | 0.354 | 0.077789 | 0.023191 | 0.21971 | 0.049729 | 0.85028 | 0 | 0.26917 | 0 | 0.0085273 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.1763 | 3.07% | CZ 2B | 11.7072 | 2.5726 | 2.3426 | 14.0266 | 1.6446 | 28.12 | 0 | 8.9019 | 0 | 0.28201 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 116.3149 | 3.07% | CZ 2B | 3.4302 | 0.75376 | 0 | 1.1647 | 0.48186 | 8.2391 | 0 | 2.6082 | 0 | 0.082628 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 29.171 | 3.07% | CZ 2B | 0 | 0 | 0.023426 | 0.10051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16754 | 3.07% | CZ 2B | 35.9104 | 7.8912 | 2.5604 | 23.1797 | 5.0446 | 86.2551 | 0 | 27.3055 | 0 | 0.86504 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 323.7038 | 3.07%
CZ 3A | 0.35423 | 0.077831 | 0.026567 | 0.39362 | 0.046767 | 0.72085 | 0 | 0.25755 | 0.015696 | 0.0098785 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.2269 | 13.3% | CZ 3A | 11.7148 | 2.574 | 2.6835 | 21.6126 | 1.5467 | 23.8396 | 0 | 8.5175 | 0.5191 | 0.3267 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 120.0521 | 13.3% | CZ 3A | 3.4324 | 0.75417 | 0 | 2.5883 | 0.45317 | 6.9849 | 0 | 2.4956 | 0.1521 | 0.095721 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 29.3669 | 13.3% | CZ 3A | 0 | 0 | 0.026835 | 0.12779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19823 | 13.3% | CZ 3A | 35.9338 | 7.8954 | 2.9331 | 41.0639 | 4.7442 | 73.1254 | 0 | 26.1265 | 1.5923 | 1.0021 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 329.1087 | 13.3%
CZ 3B | 0.35395 | 0.077789 | 0.025912 | 0.22383 | 0.094984 | 0.57706 | 0 | 0.26861 | 0 | 0.0080443 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.9541 | 6.287% | CZ 3B | 11.7055 | 2.5726 | 2.6173 | 13.217 | 3.1412 | 19.0841 | 0 | 8.8833 | 0 | 0.26603 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 108.2048 | 6.287% | CZ 3B | 3.4297 | 0.75376 | 0 | 1.3395 | 0.92038 | 5.5916 | 0 | 2.6028 | 0 | 0.077947 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 27.1262 | 6.287% | CZ 3B | 0 | 0 | 0.026173 | 0.086453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15623 | 6.287% | CZ 3B | 35.9054 | 7.8912 | 2.8608 | 23.4724 | 9.6354 | 58.5384 | 0 | 27.2487 | 0 | 0.81603 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 301.0602 | 6.287%
CZ 3C | 0.35419 | 0.077803 | 0.028643 | 0.22504 | 0.0035706 | 0.35714 | 0 | 0.24873 | 0 | 0.0084293 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.6275 | 1.4% | CZ 3C | 11.7134 | 2.5731 | 2.8933 | 15.8007 | 0.11808 | 11.8111 | 0 | 8.2258 | 0 | 0.27877 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 100.1317 | 1.4% | CZ 3C | 3.432 | 0.7539 | 0 | 0.98842 | 0.034598 | 3.4606 | 0 | 2.4101 | 0 | 0.081679 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 23.5719 | 1.4% | CZ 3C | 0 | 0 | 0.028933 | 0.12427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19681 | 1.4% | CZ 3C | 35.9296 | 7.8926 | 3.1623 | 23.9307 | 0.36221 | 36.2293 | 0 | 25.2317 | 0 | 0.85509 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 268.2853 | 1.4%
CZ 4A | 0.35245 | 0.077817 | 0.028921 | 0.3162 | 0.088809 | 0.54581 | 0 | 0.26566 | 0.01578 | 0.010684 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.0261 | 18.71% | CZ 4A | 11.656 | 2.5735 | 2.9213 | 20.1232 | 2.937 | 18.0508 | 0 | 8.7859 | 0.52188 | 0.35332 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 114.6405 | 18.71% | CZ 4A | 3.4152 | 0.75404 | 0 | 1.6853 | 0.86054 | 5.2888 | 0 | 2.5742 | 0.15291 | 0.10352 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 27.2451 | 18.71% | CZ 4A | 0 | 0 | 0.029213 | 0.14371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21653 | 18.71% | CZ 4A | 35.7534 | 7.894 | 3.193 | 33.351 | 9.009 | 55.3687 | 0 | 26.9497 | 1.6008 | 1.0838 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 308.8953 | 18.71%
CZ 4B | 0.35234 | 0.077761 | 0.028563 | 0.24955 | 0.13412 | 0.44034 | 0 | 0.28291 | 0 | 0.0083733 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.8979 | 0.5317% | CZ 4B | 11.6523 | 2.5717 | 2.8852 | 14.2847 | 4.4355 | 14.5627 | 0 | 9.3564 | 0 | 0.27692 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 106.7429 | 0.5317% | CZ 4B | 3.4141 | 0.75349 | 0 | 1.5578 | 1.2996 | 4.2668 | 0 | 2.7414 | 0 | 0.081136 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 26.5249 | 0.5317% | CZ 4B | 0 | 0 | 0.028852 | 0.08968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16214 | 0.5317% | CZ 4B | 35.7421 | 7.8883 | 3.1535 | 26.1106 | 13.6055 | 44.6694 | 0 | 28.6996 | 0 | 0.84941 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 295.4103 | 0.5317%
CZ 4C | 0.35298 | 0.077873 | 0.029922 | 0.27936 | 0.018357 | 0.3412 | 0 | 0.25406 | 0 | 0.010019 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.6877 | 4.138% | CZ 4C | 11.6736 | 2.5754 | 3.0224 | 19.3062 | 0.60709 | 11.2839 | 0 | 8.402 | 0 | 0.33133 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 103.9195 | 4.138% | CZ 4C | 3.4203 | 0.75458 | 0 | 1.271 | 0.17787 | 3.3062 | 0 | 2.4618 | 0 | 0.097078 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 23.8994 | 4.138% | CZ 4C | 0 | 0 | 0.030224 | 0.14968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22351 | 4.138% | CZ 4C | 35.8074 | 7.8997 | 3.3035 | 29.6667 | 1.8622 | 34.6121 | 0 | 25.7721 | 0 | 1.0163 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 274.6319 | 4.138%
CZ 5A | 0.3525 | 0.078055 | 0.030591 | 0.38403 | 0.10215 | 0.45633 | 0 | 0.25998 | 0.016502 | 0.013372 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.0175 | 24.21% | CZ 5A | 11.6578 | 2.5814 | 3.09 | 24.8461 | 3.3781 | 15.0915 | 0 | 8.5979 | 0.54573 | 0.44223 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 116.9484 | 24.21% | CZ 5A | 3.4157 | 0.75634 | 0 | 1.9889 | 0.98978 | 4.4218 | 0 | 2.5191 | 0.1599 | 0.12957 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 26.7917 | 24.21% | CZ 5A | 0 | 0 | 0.0309 | 0.18058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25508 | 24.21% | CZ 5A | 35.7591 | 7.9181 | 3.3774 | 40.5593 | 10.362 | 46.2915 | 0 | 26.373 | 1.674 | 1.3565 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 308.3628 | 24.21%
CZ 5B | 0.35302 | 0.077628 | 0.030273 | 0.31496 | 0.086232 | 0.33707 | 0 | 0.27129 | 0 | 0.011433 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.8059 | 4.982% | CZ 5B | 11.6747 | 2.5673 | 3.0578 | 19.9725 | 2.8518 | 11.1475 | 0 | 8.972 | 0 | 0.3781 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 107.3394 | 4.982% | CZ 5B | 3.4207 | 0.7522 | 0 | 1.6889 | 0.83558 | 3.2662 | 0 | 2.6288 | 0 | 0.11078 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 25.1137 | 4.982% | CZ 5B | 0 | 0 | 0.030578 | 0.14208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21626 | 4.982% | CZ 5B | 35.811 | 7.8748 | 3.3422 | 33.211 | 8.7477 | 34.1938 | 0 | 27.5207 | 0 | 1.1598 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 286.5528 | 4.982%
CZ 5C | 0.35442 | 0.077943 | 0.030596 | 0.2916 | 0.025533 | 0.26168 | 0 | 0.26619 | 0 | 0.010432 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.6423 | 0% | CZ 5C | 11.7213 | 2.5777 | 3.0905 | 20.2118 | 0.84441 | 8.6541 | 0 | 8.8032 | 0 | 0.34499 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 102.9656 | 0% | CZ 5C | 3.4343 | 0.75526 | 0 | 1.3183 | 0.24741 | 2.5356 | 0 | 2.5793 | 0 | 0.10108 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 23.3819 | 0% | CZ 5C | 0 | 0 | 0.030905 | 0.15712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23163 | 0% | CZ 5C | 35.9537 | 7.9068 | 3.3779 | 30.9752 | 2.5901 | 26.5455 | 0 | 27.0029 | 0 | 1.0582 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 270.1022 | 0%
CZ 6A | 0.35276 | 0.07809 | 0.032046 | 0.41544 | 0.13625 | 0.36102 | 0 | 0.26016 | 0.016145 | 0.014352 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.9902 | 7.834% | CZ 6A | 11.6664 | 2.5826 | 3.237 | 27.1485 | 4.5059 | 11.9394 | 0 | 8.6039 | 0.53392 | 0.47465 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 117.4098 | 7.834% | CZ 6A | 3.4182 | 0.75668 | 0 | 2.113 | 1.3202 | 3.4982 | 0 | 2.5209 | 0.15644 | 0.13907 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 26.3333 | 7.834% | CZ 6A | 0 | 0 | 0.03237 | 0.19937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27534 | 7.834% | CZ 6A | 35.7854 | 7.9217 | 3.5381 | 43.912 | 13.8214 | 36.6227 | 0 | 26.3914 | 1.6377 | 1.4559 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 305.7782 | 7.834%
CZ 6B | 0.35288 | 0.077761 | 0.03226 | 0.38054 | 0.13554 | 0.26041 | 0 | 0.27689 | 0 | 0.013463 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 2.8537 | 0.7615% | CZ 6B | 11.6703 | 2.5717 | 3.2585 | 24.3605 | 4.4825 | 8.6122 | 0 | 9.1572 | 0 | 0.44524 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 111.2759 | 0.7615% | CZ 6B | 3.4194 | 0.75349 | 0 | 2.0078 | 1.3134 | 2.5234 | 0 | 2.683 | 0 | 0.13046 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 25.2415 | 0.7615% | CZ 6B | 0 | 0 | 0.032585 | 0.17508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25127 | 0.7615% | CZ 6B | 35.7975 | 7.8883 | 3.5616 | 40.1561 | 13.7497 | 26.417 | 0 | 28.0888 | 0 | 1.3657 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 291.7166 | 0.7615%
CZ 7 | 0.35156 | 0.077922 | 0.03437 | 0.45908 | 0.16633 | 0.30288 | 0 | 0.27182 | 0.016166 | 0.015766 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.0198 | 0.8914% | CZ 7 | 11.6266 | 2.577 | 3.4717 | 31.2921 | 5.5008 | 10.0167 | 0 | 8.9896 | 0.53462 | 0.52142 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 121.2481 | 0.8914% | CZ 7 | 3.4066 | 0.75505 | 0 | 2.1507 | 1.6117 | 2.9349 | 0 | 2.6339 | 0.15664 | 0.15277 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 26.2128 | 0.8914% | CZ 7 | 0 | 0 | 0.034717 | 0.23952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.31784 | 0.8914% | CZ 7 | 35.6632 | 7.9046 | 3.7946 | 48.695 | 16.8732 | 30.7251 | 0 | 27.5746 | 1.6399 | 1.5994 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 309.1616 | 0.8914%
CZ 8 | 0.35402 | 0.078307 | 0.037219 | 0.71128 | 0.26828 | 0.20891 | 0 | 0.2745 | 0.015829 | 0.020576 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.2929 | 0.0471% | CZ 8 | 11.7081 | 2.5897 | 3.7595 | 49.9707 | 8.8725 | 6.9088 | 0 | 9.0781 | 0.5235 | 0.68048 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 140.8089 | 0.0471% | CZ 8 | 3.4304 | 0.75878 | 0 | 3.1201 | 2.5996 | 2.0243 | 0 | 2.6598 | 0.15338 | 0.19938 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 27.3563 | 0.0471% | CZ 8 | 0 | 0 | 0.037595 | 0.39322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.47442 | 0.0471% | CZ 8 | 35.9132 | 7.9437 | 4.1091 | 75.6429 | 27.2153 | 21.192 | 0 | 27.8459 | 1.6058 | 2.0873 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 338.2471 | 0.0471%
Us Weighted | 0.35314 | 0.077889 | 0.028459 | 0.33999 | 0.076218 | 0.57012 | 0 | 0.26101 | 0.012804 | 0.011024 | 0 | 0.44756 | 0 | 0 | 0 | 0.87639 | 3.0546 | 100% | Us Weighted | 11.6788 | 2.5759 | 2.8746 | 21.1247 | 2.5206 | 18.8548 | 0 | 8.632 | 0.42346 | 0.36456 | 0 | 14.8015 | 0 | 0 | 0 | 31.916 | 115.767 | 100% | Us Weighted | 3.4218 | 0.75473 | 0 | 1.8852 | 0.73854 | 5.5244 | 0 | 2.5292 | 0.12407 | 0.10682 | 0 | 4.3368 | 0 | 0 | 0 | 8.0737 | 27.4953 | 100% | Us Weighted | 0 | 0 | 0.028746 | 0.14691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21926 | 100% | Us Weighted | 35.8233 | 7.9013 | 3.1419 | 35.7928 | 7.7318 | 57.8351 | 0 | 26.4778 | 1.2989 | 1.1183 | 0 | 45.4021 | 0 | 0 | 0 | 89.2898 | 311.813 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.37938 | 0.077852 | 0.022229 | 0.23762 | 0.0011342 | 1.2449 | 0 | 0.29917 | 0 | 0.006609 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.5959 | 0.8522% | CZ 1A | 12.5465 | 2.5747 | 2.2454 | 15.2002 | 0.037509 | 41.1694 | 0 | 9.894 | 0 | 0.21857 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 130.7045 | 0.8522% | CZ 1A | 3.6761 | 0.75437 | 0 | 1.2554 | 0.01099 | 12.0625 | 0 | 2.8989 | 0 | 0.06404 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 33.1624 | 0.8522% | CZ 1A | 0 | 0 | 0.022454 | 0.10915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17521 | 0.8522% | CZ 1A | 38.4849 | 7.8975 | 2.4542 | 25.0737 | 0.11505 | 126.2826 | 0 | 30.3487 | 0 | 0.67044 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 366.328 | 0.8522%
CZ 1B | 0.37947 | 0.077838 | 0.021138 | 0.35344 | 0.1861 | 1.026 | 0 | 0.33551 | 0 | 0.0059089 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.7123 | 0% | CZ 1B | 12.5495 | 2.5742 | 2.1352 | 16.0455 | 6.1545 | 33.93 | 0 | 11.0957 | 0 | 0.19542 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 131.4981 | 0% | CZ 1B | 3.677 | 0.75424 | 0 | 2.8034 | 1.8032 | 9.9414 | 0 | 3.251 | 0 | 0.057256 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 34.7275 | 0% | CZ 1B | 0 | 0 | 0.021352 | 0.064775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.12973 | 0% | CZ 1B | 38.4941 | 7.8961 | 2.3337 | 36.4287 | 18.8781 | 104.0764 | 0 | 34.0347 | 0 | 0.59942 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 377.7421 | 0%
CZ 2A | 0.37949 | 0.077817 | 0.024683 | 0.35004 | 0.015451 | 0.96682 | 0 | 0.28312 | 0 | 0.0076732 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.4321 | 12.98% | CZ 2A | 12.5502 | 2.5735 | 2.4933 | 19.8445 | 0.511 | 31.974 | 0 | 9.3631 | 0 | 0.25376 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 126.3816 | 12.98% | CZ 2A | 3.6772 | 0.75404 | 0 | 2.2125 | 0.14972 | 9.3683 | 0 | 2.7434 | 0 | 0.074352 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 31.4195 | 12.98% | CZ 2A | 0 | 0 | 0.024933 | 0.12293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19147 | 12.98% | CZ 2A | 38.4963 | 7.894 | 2.7251 | 36.5993 | 1.5674 | 98.0766 | 0 | 28.7202 | 0 | 0.77839 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 349.8581 | 12.98%
CZ 2B | 0.37953 | 0.077789 | 0.023203 | 0.26859 | 0.071152 | 0.90997 | 0 | 0.30647 | 0 | 0.0073932 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.3711 | 3.07% | CZ 2B | 12.5516 | 2.5726 | 2.3437 | 15.4408 | 2.3531 | 30.0939 | 0 | 10.1353 | 0 | 0.2445 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 122.5538 | 3.07% | CZ 2B | 3.6776 | 0.75376 | 0 | 1.6673 | 0.68945 | 8.8174 | 0 | 2.9696 | 0 | 0.071638 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 31.0868 | 3.07% | CZ 2B | 0 | 0 | 0.023437 | 0.097504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16455 | 3.07% | CZ 2B | 38.5005 | 7.8912 | 2.5617 | 28.112 | 7.2179 | 92.3096 | 0 | 31.0888 | 0 | 0.74998 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 343.4325 | 3.07%
CZ 3A | 0.37919 | 0.077831 | 0.026599 | 0.41845 | 0.049883 | 0.73418 | 0 | 0.27463 | 0 | 0.0097945 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.2975 | 13.3% | CZ 3A | 12.5402 | 2.574 | 2.6868 | 22.5589 | 1.6497 | 24.2802 | 0 | 9.0825 | 0 | 0.32392 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 122.5145 | 13.3% | CZ 3A | 3.6743 | 0.75417 | 0 | 2.8111 | 0.48336 | 7.114 | 0 | 2.6611 | 0 | 0.094907 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 30.033 | 13.3% | CZ 3A | 0 | 0 | 0.026868 | 0.12965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20012 | 13.3% | CZ 3A | 38.4657 | 7.8954 | 2.9367 | 43.5994 | 5.0603 | 74.477 | 0 | 27.8594 | 0 | 0.99358 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 336.2883 | 13.3%
CZ 3B | 0.37917 | 0.077789 | 0.025914 | 0.28686 | 0.19279 | 0.60836 | 0 | 0.3038 | 0 | 0.0078972 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.2096 | 6.287% | CZ 3B | 12.5395 | 2.5726 | 2.6176 | 14.2516 | 6.3758 | 20.1193 | 0 | 10.047 | 0 | 0.26117 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 115.6029 | 6.287% | CZ 3B | 3.674 | 0.75376 | 0 | 2.1 | 1.8681 | 5.8949 | 0 | 2.9438 | 0 | 0.076523 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 29.7512 | 6.287% | CZ 3B | 0 | 0 | 0.026176 | 0.070842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.14062 | 6.287% | CZ 3B | 38.4636 | 7.8912 | 2.861 | 29.7283 | 19.5571 | 61.7138 | 0 | 30.8182 | 0 | 0.80112 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 326.835 | 6.287%
CZ 3C | 0.37919 | 0.077803 | 0.028689 | 0.22962 | 0.0039136 | 0.37086 | 0 | 0.28327 | 0 | 0.0082193 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 2.7086 | 1.4% | CZ 3C | 12.5404 | 2.5731 | 2.8979 | 16.2431 | 0.12943 | 12.2649 | 0 | 9.3682 | 0 | 0.27182 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 103.1071 | 1.4% | CZ 3C | 3.6743 | 0.7539 | 0 | 0.99141 | 0.037922 | 3.5936 | 0 | 2.7449 | 0 | 0.079643 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 24.3157 | 1.4% | CZ 3C | 0 | 0 | 0.028979 | 0.12859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20118 | 1.4% | CZ 3C | 38.4664 | 7.8926 | 3.1674 | 24.4343 | 0.39701 | 37.6213 | 0 | 28.7358 | 0 | 0.83379 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 276.5495 | 1.4%
CZ 4A | 0.37898 | 0.077817 | 0.028964 | 0.36643 | 0.094326 | 0.54004 | 0 | 0.28179 | 0 | 0.010565 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.1059 | 18.71% | CZ 4A | 12.5335 | 2.5735 | 2.9257 | 22.2557 | 3.1195 | 17.8598 | 0 | 9.3193 | 0 | 0.34939 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 117.7547 | 18.71% | CZ 4A | 3.6723 | 0.75404 | 0 | 2.1049 | 0.914 | 5.2329 | 0 | 2.7305 | 0 | 0.10237 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 27.951 | 18.71% | CZ 4A | 0 | 0 | 0.029257 | 0.15072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22358 | 18.71% | CZ 4A | 38.4451 | 7.894 | 3.1978 | 38.5093 | 9.5687 | 54.7828 | 0 | 28.586 | 0 | 1.0717 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 317.0562 | 18.71%
CZ 4B | 0.37897 | 0.077761 | 0.028602 | 0.33107 | 0.3031 | 0.47821 | 0 | 0.32971 | 0 | 0.0078622 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.2623 | 0.5317% | CZ 4B | 12.533 | 2.5717 | 2.8891 | 15.6446 | 10.0239 | 15.8151 | 0 | 10.904 | 0 | 0.26001 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 117.4596 | 0.5317% | CZ 4B | 3.6721 | 0.75349 | 0 | 2.5383 | 2.937 | 4.6338 | 0 | 3.1948 | 0 | 0.076184 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 30.2458 | 0.5317% | CZ 4B | 0 | 0 | 0.028891 | 0.069812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.14231 | 0.5317% | CZ 4B | 38.4437 | 7.8883 | 3.1578 | 34.2044 | 30.7472 | 48.5109 | 0 | 33.4467 | 0 | 0.79757 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 332.1974 | 0.5317%
CZ 4C | 0.37905 | 0.077873 | 0.029959 | 0.29718 | 0.020632 | 0.35374 | 0 | 0.27878 | 0 | 0.0096755 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 2.7739 | 4.138% | CZ 4C | 12.5356 | 2.5754 | 3.0261 | 20.1519 | 0.68234 | 11.6986 | 0 | 9.2195 | 0 | 0.31998 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 107.0278 | 4.138% | CZ 4C | 3.6729 | 0.75458 | 0 | 1.4071 | 0.19992 | 3.4277 | 0 | 2.7013 | 0 | 0.093754 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 24.6973 | 4.138% | CZ 4C | 0 | 0 | 0.030261 | 0.15349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22736 | 4.138% | CZ 4C | 38.4515 | 7.8997 | 3.3076 | 31.5081 | 2.093 | 35.8841 | 0 | 28.2799 | 0 | 0.98151 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 283.4062 | 4.138%
CZ 5A | 0.37898 | 0.078055 | 0.03061 | 0.44635 | 0.11251 | 0.44753 | 0 | 0.2791 | 0 | 0.013141 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.1133 | 24.21% | CZ 5A | 12.5335 | 2.5814 | 3.0919 | 27.5729 | 3.7208 | 14.8005 | 0 | 9.2302 | 0 | 0.43459 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 120.784 | 24.21% | CZ 5A | 3.6723 | 0.75634 | 0 | 2.4978 | 1.0902 | 4.3365 | 0 | 2.7044 | 0 | 0.12733 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 27.6249 | 24.21% | CZ 5A | 0 | 0 | 0.030919 | 0.19048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.265 | 24.21% | CZ 5A | 38.4451 | 7.9181 | 3.3794 | 46.9687 | 11.4131 | 45.3988 | 0 | 28.3126 | 0 | 1.3331 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 318.1697 | 24.21%
CZ 5B | 0.37907 | 0.077628 | 0.030314 | 0.40807 | 0.18164 | 0.36485 | 0 | 0.29812 | 0 | 0.011377 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.0781 | 4.982% | CZ 5B | 12.5365 | 2.5673 | 3.062 | 21.1774 | 6.007 | 12.066 | 0 | 9.8593 | 0 | 0.37625 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 114.47 | 4.982% | CZ 5B | 3.6732 | 0.7522 | 0 | 2.8584 | 1.76 | 3.5353 | 0 | 2.8887 | 0 | 0.11024 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 28.0182 | 4.982% | CZ 5B | 0 | 0 | 0.03062 | 0.11422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18844 | 4.982% | CZ 5B | 38.4544 | 7.8748 | 3.3468 | 42.4086 | 18.4257 | 37.0112 | 0 | 30.2422 | 0 | 1.1541 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 313.9186 | 4.982%
CZ 5C | 0.37928 | 0.077943 | 0.030635 | 0.32033 | 0.027437 | 0.27131 | 0 | 0.28526 | 0 | 0.0096825 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 2.7289 | 0% | CZ 5C | 12.5432 | 2.5777 | 3.0944 | 21.3502 | 0.90739 | 8.9725 | 0 | 9.4339 | 0 | 0.32021 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 106.0179 | 0% | CZ 5C | 3.6751 | 0.75526 | 0 | 1.5697 | 0.26586 | 2.6289 | 0 | 2.7641 | 0 | 0.093822 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 24.1929 | 0% | CZ 5C | 0 | 0 | 0.030944 | 0.15993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23448 | 0% | CZ 5C | 38.475 | 7.9068 | 3.3822 | 33.9136 | 2.7833 | 27.5221 | 0 | 28.9375 | 0 | 0.98222 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 278.9035 | 0%
CZ 6A | 0.37901 | 0.07809 | 0.032085 | 0.51395 | 0.16613 | 0.35103 | 0 | 0.285 | 0 | 0.014114 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.1464 | 7.834% | CZ 6A | 12.5344 | 2.5826 | 3.2409 | 32.125 | 5.4941 | 11.6092 | 0 | 9.4254 | 0 | 0.46678 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 124.2967 | 7.834% | CZ 6A | 3.6726 | 0.75668 | 0 | 2.8224 | 1.6098 | 3.4015 | 0 | 2.7616 | 0 | 0.13676 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 27.6013 | 7.834% | CZ 6A | 0 | 0 | 0.032409 | 0.22492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.30094 | 7.834% | CZ 6A | 38.448 | 7.9217 | 3.5424 | 54.1316 | 16.8526 | 35.61 | 0 | 28.9113 | 0 | 1.4318 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 321.85 | 7.834%
CZ 6B | 0.37905 | 0.077761 | 0.032296 | 0.49992 | 0.30005 | 0.29385 | 0 | 0.30997 | 0 | 0.013358 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.2332 | 0.7615% | CZ 6B | 12.5358 | 2.5717 | 3.2622 | 27.1482 | 9.9232 | 9.718 | 0 | 10.251 | 0 | 0.44177 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 122.6702 | 0.7615% | CZ 6B | 3.673 | 0.75349 | 0 | 3.3301 | 2.9075 | 2.8474 | 0 | 3.0035 | 0 | 0.12944 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 29.0844 | 0.7615% | CZ 6B | 0 | 0 | 0.032622 | 0.15783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23405 | 0.7615% | CZ 6B | 38.4522 | 7.8883 | 3.5656 | 52.1131 | 30.4382 | 29.809 | 0 | 31.4439 | 0 | 1.3551 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 330.0662 | 0.7615%
CZ 7 | 0.37902 | 0.077922 | 0.0344 | 0.61238 | 0.21983 | 0.27273 | 0 | 0.29027 | 0 | 0.016039 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.2296 | 0.8914% | CZ 7 | 12.5347 | 2.577 | 3.4747 | 38.8168 | 7.27 | 9.0197 | 0 | 9.5995 | 0 | 0.53045 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 130.6411 | 0.8914% | CZ 7 | 3.6726 | 0.75505 | 0 | 3.286 | 2.1301 | 2.6428 | 0 | 2.8126 | 0 | 0.15542 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 27.8946 | 0.8914% | CZ 7 | 0 | 0 | 0.034747 | 0.27602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.35437 | 0.8914% | CZ 7 | 38.4487 | 7.9046 | 3.7979 | 64.5698 | 22.2999 | 27.667 | 0 | 29.4453 | 0 | 1.6271 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 330.7611 | 0.8914%
CZ 8 | 0.37938 | 0.078307 | 0.037262 | 0.92544 | 0.31292 | 0.17882 | 0 | 0.28908 | 0 | 0.020282 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.5485 | 0.0471% | CZ 8 | 12.5467 | 2.5897 | 3.7639 | 59.158 | 10.3487 | 5.9139 | 0 | 9.5601 | 0 | 0.67076 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 151.3701 | 0.0471% | CZ 8 | 3.6761 | 0.75878 | 0 | 4.895 | 3.0322 | 1.7328 | 0 | 2.8011 | 0 | 0.19653 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 29.5325 | 0.0471% | CZ 8 | 0 | 0 | 0.037639 | 0.42451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.50576 | 0.0471% | CZ 8 | 38.4856 | 7.9437 | 4.1139 | 97.6453 | 31.7436 | 18.1402 | 0 | 29.3246 | 0 | 2.0575 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 364.4552 | 0.0471%
Us Weighted | 0.37912 | 0.077889 | 0.028491 | 0.3936 | 0.096822 | 0.58215 | 0 | 0.28416 | 0 | 0.010721 | 0 | 0.4488 | 0 | 0 | 0 | 0.87819 | 3.1799 | 100% | Us Weighted | 12.538 | 2.5759 | 2.8779 | 23.2133 | 3.202 | 19.2524 | 0 | 9.3975 | 0 | 0.35456 | 0 | 14.8425 | 0 | 0 | 0 | 31.9758 | 120.2299 | 100% | Us Weighted | 3.6736 | 0.75473 | 0 | 2.3597 | 0.93819 | 5.6409 | 0 | 2.7534 | 0 | 0.10389 | 0 | 4.3488 | 0 | 0 | 0 | 8.0912 | 28.6645 | 100% | Us Weighted | 0 | 0 | 0.028779 | 0.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22398 | 100% | Us Weighted | 38.4591 | 7.9013 | 3.1455 | 41.273 | 9.8219 | 59.0546 | 0 | 28.8258 | 0 | 1.0876 | 0 | 45.5278 | 0 | 0 | 0 | 89.473 | 324.5695 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.42796 | 0.15909 | 0.022527 | 0.39584 | 0.0016243 | 1.4752 | 0 | 0.39484 | 0 | 0.0073651 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2254 | 0.8522% | CZ 1A | 14.1533 | 5.2614 | 2.2754 | 24.432 | 0.053716 | 48.7881 | 0 | 13.0579 | 0 | 0.24358 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 155.5436 | 0.8522% | CZ 1A | 4.1469 | 1.5416 | 0 | 2.2181 | 0.015739 | 14.2948 | 0 | 3.8259 | 0 | 0.071367 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.6892 | 0.8522% | CZ 1A | 0 | 0 | 0.022754 | 0.16861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.23497 | 0.8522% | CZ 1A | 43.4138 | 16.1388 | 2.4871 | 41.6513 | 0.16477 | 149.6521 | 0 | 40.0538 | 0 | 0.74714 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 430.72 | 0.8522%
CZ 1B | 0.42796 | 0.15907 | 0.021489 | 0.63451 | 0.22038 | 1.2536 | 0 | 0.43912 | 0 | 0.006672 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.5037 | 0% | CZ 1B | 14.1533 | 5.2607 | 2.1706 | 27.6428 | 7.2883 | 41.457 | 0 | 14.5222 | 0 | 0.22065 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 159.9936 | 0% | CZ 1B | 4.1469 | 1.5414 | 0 | 5.1987 | 2.1354 | 12.1468 | 0 | 4.255 | 0 | 0.064651 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 42.0636 | 0% | CZ 1B | 0 | 0 | 0.021706 | 0.098997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16431 | 0% | CZ 1B | 43.4138 | 16.1367 | 2.3725 | 65.2452 | 22.356 | 127.1647 | 0 | 44.5451 | 0 | 0.67683 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 458.3221 | 0%
CZ 2A | 0.42796 | 0.15903 | 0.024977 | 0.53676 | 0.025386 | 1.2356 | 0 | 0.3823 | 0 | 0.0086954 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1416 | 12.98% | CZ 2A | 14.1533 | 5.2593 | 2.5229 | 29.8566 | 0.83955 | 40.8622 | 0 | 12.6433 | 0 | 0.28757 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 153.7028 | 12.98% | CZ 2A | 4.1469 | 1.541 | 0 | 3.4746 | 0.24599 | 11.9725 | 0 | 3.7044 | 0 | 0.084257 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.7444 | 12.98% | CZ 2A | 0 | 0 | 0.025229 | 0.17998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24881 | 12.98% | CZ 2A | 43.4138 | 16.1324 | 2.7575 | 56.0472 | 2.5752 | 125.3401 | 0 | 38.7818 | 0 | 0.88208 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 422.3414 | 12.98%
CZ 2B | 0.42796 | 0.15899 | 0.023535 | 0.56008 | 0.0924 | 1.15 | 0 | 0.40879 | 0 | 0.0079322 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1705 | 3.07% | CZ 2B | 14.1533 | 5.2579 | 2.3773 | 28.4735 | 3.0558 | 38.0307 | 0 | 13.5194 | 0 | 0.26233 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 152.4084 | 3.07% | CZ 2B | 4.1469 | 1.5406 | 0 | 4.0078 | 0.89534 | 11.1429 | 0 | 3.9611 | 0 | 0.076862 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.3463 | 3.07% | CZ 2B | 0 | 0 | 0.023773 | 0.14795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21532 | 3.07% | CZ 2B | 43.4138 | 16.1282 | 2.5984 | 58.1285 | 9.3734 | 116.655 | 0 | 41.4692 | 0 | 0.80467 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 424.9824 | 3.07%
CZ 3A | 0.42796 | 0.15892 | 0.026895 | 0.59933 | 0.06782 | 0.99429 | 0 | 0.36951 | 0 | 0.010761 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9964 | 13.3% | CZ 3A | 14.1533 | 5.2556 | 2.7166 | 31.5152 | 2.2429 | 32.8827 | 0 | 12.2202 | 0 | 0.35587 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 148.6207 | 13.3% | CZ 3A | 4.1469 | 1.5399 | 0 | 4.1395 | 0.65716 | 9.6346 | 0 | 3.5805 | 0 | 0.10427 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.3775 | 13.3% | CZ 3A | 0 | 0 | 0.027166 | 0.17387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24464 | 13.3% | CZ 3A | 43.4138 | 16.1211 | 2.9693 | 62.3405 | 6.8798 | 100.8641 | 0 | 37.4842 | 0 | 1.0916 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 407.5757 | 13.3%
CZ 3B | 0.42796 | 0.15899 | 0.026244 | 0.54662 | 0.24689 | 0.79476 | 0 | 0.39442 | 0 | 0.0086113 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9454 | 6.287% | CZ 3B | 14.1533 | 5.2579 | 2.6509 | 25.5038 | 8.1649 | 26.2837 | 0 | 13.044 | 0 | 0.28479 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 142.6215 | 6.287% | CZ 3B | 4.1469 | 1.5406 | 0 | 4.2375 | 2.3923 | 7.7011 | 0 | 3.8219 | 0 | 0.083442 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.4983 | 6.287% | CZ 3B | 0 | 0 | 0.026509 | 0.11041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18053 | 6.287% | CZ 3B | 43.4138 | 16.1282 | 2.8974 | 56.4301 | 25.0449 | 80.6224 | 0 | 40.0111 | 0 | 0.87356 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 401.8328 | 6.287%
CZ 3C | 0.42796 | 0.15891 | 0.028992 | 0.54538 | 0.012651 | 0.61078 | 0 | 0.35773 | 0 | 0.0089124 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.4922 | 1.4% | CZ 3C | 14.1533 | 5.2554 | 2.9285 | 30.4344 | 0.41839 | 20.1992 | 0 | 11.8308 | 0 | 0.29475 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 132.7928 | 1.4% | CZ 3C | 4.1469 | 1.5398 | 0 | 3.5164 | 0.12259 | 5.9183 | 0 | 3.4664 | 0 | 0.08636 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 31.3715 | 1.4% | CZ 3C | 0 | 0 | 0.029285 | 0.18433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25722 | 1.4% | CZ 3C | 43.4138 | 16.1204 | 3.2008 | 56.9603 | 1.2834 | 61.9588 | 0 | 36.2896 | 0 | 0.9041 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 356.5424 | 1.4%
CZ 4A | 0.42796 | 0.15883 | 0.029274 | 0.697 | 0.11858 | 0.81554 | 0 | 0.36499 | 0 | 0.011566 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9646 | 18.71% | CZ 4A | 14.1533 | 5.2526 | 2.9569 | 35.7617 | 3.9215 | 26.9709 | 0 | 12.0709 | 0 | 0.3825 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 148.7485 | 18.71% | CZ 4A | 4.1469 | 1.539 | 0 | 4.9409 | 1.149 | 7.9024 | 0 | 3.5367 | 0 | 0.11207 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 35.9018 | 18.71% | CZ 4A | 0 | 0 | 0.029569 | 0.18898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26216 | 18.71% | CZ 4A | 43.4138 | 16.1118 | 3.2319 | 72.3826 | 12.0288 | 82.7303 | 0 | 37.0261 | 0 | 1.1733 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 404.5099 | 18.71%
CZ 4B | 0.42796 | 0.15887 | 0.028909 | 0.60079 | 0.35406 | 0.6354 | 0 | 0.41652 | 0 | 0.0089404 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9723 | 0.5317% | CZ 4B | 14.1533 | 5.254 | 2.9201 | 26.6976 | 11.7092 | 21.0135 | 0 | 13.775 | 0 | 0.29567 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 143.0965 | 0.5317% | CZ 4B | 4.1469 | 1.5394 | 0 | 4.8476 | 3.4308 | 6.1569 | 0 | 4.036 | 0 | 0.086631 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.819 | 0.5317% | CZ 4B | 0 | 0 | 0.029201 | 0.10153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17433 | 0.5317% | CZ 4B | 43.4138 | 16.1161 | 3.1917 | 61.8464 | 35.9168 | 64.4566 | 0 | 42.2533 | 0 | 0.90694 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 404.5129 | 0.5317%
CZ 4C | 0.42796 | 0.15875 | 0.030268 | 0.67703 | 0.044303 | 0.52372 | 0 | 0.36321 | 0 | 0.01018 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.5763 | 4.138% | CZ 4C | 14.1533 | 5.2501 | 3.0574 | 35.2668 | 1.4652 | 17.3203 | 0 | 12.0119 | 0 | 0.33665 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 136.1397 | 4.138% | CZ 4C | 4.1469 | 1.5383 | 0 | 4.7237 | 0.42929 | 5.0748 | 0 | 3.5194 | 0 | 0.098639 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 32.1058 | 4.138% | CZ 4C | 0 | 0 | 0.030574 | 0.19145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26563 | 4.138% | CZ 4C | 43.4138 | 16.104 | 3.3417 | 70.3779 | 4.4942 | 53.128 | 0 | 36.845 | 0 | 1.0326 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 365.1486 | 4.138%
CZ 5A | 0.42796 | 0.15884 | 0.030928 | 0.80313 | 0.14544 | 0.58814 | 0 | 0.36496 | 0 | 0.014156 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.8745 | 24.21% | CZ 5A | 14.1533 | 5.2531 | 3.1241 | 41.032 | 4.8099 | 19.4506 | 0 | 12.0697 | 0 | 0.46817 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 147.639 | 24.21% | CZ 5A | 4.1469 | 1.5391 | 0 | 5.7183 | 1.4093 | 5.699 | 0 | 3.5364 | 0 | 0.13717 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 34.7609 | 24.21% | CZ 5A | 0 | 0 | 0.031241 | 0.21516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29 | 24.21% | CZ 5A | 43.4138 | 16.1133 | 3.4146 | 83.3809 | 14.7539 | 59.6627 | 0 | 37.0226 | 0 | 1.436 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 395.609 | 24.21%
CZ 5B | 0.42796 | 0.1587 | 0.030632 | 0.78116 | 0.24766 | 0.51417 | 0 | 0.38624 | 0 | 0.012252 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.8997 | 4.982% | CZ 5B | 14.1533 | 5.2485 | 3.0942 | 35.2709 | 8.1904 | 17.0045 | 0 | 12.7734 | 0 | 0.40519 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 143.4183 | 4.982% | CZ 5B | 4.1469 | 1.5378 | 0 | 6.2233 | 2.3998 | 4.9823 | 0 | 3.7426 | 0 | 0.11872 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 35.7261 | 4.982% | CZ 5B | 0 | 0 | 0.030942 | 0.14031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21485 | 4.982% | CZ 5B | 43.4138 | 16.0991 | 3.3819 | 80.4874 | 25.123 | 52.1593 | 0 | 39.1809 | 0 | 1.2429 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 397.4996 | 4.982%
CZ 5C | 0.42796 | 0.15859 | 0.030949 | 0.71313 | 0.060356 | 0.42927 | 0 | 0.36378 | 0 | 0.010705 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.5356 | 0% | CZ 5C | 14.1533 | 5.2448 | 3.1261 | 35.9975 | 1.9961 | 14.1966 | 0 | 12.0308 | 0 | 0.35402 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 134.3774 | 0% | CZ 5C | 4.1469 | 1.5367 | 0 | 5.1396 | 0.58484 | 4.1596 | 0 | 3.525 | 0 | 0.10373 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 31.7712 | 0% | CZ 5C | 0 | 0 | 0.031261 | 0.18456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25942 | 0% | CZ 5C | 43.4138 | 16.0877 | 3.4169 | 73.9793 | 6.1227 | 43.5466 | 0 | 36.9033 | 0 | 1.0859 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 360.9674 | 0%
CZ 6A | 0.42796 | 0.15875 | 0.032395 | 0.88051 | 0.18335 | 0.47521 | 0 | 0.36707 | 0 | 0.015108 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.8813 | 7.834% | CZ 6A | 14.1533 | 5.2501 | 3.2722 | 45.6675 | 6.0637 | 15.7157 | 0 | 12.1397 | 0 | 0.49965 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 150.04 | 7.834% | CZ 6A | 4.1469 | 1.5383 | 0 | 6.1718 | 1.7766 | 4.6047 | 0 | 3.5569 | 0 | 0.1464 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 34.5164 | 7.834% | CZ 6A | 0 | 0 | 0.032722 | 0.24603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32236 | 7.834% | CZ 6A | 43.4138 | 16.104 | 3.5765 | 91.504 | 18.5997 | 48.2063 | 0 | 37.2371 | 0 | 1.5326 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 396.5853 | 7.834%
CZ 6B | 0.42796 | 0.1587 | 0.032612 | 0.86404 | 0.34784 | 0.4204 | 0 | 0.39827 | 0 | 0.014366 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.0051 | 0.7615% | CZ 6B | 14.1533 | 5.2485 | 3.2942 | 40.2127 | 11.5034 | 13.9033 | 0 | 13.1714 | 0 | 0.47511 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 149.2399 | 0.7615% | CZ 6B | 4.1469 | 1.5378 | 0 | 6.7126 | 3.3705 | 4.0736 | 0 | 3.8592 | 0 | 0.13921 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.4146 | 0.7615% | CZ 6B | 0 | 0 | 0.032942 | 0.17302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24957 | 0.7615% | CZ 6B | 43.4138 | 16.0991 | 3.6005 | 89.1862 | 35.2854 | 42.6467 | 0 | 40.4018 | 0 | 1.4574 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 408.5021 | 0.7615%
CZ 7 | 0.42796 | 0.15864 | 0.034732 | 0.99273 | 0.24083 | 0.38313 | 0 | 0.37476 | 0 | 0.016502 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9702 | 0.8914% | CZ 7 | 14.1533 | 5.2464 | 3.5083 | 52.2194 | 7.9646 | 12.6708 | 0 | 12.3939 | 0 | 0.54573 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 155.9806 | 0.8914% | CZ 7 | 4.1469 | 1.5372 | 0 | 6.8541 | 2.3336 | 3.7125 | 0 | 3.6314 | 0 | 0.1599 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 34.9503 | 0.8914% | CZ 7 | 0 | 0 | 0.035083 | 0.28826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.36695 | 0.8914% | CZ 7 | 43.4138 | 16.0927 | 3.8346 | 103.2627 | 24.4305 | 38.8663 | 0 | 38.0169 | 0 | 1.674 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 406.0027 | 0.8914%
CZ 8 | 0.42796 | 0.15764 | 0.037597 | 1.3671 | 0.3521 | 0.27219 | 0 | 0.37872 | 0 | 0.021297 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.3556 | 0.0471% | CZ 8 | 14.1533 | 5.2135 | 3.7977 | 74.4204 | 11.6444 | 9.0017 | 0 | 12.5249 | 0 | 0.70433 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 178.7383 | 0.0471% | CZ 8 | 4.1469 | 1.5275 | 0 | 9.0818 | 3.4118 | 2.6375 | 0 | 3.6698 | 0 | 0.20637 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.2564 | 0.0471% | CZ 8 | 0 | 0 | 0.037977 | 0.43424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.51582 | 0.0471% | CZ 8 | 43.4138 | 15.9918 | 4.1508 | 142.54 | 35.7179 | 27.6116 | 0 | 38.4189 | 0 | 2.1605 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 446.4165 | 0.0471%
Us Weighted | 0.42796 | 0.15887 | 0.028801 | 0.69202 | 0.12365 | 0.78866 | 0 | 0.37295 | 0 | 0.011653 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.9455 | 100% | Us Weighted | 14.1533 | 5.254 | 2.9092 | 35.5485 | 4.0892 | 26.0821 | 0 | 12.334 | 0 | 0.38539 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 148.0338 | 100% | Us Weighted | 4.1469 | 1.5394 | 0 | 4.8995 | 1.1981 | 7.642 | 0 | 3.6138 | 0 | 0.11292 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 35.7274 | 100% | Us Weighted | 0 | 0 | 0.029092 | 0.18826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26096 | 100% | Us Weighted | 43.4138 | 16.1161 | 3.1798 | 71.8704 | 12.5432 | 80.0038 | 0 | 37.833 | 0 | 1.1822 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 402.5535 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.42796 | 0.15909 | 0.022527 | 0.41552 | 0.0026674 | 1.57 | 0 | 0.43263 | 0 | 0.0076242 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.379 | 0.8522% | CZ 1A | 14.1533 | 5.2614 | 2.2754 | 25.0238 | 0.088215 | 51.9231 | 0 | 14.3078 | 0 | 0.25214 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 160.5633 | 0.8522% | CZ 1A | 4.1469 | 1.5416 | 0 | 2.4172 | 0.025847 | 15.2133 | 0 | 4.1921 | 0 | 0.073877 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 40.1856 | 0.8522% | CZ 1A | 0 | 0 | 0.022754 | 0.16774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2341 | 0.8522% | CZ 1A | 43.4138 | 16.1388 | 2.4871 | 43.6394 | 0.27059 | 159.2683 | 0 | 43.8875 | 0 | 0.77342 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 446.2902 | 0.8522%
CZ 1B | 0.42796 | 0.15907 | 0.021487 | 0.65916 | 0.25133 | 1.2929 | 0 | 0.47752 | 0 | 0.0072531 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.6376 | 0% | CZ 1B | 14.1533 | 5.2607 | 2.1704 | 28.3768 | 8.3117 | 42.7594 | 0 | 15.7924 | 0 | 0.23987 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 164.3426 | 0% | CZ 1B | 4.1469 | 1.5414 | 0 | 5.4491 | 2.4353 | 12.5284 | 0 | 4.6271 | 0 | 0.070282 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 43.3732 | 0% | CZ 1B | 0 | 0 | 0.021704 | 0.097791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1631 | 0% | CZ 1B | 43.4138 | 16.1367 | 2.3722 | 67.7348 | 25.4951 | 131.1596 | 0 | 48.4413 | 0 | 0.73578 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 471.9006 | 0%
CZ 2A | 0.42796 | 0.15903 | 0.024977 | 0.6068 | 0.033052 | 1.313 | 0 | 0.42193 | 0 | 0.0097595 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.3374 | 12.98% | CZ 2A | 14.1533 | 5.2593 | 2.5229 | 32.2648 | 1.0931 | 43.4213 | 0 | 13.954 | 0 | 0.32276 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 160.2696 | 12.98% | CZ 2A | 4.1469 | 1.541 | 0 | 4.1402 | 0.32027 | 12.7223 | 0 | 4.0885 | 0 | 0.094568 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 39.6285 | 12.98% | CZ 2A | 0 | 0 | 0.025229 | 0.18134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25018 | 12.98% | CZ 2A | 43.4138 | 16.1324 | 2.7575 | 63.1643 | 3.3529 | 133.1901 | 0 | 42.8023 | 0 | 0.99003 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 442.2146 | 12.98%
CZ 2B | 0.42796 | 0.15899 | 0.02354 | 0.623 | 0.12024 | 1.2133 | 0 | 0.44867 | 0 | 0.0076032 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.3642 | 3.07% | CZ 2B | 14.1533 | 5.2579 | 2.3778 | 30.4953 | 3.9766 | 40.1268 | 0 | 14.8382 | 0 | 0.25145 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 158.7555 | 3.07% | CZ 2B | 4.1469 | 1.5406 | 0 | 4.626 | 1.1651 | 11.757 | 0 | 4.3476 | 0 | 0.073674 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 40.2316 | 3.07% | CZ 2B | 0 | 0 | 0.023778 | 0.14707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21445 | 3.07% | CZ 2B | 43.4138 | 16.1282 | 2.5989 | 64.5038 | 12.1979 | 123.0845 | 0 | 45.5146 | 0 | 0.77129 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 444.6242 | 3.07%
CZ 3A | 0.42796 | 0.15892 | 0.026904 | 0.70632 | 0.088333 | 1.0533 | 0 | 0.41075 | 0 | 0.012189 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2255 | 13.3% | CZ 3A | 14.1533 | 5.2556 | 2.7176 | 36.5934 | 2.9213 | 34.8332 | 0 | 13.584 | 0 | 0.4031 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 157.7396 | 13.3% | CZ 3A | 4.1469 | 1.5399 | 0 | 4.9566 | 0.85593 | 10.206 | 0 | 3.9801 | 0 | 0.11811 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.3783 | 13.3% | CZ 3A | 0 | 0 | 0.027176 | 0.19676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26754 | 13.3% | CZ 3A | 43.4138 | 16.1211 | 2.9703 | 73.3972 | 8.9607 | 106.847 | 0 | 41.6674 | 0 | 1.2365 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 431.0252 | 13.3%
CZ 3B | 0.42796 | 0.15899 | 0.026249 | 0.6324 | 0.27731 | 0.84429 | 0 | 0.43662 | 0 | 0.0097315 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1544 | 6.287% | CZ 3B | 14.1533 | 5.2579 | 2.6514 | 28.5838 | 9.1711 | 27.9218 | 0 | 14.4395 | 0 | 0.32183 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 149.7789 | 6.287% | CZ 3B | 4.1469 | 1.5406 | 0 | 5.034 | 2.6871 | 8.181 | 0 | 4.2307 | 0 | 0.094297 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.4894 | 6.287% | CZ 3B | 0 | 0 | 0.026514 | 0.11403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18415 | 6.287% | CZ 3B | 43.4138 | 16.1282 | 2.8979 | 65.1639 | 28.1315 | 85.6472 | 0 | 44.2916 | 0 | 0.98719 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 423.0724 | 6.287%
CZ 3C | 0.42796 | 0.15891 | 0.029008 | 0.68469 | 0.018651 | 0.64537 | 0 | 0.40587 | 0 | 0.0081843 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.7195 | 1.4% | CZ 3C | 14.1533 | 5.2554 | 2.9301 | 36.0395 | 0.61681 | 21.3434 | 0 | 13.4226 | 0 | 0.27067 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 141.31 | 1.4% | CZ 3C | 4.1469 | 1.5398 | 0 | 4.7239 | 0.18072 | 6.2536 | 0 | 3.9328 | 0 | 0.079304 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 33.4318 | 1.4% | CZ 3C | 0 | 0 | 0.029301 | 0.19917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27207 | 1.4% | CZ 3C | 43.4138 | 16.1204 | 3.2026 | 71.2238 | 1.892 | 65.4687 | 0 | 41.1723 | 0 | 0.83024 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 379.735 | 1.4%
CZ 4A | 0.42796 | 0.15883 | 0.029276 | 0.85215 | 0.1532 | 0.85657 | 0 | 0.40531 | 0 | 0.013218 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2374 | 18.71% | CZ 4A | 14.1533 | 5.2526 | 2.9572 | 42.444 | 5.0665 | 28.328 | 0 | 13.4043 | 0 | 0.43714 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 159.321 | 18.71% | CZ 4A | 4.1469 | 1.539 | 0 | 6.223 | 1.4845 | 8.3 | 0 | 3.9274 | 0 | 0.12808 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.3237 | 18.71% | CZ 4A | 0 | 0 | 0.029572 | 0.21205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28522 | 18.71% | CZ 4A | 43.4138 | 16.1118 | 3.2322 | 88.3258 | 15.5408 | 86.8929 | 0 | 41.1162 | 0 | 1.3409 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 432.3857 | 18.71%
CZ 4B | 0.42796 | 0.15887 | 0.028914 | 0.7315 | 0.39224 | 0.66605 | 0 | 0.46043 | 0 | 0.01025 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2171 | 0.5317% | CZ 4B | 14.1533 | 5.254 | 2.9206 | 31.6501 | 12.972 | 22.0272 | 0 | 15.2272 | 0 | 0.33897 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 151.8215 | 0.5317% | CZ 4B | 4.1469 | 1.5394 | 0 | 6.0243 | 3.8008 | 6.4539 | 0 | 4.4615 | 0 | 0.099317 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 39.1009 | 0.5317% | CZ 4B | 0 | 0 | 0.029206 | 0.11089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1837 | 0.5317% | CZ 4B | 43.4138 | 16.1161 | 3.1922 | 75.1892 | 39.7903 | 67.5659 | 0 | 46.7077 | 0 | 1.0397 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 429.4262 | 0.5317%
CZ 4C | 0.42796 | 0.15875 | 0.030282 | 0.84995 | 0.055386 | 0.53724 | 0 | 0.40505 | 0 | 0.011363 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.8169 | 4.138% | CZ 4C | 14.1533 | 5.2501 | 3.0588 | 43.0672 | 1.8317 | 17.7674 | 0 | 13.3955 | 0 | 0.37578 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 146.1779 | 4.138% | CZ 4C | 4.1469 | 1.5383 | 0 | 6.1025 | 0.53668 | 5.2058 | 0 | 3.9248 | 0 | 0.1101 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 34.1398 | 4.138% | CZ 4C | 0 | 0 | 0.030588 | 0.22239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.29659 | 4.138% | CZ 4C | 43.4138 | 16.104 | 3.3432 | 88.1947 | 5.6185 | 54.4994 | 0 | 41.0892 | 0 | 1.1527 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 389.8269 | 4.138%
CZ 5A | 0.42796 | 0.15884 | 0.030933 | 0.95491 | 0.18343 | 0.60524 | 0 | 0.40528 | 0 | 0.01688 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1244 | 24.21% | CZ 5A | 14.1533 | 5.2531 | 3.1245 | 48.3972 | 6.0662 | 20.016 | 0 | 13.4032 | 0 | 0.55823 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 158.2499 | 24.21% | CZ 5A | 4.1469 | 1.5391 | 0 | 6.8544 | 1.7774 | 5.8646 | 0 | 3.9271 | 0 | 0.16356 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.8479 | 24.21% | CZ 5A | 0 | 0 | 0.031245 | 0.25003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32488 | 24.21% | CZ 5A | 43.4138 | 16.1133 | 3.4151 | 99.0873 | 18.6075 | 61.397 | 0 | 41.1127 | 0 | 1.7123 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 421.2703 | 24.21%
CZ 5B | 0.42796 | 0.1587 | 0.030637 | 0.90709 | 0.28044 | 0.51407 | 0 | 0.42733 | 0 | 0.014317 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1014 | 4.982% | CZ 5B | 14.1533 | 5.2485 | 3.0947 | 40.4326 | 9.2746 | 17.001 | 0 | 14.1323 | 0 | 0.47349 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 151.0885 | 4.982% | CZ 5B | 4.1469 | 1.5378 | 0 | 7.3014 | 2.7174 | 4.9812 | 0 | 4.1407 | 0 | 0.13873 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.539 | 4.982% | CZ 5B | 0 | 0 | 0.030947 | 0.15513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22968 | 4.982% | CZ 5B | 43.4138 | 16.0991 | 3.3825 | 93.3941 | 28.4489 | 52.1486 | 0 | 43.3491 | 0 | 1.4524 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 418.0998 | 4.982%
CZ 5C | 0.42796 | 0.15859 | 0.030956 | 0.85288 | 0.073932 | 0.41932 | 0 | 0.40478 | 0 | 0.01214 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 3.7215 | 0% | CZ 5C | 14.1533 | 5.2448 | 3.1268 | 42.2512 | 2.445 | 13.8676 | 0 | 13.3865 | 0 | 0.40148 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 142.1548 | 0% | CZ 5C | 4.1469 | 1.5367 | 0 | 6.2611 | 0.71638 | 4.0632 | 0 | 3.9222 | 0 | 0.11763 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 33.3389 | 0% | CZ 5C | 0 | 0 | 0.031268 | 0.20882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28369 | 0% | CZ 5C | 43.4138 | 16.0877 | 3.4176 | 88.3715 | 7.4998 | 42.5374 | 0 | 41.0615 | 0 | 1.2315 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 380.0322 | 0%
CZ 6A | 0.42796 | 0.15875 | 0.032413 | 1.0525 | 0.23119 | 0.47928 | 0 | 0.40644 | 0 | 0.017524 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.147 | 7.834% | CZ 6A | 14.1533 | 5.2501 | 3.2741 | 54.3173 | 7.6458 | 15.8505 | 0 | 13.4416 | 0 | 0.57953 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 161.7903 | 7.834% | CZ 6A | 4.1469 | 1.5383 | 0 | 7.4163 | 2.2402 | 4.6442 | 0 | 3.9383 | 0 | 0.1698 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 36.6688 | 7.834% | CZ 6A | 0 | 0 | 0.032741 | 0.29005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.3664 | 7.834% | CZ 6A | 43.4138 | 16.104 | 3.5785 | 109.3445 | 23.4526 | 48.6196 | 0 | 41.2306 | 0 | 1.7777 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 423.9326 | 7.834%
CZ 6B | 0.42796 | 0.1587 | 0.032624 | 1.0197 | 0.38939 | 0.41453 | 0 | 0.4401 | 0 | 0.016663 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2406 | 0.7615% | CZ 6B | 14.1533 | 5.2485 | 3.2953 | 47.4291 | 12.8776 | 13.7092 | 0 | 14.5546 | 0 | 0.55106 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 159.0968 | 0.7615% | CZ 6B | 4.1469 | 1.5378 | 0 | 7.9262 | 3.7731 | 4.0168 | 0 | 4.2645 | 0 | 0.16146 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 38.4014 | 0.7615% | CZ 6B | 0 | 0 | 0.032953 | 0.20377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28033 | 0.7615% | CZ 6B | 43.4138 | 16.0991 | 3.6018 | 105.2511 | 39.5005 | 42.0516 | 0 | 44.6446 | 0 | 1.6903 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 432.664 | 0.7615%
CZ 7 | 0.42796 | 0.15864 | 0.034744 | 1.1905 | 0.29883 | 0.38954 | 0 | 0.42319 | 0 | 0.019127 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.2834 | 0.8914% | CZ 7 | 14.1533 | 5.2464 | 3.5095 | 62.8658 | 9.8829 | 12.8827 | 0 | 13.9957 | 0 | 0.63256 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 170.4468 | 0.8914% | CZ 7 | 4.1469 | 1.5372 | 0 | 8.1841 | 2.8957 | 3.7746 | 0 | 4.1007 | 0 | 0.18534 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.3993 | 0.8914% | CZ 7 | 0 | 0 | 0.035095 | 0.34933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.42803 | 0.8914% | CZ 7 | 43.4138 | 16.0927 | 3.8358 | 123.8619 | 30.3146 | 39.5161 | 0 | 42.9301 | 0 | 1.9403 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 438.3167 | 0.8914%
CZ 8 | 0.42796 | 0.15764 | 0.037604 | 1.5643 | 0.43227 | 0.27105 | 0 | 0.43173 | 0 | 0.024868 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.6883 | 0.0471% | CZ 8 | 14.1533 | 5.2135 | 3.7984 | 87.6398 | 14.2957 | 8.9639 | 0 | 14.2779 | 0 | 0.82242 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 196.4431 | 0.0471% | CZ 8 | 4.1469 | 1.5275 | 0 | 10.036 | 4.1886 | 2.6264 | 0 | 4.1834 | 0 | 0.24097 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 39.5246 | 0.0471% | CZ 8 | 0 | 0 | 0.037984 | 0.53387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.61546 | 0.0471% | CZ 8 | 43.4138 | 15.9918 | 4.1516 | 163.419 | 43.8505 | 27.4958 | 0 | 43.7959 | 0 | 2.5227 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 481.0524 | 0.0471%
Us Weighted | 0.42796 | 0.15887 | 0.028807 | 0.8212 | 0.15282 | 0.82577 | 0 | 0.41363 | 0 | 0.013393 | 0 | 0.45649 | 0 | 0 | 0 | 0.88441 | 4.1833 | 100% | Us Weighted | 14.1533 | 5.254 | 2.9098 | 41.3493 | 5.054 | 27.3092 | 0 | 13.6793 | 0 | 0.44293 | 0 | 15.0967 | 0 | 0 | 0 | 32.1814 | 157.4301 | 100% | Us Weighted | 4.1469 | 1.5394 | 0 | 5.9333 | 1.4808 | 8.0015 | 0 | 4.008 | 0 | 0.12978 | 0 | 4.4233 | 0 | 0 | 0 | 8.1515 | 37.8145 | 100% | Us Weighted | 0 | 0 | 0.029098 | 0.21099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28369 | 100% | Us Weighted | 43.4138 | 16.1161 | 3.1804 | 85.1771 | 15.5026 | 83.768 | 0 | 41.9597 | 0 | 1.3586 | 0 | 46.3076 | 0 | 0 | 0 | 90.1037 | 426.8876 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 40946 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 40946 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.074569 | 0.081241 | 0.00035062 | 0.18281 | 0.0014492 | 0.4112 | 0 | 0.16682 | -0.02115 | 0.00014702 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 0.91439 | 0.8522% | CZ 1A | 2.4661 | 2.6867 | 0.035416 | 10.2567 | 0.047928 | 13.599 | 0 | 5.517 | -0.69947 | 0.0048623 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 34.4749 | 0.8522% | CZ 1A | 0.72256 | 0.78721 | 0 | 1.1708 | 0.014043 | 3.9845 | 0 | 1.6165 | -0.20494 | 0.0014246 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 8.2563 | 0.8522% | CZ 1A | 0 | 0 | 0.00035416 | 0.062608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062963 | 0.8522% | CZ 1A | 7.5645 | 8.2413 | 0.03871 | 19.0999 | 0.14701 | 41.7135 | 0 | 16.9229 | -2.1455 | 0.014914 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 93.3166 | 0.8522%
CZ 1B | 0.07438 | 0.081234 | 0.00035062 | 0.42354 | 0.16247 | 0.35607 | 0 | 0.18778 | 0 | -0.00018203 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.3026 | 0% | CZ 1B | 2.4598 | 2.6865 | 0.035416 | 15.0187 | 5.373 | 11.7757 | 0 | 6.21 | 0 | -0.0060199 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.1137 | 0% | CZ 1B | 0.72073 | 0.78714 | 0 | 3.9597 | 1.5743 | 3.4502 | 0 | 1.8195 | 0 | -0.0017638 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 12.4741 | 0% | CZ 1B | 0 | 0 | 0.00035416 | 0.015042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015396 | 0% | CZ 1B | 7.5453 | 8.2406 | 0.03871 | 43.0983 | 16.4812 | 36.1206 | 0 | 19.0486 | 0 | -0.018465 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 132.2742 | 0%
CZ 2A | 0.074016 | 0.081213 | 0.00034604 | 0.29026 | 0.017601 | 0.40347 | 0 | 0.17059 | -0.016733 | 0.0011482 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.0389 | 12.98% | CZ 2A | 2.4478 | 2.6858 | 0.034953 | 13.9635 | 0.58208 | 13.3432 | 0 | 5.6416 | -0.55337 | 0.037972 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 38.7441 | 12.98% | CZ 2A | 0.7172 | 0.78694 | 0 | 2.1901 | 0.17055 | 3.9095 | 0 | 1.653 | -0.16214 | 0.011126 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 9.4405 | 12.98% | CZ 2A | 0 | 0 | 0.00034953 | 0.064888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065238 | 12.98% | CZ 2A | 7.5083 | 8.2384 | 0.038204 | 30.02 | 1.7855 | 40.9287 | 0 | 17.305 | -1.6974 | 0.11647 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 105.9627 | 12.98%
CZ 2B | 0.073967 | 0.081199 | 0.00034833 | 0.40329 | 0.070515 | 0.36306 | 0 | 0.1795 | 0 | -0.00092414 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1879 | 3.07% | CZ 2B | 2.4462 | 2.6854 | 0.035185 | 16.4687 | 2.332 | 12.0068 | 0 | 5.9363 | 0 | -0.030563 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 42.4406 | 3.07% | CZ 2B | 0.71672 | 0.7868 | 0 | 3.4612 | 0.68328 | 3.5179 | 0 | 1.7393 | 0 | -0.0089548 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 11.0606 | 3.07% | CZ 2B | 0 | 0 | 0.00035185 | 0.046555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046907 | 3.07% | CZ 2B | 7.5034 | 8.237 | 0.038457 | 41.3242 | 7.1532 | 36.8294 | 0 | 18.2091 | 0 | -0.093748 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 120.9204 | 3.07%
CZ 3A | 0.073735 | 0.081087 | 0.00033687 | 0.3127 | 0.041565 | 0.33242 | 0 | 0.1532 | -0.015696 | 0.0023104 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 0.99861 | 13.3% | CZ 3A | 2.4385 | 2.6816 | 0.034028 | 14.9808 | 1.3746 | 10.9936 | 0 | 5.0665 | -0.5191 | 0.076407 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 37.6875 | 13.3% | CZ 3A | 0.71448 | 0.78572 | 0 | 2.3683 | 0.40276 | 3.2211 | 0 | 1.4845 | -0.1521 | 0.022387 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 9.0114 | 13.3% | CZ 3A | 0 | 0 | 0.00034028 | 0.068976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069317 | 13.3% | CZ 3A | 7.4799 | 8.2257 | 0.037192 | 32.3333 | 4.2165 | 33.7215 | 0 | 15.5408 | -1.5923 | 0.23437 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 101.9164 | 13.3%
CZ 3B | 0.074016 | 0.081199 | 0.00033687 | 0.40857 | 0.18233 | 0.26723 | 0 | 0.16801 | 0 | 0.0016873 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.2003 | 6.287% | CZ 3B | 2.4478 | 2.6854 | 0.034028 | 15.3668 | 6.0299 | 8.8377 | 0 | 5.5562 | 0 | 0.0558 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.5741 | 6.287% | CZ 3B | 0.7172 | 0.7868 | 0 | 3.6945 | 1.7667 | 2.5894 | 0 | 1.6279 | 0 | 0.016349 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 11.3632 | 6.287% | CZ 3B | 0 | 0 | 0.00034028 | 0.027576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027916 | 6.287% | CZ 3B | 7.5083 | 8.237 | 0.037192 | 41.6914 | 18.496 | 27.1087 | 0 | 17.0429 | 0 | 0.17116 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 122.0123 | 6.287%
CZ 3C | 0.073777 | 0.081108 | 0.00036437 | 0.45965 | 0.01508 | 0.28823 | 0 | 0.15714 | 0 | -0.00024504 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.0921 | 1.4% | CZ 3C | 2.4399 | 2.6823 | 0.036805 | 20.2388 | 0.49873 | 9.5323 | 0 | 5.1968 | 0 | -0.0081038 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.1782 | 1.4% | CZ 3C | 0.71489 | 0.78592 | 0 | 3.7355 | 0.14613 | 2.7929 | 0 | 1.5227 | 0 | -0.0023744 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 9.8599 | 1.4% | CZ 3C | 0 | 0 | 0.00036805 | 0.074895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075263 | 1.4% | CZ 3C | 7.4842 | 8.2278 | 0.040228 | 47.2931 | 1.5298 | 29.2394 | 0 | 15.9407 | 0 | -0.024857 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 111.4497 | 1.4%
CZ 4A | 0.075514 | 0.08101 | 0.00035521 | 0.53595 | 0.064389 | 0.31076 | 0 | 0.13965 | -0.01578 | 0.0025344 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.2113 | 18.71% | CZ 4A | 2.4973 | 2.6791 | 0.035879 | 22.3207 | 2.1294 | 10.2772 | 0 | 4.6184 | -0.52188 | 0.083816 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.6806 | 18.71% | CZ 4A | 0.73172 | 0.78497 | 0 | 4.5378 | 0.62392 | 3.0112 | 0 | 1.3532 | -0.15291 | 0.024558 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 11.0787 | 18.71% | CZ 4A | 0 | 0 | 0.00035879 | 0.068333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068692 | 18.71% | CZ 4A | 7.6603 | 8.2178 | 0.039216 | 54.9748 | 6.5318 | 31.5241 | 0 | 14.1666 | -1.6008 | 0.2571 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 123.4904 | 18.71%
CZ 4B | 0.075626 | 0.081108 | 0.00035062 | 0.48195 | 0.25812 | 0.22571 | 0 | 0.17752 | 0 | 0.0018763 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.3192 | 0.5317% | CZ 4B | 2.5011 | 2.6823 | 0.035416 | 17.3654 | 8.5365 | 7.4645 | 0 | 5.8708 | 0 | 0.062052 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.0786 | 0.5317% | CZ 4B | 0.7328 | 0.78592 | 0 | 4.4665 | 2.5012 | 2.1871 | 0 | 1.7201 | 0 | 0.018181 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 12.5761 | 0.5317% | CZ 4B | 0 | 0 | 0.00035416 | 0.02121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021565 | 0.5317% | CZ 4B | 7.6717 | 8.2278 | 0.03871 | 49.0786 | 26.1848 | 22.8965 | 0 | 18.0081 | 0 | 0.19034 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 134.0159 | 0.5317%
CZ 4C | 0.074982 | 0.080877 | 0.00035979 | 0.5706 | 0.037029 | 0.19604 | 0 | 0.15099 | 0 | 0.0013442 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1292 | 4.138% | CZ 4C | 2.4797 | 2.6747 | 0.036342 | 23.761 | 1.2246 | 6.4835 | 0 | 4.9935 | 0 | 0.044455 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 42.2584 | 4.138% | CZ 4C | 0.72656 | 0.78368 | 0 | 4.8315 | 0.3588 | 1.8996 | 0 | 1.4631 | 0 | 0.013025 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 10.2405 | 4.138% | CZ 4C | 0 | 0 | 0.00036342 | 0.072712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073076 | 4.138% | CZ 4C | 7.6064 | 8.2044 | 0.039722 | 58.528 | 3.7563 | 19.8873 | 0 | 15.3171 | 0 | 0.13636 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 115.1949 | 4.138%
CZ 5A | 0.075458 | 0.080786 | 0.00034146 | 0.57088 | 0.081283 | 0.14891 | 0 | 0.1453 | -0.016502 | 0.0035075 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1069 | 24.21% | CZ 5A | 2.4955 | 2.6717 | 0.03449 | 23.5511 | 2.6881 | 4.9245 | 0 | 4.8053 | -0.54573 | 0.116 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.3015 | 24.21% | CZ 5A | 0.73117 | 0.7828 | 0 | 4.8655 | 0.78762 | 1.4429 | 0 | 1.4079 | -0.1599 | 0.033988 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 10.0562 | 24.21% | CZ 5A | 0 | 0 | 0.0003449 | 0.069451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069796 | 24.21% | CZ 5A | 7.6547 | 8.1951 | 0.037698 | 58.528 | 8.2455 | 15.1055 | 0 | 14.7397 | -1.674 | 0.35582 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 112.9075 | 24.21%
CZ 5B | 0.074947 | 0.081073 | 0.00036437 | 0.59213 | 0.19421 | 0.17699 | 0 | 0.15603 | 0 | 0.0028844 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.2956 | 4.982% | CZ 5B | 2.4786 | 2.6812 | 0.036805 | 20.46 | 6.4228 | 5.8535 | 0 | 5.1602 | 0 | 0.095393 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 43.7491 | 4.982% | CZ 5B | 0.72622 | 0.78558 | 0 | 5.6125 | 1.8819 | 1.715 | 0 | 1.5119 | 0 | 0.02795 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 12.4253 | 4.982% | CZ 5B | 0 | 0 | 0.00036805 | 0.013046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013414 | 4.982% | CZ 5B | 7.6028 | 8.2242 | 0.040228 | 60.1831 | 19.7012 | 17.9548 | 0 | 15.8285 | 0 | 0.29261 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 131.547 | 4.982%
CZ 5C | 0.073539 | 0.080646 | 0.00035979 | 0.56128 | 0.048399 | 0.15764 | 0 | 0.13859 | 0 | 0.0017083 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.0791 | 0% | CZ 5C | 2.4321 | 2.6671 | 0.036342 | 22.0393 | 1.6006 | 5.2135 | 0 | 4.5833 | 0 | 0.056495 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 39.1892 | 0% | CZ 5C | 0.71259 | 0.78144 | 0 | 4.9428 | 0.46897 | 1.5275 | 0 | 1.3429 | 0 | 0.016553 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 9.957 | 0% | CZ 5C | 0 | 0 | 0.00036342 | 0.051696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05206 | 0% | CZ 5C | 7.4601 | 8.1809 | 0.039722 | 57.3964 | 4.9097 | 15.9918 | 0 | 14.0586 | 0 | 0.17329 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 109.9299 | 0%
CZ 6A | 0.075199 | 0.08066 | 0.00036666 | 0.63709 | 0.094942 | 0.11826 | 0 | 0.14628 | -0.016145 | 0.0031715 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1568 | 7.834% | CZ 6A | 2.4869 | 2.6675 | 0.037037 | 27.1688 | 3.1399 | 3.9111 | 0 | 4.8377 | -0.53392 | 0.10489 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.3804 | 7.834% | CZ 6A | 0.72866 | 0.78158 | 0 | 5.3033 | 0.91997 | 1.1459 | 0 | 1.4174 | -0.15644 | 0.030731 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 10.3355 | 7.834% | CZ 6A | 0 | 0 | 0.00037037 | 0.090685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091055 | 7.834% | CZ 6A | 7.6284 | 8.1823 | 0.040481 | 65.4325 | 9.6312 | 11.9969 | 0 | 14.8391 | -1.6377 | 0.32173 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 118.1543 | 7.834%
CZ 6B | 0.07508 | 0.08094 | 0.00036437 | 0.63918 | 0.25385 | 0.15412 | 0 | 0.1632 | 0 | 0.0031995 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.3869 | 0.7615% | CZ 6B | 2.483 | 2.6768 | 0.036805 | 23.0686 | 8.395 | 5.097 | 0 | 5.3973 | 0 | 0.10581 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 47.821 | 0.7615% | CZ 6B | 0.72751 | 0.78429 | 0 | 5.9183 | 2.4597 | 1.4934 | 0 | 1.5814 | 0 | 0.031003 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 13.1599 | 0.7615% | CZ 6B | 0 | 0 | 0.00036805 | 0.028694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029062 | 0.7615% | CZ 6B | 7.6163 | 8.2107 | 0.040228 | 65.0951 | 25.7508 | 15.6346 | 0 | 16.5557 | 0 | 0.32457 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 140.9475 | 0.7615%
CZ 7 | 0.076403 | 0.080716 | 0.00037354 | 0.73137 | 0.1325 | 0.08666 | 0 | 0.15137 | -0.016166 | 0.0033605 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.2635 | 0.8914% | CZ 7 | 2.5268 | 2.6694 | 0.037731 | 31.5737 | 4.382 | 2.866 | 0 | 5.006 | -0.53462 | 0.11114 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 49.1987 | 0.8914% | CZ 7 | 0.74033 | 0.78212 | 0 | 6.0334 | 1.2839 | 0.83972 | 0 | 1.4668 | -0.15664 | 0.032563 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 11.1864 | 0.8914% | CZ 7 | 0 | 0 | 0.00037731 | 0.10982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11019 | 0.8914% | CZ 7 | 7.7505 | 8.188 | 0.04124 | 75.1669 | 13.4414 | 8.791 | 0 | 15.3555 | -1.6399 | 0.3409 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 129.1551 | 0.8914%
CZ 8 | 0.073939 | 0.079336 | 0.000385 | 0.85298 | 0.16399 | 0.062142 | 0 | 0.15723 | -0.015829 | 0.0042917 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.3954 | 0.0471% | CZ 8 | 2.4453 | 2.6238 | 0.038889 | 37.6691 | 5.4233 | 2.0551 | 0 | 5.1998 | -0.5235 | 0.14193 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 55.6342 | 0.0471% | CZ 8 | 0.71645 | 0.76876 | 0 | 6.916 | 1.589 | 0.60214 | 0 | 1.5235 | -0.15338 | 0.041586 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 12.1683 | 0.0471% | CZ 8 | 0 | 0 | 0.00038889 | 0.14065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14104 | 0.0471% | CZ 8 | 7.5005 | 8.0481 | 0.042505 | 87.7761 | 16.6353 | 6.3038 | 0 | 15.9499 | -1.6058 | 0.43536 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 142.8053 | 0.0471%
Us Weighted | 0.074825 | 0.08098 | 0.00034874 | 0.48121 | 0.076603 | 0.25564 | 0 | 0.15262 | -0.012804 | 0.0023694 | 0 | 0.0089264 | 0 | 0 | 0 | 0.0080233 | 1.1287 | 100% | Us Weighted | 2.4746 | 2.6781 | 0.035226 | 20.2246 | 2.5334 | 8.4544 | 0 | 5.0473 | -0.42346 | 0.078361 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.663 | 100% | Us Weighted | 0.72504 | 0.78468 | 0 | 4.0481 | 0.74227 | 2.4771 | 0 | 1.4788 | -0.12407 | 0.022959 | 0 | 0.086496 | 0 | 0 | 0 | 0.077743 | 10.3192 | 100% | Us Weighted | 0 | 0 | 0.00035226 | 0.064083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064436 | 100% | Us Weighted | 7.5904 | 8.2148 | 0.038502 | 49.3843 | 7.7709 | 25.9329 | 0 | 15.482 | -1.2989 | 0.24036 | 0 | 0.90553 | 0 | 0 | 0 | 0.81389 | 115.0746 | 100%
Building Type: | Outpatient Healthcare |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 40946 | [17 empty] | Prototype Floor Area: | 40946 | [17 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 17.42% | 51.06% | 1.556% | 43.99% | 54.33% | 26.19% | 0% | 38.56% | 0% | 1.928% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 20.88% | 0.8522% | CZ 1A | 17.42% | 51.06% | 1.556% | 40.99% | 54.33% | 26.19% | 0% | 38.56% | 0% | 1.928% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 21.47% | 0.8522% | CZ 1A | 17.42% | 51.06% | 0% | 48.44% | 54.33% | 26.19% | 0% | 38.56% | 0% | 1.928% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 20.55% | 0.8522% | CZ 1A | 0% | 0% | 1.556% | 37.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.9% | 0.8522% | CZ 1A | 17.42% | 51.06% | 1.556% | 43.77% | 54.33% | 26.19% | 0% | 38.56% | 0% | 1.928% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 20.91% | 0.8522%
CZ 1B | 17.38% | 51.07% | 1.632% | 64.25% | 64.64% | 27.54% | 0% | 39.32% | 0% | -2.51% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 28.09% | 0% | CZ 1B | 17.38% | 51.07% | 1.632% | 52.93% | 64.64% | 27.54% | 0% | 39.32% | 0% | -2.51% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 26.84% | 0% | CZ 1B | 17.38% | 51.07% | 0% | 72.67% | 64.64% | 27.54% | 0% | 39.32% | 0% | -2.51% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 28.76% | 0% | CZ 1B | 0% | 0% | 1.632% | 15.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.44% | 0% | CZ 1B | 17.38% | 51.07% | 1.632% | 63.63% | 64.64% | 27.54% | 0% | 39.32% | 0% | -2.51% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.03% | 0%
CZ 2A | 17.29% | 51.07% | 1.385% | 47.83% | 53.25% | 30.73% | 0% | 40.43% | 0% | 11.76% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 23.95% | 12.98% | CZ 2A | 17.29% | 51.07% | 1.385% | 43.28% | 53.25% | 30.73% | 0% | 40.43% | 0% | 11.76% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 24.17% | 12.98% | CZ 2A | 17.29% | 51.07% | 0% | 52.9% | 53.25% | 30.73% | 0% | 40.43% | 0% | 11.76% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 23.82% | 12.98% | CZ 2A | 0% | 0% | 1.385% | 35.78% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.08% | 12.98% | CZ 2A | 17.29% | 51.07% | 1.385% | 47.53% | 53.25% | 30.73% | 0% | 40.43% | 0% | 11.76% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 23.96% | 12.98%
CZ 2B | 17.28% | 51.07% | 1.48% | 64.73% | 58.64% | 29.92% | 0% | 40.01% | 0% | -12.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 27.22% | 3.07% | CZ 2B | 17.28% | 51.07% | 1.48% | 54% | 58.64% | 29.92% | 0% | 40.01% | 0% | -12.15% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 26.73% | 3.07% | CZ 2B | 17.28% | 51.07% | 0% | 74.82% | 58.64% | 29.92% | 0% | 40.01% | 0% | -12.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 27.49% | 3.07% | CZ 2B | 0% | 0% | 1.48% | 31.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.87% | 3.07% | CZ 2B | 17.28% | 51.07% | 1.48% | 64.06% | 58.64% | 29.92% | 0% | 40.01% | 0% | -12.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 27.2% | 3.07%
CZ 3A | 17.23% | 51.02% | 1.252% | 44.27% | 47.06% | 31.56% | 0% | 37.3% | 0% | 18.95% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 23.63% | 13.3% | CZ 3A | 17.23% | 51.02% | 1.252% | 40.94% | 47.06% | 31.56% | 0% | 37.3% | 0% | 18.95% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 23.89% | 13.3% | CZ 3A | 17.23% | 51.02% | 0% | 47.78% | 47.06% | 31.56% | 0% | 37.3% | 0% | 18.95% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 23.48% | 13.3% | CZ 3A | 0% | 0% | 1.252% | 35.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.91% | 13.3% | CZ 3A | 17.23% | 51.02% | 1.252% | 44.05% | 47.06% | 31.56% | 0% | 37.3% | 0% | 18.95% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 23.65% | 13.3%
CZ 3B | 17.29% | 51.07% | 1.283% | 64.61% | 65.75% | 31.65% | 0% | 38.48% | 0% | 17.34% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 28.89% | 6.287% | CZ 3B | 17.29% | 51.07% | 1.283% | 53.76% | 65.75% | 31.65% | 0% | 38.48% | 0% | 17.34% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 27.76% | 6.287% | CZ 3B | 17.29% | 51.07% | 0% | 73.39% | 65.75% | 31.65% | 0% | 38.48% | 0% | 17.34% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 29.52% | 6.287% | CZ 3B | 0% | 0% | 1.283% | 24.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.16% | 6.287% | CZ 3B | 17.29% | 51.07% | 1.283% | 63.98% | 65.75% | 31.65% | 0% | 38.48% | 0% | 17.34% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.84% | 6.287%
CZ 3C | 17.24% | 51.04% | 1.256% | 67.13% | 80.86% | 44.66% | 0% | 38.72% | 0% | -2.994% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 29.36% | 1.4% | CZ 3C | 17.24% | 51.04% | 1.256% | 56.16% | 80.86% | 44.66% | 0% | 38.72% | 0% | -2.994% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.14% | 1.4% | CZ 3C | 17.24% | 51.04% | 0% | 79.08% | 80.86% | 44.66% | 0% | 38.72% | 0% | -2.994% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 29.49% | 1.4% | CZ 3C | 0% | 0% | 1.256% | 37.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.66% | 1.4% | CZ 3C | 17.24% | 51.04% | 1.256% | 66.4% | 80.86% | 44.66% | 0% | 38.72% | 0% | -2.994% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 29.35% | 1.4%
CZ 4A | 17.64% | 51.01% | 1.213% | 62.89% | 42.03% | 36.28% | 0% | 34.45% | 0% | 19.17% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 28.59% | 18.71% | CZ 4A | 17.64% | 51.01% | 1.213% | 52.59% | 42.03% | 36.28% | 0% | 34.45% | 0% | 19.17% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.04% | 18.71% | CZ 4A | 17.64% | 51.01% | 0% | 72.92% | 42.03% | 36.28% | 0% | 34.45% | 0% | 19.17% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 28.91% | 18.71% | CZ 4A | 0% | 0% | 1.213% | 32.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.08% | 18.71% | CZ 4A | 17.64% | 51.01% | 1.213% | 62.24% | 42.03% | 36.28% | 0% | 34.45% | 0% | 19.17% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.56% | 18.71%
CZ 4B | 17.67% | 51.05% | 1.213% | 65.89% | 65.81% | 33.89% | 0% | 38.55% | 0% | 18.31% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 31.28% | 0.5317% | CZ 4B | 17.67% | 51.05% | 1.213% | 54.87% | 65.81% | 33.89% | 0% | 38.55% | 0% | 18.31% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 29.69% | 0.5317% | CZ 4B | 17.67% | 51.05% | 0% | 74.14% | 65.81% | 33.89% | 0% | 38.55% | 0% | 18.31% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 32.16% | 0.5317% | CZ 4B | 0% | 0% | 1.213% | 19.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.74% | 0.5317% | CZ 4B | 17.67% | 51.05% | 1.213% | 65.27% | 65.81% | 33.89% | 0% | 38.55% | 0% | 18.31% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.21% | 0.5317%
CZ 4C | 17.52% | 50.95% | 1.188% | 67.13% | 66.86% | 36.49% | 0% | 37.28% | 0% | 11.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 29.58% | 4.138% | CZ 4C | 17.52% | 50.95% | 1.188% | 55.17% | 66.86% | 36.49% | 0% | 37.28% | 0% | 11.83% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.91% | 4.138% | CZ 4C | 17.52% | 50.95% | 0% | 79.17% | 66.86% | 36.49% | 0% | 37.28% | 0% | 11.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 30% | 4.138% | CZ 4C | 0% | 0% | 1.188% | 32.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.64% | 4.138% | CZ 4C | 17.52% | 50.95% | 1.188% | 66.36% | 66.86% | 36.49% | 0% | 37.28% | 0% | 11.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 29.55% | 4.138%
CZ 5A | 17.63% | 50.86% | 1.104% | 59.78% | 44.31% | 24.6% | 0% | 35.85% | 0% | 20.78% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 26.84% | 24.21% | CZ 5A | 17.63% | 50.86% | 1.104% | 48.66% | 44.31% | 24.6% | 0% | 35.85% | 0% | 20.78% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 26.1% | 24.21% | CZ 5A | 17.63% | 50.86% | 0% | 70.98% | 44.31% | 24.6% | 0% | 35.85% | 0% | 20.78% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 27.29% | 24.21% | CZ 5A | 0% | 0% | 1.104% | 27.78% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.48% | 24.21% | CZ 5A | 17.63% | 50.86% | 1.104% | 59.07% | 44.31% | 24.6% | 0% | 35.85% | 0% | 20.78% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 26.8% | 24.21%
CZ 5B | 17.51% | 51.09% | 1.189% | 65.28% | 69.25% | 34.43% | 0% | 36.51% | 0% | 20.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 31.59% | 4.982% | CZ 5B | 17.51% | 51.09% | 1.189% | 50.6% | 69.25% | 34.43% | 0% | 36.51% | 0% | 20.15% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.96% | 4.982% | CZ 5B | 17.51% | 51.09% | 0% | 76.87% | 69.25% | 34.43% | 0% | 36.51% | 0% | 20.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 33.1% | 4.982% | CZ 5B | 0% | 0% | 1.189% | 8.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.84% | 4.982% | CZ 5B | 17.51% | 51.09% | 1.189% | 64.44% | 69.25% | 34.43% | 0% | 36.51% | 0% | 20.15% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.46% | 4.982%
CZ 5C | 17.18% | 50.85% | 1.162% | 65.81% | 65.46% | 37.59% | 0% | 34.24% | 0% | 14.07% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 29% | 0% | CZ 5C | 17.18% | 50.85% | 1.162% | 52.16% | 65.46% | 37.59% | 0% | 34.24% | 0% | 14.07% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 27.57% | 0% | CZ 5C | 17.18% | 50.85% | 0% | 78.94% | 65.46% | 37.59% | 0% | 34.24% | 0% | 14.07% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 29.87% | 0% | CZ 5C | 0% | 0% | 1.162% | 24.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.35% | 0% | CZ 5C | 17.18% | 50.85% | 1.162% | 64.95% | 65.46% | 37.59% | 0% | 34.24% | 0% | 14.07% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 28.93% | 0%
CZ 6A | 17.57% | 50.81% | 1.131% | 60.53% | 41.07% | 24.67% | 0% | 35.99% | 0% | 18.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 27.89% | 7.834% | CZ 6A | 17.57% | 50.81% | 1.131% | 50.02% | 41.07% | 24.67% | 0% | 35.99% | 0% | 18.1% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 27.43% | 7.834% | CZ 6A | 17.57% | 50.81% | 0% | 71.51% | 41.07% | 24.67% | 0% | 35.99% | 0% | 18.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 28.19% | 7.834% | CZ 6A | 0% | 0% | 1.131% | 31.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.85% | 7.834% | CZ 6A | 17.57% | 50.81% | 1.131% | 59.84% | 41.07% | 24.67% | 0% | 35.99% | 0% | 18.1% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 27.87% | 7.834%
CZ 6B | 17.54% | 51% | 1.117% | 62.68% | 65.19% | 37.18% | 0% | 37.08% | 0% | 19.2% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 32.71% | 0.7615% | CZ 6B | 17.54% | 51% | 1.117% | 48.64% | 65.19% | 37.18% | 0% | 37.08% | 0% | 19.2% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 30.06% | 0.7615% | CZ 6B | 17.54% | 51% | 0% | 74.67% | 65.19% | 37.18% | 0% | 37.08% | 0% | 19.2% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 34.27% | 0.7615% | CZ 6B | 0% | 0% | 1.117% | 14.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.37% | 0.7615% | CZ 6B | 17.54% | 51% | 1.117% | 61.85% | 65.19% | 37.18% | 0% | 37.08% | 0% | 19.2% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 32.58% | 0.7615%
CZ 7 | 17.85% | 50.88% | 1.075% | 61.44% | 44.34% | 22.25% | 0% | 35.77% | 0% | 17.57% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 29.5% | 0.8914% | CZ 7 | 17.85% | 50.88% | 1.075% | 50.22% | 44.34% | 22.25% | 0% | 35.77% | 0% | 17.57% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.86% | 0.8914% | CZ 7 | 17.85% | 50.88% | 0% | 73.72% | 44.34% | 22.25% | 0% | 35.77% | 0% | 17.57% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 29.91% | 0.8914% | CZ 7 | 0% | 0% | 1.075% | 31.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.74% | 0.8914% | CZ 7 | 17.85% | 50.88% | 1.075% | 60.69% | 44.34% | 22.25% | 0% | 35.77% | 0% | 17.57% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 29.47% | 0.8914%
CZ 8 | 17.28% | 50.33% | 1.024% | 54.53% | 37.94% | 22.93% | 0% | 36.42% | 0% | 17.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 29.76% | 0.0471% | CZ 8 | 17.28% | 50.33% | 1.024% | 42.98% | 37.94% | 22.93% | 0% | 36.42% | 0% | 17.26% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 28.32% | 0.0471% | CZ 8 | 17.28% | 50.33% | 0% | 68.91% | 37.94% | 22.93% | 0% | 36.42% | 0% | 17.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 30.79% | 0.0471% | CZ 8 | 0% | 0% | 1.024% | 26.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.92% | 0.0471% | CZ 8 | 17.28% | 50.33% | 1.024% | 53.71% | 37.94% | 22.93% | 0% | 36.42% | 0% | 17.26% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 29.69% | 0.0471%
Us Weighted | 17.48% | 50.97% | 1.211% | 58.6% | 50.13% | 30.96% | 0% | 36.9% | 0% | 17.69% | 0% | 1.955% | 0% | 0% | 0% | 0.9072% | 26.98% | 100% | Us Weighted | 17.48% | 50.97% | 1.211% | 48.91% | 50.13% | 30.96% | 0% | 36.9% | 0% | 17.69% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 26.46% | 100% | Us Weighted | 17.48% | 50.97% | 0% | 68.23% | 50.13% | 30.96% | 0% | 36.9% | 0% | 17.69% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 27.29% | 100% | Us Weighted | 0% | 0% | 1.211% | 30.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.71% | 100% | Us Weighted | 17.48% | 50.97% | 1.211% | 57.98% | 50.13% | 30.96% | 0% | 36.9% | 0% | 17.69% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 26.96% | 100%

## FastFood
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Quick-service Restaurant | [14 empty] | Prototype Floor Area: | 2501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.37087 | 0.17694 | 0.67271 | 1.3731 | 0 | 0.75108 | 0 | 0.76157 | 0 | 0 | 0.97705 | 0 | 0 | 4.4699 | 0 | 0 | 9.5532 |  | STD2013 | 12.2652 | 5.8516 | 67.9503 | 138.6935 | 0 | 24.8391 | 0 | 25.1861 | 0 | 0 | 32.3126 | 0 | 0 | 269.4851 | 0 | 0 | 576.5835 |  | STD2013 | 3.5937 | 1.7145 | 0 | 0 | 0 | 7.2778 | 0 | 7.3794 | 0 | 0 | 9.4675 | 0 | 0 | 25.9618 | 0 | 0 | 55.3948 |  | STD2013 | 0 | 0 | 0.6795 | 1.3869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8752 |  | STD2013 | 37.6222 | 17.9492 | 74.2696 | 151.592 | 0 | 76.1913 | 0 | 77.2554 | 0 | 0 | 99.1152 | 0 | 0 | 469.4934 | 0 | 0 | 1003.4884
STD2010 | 0.39978 | 0.17694 | 0.67258 | 1.3824 | 0 | 0.81682 | 0 | 1.2195 | 0 | 0 | 1.2409 | 0 | 0 | 4.4699 | 0 | 0 | 10.3789 |  | STD2010 | 13.2212 | 5.8516 | 67.9375 | 139.6318 | 0 | 27.0133 | 0 | 40.3311 | 0 | 0 | 41.0395 | 0 | 0 | 269.4851 | 0 | 0 | 604.5111 |  | STD2010 | 3.8738 | 1.7145 | 0 | 0 | 0 | 7.9148 | 0 | 11.8169 | 0 | 0 | 12.0245 | 0 | 0 | 25.9618 | 0 | 0 | 63.3063 |  | STD2010 | 0 | 0 | 0.67938 | 1.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8845 |  | STD2010 | 40.5545 | 17.9492 | 74.2557 | 152.6176 | 0 | 82.8602 | 0 | 123.7111 | 0 | 0 | 125.8842 | 0 | 0 | 469.4934 | 0 | 0 | 1087.3259
STD2007 | 0.86057 | 0.31396 | 0.67256 | 1.3297 | 0 | 1.1327 | 0 | 1.5582 | 0 | 0 | 1.2415 | 0 | 0 | 4.4699 | 0 | 0 | 11.5792 |  | STD2007 | 28.4604 | 10.3832 | 67.9355 | 134.3172 | 0 | 37.461 | 0 | 51.5328 | 0 | 0 | 41.0583 | 0 | 0 | 269.4851 | 0 | 0 | 640.6335 |  | STD2007 | 8.3388 | 3.0422 | 0 | 0 | 0 | 10.976 | 0 | 15.099 | 0 | 0 | 12.03 | 0 | 0 | 25.9618 | 0 | 0 | 75.4478 |  | STD2007 | 0 | 0 | 0.67935 | 1.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8313 |  | STD2007 | 87.299 | 31.8492 | 74.2535 | 146.8087 | 0 | 114.9076 | 0 | 158.0712 | 0 | 0 | 125.9417 | 0 | 0 | 469.4934 | 0 | 0 | 1208.6244
STD2004 | 0.86057 | 0.31396 | 0.67227 | 1.4945 | 0 | 1.106 | 0 | 1.4763 | 0 | 0 | 1.2419 | 0 | 0 | 4.4699 | 0 | 0 | 11.6355 |  | STD2004 | 28.4604 | 10.3832 | 67.9061 | 150.9642 | 0 | 36.5771 | 0 | 48.8229 | 0 | 0 | 41.0722 | 0 | 0 | 269.4851 | 0 | 0 | 653.671 |  | STD2004 | 8.3388 | 3.0422 | 0 | 0 | 0 | 10.717 | 0 | 14.305 | 0 | 0 | 12.034 | 0 | 0 | 25.9618 | 0 | 0 | 74.3989 |  | STD2004 | 0 | 0 | 0.67906 | 1.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.9975 |  | STD2004 | 87.299 | 31.8492 | 74.2213 | 165.0039 | 0 | 112.1961 | 0 | 149.759 | 0 | 0 | 125.9843 | 0 | 0 | 469.4934 | 0 | 0 | 1215.8062
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | -0.00029144 | 0.16481 | 0 | -0.02673 | 0 | -0.08194 | 0 | 0 | 0.0004195 | 0 | 0 | 0 | 0 | 0 | 0.056263 |  | 2004-2007 | 0 | 0 | -0.029439 | 16.647 | 0 | -0.88399 | 0 | -2.7099 | 0 | 0 | 0.013873 | 0 | 0 | 0 | 0 | 0 | 13.0376 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | -0.25901 | 0 | -0.79399 | 0 | 0 | 0.0040649 | 0 | 0 | 0 | 0 | 0 | -1.0489 |  | 2004-2007 | 0 | 0 | -0.00029439 | 0.16647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16618 |  | 2004-2007 | 0 | 0 | -0.032176 | 18.1952 | 0 | -2.7115 | 0 | -8.3123 | 0 | 0 | 0.042555 | 0 | 0 | 0 | 0 | 0 | 7.1818
2007-2010 | 0.4608 | 0.13702 | -2.0083e-05 | -0.052615 | 0 | 0.31592 | 0 | 0.33871 | 0 | 0 | 0.00056712 | 0 | 0 | 0 | 0 | 0 | 1.2004 |  | 2007-2010 | 15.2392 | 4.5316 | -0.0020285 | -5.3146 | 0 | 10.4478 | 0 | 11.2017 | 0 | 0 | 0.018755 | 0 | 0 | 0 | 0 | 0 | 36.1224 |  | 2007-2010 | 4.465 | 1.3277 | 0 | 0 | 0 | 3.0612 | 0 | 3.2821 | 0 | 0 | 0.0054953 | 0 | 0 | 0 | 0 | 0 | 12.1415 |  | 2007-2010 | 0 | 0 | -2.0285e-05 | -0.053146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.053167 |  | 2007-2010 | 46.7445 | 13.9001 | -0.0022172 | -5.8089 | 0 | 32.0474 | 0 | 34.3601 | 0 | 0 | 0.05753 | 0 | 0 | 0 | 0 | 0 | 121.2985
2010-2013 | 0.028906 | 0 | -0.00012616 | 0.0092893 | 0 | 0.06574 | 0 | 0.45795 | 0 | 0 | 0.26388 | 0 | 0 | 0 | 0 | 0 | 0.82564 |  | 2010-2013 | 0.95595 | 0 | -0.012743 | 0.93831 | 0 | 2.1741 | 0 | 15.145 | 0 | 0 | 8.727 | 0 | 0 | 0 | 0 | 0 | 27.9276 |  | 2010-2013 | 0.28009 | 0 | 0 | 0 | 0 | 0.63701 | 0 | 4.4375 | 0 | 0 | 2.557 | 0 | 0 | 0 | 0 | 0 | 7.9115 |  | 2010-2013 | 0 | 0 | -0.00012743 | 0.0093831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092557 |  | 2010-2013 | 2.9323 | 0 | -0.013928 | 1.0256 | 0 | 6.6688 | 0 | 46.4557 | 0 | 0 | 26.769 | 0 | 0 | 0 | 0 | 0 | 83.8375
2004-2013 | 0.4897 | 0.13702 | -0.00043768 | 0.12148 | 0 | 0.35493 | 0 | 0.71472 | 0 | 0 | 0.26487 | 0 | 0 | 0 | 0 | 0 | 2.0823 |  | 2004-2013 | 16.1951 | 4.5316 | -0.04421 | 12.2707 | 0 | 11.7379 | 0 | 23.6369 | 0 | 0 | 8.7596 | 0 | 0 | 0 | 0 | 0 | 77.0876 |  | 2004-2013 | 4.7451 | 1.3277 | 0 | 0 | 0 | 3.4392 | 0 | 6.9255 | 0 | 0 | 2.5665 | 0 | 0 | 0 | 0 | 0 | 19.0041 |  | 2004-2013 | 0 | 0 | -0.0004421 | 0.12271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12226 |  | 2004-2013 | 49.6768 | 13.9001 | -0.048322 | 13.4118 | 0 | 36.0047 | 0 | 72.5035 | 0 | 0 | 26.8691 | 0 | 0 | 0 | 0 | 0 | 212.3177
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | -0.04335% | 11.03% |  | -2.417% |  | -5.55% |  |  | 0.03378% |  |  | 0% |  |  | 0.4835% |  | 2004-2007 | 0% | 0% | -0.04335% | 11.03% |  | -2.417% |  | -5.55% |  |  | 0.03378% |  |  | 0% |  |  | 1.995% |  | 2004-2007 | 0% | 0% |  |  |  | -2.417% |  | -5.55% |  |  | 0.03378% |  |  | 0% |  |  | -1.41% |  | 2004-2007 |  |  | -0.04335% | 11.03% | [9 empty] | 0% |  |  | 4.157% |  | 2004-2007 | 0% | 0% | -0.04335% | 11.03% |  | -2.417% |  | -5.55% |  |  | 0.03378% |  |  | 0% |  |  | 0.5907%
2007-2010 | 53.55% | 43.64% | -0.002986% | -3.957% |  | 27.89% |  | 21.74% |  |  | 0.04568% |  |  | 0% |  |  | 10.37% |  | 2007-2010 | 53.55% | 43.64% | -0.002986% | -3.957% |  | 27.89% |  | 21.74% |  |  | 0.04568% |  |  | 0% |  |  | 5.639% |  | 2007-2010 | 53.55% | 43.64% |  |  |  | 27.89% |  | 21.74% |  |  | 0.04568% |  |  | 0% |  |  | 16.09% |  | 2007-2010 |  |  | -0.002986% | -3.957% | [9 empty] | 0% |  |  | -1.388% |  | 2007-2010 | 53.55% | 43.64% | -0.002986% | -3.957% |  | 27.89% |  | 21.74% |  |  | 0.04568% |  |  | 0% |  |  | 10.04%
2010-2013 | 7.23% | 0% | -0.01876% | 0.672% |  | 8.048% |  | 37.55% |  |  | 21.26% |  |  | 0% |  |  | 7.955% |  | 2010-2013 | 7.23% | 0% | -0.01876% | 0.672% |  | 8.048% |  | 37.55% |  |  | 21.26% |  |  | 0% |  |  | 4.62% |  | 2010-2013 | 7.23% | 0% |  |  |  | 8.048% |  | 37.55% |  |  | 21.26% |  |  | 0% |  |  | 12.5% |  | 2010-2013 |  |  | -0.01876% | 0.672% | [9 empty] | 0% |  |  | 0.2383% |  | 2010-2013 | 7.23% | 0% | -0.01876% | 0.672% |  | 8.048% |  | 37.55% |  |  | 21.26% |  |  | 0% |  |  | 7.71%
2004-2013 | 56.9% | 43.64% | -0.0651% | 8.128% |  | 32.09% |  | 48.41% |  |  | 21.33% |  |  | 0% |  |  | 17.9% |  | 2004-2013 | 56.9% | 43.64% | -0.0651% | 8.128% |  | 32.09% |  | 48.41% |  |  | 21.33% |  |  | 0% |  |  | 11.79% |  | 2004-2013 | 56.9% | 43.64% |  |  |  | 32.09% |  | 48.41% |  |  | 21.33% |  |  | 0% |  |  | 25.54% |  | 2004-2013 |  |  | -0.0651% | 8.128% | [9 empty] | 0% |  |  | 3.059% |  | 2004-2013 | 56.9% | 43.64% | -0.0651% | 8.128% |  | 32.09% |  | 48.41% |  |  | 21.33% |  |  | 0% |  |  | 17.46%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.37011 | 0.17686 | 0.51884 | 0.18054 | 0 | 1.9324 | 0 | 0.91811 | 0 | 0 | 1.0163 | 0 | 0 | 4.4699 | 0 | 0 | 9.5831 | 1.331% | CZ 1A | 12.2401 | 5.849 | 52.4085 | 18.2363 | 0 | 63.9069 | 0 | 30.3633 | 0 | 0 | 33.612 | 0 | 0 | 269.4851 | 0 | 0 | 486.1011 | 1.331% | CZ 1A | 3.5863 | 1.7137 | 0 | 0 | 0 | 18.7246 | 0 | 8.8964 | 0 | 0 | 9.8482 | 0 | 0 | 25.9618 | 0 | 0 | 68.731 | 1.331% | CZ 1A | 0 | 0 | 0.52408 | 0.18236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.5152 | 1.331% | CZ 1A | 37.5451 | 17.9412 | 57.2825 | 19.9323 | 0 | 196.0274 | 0 | 93.136 | 0 | 0 | 103.1011 | 0 | 0 | 469.4934 | 0 | 0 | 994.4589 | 1.331%
CZ 1B | 0.37045 | 0.17675 | 0.49074 | 0.28435 | 0 | 1.9076 | 0 | 1.1257 | 0 | 0 | 0.99663 | 0 | 0 | 4.4699 | 0 | 0 | 9.8222 | 0% | CZ 1B | 12.2515 | 5.8452 | 49.57 | 28.7225 | 0 | 63.0881 | 0 | 37.2282 | 0 | 0 | 32.96 | 0 | 0 | 269.4851 | 0 | 0 | 499.1506 | 0% | CZ 1B | 3.5896 | 1.7126 | 0 | 0 | 0 | 18.4847 | 0 | 10.9078 | 0 | 0 | 9.6572 | 0 | 0 | 25.9618 | 0 | 0 | 70.3137 | 0% | CZ 1B | 0 | 0 | 0.4957 | 0.28723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.5917 | 0% | CZ 1B | 37.58 | 17.9296 | 54.18 | 31.3937 | 0 | 193.5159 | 0 | 114.1933 | 0 | 0 | 101.1012 | 0 | 0 | 469.4934 | 0 | 0 | 1019.387 | 0%
CZ 2A | 0.37103 | 0.17675 | 0.58551 | 0.64539 | 0 | 1.3799 | 0 | 0.86103 | 0 | 0 | 0.99823 | 0 | 0 | 4.4699 | 0 | 0 | 9.4878 | 15.62% | CZ 2A | 12.2704 | 5.8452 | 59.1429 | 65.1913 | 0 | 45.6359 | 0 | 28.4755 | 0 | 0 | 33.0131 | 0 | 0 | 269.4851 | 0 | 0 | 519.0594 | 15.62% | CZ 2A | 3.5952 | 1.7126 | 0 | 0 | 0 | 13.3712 | 0 | 8.3433 | 0 | 0 | 9.6727 | 0 | 0 | 25.9618 | 0 | 0 | 62.6569 | 15.62% | CZ 2A | 0 | 0 | 0.59143 | 0.65191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.0521 | 15.62% | CZ 2A | 37.6381 | 17.9296 | 64.6432 | 71.2541 | 0 | 139.9831 | 0 | 87.3455 | 0 | 0 | 101.2639 | 0 | 0 | 469.4934 | 0 | 0 | 989.5509 | 15.62%
CZ 2B | 0.36747 | 0.17675 | 0.54706 | 0.44339 | 0 | 1.6062 | 0 | 1.0458 | 0 | 0 | 0.99273 | 0 | 0 | 4.4699 | 0 | 0 | 9.6493 | 3.461% | CZ 2B | 12.1529 | 5.8452 | 55.2584 | 44.7873 | 0 | 53.1187 | 0 | 34.5861 | 0 | 0 | 32.8311 | 0 | 0 | 269.4851 | 0 | 0 | 508.0647 | 3.461% | CZ 2B | 3.5608 | 1.7126 | 0 | 0 | 0 | 15.5636 | 0 | 10.1336 | 0 | 0 | 9.6194 | 0 | 0 | 25.9618 | 0 | 0 | 66.5519 | 3.461% | CZ 2B | 0 | 0 | 0.55258 | 0.44787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.8092 | 3.461% | CZ 2B | 37.2777 | 17.9296 | 60.3974 | 48.9525 | 0 | 162.9357 | 0 | 106.089 | 0 | 0 | 100.7058 | 0 | 0 | 469.4934 | 0 | 0 | 1003.781 | 3.461%
CZ 3A | 0.37343 | 0.17686 | 0.63774 | 1.1435 | 0 | 0.97657 | 0 | 0.80899 | 0 | 0 | 0.98299 | 0 | 0 | 4.4699 | 0 | 0 | 9.5701 | 17.35% | CZ 3A | 12.35 | 5.849 | 64.4182 | 115.5079 | 0 | 32.2965 | 0 | 26.7546 | 0 | 0 | 32.5089 | 0 | 0 | 269.4851 | 0 | 0 | 559.1702 | 17.35% | CZ 3A | 3.6185 | 1.7137 | 0 | 0 | 0 | 9.4628 | 0 | 7.839 | 0 | 0 | 9.525 | 0 | 0 | 25.9618 | 0 | 0 | 58.1209 | 17.35% | CZ 3A | 0 | 0 | 0.64418 | 1.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.608 | 17.35% | CZ 3A | 37.8823 | 17.9412 | 70.4091 | 126.2501 | 0 | 99.066 | 0 | 82.0667 | 0 | 0 | 99.7175 | 0 | 0 | 469.4934 | 0 | 0 | 1002.8262 | 17.35%
CZ 3B | 0.36988 | 0.17675 | 0.62041 | 0.77307 | 0 | 0.77541 | 0 | 0.8741 | 0 | 0 | 0.9823 | 0 | 0 | 4.4699 | 0 | 0 | 9.0419 | 10.77% | CZ 3B | 12.2325 | 5.8452 | 62.6673 | 78.0879 | 0 | 25.6439 | 0 | 28.9077 | 0 | 0 | 32.4862 | 0 | 0 | 269.4851 | 0 | 0 | 515.3557 | 10.77% | CZ 3B | 3.5841 | 1.7126 | 0 | 0 | 0 | 7.5136 | 0 | 8.4699 | 0 | 0 | 9.5184 | 0 | 0 | 25.9618 | 0 | 0 | 56.7604 | 10.77% | CZ 3B | 0 | 0 | 0.62667 | 0.78088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.2163 | 10.77% | CZ 3B | 37.5218 | 17.9296 | 68.4954 | 85.35 | 0 | 78.6598 | 0 | 88.6711 | 0 | 0 | 99.6477 | 0 | 0 | 469.4934 | 0 | 0 | 945.7688 | 10.77%
CZ 3C | 0.37172 | 0.17675 | 0.69409 | 1.0574 | 0 | 0.046078 | 0 | 0.76693 | 0 | 0 | 0.97233 | 0 | 0 | 4.4699 | 0 | 0 | 8.5552 | 1.179% | CZ 3C | 12.2931 | 5.8452 | 70.1104 | 106.8066 | 0 | 1.5238 | 0 | 25.3634 | 0 | 0 | 32.1564 | 0 | 0 | 269.4851 | 0 | 0 | 523.5841 | 1.179% | CZ 3C | 3.6019 | 1.7126 | 0 | 0 | 0 | 0.44648 | 0 | 7.4314 | 0 | 0 | 9.4217 | 0 | 0 | 25.9618 | 0 | 0 | 48.576 | 1.179% | CZ 3C | 0 | 0 | 0.7011 | 1.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.5779 | 1.179% | CZ 3C | 37.7079 | 17.9296 | 76.6307 | 116.7396 | 0 | 4.6742 | 0 | 77.7994 | 0 | 0 | 98.6361 | 0 | 0 | 469.4934 | 0 | 0 | 899.6109 | 1.179%
CZ 4A | 0.36954 | 0.17675 | 0.70152 | 1.5299 | 0 | 0.53677 | 0 | 0.6828 | 0 | 0 | 0.97107 | 0 | 0 | 4.4699 | 0 | 0 | 9.4383 | 15.17% | CZ 4A | 12.2211 | 5.8452 | 70.8608 | 154.5347 | 0 | 17.7517 | 0 | 22.581 | 0 | 0 | 32.1147 | 0 | 0 | 269.4851 | 0 | 0 | 585.3944 | 15.17% | CZ 4A | 3.5808 | 1.7126 | 0 | 0 | 0 | 5.2012 | 0 | 6.6162 | 0 | 0 | 9.4095 | 0 | 0 | 25.9618 | 0 | 0 | 52.4821 | 15.17% | CZ 4A | 0 | 0 | 0.70861 | 1.5453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.0627 | 15.17% | CZ 4A | 37.4869 | 17.9296 | 77.4508 | 168.9065 | 0 | 54.4514 | 0 | 69.2648 | 0 | 0 | 98.5082 | 0 | 0 | 469.4934 | 0 | 0 | 993.4917 | 15.17%
CZ 4B | 0.36782 | 0.17663 | 0.69143 | 1.1039 | 0 | 0.42478 | 0 | 0.72119 | 0 | 0 | 0.97302 | 0 | 0 | 4.4699 | 0 | 0 | 8.9288 | 0.908% | CZ 4B | 12.1643 | 5.8414 | 69.8414 | 111.5097 | 0 | 14.0482 | 0 | 23.8509 | 0 | 0 | 32.1791 | 0 | 0 | 269.4851 | 0 | 0 | 538.9201 | 0.908% | CZ 4B | 3.5641 | 1.7115 | 0 | 0 | 0 | 4.1161 | 0 | 6.9883 | 0 | 0 | 9.4284 | 0 | 0 | 25.9618 | 0 | 0 | 51.7702 | 0.908% | CZ 4B | 0 | 0 | 0.69841 | 1.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6223 | 0.908% | CZ 4B | 37.3125 | 17.9179 | 76.3366 | 121.8801 | 0 | 43.0914 | 0 | 73.16 | 0 | 0 | 98.7059 | 0 | 0 | 469.4934 | 0 | 0 | 937.8978 | 0.908%
CZ 4C | 0.37126 | 0.17697 | 0.72869 | 1.4779 | 0 | 0.19382 | 0 | 0.61953 | 0 | 0 | 0.96339 | 0 | 0 | 4.4699 | 0 | 0 | 9.0015 | 2.44% | CZ 4C | 12.278 | 5.8528 | 73.6046 | 149.2859 | 0 | 6.41 | 0 | 20.4886 | 0 | 0 | 31.8607 | 0 | 0 | 269.4851 | 0 | 0 | 569.2657 | 2.44% | CZ 4C | 3.5974 | 1.7149 | 0 | 0 | 0 | 1.8781 | 0 | 6.0031 | 0 | 0 | 9.3351 | 0 | 0 | 25.9618 | 0 | 0 | 48.4904 | 2.44% | CZ 4C | 0 | 0 | 0.73605 | 1.4929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.0377 | 2.44% | CZ 4C | 37.6614 | 17.9528 | 80.4498 | 163.1695 | 0 | 19.662 | 0 | 62.8465 | 0 | 0 | 97.7292 | 0 | 0 | 469.4934 | 0 | 0 | 948.9646 | 2.44%
CZ 5A | 0.37126 | 0.17743 | 0.74594 | 2.1428 | 0 | 0.39601 | 0 | 0.664 | 0 | 0 | 0.96419 | 0 | 0 | 4.4699 | 0 | 0 | 9.9316 | 21.9% | CZ 5A | 12.278 | 5.868 | 75.3479 | 216.4479 | 0 | 13.0968 | 0 | 21.9594 | 0 | 0 | 31.8872 | 0 | 0 | 269.4851 | 0 | 0 | 646.3702 | 21.9% | CZ 5A | 3.5974 | 1.7193 | 0 | 0 | 0 | 3.8373 | 0 | 6.434 | 0 | 0 | 9.3429 | 0 | 0 | 25.9618 | 0 | 0 | 50.8928 | 21.9% | CZ 5A | 0 | 0 | 0.75348 | 2.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.7267 | 21.9% | CZ 5A | 37.6614 | 17.9993 | 82.3552 | 236.5776 | 0 | 40.1729 | 0 | 67.3579 | 0 | 0 | 97.8106 | 0 | 0 | 469.4934 | 0 | 0 | 1049.4283 | 21.9%
CZ 5B | 0.36793 | 0.17629 | 0.73795 | 1.6414 | 0 | 0.30501 | 0 | 0.68761 | 0 | 0 | 0.96178 | 0 | 0 | 4.4699 | 0 | 0 | 9.348 | 4.373% | CZ 5B | 12.1681 | 5.8301 | 74.5406 | 165.8017 | 0 | 10.087 | 0 | 22.7402 | 0 | 0 | 31.8076 | 0 | 0 | 269.4851 | 0 | 0 | 592.4604 | 4.373% | CZ 5B | 3.5652 | 1.7082 | 0 | 0 | 0 | 2.9555 | 0 | 6.6628 | 0 | 0 | 9.3196 | 0 | 0 | 25.9618 | 0 | 0 | 50.1731 | 4.373% | CZ 5B | 0 | 0 | 0.74541 | 1.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.2122 | 4.373% | CZ 5B | 37.3242 | 17.883 | 81.4729 | 181.2212 | 0 | 30.9407 | 0 | 69.7532 | 0 | 0 | 97.5664 | 0 | 0 | 469.4934 | 0 | 0 | 985.655 | 4.373%
CZ 5C | 0.37859 | 0.1772 | 0.74722 | 1.753 | 0 | 0.032438 | 0 | 0.52152 | 0 | 0 | 0.95582 | 0 | 0 | 4.4699 | 0 | 0 | 9.0357 | 0% | CZ 5C | 12.5206 | 5.8604 | 75.4767 | 177.0686 | 0 | 1.0728 | 0 | 17.2476 | 0 | 0 | 31.6105 | 0 | 0 | 269.4851 | 0 | 0 | 590.3422 | 0% | CZ 5C | 3.6685 | 1.7171 | 0 | 0 | 0 | 0.31432 | 0 | 5.0535 | 0 | 0 | 9.2618 | 0 | 0 | 25.9618 | 0 | 0 | 45.977 | 0% | CZ 5C | 0 | 0 | 0.75477 | 1.7707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.3342 | 0% | CZ 5C | 38.4055 | 17.9761 | 82.496 | 193.536 | 0 | 3.2906 | 0 | 52.905 | 0 | 0 | 96.9618 | 0 | 0 | 469.4934 | 0 | 0 | 955.0643 | 0%
CZ 6A | 0.37206 | 0.17755 | 0.78545 | 2.5007 | 0 | 0.21044 | 0 | 0.62457 | 0 | 0 | 0.95697 | 0 | 0 | 4.4699 | 0 | 0 | 10.0977 | 4.324% | CZ 6A | 12.3045 | 5.8718 | 79.3385 | 252.5984 | 0 | 6.9597 | 0 | 20.6554 | 0 | 0 | 31.6484 | 0 | 0 | 269.4851 | 0 | 0 | 678.8617 | 4.324% | CZ 6A | 3.6052 | 1.7204 | 0 | 0 | 0 | 2.0392 | 0 | 6.052 | 0 | 0 | 9.2729 | 0 | 0 | 25.9618 | 0 | 0 | 48.6515 | 4.324% | CZ 6A | 0 | 0 | 0.79338 | 2.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.1281 | 4.324% | CZ 6A | 37.7428 | 18.0109 | 86.7169 | 276.09 | 0 | 21.348 | 0 | 63.3581 | 0 | 0 | 97.0781 | 0 | 0 | 469.4934 | 0 | 0 | 1069.8382 | 4.324%
CZ 6B | 0.36816 | 0.17663 | 0.79089 | 2.2229 | 0 | 0.16437 | 0 | 0.65804 | 0 | 0 | 0.95617 | 0 | 0 | 4.4699 | 0 | 0 | 9.8071 | 0.5275% | CZ 6B | 12.1756 | 5.8414 | 79.888 | 224.5353 | 0 | 5.4358 | 0 | 21.7622 | 0 | 0 | 31.6219 | 0 | 0 | 269.4851 | 0 | 0 | 650.7453 | 0.5275% | CZ 6B | 3.5674 | 1.7115 | 0 | 0 | 0 | 1.5927 | 0 | 6.3763 | 0 | 0 | 9.2651 | 0 | 0 | 25.9618 | 0 | 0 | 48.4749 | 0.5275% | CZ 6B | 0 | 0 | 0.79888 | 2.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.853 | 0.5275% | CZ 6B | 37.3474 | 17.9179 | 87.3176 | 245.417 | 0 | 16.6738 | 0 | 66.7533 | 0 | 0 | 96.9967 | 0 | 0 | 469.4934 | 0 | 0 | 1037.9171 | 0.5275%
CZ 7 | 0.3677 | 0.17709 | 0.84766 | 3.1931 | 0 | 0.11439 | 0 | 0.60669 | 0 | 0 | 0.95089 | 0 | 0 | 4.4699 | 0 | 0 | 10.7275 | 0.6086% | CZ 7 | 12.1605 | 5.8566 | 85.6219 | 322.5345 | 0 | 3.7831 | 0 | 20.064 | 0 | 0 | 31.4475 | 0 | 0 | 269.4851 | 0 | 0 | 750.9531 | 0.6086% | CZ 7 | 3.563 | 1.716 | 0 | 0 | 0 | 1.1084 | 0 | 5.8787 | 0 | 0 | 9.214 | 0 | 0 | 25.9618 | 0 | 0 | 47.442 | 0.6086% | CZ 7 | 0 | 0 | 0.85622 | 3.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.8903 | 0.6086% | CZ 7 | 37.3009 | 17.9644 | 93.5847 | 352.5302 | 0 | 11.6042 | 0 | 61.5442 | 0 | 0 | 96.4618 | 0 | 0 | 469.4934 | 0 | 0 | 1140.4838 | 0.6086%
CZ 8 | 0.37573 | 0.17835 | 0.92438 | 4.7177 | 0 | 0.038169 | 0 | 0.59259 | 0 | 0 | 0.94184 | 0 | 0 | 4.4699 | 0 | 0 | 12.2387 | 0.03762% | CZ 8 | 12.4258 | 5.8983 | 93.3719 | 476.5311 | 0 | 1.2623 | 0 | 19.5978 | 0 | 0 | 31.1481 | 0 | 0 | 269.4851 | 0 | 0 | 909.7203 | 0.03762% | CZ 8 | 3.6407 | 1.7282 | 0 | 0 | 0 | 0.36985 | 0 | 5.7421 | 0 | 0 | 9.1263 | 0 | 0 | 25.9618 | 0 | 0 | 46.569 | 0.03762% | CZ 8 | 0 | 0 | 0.93372 | 4.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 7.5078 | 0.03762% | CZ 8 | 38.1148 | 18.0923 | 102.0555 | 520.8485 | 0 | 3.8719 | 0 | 60.114 | 0 | 0 | 95.5432 | 0 | 0 | 469.4934 | 0 | 0 | 1308.1337 | 0.03762%
Us Weighted | 0.37087 | 0.17694 | 0.67271 | 1.3731 | 0 | 0.75108 | 0 | 0.76157 | 0 | 0 | 0.97705 | 0 | 0 | 4.4699 | 0 | 0 | 9.5532 | 100% | Us Weighted | 12.2652 | 5.8516 | 67.9503 | 138.6935 | 0 | 24.8391 | 0 | 25.1861 | 0 | 0 | 32.3126 | 0 | 0 | 269.4851 | 0 | 0 | 576.5835 | 100% | Us Weighted | 3.5937 | 1.7145 | 0 | 0 | 0 | 7.2778 | 0 | 7.3794 | 0 | 0 | 9.4675 | 0 | 0 | 25.9618 | 0 | 0 | 55.3948 | 100% | Us Weighted | 0 | 0 | 0.6795 | 1.3869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8752 | 100% | Us Weighted | 37.6222 | 17.9492 | 74.2696 | 151.592 | 0 | 76.1913 | 0 | 77.2554 | 0 | 0 | 99.1152 | 0 | 0 | 469.4934 | 0 | 0 | 1003.4884 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.40415 | 0.17686 | 0.51907 | 0.15626 | 0 | 2.1368 | 0 | 1.3235 | 0 | 0 | 1.2746 | 0 | 0 | 4.4699 | 0 | 0 | 10.4612 | 1.331% | CZ 1A | 13.3659 | 5.849 | 52.4312 | 15.7843 | 0 | 70.6657 | 0 | 43.7709 | 0 | 0 | 42.1524 | 0 | 0 | 269.4851 | 0 | 0 | 513.5045 | 1.331% | CZ 1A | 3.9162 | 1.7137 | 0 | 0 | 0 | 20.7049 | 0 | 12.8248 | 0 | 0 | 12.3505 | 0 | 0 | 25.9618 | 0 | 0 | 77.4719 | 1.331% | CZ 1A | 0 | 0 | 0.52431 | 0.15784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.4909 | 1.331% | CZ 1A | 40.9984 | 17.9412 | 57.3073 | 17.2523 | 0 | 216.7592 | 0 | 134.2623 | 0 | 0 | 129.2979 | 0 | 0 | 469.4934 | 0 | 0 | 1083.312 | 1.331%
CZ 1B | 0.40656 | 0.17675 | 0.49048 | 0.28304 | 0 | 2.0036 | 0 | 1.513 | 0 | 0 | 1.2608 | 0 | 0 | 4.4699 | 0 | 0 | 10.6042 | 0% | CZ 1B | 13.4455 | 5.8452 | 49.5434 | 28.5899 | 0 | 66.2609 | 0 | 50.0369 | 0 | 0 | 41.6975 | 0 | 0 | 269.4851 | 0 | 0 | 524.9045 | 0% | CZ 1B | 3.9395 | 1.7126 | 0 | 0 | 0 | 19.4143 | 0 | 14.6607 | 0 | 0 | 12.2173 | 0 | 0 | 25.9618 | 0 | 0 | 77.9062 | 0% | CZ 1B | 0 | 0 | 0.49543 | 0.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.5901 | 0% | CZ 1B | 41.2426 | 17.9296 | 54.151 | 31.2488 | 0 | 203.2481 | 0 | 153.4825 | 0 | 0 | 127.9026 | 0 | 0 | 469.4934 | 0 | 0 | 1098.6985 | 0%
CZ 2A | 0.40782 | 0.17675 | 0.58548 | 0.65691 | 0 | 1.5149 | 0 | 1.3004 | 0 | 0 | 1.26 | 0 | 0 | 4.4699 | 0 | 0 | 10.3722 | 15.62% | CZ 2A | 13.4872 | 5.8452 | 59.1391 | 66.3548 | 0 | 50.1013 | 0 | 43.0052 | 0 | 0 | 41.671 | 0 | 0 | 269.4851 | 0 | 0 | 549.0888 | 15.62% | CZ 2A | 3.9517 | 1.7126 | 0 | 0 | 0 | 14.6796 | 0 | 12.6004 | 0 | 0 | 12.2095 | 0 | 0 | 25.9618 | 0 | 0 | 71.1156 | 15.62% | CZ 2A | 0 | 0 | 0.59139 | 0.66355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.0637 | 15.62% | CZ 2A | 41.3705 | 17.9296 | 64.639 | 72.5258 | 0 | 153.6802 | 0 | 131.9136 | 0 | 0 | 127.8212 | 0 | 0 | 469.4934 | 0 | 0 | 1079.3733 | 15.62%
CZ 2B | 0.40484 | 0.17675 | 0.54676 | 0.44433 | 0 | 1.6884 | 0 | 1.4425 | 0 | 0 | 1.2577 | 0 | 0 | 4.4699 | 0 | 0 | 10.4312 | 3.461% | CZ 2B | 13.3887 | 5.8452 | 55.2281 | 44.882 | 0 | 55.8366 | 0 | 47.7056 | 0 | 0 | 41.5952 | 0 | 0 | 269.4851 | 0 | 0 | 533.9664 | 3.461% | CZ 2B | 3.9228 | 1.7126 | 0 | 0 | 0 | 16.36 | 0 | 13.9776 | 0 | 0 | 12.1873 | 0 | 0 | 25.9618 | 0 | 0 | 74.1222 | 3.461% | CZ 2B | 0 | 0 | 0.55228 | 0.44882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.8099 | 3.461% | CZ 2B | 41.0682 | 17.9296 | 60.3643 | 49.0561 | 0 | 171.2726 | 0 | 146.3317 | 0 | 0 | 127.5886 | 0 | 0 | 469.4934 | 0 | 0 | 1083.1044 | 3.461%
CZ 3A | 0.4006 | 0.17686 | 0.63763 | 1.1478 | 0 | 1.0591 | 0 | 1.2411 | 0 | 0 | 1.2466 | 0 | 0 | 4.4699 | 0 | 0 | 10.3796 | 17.35% | CZ 3A | 13.2484 | 5.849 | 64.4068 | 115.9361 | 0 | 35.0258 | 0 | 41.0454 | 0 | 0 | 41.2275 | 0 | 0 | 269.4851 | 0 | 0 | 586.2241 | 17.35% | CZ 3A | 3.8817 | 1.7137 | 0 | 0 | 0 | 10.2625 | 0 | 12.0262 | 0 | 0 | 12.0795 | 0 | 0 | 25.9618 | 0 | 0 | 65.9255 | 17.35% | CZ 3A | 0 | 0 | 0.64407 | 1.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6122 | 17.35% | CZ 3A | 40.638 | 17.9412 | 70.3967 | 126.7182 | 0 | 107.4378 | 0 | 125.9022 | 0 | 0 | 126.4608 | 0 | 0 | 469.4934 | 0 | 0 | 1084.9882 | 17.35%
CZ 3B | 0.39762 | 0.17675 | 0.62007 | 0.77735 | 0 | 0.82527 | 0 | 1.2866 | 0 | 0 | 1.2484 | 0 | 0 | 4.4699 | 0 | 0 | 9.8021 | 10.77% | CZ 3B | 13.1498 | 5.8452 | 62.6332 | 78.5199 | 0 | 27.2928 | 0 | 42.5503 | 0 | 0 | 41.2881 | 0 | 0 | 269.4851 | 0 | 0 | 540.7645 | 10.77% | CZ 3B | 3.8529 | 1.7126 | 0 | 0 | 0 | 7.9967 | 0 | 12.4671 | 0 | 0 | 12.0973 | 0 | 0 | 25.9618 | 0 | 0 | 64.0885 | 10.77% | CZ 3B | 0 | 0 | 0.62633 | 0.7852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.2203 | 10.77% | CZ 3B | 40.3357 | 17.9296 | 68.4581 | 85.8222 | 0 | 83.7178 | 0 | 130.5183 | 0 | 0 | 126.6468 | 0 | 0 | 469.4934 | 0 | 0 | 1022.9219 | 10.77%
CZ 3C | 0.39922 | 0.17675 | 0.69387 | 1.0995 | 0 | 0.059374 | 0 | 1.2894 | 0 | 0 | 1.2379 | 0 | 0 | 4.4699 | 0 | 0 | 9.426 | 1.179% | CZ 3C | 13.2029 | 5.8452 | 70.0877 | 111.0625 | 0 | 1.9636 | 0 | 42.6413 | 0 | 0 | 40.9394 | 0 | 0 | 269.4851 | 0 | 0 | 555.2276 | 1.179% | CZ 3C | 3.8684 | 1.7126 | 0 | 0 | 0 | 0.57532 | 0 | 12.4938 | 0 | 0 | 11.9951 | 0 | 0 | 25.9618 | 0 | 0 | 56.6071 | 1.179% | CZ 3C | 0 | 0 | 0.70088 | 1.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6203 | 1.179% | CZ 3C | 40.4985 | 17.9296 | 76.6058 | 121.3913 | 0 | 6.023 | 0 | 130.7974 | 0 | 0 | 125.5771 | 0 | 0 | 469.4934 | 0 | 0 | 988.316 | 1.179%
CZ 4A | 0.39624 | 0.17675 | 0.70145 | 1.549 | 0 | 0.58892 | 0 | 1.1193 | 0 | 0 | 1.2345 | 0 | 0 | 4.4699 | 0 | 0 | 10.236 | 15.17% | CZ 4A | 13.1044 | 5.8452 | 70.8532 | 156.4599 | 0 | 19.4765 | 0 | 37.0159 | 0 | 0 | 40.8257 | 0 | 0 | 269.4851 | 0 | 0 | 613.0659 | 15.17% | CZ 4A | 3.8395 | 1.7126 | 0 | 0 | 0 | 5.7066 | 0 | 10.8456 | 0 | 0 | 11.9618 | 0 | 0 | 25.9618 | 0 | 0 | 60.0279 | 15.17% | CZ 4A | 0 | 0 | 0.70853 | 1.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.0819 | 15.17% | CZ 4A | 40.1961 | 17.9296 | 77.4426 | 171.0107 | 0 | 59.7419 | 0 | 113.5422 | 0 | 0 | 125.2283 | 0 | 0 | 469.4934 | 0 | 0 | 1074.5847 | 15.17%
CZ 4B | 0.39452 | 0.17663 | 0.69135 | 1.0601 | 0 | 0.47843 | 0 | 1.4542 | 0 | 0 | 1.2365 | 0 | 0 | 4.4699 | 0 | 0 | 9.9617 | 0.908% | CZ 4B | 13.0475 | 5.8414 | 69.8338 | 107.0795 | 0 | 15.8223 | 0 | 48.0922 | 0 | 0 | 40.8939 | 0 | 0 | 269.4851 | 0 | 0 | 570.0956 | 0.908% | CZ 4B | 3.8229 | 1.7115 | 0 | 0 | 0 | 4.6359 | 0 | 14.0909 | 0 | 0 | 11.9818 | 0 | 0 | 25.9618 | 0 | 0 | 62.2048 | 0.908% | CZ 4B | 0 | 0 | 0.69834 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.5779 | 0.908% | CZ 4B | 40.0217 | 17.9179 | 76.3283 | 117.0378 | 0 | 48.533 | 0 | 147.5177 | 0 | 0 | 125.4376 | 0 | 0 | 469.4934 | 0 | 0 | 1042.2875 | 0.908%
CZ 4C | 0.39796 | 0.17697 | 0.7285 | 1.4747 | 0 | 0.2203 | 0 | 1.3345 | 0 | 0 | 1.2288 | 0 | 0 | 4.4699 | 0 | 0 | 10.0318 | 2.44% | CZ 4C | 13.1612 | 5.8528 | 73.5856 | 148.96 | 0 | 7.2857 | 0 | 44.1348 | 0 | 0 | 40.6399 | 0 | 0 | 269.4851 | 0 | 0 | 603.1051 | 2.44% | CZ 4C | 3.8562 | 1.7149 | 0 | 0 | 0 | 2.1347 | 0 | 12.9314 | 0 | 0 | 11.9074 | 0 | 0 | 25.9618 | 0 | 0 | 58.5063 | 2.44% | CZ 4C | 0 | 0 | 0.73586 | 1.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.0342 | 2.44% | CZ 4C | 40.3706 | 17.9528 | 80.4291 | 162.8133 | 0 | 22.348 | 0 | 135.3786 | 0 | 0 | 124.6585 | 0 | 0 | 469.4934 | 0 | 0 | 1053.4442 | 2.44%
CZ 5A | 0.39762 | 0.17743 | 0.74587 | 2.1637 | 0 | 0.43029 | 0 | 1.0958 | 0 | 0 | 1.2282 | 0 | 0 | 4.4699 | 0 | 0 | 10.7088 | 21.9% | CZ 5A | 13.1498 | 5.868 | 75.3403 | 218.5588 | 0 | 14.2302 | 0 | 36.2388 | 0 | 0 | 40.6172 | 0 | 0 | 269.4851 | 0 | 0 | 673.4882 | 21.9% | CZ 5A | 3.8529 | 1.7193 | 0 | 0 | 0 | 4.1694 | 0 | 10.6179 | 0 | 0 | 11.9007 | 0 | 0 | 25.9618 | 0 | 0 | 58.222 | 21.9% | CZ 5A | 0 | 0 | 0.7534 | 2.1856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.7478 | 21.9% | CZ 5A | 40.3357 | 17.9993 | 82.3469 | 238.8848 | 0 | 43.6495 | 0 | 111.1586 | 0 | 0 | 124.5887 | 0 | 0 | 469.4934 | 0 | 0 | 1128.4569 | 21.9%
CZ 5B | 0.3951 | 0.17629 | 0.7378 | 1.5996 | 0 | 0.33905 | 0 | 1.4349 | 0 | 0 | 1.2263 | 0 | 0 | 4.4699 | 0 | 0 | 10.3791 | 4.373% | CZ 5B | 13.0664 | 5.8301 | 74.5255 | 161.5799 | 0 | 11.2128 | 0 | 47.4554 | 0 | 0 | 40.5565 | 0 | 0 | 269.4851 | 0 | 0 | 623.7117 | 4.373% | CZ 5B | 3.8284 | 1.7082 | 0 | 0 | 0 | 3.2853 | 0 | 13.9043 | 0 | 0 | 11.883 | 0 | 0 | 25.9618 | 0 | 0 | 60.5711 | 4.373% | CZ 5B | 0 | 0 | 0.74525 | 1.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.1698 | 4.373% | CZ 5B | 40.0799 | 17.883 | 81.4564 | 176.6068 | 0 | 34.394 | 0 | 145.5642 | 0 | 0 | 124.4027 | 0 | 0 | 469.4934 | 0 | 0 | 1089.8805 | 4.373%
CZ 5C | 0.40415 | 0.1772 | 0.74692 | 1.7576 | 0 | 0.047109 | 0 | 1.1555 | 0 | 0 | 1.2222 | 0 | 0 | 4.4699 | 0 | 0 | 9.9806 | 0% | CZ 5C | 13.3659 | 5.8604 | 75.4464 | 177.531 | 0 | 1.558 | 0 | 38.2138 | 0 | 0 | 40.4201 | 0 | 0 | 269.4851 | 0 | 0 | 621.8805 | 0% | CZ 5C | 3.9162 | 1.7171 | 0 | 0 | 0 | 0.45648 | 0 | 11.1965 | 0 | 0 | 11.843 | 0 | 0 | 25.9618 | 0 | 0 | 55.0911 | 0% | CZ 5C | 0 | 0 | 0.75446 | 1.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.3385 | 0% | CZ 5C | 40.9984 | 17.9761 | 82.4629 | 194.0413 | 0 | 4.7789 | 0 | 117.2165 | 0 | 0 | 123.9841 | 0 | 0 | 469.4934 | 0 | 0 | 1050.9516 | 0%
CZ 6A | 0.39854 | 0.17755 | 0.78519 | 2.531 | 0 | 0.23199 | 0 | 1.0669 | 0 | 0 | 1.2231 | 0 | 0 | 4.4699 | 0 | 0 | 10.8843 | 4.324% | CZ 6A | 13.1802 | 5.8718 | 79.3119 | 255.6605 | 0 | 7.6723 | 0 | 35.2836 | 0 | 0 | 40.4504 | 0 | 0 | 269.4851 | 0 | 0 | 706.9157 | 4.324% | CZ 6A | 3.8618 | 1.7204 | 0 | 0 | 0 | 2.248 | 0 | 10.338 | 0 | 0 | 11.8519 | 0 | 0 | 25.9618 | 0 | 0 | 55.9818 | 4.324% | CZ 6A | 0 | 0 | 0.79312 | 2.5566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.1585 | 4.324% | CZ 6A | 40.4287 | 18.0109 | 86.688 | 279.4369 | 0 | 23.534 | 0 | 108.2285 | 0 | 0 | 124.0771 | 0 | 0 | 469.4934 | 0 | 0 | 1149.8975 | 4.324%
CZ 6B | 0.39544 | 0.17663 | 0.79067 | 2.1804 | 0 | 0.18832 | 0 | 1.379 | 0 | 0 | 1.2225 | 0 | 0 | 4.4699 | 0 | 0 | 10.8029 | 0.5275% | CZ 6B | 13.0778 | 5.8414 | 79.8652 | 220.2415 | 0 | 6.2281 | 0 | 45.6056 | 0 | 0 | 40.4315 | 0 | 0 | 269.4851 | 0 | 0 | 680.7761 | 0.5275% | CZ 6B | 3.8318 | 1.7115 | 0 | 0 | 0 | 1.8248 | 0 | 13.3623 | 0 | 0 | 11.8463 | 0 | 0 | 25.9618 | 0 | 0 | 58.5386 | 0.5275% | CZ 6B | 0 | 0 | 0.79865 | 2.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.8098 | 0.5275% | CZ 6B | 40.1148 | 17.9179 | 87.2927 | 240.7239 | 0 | 19.1039 | 0 | 139.89 | 0 | 0 | 124.019 | 0 | 0 | 469.4934 | 0 | 0 | 1138.5557 | 0.5275%
CZ 7 | 0.39739 | 0.17709 | 0.84732 | 3.167 | 0 | 0.13743 | 0 | 1.2513 | 0 | 0 | 1.2178 | 0 | 0 | 4.4699 | 0 | 0 | 11.6653 | 0.6086% | CZ 7 | 13.1423 | 5.8566 | 85.5878 | 319.8968 | 0 | 4.545 | 0 | 41.3828 | 0 | 0 | 40.276 | 0 | 0 | 269.4851 | 0 | 0 | 780.1723 | 0.6086% | CZ 7 | 3.8506 | 1.716 | 0 | 0 | 0 | 1.3317 | 0 | 12.125 | 0 | 0 | 11.8008 | 0 | 0 | 25.9618 | 0 | 0 | 56.7859 | 0.6086% | CZ 7 | 0 | 0 | 0.85588 | 3.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.8636 | 0.6086% | CZ 7 | 40.3124 | 17.9644 | 93.5474 | 349.6472 | 0 | 13.9413 | 0 | 126.937 | 0 | 0 | 123.5423 | 0 | 0 | 469.4934 | 0 | 0 | 1235.3855 | 0.6086%
CZ 8 | 0.4053 | 0.17835 | 0.92404 | 4.7087 | 0 | 0.049516 | 0 | 1.2016 | 0 | 0 | 1.2095 | 0 | 0 | 4.4699 | 0 | 0 | 13.1469 | 0.03762% | CZ 8 | 13.4038 | 5.8983 | 93.3378 | 475.6215 | 0 | 1.6376 | 0 | 39.7376 | 0 | 0 | 39.9993 | 0 | 0 | 269.4851 | 0 | 0 | 939.121 | 0.03762% | CZ 8 | 3.9273 | 1.7282 | 0 | 0 | 0 | 0.4798 | 0 | 11.643 | 0 | 0 | 11.7197 | 0 | 0 | 25.9618 | 0 | 0 | 55.4598 | 0.03762% | CZ 8 | 0 | 0 | 0.93338 | 4.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 7.4984 | 0.03762% | CZ 8 | 41.1147 | 18.0923 | 102.0182 | 519.8543 | 0 | 5.0231 | 0 | 121.8907 | 0 | 0 | 122.6935 | 0 | 0 | 469.4934 | 0 | 0 | 1400.1803 | 0.03762%
Us Weighted | 0.39978 | 0.17694 | 0.67258 | 1.3824 | 0 | 0.81682 | 0 | 1.2195 | 0 | 0 | 1.2409 | 0 | 0 | 4.4699 | 0 | 0 | 10.3789 | 100% | Us Weighted | 13.2212 | 5.8516 | 67.9375 | 139.6318 | 0 | 27.0133 | 0 | 40.3311 | 0 | 0 | 41.0395 | 0 | 0 | 269.4851 | 0 | 0 | 604.5111 | 100% | Us Weighted | 3.8738 | 1.7145 | 0 | 0 | 0 | 7.9148 | 0 | 11.8169 | 0 | 0 | 12.0245 | 0 | 0 | 25.9618 | 0 | 0 | 63.3063 | 100% | Us Weighted | 0 | 0 | 0.67938 | 1.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8845 | 100% | Us Weighted | 40.5545 | 17.9492 | 74.2557 | 152.6176 | 0 | 82.8602 | 0 | 123.7111 | 0 | 0 | 125.8842 | 0 | 0 | 469.4934 | 0 | 0 | 1087.3259 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.86057 | 0.3144 | 0.51907 | 0.14538 | 0 | 2.8129 | 0 | 1.5626 | 0 | 0 | 1.2746 | 0 | 0 | 4.4699 | 0 | 0 | 11.9595 | 1.331% | CZ 1A | 28.4604 | 10.3978 | 52.4312 | 14.6853 | 0 | 93.0269 | 0 | 51.6782 | 0 | 0 | 42.1524 | 0 | 0 | 269.4851 | 0 | 0 | 562.3173 | 1.331% | CZ 1A | 8.3388 | 3.0465 | 0 | 0 | 0 | 27.2566 | 0 | 15.1416 | 0 | 0 | 12.3505 | 0 | 0 | 25.9618 | 0 | 0 | 92.0959 | 1.331% | CZ 1A | 0 | 0 | 0.52431 | 0.14685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.4799 | 1.331% | CZ 1A | 87.299 | 31.8941 | 57.3073 | 16.051 | 0 | 285.3496 | 0 | 158.5172 | 0 | 0 | 129.2979 | 0 | 0 | 469.4934 | 0 | 0 | 1235.2096 | 1.331%
CZ 1B | 0.86057 | 0.31429 | 0.49048 | 0.25231 | 0 | 2.5541 | 0 | 1.9314 | 0 | 0 | 1.2619 | 0 | 0 | 4.4699 | 0 | 0 | 12.1349 | 0% | CZ 1B | 28.4604 | 10.394 | 49.5434 | 25.4861 | 0 | 84.4675 | 0 | 63.8728 | 0 | 0 | 41.7317 | 0 | 0 | 269.4851 | 0 | 0 | 573.441 | 0% | CZ 1B | 8.3388 | 3.0454 | 0 | 0 | 0 | 24.7488 | 0 | 18.7146 | 0 | 0 | 12.2273 | 0 | 0 | 25.9618 | 0 | 0 | 93.0367 | 0% | CZ 1B | 0 | 0 | 0.49543 | 0.25486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.5591 | 0% | CZ 1B | 87.299 | 31.8825 | 54.151 | 27.8563 | 0 | 259.0948 | 0 | 195.9228 | 0 | 0 | 128.0072 | 0 | 0 | 469.4934 | 0 | 0 | 1253.707 | 0%
CZ 2A | 0.86057 | 0.31418 | 0.58544 | 0.59602 | 0 | 2.0479 | 0 | 1.6476 | 0 | 0 | 1.2606 | 0 | 0 | 4.4699 | 0 | 0 | 11.7822 | 15.62% | CZ 2A | 28.4604 | 10.3902 | 59.1353 | 60.204 | 0 | 67.7279 | 0 | 54.4871 | 0 | 0 | 41.69 | 0 | 0 | 269.4851 | 0 | 0 | 591.58 | 15.62% | CZ 2A | 8.3388 | 3.0443 | 0 | 0 | 0 | 19.8441 | 0 | 15.9646 | 0 | 0 | 12.215 | 0 | 0 | 25.9618 | 0 | 0 | 85.3687 | 15.62% | CZ 2A | 0 | 0 | 0.59135 | 0.60204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.0022 | 15.62% | CZ 2A | 87.299 | 31.8709 | 64.6349 | 65.803 | 0 | 207.7479 | 0 | 167.1332 | 0 | 0 | 127.8793 | 0 | 0 | 469.4934 | 0 | 0 | 1221.8616 | 15.62%
CZ 2B | 0.86057 | 0.31418 | 0.54672 | 0.3959 | 0 | 2.1873 | 0 | 1.8797 | 0 | 0 | 1.2587 | 0 | 0 | 4.4699 | 0 | 0 | 11.9129 | 3.461% | CZ 2B | 28.4604 | 10.3902 | 55.2243 | 39.9895 | 0 | 72.3374 | 0 | 62.1632 | 0 | 0 | 41.6255 | 0 | 0 | 269.4851 | 0 | 0 | 579.6755 | 3.461% | CZ 2B | 8.3388 | 3.0443 | 0 | 0 | 0 | 21.1947 | 0 | 18.2137 | 0 | 0 | 12.1962 | 0 | 0 | 25.9618 | 0 | 0 | 88.9494 | 3.461% | CZ 2B | 0 | 0 | 0.55224 | 0.39989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.7609 | 3.461% | CZ 2B | 87.299 | 31.8709 | 60.3601 | 43.7085 | 0 | 221.8869 | 0 | 190.6788 | 0 | 0 | 127.6817 | 0 | 0 | 469.4934 | 0 | 0 | 1232.9793 | 3.461%
CZ 3A | 0.86057 | 0.31406 | 0.63759 | 1.0628 | 0 | 1.465 | 0 | 1.6113 | 0 | 0 | 1.2473 | 0 | 0 | 4.4699 | 0 | 0 | 11.6686 | 17.35% | CZ 3A | 28.4604 | 10.3864 | 64.4031 | 107.3561 | 0 | 48.4486 | 0 | 53.2893 | 0 | 0 | 41.2502 | 0 | 0 | 269.4851 | 0 | 0 | 623.0791 | 17.35% | CZ 3A | 8.3388 | 3.0432 | 0 | 0 | 0 | 14.1953 | 0 | 15.6136 | 0 | 0 | 12.0862 | 0 | 0 | 25.9618 | 0 | 0 | 79.239 | 17.35% | CZ 3A | 0 | 0 | 0.64403 | 1.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.5264 | 17.35% | CZ 3A | 87.299 | 31.8593 | 70.3925 | 117.3402 | 0 | 148.6106 | 0 | 163.4589 | 0 | 0 | 126.5305 | 0 | 0 | 469.4934 | 0 | 0 | 1214.9845 | 17.35%
CZ 3B | 0.86057 | 0.31418 | 0.62003 | 0.69286 | 0 | 1.1184 | 0 | 1.7183 | 0 | 0 | 1.2494 | 0 | 0 | 4.4699 | 0 | 0 | 11.0436 | 10.77% | CZ 3B | 28.4604 | 10.3902 | 62.6295 | 69.9854 | 0 | 36.9856 | 0 | 56.826 | 0 | 0 | 41.3185 | 0 | 0 | 269.4851 | 0 | 0 | 576.0805 | 10.77% | CZ 3B | 8.3388 | 3.0443 | 0 | 0 | 0 | 10.8367 | 0 | 16.6499 | 0 | 0 | 12.1062 | 0 | 0 | 25.9618 | 0 | 0 | 76.9377 | 10.77% | CZ 3B | 0 | 0 | 0.62629 | 0.69985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.1349 | 10.77% | CZ 3B | 87.299 | 31.8709 | 68.454 | 76.494 | 0 | 113.4492 | 0 | 174.3073 | 0 | 0 | 126.7398 | 0 | 0 | 469.4934 | 0 | 0 | 1148.1076 | 10.77%
CZ 3C | 0.86057 | 0.31395 | 0.69383 | 1.0547 | 0 | 0.081266 | 0 | 1.3312 | 0 | 0 | 1.2389 | 0 | 0 | 4.4699 | 0 | 0 | 10.0444 | 1.179% | CZ 3C | 28.4604 | 10.3826 | 70.0839 | 106.5375 | 0 | 2.6876 | 0 | 44.0249 | 0 | 0 | 40.9735 | 0 | 0 | 269.4851 | 0 | 0 | 572.6355 | 1.179% | CZ 3C | 8.3388 | 3.0421 | 0 | 0 | 0 | 0.78746 | 0 | 12.8992 | 0 | 0 | 12.0051 | 0 | 0 | 25.9618 | 0 | 0 | 63.0345 | 1.179% | CZ 3C | 0 | 0 | 0.70084 | 1.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.575 | 1.179% | CZ 3C | 87.299 | 31.8476 | 76.6017 | 116.4455 | 0 | 8.2439 | 0 | 135.0414 | 0 | 0 | 125.6817 | 0 | 0 | 469.4934 | 0 | 0 | 1050.6542 | 1.179%
CZ 4A | 0.86057 | 0.31383 | 0.70145 | 1.6064 | 0 | 0.89381 | 0 | 1.5545 | 0 | 0 | 1.2348 | 0 | 0 | 4.4699 | 0 | 0 | 11.6353 | 15.17% | CZ 4A | 28.4604 | 10.3789 | 70.8532 | 162.2583 | 0 | 29.5597 | 0 | 51.4091 | 0 | 0 | 40.8371 | 0 | 0 | 269.4851 | 0 | 0 | 663.2416 | 15.17% | CZ 4A | 8.3388 | 3.041 | 0 | 0 | 0 | 8.6609 | 0 | 15.0627 | 0 | 0 | 11.9651 | 0 | 0 | 25.9618 | 0 | 0 | 73.0304 | 15.17% | CZ 4A | 0 | 0 | 0.70853 | 1.6226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.1399 | 15.17% | CZ 4A | 87.299 | 31.836 | 77.4426 | 177.3483 | 0 | 90.671 | 0 | 157.6917 | 0 | 0 | 125.2631 | 0 | 0 | 469.4934 | 0 | 0 | 1217.0451 | 15.17%
CZ 4B | 0.86057 | 0.31395 | 0.69132 | 1.1123 | 0 | 0.63947 | 0 | 1.6613 | 0 | 0 | 1.2366 | 0 | 0 | 4.4699 | 0 | 0 | 10.9856 | 0.908% | CZ 4B | 28.4604 | 10.3826 | 69.83 | 112.3586 | 0 | 21.1482 | 0 | 54.942 | 0 | 0 | 40.8977 | 0 | 0 | 269.4851 | 0 | 0 | 607.5045 | 0.908% | CZ 4B | 8.3388 | 3.0421 | 0 | 0 | 0 | 6.1964 | 0 | 16.0979 | 0 | 0 | 11.9829 | 0 | 0 | 25.9618 | 0 | 0 | 71.6199 | 0.908% | CZ 4B | 0 | 0 | 0.6983 | 1.1236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6307 | 0.908% | CZ 4B | 87.299 | 31.8476 | 76.3242 | 122.8079 | 0 | 64.8696 | 0 | 168.5285 | 0 | 0 | 125.4492 | 0 | 0 | 469.4934 | 0 | 0 | 1146.6194 | 0.908%
CZ 4C | 0.86057 | 0.31372 | 0.7285 | 1.5626 | 0 | 0.29675 | 0 | 1.4999 | 0 | 0 | 1.2291 | 0 | 0 | 4.4699 | 0 | 0 | 10.9611 | 2.44% | CZ 4C | 28.4604 | 10.3751 | 73.5856 | 157.8394 | 0 | 9.814 | 0 | 49.6047 | 0 | 0 | 40.6475 | 0 | 0 | 269.4851 | 0 | 0 | 639.8118 | 2.44% | CZ 4C | 8.3388 | 3.0399 | 0 | 0 | 0 | 2.8755 | 0 | 14.5341 | 0 | 0 | 11.9096 | 0 | 0 | 25.9618 | 0 | 0 | 66.6597 | 2.44% | CZ 4C | 0 | 0 | 0.73586 | 1.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.123 | 2.44% | CZ 4C | 87.299 | 31.8244 | 80.4291 | 172.5185 | 0 | 30.1035 | 0 | 152.157 | 0 | 0 | 124.6818 | 0 | 0 | 469.4934 | 0 | 0 | 1148.5066 | 2.44%
CZ 5A | 0.86057 | 0.31383 | 0.74587 | 2.066 | 0 | 0.62617 | 0 | 1.4023 | 0 | 0 | 1.2286 | 0 | 0 | 4.4699 | 0 | 0 | 11.7132 | 21.9% | CZ 5A | 28.4604 | 10.3789 | 75.3403 | 208.6827 | 0 | 20.7084 | 0 | 46.3751 | 0 | 0 | 40.6324 | 0 | 0 | 269.4851 | 0 | 0 | 700.0632 | 21.9% | CZ 5A | 8.3388 | 3.041 | 0 | 0 | 0 | 6.0675 | 0 | 13.5878 | 0 | 0 | 11.9052 | 0 | 0 | 25.9618 | 0 | 0 | 68.9021 | 21.9% | CZ 5A | 0 | 0 | 0.7534 | 2.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.649 | 21.9% | CZ 5A | 87.299 | 31.836 | 82.3469 | 228.0902 | 0 | 63.5208 | 0 | 142.2504 | 0 | 0 | 124.6353 | 0 | 0 | 469.4934 | 0 | 0 | 1229.4721 | 21.9%
CZ 5B | 0.86057 | 0.3136 | 0.7378 | 1.5592 | 0 | 0.45184 | 0 | 1.5084 | 0 | 0 | 1.227 | 0 | 0 | 4.4699 | 0 | 0 | 11.1284 | 4.373% | CZ 5B | 28.4604 | 10.3713 | 74.5255 | 157.4983 | 0 | 14.9428 | 0 | 49.8852 | 0 | 0 | 40.5793 | 0 | 0 | 269.4851 | 0 | 0 | 645.7479 | 4.373% | CZ 5B | 8.3388 | 3.0388 | 0 | 0 | 0 | 4.3782 | 0 | 14.6162 | 0 | 0 | 11.8896 | 0 | 0 | 25.9618 | 0 | 0 | 68.2235 | 4.373% | CZ 5B | 0 | 0 | 0.74525 | 1.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.129 | 4.373% | CZ 5B | 87.299 | 31.8127 | 81.4564 | 172.1457 | 0 | 45.8355 | 0 | 153.0174 | 0 | 0 | 124.4725 | 0 | 0 | 469.4934 | 0 | 0 | 1165.5326 | 4.373%
CZ 5C | 0.86057 | 0.31337 | 0.74688 | 1.6938 | 0 | 0.071409 | 0 | 1.2178 | 0 | 0 | 1.223 | 0 | 0 | 4.4699 | 0 | 0 | 10.5968 | 0% | CZ 5C | 28.4604 | 10.3637 | 75.4426 | 171.0884 | 0 | 2.3616 | 0 | 40.2759 | 0 | 0 | 40.4466 | 0 | 0 | 269.4851 | 0 | 0 | 637.9242 | 0% | CZ 5C | 8.3388 | 3.0365 | 0 | 0 | 0 | 0.69194 | 0 | 11.8007 | 0 | 0 | 11.8508 | 0 | 0 | 25.9618 | 0 | 0 | 61.6806 | 0% | CZ 5C | 0 | 0 | 0.75443 | 1.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.2741 | 0% | CZ 5C | 87.299 | 31.7895 | 82.4588 | 186.9996 | 0 | 7.2439 | 0 | 123.5418 | 0 | 0 | 124.0655 | 0 | 0 | 469.4934 | 0 | 0 | 1112.8915 | 0%
CZ 6A | 0.86057 | 0.31372 | 0.78515 | 2.4269 | 0 | 0.36644 | 0 | 1.344 | 0 | 0 | 1.2236 | 0 | 0 | 4.4699 | 0 | 0 | 11.7903 | 4.324% | CZ 6A | 28.4604 | 10.3751 | 79.3082 | 245.1401 | 0 | 12.1188 | 0 | 44.4494 | 0 | 0 | 40.4656 | 0 | 0 | 269.4851 | 0 | 0 | 729.8026 | 4.324% | CZ 6A | 8.3388 | 3.0399 | 0 | 0 | 0 | 3.5508 | 0 | 13.0236 | 0 | 0 | 11.8563 | 0 | 0 | 25.9618 | 0 | 0 | 65.7712 | 4.324% | CZ 6A | 0 | 0 | 0.79308 | 2.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.0533 | 4.324% | CZ 6A | 87.299 | 31.8244 | 86.6838 | 267.9382 | 0 | 37.173 | 0 | 136.3437 | 0 | 0 | 124.1237 | 0 | 0 | 469.4934 | 0 | 0 | 1240.8791 | 4.324%
CZ 6B | 0.86057 | 0.3136 | 0.79063 | 2.1341 | 0 | 0.26833 | 0 | 1.4516 | 0 | 0 | 1.2235 | 0 | 0 | 4.4699 | 0 | 0 | 11.5122 | 0.5275% | CZ 6B | 28.4604 | 10.3713 | 79.8615 | 215.5687 | 0 | 8.874 | 0 | 48.0051 | 0 | 0 | 40.4618 | 0 | 0 | 269.4851 | 0 | 0 | 701.0877 | 0.5275% | CZ 6B | 8.3388 | 3.0388 | 0 | 0 | 0 | 2.6 | 0 | 14.0654 | 0 | 0 | 11.8552 | 0 | 0 | 25.9618 | 0 | 0 | 65.86 | 0.5275% | CZ 6B | 0 | 0 | 0.79861 | 2.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.7631 | 0.5275% | CZ 6B | 87.299 | 31.8127 | 87.2886 | 235.6166 | 0 | 27.2199 | 0 | 147.2502 | 0 | 0 | 124.112 | 0 | 0 | 469.4934 | 0 | 0 | 1210.0925 | 0.5275%
CZ 7 | 0.86057 | 0.31349 | 0.84736 | 3.1184 | 0 | 0.21927 | 0 | 1.2991 | 0 | 0 | 1.2181 | 0 | 0 | 4.4699 | 0 | 0 | 12.3462 | 0.6086% | CZ 7 | 28.4604 | 10.3675 | 85.5916 | 314.9891 | 0 | 7.2516 | 0 | 42.9635 | 0 | 0 | 40.2836 | 0 | 0 | 269.4851 | 0 | 0 | 799.3922 | 0.6086% | CZ 7 | 8.3388 | 3.0376 | 0 | 0 | 0 | 2.1247 | 0 | 12.5882 | 0 | 0 | 11.803 | 0 | 0 | 25.9618 | 0 | 0 | 63.8542 | 0.6086% | CZ 7 | 0 | 0 | 0.85592 | 3.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.8146 | 0.6086% | CZ 7 | 87.299 | 31.8011 | 93.5516 | 344.2831 | 0 | 22.2433 | 0 | 131.7857 | 0 | 0 | 123.5655 | 0 | 0 | 469.4934 | 0 | 0 | 1304.0227 | 0.6086%
CZ 8 | 0.86057 | 0.31154 | 0.92404 | 4.6596 | 0 | 0.088602 | 0 | 1.2672 | 0 | 0 | 1.2103 | 0 | 0 | 4.4699 | 0 | 0 | 13.7919 | 0.03762% | CZ 8 | 28.4604 | 10.303 | 93.3378 | 470.6683 | 0 | 2.9302 | 0 | 41.9097 | 0 | 0 | 40.0258 | 0 | 0 | 269.4851 | 0 | 0 | 957.1203 | 0.03762% | CZ 8 | 8.3388 | 3.0188 | 0 | 0 | 0 | 0.85854 | 0 | 12.2794 | 0 | 0 | 11.7275 | 0 | 0 | 25.9618 | 0 | 0 | 62.1848 | 0.03762% | CZ 8 | 0 | 0 | 0.93338 | 4.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 7.4488 | 0.03762% | CZ 8 | 87.299 | 31.6035 | 102.0182 | 514.4405 | 0 | 8.988 | 0 | 128.5533 | 0 | 0 | 122.7749 | 0 | 0 | 469.4934 | 0 | 0 | 1465.1707 | 0.03762%
Us Weighted | 0.86057 | 0.31396 | 0.67256 | 1.3297 | 0 | 1.1327 | 0 | 1.5582 | 0 | 0 | 1.2415 | 0 | 0 | 4.4699 | 0 | 0 | 11.5792 | 100% | Us Weighted | 28.4604 | 10.3832 | 67.9355 | 134.3172 | 0 | 37.461 | 0 | 51.5328 | 0 | 0 | 41.0583 | 0 | 0 | 269.4851 | 0 | 0 | 640.6335 | 100% | Us Weighted | 8.3388 | 3.0422 | 0 | 0 | 0 | 10.976 | 0 | 15.099 | 0 | 0 | 12.03 | 0 | 0 | 25.9618 | 0 | 0 | 75.4478 | 100% | Us Weighted | 0 | 0 | 0.67935 | 1.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.8313 | 100% | Us Weighted | 87.299 | 31.8492 | 74.2535 | 146.8087 | 0 | 114.9076 | 0 | 158.0712 | 0 | 0 | 125.9417 | 0 | 0 | 469.4934 | 0 | 0 | 1208.6244 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.86057 | 0.3144 | 0.51903 | 0.11319 | 0 | 2.7284 | 0 | 1.4286 | 0 | 0 | 1.2698 | 0 | 0 | 4.4699 | 0 | 0 | 11.704 | 1.331% | CZ 1A | 28.4604 | 10.3978 | 52.4274 | 11.4337 | 0 | 90.2331 | 0 | 47.2469 | 0 | 0 | 41.9932 | 0 | 0 | 269.4851 | 0 | 0 | 551.6777 | 1.331% | CZ 1A | 8.3388 | 3.0465 | 0 | 0 | 0 | 26.4381 | 0 | 13.8432 | 0 | 0 | 12.3039 | 0 | 0 | 25.9618 | 0 | 0 | 89.9324 | 1.331% | CZ 1A | 0 | 0 | 0.52427 | 0.11434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.4474 | 1.331% | CZ 1A | 87.299 | 31.8941 | 57.3032 | 12.497 | 0 | 276.7802 | 0 | 144.9247 | 0 | 0 | 128.8095 | 0 | 0 | 469.4934 | 0 | 0 | 1209.0012 | 1.331%
CZ 1B | 0.86057 | 0.31429 | 0.49059 | 0.19874 | 0 | 2.5549 | 0 | 1.8486 | 0 | 0 | 1.2595 | 0 | 0 | 4.4699 | 0 | 0 | 11.9971 | 0% | CZ 1B | 28.4604 | 10.394 | 49.5548 | 20.0743 | 0 | 84.4941 | 0 | 61.136 | 0 | 0 | 41.652 | 0 | 0 | 269.4851 | 0 | 0 | 565.2506 | 0% | CZ 1B | 8.3388 | 3.0454 | 0 | 0 | 0 | 24.7565 | 0 | 17.9127 | 0 | 0 | 12.2039 | 0 | 0 | 25.9618 | 0 | 0 | 92.2192 | 0% | CZ 1B | 0 | 0 | 0.49555 | 0.20074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.5051 | 0% | CZ 1B | 87.299 | 31.8825 | 54.1634 | 21.9412 | 0 | 259.1762 | 0 | 187.5278 | 0 | 0 | 127.763 | 0 | 0 | 469.4934 | 0 | 0 | 1239.2466 | 0%
CZ 2A | 0.86057 | 0.31418 | 0.58529 | 0.60427 | 0 | 1.9857 | 0 | 1.52 | 0 | 0 | 1.2578 | 0 | 0 | 4.4699 | 0 | 0 | 11.5978 | 15.62% | CZ 2A | 28.4604 | 10.3902 | 59.1201 | 61.0378 | 0 | 65.6696 | 0 | 50.2681 | 0 | 0 | 41.599 | 0 | 0 | 269.4851 | 0 | 0 | 586.0302 | 15.62% | CZ 2A | 8.3388 | 3.0443 | 0 | 0 | 0 | 19.241 | 0 | 14.7284 | 0 | 0 | 12.1884 | 0 | 0 | 25.9618 | 0 | 0 | 83.5028 | 15.62% | CZ 2A | 0 | 0 | 0.5912 | 0.61038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.0104 | 15.62% | CZ 2A | 87.299 | 31.8709 | 64.6183 | 66.7143 | 0 | 201.4342 | 0 | 154.1918 | 0 | 0 | 127.6003 | 0 | 0 | 469.4934 | 0 | 0 | 1203.2222 | 15.62%
CZ 2B | 0.86057 | 0.31418 | 0.54672 | 0.36483 | 0 | 2.2097 | 0 | 1.7872 | 0 | 0 | 1.2567 | 0 | 0 | 4.4699 | 0 | 0 | 11.8098 | 3.461% | CZ 2B | 28.4604 | 10.3902 | 55.2243 | 36.8516 | 0 | 73.0766 | 0 | 59.1042 | 0 | 0 | 41.5611 | 0 | 0 | 269.4851 | 0 | 0 | 574.1533 | 3.461% | CZ 2B | 8.3388 | 3.0443 | 0 | 0 | 0 | 21.4112 | 0 | 17.3174 | 0 | 0 | 12.1773 | 0 | 0 | 25.9618 | 0 | 0 | 88.2508 | 3.461% | CZ 2B | 0 | 0 | 0.55224 | 0.36852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 2.7295 | 3.461% | CZ 2B | 87.299 | 31.8709 | 60.3601 | 40.2787 | 0 | 224.1543 | 0 | 181.2954 | 0 | 0 | 127.484 | 0 | 0 | 469.4934 | 0 | 0 | 1222.2359 | 3.461%
CZ 3A | 0.86057 | 0.31406 | 0.63729 | 1.1225 | 0 | 1.4145 | 0 | 1.4889 | 0 | 0 | 1.247 | 0 | 0 | 4.4699 | 0 | 0 | 11.5548 | 17.35% | CZ 3A | 28.4604 | 10.3864 | 64.3727 | 113.3818 | 0 | 46.7807 | 0 | 49.2408 | 0 | 0 | 41.2389 | 0 | 0 | 269.4851 | 0 | 0 | 623.3468 | 17.35% | CZ 3A | 8.3388 | 3.0432 | 0 | 0 | 0 | 13.7066 | 0 | 14.4274 | 0 | 0 | 12.0829 | 0 | 0 | 25.9618 | 0 | 0 | 77.5608 | 17.35% | CZ 3A | 0 | 0 | 0.64373 | 1.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.5863 | 17.35% | CZ 3A | 87.299 | 31.8593 | 70.3594 | 123.9263 | 0 | 143.4946 | 0 | 151.0408 | 0 | 0 | 126.4957 | 0 | 0 | 469.4934 | 0 | 0 | 1203.9684 | 17.35%
CZ 3B | 0.86057 | 0.31418 | 0.61999 | 0.66292 | 0 | 1.1095 | 0 | 1.6495 | 0 | 0 | 1.2479 | 0 | 0 | 4.4699 | 0 | 0 | 10.9345 | 10.77% | CZ 3B | 28.4604 | 10.3902 | 62.6257 | 66.9611 | 0 | 36.6937 | 0 | 54.5516 | 0 | 0 | 41.2692 | 0 | 0 | 269.4851 | 0 | 0 | 570.4369 | 10.77% | CZ 3B | 8.3388 | 3.0443 | 0 | 0 | 0 | 10.7512 | 0 | 15.9835 | 0 | 0 | 12.0918 | 0 | 0 | 25.9618 | 0 | 0 | 76.1713 | 10.77% | CZ 3B | 0 | 0 | 0.62626 | 0.66961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.1046 | 10.77% | CZ 3B | 87.299 | 31.8709 | 68.4498 | 73.1885 | 0 | 112.5539 | 0 | 167.3309 | 0 | 0 | 126.5887 | 0 | 0 | 469.4934 | 0 | 0 | 1136.7751 | 10.77%
CZ 3C | 0.86057 | 0.31395 | 0.69323 | 1.1676 | 0 | 0.093416 | 0 | 1.2139 | 0 | 0 | 1.2421 | 0 | 0 | 4.4699 | 0 | 0 | 10.0548 | 1.179% | CZ 3C | 28.4604 | 10.3826 | 70.0233 | 117.9409 | 0 | 3.0894 | 0 | 40.147 | 0 | 0 | 41.0797 | 0 | 0 | 269.4851 | 0 | 0 | 580.6083 | 1.179% | CZ 3C | 8.3388 | 3.0421 | 0 | 0 | 0 | 0.90519 | 0 | 11.763 | 0 | 0 | 12.0362 | 0 | 0 | 25.9618 | 0 | 0 | 62.0471 | 1.179% | CZ 3C | 0 | 0 | 0.70023 | 1.1794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6884 | 1.179% | CZ 3C | 87.299 | 31.8476 | 76.5354 | 128.9094 | 0 | 9.4764 | 0 | 123.1465 | 0 | 0 | 126.0073 | 0 | 0 | 469.4934 | 0 | 0 | 1052.715 | 1.179%
CZ 4A | 0.86057 | 0.31383 | 0.70103 | 1.7549 | 0 | 0.85003 | 0 | 1.4259 | 0 | 0 | 1.2371 | 0 | 0 | 4.4699 | 0 | 0 | 11.6133 | 15.17% | CZ 4A | 28.4604 | 10.3789 | 70.8115 | 177.2657 | 0 | 28.1116 | 0 | 47.156 | 0 | 0 | 40.9129 | 0 | 0 | 269.4851 | 0 | 0 | 672.5819 | 15.17% | CZ 4A | 8.3388 | 3.041 | 0 | 0 | 0 | 8.2366 | 0 | 13.8166 | 0 | 0 | 11.9874 | 0 | 0 | 25.9618 | 0 | 0 | 71.3822 | 15.17% | CZ 4A | 0 | 0 | 0.70812 | 1.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.2895 | 15.17% | CZ 4A | 87.299 | 31.836 | 77.397 | 193.7514 | 0 | 86.2293 | 0 | 144.6457 | 0 | 0 | 125.4957 | 0 | 0 | 469.4934 | 0 | 0 | 1216.1474 | 15.17%
CZ 4B | 0.86057 | 0.31395 | 0.69132 | 1.1169 | 0 | 0.67661 | 0 | 1.6043 | 0 | 0 | 1.2358 | 0 | 0 | 4.4699 | 0 | 0 | 10.9695 | 0.908% | CZ 4B | 28.4604 | 10.3826 | 69.83 | 112.8171 | 0 | 22.3763 | 0 | 53.058 | 0 | 0 | 40.8712 | 0 | 0 | 269.4851 | 0 | 0 | 607.2807 | 0.908% | CZ 4B | 8.3388 | 3.0421 | 0 | 0 | 0 | 6.5562 | 0 | 15.5459 | 0 | 0 | 11.9751 | 0 | 0 | 25.9618 | 0 | 0 | 71.42 | 0.908% | CZ 4B | 0 | 0 | 0.6983 | 1.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.6352 | 0.908% | CZ 4B | 87.299 | 31.8476 | 76.3242 | 123.3091 | 0 | 68.6369 | 0 | 162.7496 | 0 | 0 | 125.3678 | 0 | 0 | 469.4934 | 0 | 0 | 1145.0277 | 0.908%
CZ 4C | 0.86057 | 0.31372 | 0.72786 | 1.7584 | 0 | 0.30226 | 0 | 1.3677 | 0 | 0 | 1.2332 | 0 | 0 | 4.4699 | 0 | 0 | 11.0336 | 2.44% | CZ 4C | 28.4604 | 10.3751 | 73.5212 | 177.6181 | 0 | 9.996 | 0 | 45.2303 | 0 | 0 | 40.784 | 0 | 0 | 269.4851 | 0 | 0 | 655.4701 | 2.44% | CZ 4C | 8.3388 | 3.0399 | 0 | 0 | 0 | 2.9288 | 0 | 13.2524 | 0 | 0 | 11.9496 | 0 | 0 | 25.9618 | 0 | 0 | 65.4713 | 2.44% | CZ 4C | 0 | 0 | 0.73521 | 1.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.3202 | 2.44% | CZ 4C | 87.299 | 31.8244 | 80.3587 | 194.1366 | 0 | 30.6616 | 0 | 138.7389 | 0 | 0 | 125.1004 | 0 | 0 | 469.4934 | 0 | 0 | 1157.613 | 2.44%
CZ 5A | 0.86057 | 0.31383 | 0.74546 | 2.4742 | 0 | 0.62342 | 0 | 1.3878 | 0 | 0 | 1.2308 | 0 | 0 | 4.4699 | 0 | 0 | 12.106 | 21.9% | CZ 5A | 28.4604 | 10.3789 | 75.2986 | 249.9152 | 0 | 20.6175 | 0 | 45.8975 | 0 | 0 | 40.7044 | 0 | 0 | 269.4851 | 0 | 0 | 740.7574 | 21.9% | CZ 5A | 8.3388 | 3.041 | 0 | 0 | 0 | 6.0409 | 0 | 13.4478 | 0 | 0 | 11.9263 | 0 | 0 | 25.9618 | 0 | 0 | 68.7566 | 21.9% | CZ 5A | 0 | 0 | 0.75299 | 2.4992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.0609 | 21.9% | CZ 5A | 87.299 | 31.836 | 82.3014 | 273.1574 | 0 | 63.2418 | 0 | 140.7854 | 0 | 0 | 124.8562 | 0 | 0 | 469.4934 | 0 | 0 | 1272.9704 | 21.9%
CZ 5B | 0.86057 | 0.3136 | 0.7375 | 1.8173 | 0 | 0.47017 | 0 | 1.5515 | 0 | 0 | 1.229 | 0 | 0 | 4.4699 | 0 | 0 | 11.4496 | 4.373% | CZ 5B | 28.4604 | 10.3713 | 74.4952 | 183.5642 | 0 | 15.5493 | 0 | 51.3105 | 0 | 0 | 40.6437 | 0 | 0 | 269.4851 | 0 | 0 | 673.8797 | 4.373% | CZ 5B | 8.3388 | 3.0388 | 0 | 0 | 0 | 4.5559 | 0 | 15.0338 | 0 | 0 | 11.9085 | 0 | 0 | 25.9618 | 0 | 0 | 68.8377 | 4.373% | CZ 5B | 0 | 0 | 0.74495 | 1.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.3894 | 4.373% | CZ 5B | 87.299 | 31.8127 | 81.4232 | 200.6357 | 0 | 47.6959 | 0 | 157.3894 | 0 | 0 | 124.6701 | 0 | 0 | 469.4934 | 0 | 0 | 1200.4195 | 4.373%
CZ 5C | 0.86057 | 0.31337 | 0.74587 | 2.2747 | 0 | 0.063271 | 0 | 1.0899 | 0 | 0 | 1.2316 | 0 | 0 | 4.4699 | 0 | 0 | 11.0493 | 0% | CZ 5C | 28.4604 | 10.3637 | 75.3403 | 229.7727 | 0 | 2.0925 | 0 | 36.0455 | 0 | 0 | 40.7309 | 0 | 0 | 269.4851 | 0 | 0 | 692.291 | 0% | CZ 5C | 8.3388 | 3.0365 | 0 | 0 | 0 | 0.61308 | 0 | 10.5612 | 0 | 0 | 11.9341 | 0 | 0 | 25.9618 | 0 | 0 | 60.4456 | 0% | CZ 5C | 0 | 0 | 0.7534 | 2.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 4.8599 | 0% | CZ 5C | 87.299 | 31.7895 | 82.3469 | 251.1416 | 0 | 6.4184 | 0 | 110.5656 | 0 | 0 | 124.9376 | 0 | 0 | 469.4934 | 0 | 0 | 1163.9919 | 0%
CZ 6A | 0.86057 | 0.31372 | 0.7847 | 2.9474 | 0 | 0.34329 | 0 | 1.2923 | 0 | 0 | 1.2268 | 0 | 0 | 4.4699 | 0 | 0 | 12.2388 | 4.324% | CZ 6A | 28.4604 | 10.3751 | 79.2627 | 297.7192 | 0 | 11.3531 | 0 | 42.7398 | 0 | 0 | 40.5717 | 0 | 0 | 269.4851 | 0 | 0 | 779.9669 | 4.324% | CZ 6A | 8.3388 | 3.0399 | 0 | 0 | 0 | 3.3264 | 0 | 12.5227 | 0 | 0 | 11.8874 | 0 | 0 | 25.9618 | 0 | 0 | 65.077 | 4.324% | CZ 6A | 0 | 0 | 0.79263 | 2.9772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.5786 | 4.324% | CZ 6A | 87.299 | 31.8244 | 86.6341 | 325.4071 | 0 | 34.8243 | 0 | 131.0997 | 0 | 0 | 124.4492 | 0 | 0 | 469.4934 | 0 | 0 | 1291.0311 | 4.324%
CZ 6B | 0.86057 | 0.3136 | 0.79052 | 2.4745 | 0 | 0.26707 | 0 | 1.4697 | 0 | 0 | 1.2237 | 0 | 0 | 4.4699 | 0 | 0 | 11.8695 | 0.5275% | CZ 6B | 28.4604 | 10.3713 | 79.8501 | 249.9456 | 0 | 8.8323 | 0 | 48.604 | 0 | 0 | 40.4694 | 0 | 0 | 269.4851 | 0 | 0 | 736.018 | 0.5275% | CZ 6B | 8.3388 | 3.0388 | 0 | 0 | 0 | 2.5878 | 0 | 14.2408 | 0 | 0 | 11.8574 | 0 | 0 | 25.9618 | 0 | 0 | 66.0255 | 0.5275% | CZ 6B | 0 | 0 | 0.7985 | 2.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 5.1067 | 0.5275% | CZ 6B | 87.299 | 31.8127 | 87.2761 | 273.1905 | 0 | 27.092 | 0 | 149.0874 | 0 | 0 | 124.1353 | 0 | 0 | 469.4934 | 0 | 0 | 1249.3864 | 0.5275%
CZ 7 | 0.86057 | 0.31349 | 0.84702 | 3.7441 | 0 | 0.20013 | 0 | 1.251 | 0 | 0 | 1.2204 | 0 | 0 | 4.4699 | 0 | 0 | 12.9066 | 0.6086% | CZ 7 | 28.4604 | 10.3675 | 85.5575 | 378.1946 | 0 | 6.6185 | 0 | 41.3714 | 0 | 0 | 40.3594 | 0 | 0 | 269.4851 | 0 | 0 | 860.4143 | 0.6086% | CZ 7 | 8.3388 | 3.0376 | 0 | 0 | 0 | 1.9392 | 0 | 12.1217 | 0 | 0 | 11.8252 | 0 | 0 | 25.9618 | 0 | 0 | 63.2244 | 0.6086% | CZ 7 | 0 | 0 | 0.85557 | 3.7819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 6.4463 | 0.6086% | CZ 7 | 87.299 | 31.8011 | 93.5143 | 413.3667 | 0 | 20.3016 | 0 | 126.9022 | 0 | 0 | 123.7981 | 0 | 0 | 469.4934 | 0 | 0 | 1366.4763 | 0.6086%
CZ 8 | 0.86057 | 0.31154 | 0.92273 | 5.6995 | 0 | 0.076452 | 0 | 1.1639 | 0 | 0 | 1.2251 | 0 | 0 | 4.4699 | 0 | 0 | 14.7297 | 0.03762% | CZ 8 | 28.4604 | 10.303 | 93.2052 | 575.7089 | 0 | 2.5284 | 0 | 38.4905 | 0 | 0 | 40.5148 | 0 | 0 | 269.4851 | 0 | 0 | 1058.6963 | 0.03762% | CZ 8 | 8.3388 | 3.0188 | 0 | 0 | 0 | 0.74081 | 0 | 11.2776 | 0 | 0 | 11.8707 | 0 | 0 | 25.9618 | 0 | 0 | 61.2086 | 0.03762% | CZ 8 | 0 | 0 | 0.93205 | 5.7571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 8.4979 | 0.03762% | CZ 8 | 87.299 | 31.6035 | 101.8733 | 629.2498 | 0 | 7.7555 | 0 | 118.0653 | 0 | 0 | 124.2748 | 0 | 0 | 469.4934 | 0 | 0 | 1569.6145 | 0.03762%
Us Weighted | 0.86057 | 0.31396 | 0.67227 | 1.4945 | 0 | 1.106 | 0 | 1.4763 | 0 | 0 | 1.2419 | 0 | 0 | 4.4699 | 0 | 0 | 11.6355 | 100% | Us Weighted | 28.4604 | 10.3832 | 67.9061 | 150.9642 | 0 | 36.5771 | 0 | 48.8229 | 0 | 0 | 41.0722 | 0 | 0 | 269.4851 | 0 | 0 | 653.671 | 100% | Us Weighted | 8.3388 | 3.0422 | 0 | 0 | 0 | 10.717 | 0 | 14.305 | 0 | 0 | 12.034 | 0 | 0 | 25.9618 | 0 | 0 | 74.3989 | 100% | Us Weighted | 0 | 0 | 0.67906 | 1.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8088 | 0 | 0 | 3.9975 | 100% | Us Weighted | 87.299 | 31.8492 | 74.2213 | 165.0039 | 0 | 112.1961 | 0 | 149.759 | 0 | 0 | 125.9843 | 0 | 0 | 469.4934 | 0 | 0 | 1215.8062 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 2501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 2501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.49046 | 0.13754 | 0.00018759 | -0.067346 | 0 | 0.79604 | 0 | 0.51052 | 0 | 0 | 0.25343 | 0 | 0 | 0 | 0 | 0 | 2.1208 | 1.331% | CZ 1A | 16.2203 | 4.5488 | 0.018949 | -6.8026 | 0 | 26.3262 | 0 | 16.8837 | 0 | 0 | 8.3812 | 0 | 0 | 0 | 0 | 0 | 65.5765 | 1.331% | CZ 1A | 4.7525 | 1.3328 | 0 | 0 | 0 | 7.7135 | 0 | 4.9469 | 0 | 0 | 2.4557 | 0 | 0 | 0 | 0 | 0 | 21.2013 | 1.331% | CZ 1A | 0 | 0 | 0.00018949 | -0.068026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.067837 | 1.331% | CZ 1A | 49.7539 | 13.953 | 0.020711 | -7.4352 | 0 | 80.7527 | 0 | 51.7887 | 0 | 0 | 25.7084 | 0 | 0 | 0 | 0 | 0 | 214.5423 | 1.331%
CZ 1B | 0.49012 | 0.13754 | -0.00015007 | -0.085617 | 0 | 0.64726 | 0 | 0.72291 | 0 | 0 | 0.26283 | 0 | 0 | 0 | 0 | 0 | 2.1749 | 0% | CZ 1B | 16.2089 | 4.5488 | -0.015159 | -8.6482 | 0 | 21.4059 | 0 | 23.9078 | 0 | 0 | 8.692 | 0 | 0 | 0 | 0 | 0 | 66.1001 | 0% | CZ 1B | 4.7492 | 1.3328 | 0 | 0 | 0 | 6.2719 | 0 | 7.0049 | 0 | 0 | 2.5467 | 0 | 0 | 0 | 0 | 0 | 21.9055 | 0% | CZ 1B | 0 | 0 | -0.00015159 | -0.086482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.086634 | 0% | CZ 1B | 49.719 | 13.953 | -0.016569 | -9.4525 | 0 | 65.6603 | 0 | 73.3344 | 0 | 0 | 26.6619 | 0 | 0 | 0 | 0 | 0 | 219.8596 | 0%
CZ 2A | 0.48955 | 0.13743 | -0.00022511 | -0.04112 | 0 | 0.60577 | 0 | 0.65896 | 0 | 0 | 0.25962 | 0 | 0 | 0 | 0 | 0 | 2.11 | 15.62% | CZ 2A | 16.19 | 4.545 | -0.022739 | -4.1536 | 0 | 20.0337 | 0 | 21.7926 | 0 | 0 | 8.5859 | 0 | 0 | 0 | 0 | 0 | 66.9708 | 15.62% | CZ 2A | 4.7436 | 1.3317 | 0 | 0 | 0 | 5.8698 | 0 | 6.3852 | 0 | 0 | 2.5156 | 0 | 0 | 0 | 0 | 0 | 20.8459 | 15.62% | CZ 2A | 0 | 0 | -0.00022739 | -0.041536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.041763 | 15.62% | CZ 2A | 49.6609 | 13.9413 | -0.024853 | -4.5399 | 0 | 61.4512 | 0 | 66.8463 | 0 | 0 | 26.3363 | 0 | 0 | 0 | 0 | 0 | 213.6713 | 15.62%
CZ 2B | 0.4931 | 0.13743 | -0.00033767 | -0.078564 | 0 | 0.60348 | 0 | 0.74137 | 0 | 0 | 0.26397 | 0 | 0 | 0 | 0 | 0 | 2.1604 | 3.461% | CZ 2B | 16.3075 | 4.545 | -0.034108 | -7.9357 | 0 | 19.9579 | 0 | 24.5181 | 0 | 0 | 8.73 | 0 | 0 | 0 | 0 | 0 | 66.0885 | 3.461% | CZ 2B | 4.778 | 1.3317 | 0 | 0 | 0 | 5.8476 | 0 | 7.1837 | 0 | 0 | 2.5579 | 0 | 0 | 0 | 0 | 0 | 21.6989 | 3.461% | CZ 2B | 0 | 0 | -0.00034108 | -0.079357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.079698 | 3.461% | CZ 2B | 50.0214 | 13.9413 | -0.03728 | -8.6738 | 0 | 61.2186 | 0 | 75.2064 | 0 | 0 | 26.7782 | 0 | 0 | 0 | 0 | 0 | 218.4549 | 3.461%
CZ 3A | 0.48714 | 0.1372 | -0.00045022 | -0.021048 | 0 | 0.43797 | 0 | 0.67993 | 0 | 0 | 0.26397 | 0 | 0 | 0 | 0 | 0 | 1.9847 | 17.35% | CZ 3A | 16.1104 | 4.5374 | -0.045477 | -2.1261 | 0 | 14.4842 | 0 | 22.4863 | 0 | 0 | 8.73 | 0 | 0 | 0 | 0 | 0 | 64.1766 | 17.35% | CZ 3A | 4.7203 | 1.3295 | 0 | 0 | 0 | 4.2438 | 0 | 6.5884 | 0 | 0 | 2.5579 | 0 | 0 | 0 | 0 | 0 | 19.4398 | 17.35% | CZ 3A | 0 | 0 | -0.00045477 | -0.021261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.021715 | 17.35% | CZ 3A | 49.4167 | 13.9181 | -0.049706 | -2.3238 | 0 | 44.4285 | 0 | 68.9741 | 0 | 0 | 26.7782 | 0 | 0 | 0 | 0 | 0 | 201.1422 | 17.35%
CZ 3B | 0.49069 | 0.13743 | -0.0004127 | -0.11015 | 0 | 0.33412 | 0 | 0.77541 | 0 | 0 | 0.26558 | 0 | 0 | 0 | 0 | 0 | 1.8927 | 10.77% | CZ 3B | 16.2279 | 4.545 | -0.041687 | -11.1267 | 0 | 11.0498 | 0 | 25.6439 | 0 | 0 | 8.783 | 0 | 0 | 0 | 0 | 0 | 55.0812 | 10.77% | CZ 3B | 4.7547 | 1.3317 | 0 | 0 | 0 | 3.2376 | 0 | 7.5136 | 0 | 0 | 2.5734 | 0 | 0 | 0 | 0 | 0 | 19.411 | 10.77% | CZ 3B | 0 | 0 | -0.00041687 | -0.11127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11168 | 10.77% | CZ 3B | 49.7772 | 13.9413 | -0.045564 | -12.1615 | 0 | 33.8941 | 0 | 78.6598 | 0 | 0 | 26.941 | 0 | 0 | 0 | 0 | 0 | 191.0063 | 10.77%
CZ 3C | 0.48886 | 0.1372 | -0.00086293 | 0.11023 | 0 | 0.047338 | 0 | 0.44702 | 0 | 0 | 0.26982 | 0 | 0 | 0 | 0 | 0 | 1.4996 | 1.179% | CZ 3C | 16.1672 | 4.5374 | -0.087164 | 11.1343 | 0 | 1.5655 | 0 | 14.7836 | 0 | 0 | 8.9233 | 0 | 0 | 0 | 0 | 0 | 57.0242 | 1.179% | CZ 3C | 4.737 | 1.3295 | 0 | 0 | 0 | 0.4587 | 0 | 4.3316 | 0 | 0 | 2.6145 | 0 | 0 | 0 | 0 | 0 | 13.4712 | 1.179% | CZ 3C | 0 | 0 | -0.00087164 | 0.11134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11047 | 1.179% | CZ 3C | 49.5911 | 13.9181 | -0.095271 | 12.1698 | 0 | 4.8021 | 0 | 45.3471 | 0 | 0 | 27.3712 | 0 | 0 | 0 | 0 | 0 | 153.1042 | 1.179%
CZ 4A | 0.49104 | 0.13709 | -0.00048774 | 0.22504 | 0 | 0.31326 | 0 | 0.74309 | 0 | 0 | 0.26603 | 0 | 0 | 0 | 0 | 0 | 2.1751 | 15.17% | CZ 4A | 16.2392 | 4.5336 | -0.049267 | 22.7309 | 0 | 10.3599 | 0 | 24.5749 | 0 | 0 | 8.7982 | 0 | 0 | 0 | 0 | 0 | 87.1876 | 15.17% | CZ 4A | 4.7581 | 1.3283 | 0 | 0 | 0 | 3.0354 | 0 | 7.2004 | 0 | 0 | 2.5778 | 0 | 0 | 0 | 0 | 0 | 18.9001 | 15.17% | CZ 4A | 0 | 0 | -0.00049267 | 0.22731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22682 | 15.17% | CZ 4A | 49.8121 | 13.9064 | -0.053849 | 24.8449 | 0 | 31.7779 | 0 | 75.3809 | 0 | 0 | 26.9875 | 0 | 0 | 0 | 0 | 0 | 222.6558 | 15.17%
CZ 4B | 0.49275 | 0.13732 | -0.00011256 | 0.012944 | 0 | 0.25182 | 0 | 0.88315 | 0 | 0 | 0.26283 | 0 | 0 | 0 | 0 | 0 | 2.0407 | 0.908% | CZ 4B | 16.2961 | 4.5412 | -0.011369 | 1.3075 | 0 | 8.3281 | 0 | 29.2071 | 0 | 0 | 8.692 | 0 | 0 | 0 | 0 | 0 | 68.3607 | 0.908% | CZ 4B | 4.7747 | 1.3306 | 0 | 0 | 0 | 2.4401 | 0 | 8.5576 | 0 | 0 | 2.5467 | 0 | 0 | 0 | 0 | 0 | 19.6498 | 0.908% | CZ 4B | 0 | 0 | -0.00011369 | 0.013075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012961 | 0.908% | CZ 4B | 49.9865 | 13.9297 | -0.012427 | 1.4291 | 0 | 25.5455 | 0 | 89.5896 | 0 | 0 | 26.6619 | 0 | 0 | 0 | 0 | 0 | 207.1299 | 0.908%
CZ 4C | 0.48932 | 0.13674 | -0.00082541 | 0.28049 | 0 | 0.10843 | 0 | 0.74813 | 0 | 0 | 0.26982 | 0 | 0 | 0 | 0 | 0 | 2.0321 | 2.44% | CZ 4C | 16.1824 | 4.5223 | -0.083375 | 28.3322 | 0 | 3.586 | 0 | 24.7417 | 0 | 0 | 8.9233 | 0 | 0 | 0 | 0 | 0 | 86.2044 | 2.44% | CZ 4C | 4.7414 | 1.325 | 0 | 0 | 0 | 1.0507 | 0 | 7.2493 | 0 | 0 | 2.6145 | 0 | 0 | 0 | 0 | 0 | 16.9808 | 2.44% | CZ 4C | 0 | 0 | -0.00083375 | 0.28332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28249 | 2.44% | CZ 4C | 49.6377 | 13.8716 | -0.091128 | 30.9671 | 0 | 10.9996 | 0 | 75.8925 | 0 | 0 | 27.3712 | 0 | 0 | 0 | 0 | 0 | 208.6484 | 2.44%
CZ 5A | 0.48932 | 0.1364 | -0.00048774 | 0.33133 | 0 | 0.22741 | 0 | 0.72383 | 0 | 0 | 0.26661 | 0 | 0 | 0 | 0 | 0 | 2.1744 | 21.9% | CZ 5A | 16.1824 | 4.5109 | -0.049267 | 33.4673 | 0 | 7.5207 | 0 | 23.9381 | 0 | 0 | 8.8171 | 0 | 0 | 0 | 0 | 0 | 94.3872 | 21.9% | CZ 5A | 4.7414 | 1.3217 | 0 | 0 | 0 | 2.2035 | 0 | 7.0138 | 0 | 0 | 2.5834 | 0 | 0 | 0 | 0 | 0 | 17.8638 | 21.9% | CZ 5A | 0 | 0 | -0.00049267 | 0.33467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33418 | 21.9% | CZ 5A | 49.6377 | 13.8367 | -0.053849 | 36.5798 | 0 | 23.0689 | 0 | 73.4274 | 0 | 0 | 27.0456 | 0 | 0 | 0 | 0 | 0 | 223.5422 | 21.9%
CZ 5B | 0.49264 | 0.13732 | -0.00045022 | 0.17585 | 0 | 0.16517 | 0 | 0.8639 | 0 | 0 | 0.26718 | 0 | 0 | 0 | 0 | 0 | 2.1016 | 4.373% | CZ 5B | 16.2923 | 4.5412 | -0.045477 | 17.7626 | 0 | 5.4624 | 0 | 28.5703 | 0 | 0 | 8.8361 | 0 | 0 | 0 | 0 | 0 | 81.4194 | 4.373% | CZ 5B | 4.7736 | 1.3306 | 0 | 0 | 0 | 1.6005 | 0 | 8.371 | 0 | 0 | 2.589 | 0 | 0 | 0 | 0 | 0 | 18.6646 | 4.373% | CZ 5B | 0 | 0 | -0.00045477 | 0.17763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17717 | 4.373% | CZ 5B | 49.9748 | 13.9297 | -0.049706 | 19.4145 | 0 | 16.7552 | 0 | 87.6362 | 0 | 0 | 27.1037 | 0 | 0 | 0 | 0 | 0 | 214.7645 | 4.373%
CZ 5C | 0.48198 | 0.13617 | -0.0013507 | 0.52177 | 0 | 0.030833 | 0 | 0.5684 | 0 | 0 | 0.27578 | 0 | 0 | 0 | 0 | 0 | 2.0136 | 0% | CZ 5C | 15.9398 | 4.5033 | -0.13643 | 52.7041 | 0 | 1.0197 | 0 | 18.7979 | 0 | 0 | 9.1204 | 0 | 0 | 0 | 0 | 0 | 101.9488 | 0% | CZ 5C | 4.6703 | 1.3195 | 0 | 0 | 0 | 0.29877 | 0 | 5.5077 | 0 | 0 | 2.6723 | 0 | 0 | 0 | 0 | 0 | 14.4685 | 0% | CZ 5C | 0 | 0 | -0.0013643 | 0.52704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52568 | 0% | CZ 5C | 48.8935 | 13.8134 | -0.14912 | 57.6056 | 0 | 3.1278 | 0 | 57.6606 | 0 | 0 | 27.9758 | 0 | 0 | 0 | 0 | 0 | 208.9276 | 0%
CZ 6A | 0.48851 | 0.13617 | -0.00075037 | 0.4467 | 0 | 0.13285 | 0 | 0.66778 | 0 | 0 | 0.26982 | 0 | 0 | 0 | 0 | 0 | 2.1411 | 4.324% | CZ 6A | 16.1558 | 4.5033 | -0.075795 | 45.1208 | 0 | 4.3934 | 0 | 22.0845 | 0 | 0 | 8.9233 | 0 | 0 | 0 | 0 | 0 | 101.1053 | 4.324% | CZ 6A | 4.7336 | 1.3195 | 0 | 0 | 0 | 1.2873 | 0 | 6.4707 | 0 | 0 | 2.6145 | 0 | 0 | 0 | 0 | 0 | 16.4255 | 4.324% | CZ 6A | 0 | 0 | -0.00075795 | 0.45121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45045 | 4.324% | CZ 6A | 49.5563 | 13.8134 | -0.082844 | 49.317 | 0 | 13.4762 | 0 | 67.7416 | 0 | 0 | 27.3712 | 0 | 0 | 0 | 0 | 0 | 221.1929 | 4.324%
CZ 6B | 0.49241 | 0.13697 | -0.00037519 | 0.25156 | 0 | 0.1027 | 0 | 0.81163 | 0 | 0 | 0.26752 | 0 | 0 | 0 | 0 | 0 | 2.0624 | 0.5275% | CZ 6B | 16.2847 | 4.5299 | -0.037898 | 25.4103 | 0 | 3.3964 | 0 | 26.8417 | 0 | 0 | 8.8475 | 0 | 0 | 0 | 0 | 0 | 85.2726 | 0.5275% | CZ 6B | 4.7714 | 1.3272 | 0 | 0 | 0 | 0.99515 | 0 | 7.8646 | 0 | 0 | 2.5923 | 0 | 0 | 0 | 0 | 0 | 17.5506 | 0.5275% | CZ 6B | 0 | 0 | -0.00037898 | 0.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25372 | 0.5275% | CZ 6B | 49.9516 | 13.8948 | -0.041422 | 27.7734 | 0 | 10.4182 | 0 | 82.3341 | 0 | 0 | 27.1386 | 0 | 0 | 0 | 0 | 0 | 211.4694 | 0.5275%
CZ 7 | 0.49287 | 0.1364 | -0.00063782 | 0.55103 | 0 | 0.085736 | 0 | 0.64428 | 0 | 0 | 0.26947 | 0 | 0 | 0 | 0 | 0 | 2.1792 | 0.6086% | CZ 7 | 16.2999 | 4.5109 | -0.064426 | 55.6601 | 0 | 2.8354 | 0 | 21.3074 | 0 | 0 | 8.9119 | 0 | 0 | 0 | 0 | 0 | 109.4611 | 0.6086% | CZ 7 | 4.7758 | 1.3217 | 0 | 0 | 0 | 0.83077 | 0 | 6.243 | 0 | 0 | 2.6112 | 0 | 0 | 0 | 0 | 0 | 15.7824 | 0.6086% | CZ 7 | 0 | 0 | -0.00064426 | 0.5566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55596 | 0.6086% | CZ 7 | 49.9981 | 13.8367 | -0.070417 | 60.8365 | 0 | 8.6973 | 0 | 65.358 | 0 | 0 | 27.3363 | 0 | 0 | 0 | 0 | 0 | 225.9925 | 0.6086%
CZ 8 | 0.48485 | 0.13319 | -0.0016508 | 0.98186 | 0 | 0.038283 | 0 | 0.57127 | 0 | 0 | 0.28323 | 0 | 0 | 0 | 0 | 0 | 2.491 | 0.03762% | CZ 8 | 16.0345 | 4.4048 | -0.16675 | 99.1778 | 0 | 1.2661 | 0 | 18.8927 | 0 | 0 | 9.3668 | 0 | 0 | 0 | 0 | 0 | 148.976 | 0.03762% | CZ 8 | 4.6981 | 1.2906 | 0 | 0 | 0 | 0.37096 | 0 | 5.5355 | 0 | 0 | 2.7444 | 0 | 0 | 0 | 0 | 0 | 14.6396 | 0.03762% | CZ 8 | 0 | 0 | -0.0016675 | 0.99178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99011 | 0.03762% | CZ 8 | 49.1842 | 13.5111 | -0.18226 | 108.4014 | 0 | 3.8836 | 0 | 57.9513 | 0 | 0 | 28.7316 | 0 | 0 | 0 | 0 | 0 | 261.4808 | 0.03762%
Us Weighted | 0.4897 | 0.13702 | -0.00043768 | 0.12148 | 0 | 0.35493 | 0 | 0.71472 | 0 | 0 | 0.26487 | 0 | 0 | 0 | 0 | 0 | 2.0823 | 100% | Us Weighted | 16.1951 | 4.5316 | -0.04421 | 12.2707 | 0 | 11.7379 | 0 | 23.6369 | 0 | 0 | 8.7596 | 0 | 0 | 0 | 0 | 0 | 77.0876 | 100% | Us Weighted | 4.7451 | 1.3277 | 0 | 0 | 0 | 3.4392 | 0 | 6.9255 | 0 | 0 | 2.5665 | 0 | 0 | 0 | 0 | 0 | 19.0041 | 100% | Us Weighted | 0 | 0 | -0.0004421 | 0.12271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12226 | 100% | Us Weighted | 49.6768 | 13.9001 | -0.048322 | 13.4118 | 0 | 36.0047 | 0 | 72.5035 | 0 | 0 | 26.8691 | 0 | 0 | 0 | 0 | 0 | 212.3177 | 100%
Building Type: | Quick-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 2501 | [17 empty] | Prototype Floor Area: | 2501 | [17 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 56.99% | 43.75% | 0.03614% | -59.5% | 0% | 29.18% | 0% | 35.73% | 0% | 0% | 19.96% | 0% | 0% | 0% | 0% | 0% | 18.12% | 1.331% | CZ 1A | 56.99% | 43.75% | 0.03614% | -59.5% | 0% | 29.18% | 0% | 35.73% | 0% | 0% | 19.96% | 0% | 0% | 0% | 0% | 0% | 11.89% | 1.331% | CZ 1A | 56.99% | 43.75% | 0% | 0% | 0% | 29.18% | 0% | 35.73% | 0% | 0% | 19.96% | 0% | 0% | 0% | 0% | 0% | 23.57% | 1.331% | CZ 1A | 0% | 0% | 0.03614% | -59.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.772% | 1.331% | CZ 1A | 56.99% | 43.75% | 0.03614% | -59.5% | 0% | 29.18% | 0% | 35.73% | 0% | 0% | 19.96% | 0% | 0% | 0% | 0% | 0% | 17.75% | 1.331%
CZ 1B | 56.95% | 43.76% | -0.03059% | -43.08% | 0% | 25.33% | 0% | 39.11% | 0% | 0% | 20.87% | 0% | 0% | 0% | 0% | 0% | 18.13% | 0% | CZ 1B | 56.95% | 43.76% | -0.03059% | -43.08% | 0% | 25.33% | 0% | 39.11% | 0% | 0% | 20.87% | 0% | 0% | 0% | 0% | 0% | 11.69% | 0% | CZ 1B | 56.95% | 43.76% | 0% | 0% | 0% | 25.33% | 0% | 39.11% | 0% | 0% | 20.87% | 0% | 0% | 0% | 0% | 0% | 23.75% | 0% | CZ 1B | 0% | 0% | -0.03059% | -43.08% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.458% | 0% | CZ 1B | 56.95% | 43.76% | -0.03059% | -43.08% | 0% | 25.33% | 0% | 39.11% | 0% | 0% | 20.87% | 0% | 0% | 0% | 0% | 0% | 17.74% | 0%
CZ 2A | 56.89% | 43.74% | -0.03846% | -6.805% | 0% | 30.51% | 0% | 43.35% | 0% | 0% | 20.64% | 0% | 0% | 0% | 0% | 0% | 18.19% | 15.62% | CZ 2A | 56.89% | 43.74% | -0.03846% | -6.805% | 0% | 30.51% | 0% | 43.35% | 0% | 0% | 20.64% | 0% | 0% | 0% | 0% | 0% | 11.43% | 15.62% | CZ 2A | 56.89% | 43.74% | 0% | 0% | 0% | 30.51% | 0% | 43.35% | 0% | 0% | 20.64% | 0% | 0% | 0% | 0% | 0% | 24.96% | 15.62% | CZ 2A | 0% | 0% | -0.03846% | -6.805% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -1.387% | 15.62% | CZ 2A | 56.89% | 43.74% | -0.03846% | -6.805% | 0% | 30.51% | 0% | 43.35% | 0% | 0% | 20.64% | 0% | 0% | 0% | 0% | 0% | 17.76% | 15.62%
CZ 2B | 57.3% | 43.74% | -0.06176% | -21.53% | 0% | 27.31% | 0% | 41.48% | 0% | 0% | 21.01% | 0% | 0% | 0% | 0% | 0% | 18.29% | 3.461% | CZ 2B | 57.3% | 43.74% | -0.06176% | -21.53% | 0% | 27.31% | 0% | 41.48% | 0% | 0% | 21.01% | 0% | 0% | 0% | 0% | 0% | 11.51% | 3.461% | CZ 2B | 57.3% | 43.74% | 0% | 0% | 0% | 27.31% | 0% | 41.48% | 0% | 0% | 21.01% | 0% | 0% | 0% | 0% | 0% | 24.59% | 3.461% | CZ 2B | 0% | 0% | -0.06176% | -21.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.92% | 3.461% | CZ 2B | 57.3% | 43.74% | -0.06176% | -21.53% | 0% | 27.31% | 0% | 41.48% | 0% | 0% | 21.01% | 0% | 0% | 0% | 0% | 0% | 17.87% | 3.461%
CZ 3A | 56.61% | 43.69% | -0.07065% | -1.875% | 0% | 30.96% | 0% | 45.67% | 0% | 0% | 21.17% | 0% | 0% | 0% | 0% | 0% | 17.18% | 17.35% | CZ 3A | 56.61% | 43.69% | -0.07065% | -1.875% | 0% | 30.96% | 0% | 45.67% | 0% | 0% | 21.17% | 0% | 0% | 0% | 0% | 0% | 10.3% | 17.35% | CZ 3A | 56.61% | 43.69% | 0% | 0% | 0% | 30.96% | 0% | 45.67% | 0% | 0% | 21.17% | 0% | 0% | 0% | 0% | 0% | 25.06% | 17.35% | CZ 3A | 0% | 0% | -0.07065% | -1.875% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.6055% | 17.35% | CZ 3A | 56.61% | 43.69% | -0.07065% | -1.875% | 0% | 30.96% | 0% | 45.67% | 0% | 0% | 21.17% | 0% | 0% | 0% | 0% | 0% | 16.71% | 17.35%
CZ 3B | 57.02% | 43.74% | -0.06657% | -16.62% | 0% | 30.11% | 0% | 47.01% | 0% | 0% | 21.28% | 0% | 0% | 0% | 0% | 0% | 17.31% | 10.77% | CZ 3B | 57.02% | 43.74% | -0.06657% | -16.62% | 0% | 30.11% | 0% | 47.01% | 0% | 0% | 21.28% | 0% | 0% | 0% | 0% | 0% | 9.656% | 10.77% | CZ 3B | 57.02% | 43.74% | 0% | 0% | 0% | 30.11% | 0% | 47.01% | 0% | 0% | 21.28% | 0% | 0% | 0% | 0% | 0% | 25.48% | 10.77% | CZ 3B | 0% | 0% | -0.06657% | -16.62% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -3.597% | 10.77% | CZ 3B | 57.02% | 43.74% | -0.06657% | -16.62% | 0% | 30.11% | 0% | 47.01% | 0% | 0% | 21.28% | 0% | 0% | 0% | 0% | 0% | 16.8% | 10.77%
CZ 3C | 56.81% | 43.7% | -0.1245% | 9.441% | 0% | 50.67% | 0% | 36.82% | 0% | 0% | 21.72% | 0% | 0% | 0% | 0% | 0% | 14.91% | 1.179% | CZ 3C | 56.81% | 43.7% | -0.1245% | 9.441% | 0% | 50.67% | 0% | 36.82% | 0% | 0% | 21.72% | 0% | 0% | 0% | 0% | 0% | 9.821% | 1.179% | CZ 3C | 56.81% | 43.7% | 0% | 0% | 0% | 50.67% | 0% | 36.82% | 0% | 0% | 21.72% | 0% | 0% | 0% | 0% | 0% | 21.71% | 1.179% | CZ 3C | 0% | 0% | -0.1245% | 9.441% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.995% | 1.179% | CZ 3C | 56.81% | 43.7% | -0.1245% | 9.441% | 0% | 50.67% | 0% | 36.82% | 0% | 0% | 21.72% | 0% | 0% | 0% | 0% | 0% | 14.54% | 1.179%
CZ 4A | 57.06% | 43.68% | -0.06957% | 12.82% | 0% | 36.85% | 0% | 52.11% | 0% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 18.73% | 15.17% | CZ 4A | 57.06% | 43.68% | -0.06957% | 12.82% | 0% | 36.85% | 0% | 52.11% | 0% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 12.96% | 15.17% | CZ 4A | 57.06% | 43.68% | 0% | 0% | 0% | 36.85% | 0% | 52.11% | 0% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 26.48% | 15.17% | CZ 4A | 0% | 0% | -0.06957% | 12.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.288% | 15.17% | CZ 4A | 57.06% | 43.68% | -0.06957% | 12.82% | 0% | 36.85% | 0% | 52.11% | 0% | 0% | 21.5% | 0% | 0% | 0% | 0% | 0% | 18.31% | 15.17%
CZ 4B | 57.26% | 43.74% | -0.01628% | 1.159% | 0% | 37.22% | 0% | 55.05% | 0% | 0% | 21.27% | 0% | 0% | 0% | 0% | 0% | 18.6% | 0.908% | CZ 4B | 57.26% | 43.74% | -0.01628% | 1.159% | 0% | 37.22% | 0% | 55.05% | 0% | 0% | 21.27% | 0% | 0% | 0% | 0% | 0% | 11.26% | 0.908% | CZ 4B | 57.26% | 43.74% | 0% | 0% | 0% | 37.22% | 0% | 55.05% | 0% | 0% | 21.27% | 0% | 0% | 0% | 0% | 0% | 27.51% | 0.908% | CZ 4B | 0% | 0% | -0.01628% | 1.159% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.3565% | 0.908% | CZ 4B | 57.26% | 43.74% | -0.01628% | 1.159% | 0% | 37.22% | 0% | 55.05% | 0% | 0% | 21.27% | 0% | 0% | 0% | 0% | 0% | 18.09% | 0.908%
CZ 4C | 56.86% | 43.59% | -0.1134% | 15.95% | 0% | 35.87% | 0% | 54.7% | 0% | 0% | 21.88% | 0% | 0% | 0% | 0% | 0% | 18.42% | 2.44% | CZ 4C | 56.86% | 43.59% | -0.1134% | 15.95% | 0% | 35.87% | 0% | 54.7% | 0% | 0% | 21.88% | 0% | 0% | 0% | 0% | 0% | 13.15% | 2.44% | CZ 4C | 56.86% | 43.59% | 0% | 0% | 0% | 35.87% | 0% | 54.7% | 0% | 0% | 21.88% | 0% | 0% | 0% | 0% | 0% | 25.94% | 2.44% | CZ 4C | 0% | 0% | -0.1134% | 15.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.539% | 2.44% | CZ 4C | 56.86% | 43.59% | -0.1134% | 15.95% | 0% | 35.87% | 0% | 54.7% | 0% | 0% | 21.88% | 0% | 0% | 0% | 0% | 0% | 18.02% | 2.44%
CZ 5A | 56.86% | 43.46% | -0.06543% | 13.39% | 0% | 36.48% | 0% | 52.16% | 0% | 0% | 21.66% | 0% | 0% | 0% | 0% | 0% | 17.96% | 21.9% | CZ 5A | 56.86% | 43.46% | -0.06543% | 13.39% | 0% | 36.48% | 0% | 52.16% | 0% | 0% | 21.66% | 0% | 0% | 0% | 0% | 0% | 12.74% | 21.9% | CZ 5A | 56.86% | 43.46% | 0% | 0% | 0% | 36.48% | 0% | 52.16% | 0% | 0% | 21.66% | 0% | 0% | 0% | 0% | 0% | 25.98% | 21.9% | CZ 5A | 0% | 0% | -0.06543% | 13.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.603% | 21.9% | CZ 5A | 56.86% | 43.46% | -0.06543% | 13.39% | 0% | 36.48% | 0% | 52.16% | 0% | 0% | 21.66% | 0% | 0% | 0% | 0% | 0% | 17.56% | 21.9%
CZ 5B | 57.25% | 43.79% | -0.06105% | 9.676% | 0% | 35.13% | 0% | 55.68% | 0% | 0% | 21.74% | 0% | 0% | 0% | 0% | 0% | 18.36% | 4.373% | CZ 5B | 57.25% | 43.79% | -0.06105% | 9.676% | 0% | 35.13% | 0% | 55.68% | 0% | 0% | 21.74% | 0% | 0% | 0% | 0% | 0% | 12.08% | 4.373% | CZ 5B | 57.25% | 43.79% | 0% | 0% | 0% | 35.13% | 0% | 55.68% | 0% | 0% | 21.74% | 0% | 0% | 0% | 0% | 0% | 27.11% | 4.373% | CZ 5B | 0% | 0% | -0.06105% | 9.676% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.036% | 4.373% | CZ 5B | 57.25% | 43.79% | -0.06105% | 9.676% | 0% | 35.13% | 0% | 55.68% | 0% | 0% | 21.74% | 0% | 0% | 0% | 0% | 0% | 17.89% | 4.373%
CZ 5C | 56.01% | 43.45% | -0.1811% | 22.94% | 0% | 48.73% | 0% | 52.15% | 0% | 0% | 22.39% | 0% | 0% | 0% | 0% | 0% | 18.22% | 0% | CZ 5C | 56.01% | 43.45% | -0.1811% | 22.94% | 0% | 48.73% | 0% | 52.15% | 0% | 0% | 22.39% | 0% | 0% | 0% | 0% | 0% | 14.73% | 0% | CZ 5C | 56.01% | 43.45% | 0% | 0% | 0% | 48.73% | 0% | 52.15% | 0% | 0% | 22.39% | 0% | 0% | 0% | 0% | 0% | 23.94% | 0% | CZ 5C | 0% | 0% | -0.1811% | 22.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.82% | 0% | CZ 5C | 56.01% | 43.45% | -0.1811% | 22.94% | 0% | 48.73% | 0% | 52.15% | 0% | 0% | 22.39% | 0% | 0% | 0% | 0% | 0% | 17.95% | 0%
CZ 6A | 56.77% | 43.41% | -0.09563% | 15.16% | 0% | 38.7% | 0% | 51.67% | 0% | 0% | 21.99% | 0% | 0% | 0% | 0% | 0% | 17.49% | 4.324% | CZ 6A | 56.77% | 43.41% | -0.09563% | 15.16% | 0% | 38.7% | 0% | 51.67% | 0% | 0% | 21.99% | 0% | 0% | 0% | 0% | 0% | 12.96% | 4.324% | CZ 6A | 56.77% | 43.41% | 0% | 0% | 0% | 38.7% | 0% | 51.67% | 0% | 0% | 21.99% | 0% | 0% | 0% | 0% | 0% | 25.24% | 4.324% | CZ 6A | 0% | 0% | -0.09563% | 15.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.075% | 4.324% | CZ 6A | 56.77% | 43.41% | -0.09563% | 15.16% | 0% | 38.7% | 0% | 51.67% | 0% | 0% | 21.99% | 0% | 0% | 0% | 0% | 0% | 17.13% | 4.324%
CZ 6B | 57.22% | 43.68% | -0.04746% | 10.17% | 0% | 38.45% | 0% | 55.23% | 0% | 0% | 21.86% | 0% | 0% | 0% | 0% | 0% | 17.38% | 0.5275% | CZ 6B | 57.22% | 43.68% | -0.04746% | 10.17% | 0% | 38.45% | 0% | 55.23% | 0% | 0% | 21.86% | 0% | 0% | 0% | 0% | 0% | 11.59% | 0.5275% | CZ 6B | 57.22% | 43.68% | 0% | 0% | 0% | 38.45% | 0% | 55.23% | 0% | 0% | 21.86% | 0% | 0% | 0% | 0% | 0% | 26.58% | 0.5275% | CZ 6B | 0% | 0% | -0.04746% | 10.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.968% | 0.5275% | CZ 6B | 57.22% | 43.68% | -0.04746% | 10.17% | 0% | 38.45% | 0% | 55.23% | 0% | 0% | 21.86% | 0% | 0% | 0% | 0% | 0% | 16.93% | 0.5275%
CZ 7 | 57.27% | 43.51% | -0.0753% | 14.72% | 0% | 42.84% | 0% | 51.5% | 0% | 0% | 22.08% | 0% | 0% | 0% | 0% | 0% | 16.88% | 0.6086% | CZ 7 | 57.27% | 43.51% | -0.0753% | 14.72% | 0% | 42.84% | 0% | 51.5% | 0% | 0% | 22.08% | 0% | 0% | 0% | 0% | 0% | 12.72% | 0.6086% | CZ 7 | 57.27% | 43.51% | 0% | 0% | 0% | 42.84% | 0% | 51.5% | 0% | 0% | 22.08% | 0% | 0% | 0% | 0% | 0% | 24.96% | 0.6086% | CZ 7 | 0% | 0% | -0.0753% | 14.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.624% | 0.6086% | CZ 7 | 57.27% | 43.51% | -0.0753% | 14.72% | 0% | 42.84% | 0% | 51.5% | 0% | 0% | 22.08% | 0% | 0% | 0% | 0% | 0% | 16.54% | 0.6086%
CZ 8 | 56.34% | 42.75% | -0.1789% | 17.23% | 0% | 50.07% | 0% | 49.08% | 0% | 0% | 23.12% | 0% | 0% | 0% | 0% | 0% | 16.91% | 0.03762% | CZ 8 | 56.34% | 42.75% | -0.1789% | 17.23% | 0% | 50.07% | 0% | 49.08% | 0% | 0% | 23.12% | 0% | 0% | 0% | 0% | 0% | 14.07% | 0.03762% | CZ 8 | 56.34% | 42.75% | 0% | 0% | 0% | 50.07% | 0% | 49.08% | 0% | 0% | 23.12% | 0% | 0% | 0% | 0% | 0% | 23.92% | 0.03762% | CZ 8 | 0% | 0% | -0.1789% | 17.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.65% | 0.03762% | CZ 8 | 56.34% | 42.75% | -0.1789% | 17.23% | 0% | 50.07% | 0% | 49.08% | 0% | 0% | 23.12% | 0% | 0% | 0% | 0% | 0% | 16.66% | 0.03762%
Us Weighted | 56.9% | 43.64% | -0.0651% | 8.128% | 0% | 32.09% | 0% | 48.41% | 0% | 0% | 21.33% | 0% | 0% | 0% | 0% | 0% | 17.9% | 100% | Us Weighted | 56.9% | 43.64% | -0.0651% | 8.128% | 0% | 32.09% | 0% | 48.41% | 0% | 0% | 21.33% | 0% | 0% | 0% | 0% | 0% | 11.79% | 100% | Us Weighted | 56.9% | 43.64% | 0% | 0% | 0% | 32.09% | 0% | 48.41% | 0% | 0% | 21.33% | 0% | 0% | 0% | 0% | 0% | 25.54% | 100% | Us Weighted | 0% | 0% | -0.0651% | 8.128% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.059% | 100% | Us Weighted | 56.9% | 43.64% | -0.0651% | 8.128% | 0% | 32.09% | 0% | 48.41% | 0% | 0% | 21.33% | 0% | 0% | 0% | 0% | 0% | 17.46% | 100%

## Restaurant
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Full-service Restaurant | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.37178 | 0.17255 | 0.92479 | 0.81604 | 0 | 0.59382 | 0 | 0.56032 | 0 | 0.0023446 | 0.43488 | 0 | 0 | 2.9771 | 0 | 0 | 6.8537 |  | STD2013 | 12.2953 | 5.7064 | 66.7013 | 82.4282 | 0 | 19.6385 | 0 | 18.5305 | 0 | 0.077539 | 14.3821 | 0 | 0 | 152.9054 | 0 | 0 | 372.6653 |  | STD2013 | 3.6025 | 1.672 | 3.8098 | 0 | 0 | 5.754 | 0 | 5.4294 | 0 | 0.022719 | 4.2139 | 0 | 0 | 21.0827 | 0 | 0 | 45.5871 |  | STD2013 | 0 | 0 | 0.53698 | 0.82428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.1708 |  | STD2013 | 37.7146 | 17.5039 | 98.5772 | 90.094 | 0 | 60.2389 | 0 | 56.8402 | 0 | 0.23784 | 44.1156 | 0 | 0 | 309.1936 | 0 | 0 | 714.5158
STD2010 | 0.39942 | 0.17255 | 0.92484 | 0.8491 | 0 | 0.63813 | 0 | 0.76913 | 0 | 0.0023446 | 0.55385 | 0 | 0 | 2.9771 | 0 | 0 | 7.2865 |  | STD2010 | 13.2094 | 5.7064 | 66.7044 | 85.768 | 0 | 21.1037 | 0 | 25.4361 | 0 | 0.077539 | 18.3167 | 0 | 0 | 152.9054 | 0 | 0 | 389.2278 |  | STD2010 | 3.8703 | 1.672 | 3.81 | 0 | 0 | 6.1833 | 0 | 7.4527 | 0 | 0.022719 | 5.3668 | 0 | 0 | 21.0827 | 0 | 0 | 49.4606 |  | STD2010 | 0 | 0 | 0.53701 | 0.85768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2042 |  | STD2010 | 40.5184 | 17.5039 | 98.5823 | 93.7444 | 0 | 64.7334 | 0 | 78.0224 | 0 | 0.23784 | 56.1845 | 0 | 0 | 309.1936 | 0 | 0 | 758.7207
STD2007 | 0.96728 | 0.30253 | 0.93645 | 0.91331 | 0 | 0.94757 | 0 | 1.296 | 0 | 0.0023446 | 0.55447 | 0 | 0 | 2.9771 | 0 | 0 | 8.8971 |  | STD2007 | 31.9893 | 10.0053 | 67.1131 | 92.2535 | 0 | 31.3374 | 0 | 42.859 | 0 | 0.077539 | 18.3373 | 0 | 0 | 152.9054 | 0 | 0 | 446.8778 |  | STD2007 | 9.3728 | 2.9315 | 3.9191 | 0 | 0 | 9.1818 | 0 | 12.5576 | 0 | 0.022719 | 5.3728 | 0 | 0 | 21.0827 | 0 | 0 | 64.4409 |  | STD2007 | 0 | 0 | 0.53737 | 0.92254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2694 |  | STD2007 | 98.1235 | 30.69 | 99.7635 | 100.8331 | 0 | 96.1241 | 0 | 131.4653 | 0 | 0.23784 | 56.2475 | 0 | 0 | 309.1936 | 0 | 0 | 922.6784
STD2004 | 0.96728 | 0.30253 | 0.9357 | 1.0933 | 0 | 0.94371 | 0 | 1.4846 | 0 | 0.0023446 | 0.55778 | 0 | 0 | 2.9771 | 0 | 0 | 9.2643 |  | STD2004 | 31.9893 | 10.0053 | 67.0562 | 110.4323 | 0 | 31.2097 | 0 | 49.097 | 0 | 0.077539 | 18.4466 | 0 | 0 | 152.9054 | 0 | 0 | 471.2194 |  | STD2004 | 9.3728 | 2.9315 | 3.9164 | 0 | 0 | 9.1444 | 0 | 14.3853 | 0 | 0.022719 | 5.4048 | 0 | 0 | 21.0827 | 0 | 0 | 66.2606 |  | STD2004 | 0 | 0 | 0.5369 | 1.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4507 |  | STD2004 | 98.1235 | 30.69 | 99.6834 | 120.7025 | 0 | 95.7324 | 0 | 150.5996 | 0 | 0.23784 | 56.5829 | 0 | 0 | 309.1936 | 0 | 0 | 961.5459
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | -0.00074736 | 0.17997 | 0 | -0.0038608 | 0 | 0.18862 | 0 | 0 | 0.0033067 | 0 | 0 | 0 | 0 | 0 | 0.36729 |  | 2004-2007 | 0 | 0 | -0.056881 | 18.1788 | 0 | -0.12768 | 0 | 6.238 | 0 | 0 | 0.10936 | 0 | 0 | 0 | 0 | 0 | 24.3416 |  | 2004-2007 | 0 | 0 | -0.0026543 | 0 | 0 | -0.037411 | 0 | 1.8277 | 0 | 0 | 0.032041 | 0 | 0 | 0 | 0 | 0 | 1.8197 |  | 2004-2007 | 0 | 0 | -0.00047822 | 0.18179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18131 |  | 2004-2007 | 0 | 0 | -0.080057 | 19.8694 | 0 | -0.39165 | 0 | 19.1343 | 0 | 0 | 0.33544 | 0 | 0 | 0 | 0 | 0 | 38.8675
2007-2010 | 0.56786 | 0.12999 | 0.011612 | 0.064207 | 0 | 0.30944 | 0 | 0.52683 | 0 | 0 | 0.00062084 | 0 | 0 | 0 | 0 | 0 | 1.6106 |  | 2007-2010 | 18.7798 | 4.2988 | 0.40866 | 6.4855 | 0 | 10.2337 | 0 | 17.4229 | 0 | 0 | 0.020532 | 0 | 0 | 0 | 0 | 0 | 57.65 |  | 2007-2010 | 5.5024 | 1.2595 | 0.109 | 0 | 0 | 2.9984 | 0 | 5.1049 | 0 | 0 | 0.0060158 | 0 | 0 | 0 | 0 | 0 | 14.9803 |  | 2007-2010 | 0 | 0 | 0.00036626 | 0.064855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065222 |  | 2007-2010 | 57.6051 | 13.1862 | 1.1812 | 7.0887 | 0 | 31.3907 | 0 | 53.4429 | 0 | 0 | 0.06298 | 0 | 0 | 0 | 0 | 0 | 163.9577
2010-2013 | 0.027639 | 0 | 4.866e-05 | 0.033064 | 0 | 0.044305 | 0 | 0.20881 | 0 | 0 | 0.11897 | 0 | 0 | 0 | 0 | 0 | 0.43284 |  | 2010-2013 | 0.91408 | 0 | 0.0031401 | 3.3398 | 0 | 1.4652 | 0 | 6.9056 | 0 | 0 | 3.9346 | 0 | 0 | 0 | 0 | 0 | 16.5625 |  | 2010-2013 | 0.26782 | 0 | 0.00025317 | 0 | 0 | 0.42931 | 0 | 2.0233 | 0 | 0 | 1.1528 | 0 | 0 | 0 | 0 | 0 | 3.8735 |  | 2010-2013 | 0 | 0 | 2.276e-05 | 0.033398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033421 |  | 2010-2013 | 2.8038 | 0 | 0.0051381 | 3.6504 | 0 | 4.4944 | 0 | 21.1822 | 0 | 0 | 12.0689 | 0 | 0 | 0 | 0 | 0 | 44.2049
2004-2013 | 0.5955 | 0.12999 | 0.010913 | 0.27724 | 0 | 0.34989 | 0 | 0.92426 | 0 | 0 | 0.1229 | 0 | 0 | 0 | 0 | 0 | 2.4107 |  | 2004-2013 | 19.6939 | 4.2988 | 0.35492 | 28.0042 | 0 | 11.5712 | 0 | 30.5665 | 0 | 0 | 4.0645 | 0 | 0 | 0 | 0 | 0 | 98.554 |  | 2004-2013 | 5.7703 | 1.2595 | 0.1066 | 0 | 0 | 3.3903 | 0 | 8.9559 | 0 | 0 | 1.1909 | 0 | 0 | 0 | 0 | 0 | 20.6735 |  | 2004-2013 | 0 | 0 | -8.9202e-05 | 0.28004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27995 |  | 2004-2013 | 60.4089 | 13.1862 | 1.1063 | 30.6085 | 0 | 35.4935 | 0 | 93.7594 | 0 | 0 | 12.4673 | 0 | 0 | 0 | 0 | 0 | 247.0301
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | -0.07987% | 16.46% |  | -0.4091% |  | 12.71% |  | 0% | 0.5928% |  |  | 0% |  |  | 3.965% |  | 2004-2007 | 0% | 0% | -0.08483% | 16.46% |  | -0.4091% |  | 12.71% |  | 0% | 0.5928% |  |  | 0% |  |  | 5.166% |  | 2004-2007 | 0% | 0% | -0.06777% |  |  | -0.4091% |  | 12.71% |  | 0% | 0.5928% |  |  | 0% |  |  | 2.746% |  | 2004-2007 |  |  | -0.08907% | 16.46% | [9 empty] | 0% |  |  | 7.398% |  | 2004-2007 | 0% | 0% | -0.08031% | 16.46% |  | -0.4091% |  | 12.71% |  | 0% | 0.5928% |  |  | 0% |  |  | 4.042%
2007-2010 | 58.71% | 42.97% | 1.24% | 7.03% |  | 32.66% |  | 40.65% |  | 0% | 0.112% |  |  | 0% |  |  | 18.1% |  | 2007-2010 | 58.71% | 42.97% | 0.6089% | 7.03% |  | 32.66% |  | 40.65% |  | 0% | 0.112% |  |  | 0% |  |  | 12.9% |  | 2007-2010 | 58.71% | 42.97% | 2.781% |  |  | 32.66% |  | 40.65% |  | 0% | 0.112% |  |  | 0% |  |  | 23.25% |  | 2007-2010 |  |  | 0.06816% | 7.03% | [9 empty] | 0% |  |  | 2.874% |  | 2007-2010 | 58.71% | 42.97% | 1.184% | 7.03% |  | 32.66% |  | 40.65% |  | 0% | 0.112% |  |  | 0% |  |  | 17.77%
2010-2013 | 6.92% | 0% | 0.005261% | 3.894% |  | 6.943% |  | 27.15% |  | 0% | 21.48% |  |  | 0% |  |  | 5.94% |  | 2010-2013 | 6.92% | 0% | 0.004707% | 3.894% |  | 6.943% |  | 27.15% |  | 0% | 21.48% |  |  | 0% |  |  | 4.255% |  | 2010-2013 | 6.92% | 0% | 0.006645% |  |  | 6.943% |  | 27.15% |  | 0% | 21.48% |  |  | 0% |  |  | 7.832% |  | 2010-2013 |  |  | 0.004238% | 3.894% | [9 empty] | 0% |  |  | 1.516% |  | 2010-2013 | 6.92% | 0% | 0.005212% | 3.894% |  | 6.943% |  | 27.15% |  | 0% | 21.48% |  |  | 0% |  |  | 5.826%
2004-2013 | 61.56% | 42.97% | 1.166% | 25.36% |  | 37.08% |  | 62.26% |  | 0% | 22.03% |  |  | 0% |  |  | 26.02% |  | 2004-2013 | 61.56% | 42.97% | 0.5293% | 25.36% |  | 37.08% |  | 62.26% |  | 0% | 22.03% |  |  | 0% |  |  | 20.91% |  | 2004-2013 | 61.56% | 42.97% | 2.722% |  |  | 37.08% |  | 62.26% |  | 0% | 22.03% |  |  | 0% |  |  | 31.2% |  | 2004-2013 |  |  | -0.01661% | 25.36% | [9 empty] | 0% |  |  | 11.42% |  | 2004-2013 | 61.56% | 42.97% | 1.11% | 25.36% |  | 37.08% |  | 62.26% |  | 0% | 22.03% |  |  | 0% |  |  | 25.69%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.37066 | 0.17246 | 0.79993 | 0.051675 | 0 | 1.5319 | 0 | 0.64461 | 0 | 0.0023446 | 0.45011 | 0 | 0 | 2.9771 | 0 | 0 | 7.0008 | 1.368% | CZ 1A | 12.2581 | 5.7034 | 54.1107 | 5.2197 | 0 | 50.6607 | 0 | 21.3181 | 0 | 0.077539 | 14.8859 | 0 | 0 | 152.9054 | 0 | 0 | 317.1396 | 1.368% | CZ 1A | 3.5916 | 1.6711 | 3.8067 | 0 | 0 | 14.8435 | 0 | 6.2462 | 0 | 0.022719 | 4.3615 | 0 | 0 | 21.0827 | 0 | 0 | 55.6259 | 1.368% | CZ 1A | 0 | 0 | 0.41119 | 0.052197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.2729 | 1.368% | CZ 1A | 37.6004 | 17.4947 | 84.7946 | 5.7051 | 0 | 155.3962 | 0 | 65.391 | 0 | 0.23784 | 45.6608 | 0 | 0 | 309.1936 | 0 | 0 | 721.4741 | 1.368%
CZ 1B | 0.37165 | 0.17246 | 0.77731 | 0.10071 | 0 | 1.5281 | 0 | 0.99896 | 0 | 0.0023446 | 0.4424 | 0 | 0 | 2.9771 | 0 | 0 | 7.3711 | 0% | CZ 1B | 12.2908 | 5.7034 | 51.823 | 10.1724 | 0 | 50.5367 | 0 | 33.0369 | 0 | 0.077539 | 14.6309 | 0 | 0 | 152.9054 | 0 | 0 | 331.1771 | 0% | CZ 1B | 3.6012 | 1.6711 | 3.8072 | 0 | 0 | 14.8071 | 0 | 9.6797 | 0 | 0.022719 | 4.2868 | 0 | 0 | 21.0827 | 0 | 0 | 58.9585 | 0% | CZ 1B | 0 | 0 | 0.38829 | 0.10172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.2995 | 0% | CZ 1B | 37.7008 | 17.4947 | 82.2975 | 11.1184 | 0 | 155.0156 | 0 | 101.337 | 0 | 0.23784 | 44.8785 | 0 | 0 | 309.1936 | 0 | 0 | 759.274 | 0%
CZ 2A | 0.37196 | 0.17241 | 0.85319 | 0.30763 | 0 | 1.0772 | 0 | 0.60048 | 0 | 0.0023446 | 0.44292 | 0 | 0 | 2.9771 | 0 | 0 | 6.8052 | 16% | CZ 2A | 12.3012 | 5.7017 | 59.4803 | 31.0737 | 0 | 35.6233 | 0 | 19.8587 | 0 | 0.077539 | 14.6481 | 0 | 0 | 152.9054 | 0 | 0 | 331.6698 | 16% | CZ 2A | 3.6042 | 1.6706 | 3.8082 | 0 | 0 | 10.4375 | 0 | 5.8185 | 0 | 0.022719 | 4.2918 | 0 | 0 | 21.0827 | 0 | 0 | 50.7363 | 16% | CZ 2A | 0 | 0 | 0.46483 | 0.31074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.5851 | 16% | CZ 2A | 37.7325 | 17.4894 | 90.6737 | 33.9635 | 0 | 109.2704 | 0 | 60.9143 | 0 | 0.23784 | 44.9314 | 0 | 0 | 309.1936 | 0 | 0 | 704.4066 | 16%
CZ 2B | 0.36758 | 0.17235 | 0.82237 | 0.18516 | 0 | 1.284 | 0 | 0.91731 | 0 | 0.0023446 | 0.44105 | 0 | 0 | 2.9771 | 0 | 0 | 7.1693 | 3.722% | CZ 2B | 12.1564 | 5.7 | 56.3709 | 18.7031 | 0 | 42.4622 | 0 | 30.3368 | 0 | 0.077539 | 14.5861 | 0 | 0 | 152.9054 | 0 | 0 | 333.2985 | 3.722% | CZ 2B | 3.5618 | 1.6701 | 3.8077 | 0 | 0 | 12.4413 | 0 | 8.8886 | 0 | 0.022719 | 4.2737 | 0 | 0 | 21.0827 | 0 | 0 | 55.7486 | 3.722% | CZ 2B | 0 | 0 | 0.43375 | 0.18703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.4303 | 3.722% | CZ 2B | 37.2885 | 17.4841 | 87.2717 | 20.4425 | 0 | 130.2482 | 0 | 93.0548 | 0 | 0.23784 | 44.7411 | 0 | 0 | 309.1936 | 0 | 0 | 739.9624 | 3.722%
CZ 3A | 0.37482 | 0.17246 | 0.89489 | 0.61579 | 0 | 0.76622 | 0 | 0.56484 | 0 | 0.0023446 | 0.43714 | 0 | 0 | 2.9771 | 0 | 0 | 6.8056 | 16.86% | CZ 3A | 12.3959 | 5.7034 | 63.6854 | 62.2007 | 0 | 25.3398 | 0 | 18.6801 | 0 | 0.077539 | 14.4568 | 0 | 0 | 152.9054 | 0 | 0 | 355.4451 | 16.86% | CZ 3A | 3.632 | 1.6711 | 3.8092 | 0 | 0 | 7.4245 | 0 | 5.4732 | 0 | 0.022719 | 4.2358 | 0 | 0 | 21.0827 | 0 | 0 | 47.3512 | 16.86% | CZ 3A | 0 | 0 | 0.50685 | 0.62201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9384 | 16.86% | CZ 3A | 38.0232 | 17.4947 | 95.2767 | 67.9854 | 0 | 77.7271 | 0 | 57.2991 | 0 | 0.23784 | 44.3447 | 0 | 0 | 309.1936 | 0 | 0 | 707.5822 | 16.86%
CZ 3B | 0.36993 | 0.17235 | 0.88116 | 0.34865 | 0 | 0.6593 | 0 | 0.81248 | 0 | 0.0023446 | 0.43693 | 0 | 0 | 2.9771 | 0 | 0 | 6.6603 | 7.194% | CZ 3B | 12.234 | 5.7 | 62.2986 | 35.2167 | 0 | 21.804 | 0 | 26.8699 | 0 | 0.077539 | 14.4499 | 0 | 0 | 152.9054 | 0 | 0 | 331.5561 | 7.194% | CZ 3B | 3.5845 | 1.6701 | 3.8092 | 0 | 0 | 6.3885 | 0 | 7.8728 | 0 | 0.022719 | 4.2338 | 0 | 0 | 21.0827 | 0 | 0 | 48.6644 | 7.194% | CZ 3B | 0 | 0 | 0.49298 | 0.35217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6546 | 7.194% | CZ 3B | 37.5264 | 17.4841 | 93.7609 | 38.4918 | 0 | 66.8815 | 0 | 82.4206 | 0 | 0.23784 | 44.3236 | 0 | 0 | 309.1936 | 0 | 0 | 690.3203 | 7.194%
CZ 3C | 0.37269 | 0.17235 | 0.93998 | 0.56594 | 0 | 0.037201 | 0 | 0.38024 | 0 | 0.0023446 | 0.43339 | 0 | 0 | 2.9771 | 0 | 0 | 5.8813 | 0.8731% | CZ 3C | 12.3253 | 5.7 | 68.2332 | 57.1653 | 0 | 1.2303 | 0 | 12.5751 | 0 | 0.077539 | 14.3328 | 0 | 0 | 152.9054 | 0 | 0 | 324.545 | 0.8731% | CZ 3C | 3.6113 | 1.6701 | 3.8102 | 0 | 0 | 0.36047 | 0 | 3.6845 | 0 | 0.022719 | 4.1995 | 0 | 0 | 21.0827 | 0 | 0 | 38.4414 | 0.8731% | CZ 3C | 0 | 0 | 0.55229 | 0.57165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9334 | 0.8731% | CZ 3C | 37.8065 | 17.4841 | 100.2543 | 62.4817 | 0 | 3.7738 | 0 | 38.5729 | 0 | 0.23784 | 43.9641 | 0 | 0 | 309.1936 | 0 | 0 | 613.7688 | 0.8731%
CZ 4A | 0.37045 | 0.17241 | 0.9459 | 0.91642 | 0 | 0.42229 | 0 | 0.50013 | 0 | 0.0023446 | 0.43266 | 0 | 0 | 2.9771 | 0 | 0 | 6.7397 | 19.27% | CZ 4A | 12.2512 | 5.7017 | 68.831 | 92.5681 | 0 | 13.9657 | 0 | 16.54 | 0 | 0.077539 | 14.3086 | 0 | 0 | 152.9054 | 0 | 0 | 377.1493 | 19.27% | CZ 4A | 3.5896 | 1.6706 | 3.8102 | 0 | 0 | 4.0919 | 0 | 4.8462 | 0 | 0.022719 | 4.1924 | 0 | 0 | 21.0827 | 0 | 0 | 43.3063 | 19.27% | CZ 4A | 0 | 0 | 0.55827 | 0.92568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2934 | 19.27% | CZ 4A | 37.5792 | 17.4894 | 100.9076 | 101.1769 | 0 | 42.8382 | 0 | 50.7346 | 0 | 0.23784 | 43.8901 | 0 | 0 | 309.1936 | 0 | 0 | 704.0475 | 19.27%
CZ 4B | 0.36789 | 0.1723 | 0.93806 | 0.58644 | 0 | 0.33246 | 0 | 0.55379 | 0 | 0.0023446 | 0.43271 | 0 | 0 | 2.9771 | 0 | 0 | 6.3631 | 0.8813% | CZ 4B | 12.1668 | 5.6983 | 68.042 | 59.236 | 0 | 10.9951 | 0 | 18.3148 | 0 | 0.077539 | 14.3104 | 0 | 0 | 152.9054 | 0 | 0 | 341.7462 | 0.8813% | CZ 4B | 3.5648 | 1.6696 | 3.8097 | 0 | 0 | 3.2215 | 0 | 5.3662 | 0 | 0.022719 | 4.1929 | 0 | 0 | 21.0827 | 0 | 0 | 42.9302 | 0.8813% | CZ 4B | 0 | 0 | 0.5504 | 0.59236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9523 | 0.8813% | CZ 4B | 37.3202 | 17.4788 | 100.0419 | 64.7449 | 0 | 33.7262 | 0 | 56.1786 | 0 | 0.23784 | 43.8954 | 0 | 0 | 309.1936 | 0 | 0 | 662.8174 | 0.8813%
CZ 4C | 0.37112 | 0.17256 | 0.96742 | 0.91122 | 0 | 0.16115 | 0 | 0.45715 | 0 | 0.0023446 | 0.4313 | 0 | 0 | 2.9771 | 0 | 0 | 6.4514 | 1.548% | CZ 4C | 12.2736 | 5.7069 | 71.0016 | 92.0427 | 0 | 5.3295 | 0 | 15.1184 | 0 | 0.077539 | 14.2638 | 0 | 0 | 152.9054 | 0 | 0 | 368.7195 | 1.548% | CZ 4C | 3.5961 | 1.6721 | 3.8107 | 0 | 0 | 1.5615 | 0 | 4.4297 | 0 | 0.022719 | 4.1793 | 0 | 0 | 21.0827 | 0 | 0 | 40.3549 | 1.548% | CZ 4C | 0 | 0 | 0.57996 | 0.92043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.3099 | 1.548% | CZ 4C | 37.6479 | 17.5053 | 103.2835 | 100.6026 | 0 | 16.3478 | 0 | 46.3741 | 0 | 0.23784 | 43.7527 | 0 | 0 | 309.1936 | 0 | 0 | 674.9453 | 1.548%
CZ 5A | 0.37258 | 0.17298 | 0.9815 | 1.3331 | 0 | 0.31433 | 0 | 0.48643 | 0 | 0.0023446 | 0.4301 | 0 | 0 | 2.9771 | 0 | 0 | 7.0705 | 21.68% | CZ 5A | 12.3219 | 5.7207 | 72.4193 | 134.6548 | 0 | 10.3954 | 0 | 16.0868 | 0 | 0.077539 | 14.2242 | 0 | 0 | 152.9054 | 0 | 0 | 418.8061 | 21.68% | CZ 5A | 3.6103 | 1.6761 | 3.8112 | 0 | 0 | 3.0458 | 0 | 4.7134 | 0 | 0.022719 | 4.1677 | 0 | 0 | 21.0827 | 0 | 0 | 42.13 | 21.68% | CZ 5A | 0 | 0 | 0.59412 | 1.3465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.7502 | 21.68% | CZ 5A | 37.7959 | 17.5475 | 104.8365 | 147.1777 | 0 | 31.8868 | 0 | 49.3445 | 0 | 0.23784 | 43.6312 | 0 | 0 | 309.1936 | 0 | 0 | 741.6516 | 21.68%
CZ 5B | 0.36847 | 0.17199 | 0.97512 | 0.97062 | 0 | 0.23941 | 0 | 0.4982 | 0 | 0.0023446 | 0.42901 | 0 | 0 | 2.9771 | 0 | 0 | 6.6323 | 4.706% | CZ 5B | 12.1857 | 5.6879 | 71.7785 | 98.0427 | 0 | 7.9176 | 0 | 16.4762 | 0 | 0.077539 | 14.188 | 0 | 0 | 152.9054 | 0 | 0 | 379.2597 | 4.706% | CZ 5B | 3.5704 | 1.6666 | 3.8107 | 0 | 0 | 2.3198 | 0 | 4.8275 | 0 | 0.022719 | 4.1571 | 0 | 0 | 21.0827 | 0 | 0 | 41.4575 | 4.706% | CZ 5B | 0 | 0 | 0.58773 | 0.98043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.3777 | 4.706% | CZ 5B | 37.3784 | 17.4471 | 104.1327 | 107.1607 | 0 | 24.2864 | 0 | 50.539 | 0 | 0.23784 | 43.5202 | 0 | 0 | 309.1936 | 0 | 0 | 693.8959 | 4.706%
CZ 5C | 0.38337 | 0.17277 | 0.98216 | 1.0933 | 0 | 0.029438 | 0 | 0.37972 | 0 | 0.0023446 | 0.42807 | 0 | 0 | 2.9771 | 0 | 0 | 6.4483 | 0% | CZ 5C | 12.6785 | 5.7138 | 72.4831 | 110.4305 | 0 | 0.97355 | 0 | 12.5579 | 0 | 0.077539 | 14.157 | 0 | 0 | 152.9054 | 0 | 0 | 381.9773 | 0% | CZ 5C | 3.7148 | 1.6741 | 3.8117 | 0 | 0 | 0.28525 | 0 | 3.6794 | 0 | 0.022719 | 4.148 | 0 | 0 | 21.0827 | 0 | 0 | 38.4187 | 0% | CZ 5C | 0 | 0 | 0.59474 | 1.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.5085 | 0% | CZ 5C | 38.89 | 17.5264 | 104.9096 | 120.7006 | 0 | 2.9863 | 0 | 38.52 | 0 | 0.23784 | 43.425 | 0 | 0 | 309.1936 | 0 | 0 | 676.3892 | 0%
CZ 6A | 0.37357 | 0.17308 | 1.013 | 1.5841 | 0 | 0.1734 | 0 | 0.45584 | 0 | 0.0023446 | 0.42797 | 0 | 0 | 2.9771 | 0 | 0 | 7.1805 | 4.701% | CZ 6A | 12.3546 | 5.7241 | 75.5977 | 160.0143 | 0 | 5.7345 | 0 | 15.0754 | 0 | 0.077539 | 14.1536 | 0 | 0 | 152.9054 | 0 | 0 | 441.6371 | 4.701% | CZ 6A | 3.6199 | 1.6772 | 3.8112 | 0 | 0 | 1.6802 | 0 | 4.417 | 0 | 0.022719 | 4.147 | 0 | 0 | 21.0827 | 0 | 0 | 40.4579 | 4.701% | CZ 6A | 0 | 0 | 0.6259 | 1.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.0355 | 4.701% | CZ 6A | 37.8963 | 17.5581 | 108.3104 | 174.8957 | 0 | 17.5898 | 0 | 46.242 | 0 | 0.23784 | 43.4145 | 0 | 0 | 309.1936 | 0 | 0 | 755.3382 | 4.701%
CZ 6B | 0.36868 | 0.1723 | 1.0175 | 1.3531 | 0 | 0.13229 | 0 | 0.48898 | 0 | 0.0023446 | 0.42698 | 0 | 0 | 2.9771 | 0 | 0 | 6.9393 | 0.6064% | CZ 6B | 12.1926 | 5.6983 | 76.0576 | 136.6789 | 0 | 4.3749 | 0 | 16.1712 | 0 | 0.077539 | 14.1208 | 0 | 0 | 152.9054 | 0 | 0 | 418.2774 | 0.6064% | CZ 6B | 3.5724 | 1.6696 | 3.8112 | 0 | 0 | 1.2818 | 0 | 4.7381 | 0 | 0.022719 | 4.1374 | 0 | 0 | 21.0827 | 0 | 0 | 40.316 | 0.6064% | CZ 6B | 0 | 0 | 0.6305 | 1.3668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.8068 | 0.6064% | CZ 6B | 37.3995 | 17.4788 | 108.8132 | 149.3901 | 0 | 13.4196 | 0 | 49.6035 | 0 | 0.23784 | 43.314 | 0 | 0 | 309.1936 | 0 | 0 | 728.8502 | 0.6064%
CZ 7 | 0.36701 | 0.17267 | 1.0627 | 2.0467 | 0 | 0.096337 | 0 | 0.44803 | 0 | 0.0023446 | 0.42588 | 0 | 0 | 2.9771 | 0 | 0 | 7.5988 | 0.5553% | CZ 7 | 12.1375 | 5.7103 | 80.6227 | 206.7333 | 0 | 3.186 | 0 | 14.8169 | 0 | 0.077539 | 14.0846 | 0 | 0 | 152.9054 | 0 | 0 | 490.2744 | 0.5553% | CZ 7 | 3.5563 | 1.6731 | 3.8117 | 0 | 0 | 0.93349 | 0 | 4.3413 | 0 | 0.022719 | 4.1268 | 0 | 0 | 21.0827 | 0 | 0 | 39.5481 | 0.5553% | CZ 7 | 0 | 0 | 0.67613 | 2.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.553 | 0.5553% | CZ 7 | 37.2304 | 17.5158 | 113.8062 | 225.9596 | 0 | 9.7727 | 0 | 45.4492 | 0 | 0.23784 | 43.203 | 0 | 0 | 309.1936 | 0 | 0 | 802.3683 | 0.5553%
CZ 8 | 0.37623 | 0.17366 | 1.124 | 3.1187 | 0 | 0.035273 | 0 | 0.41723 | 0 | 0.0023446 | 0.42333 | 0 | 0 | 2.9771 | 0 | 0 | 8.6479 | 0.02085% | CZ 8 | 12.4425 | 5.7431 | 86.8089 | 315.0191 | 0 | 1.1665 | 0 | 13.7985 | 0 | 0.077539 | 14.0002 | 0 | 0 | 152.9054 | 0 | 0 | 601.9618 | 0.02085% | CZ 8 | 3.6456 | 1.6827 | 3.8122 | 0 | 0 | 0.34179 | 0 | 4.0429 | 0 | 0.022719 | 4.102 | 0 | 0 | 21.0827 | 0 | 0 | 38.7327 | 0.02085% | CZ 8 | 0 | 0 | 0.73798 | 3.1502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 4.6977 | 0.02085% | CZ 8 | 38.1659 | 17.6163 | 120.5711 | 344.3159 | 0 | 3.5782 | 0 | 42.3255 | 0 | 0.23784 | 42.9441 | 0 | 0 | 309.1936 | 0 | 0 | 918.9483 | 0.02085%
Us Weighted | 0.37178 | 0.17255 | 0.92479 | 0.81604 | 0 | 0.59382 | 0 | 0.56032 | 0 | 0.0023446 | 0.43488 | 0 | 0 | 2.9771 | 0 | 0 | 6.8537 | 100% | Us Weighted | 12.2953 | 5.7064 | 66.7013 | 82.4282 | 0 | 19.6385 | 0 | 18.5305 | 0 | 0.077539 | 14.3821 | 0 | 0 | 152.9054 | 0 | 0 | 372.6653 | 100% | Us Weighted | 3.6025 | 1.672 | 3.8098 | 0 | 0 | 5.754 | 0 | 5.4294 | 0 | 0.022719 | 4.2139 | 0 | 0 | 21.0827 | 0 | 0 | 45.5871 | 100% | Us Weighted | 0 | 0 | 0.53698 | 0.82428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.1708 | 100% | Us Weighted | 37.7146 | 17.5039 | 98.5772 | 90.094 | 0 | 60.2389 | 0 | 56.8402 | 0 | 0.23784 | 44.1156 | 0 | 0 | 309.1936 | 0 | 0 | 714.5158 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.40379 | 0.17246 | 0.8001 | 0.074426 | 0 | 1.6487 | 0 | 0.88272 | 0 | 0.0023446 | 0.56729 | 0 | 0 | 2.9771 | 0 | 0 | 7.529 | 1.368% | CZ 1A | 13.354 | 5.7034 | 54.1245 | 7.5178 | 0 | 54.5256 | 0 | 29.1927 | 0 | 0.077539 | 18.7611 | 0 | 0 | 152.9054 | 0 | 0 | 336.1621 | 1.368% | CZ 1A | 3.9127 | 1.6711 | 3.8072 | 0 | 0 | 15.9759 | 0 | 8.5534 | 0 | 0.022719 | 5.497 | 0 | 0 | 21.0827 | 0 | 0 | 60.5226 | 1.368% | CZ 1A | 0 | 0 | 0.41131 | 0.075178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.296 | 1.368% | CZ 1A | 40.9619 | 17.4947 | 84.813 | 8.2169 | 0 | 167.2513 | 0 | 89.5453 | 0 | 0.23784 | 57.5477 | 0 | 0 | 309.1936 | 0 | 0 | 775.2622 | 1.368%
CZ 1B | 0.40775 | 0.17246 | 0.77723 | 0.10347 | 0 | 1.5971 | 0 | 1.2165 | 0 | 0.0023446 | 0.56198 | 0 | 0 | 2.9771 | 0 | 0 | 7.8159 | 0% | CZ 1B | 13.4849 | 5.7034 | 51.8144 | 10.4515 | 0 | 52.818 | 0 | 40.2308 | 0 | 0.077539 | 18.5854 | 0 | 0 | 152.9054 | 0 | 0 | 346.0714 | 0% | CZ 1B | 3.9511 | 1.6711 | 3.8072 | 0 | 0 | 15.4755 | 0 | 11.7875 | 0 | 0.022719 | 5.4455 | 0 | 0 | 21.0827 | 0 | 0 | 63.2433 | 0% | CZ 1B | 0 | 0 | 0.38821 | 0.10451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.3022 | 0% | CZ 1B | 41.3636 | 17.4947 | 82.2881 | 11.4235 | 0 | 162.0135 | 0 | 123.4036 | 0 | 0.23784 | 57.0086 | 0 | 0 | 309.1936 | 0 | 0 | 804.4269 | 0%
CZ 2A | 0.4078 | 0.17241 | 0.85331 | 0.33863 | 0 | 1.1576 | 0 | 0.82655 | 0 | 0.0023446 | 0.56099 | 0 | 0 | 2.9771 | 0 | 0 | 7.2967 | 16% | CZ 2A | 13.4867 | 5.7017 | 59.4889 | 34.2055 | 0 | 38.282 | 0 | 27.3352 | 0 | 0.077539 | 18.5526 | 0 | 0 | 152.9054 | 0 | 0 | 350.0356 | 16% | CZ 2A | 3.9516 | 1.6706 | 3.8087 | 0 | 0 | 11.2165 | 0 | 8.0091 | 0 | 0.022719 | 5.4359 | 0 | 0 | 21.0827 | 0 | 0 | 55.1978 | 16% | CZ 2A | 0 | 0 | 0.4649 | 0.34205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6165 | 16% | CZ 2A | 41.3689 | 17.4894 | 90.6865 | 37.3866 | 0 | 117.4258 | 0 | 83.8476 | 0 | 0.23784 | 56.9081 | 0 | 0 | 309.1936 | 0 | 0 | 754.5444 | 16%
CZ 2B | 0.40671 | 0.17235 | 0.8223 | 0.18782 | 0 | 1.3508 | 0 | 1.1358 | 0 | 0.0023446 | 0.56062 | 0 | 0 | 2.9771 | 0 | 0 | 7.6159 | 3.722% | CZ 2B | 13.4505 | 5.7 | 56.364 | 18.9718 | 0 | 44.673 | 0 | 37.5635 | 0 | 0.077539 | 18.5406 | 0 | 0 | 152.9054 | 0 | 0 | 348.2463 | 3.722% | CZ 2B | 3.941 | 1.6701 | 3.8077 | 0 | 0 | 13.0891 | 0 | 11.006 | 0 | 0.022719 | 5.4323 | 0 | 0 | 21.0827 | 0 | 0 | 60.0516 | 3.722% | CZ 2B | 0 | 0 | 0.43368 | 0.18972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.4329 | 3.722% | CZ 2B | 41.2579 | 17.4841 | 87.2642 | 20.7362 | 0 | 137.0294 | 0 | 115.2218 | 0 | 0.23784 | 56.8712 | 0 | 0 | 309.1936 | 0 | 0 | 785.2961 | 3.722%
CZ 3A | 0.40009 | 0.17246 | 0.89499 | 0.64084 | 0 | 0.80816 | 0 | 0.77012 | 0 | 0.0023446 | 0.55593 | 0 | 0 | 2.9771 | 0 | 0 | 7.2221 | 16.86% | CZ 3A | 13.2316 | 5.7034 | 63.6923 | 64.7313 | 0 | 26.7269 | 0 | 25.4691 | 0 | 0.077539 | 18.3855 | 0 | 0 | 152.9054 | 0 | 0 | 370.9231 | 16.86% | CZ 3A | 3.8768 | 1.6711 | 3.8097 | 0 | 0 | 7.8309 | 0 | 7.4624 | 0 | 0.022719 | 5.3869 | 0 | 0 | 21.0827 | 0 | 0 | 51.1433 | 16.86% | CZ 3A | 0 | 0 | 0.5069 | 0.64731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9637 | 16.86% | CZ 3A | 40.5866 | 17.4947 | 95.2876 | 70.7513 | 0 | 81.9819 | 0 | 78.1236 | 0 | 0.23784 | 56.3955 | 0 | 0 | 309.1936 | 0 | 0 | 750.0525 | 16.86%
CZ 3B | 0.39863 | 0.17235 | 0.88101 | 0.35318 | 0 | 0.68212 | 0 | 0.99724 | 0 | 0.0023446 | 0.55692 | 0 | 0 | 2.9771 | 0 | 0 | 7.0209 | 7.194% | CZ 3B | 13.1834 | 5.7 | 62.2866 | 35.6749 | 0 | 22.5588 | 0 | 32.98 | 0 | 0.077539 | 18.4182 | 0 | 0 | 152.9054 | 0 | 0 | 343.7849 | 7.194% | CZ 3B | 3.8627 | 1.6701 | 3.8087 | 0 | 0 | 6.6097 | 0 | 9.6631 | 0 | 0.022719 | 5.3965 | 0 | 0 | 21.0827 | 0 | 0 | 52.1161 | 7.194% | CZ 3B | 0 | 0 | 0.49288 | 0.35675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6591 | 7.194% | CZ 3B | 40.4386 | 17.4841 | 93.7443 | 38.9927 | 0 | 69.1965 | 0 | 101.1626 | 0 | 0.23784 | 56.4959 | 0 | 0 | 309.1936 | 0 | 0 | 726.9462 | 7.194%
CZ 3C | 0.39921 | 0.17235 | 0.93978 | 0.61722 | 0 | 0.044235 | 0 | 0.68087 | 0 | 0.0023446 | 0.55406 | 0 | 0 | 2.9771 | 0 | 0 | 6.3872 | 0.8731% | CZ 3C | 13.2024 | 5.7 | 68.216 | 62.3454 | 0 | 1.4629 | 0 | 22.5174 | 0 | 0.077539 | 18.3235 | 0 | 0 | 152.9054 | 0 | 0 | 344.7505 | 0.8731% | CZ 3C | 3.8683 | 1.6701 | 3.8097 | 0 | 0 | 0.42863 | 0 | 6.5975 | 0 | 0.022719 | 5.3687 | 0 | 0 | 21.0827 | 0 | 0 | 42.8484 | 0.8731% | CZ 3C | 0 | 0 | 0.55214 | 0.62345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9851 | 0.8731% | CZ 3C | 40.4968 | 17.4841 | 100.232 | 68.1435 | 0 | 4.4873 | 0 | 69.0697 | 0 | 0.23784 | 56.2052 | 0 | 0 | 309.1936 | 0 | 0 | 665.55 | 0.8731%
CZ 4A | 0.39566 | 0.17241 | 0.946 | 0.95521 | 0 | 0.47028 | 0 | 0.6964 | 0 | 0.0023446 | 0.55155 | 0 | 0 | 2.9771 | 0 | 0 | 7.167 | 19.27% | CZ 4A | 13.0852 | 5.7017 | 68.8379 | 96.4854 | 0 | 15.5527 | 0 | 23.0309 | 0 | 0.077539 | 18.2408 | 0 | 0 | 152.9054 | 0 | 0 | 393.9175 | 19.27% | CZ 4A | 3.8339 | 1.6706 | 3.8107 | 0 | 0 | 4.5569 | 0 | 6.748 | 0 | 0.022719 | 5.3445 | 0 | 0 | 21.0827 | 0 | 0 | 47.07 | 19.27% | CZ 4A | 0 | 0 | 0.55832 | 0.96485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.3327 | 19.27% | CZ 4A | 40.1374 | 17.4894 | 100.9186 | 105.4586 | 0 | 47.7061 | 0 | 70.6447 | 0 | 0.23784 | 55.9515 | 0 | 0 | 309.1936 | 0 | 0 | 747.7376 | 19.27%
CZ 4B | 0.39452 | 0.1723 | 0.938 | 0.62957 | 0 | 0.35904 | 0 | 0.83806 | 0 | 0.0023446 | 0.55234 | 0 | 0 | 2.9771 | 0 | 0 | 6.8633 | 0.8813% | CZ 4B | 13.0473 | 5.6983 | 68.0369 | 63.5926 | 0 | 11.8738 | 0 | 27.716 | 0 | 0.077539 | 18.2666 | 0 | 0 | 152.9054 | 0 | 0 | 361.2144 | 0.8813% | CZ 4B | 3.8228 | 1.6696 | 3.8097 | 0 | 0 | 3.479 | 0 | 8.1207 | 0 | 0.022719 | 5.3521 | 0 | 0 | 21.0827 | 0 | 0 | 47.3593 | 0.8813% | CZ 4B | 0 | 0 | 0.55034 | 0.63593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9958 | 0.8813% | CZ 4B | 40.0211 | 17.4788 | 100.0362 | 69.5068 | 0 | 36.4217 | 0 | 85.0157 | 0 | 0.23784 | 56.0308 | 0 | 0 | 309.1936 | 0 | 0 | 713.9425 | 0.8813%
CZ 4C | 0.39712 | 0.17256 | 0.96737 | 0.97647 | 0 | 0.16944 | 0 | 0.71839 | 0 | 0.0023446 | 0.55103 | 0 | 0 | 2.9771 | 0 | 0 | 6.9319 | 1.548% | CZ 4C | 13.1334 | 5.7069 | 70.9964 | 98.6336 | 0 | 5.6035 | 0 | 23.758 | 0 | 0.077539 | 18.2235 | 0 | 0 | 152.9054 | 0 | 0 | 389.0384 | 1.548% | CZ 4C | 3.8481 | 1.6721 | 3.8107 | 0 | 0 | 1.6418 | 0 | 6.961 | 0 | 0.022719 | 5.3394 | 0 | 0 | 21.0827 | 0 | 0 | 44.3786 | 1.548% | CZ 4C | 0 | 0 | 0.5799 | 0.98634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.3757 | 1.548% | CZ 4C | 40.2853 | 17.5053 | 103.2778 | 107.8065 | 0 | 17.1881 | 0 | 72.8751 | 0 | 0.23784 | 55.8986 | 0 | 0 | 309.1936 | 0 | 0 | 724.2683 | 1.548%
CZ 5A | 0.39681 | 0.17298 | 0.98153 | 1.3727 | 0 | 0.35002 | 0 | 0.67759 | 0 | 0.0023446 | 0.54911 | 0 | 0 | 2.9771 | 0 | 0 | 7.4802 | 21.68% | CZ 5A | 13.1231 | 5.7207 | 72.4228 | 138.6583 | 0 | 11.5758 | 0 | 22.4089 | 0 | 0.077539 | 18.1598 | 0 | 0 | 152.9054 | 0 | 0 | 435.0522 | 21.68% | CZ 5A | 3.845 | 1.6761 | 3.8112 | 0 | 0 | 3.3917 | 0 | 6.5657 | 0 | 0.022719 | 5.3208 | 0 | 0 | 21.0827 | 0 | 0 | 45.716 | 21.68% | CZ 5A | 0 | 0 | 0.59415 | 1.3866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.7902 | 21.68% | CZ 5A | 40.2536 | 17.5475 | 104.8403 | 151.5535 | 0 | 35.5073 | 0 | 68.7367 | 0 | 0.23784 | 55.7031 | 0 | 0 | 309.1936 | 0 | 0 | 783.5735 | 21.68%
CZ 5B | 0.39467 | 0.17199 | 0.9752 | 1.02 | 0 | 0.24879 | 0 | 0.6928 | 0 | 0.0023446 | 0.54812 | 0 | 0 | 2.9771 | 0 | 0 | 7.0311 | 4.706% | CZ 5B | 13.0524 | 5.6879 | 71.7837 | 103.0333 | 0 | 8.2278 | 0 | 22.912 | 0 | 0.077539 | 18.127 | 0 | 0 | 152.9054 | 0 | 0 | 395.8071 | 4.706% | CZ 5B | 3.8243 | 1.6666 | 3.8112 | 0 | 0 | 2.4107 | 0 | 6.7132 | 0 | 0.022719 | 5.3112 | 0 | 0 | 21.0827 | 0 | 0 | 44.8426 | 4.706% | CZ 5B | 0 | 0 | 0.58776 | 1.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4276 | 4.706% | CZ 5B | 40.0369 | 17.4471 | 104.1417 | 112.6154 | 0 | 25.2378 | 0 | 70.28 | 0 | 0.23784 | 55.6027 | 0 | 0 | 309.1936 | 0 | 0 | 734.7931 | 4.706%
CZ 5C | 0.40296 | 0.17277 | 0.98204 | 1.1406 | 0 | 0.035117 | 0 | 0.66576 | 0 | 0.0023446 | 0.54827 | 0 | 0 | 2.9771 | 0 | 0 | 6.927 | 0% | CZ 5C | 13.3264 | 5.7138 | 72.4745 | 115.2109 | 0 | 1.1614 | 0 | 22.0177 | 0 | 0.077539 | 18.1322 | 0 | 0 | 152.9054 | 0 | 0 | 401.0198 | 0% | CZ 5C | 3.9046 | 1.6741 | 3.8112 | 0 | 0 | 0.34028 | 0 | 6.4511 | 0 | 0.022719 | 5.3127 | 0 | 0 | 21.0827 | 0 | 0 | 42.5995 | 0% | CZ 5C | 0 | 0 | 0.59467 | 1.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.5563 | 0% | CZ 5C | 40.8773 | 17.5264 | 104.8968 | 125.9256 | 0 | 3.5624 | 0 | 67.5369 | 0 | 0.23784 | 55.6185 | 0 | 0 | 309.1936 | 0 | 0 | 725.3752 | 0%
CZ 6A | 0.39744 | 0.17308 | 1.0129 | 1.6339 | 0 | 0.18746 | 0 | 0.72198 | 0 | 0.0023446 | 0.54817 | 0 | 0 | 2.9771 | 0 | 0 | 7.6544 | 4.701% | CZ 6A | 13.1438 | 5.7241 | 75.5891 | 165.0446 | 0 | 6.1997 | 0 | 23.8769 | 0 | 0.077539 | 18.1288 | 0 | 0 | 152.9054 | 0 | 0 | 460.6898 | 4.701% | CZ 6A | 3.8511 | 1.6772 | 3.8112 | 0 | 0 | 1.8165 | 0 | 6.9959 | 0 | 0.022719 | 5.3117 | 0 | 0 | 21.0827 | 0 | 0 | 44.569 | 4.701% | CZ 6A | 0 | 0 | 0.62581 | 1.6504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.0858 | 4.701% | CZ 6A | 40.3171 | 17.5581 | 108.301 | 180.3937 | 0 | 19.0169 | 0 | 73.2398 | 0 | 0.23784 | 55.6079 | 0 | 0 | 309.1936 | 0 | 0 | 803.8659 | 4.701%
CZ 6B | 0.39494 | 0.1723 | 1.0174 | 1.395 | 0 | 0.14432 | 0 | 0.76794 | 0 | 0.0023446 | 0.54723 | 0 | 0 | 2.9771 | 0 | 0 | 7.4187 | 0.6064% | CZ 6B | 13.0611 | 5.6983 | 76.049 | 140.9116 | 0 | 4.773 | 0 | 25.3967 | 0 | 0.077539 | 18.0977 | 0 | 0 | 152.9054 | 0 | 0 | 436.9703 | 0.6064% | CZ 6B | 3.8269 | 1.6696 | 3.8112 | 0 | 0 | 1.3985 | 0 | 7.4412 | 0 | 0.022719 | 5.3026 | 0 | 0 | 21.0827 | 0 | 0 | 44.5553 | 0.6064% | CZ 6B | 0 | 0 | 0.63041 | 1.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.849 | 0.6064% | CZ 6B | 40.0634 | 17.4788 | 108.8037 | 154.0163 | 0 | 14.6406 | 0 | 77.9016 | 0 | 0.23784 | 55.5128 | 0 | 0 | 309.1936 | 0 | 0 | 777.8486 | 0.6064%
CZ 7 | 0.3966 | 0.17267 | 1.0627 | 2.1005 | 0 | 0.10551 | 0 | 0.71078 | 0 | 0.0023446 | 0.54624 | 0 | 0 | 2.9771 | 0 | 0 | 8.0744 | 0.5553% | CZ 7 | 13.1162 | 5.7103 | 80.6141 | 212.1701 | 0 | 3.4893 | 0 | 23.5065 | 0 | 0.077539 | 18.065 | 0 | 0 | 152.9054 | 0 | 0 | 509.6545 | 0.5553% | CZ 7 | 3.843 | 1.6731 | 3.8117 | 0 | 0 | 1.0223 | 0 | 6.8873 | 0 | 0.022719 | 5.293 | 0 | 0 | 21.0827 | 0 | 0 | 43.636 | 0.5553% | CZ 7 | 0 | 0 | 0.67605 | 2.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.6072 | 0.5553% | CZ 7 | 40.2325 | 17.5158 | 113.7968 | 231.9019 | 0 | 10.7029 | 0 | 72.1035 | 0 | 0.23784 | 55.4124 | 0 | 0 | 309.1936 | 0 | 0 | 851.0973 | 0.5553%
CZ 8 | 0.40364 | 0.17366 | 1.1239 | 3.1908 | 0 | 0.039598 | 0 | 0.6928 | 0 | 0.0023446 | 0.54416 | 0 | 0 | 2.9771 | 0 | 0 | 9.148 | 0.02085% | CZ 8 | 13.3488 | 5.7431 | 86.7968 | 322.3009 | 0 | 1.3096 | 0 | 22.912 | 0 | 0.077539 | 17.9961 | 0 | 0 | 152.9054 | 0 | 0 | 623.3902 | 0.02085% | CZ 8 | 3.9112 | 1.6827 | 3.8122 | 0 | 0 | 0.3837 | 0 | 6.7132 | 0 | 0.022719 | 5.2728 | 0 | 0 | 21.0827 | 0 | 0 | 42.8812 | 0.02085% | CZ 8 | 0 | 0 | 0.73786 | 3.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 4.7704 | 0.02085% | CZ 8 | 40.946 | 17.6163 | 120.5579 | 352.2749 | 0 | 4.0169 | 0 | 70.28 | 0 | 0.23784 | 55.201 | 0 | 0 | 309.1936 | 0 | 0 | 970.3243 | 0.02085%
Us Weighted | 0.39942 | 0.17255 | 0.92484 | 0.8491 | 0 | 0.63813 | 0 | 0.76913 | 0 | 0.0023446 | 0.55385 | 0 | 0 | 2.9771 | 0 | 0 | 7.2865 | 100% | Us Weighted | 13.2094 | 5.7064 | 66.7044 | 85.768 | 0 | 21.1037 | 0 | 25.4361 | 0 | 0.077539 | 18.3167 | 0 | 0 | 152.9054 | 0 | 0 | 389.2278 | 100% | Us Weighted | 3.8703 | 1.672 | 3.81 | 0 | 0 | 6.1833 | 0 | 7.4527 | 0 | 0.022719 | 5.3668 | 0 | 0 | 21.0827 | 0 | 0 | 49.4606 | 100% | Us Weighted | 0 | 0 | 0.53701 | 0.85768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2042 | 100% | Us Weighted | 40.5184 | 17.5039 | 98.5823 | 93.7444 | 0 | 64.7334 | 0 | 78.0224 | 0 | 0.23784 | 56.1845 | 0 | 0 | 309.1936 | 0 | 0 | 758.7207 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.96728 | 0.30292 | 0.81133 | 0.097569 | 0 | 2.2017 | 0 | 1.1458 | 0 | 0.0023446 | 0.56786 | 0 | 0 | 2.9771 | 0 | 0 | 9.074 | 1.368% | CZ 1A | 31.9893 | 10.0181 | 54.5156 | 9.8554 | 0 | 72.8146 | 0 | 37.8926 | 0 | 0.077539 | 18.7801 | 0 | 0 | 152.9054 | 0 | 0 | 388.8486 | 1.368% | CZ 1A | 9.3728 | 2.9353 | 3.9132 | 0 | 0 | 21.3345 | 0 | 11.1024 | 0 | 0.022719 | 5.5025 | 0 | 0 | 21.0827 | 0 | 0 | 75.2661 | 1.368% | CZ 1A | 0 | 0 | 0.4116 | 0.098554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.3197 | 1.368% | CZ 1A | 98.1235 | 30.7293 | 85.955 | 10.772 | 0 | 223.3506 | 0 | 116.2313 | 0 | 0.23784 | 57.6058 | 0 | 0 | 309.1936 | 0 | 0 | 932.199 | 1.368%
CZ 1B | 0.96728 | 0.30287 | 0.78829 | 0.13609 | 0 | 2.0805 | 0 | 1.6935 | 0 | 0.0023446 | 0.56333 | 0 | 0 | 2.9771 | 0 | 0 | 9.5114 | 0% | CZ 1B | 31.9893 | 10.0164 | 52.1917 | 13.747 | 0 | 68.8066 | 0 | 56.0058 | 0 | 0.077539 | 18.6302 | 0 | 0 | 152.9054 | 0 | 0 | 404.3698 | 0% | CZ 1B | 9.3728 | 2.9348 | 3.9127 | 0 | 0 | 20.1602 | 0 | 16.4095 | 0 | 0.022719 | 5.4586 | 0 | 0 | 21.0827 | 0 | 0 | 79.354 | 0% | CZ 1B | 0 | 0 | 0.38838 | 0.13747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.3353 | 0% | CZ 1B | 98.1235 | 30.7241 | 83.4116 | 15.0254 | 0 | 211.0567 | 0 | 171.7915 | 0 | 0.23784 | 57.146 | 0 | 0 | 309.1936 | 0 | 0 | 976.7102 | 0%
CZ 2A | 0.96728 | 0.30282 | 0.86463 | 0.3622 | 0 | 1.7188 | 0 | 1.5185 | 0 | 0.0023446 | 0.56203 | 0 | 0 | 2.9771 | 0 | 0 | 9.2757 | 16% | CZ 2A | 31.9893 | 10.0146 | 59.8818 | 36.5862 | 0 | 56.8432 | 0 | 50.2179 | 0 | 0.077539 | 18.5871 | 0 | 0 | 152.9054 | 0 | 0 | 417.103 | 16% | CZ 2A | 9.3728 | 2.9343 | 3.9157 | 0 | 0 | 16.6549 | 0 | 14.7137 | 0 | 0.022719 | 5.446 | 0 | 0 | 21.0827 | 0 | 0 | 74.1428 | 16% | CZ 2A | 0 | 0 | 0.46517 | 0.36586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6405 | 16% | CZ 2A | 98.1235 | 30.7188 | 91.8372 | 39.9887 | 0 | 174.3602 | 0 | 154.0378 | 0 | 0.23784 | 57.0139 | 0 | 0 | 309.1936 | 0 | 0 | 955.5115 | 16%
CZ 2B | 0.96728 | 0.30271 | 0.83343 | 0.23269 | 0 | 1.7933 | 0 | 1.6363 | 0 | 0.0023446 | 0.56218 | 0 | 0 | 2.9771 | 0 | 0 | 9.3073 | 3.722% | CZ 2B | 31.9893 | 10.0112 | 56.7448 | 23.5042 | 0 | 59.3055 | 0 | 54.1138 | 0 | 0.077539 | 18.5923 | 0 | 0 | 152.9054 | 0 | 0 | 407.2439 | 3.722% | CZ 2B | 9.3728 | 2.9333 | 3.9137 | 0 | 0 | 17.3764 | 0 | 15.8552 | 0 | 0.022719 | 5.4475 | 0 | 0 | 21.0827 | 0 | 0 | 76.0042 | 3.722% | CZ 2B | 0 | 0 | 0.43387 | 0.23504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.4784 | 3.722% | CZ 2B | 98.1235 | 30.7082 | 88.3948 | 25.6901 | 0 | 181.913 | 0 | 165.9881 | 0 | 0.23784 | 57.0297 | 0 | 0 | 309.1936 | 0 | 0 | 957.2789 | 3.722%
CZ 3A | 0.96728 | 0.30261 | 0.90647 | 0.65955 | 0 | 1.237 | 0 | 1.4751 | 0 | 0.0023446 | 0.55687 | 0 | 0 | 2.9771 | 0 | 0 | 9.0843 | 16.86% | CZ 3A | 31.9893 | 10.0077 | 64.0903 | 66.6211 | 0 | 40.908 | 0 | 48.7825 | 0 | 0.077539 | 18.4165 | 0 | 0 | 152.9054 | 0 | 0 | 433.7984 | 16.86% | CZ 3A | 9.3728 | 2.9322 | 3.9182 | 0 | 0 | 11.9859 | 0 | 14.2932 | 0 | 0.022719 | 5.396 | 0 | 0 | 21.0827 | 0 | 0 | 69.0038 | 16.86% | CZ 3A | 0 | 0 | 0.50717 | 0.66621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.9829 | 16.86% | CZ 3A | 98.1235 | 30.6976 | 96.4541 | 72.8169 | 0 | 125.4808 | 0 | 149.6351 | 0 | 0.23784 | 56.4906 | 0 | 0 | 309.1936 | 0 | 0 | 939.1299 | 16.86%
CZ 3B | 0.96728 | 0.30271 | 0.89227 | 0.39111 | 0 | 0.96994 | 0 | 1.5848 | 0 | 0.0023446 | 0.55848 | 0 | 0 | 2.9771 | 0 | 0 | 8.6461 | 7.194% | CZ 3B | 31.9893 | 10.0112 | 62.6742 | 39.5062 | 0 | 32.0771 | 0 | 52.4114 | 0 | 0.077539 | 18.4699 | 0 | 0 | 152.9054 | 0 | 0 | 400.1222 | 7.194% | CZ 3B | 9.3728 | 2.9333 | 3.9157 | 0 | 0 | 9.3985 | 0 | 15.3564 | 0 | 0.022719 | 5.4116 | 0 | 0 | 21.0827 | 0 | 0 | 67.4937 | 7.194% | CZ 3B | 0 | 0 | 0.4931 | 0.39506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6977 | 7.194% | CZ 3B | 98.1235 | 30.7082 | 94.8893 | 43.1802 | 0 | 98.3931 | 0 | 160.7661 | 0 | 0.23784 | 56.6545 | 0 | 0 | 309.1936 | 0 | 0 | 892.1463 | 7.194%
CZ 3C | 0.96728 | 0.30256 | 0.95166 | 0.64527 | 0 | 0.067004 | 0 | 1.0202 | 0 | 0.0023446 | 0.55353 | 0 | 0 | 2.9771 | 0 | 0 | 7.487 | 0.8731% | CZ 3C | 31.9893 | 10.006 | 68.645 | 65.1792 | 0 | 2.2159 | 0 | 33.7399 | 0 | 0.077539 | 18.3062 | 0 | 0 | 152.9054 | 0 | 0 | 383.0645 | 0.8731% | CZ 3C | 9.3728 | 2.9317 | 3.9198 | 0 | 0 | 0.64925 | 0 | 9.8857 | 0 | 0.022719 | 5.3637 | 0 | 0 | 21.0827 | 0 | 0 | 53.2284 | 0.8731% | CZ 3C | 0 | 0 | 0.55267 | 0.65179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.014 | 0.8731% | CZ 3C | 98.1235 | 30.6923 | 101.4426 | 71.2409 | 0 | 6.797 | 0 | 103.4935 | 0 | 0.23784 | 56.1523 | 0 | 0 | 309.1936 | 0 | 0 | 777.3736 | 0.8731%
CZ 4A | 0.96728 | 0.3024 | 0.95772 | 1.0677 | 0 | 0.7151 | 0 | 1.1069 | 0 | 0.0023446 | 0.55197 | 0 | 0 | 2.9771 | 0 | 0 | 8.6486 | 19.27% | CZ 4A | 31.9893 | 10.0008 | 69.2532 | 107.8517 | 0 | 23.6495 | 0 | 36.6054 | 0 | 0.077539 | 18.2545 | 0 | 0 | 152.9054 | 0 | 0 | 450.5873 | 19.27% | CZ 4A | 9.3728 | 2.9302 | 3.9203 | 0 | 0 | 6.9292 | 0 | 10.7253 | 0 | 0.022719 | 5.3485 | 0 | 0 | 21.0827 | 0 | 0 | 60.3318 | 19.27% | CZ 4A | 0 | 0 | 0.55873 | 1.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4468 | 19.27% | CZ 4A | 98.1235 | 30.6765 | 102.1107 | 117.8819 | 0 | 72.5422 | 0 | 112.2831 | 0 | 0.23784 | 55.9938 | 0 | 0 | 309.1936 | 0 | 0 | 899.043 | 19.27%
CZ 4B | 0.96728 | 0.30251 | 0.9496 | 0.67297 | 0 | 0.55135 | 0 | 1.6109 | 0 | 0.0023446 | 0.55317 | 0 | 0 | 2.9771 | 0 | 0 | 8.5873 | 0.8813% | CZ 4B | 31.9893 | 10.0043 | 68.4435 | 67.9769 | 0 | 18.2338 | 0 | 53.2764 | 0 | 0.077539 | 18.2942 | 0 | 0 | 152.9054 | 0 | 0 | 421.2012 | 0.8813% | CZ 4B | 9.3728 | 2.9312 | 3.9187 | 0 | 0 | 5.3425 | 0 | 15.6098 | 0 | 0.022719 | 5.3601 | 0 | 0 | 21.0827 | 0 | 0 | 63.6406 | 0.8813% | CZ 4B | 0 | 0 | 0.55069 | 0.67977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.04 | 0.8813% | CZ 4B | 98.1235 | 30.6871 | 101.2155 | 74.2987 | 0 | 55.9301 | 0 | 163.4194 | 0 | 0.23784 | 56.1153 | 0 | 0 | 309.1936 | 0 | 0 | 889.2211 | 0.8813%
CZ 4C | 0.96728 | 0.30225 | 0.97947 | 1.0283 | 0 | 0.24566 | 0 | 1.0799 | 0 | 0.0023446 | 0.54968 | 0 | 0 | 2.9771 | 0 | 0 | 8.132 | 1.548% | CZ 4C | 31.9893 | 9.9957 | 71.4392 | 103.8654 | 0 | 8.1244 | 0 | 35.7146 | 0 | 0.077539 | 18.1787 | 0 | 0 | 152.9054 | 0 | 0 | 432.2902 | 1.548% | CZ 4C | 9.3728 | 2.9287 | 3.9218 | 0 | 0 | 2.3804 | 0 | 10.4643 | 0 | 0.022719 | 5.3263 | 0 | 0 | 21.0827 | 0 | 0 | 55.4997 | 1.548% | CZ 4C | 0 | 0 | 0.58054 | 1.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4287 | 1.548% | CZ 4C | 98.1235 | 30.6606 | 104.5103 | 113.5249 | 0 | 24.9207 | 0 | 109.5506 | 0 | 0.23784 | 55.7612 | 0 | 0 | 309.1936 | 0 | 0 | 846.4832 | 1.548%
CZ 5A | 0.96728 | 0.30245 | 0.99338 | 1.4769 | 0 | 0.52321 | 0 | 1.0578 | 0 | 0.0023446 | 0.54937 | 0 | 0 | 2.9771 | 0 | 0 | 8.8499 | 21.68% | CZ 5A | 31.9893 | 10.0026 | 72.8449 | 149.1821 | 0 | 17.3033 | 0 | 34.9823 | 0 | 0.077539 | 18.1684 | 0 | 0 | 152.9054 | 0 | 0 | 487.4558 | 21.68% | CZ 5A | 9.3728 | 2.9307 | 3.9218 | 0 | 0 | 5.0698 | 0 | 10.2497 | 0 | 0.022719 | 5.3233 | 0 | 0 | 21.0827 | 0 | 0 | 57.9736 | 21.68% | CZ 5A | 0 | 0 | 0.5946 | 1.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.8959 | 21.68% | CZ 5A | 98.1235 | 30.6818 | 106.0467 | 163.0561 | 0 | 53.076 | 0 | 107.3043 | 0 | 0.23784 | 55.7295 | 0 | 0 | 309.1936 | 0 | 0 | 923.4493 | 21.68%
CZ 5B | 0.96728 | 0.30219 | 0.98692 | 1.0451 | 0 | 0.4176 | 0 | 1.4459 | 0 | 0.0023446 | 0.54931 | 0 | 0 | 2.9771 | 0 | 0 | 8.6938 | 4.706% | CZ 5B | 31.9893 | 9.994 | 72.1955 | 105.564 | 0 | 13.8106 | 0 | 47.8193 | 0 | 0.077539 | 18.1667 | 0 | 0 | 152.9054 | 0 | 0 | 452.5222 | 4.706% | CZ 5B | 9.3728 | 2.9282 | 3.9213 | 0 | 0 | 4.0465 | 0 | 14.0109 | 0 | 0.022719 | 5.3228 | 0 | 0 | 21.0827 | 0 | 0 | 60.7079 | 4.706% | CZ 5B | 0 | 0 | 0.58812 | 1.0556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4533 | 4.706% | CZ 5B | 98.1235 | 30.6553 | 105.3335 | 115.3814 | 0 | 42.3625 | 0 | 146.6805 | 0 | 0.23784 | 55.7242 | 0 | 0 | 309.1936 | 0 | 0 | 903.6924 | 4.706%
CZ 5C | 0.96728 | 0.30193 | 0.99426 | 1.1664 | 0 | 0.054082 | 0 | 0.97671 | 0 | 0.0023446 | 0.54692 | 0 | 0 | 2.9771 | 0 | 0 | 7.9871 | 0% | CZ 5C | 31.9893 | 9.9853 | 72.9225 | 117.8225 | 0 | 1.7886 | 0 | 32.3011 | 0 | 0.077539 | 18.0874 | 0 | 0 | 152.9054 | 0 | 0 | 437.8796 | 0% | CZ 5C | 9.3728 | 2.9257 | 3.9233 | 0 | 0 | 0.52405 | 0 | 9.4641 | 0 | 0.022719 | 5.2996 | 0 | 0 | 21.0827 | 0 | 0 | 52.6149 | 0% | CZ 5C | 0 | 0 | 0.59532 | 1.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.583 | 0% | CZ 5C | 98.1235 | 30.6289 | 106.1417 | 128.78 | 0 | 5.4862 | 0 | 99.0802 | 0 | 0.23784 | 55.4811 | 0 | 0 | 309.1936 | 0 | 0 | 833.153 | 0%
CZ 6A | 0.96728 | 0.30225 | 1.025 | 1.7322 | 0 | 0.30876 | 0 | 1.0314 | 0 | 0.0023446 | 0.54707 | 0 | 0 | 2.9771 | 0 | 0 | 8.8935 | 4.701% | CZ 6A | 31.9893 | 9.9957 | 76.0336 | 174.9672 | 0 | 10.2111 | 0 | 34.1104 | 0 | 0.077539 | 18.0926 | 0 | 0 | 152.9054 | 0 | 0 | 508.3827 | 4.701% | CZ 6A | 9.3728 | 2.9287 | 3.9228 | 0 | 0 | 2.9918 | 0 | 9.9943 | 0 | 0.022719 | 5.3011 | 0 | 0 | 21.0827 | 0 | 0 | 55.6169 | 4.701% | CZ 6A | 0 | 0 | 0.62645 | 1.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.1856 | 4.701% | CZ 6A | 98.1235 | 30.6606 | 109.5388 | 191.2391 | 0 | 31.3213 | 0 | 104.6299 | 0 | 0.23784 | 55.4969 | 0 | 0 | 309.1936 | 0 | 0 | 930.4415 | 4.701%
CZ 6B | 0.96728 | 0.30219 | 1.0293 | 1.4376 | 0 | 0.25353 | 0 | 1.4325 | 0 | 0.0023446 | 0.54759 | 0 | 0 | 2.9771 | 0 | 0 | 8.9496 | 0.6064% | CZ 6B | 31.9893 | 9.994 | 76.4763 | 145.2165 | 0 | 8.3846 | 0 | 47.3748 | 0 | 0.077539 | 18.1098 | 0 | 0 | 152.9054 | 0 | 0 | 490.5282 | 0.6064% | CZ 6B | 9.3728 | 2.9282 | 3.9218 | 0 | 0 | 2.4567 | 0 | 13.8807 | 0 | 0.022719 | 5.3061 | 0 | 0 | 21.0827 | 0 | 0 | 58.9717 | 0.6064% | CZ 6B | 0 | 0 | 0.63091 | 1.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.8926 | 0.6064% | CZ 6B | 98.1235 | 30.6553 | 110.0158 | 158.7217 | 0 | 25.7188 | 0 | 145.3169 | 0 | 0.23784 | 55.5498 | 0 | 0 | 309.1936 | 0 | 0 | 933.5333 | 0.6064%
CZ 7 | 0.96728 | 0.30204 | 1.075 | 2.2376 | 0 | 0.18627 | 0 | 1.0214 | 0 | 0.0023446 | 0.54483 | 0 | 0 | 2.9771 | 0 | 0 | 9.3139 | 0.5553% | CZ 7 | 31.9893 | 9.9888 | 81.069 | 226.0222 | 0 | 6.1601 | 0 | 33.7778 | 0 | 0.077539 | 18.0185 | 0 | 0 | 152.9054 | 0 | 0 | 560.0085 | 0.5553% | CZ 7 | 9.3728 | 2.9267 | 3.9243 | 0 | 0 | 1.8049 | 0 | 9.8968 | 0 | 0.022719 | 5.2794 | 0 | 0 | 21.0827 | 0 | 0 | 54.3103 | 0.5553% | CZ 7 | 0 | 0 | 0.67675 | 2.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.7465 | 0.5553% | CZ 7 | 98.1235 | 30.6395 | 115.0526 | 247.0422 | 0 | 18.8953 | 0 | 103.6098 | 0 | 0.23784 | 55.2697 | 0 | 0 | 309.1936 | 0 | 0 | 978.064 | 0.5553%
CZ 8 | 0.96728 | 0.30016 | 1.1364 | 3.3808 | 0 | 0.076069 | 0 | 0.99281 | 0 | 0.0023446 | 0.54155 | 0 | 0 | 2.9771 | 0 | 0 | 10.3746 | 0.02085% | CZ 8 | 31.9893 | 9.9268 | 87.2706 | 341.4932 | 0 | 2.5157 | 0 | 32.8336 | 0 | 0.077539 | 17.9099 | 0 | 0 | 152.9054 | 0 | 0 | 676.9221 | 0.02085% | CZ 8 | 9.3728 | 2.9085 | 3.9253 | 0 | 0 | 0.7371 | 0 | 9.6202 | 0 | 0.022719 | 5.2476 | 0 | 0 | 21.0827 | 0 | 0 | 52.9169 | 0.02085% | CZ 8 | 0 | 0 | 0.73874 | 3.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 4.9632 | 0.02085% | CZ 8 | 98.1235 | 30.4492 | 121.8378 | 373.2521 | 0 | 7.7167 | 0 | 100.7134 | 0 | 0.23784 | 54.9367 | 0 | 0 | 309.1936 | 0 | 0 | 1096.4608 | 0.02085%
Us Weighted | 0.96728 | 0.30253 | 0.93645 | 0.91331 | 0 | 0.94757 | 0 | 1.296 | 0 | 0.0023446 | 0.55447 | 0 | 0 | 2.9771 | 0 | 0 | 8.8971 | 100% | Us Weighted | 31.9893 | 10.0053 | 67.1131 | 92.2535 | 0 | 31.3374 | 0 | 42.859 | 0 | 0.077539 | 18.3373 | 0 | 0 | 152.9054 | 0 | 0 | 446.8778 | 100% | Us Weighted | 9.3728 | 2.9315 | 3.9191 | 0 | 0 | 9.1818 | 0 | 12.5576 | 0 | 0.022719 | 5.3728 | 0 | 0 | 21.0827 | 0 | 0 | 64.4409 | 100% | Us Weighted | 0 | 0 | 0.53737 | 0.92254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2694 | 100% | Us Weighted | 98.1235 | 30.69 | 99.7635 | 100.8331 | 0 | 96.1241 | 0 | 131.4653 | 0 | 0.23784 | 56.2475 | 0 | 0 | 309.1936 | 0 | 0 | 922.6784 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.96728 | 0.30292 | 0.81133 | 0.079815 | 0 | 2.1497 | 0 | 1.2016 | 0 | 0.0023446 | 0.56609 | 0 | 0 | 2.9771 | 0 | 0 | 9.0582 | 1.368% | CZ 1A | 31.9893 | 10.0181 | 54.5156 | 8.0621 | 0 | 71.0949 | 0 | 39.738 | 0 | 0.077539 | 18.7215 | 0 | 0 | 152.9054 | 0 | 0 | 387.1225 | 1.368% | CZ 1A | 9.3728 | 2.9353 | 3.9132 | 0 | 0 | 20.8306 | 0 | 11.6431 | 0 | 0.022719 | 5.4853 | 0 | 0 | 21.0827 | 0 | 0 | 75.2858 | 1.368% | CZ 1A | 0 | 0 | 0.4116 | 0.080621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.3017 | 1.368% | CZ 1A | 98.1235 | 30.7293 | 85.955 | 8.8119 | 0 | 218.0758 | 0 | 121.892 | 0 | 0.23784 | 57.4261 | 0 | 0 | 309.1936 | 0 | 0 | 930.445 | 1.368%
CZ 1B | 0.96728 | 0.30287 | 0.7882 | 0.10763 | 0 | 2.1831 | 0 | 1.8624 | 0 | 0.0023446 | 0.56349 | 0 | 0 | 2.9771 | 0 | 0 | 9.7545 | 0% | CZ 1B | 31.9893 | 10.0164 | 52.1866 | 10.8718 | 0 | 72.1994 | 0 | 61.592 | 0 | 0.077539 | 18.6353 | 0 | 0 | 152.9054 | 0 | 0 | 410.4737 | 0% | CZ 1B | 9.3728 | 2.9348 | 3.9122 | 0 | 0 | 21.1542 | 0 | 18.0463 | 0 | 0.022719 | 5.4601 | 0 | 0 | 21.0827 | 0 | 0 | 81.9858 | 0% | CZ 1B | 0 | 0 | 0.38834 | 0.10872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.3066 | 0% | CZ 1B | 98.1235 | 30.7241 | 83.4025 | 11.8829 | 0 | 221.4637 | 0 | 188.9268 | 0 | 0.23784 | 57.1618 | 0 | 0 | 309.1936 | 0 | 0 | 1001.1167 | 0%
CZ 2A | 0.96728 | 0.30282 | 0.86432 | 0.40099 | 0 | 1.6922 | 0 | 1.6629 | 0 | 0.0023446 | 0.56224 | 0 | 0 | 2.9771 | 0 | 0 | 9.4323 | 16% | CZ 2A | 31.9893 | 10.0146 | 59.8577 | 40.5036 | 0 | 55.9627 | 0 | 54.996 | 0 | 0.077539 | 18.594 | 0 | 0 | 152.9054 | 0 | 0 | 424.9008 | 16% | CZ 2A | 9.3728 | 2.9343 | 3.9147 | 0 | 0 | 16.3969 | 0 | 16.1137 | 0 | 0.022719 | 5.448 | 0 | 0 | 21.0827 | 0 | 0 | 75.2858 | 16% | CZ 2A | 0 | 0 | 0.46497 | 0.40504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.6795 | 16% | CZ 2A | 98.1235 | 30.7188 | 91.804 | 44.2704 | 0 | 171.6593 | 0 | 168.6942 | 0 | 0.23784 | 57.035 | 0 | 0 | 309.1936 | 0 | 0 | 971.7367 | 16%
CZ 2B | 0.96728 | 0.30271 | 0.83317 | 0.23593 | 0 | 1.88 | 0 | 1.8104 | 0 | 0.0023446 | 0.56286 | 0 | 0 | 2.9771 | 0 | 0 | 9.5719 | 3.722% | CZ 2B | 31.9893 | 10.0112 | 56.7258 | 23.8315 | 0 | 62.1727 | 0 | 59.8741 | 0 | 0.077539 | 18.6147 | 0 | 0 | 152.9054 | 0 | 0 | 416.2022 | 3.722% | CZ 2B | 9.3728 | 2.9333 | 3.9127 | 0 | 0 | 18.2164 | 0 | 17.543 | 0 | 0.022719 | 5.454 | 0 | 0 | 21.0827 | 0 | 0 | 78.5376 | 3.722% | CZ 2B | 0 | 0 | 0.43372 | 0.23832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.4815 | 3.722% | CZ 2B | 98.1235 | 30.7082 | 88.3673 | 26.0479 | 0 | 190.7079 | 0 | 183.6572 | 0 | 0.23784 | 57.0984 | 0 | 0 | 309.1936 | 0 | 0 | 984.1419 | 3.722%
CZ 3A | 0.96728 | 0.30261 | 0.90583 | 0.77294 | 0 | 1.2144 | 0 | 1.6267 | 0 | 0.0023446 | 0.55911 | 0 | 0 | 2.9771 | 0 | 0 | 9.3283 | 16.86% | CZ 3A | 31.9893 | 10.0077 | 64.0438 | 78.0752 | 0 | 40.1619 | 0 | 53.7968 | 0 | 0.077539 | 18.4906 | 0 | 0 | 152.9054 | 0 | 0 | 449.5482 | 16.86% | CZ 3A | 9.3728 | 2.9322 | 3.9157 | 0 | 0 | 11.7673 | 0 | 15.7623 | 0 | 0.022719 | 5.4177 | 0 | 0 | 21.0827 | 0 | 0 | 70.2735 | 16.86% | CZ 3A | 0 | 0 | 0.50679 | 0.78075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.097 | 16.86% | CZ 3A | 98.1235 | 30.6976 | 96.3862 | 85.3362 | 0 | 123.1922 | 0 | 165.0156 | 0 | 0.23784 | 56.7179 | 0 | 0 | 309.1936 | 0 | 0 | 964.9006 | 16.86%
CZ 3B | 0.96728 | 0.30271 | 0.89171 | 0.46214 | 0 | 0.98729 | 0 | 1.7419 | 0 | 0.0023446 | 0.5613 | 0 | 0 | 2.9771 | 0 | 0 | 8.8938 | 7.194% | CZ 3B | 31.9893 | 10.0112 | 62.6312 | 46.6811 | 0 | 32.6509 | 0 | 57.6082 | 0 | 0.077539 | 18.563 | 0 | 0 | 152.9054 | 0 | 0 | 413.1178 | 7.194% | CZ 3B | 9.3728 | 2.9333 | 3.9137 | 0 | 0 | 9.5666 | 0 | 16.8791 | 0 | 0.022719 | 5.4389 | 0 | 0 | 21.0827 | 0 | 0 | 69.2098 | 7.194% | CZ 3B | 0 | 0 | 0.49274 | 0.46681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 1.769 | 7.194% | CZ 3B | 98.1235 | 30.7082 | 94.8287 | 51.0225 | 0 | 100.1531 | 0 | 176.7069 | 0 | 0.23784 | 56.9399 | 0 | 0 | 309.1936 | 0 | 0 | 917.9141 | 7.194%
CZ 3C | 0.96728 | 0.30256 | 0.95098 | 0.73186 | 0 | 0.064659 | 0 | 1.0425 | 0 | 0.0023446 | 0.55583 | 0 | 0 | 2.9771 | 0 | 0 | 7.5951 | 0.8731% | CZ 3C | 31.9893 | 10.006 | 68.5934 | 73.9253 | 0 | 2.1384 | 0 | 34.4757 | 0 | 0.077539 | 18.382 | 0 | 0 | 152.9054 | 0 | 0 | 392.4929 | 0.8731% | CZ 3C | 9.3728 | 2.9317 | 3.9172 | 0 | 0 | 0.62653 | 0 | 10.1013 | 0 | 0.022719 | 5.3859 | 0 | 0 | 21.0827 | 0 | 0 | 53.4409 | 0.8731% | CZ 3C | 0 | 0 | 0.55224 | 0.73925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.101 | 0.8731% | CZ 3C | 98.1235 | 30.6923 | 101.3691 | 80.8003 | 0 | 6.5592 | 0 | 105.7504 | 0 | 0.23784 | 56.3849 | 0 | 0 | 309.1936 | 0 | 0 | 789.1111 | 0.8731%
CZ 4A | 0.96728 | 0.3024 | 0.95684 | 1.2126 | 0 | 0.75022 | 0 | 1.5665 | 0 | 0.0023446 | 0.55604 | 0 | 0 | 2.9771 | 0 | 0 | 9.2913 | 19.27% | CZ 4A | 31.9893 | 10.0008 | 69.186 | 122.4824 | 0 | 24.8108 | 0 | 51.8049 | 0 | 0.077539 | 18.3889 | 0 | 0 | 152.9054 | 0 | 0 | 481.646 | 19.27% | CZ 4A | 9.3728 | 2.9302 | 3.9172 | 0 | 0 | 7.2695 | 0 | 15.1787 | 0 | 0.022719 | 5.3879 | 0 | 0 | 21.0827 | 0 | 0 | 65.1618 | 19.27% | CZ 4A | 0 | 0 | 0.55816 | 1.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.5925 | 19.27% | CZ 4A | 98.1235 | 30.6765 | 102.0169 | 133.8732 | 0 | 76.1045 | 0 | 158.9057 | 0 | 0.23784 | 56.406 | 0 | 0 | 309.1936 | 0 | 0 | 965.5377 | 19.27%
CZ 4B | 0.96728 | 0.30251 | 0.94871 | 0.83417 | 0 | 0.57724 | 0 | 1.7646 | 0 | 0.0023446 | 0.55822 | 0 | 0 | 2.9771 | 0 | 0 | 8.9322 | 0.8813% | CZ 4B | 31.9893 | 10.0043 | 68.3746 | 84.2596 | 0 | 19.0902 | 0 | 58.3578 | 0 | 0.077539 | 18.4613 | 0 | 0 | 152.9054 | 0 | 0 | 443.5199 | 0.8813% | CZ 4B | 9.3728 | 2.9312 | 3.9157 | 0 | 0 | 5.5934 | 0 | 17.0987 | 0 | 0.022719 | 5.4091 | 0 | 0 | 21.0827 | 0 | 0 | 65.4263 | 0.8813% | CZ 4B | 0 | 0 | 0.5501 | 0.8426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.2022 | 0.8813% | CZ 4B | 98.1235 | 30.6871 | 101.1198 | 92.0957 | 0 | 58.557 | 0 | 179.0061 | 0 | 0.23784 | 56.628 | 0 | 0 | 309.1936 | 0 | 0 | 925.6486 | 0.8813%
CZ 4C | 0.96728 | 0.30225 | 0.97845 | 1.2915 | 0 | 0.24311 | 0 | 1.095 | 0 | 0.0023446 | 0.55426 | 0 | 0 | 2.9771 | 0 | 0 | 8.4114 | 1.548% | CZ 4C | 31.9893 | 9.9957 | 71.3617 | 130.4532 | 0 | 8.04 | 0 | 36.2143 | 0 | 0.077539 | 18.3304 | 0 | 0 | 152.9054 | 0 | 0 | 459.3674 | 1.548% | CZ 4C | 9.3728 | 2.9287 | 3.9182 | 0 | 0 | 2.3557 | 0 | 10.6107 | 0 | 0.022719 | 5.3707 | 0 | 0 | 21.0827 | 0 | 0 | 55.6623 | 1.548% | CZ 4C | 0 | 0 | 0.57989 | 1.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.6939 | 1.548% | CZ 4C | 98.1235 | 30.6606 | 104.4017 | 142.5853 | 0 | 24.6617 | 0 | 111.0833 | 0 | 0.23784 | 56.2263 | 0 | 0 | 309.1936 | 0 | 0 | 877.174 | 1.548%
CZ 5A | 0.96728 | 0.30245 | 0.99237 | 1.8389 | 0 | 0.49633 | 0 | 1.1372 | 0 | 0.0023446 | 0.55458 | 0 | 0 | 2.9771 | 0 | 0 | 9.2687 | 21.68% | CZ 5A | 31.9893 | 10.0026 | 72.7674 | 185.7511 | 0 | 16.4142 | 0 | 37.61 | 0 | 0.077539 | 18.3407 | 0 | 0 | 152.9054 | 0 | 0 | 525.8582 | 21.68% | CZ 5A | 9.3728 | 2.9307 | 3.9182 | 0 | 0 | 4.8093 | 0 | 11.0196 | 0 | 0.022719 | 5.3738 | 0 | 0 | 21.0827 | 0 | 0 | 58.5299 | 21.68% | CZ 5A | 0 | 0 | 0.59394 | 1.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.261 | 21.68% | CZ 5A | 98.1235 | 30.6818 | 105.9382 | 203.026 | 0 | 50.3488 | 0 | 115.3645 | 0 | 0.23784 | 56.258 | 0 | 0 | 309.1936 | 0 | 0 | 969.1722 | 21.68%
CZ 5B | 0.96728 | 0.30219 | 0.98577 | 1.3173 | 0 | 0.4338 | 0 | 1.6613 | 0 | 0.0023446 | 0.55551 | 0 | 0 | 2.9771 | 0 | 0 | 9.2027 | 4.706% | CZ 5B | 31.9893 | 9.994 | 72.1076 | 133.0596 | 0 | 14.3465 | 0 | 54.9426 | 0 | 0.077539 | 18.3717 | 0 | 0 | 152.9054 | 0 | 0 | 487.7942 | 4.706% | CZ 5B | 9.3728 | 2.9282 | 3.9172 | 0 | 0 | 4.2035 | 0 | 16.098 | 0 | 0.022719 | 5.3829 | 0 | 0 | 21.0827 | 0 | 0 | 63.008 | 4.706% | CZ 5B | 0 | 0 | 0.58738 | 1.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.7275 | 4.706% | CZ 5B | 98.1235 | 30.6553 | 105.2102 | 145.4341 | 0 | 44.0063 | 0 | 168.5304 | 0 | 0.23784 | 56.3532 | 0 | 0 | 309.1936 | 0 | 0 | 957.7445 | 4.706%
CZ 5C | 0.96728 | 0.30193 | 0.99295 | 1.5711 | 0 | 0.046579 | 0 | 0.9753 | 0 | 0.0023446 | 0.55307 | 0 | 0 | 2.9771 | 0 | 0 | 8.3877 | 0% | CZ 5C | 31.9893 | 9.9853 | 72.8225 | 158.7017 | 0 | 1.5404 | 0 | 32.2546 | 0 | 0.077539 | 18.2907 | 0 | 0 | 152.9054 | 0 | 0 | 478.5675 | 0% | CZ 5C | 9.3728 | 2.9257 | 3.9187 | 0 | 0 | 0.45135 | 0 | 9.4505 | 0 | 0.022719 | 5.3591 | 0 | 0 | 21.0827 | 0 | 0 | 52.5836 | 0% | CZ 5C | 0 | 0 | 0.59448 | 1.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.991 | 0% | CZ 5C | 98.1235 | 30.6289 | 106.0018 | 173.4609 | 0 | 4.7252 | 0 | 98.9375 | 0 | 0.23784 | 56.1048 | 0 | 0 | 309.1936 | 0 | 0 | 877.414 | 0%
CZ 6A | 0.96728 | 0.30225 | 1.0239 | 2.1475 | 0 | 0.27807 | 0 | 1.0799 | 0 | 0.0023446 | 0.55291 | 0 | 0 | 2.9771 | 0 | 0 | 9.3313 | 4.701% | CZ 6A | 31.9893 | 9.9957 | 75.9458 | 216.9213 | 0 | 9.1962 | 0 | 35.7146 | 0 | 0.077539 | 18.2856 | 0 | 0 | 152.9054 | 0 | 0 | 551.0312 | 4.701% | CZ 6A | 9.3728 | 2.9287 | 3.9187 | 0 | 0 | 2.6945 | 0 | 10.4643 | 0 | 0.022719 | 5.3576 | 0 | 0 | 21.0827 | 0 | 0 | 55.842 | 4.701% | CZ 6A | 0 | 0 | 0.62571 | 2.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.6044 | 4.701% | CZ 6A | 98.1235 | 30.6606 | 109.4155 | 237.0949 | 0 | 28.2082 | 0 | 109.5506 | 0 | 0.23784 | 56.0889 | 0 | 0 | 309.1936 | 0 | 0 | 978.5737 | 4.701%
CZ 6B | 0.96728 | 0.30219 | 1.0282 | 1.7707 | 0 | 0.25989 | 0 | 1.6188 | 0 | 0.0023446 | 0.55426 | 0 | 0 | 2.9771 | 0 | 0 | 9.4807 | 0.6064% | CZ 6B | 31.9893 | 9.994 | 76.385 | 178.8535 | 0 | 8.5948 | 0 | 53.5366 | 0 | 0.077539 | 18.3304 | 0 | 0 | 152.9054 | 0 | 0 | 530.6665 | 0.6064% | CZ 6B | 9.3728 | 2.9282 | 3.9177 | 0 | 0 | 2.5183 | 0 | 15.6861 | 0 | 0.022719 | 5.3707 | 0 | 0 | 21.0827 | 0 | 0 | 60.8992 | 0.6064% | CZ 6B | 0 | 0 | 0.63014 | 1.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 3.2282 | 0.6064% | CZ 6B | 98.1235 | 30.6553 | 109.8888 | 195.4869 | 0 | 26.3636 | 0 | 164.2175 | 0 | 0.23784 | 56.2263 | 0 | 0 | 309.1936 | 0 | 0 | 990.3934 | 0.6064%
CZ 7 | 0.96728 | 0.30204 | 1.0737 | 2.6907 | 0 | 0.18189 | 0 | 1.0651 | 0 | 0.0023446 | 0.55124 | 0 | 0 | 2.9771 | 0 | 0 | 9.8115 | 0.5553% | CZ 7 | 31.9893 | 9.9888 | 80.976 | 271.7903 | 0 | 6.0153 | 0 | 35.2252 | 0 | 0.077539 | 18.2304 | 0 | 0 | 152.9054 | 0 | 0 | 607.1982 | 0.5553% | CZ 7 | 9.3728 | 2.9267 | 3.9198 | 0 | 0 | 1.7625 | 0 | 10.3209 | 0 | 0.022719 | 5.3415 | 0 | 0 | 21.0827 | 0 | 0 | 54.7495 | 0.5553% | CZ 7 | 0 | 0 | 0.67598 | 2.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 4.2034 | 0.5553% | CZ 7 | 98.1235 | 30.6395 | 114.9203 | 297.0668 | 0 | 18.4513 | 0 | 108.0495 | 0 | 0.23784 | 55.9198 | 0 | 0 | 309.1936 | 0 | 0 | 1032.6021 | 0.5553%
CZ 8 | 0.96728 | 0.30016 | 1.1352 | 3.8981 | 0 | 0.07857 | 0 | 1.02 | 0 | 0.0023446 | 0.54827 | 0 | 0 | 2.9771 | 0 | 0 | 10.927 | 0.02085% | CZ 8 | 31.9893 | 9.9268 | 87.1759 | 393.7472 | 0 | 2.5984 | 0 | 33.7313 | 0 | 0.077539 | 18.1322 | 0 | 0 | 152.9054 | 0 | 0 | 730.284 | 0.02085% | CZ 8 | 9.3728 | 2.9085 | 3.9213 | 0 | 0 | 0.76133 | 0 | 9.8832 | 0 | 0.022719 | 5.3127 | 0 | 0 | 21.0827 | 0 | 0 | 53.2652 | 0.02085% | CZ 8 | 0 | 0 | 0.73793 | 3.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 5.4849 | 0.02085% | CZ 8 | 98.1235 | 30.4492 | 121.7071 | 430.3657 | 0 | 7.9704 | 0 | 103.4671 | 0 | 0.23784 | 55.6185 | 0 | 0 | 309.1936 | 0 | 0 | 1157.1328 | 0.02085%
Us Weighted | 0.96728 | 0.30253 | 0.9357 | 1.0933 | 0 | 0.94371 | 0 | 1.4846 | 0 | 0.0023446 | 0.55778 | 0 | 0 | 2.9771 | 0 | 0 | 9.2643 | 100% | Us Weighted | 31.9893 | 10.0053 | 67.0562 | 110.4323 | 0 | 31.2097 | 0 | 49.097 | 0 | 0.077539 | 18.4466 | 0 | 0 | 152.9054 | 0 | 0 | 471.2194 | 100% | Us Weighted | 9.3728 | 2.9315 | 3.9164 | 0 | 0 | 9.1444 | 0 | 14.3853 | 0 | 0.022719 | 5.4048 | 0 | 0 | 21.0827 | 0 | 0 | 66.2606 | 100% | Us Weighted | 0 | 0 | 0.5369 | 1.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8095 | 0 | 0 | 2.4507 | 100% | Us Weighted | 98.1235 | 30.69 | 99.6834 | 120.7025 | 0 | 95.7324 | 0 | 150.5996 | 0 | 0.23784 | 56.5829 | 0 | 0 | 309.1936 | 0 | 0 | 961.5459 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.59662 | 0.13046 | 0.011403 | 0.02814 | 0 | 0.61788 | 0 | 0.55697 | 0 | 0 | 0.11598 | 0 | 0 | 0 | 0 | 0 | 2.0575 | 1.368% | CZ 1A | 19.7312 | 4.3146 | 0.40492 | 2.8424 | 0 | 20.4342 | 0 | 18.4199 | 0 | 0 | 3.8356 | 0 | 0 | 0 | 0 | 0 | 69.9828 | 1.368% | CZ 1A | 5.7812 | 1.2642 | 0.10653 | 0 | 0 | 5.9872 | 0 | 5.397 | 0 | 0 | 1.1238 | 0 | 0 | 0 | 0 | 0 | 19.6598 | 1.368% | CZ 1A | 0 | 0 | 0.00041344 | 0.028424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028838 | 1.368% | CZ 1A | 60.5232 | 13.2347 | 1.1604 | 3.1068 | 0 | 62.6796 | 0 | 56.501 | 0 | 0 | 11.7654 | 0 | 0 | 0 | 0 | 0 | 208.9709 | 1.368%
CZ 1B | 0.59563 | 0.13041 | 0.010888 | 0.0069241 | 0 | 0.65503 | 0 | 0.86344 | 0 | 0 | 0.12109 | 0 | 0 | 0 | 0 | 0 | 2.3834 | 0% | CZ 1B | 19.6984 | 4.3129 | 0.36357 | 0.69941 | 0 | 21.6628 | 0 | 28.5551 | 0 | 0 | 4.0045 | 0 | 0 | 0 | 0 | 0 | 79.2967 | 0% | CZ 1B | 5.7716 | 1.2637 | 0.10501 | 0 | 0 | 6.3471 | 0 | 8.3666 | 0 | 0 | 1.1733 | 0 | 0 | 0 | 0 | 0 | 23.0273 | 0% | CZ 1B | 0 | 0 | 5.168e-05 | 0.0069941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070458 | 0% | CZ 1B | 60.4227 | 13.2294 | 1.105 | 0.76445 | 0 | 66.4481 | 0 | 87.5897 | 0 | 0 | 12.2833 | 0 | 0 | 0 | 0 | 0 | 241.8427 | 0%
CZ 2A | 0.59532 | 0.13041 | 0.01113 | 0.093356 | 0 | 0.61502 | 0 | 1.0625 | 0 | 0 | 0.11931 | 0 | 0 | 0 | 0 | 0 | 2.627 | 16% | CZ 2A | 19.6881 | 4.3129 | 0.37735 | 9.4299 | 0 | 20.3394 | 0 | 35.1374 | 0 | 0 | 3.9459 | 0 | 0 | 0 | 0 | 0 | 93.231 | 16% | CZ 2A | 5.7686 | 1.2637 | 0.10653 | 0 | 0 | 5.9594 | 0 | 10.2952 | 0 | 0 | 1.1561 | 0 | 0 | 0 | 0 | 0 | 24.5494 | 16% | CZ 2A | 0 | 0 | 0.00013781 | 0.094299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094437 | 16% | CZ 2A | 60.391 | 13.2294 | 1.1303 | 10.3069 | 0 | 62.3889 | 0 | 107.78 | 0 | 0 | 12.1036 | 0 | 0 | 0 | 0 | 0 | 267.3301 | 16%
CZ 2B | 0.5997 | 0.13036 | 0.010803 | 0.050771 | 0 | 0.596 | 0 | 0.89314 | 0 | 0 | 0.12182 | 0 | 0 | 0 | 0 | 0 | 2.4026 | 3.722% | CZ 2B | 19.8328 | 4.3112 | 0.35496 | 5.1284 | 0 | 19.7105 | 0 | 29.5373 | 0 | 0 | 4.0286 | 0 | 0 | 0 | 0 | 0 | 82.9038 | 3.722% | CZ 2B | 5.811 | 1.2632 | 0.10501 | 0 | 0 | 5.7751 | 0 | 8.6544 | 0 | 0 | 1.1804 | 0 | 0 | 0 | 0 | 0 | 22.789 | 3.722% | CZ 2B | 0 | 0 | -3.4454e-05 | 0.051284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05125 | 3.722% | CZ 2B | 60.835 | 13.2241 | 1.0956 | 5.6054 | 0 | 60.4597 | 0 | 90.6024 | 0 | 0 | 12.3573 | 0 | 0 | 0 | 0 | 0 | 244.1795 | 3.722%
CZ 3A | 0.59245 | 0.13015 | 0.010942 | 0.15716 | 0 | 0.44818 | 0 | 1.0618 | 0 | 0 | 0.12197 | 0 | 0 | 0 | 0 | 0 | 2.5227 | 16.86% | CZ 3A | 19.5933 | 4.3043 | 0.35841 | 15.8745 | 0 | 14.8221 | 0 | 35.1167 | 0 | 0 | 4.0338 | 0 | 0 | 0 | 0 | 0 | 94.103 | 16.86% | CZ 3A | 5.7408 | 1.2611 | 0.10653 | 0 | 0 | 4.3428 | 0 | 10.2891 | 0 | 0 | 1.1819 | 0 | 0 | 0 | 0 | 0 | 22.9223 | 16.86% | CZ 3A | 0 | 0 | -5.168e-05 | 0.15874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15869 | 16.86% | CZ 3A | 60.1003 | 13.2029 | 1.1096 | 17.3508 | 0 | 45.465 | 0 | 107.7165 | 0 | 0 | 12.3732 | 0 | 0 | 0 | 0 | 0 | 257.3184 | 16.86%
CZ 3B | 0.59735 | 0.13036 | 0.010546 | 0.1135 | 0 | 0.32798 | 0 | 0.92945 | 0 | 0 | 0.12437 | 0 | 0 | 0 | 0 | 0 | 2.2336 | 7.194% | CZ 3B | 19.7553 | 4.3112 | 0.33256 | 11.4644 | 0 | 10.8469 | 0 | 30.7383 | 0 | 0 | 4.113 | 0 | 0 | 0 | 0 | 0 | 81.5617 | 7.194% | CZ 3B | 5.7882 | 1.2632 | 0.10451 | 0 | 0 | 3.1781 | 0 | 9.0062 | 0 | 0 | 1.2051 | 0 | 0 | 0 | 0 | 0 | 20.5454 | 7.194% | CZ 3B | 0 | 0 | -0.00024117 | 0.11464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1144 | 7.194% | CZ 3B | 60.5972 | 13.2241 | 1.0677 | 12.5306 | 0 | 33.2716 | 0 | 94.2863 | 0 | 0 | 12.6163 | 0 | 0 | 0 | 0 | 0 | 227.5938 | 7.194%
CZ 3C | 0.59459 | 0.1302 | 0.010995 | 0.16592 | 0 | 0.027458 | 0 | 0.66222 | 0 | 0 | 0.12244 | 0 | 0 | 0 | 0 | 0 | 1.7138 | 0.8731% | CZ 3C | 19.664 | 4.306 | 0.36013 | 16.7599 | 0 | 0.90807 | 0 | 21.9005 | 0 | 0 | 4.0493 | 0 | 0 | 0 | 0 | 0 | 67.9479 | 0.8731% | CZ 3C | 5.7615 | 1.2617 | 0.10703 | 0 | 0 | 0.26606 | 0 | 6.4168 | 0 | 0 | 1.1864 | 0 | 0 | 0 | 0 | 0 | 14.9995 | 0.8731% | CZ 3C | 0 | 0 | -5.168e-05 | 0.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16755 | 0.8731% | CZ 3C | 60.317 | 13.2082 | 1.1149 | 18.3186 | 0 | 2.7854 | 0 | 67.1775 | 0 | 0 | 12.4208 | 0 | 0 | 0 | 0 | 0 | 175.3424 | 0.8731%
CZ 4A | 0.59683 | 0.13 | 0.010943 | 0.29615 | 0 | 0.32793 | 0 | 1.0663 | 0 | 0 | 0.12338 | 0 | 0 | 0 | 0 | 0 | 2.5516 | 19.27% | CZ 4A | 19.7381 | 4.2991 | 0.35496 | 29.9143 | 0 | 10.8452 | 0 | 35.2649 | 0 | 0 | 4.0803 | 0 | 0 | 0 | 0 | 0 | 104.4968 | 19.27% | CZ 4A | 5.7832 | 1.2596 | 0.10703 | 0 | 0 | 3.1776 | 0 | 10.3325 | 0 | 0 | 1.1955 | 0 | 0 | 0 | 0 | 0 | 21.8555 | 19.27% | CZ 4A | 0 | 0 | -0.00010336 | 0.29914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29904 | 19.27% | CZ 4A | 60.5443 | 13.1871 | 1.1092 | 32.6963 | 0 | 33.2663 | 0 | 108.1711 | 0 | 0 | 12.5159 | 0 | 0 | 0 | 0 | 0 | 261.4902 | 19.27%
CZ 4B | 0.59938 | 0.1302 | 0.010652 | 0.24773 | 0 | 0.24478 | 0 | 1.2108 | 0 | 0 | 0.12551 | 0 | 0 | 0 | 0 | 0 | 2.5691 | 0.8813% | CZ 4B | 19.8225 | 4.306 | 0.33256 | 25.0236 | 0 | 8.0951 | 0 | 40.043 | 0 | 0 | 4.151 | 0 | 0 | 0 | 0 | 0 | 101.7737 | 0.8813% | CZ 4B | 5.8079 | 1.2617 | 0.10602 | 0 | 0 | 2.3718 | 0 | 11.7325 | 0 | 0 | 1.2162 | 0 | 0 | 0 | 0 | 0 | 22.4962 | 0.8813% | CZ 4B | 0 | 0 | -0.00029286 | 0.25024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24994 | 0.8813% | CZ 4B | 60.8033 | 13.2082 | 1.0779 | 27.3508 | 0 | 24.8308 | 0 | 122.8275 | 0 | 0 | 12.7326 | 0 | 0 | 0 | 0 | 0 | 262.8312 | 0.8813%
CZ 4C | 0.59615 | 0.12968 | 0.01103 | 0.38026 | 0 | 0.081957 | 0 | 0.63789 | 0 | 0 | 0.12296 | 0 | 0 | 0 | 0 | 0 | 1.9599 | 1.548% | CZ 4C | 19.7157 | 4.2888 | 0.36013 | 38.4105 | 0 | 2.7104 | 0 | 21.0959 | 0 | 0 | 4.0665 | 0 | 0 | 0 | 0 | 0 | 90.6479 | 1.548% | CZ 4C | 5.7766 | 1.2566 | 0.10754 | 0 | 0 | 0.79415 | 0 | 6.181 | 0 | 0 | 1.1915 | 0 | 0 | 0 | 0 | 0 | 15.3074 | 1.548% | CZ 4C | 0 | 0 | -6.8907e-05 | 0.38411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38404 | 1.548% | CZ 4C | 60.4756 | 13.1554 | 1.1183 | 41.9827 | 0 | 8.3139 | 0 | 64.7092 | 0 | 0 | 12.4736 | 0 | 0 | 0 | 0 | 0 | 202.2287 | 1.548%
CZ 5A | 0.5947 | 0.12947 | 0.010875 | 0.50585 | 0 | 0.18199 | 0 | 0.65081 | 0 | 0 | 0.12447 | 0 | 0 | 0 | 0 | 0 | 2.1982 | 21.68% | CZ 5A | 19.6674 | 4.2819 | 0.34807 | 51.0963 | 0 | 6.0188 | 0 | 21.5232 | 0 | 0 | 4.1165 | 0 | 0 | 0 | 0 | 0 | 107.0521 | 21.68% | CZ 5A | 5.7625 | 1.2546 | 0.10703 | 0 | 0 | 1.7635 | 0 | 6.3062 | 0 | 0 | 1.2061 | 0 | 0 | 0 | 0 | 0 | 16.4 | 21.68% | CZ 5A | 0 | 0 | -0.00017227 | 0.51096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51079 | 21.68% | CZ 5A | 60.3276 | 13.1342 | 1.1017 | 55.8483 | 0 | 18.4619 | 0 | 66.02 | 0 | 0 | 12.6269 | 0 | 0 | 0 | 0 | 0 | 227.5206 | 21.68%
CZ 5B | 0.59881 | 0.1302 | 0.010652 | 0.34667 | 0 | 0.19439 | 0 | 1.1631 | 0 | 0 | 0.1265 | 0 | 0 | 0 | 0 | 0 | 2.5704 | 4.706% | CZ 5B | 19.8035 | 4.306 | 0.32912 | 35.0169 | 0 | 6.4289 | 0 | 38.4664 | 0 | 0 | 4.1837 | 0 | 0 | 0 | 0 | 0 | 108.5345 | 4.706% | CZ 5B | 5.8024 | 1.2617 | 0.10653 | 0 | 0 | 1.8836 | 0 | 11.2705 | 0 | 0 | 1.2258 | 0 | 0 | 0 | 0 | 0 | 21.5506 | 4.706% | CZ 5B | 0 | 0 | -0.00034454 | 0.35017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34982 | 4.706% | CZ 5B | 60.7451 | 13.2082 | 1.0776 | 38.2734 | 0 | 19.7198 | 0 | 117.9914 | 0 | 0 | 12.833 | 0 | 0 | 0 | 0 | 0 | 263.8486 | 4.706%
CZ 5C | 0.58391 | 0.12916 | 0.01079 | 0.47788 | 0 | 0.017142 | 0 | 0.59558 | 0 | 0 | 0.12499 | 0 | 0 | 0 | 0 | 0 | 1.9395 | 0% | CZ 5C | 19.3107 | 4.2716 | 0.33946 | 48.2711 | 0 | 0.5669 | 0 | 19.6967 | 0 | 0 | 4.1337 | 0 | 0 | 0 | 0 | 0 | 96.5902 | 0% | CZ 5C | 5.658 | 1.2516 | 0.10703 | 0 | 0 | 0.1661 | 0 | 5.7711 | 0 | 0 | 1.2112 | 0 | 0 | 0 | 0 | 0 | 14.1649 | 0% | CZ 5C | 0 | 0 | -0.0002584 | 0.48271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48245 | 0% | CZ 5C | 59.2335 | 13.1025 | 1.0923 | 52.7604 | 0 | 1.7389 | 0 | 60.4175 | 0 | 0 | 12.6797 | 0 | 0 | 0 | 0 | 0 | 201.0247 | 0%
CZ 6A | 0.59371 | 0.12916 | 0.01091 | 0.56338 | 0 | 0.10467 | 0 | 0.62408 | 0 | 0 | 0.12494 | 0 | 0 | 0 | 0 | 0 | 2.1509 | 4.701% | CZ 6A | 19.6347 | 4.2716 | 0.34807 | 56.9069 | 0 | 3.4617 | 0 | 20.6392 | 0 | 0 | 4.132 | 0 | 0 | 0 | 0 | 0 | 109.3941 | 4.701% | CZ 6A | 5.7529 | 1.2516 | 0.10754 | 0 | 0 | 1.0143 | 0 | 6.0472 | 0 | 0 | 1.2107 | 0 | 0 | 0 | 0 | 0 | 15.3842 | 4.701% | CZ 6A | 0 | 0 | -0.00018949 | 0.56907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56888 | 4.701% | CZ 6A | 60.2272 | 13.1025 | 1.1051 | 62.1993 | 0 | 10.6184 | 0 | 63.3086 | 0 | 0 | 12.6744 | 0 | 0 | 0 | 0 | 0 | 223.2354 | 4.701%
CZ 6B | 0.5986 | 0.12989 | 0.010635 | 0.41753 | 0 | 0.1276 | 0 | 1.1298 | 0 | 0 | 0.12729 | 0 | 0 | 0 | 0 | 0 | 2.5414 | 0.6064% | CZ 6B | 19.7966 | 4.2957 | 0.3274 | 42.1746 | 0 | 4.2199 | 0 | 37.3653 | 0 | 0 | 4.2095 | 0 | 0 | 0 | 0 | 0 | 112.389 | 0.6064% | CZ 6B | 5.8004 | 1.2586 | 0.10653 | 0 | 0 | 1.2364 | 0 | 10.9479 | 0 | 0 | 1.2334 | 0 | 0 | 0 | 0 | 0 | 20.5832 | 0.6064% | CZ 6B | 0 | 0 | -0.00036176 | 0.42175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42138 | 0.6064% | CZ 6B | 60.724 | 13.1765 | 1.0757 | 46.0968 | 0 | 12.944 | 0 | 114.614 | 0 | 0 | 12.9123 | 0 | 0 | 0 | 0 | 0 | 261.5432 | 0.6064%
CZ 7 | 0.60027 | 0.12937 | 0.010996 | 0.64406 | 0 | 0.085552 | 0 | 0.6171 | 0 | 0 | 0.12536 | 0 | 0 | 0 | 0 | 0 | 2.2127 | 0.5553% | CZ 7 | 19.8518 | 4.2784 | 0.35324 | 65.0569 | 0 | 2.8293 | 0 | 20.4083 | 0 | 0 | 4.1458 | 0 | 0 | 0 | 0 | 0 | 116.9238 | 0.5553% | CZ 7 | 5.8165 | 1.2536 | 0.10804 | 0 | 0 | 0.82898 | 0 | 5.9796 | 0 | 0 | 1.2147 | 0 | 0 | 0 | 0 | 0 | 15.2014 | 0.5553% | CZ 7 | 0 | 0 | -0.00015504 | 0.65057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65041 | 0.5553% | CZ 7 | 60.8931 | 13.1237 | 1.1141 | 71.1072 | 0 | 8.6786 | 0 | 62.6003 | 0 | 0 | 12.7167 | 0 | 0 | 0 | 0 | 0 | 230.2338 | 0.5553%
CZ 8 | 0.59105 | 0.1265 | 0.011203 | 0.77941 | 0 | 0.043297 | 0 | 0.60272 | 0 | 0 | 0.12494 | 0 | 0 | 0 | 0 | 0 | 2.2791 | 0.02085% | CZ 8 | 19.5468 | 4.1837 | 0.36702 | 78.7281 | 0 | 1.4319 | 0 | 19.9328 | 0 | 0 | 4.132 | 0 | 0 | 0 | 0 | 0 | 128.3222 | 0.02085% | CZ 8 | 5.7272 | 1.2258 | 0.10905 | 0 | 0 | 0.41954 | 0 | 5.8402 | 0 | 0 | 1.2107 | 0 | 0 | 0 | 0 | 0 | 14.5325 | 0.02085% | CZ 8 | 0 | 0 | -5.168e-05 | 0.78728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78723 | 0.02085% | CZ 8 | 59.9576 | 12.833 | 1.136 | 86.0498 | 0 | 4.3922 | 0 | 61.1416 | 0 | 0 | 12.6744 | 0 | 0 | 0 | 0 | 0 | 238.1845 | 0.02085%
Us Weighted | 0.5955 | 0.12999 | 0.010913 | 0.27724 | 0 | 0.34989 | 0 | 0.92426 | 0 | 0 | 0.1229 | 0 | 0 | 0 | 0 | 0 | 2.4107 | 100% | Us Weighted | 19.6939 | 4.2988 | 0.35492 | 28.0042 | 0 | 11.5712 | 0 | 30.5665 | 0 | 0 | 4.0645 | 0 | 0 | 0 | 0 | 0 | 98.554 | 100% | Us Weighted | 5.7703 | 1.2595 | 0.1066 | 0 | 0 | 3.3903 | 0 | 8.9559 | 0 | 0 | 1.1909 | 0 | 0 | 0 | 0 | 0 | 20.6735 | 100% | Us Weighted | 0 | 0 | -8.9202e-05 | 0.28004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27995 | 100% | Us Weighted | 60.4089 | 13.1862 | 1.1063 | 30.6085 | 0 | 35.4935 | 0 | 93.7594 | 0 | 0 | 12.4673 | 0 | 0 | 0 | 0 | 0 | 247.0301 | 100%
Building Type: | Full-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 61.68% | 43.07% | 1.405% | 35.26% | 0% | 28.74% | 0% | 46.35% | 0% | 0% | 20.49% | 0% | 0% | 0% | 0% | 0% | 22.71% | 1.368% | CZ 1A | 61.68% | 43.07% | 0.7428% | 35.26% | 0% | 28.74% | 0% | 46.35% | 0% | 0% | 20.49% | 0% | 0% | 0% | 0% | 0% | 18.08% | 1.368% | CZ 1A | 61.68% | 43.07% | 2.722% | 0% | 0% | 28.74% | 0% | 46.35% | 0% | 0% | 20.49% | 0% | 0% | 0% | 0% | 0% | 26.11% | 1.368% | CZ 1A | 0% | 0% | 0.1004% | 35.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.215% | 1.368% | CZ 1A | 61.68% | 43.07% | 1.35% | 35.26% | 0% | 28.74% | 0% | 46.35% | 0% | 0% | 20.49% | 0% | 0% | 0% | 0% | 0% | 22.46% | 1.368%
CZ 1B | 61.58% | 43.06% | 1.381% | 6.433% | 0% | 30% | 0% | 46.36% | 0% | 0% | 21.49% | 0% | 0% | 0% | 0% | 0% | 24.43% | 0% | CZ 1B | 61.58% | 43.06% | 0.6967% | 6.433% | 0% | 30% | 0% | 46.36% | 0% | 0% | 21.49% | 0% | 0% | 0% | 0% | 0% | 19.32% | 0% | CZ 1B | 61.58% | 43.06% | 2.684% | 0% | 0% | 30% | 0% | 46.36% | 0% | 0% | 21.49% | 0% | 0% | 0% | 0% | 0% | 28.09% | 0% | CZ 1B | 0% | 0% | 0.01331% | 6.433% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.5393% | 0% | CZ 1B | 61.58% | 43.06% | 1.325% | 6.433% | 0% | 30% | 0% | 46.36% | 0% | 0% | 21.49% | 0% | 0% | 0% | 0% | 0% | 24.16% | 0%
CZ 2A | 61.55% | 43.07% | 1.288% | 23.28% | 0% | 36.34% | 0% | 63.89% | 0% | 0% | 21.22% | 0% | 0% | 0% | 0% | 0% | 27.85% | 16% | CZ 2A | 61.55% | 43.07% | 0.6304% | 23.28% | 0% | 36.34% | 0% | 63.89% | 0% | 0% | 21.22% | 0% | 0% | 0% | 0% | 0% | 21.94% | 16% | CZ 2A | 61.55% | 43.07% | 2.721% | 0% | 0% | 36.34% | 0% | 63.89% | 0% | 0% | 21.22% | 0% | 0% | 0% | 0% | 0% | 32.61% | 16% | CZ 2A | 0% | 0% | 0.02964% | 23.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.623% | 16% | CZ 2A | 61.55% | 43.07% | 1.231% | 23.28% | 0% | 36.34% | 0% | 63.89% | 0% | 0% | 21.22% | 0% | 0% | 0% | 0% | 0% | 27.51% | 16%
CZ 2B | 62% | 43.06% | 1.297% | 21.52% | 0% | 31.7% | 0% | 49.33% | 0% | 0% | 21.64% | 0% | 0% | 0% | 0% | 0% | 25.1% | 3.722% | CZ 2B | 62% | 43.06% | 0.6257% | 21.52% | 0% | 31.7% | 0% | 49.33% | 0% | 0% | 21.64% | 0% | 0% | 0% | 0% | 0% | 19.92% | 3.722% | CZ 2B | 62% | 43.06% | 2.684% | 0% | 0% | 31.7% | 0% | 49.33% | 0% | 0% | 21.64% | 0% | 0% | 0% | 0% | 0% | 29.02% | 3.722% | CZ 2B | 0% | 0% | -0.007944% | 21.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.459% | 3.722% | CZ 2B | 62% | 43.06% | 1.24% | 21.52% | 0% | 31.7% | 0% | 49.33% | 0% | 0% | 21.64% | 0% | 0% | 0% | 0% | 0% | 24.81% | 3.722%
CZ 3A | 61.25% | 43.01% | 1.208% | 20.33% | 0% | 36.91% | 0% | 65.28% | 0% | 0% | 21.82% | 0% | 0% | 0% | 0% | 0% | 27.04% | 16.86% | CZ 3A | 61.25% | 43.01% | 0.5596% | 20.33% | 0% | 36.91% | 0% | 65.28% | 0% | 0% | 21.82% | 0% | 0% | 0% | 0% | 0% | 20.93% | 16.86% | CZ 3A | 61.25% | 43.01% | 2.72% | 0% | 0% | 36.91% | 0% | 65.28% | 0% | 0% | 21.82% | 0% | 0% | 0% | 0% | 0% | 32.62% | 16.86% | CZ 3A | 0% | 0% | -0.0102% | 20.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.567% | 16.86% | CZ 3A | 61.25% | 43.01% | 1.151% | 20.33% | 0% | 36.91% | 0% | 65.28% | 0% | 0% | 21.82% | 0% | 0% | 0% | 0% | 0% | 26.67% | 16.86%
CZ 3B | 61.76% | 43.06% | 1.183% | 24.56% | 0% | 33.22% | 0% | 53.36% | 0% | 0% | 22.16% | 0% | 0% | 0% | 0% | 0% | 25.11% | 7.194% | CZ 3B | 61.76% | 43.06% | 0.531% | 24.56% | 0% | 33.22% | 0% | 53.36% | 0% | 0% | 22.16% | 0% | 0% | 0% | 0% | 0% | 19.74% | 7.194% | CZ 3B | 61.76% | 43.06% | 2.67% | 0% | 0% | 33.22% | 0% | 53.36% | 0% | 0% | 22.16% | 0% | 0% | 0% | 0% | 0% | 29.69% | 7.194% | CZ 3B | 0% | 0% | -0.04895% | 24.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.467% | 7.194% | CZ 3B | 61.76% | 43.06% | 1.126% | 24.56% | 0% | 33.22% | 0% | 53.36% | 0% | 0% | 22.16% | 0% | 0% | 0% | 0% | 0% | 24.79% | 7.194%
CZ 3C | 61.47% | 43.03% | 1.156% | 22.67% | 0% | 42.47% | 0% | 63.52% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 22.56% | 0.8731% | CZ 3C | 61.47% | 43.03% | 0.525% | 22.67% | 0% | 42.47% | 0% | 63.52% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 17.31% | 0.8731% | CZ 3C | 61.47% | 43.03% | 2.732% | 0% | 0% | 42.47% | 0% | 63.52% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 28.07% | 0.8731% | CZ 3C | 0% | 0% | -0.009358% | 22.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.975% | 0.8731% | CZ 3C | 61.47% | 43.03% | 1.1% | 22.67% | 0% | 42.47% | 0% | 63.52% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 22.22% | 0.8731%
CZ 4A | 61.7% | 42.99% | 1.144% | 24.42% | 0% | 43.71% | 0% | 68.07% | 0% | 0% | 22.19% | 0% | 0% | 0% | 0% | 0% | 27.46% | 19.27% | CZ 4A | 61.7% | 42.99% | 0.5131% | 24.42% | 0% | 43.71% | 0% | 68.07% | 0% | 0% | 22.19% | 0% | 0% | 0% | 0% | 0% | 21.7% | 19.27% | CZ 4A | 61.7% | 42.99% | 2.732% | 0% | 0% | 43.71% | 0% | 68.07% | 0% | 0% | 22.19% | 0% | 0% | 0% | 0% | 0% | 33.54% | 19.27% | CZ 4A | 0% | 0% | -0.01852% | 24.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.53% | 19.27% | CZ 4A | 61.7% | 42.99% | 1.087% | 24.42% | 0% | 43.71% | 0% | 68.07% | 0% | 0% | 22.19% | 0% | 0% | 0% | 0% | 0% | 27.08% | 19.27%
CZ 4B | 61.97% | 43.04% | 1.123% | 29.7% | 0% | 42.4% | 0% | 68.62% | 0% | 0% | 22.48% | 0% | 0% | 0% | 0% | 0% | 28.76% | 0.8813% | CZ 4B | 61.97% | 43.04% | 0.4864% | 29.7% | 0% | 42.4% | 0% | 68.62% | 0% | 0% | 22.48% | 0% | 0% | 0% | 0% | 0% | 22.95% | 0.8813% | CZ 4B | 61.97% | 43.04% | 2.708% | 0% | 0% | 42.4% | 0% | 68.62% | 0% | 0% | 22.48% | 0% | 0% | 0% | 0% | 0% | 34.38% | 0.8813% | CZ 4B | 0% | 0% | -0.05324% | 29.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.35% | 0.8813% | CZ 4B | 61.97% | 43.04% | 1.066% | 29.7% | 0% | 42.4% | 0% | 68.62% | 0% | 0% | 22.48% | 0% | 0% | 0% | 0% | 0% | 28.39% | 0.8813%
CZ 4C | 61.63% | 42.91% | 1.127% | 29.44% | 0% | 33.71% | 0% | 58.25% | 0% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 23.3% | 1.548% | CZ 4C | 61.63% | 42.91% | 0.5047% | 29.44% | 0% | 33.71% | 0% | 58.25% | 0% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 19.73% | 1.548% | CZ 4C | 61.63% | 42.91% | 2.744% | 0% | 0% | 33.71% | 0% | 58.25% | 0% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 27.5% | 1.548% | CZ 4C | 0% | 0% | -0.01188% | 29.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.26% | 1.548% | CZ 4C | 61.63% | 42.91% | 1.071% | 29.44% | 0% | 33.71% | 0% | 58.25% | 0% | 0% | 22.18% | 0% | 0% | 0% | 0% | 0% | 23.05% | 1.548%
CZ 5A | 61.48% | 42.81% | 1.096% | 27.51% | 0% | 36.67% | 0% | 57.23% | 0% | 0% | 22.44% | 0% | 0% | 0% | 0% | 0% | 23.72% | 21.68% | CZ 5A | 61.48% | 42.81% | 0.4783% | 27.51% | 0% | 36.67% | 0% | 57.23% | 0% | 0% | 22.44% | 0% | 0% | 0% | 0% | 0% | 20.36% | 21.68% | CZ 5A | 61.48% | 42.81% | 2.732% | 0% | 0% | 36.67% | 0% | 57.23% | 0% | 0% | 22.44% | 0% | 0% | 0% | 0% | 0% | 28.02% | 21.68% | CZ 5A | 0% | 0% | -0.029% | 27.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.66% | 21.68% | CZ 5A | 61.48% | 42.81% | 1.04% | 27.51% | 0% | 36.67% | 0% | 57.23% | 0% | 0% | 22.44% | 0% | 0% | 0% | 0% | 0% | 23.48% | 21.68%
CZ 5B | 61.91% | 43.09% | 1.081% | 26.32% | 0% | 44.81% | 0% | 70.01% | 0% | 0% | 22.77% | 0% | 0% | 0% | 0% | 0% | 27.93% | 4.706% | CZ 5B | 61.91% | 43.09% | 0.4564% | 26.32% | 0% | 44.81% | 0% | 70.01% | 0% | 0% | 22.77% | 0% | 0% | 0% | 0% | 0% | 22.25% | 4.706% | CZ 5B | 61.91% | 43.09% | 2.719% | 0% | 0% | 44.81% | 0% | 70.01% | 0% | 0% | 22.77% | 0% | 0% | 0% | 0% | 0% | 34.2% | 4.706% | CZ 5B | 0% | 0% | -0.05866% | 26.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.83% | 4.706% | CZ 5B | 61.91% | 43.09% | 1.024% | 26.32% | 0% | 44.81% | 0% | 70.01% | 0% | 0% | 22.77% | 0% | 0% | 0% | 0% | 0% | 27.55% | 4.706%
CZ 5C | 60.37% | 42.78% | 1.087% | 30.42% | 0% | 36.8% | 0% | 61.07% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 23.12% | 0% | CZ 5C | 60.37% | 42.78% | 0.4661% | 30.42% | 0% | 36.8% | 0% | 61.07% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 20.18% | 0% | CZ 5C | 60.37% | 42.78% | 2.731% | 0% | 0% | 36.8% | 0% | 61.07% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 26.94% | 0% | CZ 5C | 0% | 0% | -0.04347% | 30.42% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 16.13% | 0% | CZ 5C | 60.37% | 42.78% | 1.03% | 30.42% | 0% | 36.8% | 0% | 61.07% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 22.91% | 0%
CZ 6A | 61.38% | 42.73% | 1.066% | 26.23% | 0% | 37.64% | 0% | 57.79% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 23.05% | 4.701% | CZ 6A | 61.38% | 42.73% | 0.4583% | 26.23% | 0% | 37.64% | 0% | 57.79% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 19.85% | 4.701% | CZ 6A | 61.38% | 42.73% | 2.744% | 0% | 0% | 37.64% | 0% | 57.79% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 27.55% | 4.701% | CZ 6A | 0% | 0% | -0.03028% | 26.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.78% | 4.701% | CZ 6A | 61.38% | 42.73% | 1.01% | 26.23% | 0% | 37.64% | 0% | 57.79% | 0% | 0% | 22.6% | 0% | 0% | 0% | 0% | 0% | 22.81% | 4.701%
CZ 6B | 61.89% | 42.98% | 1.034% | 23.58% | 0% | 49.1% | 0% | 69.79% | 0% | 0% | 22.96% | 0% | 0% | 0% | 0% | 0% | 26.81% | 0.6064% | CZ 6B | 61.89% | 42.98% | 0.4286% | 23.58% | 0% | 49.1% | 0% | 69.79% | 0% | 0% | 22.96% | 0% | 0% | 0% | 0% | 0% | 21.18% | 0.6064% | CZ 6B | 61.89% | 42.98% | 2.719% | 0% | 0% | 49.1% | 0% | 69.79% | 0% | 0% | 22.96% | 0% | 0% | 0% | 0% | 0% | 33.8% | 0.6064% | CZ 6B | 0% | 0% | -0.05741% | 23.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.05% | 0.6064% | CZ 6B | 61.89% | 42.98% | 0.9789% | 23.58% | 0% | 49.1% | 0% | 69.79% | 0% | 0% | 22.96% | 0% | 0% | 0% | 0% | 0% | 26.41% | 0.6064%
CZ 7 | 62.06% | 42.83% | 1.024% | 23.94% | 0% | 47.04% | 0% | 57.94% | 0% | 0% | 22.74% | 0% | 0% | 0% | 0% | 0% | 22.55% | 0.5553% | CZ 7 | 62.06% | 42.83% | 0.4362% | 23.94% | 0% | 47.04% | 0% | 57.94% | 0% | 0% | 22.74% | 0% | 0% | 0% | 0% | 0% | 19.26% | 0.5553% | CZ 7 | 62.06% | 42.83% | 2.756% | 0% | 0% | 47.04% | 0% | 57.94% | 0% | 0% | 22.74% | 0% | 0% | 0% | 0% | 0% | 27.77% | 0.5553% | CZ 7 | 0% | 0% | -0.02294% | 23.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.47% | 0.5553% | CZ 7 | 62.06% | 42.83% | 0.9695% | 23.94% | 0% | 47.04% | 0% | 57.94% | 0% | 0% | 22.74% | 0% | 0% | 0% | 0% | 0% | 22.3% | 0.5553%
CZ 8 | 61.1% | 42.15% | 0.9868% | 19.99% | 0% | 55.11% | 0% | 59.09% | 0% | 0% | 22.79% | 0% | 0% | 0% | 0% | 0% | 20.86% | 0.02085% | CZ 8 | 61.1% | 42.15% | 0.421% | 19.99% | 0% | 55.11% | 0% | 59.09% | 0% | 0% | 22.79% | 0% | 0% | 0% | 0% | 0% | 17.57% | 0.02085% | CZ 8 | 61.1% | 42.15% | 2.781% | 0% | 0% | 55.11% | 0% | 59.09% | 0% | 0% | 22.79% | 0% | 0% | 0% | 0% | 0% | 27.28% | 0.02085% | CZ 8 | 0% | 0% | -0.007003% | 19.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.35% | 0.02085% | CZ 8 | 61.1% | 42.15% | 0.9334% | 19.99% | 0% | 55.11% | 0% | 59.09% | 0% | 0% | 22.79% | 0% | 0% | 0% | 0% | 0% | 20.58% | 0.02085%
Us Weighted | 61.56% | 42.97% | 1.166% | 25.36% | 0% | 37.08% | 0% | 62.26% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 26.02% | 100% | Us Weighted | 61.56% | 42.97% | 0.5293% | 25.36% | 0% | 37.08% | 0% | 62.26% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 20.91% | 100% | Us Weighted | 61.56% | 42.97% | 2.722% | 0% | 0% | 37.08% | 0% | 62.26% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 31.2% | 100% | Us Weighted | 0% | 0% | -0.01661% | 25.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.42% | 100% | Us Weighted | 61.56% | 42.97% | 1.11% | 25.36% | 0% | 37.08% | 0% | 62.26% | 0% | 0% | 22.03% | 0% | 0% | 0% | 0% | 0% | 25.69% | 100%

## RetailStore
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Standalone Retail |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Standalone Retail | [14 empty] | Prototype Floor Area: | 24692 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.43204 | 0.071256 | 0.035386 | 0.045903 | 0 | 0.17813 | 0 | 0.21495 | 0.018183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2214 |  | STD2013 | 14.288 | 2.3565 | 3.5743 | 4.6366 | 0 | 5.8911 | 0 | 7.1086 | 0.60134 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.9167 |  | STD2013 | 4.1864 | 0.69046 | 0 | 0 | 0 | 1.7261 | 0 | 2.0828 | 0.17619 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.0477 |  | STD2013 | 0 | 0 | 0.035743 | 0.046366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08211 |  | STD2013 | 43.827 | 7.2284 | 3.9067 | 5.0678 | 0 | 18.0703 | 0 | 21.8049 | 1.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 124.6328
STD2010 | 0.5194 | 0.071256 | 0.035386 | 0.068788 | 0 | 0.20151 | 0 | 0.25986 | 0.017131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3993 |  | STD2010 | 17.1772 | 2.3565 | 3.5743 | 6.9483 | 0 | 6.6642 | 0 | 8.594 | 0.56654 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.3539 |  | STD2010 | 5.0329 | 0.69046 | 0 | 0 | 0 | 1.9526 | 0 | 2.518 | 0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.5495 |  | STD2010 | 0 | 0 | 0.035743 | 0.069483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10523 |  | STD2010 | 52.6891 | 7.2284 | 3.9068 | 7.5945 | 0 | 20.4418 | 0 | 26.3611 | 1.7378 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 142.8814
STD2007 | 0.57126 | 0.13358 | 0.036146 | 0.11232 | 0 | 0.30717 | 0 | 0.38341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.7705 |  | STD2007 | 18.8922 | 4.4176 | 3.6511 | 11.3457 | 0 | 10.1586 | 0 | 12.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.6383 |  | STD2007 | 5.5354 | 1.2943 | 0 | 0 | 0 | 2.9764 | 0 | 3.7152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.7168 |  | STD2007 | 0 | 0 | 0.036511 | 0.11346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14997 |  | STD2007 | 57.9498 | 13.5504 | 3.9907 | 12.4009 | 0 | 31.1604 | 0 | 38.8943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 180.9308
STD2004 | 0.57126 | 0.13358 | 0.03616 | 0.17423 | 0 | 0.35907 | 0 | 0.47131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9722 |  | STD2004 | 18.8922 | 4.4176 | 3.6526 | 17.5994 | 0 | 11.8749 | 0 | 15.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.5168 |  | STD2004 | 5.5354 | 1.2943 | 0 | 0 | 0 | 3.4793 | 0 | 4.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0714 |  | STD2004 | 0 | 0 | 0.036526 | 0.17599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21252 |  | STD2004 | 57.9498 | 13.5504 | 3.9923 | 19.2362 | 0 | 36.425 | 0 | 47.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 201.9492
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 1.4436e-05 | 0.061911 | 0 | 0.051898 | 0 | 0.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20172 |  | 2004-2007 | 0 | 0 | 0.0014582 | 6.2537 | 0 | 1.7163 | 0 | 2.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8785 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | 0.50288 | 0 | 0.85174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3546 |  | 2004-2007 | 0 | 0 | 1.4582e-05 | 0.062537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062551 |  | 2004-2007 | 0 | 0 | 0.0015938 | 6.8353 | 0 | 5.2647 | 0 | 8.9169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0184
2007-2010 | 0.051859 | 0.062321 | 0.00076002 | 0.043535 | 0 | 0.10566 | 0 | 0.12355 | -0.017131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00061531 | 0.37117 |  | 2007-2010 | 1.715 | 2.061 | 0.07677 | 4.3975 | 0 | 3.4944 | 0 | 4.0859 | -0.56654 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020349 | 15.2844 |  | 2007-2010 | 0.5025 | 0.60388 | 0 | 0 | 0 | 1.0238 | 0 | 1.1972 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0059623 | 3.1674 |  | 2007-2010 | 0 | 0 | 0.0007677 | 0.043975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044742 |  | 2007-2010 | 5.2607 | 6.322 | 0.083909 | 4.8064 | 0 | 10.7186 | 0 | 12.5332 | -1.7378 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062419 | 38.0494
2010-2013 | 0.08736 | 0 | 2.9444e-07 | 0.022885 | 0 | 0.023377 | 0 | 0.044915 | -0.0010522 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00038312 | 0.17787 |  | 2010-2013 | 2.8891 | 0 | 2.9741e-05 | 2.3116 | 0 | 0.77312 | 0 | 1.4854 | -0.034797 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01267 | 7.4372 |  | 2010-2013 | 0.84651 | 0 | 0 | 0 | 0 | 0.22652 | 0 | 0.43521 | -0.010196 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037124 | 1.5018 |  | 2010-2013 | 0 | 0 | 2.9741e-07 | 0.023116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023117 |  | 2010-2013 | 8.8621 | 0 | 3.2507e-05 | 2.5266 | 0 | 2.3715 | 0 | 4.5563 | -0.10674 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038865 | 18.2486
2004-2013 | 0.13922 | 0.062321 | 0.00077475 | 0.12833 | 0 | 0.18094 | 0 | 0.25636 | -0.018183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.75076 |  | 2004-2013 | 4.6042 | 2.061 | 0.078258 | 12.9628 | 0 | 5.9838 | 0 | 8.4783 | -0.60134 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 33.6001 |  | 2004-2013 | 1.349 | 0.60388 | 0 | 0 | 0 | 1.7532 | 0 | 2.4841 | -0.17619 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.0237 |  | 2004-2013 | 0 | 0 | 0.00078258 | 0.12963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13041 |  | 2004-2013 | 14.1228 | 6.322 | 0.085536 | 14.1683 | 0 | 18.3547 | 0 | 26.0063 | -1.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 77.3164
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.03992% | 35.53% |  | 14.45% |  | 18.65% | [7 empty] | 0% | 10.23% |  | 2004-2007 | 0% | 0% | 0.03992% | 35.53% |  | 14.45% |  | 18.65% | [7 empty] | 0% | 13.68% |  | 2004-2007 | 0% | 0% |  |  |  | 14.45% |  | 18.65% | [7 empty] | 0% | 7.935% |  | 2004-2007 |  |  | 0.03992% | 35.53% | [12 empty] | 29.43% |  | 2004-2007 | 0% | 0% | 0.03992% | 35.53% |  | 14.45% |  | 18.65% | [7 empty] | 0% | 10.41%
2007-2010 | 9.078% | 46.66% | 2.103% | 38.76% |  | 34.4% |  | 32.22% | [7 empty] | 0.2716% | 20.96% |  | 2007-2010 | 9.078% | 46.66% | 2.103% | 38.76% |  | 34.4% |  | 32.22% | [7 empty] | 0.2716% | 22.27% |  | 2007-2010 | 9.078% | 46.66% |  |  |  | 34.4% |  | 32.22% | [7 empty] | 0.2716% | 20.15% |  | 2007-2010 |  |  | 2.103% | 38.76% | [12 empty] | 29.83% |  | 2007-2010 | 9.078% | 46.66% | 2.103% | 38.76% |  | 34.4% |  | 32.22% | [7 empty] | 0.2716% | 21.03%
2010-2013 | 16.82% | 0% | 0.0008321% | 33.27% |  | 11.6% |  | 17.28% | -6.142% | [6 empty] | 0.1696% | 12.71% |  | 2010-2013 | 16.82% | 0% | 0.0008321% | 33.27% |  | 11.6% |  | 17.28% | -6.142% | [6 empty] | 0.1696% | 13.94% |  | 2010-2013 | 16.82% | 0% |  |  |  | 11.6% |  | 17.28% | -6.142% | [6 empty] | 0.1696% | 11.97% |  | 2010-2013 |  |  | 0.0008321% | 33.27% | [12 empty] | 21.97% |  | 2010-2013 | 16.82% | 0% | 0.0008321% | 33.27% |  | 11.6% |  | 17.28% | -6.142% | [6 empty] | 0.1696% | 12.77%
2004-2013 | 24.37% | 46.66% | 2.143% | 73.65% |  | 50.39% |  | 54.39% | [7 empty] | 0.4407% | 38.07% |  | 2004-2013 | 24.37% | 46.66% | 2.143% | 73.65% |  | 50.39% |  | 54.39% | [7 empty] | 0.4407% | 42.26% |  | 2004-2013 | 24.37% | 46.66% |  |  |  | 50.39% |  | 54.39% | [7 empty] | 0.4407% | 35.29% |  | 2004-2013 |  |  | 2.143% | 73.65% | [12 empty] | 61.36% |  | 2004-2013 | 24.37% | 46.66% | 2.143% | 73.65% |  | 50.39% |  | 54.39% | [7 empty] | 0.4407% | 38.29%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.41181 | 0.071214 | 0.032617 | 0.0019191 | 0 | 0.44217 | 0 | 0.14054 | 0.031021 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.3569 | 1.47% | CZ 1A | 13.6191 | 2.3551 | 3.2946 | 0.19385 | 0 | 14.6231 | 0 | 4.6477 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.2195 | 1.47% | CZ 1A | 3.9903 | 0.69005 | 0 | 0 | 0 | 4.2845 | 0 | 1.3618 | 0.30059 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 12.8131 | 1.47% | CZ 1A | 0 | 0 | 0.032946 | 0.0019385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034885 | 1.47% | CZ 1A | 41.7749 | 7.2241 | 3.601 | 0.21188 | 0 | 44.8547 | 0 | 14.2563 | 3.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 137.953 | 1.47%
CZ 1B | 0.43009 | 0.071202 | 0.032104 | 0.014034 | 0 | 0.51488 | 0 | 0.20286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.4907 | 0% | CZ 1B | 14.2238 | 2.3548 | 3.2428 | 1.4176 | 0 | 17.0278 | 0 | 6.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 52.4356 | 0% | CZ 1B | 4.1675 | 0.68994 | 0 | 0 | 0 | 4.9891 | 0 | 1.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 13.998 | 0% | CZ 1B | 0 | 0 | 0.032428 | 0.014176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046604 | 0% | CZ 1B | 43.6299 | 7.223 | 3.5444 | 1.5494 | 0 | 52.2308 | 0 | 20.5783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 151.6388 | 0%
CZ 2A | 0.42229 | 0.071179 | 0.033765 | 0.010781 | 0 | 0.27886 | 0 | 0.22363 | 0.024183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2903 | 14.55% | CZ 2A | 13.9658 | 2.354 | 3.4106 | 1.089 | 0 | 9.2225 | 0 | 7.3956 | 0.79977 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.6973 | 14.55% | CZ 2A | 4.0919 | 0.68971 | 0 | 0 | 0 | 2.7022 | 0 | 2.1669 | 0.23433 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 12.0708 | 14.55% | CZ 2A | 0 | 0 | 0.034106 | 0.01089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044996 | 14.55% | CZ 2A | 42.8384 | 7.2206 | 3.7277 | 1.1903 | 0 | 28.2889 | 0 | 22.6853 | 2.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 131.2875 | 14.55%
CZ 2B | 0.43199 | 0.071156 | 0.033081 | 0.013954 | 0 | 0.36496 | 0 | 0.27657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.4173 | 3.321% | CZ 2B | 14.2864 | 2.3532 | 3.3415 | 1.4095 | 0 | 12.0698 | 0 | 9.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.067 | 3.321% | CZ 2B | 4.1859 | 0.68949 | 0 | 0 | 0 | 3.5364 | 0 | 2.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 13.2775 | 3.321% | CZ 2B | 0 | 0 | 0.033415 | 0.014095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04751 | 3.321% | CZ 2B | 43.8218 | 7.2183 | 3.6522 | 1.5406 | 0 | 37.0228 | 0 | 28.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 144.1945 | 3.321%
CZ 3A | 0.42582 | 0.071202 | 0.034669 | 0.02841 | 0 | 0.21394 | 0 | 0.2085 | 0.02315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2313 | 15.64% | CZ 3A | 14.0825 | 2.3548 | 3.5019 | 2.8697 | 0 | 7.0754 | 0 | 6.8953 | 0.76559 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.0053 | 15.64% | CZ 3A | 4.1261 | 0.68994 | 0 | 0 | 0 | 2.0731 | 0 | 2.0203 | 0.22432 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.3196 | 15.64% | CZ 3A | 0 | 0 | 0.035019 | 0.028697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063716 | 15.64% | CZ 3A | 43.1965 | 7.223 | 3.8276 | 3.1366 | 0 | 21.703 | 0 | 21.1507 | 2.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 125.4688 | 15.64%
CZ 3B | 0.43339 | 0.071156 | 0.034357 | 0.026822 | 0 | 0.20463 | 0 | 0.27426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2702 | 8.197% | CZ 3B | 14.3328 | 2.3532 | 3.4704 | 2.7093 | 0 | 6.7675 | 0 | 9.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.1634 | 8.197% | CZ 3B | 4.1995 | 0.68949 | 0 | 0 | 0 | 1.9829 | 0 | 2.6575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.7151 | 8.197% | CZ 3B | 0 | 0 | 0.034704 | 0.027093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061797 | 8.197% | CZ 3B | 43.9643 | 7.2183 | 3.7932 | 2.9612 | 0 | 20.7585 | 0 | 27.8213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 129.3999 | 8.197%
CZ 3C | 0.42884 | 0.071167 | 0.035634 | 0.030629 | 0 | 0.035932 | 0 | 0.17098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 0.99875 | 1.253% | CZ 3C | 14.1823 | 2.3536 | 3.5994 | 3.0939 | 0 | 1.1883 | 0 | 5.6544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 37.5321 | 1.253% | CZ 3C | 4.1554 | 0.6896 | 0 | 0 | 0 | 0.34818 | 0 | 1.6567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.0357 | 1.253% | CZ 3C | 0 | 0 | 0.035994 | 0.030939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066933 | 1.253% | CZ 3C | 43.5027 | 7.2194 | 3.9342 | 3.3816 | 0 | 3.645 | 0 | 17.3443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 101.9103 | 1.253%
CZ 4A | 0.43002 | 0.071191 | 0.035763 | 0.039412 | 0 | 0.15571 | 0 | 0.20079 | 0.023788 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.1823 | 16.69% | CZ 4A | 14.2215 | 2.3544 | 3.6125 | 3.981 | 0 | 5.1495 | 0 | 6.6404 | 0.78671 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.2061 | 16.69% | CZ 4A | 4.1669 | 0.68983 | 0 | 0 | 0 | 1.5088 | 0 | 1.9456 | 0.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.7274 | 16.69% | CZ 4A | 0 | 0 | 0.036125 | 0.03981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075934 | 16.69% | CZ 4A | 43.6228 | 7.2218 | 3.9484 | 4.3512 | 0 | 15.7956 | 0 | 20.3687 | 2.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 120.6048 | 16.69%
CZ 4B | 0.43252 | 0.071133 | 0.035589 | 0.050371 | 0 | 0.14756 | 0 | 0.26934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2321 | 0.7809% | CZ 4B | 14.304 | 2.3525 | 3.5948 | 5.088 | 0 | 4.88 | 0 | 8.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.587 | 0.7809% | CZ 4B | 4.191 | 0.68926 | 0 | 0 | 0 | 1.4298 | 0 | 2.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.1058 | 0.7809% | CZ 4B | 0 | 0 | 0.035948 | 0.05088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086828 | 0.7809% | CZ 4B | 43.876 | 7.2159 | 3.9291 | 5.5612 | 0 | 14.9688 | 0 | 27.3231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 125.7573 | 0.7809%
CZ 4C | 0.43356 | 0.07126 | 0.036227 | 0.081286 | 0 | 0.073849 | 0 | 0.20822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.13 | 2.808% | CZ 4C | 14.3386 | 2.3567 | 3.6593 | 8.2107 | 0 | 2.4423 | 0 | 6.8861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.3538 | 2.808% | CZ 4C | 4.2012 | 0.6905 | 0 | 0 | 0 | 0.71559 | 0 | 2.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.8107 | 2.808% | CZ 4C | 0 | 0 | 0.036593 | 0.082107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1187 | 2.808% | CZ 4C | 43.982 | 7.2289 | 3.9996 | 8.9743 | 0 | 7.4915 | 0 | 21.1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 115.6818 | 2.808%
CZ 5A | 0.43196 | 0.071446 | 0.036531 | 0.069182 | 0 | 0.12426 | 0 | 0.20181 | 0.022244 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.183 | 22.48% | CZ 5A | 14.2856 | 2.3628 | 3.69 | 6.9881 | 0 | 4.1094 | 0 | 6.6742 | 0.73565 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.3059 | 22.48% | CZ 5A | 4.1856 | 0.6923 | 0 | 0 | 0 | 1.204 | 0 | 1.9555 | 0.21554 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.4388 | 22.48% | CZ 5A | 0 | 0 | 0.0369 | 0.069881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10678 | 22.48% | CZ 5A | 43.8195 | 7.2477 | 4.0332 | 7.638 | 0 | 12.6051 | 0 | 20.4723 | 2.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 120.9555 | 22.48%
CZ 5B | 0.43921 | 0.071005 | 0.036387 | 0.10607 | 0 | 0.10386 | 0 | 0.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2155 | 5.194% | CZ 5B | 14.5252 | 2.3482 | 3.6754 | 10.7138 | 0 | 3.4348 | 0 | 7.7189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 49.8765 | 5.194% | CZ 5B | 4.2558 | 0.68803 | 0 | 0 | 0 | 1.0064 | 0 | 2.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.3977 | 5.194% | CZ 5B | 0 | 0 | 0.036754 | 0.10714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14389 | 5.194% | CZ 5B | 44.5544 | 7.2029 | 4.0172 | 11.7102 | 0 | 10.5359 | 0 | 23.6769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 124.5807 | 5.194%
CZ 5C | 0.44171 | 0.071353 | 0.036546 | 0.11447 | 0 | 0.027457 | 0 | 0.17017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.0873 | 0% | CZ 5C | 14.6081 | 2.3598 | 3.6915 | 11.5625 | 0 | 0.90804 | 0 | 5.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.218 | 0% | CZ 5C | 4.2801 | 0.6914 | 0 | 0 | 0 | 0.26605 | 0 | 1.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.0724 | 0% | CZ 5C | 0 | 0 | 0.036915 | 0.11563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15254 | 0% | CZ 5C | 44.8088 | 7.2383 | 4.0349 | 12.6378 | 0 | 2.7853 | 0 | 17.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 111.6512 | 0%
CZ 6A | 0.46518 | 0.071493 | 0.037204 | 0.081806 | 0 | 0.078598 | 0 | 0.19198 | 0.021211 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.173 | 6.216% | CZ 6A | 15.3841 | 2.3644 | 3.7579 | 8.2633 | 0 | 2.5993 | 0 | 6.349 | 0.70147 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.8796 | 6.216% | CZ 6A | 4.5075 | 0.69275 | 0 | 0 | 0 | 0.7616 | 0 | 1.8602 | 0.20553 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.2134 | 6.216% | CZ 6A | 0 | 0 | 0.037579 | 0.082633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12021 | 6.216% | CZ 6A | 47.1889 | 7.2524 | 4.1074 | 9.0318 | 0 | 7.9732 | 0 | 19.4748 | 2.1517 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 120.0633 | 6.216%
CZ 6B | 0.46654 | 0.071144 | 0.037299 | 0.052363 | 0 | 0.069809 | 0 | 0.25017 | 0.021014 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.1939 | 0.5978% | CZ 6B | 15.429 | 2.3528 | 3.7675 | 5.2892 | 0 | 2.3087 | 0 | 8.2733 | 0.69495 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.5756 | 0.5978% | CZ 6B | 4.5207 | 0.68938 | 0 | 0 | 0 | 0.67644 | 0 | 2.4241 | 0.20362 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.6999 | 0.5978% | CZ 6B | 0 | 0 | 0.037675 | 0.052892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090567 | 0.5978% | CZ 6B | 47.3267 | 7.2171 | 4.1179 | 5.781 | 0 | 7.0816 | 0 | 25.3775 | 2.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 121.9167 | 0.5978%
CZ 7 | 0.46716 | 0.071318 | 0.038272 | 0.12313 | 0 | 0.052685 | 0 | 0.19516 | 0.021397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.1947 | 0.7115% | CZ 7 | 15.4497 | 2.3586 | 3.8658 | 12.4373 | 0 | 1.7424 | 0 | 6.4542 | 0.70762 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.4757 | 0.7115% | CZ 7 | 4.5267 | 0.69106 | 0 | 0 | 0 | 0.51051 | 0 | 1.8911 | 0.20733 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 10.0125 | 0.7115% | CZ 7 | 0 | 0 | 0.038658 | 0.12437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16303 | 0.7115% | CZ 7 | 47.3903 | 7.2347 | 4.2253 | 13.594 | 0 | 5.3445 | 0 | 19.7975 | 2.1705 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 122.64 | 0.7115%
CZ 8 | 0.47209 | 0.071818 | 0.039575 | 0.25504 | 0 | 0.030708 | 0 | 0.17282 | 0.022651 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2903 | 0.0892% | CZ 8 | 15.6125 | 2.3751 | 3.9975 | 25.7621 | 0 | 1.0155 | 0 | 5.7155 | 0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 62.6874 | 0.0892% | CZ 8 | 4.5744 | 0.6959 | 0 | 0 | 0 | 0.29755 | 0 | 1.6746 | 0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 9.6478 | 0.0892% | CZ 8 | 0 | 0 | 0.039975 | 0.25762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2976 | 0.0892% | CZ 8 | 47.8897 | 7.2854 | 4.3692 | 28.158 | 0 | 3.1151 | 0 | 17.5316 | 2.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 133.5298 | 0.0892%
Us Weighted | 0.43204 | 0.071256 | 0.035386 | 0.045903 | 0 | 0.17813 | 0 | 0.21495 | 0.018183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22558 | 1.2214 | 100% | Us Weighted | 14.288 | 2.3565 | 3.5743 | 4.6366 | 0 | 5.8911 | 0 | 7.1086 | 0.60134 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.9167 | 100% | Us Weighted | 4.1864 | 0.69046 | 0 | 0 | 0 | 1.7261 | 0 | 2.0828 | 0.17619 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1858 | 11.0477 | 100% | Us Weighted | 0 | 0 | 0.035743 | 0.046366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08211 | 100% | Us Weighted | 43.827 | 7.2284 | 3.9067 | 5.0678 | 0 | 18.0703 | 0 | 21.8049 | 1.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8831 | 124.6328 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.5073 | 0.071214 | 0.032617 | 0.0046856 | 0 | 0.58641 | 0 | 0.21942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.6476 | 1.47% | CZ 1A | 16.777 | 2.3551 | 3.2946 | 0.47329 | 0 | 19.3933 | 0 | 7.2566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 57.0228 | 1.47% | CZ 1A | 4.9156 | 0.69005 | 0 | 0 | 0 | 5.6822 | 0 | 2.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 15.6035 | 1.47% | CZ 1A | 0 | 0 | 0.032946 | 0.0047329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037679 | 1.47% | CZ 1A | 51.4617 | 7.2241 | 3.601 | 0.51731 | 0 | 59.4867 | 0 | 22.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 167.4718 | 1.47%
CZ 1B | 0.52035 | 0.071202 | 0.032104 | 0.016668 | 0 | 0.57639 | 0 | 0.27579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.7185 | 0% | CZ 1B | 17.2086 | 2.3548 | 3.2428 | 1.6836 | 0 | 19.0619 | 0 | 9.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 60.1452 | 0% | CZ 1B | 5.0421 | 0.68994 | 0 | 0 | 0 | 5.5851 | 0 | 2.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 16.179 | 0% | CZ 1B | 0 | 0 | 0.032428 | 0.016836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049264 | 0% | CZ 1B | 52.7855 | 7.223 | 3.5444 | 1.8402 | 0 | 58.4703 | 0 | 27.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 174.7621 | 0%
CZ 2A | 0.51624 | 0.071179 | 0.033765 | 0.020817 | 0 | 0.31771 | 0 | 0.2523 | 0.024241 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.4622 | 14.55% | CZ 2A | 17.0727 | 2.354 | 3.4106 | 2.1028 | 0 | 10.5071 | 0 | 8.344 | 0.80169 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.0656 | 14.55% | CZ 2A | 5.0022 | 0.68971 | 0 | 0 | 0 | 3.0786 | 0 | 2.4448 | 0.23489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 13.6397 | 14.55% | CZ 2A | 0 | 0 | 0.034106 | 0.021028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055133 | 14.55% | CZ 2A | 52.3686 | 7.2206 | 3.7277 | 2.2983 | 0 | 32.2295 | 0 | 25.5942 | 2.4591 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 148.82 | 14.55%
CZ 2B | 0.52118 | 0.071156 | 0.033084 | 0.019689 | 0 | 0.39576 | 0 | 0.27898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.5458 | 3.321% | CZ 2B | 17.2362 | 2.3532 | 3.3418 | 1.9888 | 0 | 13.0884 | 0 | 9.2263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 54.7076 | 3.321% | CZ 2B | 5.0502 | 0.68949 | 0 | 0 | 0 | 3.8349 | 0 | 2.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 14.4673 | 3.321% | CZ 2B | 0 | 0 | 0.033418 | 0.019888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053306 | 3.321% | CZ 2B | 52.8703 | 7.2183 | 3.6526 | 2.1737 | 0 | 40.1473 | 0 | 28.3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 157.2848 | 3.321%
CZ 3A | 0.51757 | 0.071202 | 0.034669 | 0.042098 | 0 | 0.2419 | 0 | 0.24434 | 0.022918 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.4007 | 15.64% | CZ 3A | 17.1168 | 2.3548 | 3.5019 | 4.2524 | 0 | 8 | 0 | 8.0806 | 0.75792 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 51.5371 | 15.64% | CZ 3A | 5.0152 | 0.68994 | 0 | 0 | 0 | 2.344 | 0 | 2.3676 | 0.22207 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.8283 | 15.64% | CZ 3A | 0 | 0 | 0.035019 | 0.042524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077543 | 15.64% | CZ 3A | 52.504 | 7.223 | 3.8276 | 4.6478 | 0 | 24.539 | 0 | 24.7863 | 2.3248 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 142.7745 | 15.64%
CZ 3B | 0.52362 | 0.071156 | 0.034354 | 0.032396 | 0 | 0.22396 | 0 | 0.27662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3881 | 8.197% | CZ 3B | 17.3169 | 2.3532 | 3.4701 | 3.2724 | 0 | 7.4068 | 0 | 9.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.4404 | 8.197% | CZ 3B | 5.0738 | 0.68949 | 0 | 0 | 0 | 2.1702 | 0 | 2.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.8034 | 8.197% | CZ 3B | 0 | 0 | 0.034701 | 0.032724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067424 | 8.197% | CZ 3B | 53.1176 | 7.2183 | 3.7928 | 3.5767 | 0 | 22.7194 | 0 | 28.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 141.4083 | 8.197%
CZ 3C | 0.51927 | 0.071167 | 0.03563 | 0.040441 | 0 | 0.038393 | 0 | 0.19327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.1241 | 1.253% | CZ 3C | 17.1729 | 2.3536 | 3.599 | 4.085 | 0 | 1.2697 | 0 | 6.3916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 42.3446 | 1.253% | CZ 3C | 5.0316 | 0.6896 | 0 | 0 | 0 | 0.37202 | 0 | 1.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 10.1555 | 1.253% | CZ 3C | 0 | 0 | 0.03599 | 0.04085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07684 | 1.253% | CZ 3C | 52.6759 | 7.2194 | 3.9337 | 4.4649 | 0 | 3.8947 | 0 | 19.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 114.7162 | 1.253%
CZ 4A | 0.51367 | 0.071191 | 0.035763 | 0.066039 | 0 | 0.1748 | 0 | 0.25751 | 0.021617 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3666 | 16.69% | CZ 4A | 16.9878 | 2.3544 | 3.6125 | 6.6706 | 0 | 5.7807 | 0 | 8.5164 | 0.71491 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.1101 | 16.69% | CZ 4A | 4.9774 | 0.68983 | 0 | 0 | 0 | 1.6937 | 0 | 2.4953 | 0.20947 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.2552 | 16.69% | CZ 4A | 0 | 0 | 0.036125 | 0.066706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10283 | 16.69% | CZ 4A | 52.1083 | 7.2218 | 3.9484 | 7.291 | 0 | 17.7318 | 0 | 26.123 | 2.1929 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 139.5392 | 16.69%
CZ 4B | 0.51542 | 0.071133 | 0.035589 | 0.066039 | 0 | 0.16911 | 0 | 0.29743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3807 | 0.7809% | CZ 4B | 17.0458 | 2.3525 | 3.5948 | 6.6706 | 0 | 5.5926 | 0 | 9.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.5655 | 0.7809% | CZ 4B | 4.9944 | 0.68926 | 0 | 0 | 0 | 1.6386 | 0 | 2.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.3938 | 0.7809% | CZ 4B | 0 | 0 | 0.035948 | 0.066706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10265 | 0.7809% | CZ 4B | 52.2861 | 7.2159 | 3.9291 | 7.291 | 0 | 17.1547 | 0 | 30.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 140.9709 | 0.7809%
CZ 4C | 0.51699 | 0.07126 | 0.036227 | 0.10631 | 0 | 0.084147 | 0 | 0.24175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.2826 | 2.808% | CZ 4C | 17.0976 | 2.3567 | 3.6593 | 10.738 | 0 | 2.7829 | 0 | 7.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.1022 | 2.808% | CZ 4C | 5.0096 | 0.6905 | 0 | 0 | 0 | 0.81537 | 0 | 2.3425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.0475 | 2.808% | CZ 4C | 0 | 0 | 0.036593 | 0.10738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14397 | 2.808% | CZ 4C | 52.4451 | 7.2289 | 3.9996 | 11.7366 | 0 | 8.5361 | 0 | 24.5237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 131.392 | 2.808%
CZ 5A | 0.51769 | 0.071446 | 0.036531 | 0.10709 | 0 | 0.13989 | 0 | 0.26967 | 0.021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3902 | 22.48% | CZ 5A | 17.1207 | 2.3628 | 3.69 | 10.8167 | 0 | 4.6262 | 0 | 8.9184 | 0.72566 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 55.7332 | 22.48% | CZ 5A | 5.0163 | 0.6923 | 0 | 0 | 0 | 1.3555 | 0 | 2.6131 | 0.21262 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0793 | 22.48% | CZ 5A | 0 | 0 | 0.0369 | 0.10817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14507 | 22.48% | CZ 5A | 52.5158 | 7.2477 | 4.0332 | 11.8226 | 0 | 14.1904 | 0 | 27.3561 | 2.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 142.3136 | 22.48%
CZ 5B | 0.52354 | 0.071005 | 0.03639 | 0.1287 | 0 | 0.11944 | 0 | 0.28037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3854 | 5.194% | CZ 5B | 17.3142 | 2.3482 | 3.6758 | 13 | 0 | 3.9501 | 0 | 9.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 57.0335 | 5.194% | CZ 5B | 5.073 | 0.68803 | 0 | 0 | 0 | 1.1574 | 0 | 2.7168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.8247 | 5.194% | CZ 5B | 0 | 0 | 0.036758 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16676 | 5.194% | CZ 5B | 53.1093 | 7.2029 | 4.0177 | 14.2091 | 0 | 12.1164 | 0 | 28.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 142.0193 | 5.194%
CZ 5C | 0.52292 | 0.071353 | 0.03655 | 0.14744 | 0 | 0.027945 | 0 | 0.22154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.2537 | 0% | CZ 5C | 17.2938 | 2.3598 | 3.6919 | 14.8928 | 0 | 0.92417 | 0 | 7.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.9618 | 0% | CZ 5C | 5.067 | 0.6914 | 0 | 0 | 0 | 0.27078 | 0 | 2.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 10.3654 | 0% | CZ 5C | 0 | 0 | 0.036919 | 0.14893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18585 | 0% | CZ 5C | 53.0469 | 7.2383 | 4.0353 | 16.2779 | 0 | 2.8348 | 0 | 22.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 128.8284 | 0%
CZ 6A | 0.54395 | 0.071493 | 0.037208 | 0.11977 | 0 | 0.087955 | 0 | 0.257 | 0.021025 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3644 | 6.216% | CZ 6A | 17.9892 | 2.3644 | 3.7583 | 12.098 | 0 | 2.9088 | 0 | 8.4995 | 0.69533 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 55.7863 | 6.216% | CZ 6A | 5.2708 | 0.69275 | 0 | 0 | 0 | 0.85227 | 0 | 2.4903 | 0.20373 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.6994 | 6.216% | CZ 6A | 0 | 0 | 0.037583 | 0.12098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15856 | 6.216% | CZ 6A | 55.1798 | 7.2524 | 4.1079 | 13.2231 | 0 | 8.9224 | 0 | 26.0712 | 2.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 139.8116 | 6.216%
CZ 6B | 0.54373 | 0.071144 | 0.037303 | 0.18273 | 0 | 0.071585 | 0 | 0.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.4182 | 0.5978% | CZ 6B | 17.9819 | 2.3528 | 3.7679 | 18.4577 | 0 | 2.3674 | 0 | 9.4486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 61.8492 | 0.5978% | CZ 6B | 5.2686 | 0.68938 | 0 | 0 | 0 | 0.69365 | 0 | 2.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.6096 | 0.5978% | CZ 6B | 0 | 0 | 0.037679 | 0.18458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22226 | 0.5978% | CZ 6B | 55.1574 | 7.2171 | 4.1183 | 20.1743 | 0 | 7.2618 | 0 | 28.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 145.8335 | 0.5978%
CZ 7 | 0.52542 | 0.071318 | 0.038279 | 0.16523 | 0 | 0.057723 | 0 | 0.29278 | 0.021315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.398 | 0.7115% | CZ 7 | 17.3764 | 2.3586 | 3.8666 | 16.6901 | 0 | 1.909 | 0 | 9.6828 | 0.70493 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 60.0612 | 0.7115% | CZ 7 | 5.0912 | 0.69106 | 0 | 0 | 0 | 0.55933 | 0 | 2.837 | 0.20654 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 11.5747 | 0.7115% | CZ 7 | 0 | 0 | 0.038666 | 0.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20557 | 0.7115% | CZ 7 | 53.3001 | 7.2347 | 4.2262 | 18.2422 | 0 | 5.8556 | 0 | 29.701 | 2.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 143.6441 | 0.7115%
CZ 8 | 0.55035 | 0.071818 | 0.039594 | 0.33214 | 0 | 0.030568 | 0 | 0.3425 | 0.022256 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.6152 | 0.0892% | CZ 8 | 18.2007 | 2.3751 | 3.9994 | 33.5498 | 0 | 1.0109 | 0 | 11.3269 | 0.73603 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 78.6717 | 0.0892% | CZ 8 | 5.3328 | 0.6959 | 0 | 0 | 0 | 0.2962 | 0 | 3.3187 | 0.21565 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.0488 | 0.0892% | CZ 8 | 0 | 0 | 0.039994 | 0.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37549 | 0.0892% | CZ 8 | 55.8287 | 7.2854 | 4.3713 | 36.6699 | 0 | 3.1009 | 0 | 34.744 | 2.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 167.1799 | 0.0892%
Us Weighted | 0.5194 | 0.071256 | 0.035386 | 0.068788 | 0 | 0.20151 | 0 | 0.25986 | 0.017131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22596 | 1.3993 | 100% | Us Weighted | 17.1772 | 2.3565 | 3.5743 | 6.9483 | 0 | 6.6642 | 0 | 8.594 | 0.56654 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 53.3539 | 100% | Us Weighted | 5.0329 | 0.69046 | 0 | 0 | 0 | 1.9526 | 0 | 2.518 | 0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1895 | 12.5495 | 100% | Us Weighted | 0 | 0 | 0.035743 | 0.069483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10523 | 100% | Us Weighted | 52.6891 | 7.2284 | 3.9068 | 7.5945 | 0 | 20.4418 | 0 | 26.3611 | 1.7378 | 0 | 0 | 0 | 0 | 0 | 0 | 22.922 | 142.8814 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.57126 | 0.13376 | 0.033343 | 0.0026905 | 0 | 0.82597 | 0 | 0.45685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.2504 | 1.47% | CZ 1A | 18.8922 | 4.4235 | 3.368 | 0.27177 | 0 | 27.3161 | 0 | 15.1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.8734 | 1.47% | CZ 1A | 5.5354 | 1.2961 | 0 | 0 | 0 | 8.0035 | 0 | 4.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.4573 | 1.47% | CZ 1A | 0 | 0 | 0.03368 | 0.0027177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036397 | 1.47% | CZ 1A | 57.9498 | 13.5685 | 3.6812 | 0.29704 | 0 | 83.789 | 0 | 46.3445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 228.6144 | 1.47%
CZ 1B | 0.57126 | 0.13373 | 0.032818 | 0.0096676 | 0 | 0.76854 | 0 | 0.49518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.2378 | 0% | CZ 1B | 18.8922 | 4.4227 | 3.315 | 0.97653 | 0 | 25.4167 | 0 | 16.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.8924 | 0% | CZ 1B | 5.5354 | 1.2958 | 0 | 0 | 0 | 7.447 | 0 | 4.7982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.2719 | 0% | CZ 1B | 0 | 0 | 0.03315 | 0.0097653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042915 | 0% | CZ 1B | 57.9498 | 13.5662 | 3.6233 | 1.0673 | 0 | 77.9628 | 0 | 50.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 227.3859 | 0%
CZ 2A | 0.57126 | 0.1337 | 0.034506 | 0.032423 | 0 | 0.51167 | 0 | 0.37494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8851 | 14.55% | CZ 2A | 18.8922 | 4.4216 | 3.4854 | 3.2751 | 0 | 16.9218 | 0 | 12.3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 66.8888 | 14.55% | CZ 2A | 5.5354 | 1.2955 | 0 | 0 | 0 | 4.958 | 0 | 3.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.6174 | 14.55% | CZ 2A | 0 | 0 | 0.034854 | 0.032751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067605 | 14.55% | CZ 2A | 57.9498 | 13.5626 | 3.8096 | 3.5796 | 0 | 51.9057 | 0 | 38.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 191.8262 | 14.55%
CZ 2B | 0.57126 | 0.13366 | 0.033806 | 0.013757 | 0 | 0.51814 | 0 | 0.38567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8829 | 3.321% | CZ 2B | 18.8922 | 4.4204 | 3.4148 | 1.3896 | 0 | 17.1356 | 0 | 12.7548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 65.5005 | 3.321% | CZ 2B | 5.5354 | 1.2952 | 0 | 0 | 0 | 5.0207 | 0 | 3.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.7838 | 3.321% | CZ 2B | 0 | 0 | 0.034148 | 0.013896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048043 | 3.321% | CZ 2B | 57.9498 | 13.5591 | 3.7324 | 1.5188 | 0 | 52.5617 | 0 | 39.1239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 191.43 | 3.321%
CZ 3A | 0.57126 | 0.1336 | 0.035421 | 0.076247 | 0 | 0.39995 | 0 | 0.38504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8281 | 15.64% | CZ 3A | 18.8922 | 4.4185 | 3.5779 | 7.7017 | 0 | 13.227 | 0 | 12.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.0442 | 15.64% | CZ 3A | 5.5354 | 1.2946 | 0 | 0 | 0 | 3.8755 | 0 | 3.7309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.6319 | 15.64% | CZ 3A | 0 | 0 | 0.035779 | 0.077017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1128 | 15.64% | CZ 3A | 57.9498 | 13.5532 | 3.9107 | 8.4179 | 0 | 40.5725 | 0 | 39.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 186.4476 | 15.64%
CZ 3B | 0.57126 | 0.13366 | 0.035095 | 0.023227 | 0 | 0.29758 | 0 | 0.39068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6781 | 8.197% | CZ 3B | 18.8922 | 4.4204 | 3.5449 | 2.3461 | 0 | 9.8414 | 0 | 12.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 59.4585 | 8.197% | CZ 3B | 5.5354 | 1.2952 | 0 | 0 | 0 | 2.8835 | 0 | 3.7856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.6951 | 8.197% | CZ 3B | 0 | 0 | 0.035449 | 0.023461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05891 | 8.197% | CZ 3B | 57.9498 | 13.5591 | 3.8746 | 2.5643 | 0 | 30.1873 | 0 | 39.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 170.751 | 8.197%
CZ 3C | 0.57126 | 0.1336 | 0.036387 | 0.030044 | 0 | 0.079747 | 0 | 0.31424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.3919 | 1.253% | CZ 3C | 18.8922 | 4.4185 | 3.6754 | 3.0348 | 0 | 2.6373 | 0 | 10.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 50.5437 | 1.253% | CZ 3C | 5.5354 | 1.2946 | 0 | 0 | 0 | 0.77274 | 0 | 3.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 12.8431 | 1.253% | CZ 3C | 0 | 0 | 0.036754 | 0.030348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067102 | 1.253% | CZ 3C | 57.9498 | 13.5532 | 4.0172 | 3.317 | 0 | 8.0898 | 0 | 31.8774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 141.7888 | 1.253%
CZ 4A | 0.57126 | 0.13353 | 0.036531 | 0.13118 | 0 | 0.26626 | 0 | 0.37163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.737 | 16.69% | CZ 4A | 18.8922 | 4.4162 | 3.69 | 13.2507 | 0 | 8.8055 | 0 | 12.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.838 | 16.69% | CZ 4A | 5.5354 | 1.2939 | 0 | 0 | 0 | 2.58 | 0 | 3.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.2058 | 16.69% | CZ 4A | 0 | 0 | 0.0369 | 0.13251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16941 | 16.69% | CZ 4A | 57.9498 | 13.5461 | 4.0332 | 14.483 | 0 | 27.0099 | 0 | 37.6989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 177.7052 | 16.69%
CZ 4B | 0.57126 | 0.13357 | 0.036349 | 0.051272 | 0 | 0.21924 | 0 | 0.4264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6647 | 0.7809% | CZ 4B | 18.8922 | 4.4173 | 3.6716 | 5.179 | 0 | 7.2505 | 0 | 14.1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 61.0054 | 0.7809% | CZ 4B | 5.5354 | 1.2943 | 0 | 0 | 0 | 2.1244 | 0 | 4.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.2812 | 0.7809% | CZ 4B | 0 | 0 | 0.036716 | 0.05179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088506 | 0.7809% | CZ 4B | 57.9498 | 13.5497 | 4.013 | 5.6606 | 0 | 22.2401 | 0 | 43.2553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 169.653 | 0.7809%
CZ 4C | 0.57126 | 0.13347 | 0.036991 | 0.086545 | 0 | 0.11019 | 0 | 0.34347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.5085 | 2.808% | CZ 4C | 18.8922 | 4.4139 | 3.7365 | 8.7419 | 0 | 3.6441 | 0 | 11.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 58.2808 | 2.808% | CZ 4C | 5.5354 | 1.2933 | 0 | 0 | 0 | 1.0677 | 0 | 3.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.42 | 2.808% | CZ 4C | 0 | 0 | 0.037365 | 0.087419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12478 | 2.808% | CZ 4C | 57.9498 | 13.5391 | 4.0839 | 9.5549 | 0 | 11.1778 | 0 | 34.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 154.1328 | 2.808%
CZ 5A | 0.57126 | 0.13355 | 0.03731 | 0.19802 | 0 | 0.21027 | 0 | 0.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.7668 | 22.48% | CZ 5A | 18.8922 | 4.4166 | 3.7687 | 20.002 | 0 | 6.9541 | 0 | 12.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 74.4178 | 22.48% | CZ 5A | 5.5354 | 1.294 | 0 | 0 | 0 | 2.0375 | 0 | 3.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.8395 | 22.48% | CZ 5A | 0 | 0 | 0.037687 | 0.20002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23771 | 22.48% | CZ 5A | 57.9498 | 13.5473 | 4.1192 | 21.8621 | 0 | 21.3309 | 0 | 39.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 181.3357 | 22.48%
CZ 5B | 0.57126 | 0.13343 | 0.037154 | 0.10316 | 0 | 0.16685 | 0 | 0.40442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6428 | 5.194% | CZ 5B | 18.8922 | 4.4127 | 3.753 | 10.4198 | 0 | 5.5181 | 0 | 13.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 63.8638 | 5.194% | CZ 5B | 5.5354 | 1.2929 | 0 | 0 | 0 | 1.6168 | 0 | 3.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.5594 | 5.194% | CZ 5B | 0 | 0 | 0.03753 | 0.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14173 | 5.194% | CZ 5B | 57.9498 | 13.5355 | 4.102 | 11.3888 | 0 | 16.9262 | 0 | 41.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 167.9126 | 5.194%
CZ 5C | 0.57126 | 0.13333 | 0.037318 | 0.12283 | 0 | 0.052476 | 0 | 0.3348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.4786 | 0% | CZ 5C | 18.8922 | 4.4093 | 3.7695 | 12.4074 | 0 | 1.7354 | 0 | 11.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 59.7792 | 0% | CZ 5C | 5.5354 | 1.2919 | 0 | 0 | 0 | 0.50848 | 0 | 3.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 12.7754 | 0% | CZ 5C | 0 | 0 | 0.037695 | 0.12407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16177 | 0% | CZ 5C | 57.9498 | 13.525 | 4.12 | 13.5613 | 0 | 5.3233 | 0 | 33.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 151.4268 | 0%
CZ 6A | 0.57126 | 0.13347 | 0.037987 | 0.23482 | 0 | 0.14138 | 0 | 0.37975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.7252 | 6.216% | CZ 6A | 18.8922 | 4.4139 | 3.837 | 23.7196 | 0 | 4.6757 | 0 | 12.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 75.5906 | 6.216% | CZ 6A | 5.5354 | 1.2933 | 0 | 0 | 0 | 1.37 | 0 | 3.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.0738 | 6.216% | CZ 6A | 0 | 0 | 0.03837 | 0.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27557 | 6.216% | CZ 6A | 57.9498 | 13.5391 | 4.1939 | 25.9255 | 0 | 14.3423 | 0 | 38.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 177.4582 | 6.216%
CZ 6B | 0.57126 | 0.13343 | 0.038074 | 0.158 | 0 | 0.11186 | 0 | 0.41321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6524 | 0.5978% | CZ 6B | 18.8922 | 4.4127 | 3.8459 | 15.9596 | 0 | 3.6993 | 0 | 13.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 67.9684 | 0.5978% | CZ 6B | 5.5354 | 1.2929 | 0 | 0 | 0 | 1.0839 | 0 | 4.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.1116 | 0.5978% | CZ 6B | 0 | 0 | 0.038459 | 0.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19805 | 0.5978% | CZ 6B | 57.9498 | 13.5355 | 4.2035 | 17.4438 | 0 | 11.3473 | 0 | 41.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 169.3819 | 0.5978%
CZ 7 | 0.57126 | 0.13337 | 0.039066 | 0.32114 | 0 | 0.10168 | 0 | 0.42529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8184 | 0.7115% | CZ 7 | 18.8922 | 4.4108 | 3.946 | 32.4381 | 0 | 3.3626 | 0 | 14.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 84.6078 | 0.7115% | CZ 7 | 5.5354 | 1.2924 | 0 | 0 | 0 | 0.98524 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.1294 | 0.7115% | CZ 7 | 0 | 0 | 0.03946 | 0.32438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36384 | 0.7115% | CZ 7 | 57.9498 | 13.5297 | 4.313 | 35.4549 | 0 | 10.3145 | 0 | 43.1423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 187.6885 | 0.7115%
CZ 8 | 0.57126 | 0.13254 | 0.040384 | 0.53761 | 0 | 0.062147 | 0 | 0.46474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.0352 | 0.0892% | CZ 8 | 18.8922 | 4.3832 | 4.0792 | 54.3037 | 0 | 2.0553 | 0 | 15.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 106.5762 | 0.0892% | CZ 8 | 5.5354 | 1.2843 | 0 | 0 | 0 | 0.60219 | 0 | 4.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.1205 | 0.0892% | CZ 8 | 0 | 0 | 0.040792 | 0.54304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58383 | 0.0892% | CZ 8 | 57.9498 | 13.4449 | 4.4586 | 59.354 | 0 | 6.3043 | 0 | 47.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 211.6401 | 0.0892%
Us Weighted | 0.57126 | 0.13358 | 0.036146 | 0.11232 | 0 | 0.30717 | 0 | 0.38341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.7705 | 100% | Us Weighted | 18.8922 | 4.4176 | 3.6511 | 11.3457 | 0 | 10.1586 | 0 | 12.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.6383 | 100% | Us Weighted | 5.5354 | 1.2943 | 0 | 0 | 0 | 2.9764 | 0 | 3.7152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.7168 | 100% | Us Weighted | 0 | 0 | 0.036511 | 0.11346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14997 | 100% | Us Weighted | 57.9498 | 13.5504 | 3.9907 | 12.4009 | 0 | 31.1604 | 0 | 38.8943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 180.9308 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.57126 | 0.13376 | 0.033347 | 0.0035342 | 0 | 0.88392 | 0 | 0.48537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.3377 | 1.47% | CZ 1A | 18.8922 | 4.4235 | 3.3683 | 0.35699 | 0 | 29.2323 | 0 | 16.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.8183 | 1.47% | CZ 1A | 5.5354 | 1.2961 | 0 | 0 | 0 | 8.565 | 0 | 4.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 22.295 | 1.47% | CZ 1A | 0 | 0 | 0.033683 | 0.0035699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037253 | 1.47% | CZ 1A | 57.9498 | 13.5685 | 3.6816 | 0.39019 | 0 | 89.667 | 0 | 49.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 237.4785 | 1.47%
CZ 1B | 0.57126 | 0.13373 | 0.032818 | 0.012172 | 0 | 0.80968 | 0 | 0.51959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.3058 | 0% | CZ 1B | 18.8922 | 4.4227 | 3.315 | 1.2295 | 0 | 26.7774 | 0 | 17.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.3136 | 0% | CZ 1B | 5.5354 | 1.2958 | 0 | 0 | 0 | 7.8457 | 0 | 5.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 21.9071 | 0% | CZ 1B | 0 | 0 | 0.03315 | 0.012295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045445 | 0% | CZ 1B | 57.9498 | 13.5662 | 3.6233 | 1.3438 | 0 | 82.1366 | 0 | 52.7089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 234.313 | 0%
CZ 2A | 0.57126 | 0.1337 | 0.034528 | 0.058542 | 0 | 0.66305 | 0 | 0.49921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.1869 | 14.55% | CZ 2A | 18.8922 | 4.4216 | 3.4877 | 5.9133 | 0 | 21.9281 | 0 | 16.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 78.6455 | 14.55% | CZ 2A | 5.5354 | 1.2955 | 0 | 0 | 0 | 6.4249 | 0 | 4.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 20.2884 | 14.55% | CZ 2A | 0 | 0 | 0.034877 | 0.059133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09401 | 14.55% | CZ 2A | 57.9498 | 13.5626 | 3.8121 | 6.4632 | 0 | 67.262 | 0 | 50.6408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 222.675 | 14.55%
CZ 2B | 0.57126 | 0.13366 | 0.033799 | 0.024447 | 0 | 0.70498 | 0 | 0.51718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.2119 | 3.321% | CZ 2B | 18.8922 | 4.4204 | 3.414 | 2.4693 | 0 | 23.3145 | 0 | 17.1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 77.1074 | 3.321% | CZ 2B | 5.5354 | 1.2952 | 0 | 0 | 0 | 6.8311 | 0 | 5.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 20.8685 | 3.321% | CZ 2B | 0 | 0 | 0.03414 | 0.024693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058834 | 3.321% | CZ 2B | 57.9498 | 13.5591 | 3.7315 | 2.699 | 0 | 71.5148 | 0 | 52.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 224.9025 | 3.321%
CZ 3A | 0.57126 | 0.1336 | 0.035429 | 0.11944 | 0 | 0.44853 | 0 | 0.44697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9818 | 15.64% | CZ 3A | 18.8922 | 4.4185 | 3.5787 | 12.065 | 0 | 14.8335 | 0 | 14.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.063 | 15.64% | CZ 3A | 5.5354 | 1.2946 | 0 | 0 | 0 | 4.3462 | 0 | 4.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.7027 | 15.64% | CZ 3A | 0 | 0 | 0.035787 | 0.12065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15644 | 15.64% | CZ 3A | 57.9498 | 13.5532 | 3.9115 | 13.187 | 0 | 45.5001 | 0 | 45.3423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 202.4283 | 15.64%
CZ 3B | 0.57126 | 0.13366 | 0.035106 | 0.03658 | 0 | 0.3447 | 0 | 0.45931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8072 | 8.197% | CZ 3B | 18.8922 | 4.4204 | 3.5461 | 3.695 | 0 | 11.3998 | 0 | 15.1902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 64.6368 | 8.197% | CZ 3B | 5.5354 | 1.2952 | 0 | 0 | 0 | 3.3401 | 0 | 4.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.8168 | 8.197% | CZ 3B | 0 | 0 | 0.035461 | 0.03695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072411 | 8.197% | CZ 3B | 57.9498 | 13.5591 | 3.8758 | 4.0386 | 0 | 34.9677 | 0 | 46.5942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 183.9697 | 8.197%
CZ 3C | 0.57126 | 0.1336 | 0.036406 | 0.048372 | 0 | 0.072909 | 0 | 0.38545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.4746 | 1.253% | CZ 3C | 18.8922 | 4.4185 | 3.6773 | 4.8861 | 0 | 2.4112 | 0 | 12.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 54.526 | 1.253% | CZ 3C | 5.5354 | 1.2946 | 0 | 0 | 0 | 0.70648 | 0 | 3.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.4669 | 1.253% | CZ 3C | 0 | 0 | 0.036773 | 0.048861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085634 | 1.253% | CZ 3C | 57.9498 | 13.5532 | 4.0193 | 5.3405 | 0 | 7.3961 | 0 | 39.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 150.3448 | 1.253%
CZ 4A | 0.57126 | 0.13353 | 0.036546 | 0.21105 | 0 | 0.29447 | 0 | 0.43871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9121 | 16.69% | CZ 4A | 18.8922 | 4.4162 | 3.6915 | 21.3186 | 0 | 9.7385 | 0 | 14.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 80.0588 | 16.69% | CZ 4A | 5.5354 | 1.2939 | 0 | 0 | 0 | 2.8533 | 0 | 4.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.1291 | 16.69% | CZ 4A | 0 | 0 | 0.036915 | 0.21319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2501 | 16.69% | CZ 4A | 57.9498 | 13.5461 | 4.0349 | 23.3012 | 0 | 29.8717 | 0 | 44.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 196.1919 | 16.69%
CZ 4B | 0.57126 | 0.13357 | 0.036368 | 0.085508 | 0 | 0.2394 | 0 | 0.50421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.7969 | 0.7809% | CZ 4B | 18.8922 | 4.4173 | 3.6735 | 8.6371 | 0 | 7.9174 | 0 | 16.6749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 67.7057 | 0.7809% | CZ 4B | 5.5354 | 1.2943 | 0 | 0 | 0 | 2.3198 | 0 | 4.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 16.2306 | 0.7809% | CZ 4B | 0 | 0 | 0.036735 | 0.086371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12311 | 0.7809% | CZ 4B | 57.9498 | 13.5497 | 4.0151 | 9.4404 | 0 | 24.2858 | 0 | 51.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 183.3736 | 0.7809%
CZ 4C | 0.57126 | 0.13347 | 0.037014 | 0.14848 | 0 | 0.12341 | 0 | 0.40805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6482 | 2.808% | CZ 4C | 18.8922 | 4.4139 | 3.7388 | 14.9976 | 0 | 4.0814 | 0 | 13.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 67.1117 | 2.808% | CZ 4C | 5.5354 | 1.2933 | 0 | 0 | 0 | 1.1958 | 0 | 3.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 14.1738 | 2.808% | CZ 4C | 0 | 0 | 0.037388 | 0.14998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18736 | 2.808% | CZ 4C | 57.9498 | 13.5391 | 4.0865 | 16.3924 | 0 | 12.5192 | 0 | 41.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 168.8647 | 2.808%
CZ 5A | 0.57126 | 0.13355 | 0.037325 | 0.29678 | 0 | 0.23035 | 0 | 0.48465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9805 | 22.48% | CZ 5A | 18.8922 | 4.4166 | 3.7702 | 29.978 | 0 | 7.6179 | 0 | 16.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 88.196 | 22.48% | CZ 5A | 5.5354 | 1.294 | 0 | 0 | 0 | 2.232 | 0 | 4.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.9531 | 22.48% | CZ 5A | 0 | 0 | 0.037702 | 0.29978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33748 | 22.48% | CZ 5A | 57.9498 | 13.5473 | 4.1209 | 32.766 | 0 | 23.3672 | 0 | 49.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 203.8995 | 22.48%
CZ 5B | 0.57126 | 0.13343 | 0.037173 | 0.16189 | 0 | 0.18608 | 0 | 0.51419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8306 | 5.194% | CZ 5B | 18.8922 | 4.4127 | 3.7549 | 16.3526 | 0 | 6.1539 | 0 | 17.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 74.0647 | 5.194% | CZ 5B | 5.5354 | 1.2929 | 0 | 0 | 0 | 1.8031 | 0 | 4.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.8093 | 5.194% | CZ 5B | 0 | 0 | 0.037549 | 0.16353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20108 | 5.194% | CZ 5B | 57.9498 | 13.5355 | 4.1041 | 17.8734 | 0 | 18.8765 | 0 | 52.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 187.485 | 5.194%
CZ 5C | 0.57126 | 0.13333 | 0.037344 | 0.20287 | 0 | 0.050874 | 0 | 0.39366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.6159 | 0% | CZ 5C | 18.8922 | 4.4093 | 3.7722 | 20.4922 | 0 | 1.6825 | 0 | 13.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.7603 | 0% | CZ 5C | 5.5354 | 1.2919 | 0 | 0 | 0 | 0.49296 | 0 | 3.8145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 13.3302 | 0% | CZ 5C | 0 | 0 | 0.037722 | 0.20492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24264 | 0% | CZ 5C | 57.9498 | 13.525 | 4.123 | 22.3979 | 0 | 5.1608 | 0 | 39.9342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 166.075 | 0%
CZ 6A | 0.57126 | 0.13347 | 0.038002 | 0.35241 | 0 | 0.15078 | 0 | 0.48285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9553 | 6.216% | CZ 6A | 18.8922 | 4.4139 | 3.8386 | 35.5965 | 0 | 4.9863 | 0 | 15.9684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 91.1891 | 6.216% | CZ 6A | 5.5354 | 1.2933 | 0 | 0 | 0 | 1.461 | 0 | 4.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.1638 | 6.216% | CZ 6A | 0 | 0 | 0.038386 | 0.35596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39435 | 6.216% | CZ 6A | 57.9498 | 13.5391 | 4.1955 | 38.907 | 0 | 15.2951 | 0 | 48.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 201.8523 | 6.216%
CZ 6B | 0.57126 | 0.13343 | 0.038097 | 0.24245 | 0 | 0.12263 | 0 | 0.55518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.8896 | 0.5978% | CZ 6B | 18.8922 | 4.4127 | 3.8482 | 24.4896 | 0 | 4.0557 | 0 | 18.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 81.552 | 0.5978% | CZ 6B | 5.5354 | 1.2929 | 0 | 0 | 0 | 1.1883 | 0 | 5.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.5916 | 0.5978% | CZ 6B | 0 | 0 | 0.038482 | 0.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28338 | 0.5978% | CZ 6B | 57.9498 | 13.5355 | 4.206 | 26.7672 | 0 | 12.4403 | 0 | 56.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 194.2018 | 0.5978%
CZ 7 | 0.57126 | 0.13337 | 0.039085 | 0.47547 | 0 | 0.10762 | 0 | 0.54086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.0942 | 0.7115% | CZ 7 | 18.8922 | 4.4108 | 3.948 | 48.0269 | 0 | 3.5592 | 0 | 17.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 104.2173 | 0.7115% | CZ 7 | 5.5354 | 1.2924 | 0 | 0 | 0 | 1.0428 | 0 | 5.2409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.3069 | 0.7115% | CZ 7 | 0 | 0 | 0.03948 | 0.48027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51975 | 0.7115% | CZ 7 | 57.9498 | 13.5297 | 4.3151 | 52.4934 | 0 | 10.9175 | 0 | 54.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 217.0563 | 0.7115%
CZ 8 | 0.57126 | 0.13254 | 0.040392 | 0.71941 | 0 | 0.060057 | 0 | 0.58059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 2.3308 | 0.0892% | CZ 8 | 18.8922 | 4.3832 | 4.08 | 72.6674 | 0 | 1.9862 | 0 | 19.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 128.703 | 0.0892% | CZ 8 | 5.5354 | 1.2843 | 0 | 0 | 0 | 0.58194 | 0 | 5.6258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 15.2229 | 0.0892% | CZ 8 | 0 | 0 | 0.0408 | 0.72667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76747 | 0.0892% | CZ 8 | 57.9498 | 13.4449 | 4.4594 | 79.4255 | 0 | 6.0924 | 0 | 58.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 243.253 | 0.0892%
Us Weighted | 0.57126 | 0.13358 | 0.03616 | 0.17423 | 0 | 0.35907 | 0 | 0.47131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22657 | 1.9722 | 100% | Us Weighted | 18.8922 | 4.4176 | 3.6526 | 17.5994 | 0 | 11.8749 | 0 | 15.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 79.5168 | 100% | Us Weighted | 5.5354 | 1.2943 | 0 | 0 | 0 | 3.4793 | 0 | 4.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1955 | 17.0714 | 100% | Us Weighted | 0 | 0 | 0.036526 | 0.17599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21252 | 100% | Us Weighted | 57.9498 | 13.5504 | 3.9923 | 19.2362 | 0 | 36.425 | 0 | 47.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9844 | 201.9492 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 24692 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 24692 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.15945 | 0.062541 | 0.00072963 | 0.0016151 | 0 | 0.44175 | 0 | 0.34483 | -0.031021 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.98089 | 1.47% | CZ 1A | 5.2732 | 2.0683 | 0.0737 | 0.16314 | 0 | 14.6093 | 0 | 11.4041 | -1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 32.5988 | 1.47% | CZ 1A | 1.545 | 0.60602 | 0 | 0 | 0 | 4.2805 | 0 | 3.3414 | -0.30059 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 9.482 | 1.47% | CZ 1A | 0 | 0 | 0.000737 | 0.0016314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023684 | 1.47% | CZ 1A | 16.1748 | 6.3444 | 0.080554 | 0.17831 | 0 | 44.8123 | 0 | 34.9807 | -3.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 99.5255 | 1.47%
CZ 1B | 0.14116 | 0.06253 | 0.00071443 | -0.0018621 | 0 | 0.29481 | 0 | 0.31674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.81508 | 0% | CZ 1B | 4.6684 | 2.0679 | 0.072165 | -0.18809 | 0 | 9.7496 | 0 | 10.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 26.878 | 0% | CZ 1B | 1.3678 | 0.6059 | 0 | 0 | 0 | 2.8566 | 0 | 3.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.9091 | 0% | CZ 1B | 0 | 0 | 0.00072165 | -0.0018809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0011592 | 0% | CZ 1B | 14.3199 | 6.3432 | 0.078876 | -0.20558 | 0 | 29.9059 | 0 | 32.1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 82.6742 | 0%
CZ 2A | 0.14896 | 0.062518 | 0.00076383 | 0.047761 | 0 | 0.38419 | 0 | 0.27558 | -0.024183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.89659 | 14.55% | CZ 2A | 4.9265 | 2.0676 | 0.077155 | 4.8243 | 0 | 12.7056 | 0 | 9.1138 | -0.79977 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 32.9482 | 14.55% | CZ 2A | 1.4434 | 0.60579 | 0 | 0 | 0 | 3.7227 | 0 | 2.6703 | -0.23433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 8.2176 | 14.55% | CZ 2A | 0 | 0 | 0.00077155 | 0.048243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049015 | 14.55% | CZ 2A | 15.1113 | 6.342 | 0.08433 | 5.273 | 0 | 38.9731 | 0 | 27.9556 | -2.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 91.3875 | 14.55%
CZ 2B | 0.13927 | 0.062507 | 0.00071823 | 0.010492 | 0 | 0.34001 | 0 | 0.24061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.79461 | 3.321% | CZ 2B | 4.6059 | 2.0672 | 0.072549 | 1.0598 | 0 | 11.2447 | 0 | 7.9573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 27.0405 | 3.321% | CZ 2B | 1.3495 | 0.60568 | 0 | 0 | 0 | 3.2947 | 0 | 2.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 7.591 | 3.321% | CZ 2B | 0 | 0 | 0.00072549 | 0.010598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011324 | 3.321% | CZ 2B | 14.1279 | 6.3409 | 0.079296 | 1.1584 | 0 | 34.4919 | 0 | 24.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 80.708 | 3.321%
CZ 3A | 0.14543 | 0.062402 | 0.00076003 | 0.091033 | 0 | 0.23459 | 0 | 0.23847 | -0.02315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.75054 | 15.64% | CZ 3A | 4.8097 | 2.0637 | 0.076771 | 9.1953 | 0 | 7.7581 | 0 | 7.8867 | -0.76559 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 31.0577 | 15.64% | CZ 3A | 1.4092 | 0.60467 | 0 | 0 | 0 | 2.2731 | 0 | 2.3108 | -0.22432 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.3831 | 15.64% | CZ 3A | 0 | 0 | 0.00076771 | 0.091953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09272 | 15.64% | CZ 3A | 14.7533 | 6.3303 | 0.083911 | 10.0504 | 0 | 23.797 | 0 | 24.1916 | -2.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 76.9594 | 15.64%
CZ 3B | 0.13787 | 0.062507 | 0.00074863 | 0.0097588 | 0 | 0.14007 | 0 | 0.18506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.53701 | 8.197% | CZ 3B | 4.5594 | 2.0672 | 0.07562 | 0.98574 | 0 | 4.6323 | 0 | 6.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 18.4735 | 8.197% | CZ 3B | 1.3359 | 0.60568 | 0 | 0 | 0 | 1.3573 | 0 | 1.7932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.1017 | 8.197% | CZ 3B | 0 | 0 | 0.0007562 | 0.0098574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010614 | 8.197% | CZ 3B | 13.9854 | 6.3409 | 0.082652 | 1.0774 | 0 | 14.2092 | 0 | 18.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 54.5697 | 8.197%
CZ 3C | 0.14242 | 0.062437 | 0.00077144 | 0.017743 | 0 | 0.036977 | 0 | 0.21448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.47582 | 1.253% | CZ 3C | 4.7099 | 2.0649 | 0.077923 | 1.7922 | 0 | 1.2229 | 0 | 7.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 16.9939 | 1.253% | CZ 3C | 1.38 | 0.605 | 0 | 0 | 0 | 0.3583 | 0 | 2.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 4.4312 | 1.253% | CZ 3C | 0 | 0 | 0.00077923 | 0.017922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018701 | 1.253% | CZ 3C | 14.4471 | 6.3338 | 0.08517 | 1.9589 | 0 | 3.751 | 0 | 21.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 48.4345 | 1.253%
CZ 4A | 0.14123 | 0.062344 | 0.00078284 | 0.17164 | 0 | 0.13876 | 0 | 0.23792 | -0.023788 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.72989 | 16.69% | CZ 4A | 4.6707 | 2.0618 | 0.079074 | 17.3376 | 0 | 4.589 | 0 | 7.8683 | -0.78671 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 35.8528 | 16.69% | CZ 4A | 1.3685 | 0.6041 | 0 | 0 | 0 | 1.3446 | 0 | 2.3054 | -0.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.4017 | 16.69% | CZ 4A | 0 | 0 | 0.00079074 | 0.17338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17417 | 16.69% | CZ 4A | 14.327 | 6.3244 | 0.086428 | 18.95 | 0 | 14.0761 | 0 | 24.135 | -2.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 75.5871 | 16.69%
CZ 4B | 0.13874 | 0.062437 | 0.00077904 | 0.035136 | 0 | 0.091844 | 0 | 0.23486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.5648 | 0.7809% | CZ 4B | 4.5882 | 2.0649 | 0.07869 | 3.5491 | 0 | 3.0374 | 0 | 7.7673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 21.1186 | 0.7809% | CZ 4B | 1.3443 | 0.605 | 0 | 0 | 0 | 0.88996 | 0 | 2.2758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.1248 | 0.7809% | CZ 4B | 0 | 0 | 0.0007869 | 0.035491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036278 | 0.7809% | CZ 4B | 14.0738 | 6.3338 | 0.086009 | 3.8792 | 0 | 9.317 | 0 | 23.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 57.6163 | 0.7809%
CZ 4C | 0.13769 | 0.062205 | 0.00078664 | 0.067191 | 0 | 0.049562 | 0 | 0.19983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.51826 | 2.808% | CZ 4C | 4.5536 | 2.0572 | 0.079458 | 6.787 | 0 | 1.6391 | 0 | 6.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 21.7579 | 2.808% | CZ 4C | 1.3342 | 0.60275 | 0 | 0 | 0 | 0.48025 | 0 | 1.9363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 4.3632 | 2.808% | CZ 4C | 0 | 0 | 0.00079458 | 0.06787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068664 | 2.808% | CZ 4C | 13.9678 | 6.3102 | 0.086848 | 7.4181 | 0 | 5.0277 | 0 | 20.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 53.1829 | 2.808%
CZ 5A | 0.13929 | 0.0621 | 0.00079424 | 0.2276 | 0 | 0.10609 | 0 | 0.28284 | -0.022244 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.79747 | 22.48% | CZ 5A | 4.6066 | 2.0537 | 0.080226 | 22.9899 | 0 | 3.5085 | 0 | 9.3538 | -0.73565 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 41.8902 | 22.48% | CZ 5A | 1.3497 | 0.60174 | 0 | 0 | 0 | 1.028 | 0 | 2.7406 | -0.21554 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.5142 | 22.48% | CZ 5A | 0 | 0 | 0.00080226 | 0.2299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2307 | 22.48% | CZ 5A | 14.1303 | 6.2996 | 0.087687 | 25.128 | 0 | 10.762 | 0 | 28.6916 | -2.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 82.944 | 22.48%
CZ 5B | 0.13205 | 0.062425 | 0.00078664 | 0.055825 | 0 | 0.08222 | 0 | 0.28079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.6151 | 5.194% | CZ 5B | 4.367 | 2.0645 | 0.079458 | 5.6388 | 0 | 2.7191 | 0 | 9.2862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 24.1882 | 5.194% | CZ 5B | 1.2795 | 0.60489 | 0 | 0 | 0 | 0.7967 | 0 | 2.7208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.4116 | 5.194% | CZ 5B | 0 | 0 | 0.00079458 | 0.056388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057183 | 5.194% | CZ 5B | 13.3954 | 6.3326 | 0.086848 | 6.1633 | 0 | 8.3406 | 0 | 28.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 62.9044 | 5.194%
CZ 5C | 0.12954 | 0.061973 | 0.00079804 | 0.088403 | 0 | 0.023417 | 0 | 0.22349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.52862 | 0% | CZ 5C | 4.2841 | 2.0495 | 0.08061 | 8.9296 | 0 | 0.77443 | 0 | 7.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 23.5423 | 0% | CZ 5C | 1.2552 | 0.6005 | 0 | 0 | 0 | 0.2269 | 0 | 2.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 4.2579 | 0% | CZ 5C | 0 | 0 | 0.0008061 | 0.089296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090103 | 0% | CZ 5C | 13.141 | 6.2867 | 0.088106 | 9.7601 | 0 | 2.3755 | 0 | 22.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 54.4238 | 0%
CZ 6A | 0.10608 | 0.061973 | 0.00079804 | 0.2706 | 0 | 0.072177 | 0 | 0.29087 | -0.021211 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.78228 | 6.216% | CZ 6A | 3.5081 | 2.0495 | 0.08061 | 27.3332 | 0 | 2.387 | 0 | 9.6195 | -0.70147 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 44.3095 | 6.216% | CZ 6A | 1.0279 | 0.6005 | 0 | 0 | 0 | 0.69939 | 0 | 2.8185 | -0.20553 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 4.9504 | 6.216% | CZ 6A | 0 | 0 | 0.0008061 | 0.27333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27414 | 6.216% | CZ 6A | 10.7608 | 6.2867 | 0.088106 | 29.8752 | 0 | 7.3219 | 0 | 29.5066 | -2.1517 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 81.7889 | 6.216%
CZ 6B | 0.10472 | 0.062286 | 0.00079804 | 0.19008 | 0 | 0.052824 | 0 | 0.30501 | -0.021014 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.69571 | 0.5978% | CZ 6B | 3.4632 | 2.0599 | 0.08061 | 19.2005 | 0 | 1.747 | 0 | 10.0871 | -0.69495 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 35.9763 | 0.5978% | CZ 6B | 1.0147 | 0.60354 | 0 | 0 | 0 | 0.51186 | 0 | 2.9555 | -0.20362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 4.8917 | 0.5978% | CZ 6B | 0 | 0 | 0.0008061 | 0.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19281 | 0.5978% | CZ 6B | 10.623 | 6.3185 | 0.088106 | 20.9861 | 0 | 5.3586 | 0 | 30.9411 | -2.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 72.2851 | 0.5978%
CZ 7 | 0.10409 | 0.062054 | 0.00081324 | 0.35234 | 0 | 0.054937 | 0 | 0.3457 | -0.021397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.89954 | 0.7115% | CZ 7 | 3.4425 | 2.0522 | 0.082145 | 35.5896 | 0 | 1.8168 | 0 | 11.4329 | -0.70762 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 53.7415 | 0.7115% | CZ 7 | 1.0086 | 0.60129 | 0 | 0 | 0 | 0.53233 | 0 | 3.3498 | -0.20733 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.2944 | 0.7115% | CZ 7 | 0 | 0 | 0.00082145 | 0.3559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35672 | 0.7115% | CZ 7 | 10.5594 | 6.2949 | 0.089785 | 38.8994 | 0 | 5.573 | 0 | 35.069 | -2.1705 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 94.4163 | 0.7115%
CZ 8 | 0.09917 | 0.060719 | 0.00081704 | 0.46436 | 0 | 0.029349 | 0 | 0.40777 | -0.022651 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 1.0405 | 0.0892% | CZ 8 | 3.2797 | 2.0081 | 0.082529 | 46.9053 | 0 | 0.97062 | 0 | 13.4854 | -0.74908 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 66.0156 | 0.0892% | CZ 8 | 0.96094 | 0.58835 | 0 | 0 | 0 | 0.28439 | 0 | 3.9512 | -0.21948 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 5.5751 | 0.0892% | CZ 8 | 0 | 0 | 0.00082529 | 0.46905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46988 | 0.0892% | CZ 8 | 10.0601 | 6.1595 | 0.090204 | 51.2675 | 0 | 2.9773 | 0 | 41.3651 | -2.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 109.7232 | 0.0892%
Us Weighted | 0.13922 | 0.062321 | 0.00077475 | 0.12833 | 0 | 0.18094 | 0 | 0.25636 | -0.018183 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099843 | 0.75076 | 100% | Us Weighted | 4.6042 | 2.061 | 0.078258 | 12.9628 | 0 | 5.9838 | 0 | 8.4783 | -0.60134 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 33.6001 | 100% | Us Weighted | 1.349 | 0.60388 | 0 | 0 | 0 | 1.7532 | 0 | 2.4841 | -0.17619 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096747 | 6.0237 | 100% | Us Weighted | 0 | 0 | 0.00078258 | 0.12963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13041 | 100% | Us Weighted | 14.1228 | 6.322 | 0.085536 | 14.1683 | 0 | 18.3547 | 0 | 26.0063 | -1.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10128 | 77.3164 | 100%
Building Type: | Standalone Retail |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 24692 | [17 empty] | Prototype Floor Area: | 24692 | [17 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 27.91% | 46.76% | 2.188% | 45.7% | 0% | 49.98% | 0% | 71.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.96% | 1.47% | CZ 1A | 27.91% | 46.76% | 2.188% | 45.7% | 0% | 49.98% | 0% | 71.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.84% | 1.47% | CZ 1A | 27.91% | 46.76% | 0% | 0% | 0% | 49.98% | 0% | 71.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.53% | 1.47% | CZ 1A | 0% | 0% | 2.188% | 45.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.358% | 1.47% | CZ 1A | 27.91% | 46.76% | 2.188% | 45.7% | 0% | 49.98% | 0% | 71.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.91% | 1.47%
CZ 1B | 24.71% | 46.76% | 2.177% | -15.3% | 0% | 36.41% | 0% | 60.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.35% | 0% | CZ 1B | 24.71% | 46.76% | 2.177% | -15.3% | 0% | 36.41% | 0% | 60.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 33.89% | 0% | CZ 1B | 24.71% | 46.76% | 0% | 0% | 0% | 36.41% | 0% | 60.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.1% | 0% | CZ 1B | 0% | 0% | 2.177% | -15.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.551% | 0% | CZ 1B | 24.71% | 46.76% | 2.177% | -15.3% | 0% | 36.41% | 0% | 60.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.28% | 0%
CZ 2A | 26.08% | 46.76% | 2.212% | 81.58% | 0% | 57.94% | 0% | 55.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41% | 14.55% | CZ 2A | 26.08% | 46.76% | 2.212% | 81.58% | 0% | 57.94% | 0% | 55.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.89% | 14.55% | CZ 2A | 26.08% | 46.76% | 0% | 0% | 0% | 57.94% | 0% | 55.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.5% | 14.55% | CZ 2A | 0% | 0% | 2.212% | 81.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 52.14% | 14.55% | CZ 2A | 26.08% | 46.76% | 2.212% | 81.58% | 0% | 57.94% | 0% | 55.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 41.04% | 14.55%
CZ 2B | 24.38% | 46.76% | 2.125% | 42.92% | 0% | 48.23% | 0% | 46.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.92% | 3.321% | CZ 2B | 24.38% | 46.76% | 2.125% | 42.92% | 0% | 48.23% | 0% | 46.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.07% | 3.321% | CZ 2B | 24.38% | 46.76% | 0% | 0% | 0% | 48.23% | 0% | 46.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.38% | 3.321% | CZ 2B | 0% | 0% | 2.125% | 42.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.25% | 3.321% | CZ 2B | 24.38% | 46.76% | 2.125% | 42.92% | 0% | 48.23% | 0% | 46.52% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.89% | 3.321%
CZ 3A | 25.46% | 46.71% | 2.145% | 76.21% | 0% | 52.3% | 0% | 53.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.87% | 15.64% | CZ 3A | 25.46% | 46.71% | 2.145% | 76.21% | 0% | 52.3% | 0% | 53.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.83% | 15.64% | CZ 3A | 25.46% | 46.71% | 0% | 0% | 0% | 52.3% | 0% | 53.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.06% | 15.64% | CZ 3A | 0% | 0% | 2.145% | 76.21% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 59.27% | 15.64% | CZ 3A | 25.46% | 46.71% | 2.145% | 76.21% | 0% | 52.3% | 0% | 53.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.02% | 15.64%
CZ 3B | 24.13% | 46.76% | 2.132% | 26.68% | 0% | 40.64% | 0% | 40.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 29.71% | 8.197% | CZ 3B | 24.13% | 46.76% | 2.132% | 26.68% | 0% | 40.64% | 0% | 40.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 28.58% | 8.197% | CZ 3B | 24.13% | 46.76% | 0% | 0% | 0% | 40.64% | 0% | 40.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 30.34% | 8.197% | CZ 3B | 0% | 0% | 2.132% | 26.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.66% | 8.197% | CZ 3B | 24.13% | 46.76% | 2.132% | 26.68% | 0% | 40.64% | 0% | 40.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 29.66% | 8.197%
CZ 3C | 24.93% | 46.73% | 2.119% | 36.68% | 0% | 50.72% | 0% | 55.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.27% | 1.253% | CZ 3C | 24.93% | 46.73% | 2.119% | 36.68% | 0% | 50.72% | 0% | 55.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.17% | 1.253% | CZ 3C | 24.93% | 46.73% | 0% | 0% | 0% | 50.72% | 0% | 55.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.9% | 1.253% | CZ 3C | 0% | 0% | 2.119% | 36.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.84% | 1.253% | CZ 3C | 24.93% | 46.73% | 2.119% | 36.68% | 0% | 50.72% | 0% | 55.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.22% | 1.253%
CZ 4A | 24.72% | 46.69% | 2.142% | 81.33% | 0% | 47.12% | 0% | 54.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.17% | 16.69% | CZ 4A | 24.72% | 46.69% | 2.142% | 81.33% | 0% | 47.12% | 0% | 54.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.78% | 16.69% | CZ 4A | 24.72% | 46.69% | 0% | 0% | 0% | 47.12% | 0% | 54.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 33.49% | 16.69% | CZ 4A | 0% | 0% | 2.142% | 81.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 69.64% | 16.69% | CZ 4A | 24.72% | 46.69% | 2.142% | 81.33% | 0% | 47.12% | 0% | 54.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.53% | 16.69%
CZ 4B | 24.29% | 46.74% | 2.142% | 41.09% | 0% | 38.36% | 0% | 46.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.43% | 0.7809% | CZ 4B | 24.29% | 46.74% | 2.142% | 41.09% | 0% | 38.36% | 0% | 46.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.19% | 0.7809% | CZ 4B | 24.29% | 46.74% | 0% | 0% | 0% | 38.36% | 0% | 46.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.57% | 0.7809% | CZ 4B | 0% | 0% | 2.142% | 41.09% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.47% | 0.7809% | CZ 4B | 24.29% | 46.74% | 2.142% | 41.09% | 0% | 38.36% | 0% | 46.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.42% | 0.7809%
CZ 4C | 24.1% | 46.61% | 2.125% | 45.25% | 0% | 40.16% | 0% | 48.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.44% | 2.808% | CZ 4C | 24.1% | 46.61% | 2.125% | 45.25% | 0% | 40.16% | 0% | 48.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.42% | 2.808% | CZ 4C | 24.1% | 46.61% | 0% | 0% | 0% | 40.16% | 0% | 48.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 30.78% | 2.808% | CZ 4C | 0% | 0% | 2.125% | 45.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.65% | 2.808% | CZ 4C | 24.1% | 46.61% | 2.125% | 45.25% | 0% | 40.16% | 0% | 48.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.49% | 2.808%
CZ 5A | 24.38% | 46.5% | 2.128% | 76.69% | 0% | 46.06% | 0% | 58.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.27% | 22.48% | CZ 5A | 24.38% | 46.5% | 2.128% | 76.69% | 0% | 46.06% | 0% | 58.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 47.5% | 22.48% | CZ 5A | 24.38% | 46.5% | 0% | 0% | 0% | 46.06% | 0% | 58.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 34.57% | 22.48% | CZ 5A | 0% | 0% | 2.128% | 76.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 68.36% | 22.48% | CZ 5A | 24.38% | 46.5% | 2.128% | 76.69% | 0% | 46.06% | 0% | 58.36% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.68% | 22.48%
CZ 5B | 23.12% | 46.78% | 2.116% | 34.48% | 0% | 44.19% | 0% | 54.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 33.6% | 5.194% | CZ 5B | 23.12% | 46.78% | 2.116% | 34.48% | 0% | 44.19% | 0% | 54.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.66% | 5.194% | CZ 5B | 23.12% | 46.78% | 0% | 0% | 0% | 44.19% | 0% | 54.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 34.23% | 5.194% | CZ 5B | 0% | 0% | 2.116% | 34.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.44% | 5.194% | CZ 5B | 23.12% | 46.78% | 2.116% | 34.48% | 0% | 44.19% | 0% | 54.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 33.55% | 5.194%
CZ 5C | 22.68% | 46.48% | 2.137% | 43.58% | 0% | 46.03% | 0% | 56.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.71% | 0% | CZ 5C | 22.68% | 46.48% | 2.137% | 43.58% | 0% | 46.03% | 0% | 56.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 33.75% | 0% | CZ 5C | 22.68% | 46.48% | 0% | 0% | 0% | 46.03% | 0% | 56.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.94% | 0% | CZ 5C | 0% | 0% | 2.137% | 43.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.13% | 0% | CZ 5C | 22.68% | 46.48% | 2.137% | 43.58% | 0% | 46.03% | 0% | 56.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.77% | 0%
CZ 6A | 18.57% | 46.43% | 2.1% | 76.79% | 0% | 47.87% | 0% | 60.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.01% | 6.216% | CZ 6A | 18.57% | 46.43% | 2.1% | 76.79% | 0% | 47.87% | 0% | 60.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 48.59% | 6.216% | CZ 6A | 18.57% | 46.43% | 0% | 0% | 0% | 47.87% | 0% | 60.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 32.65% | 6.216% | CZ 6A | 0% | 0% | 2.1% | 76.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 69.52% | 6.216% | CZ 6A | 18.57% | 46.43% | 2.1% | 76.79% | 0% | 47.87% | 0% | 60.24% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 40.52% | 6.216%
CZ 6B | 18.33% | 46.68% | 2.095% | 78.4% | 0% | 43.07% | 0% | 54.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.82% | 0.5978% | CZ 6B | 18.33% | 46.68% | 2.095% | 78.4% | 0% | 43.07% | 0% | 54.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.11% | 0.5978% | CZ 6B | 18.33% | 46.68% | 0% | 0% | 0% | 43.07% | 0% | 54.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 31.37% | 0.5978% | CZ 6B | 0% | 0% | 2.095% | 78.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 68.04% | 0.5978% | CZ 6B | 18.33% | 46.68% | 2.095% | 78.4% | 0% | 43.07% | 0% | 54.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 37.22% | 0.5978%
CZ 7 | 18.22% | 46.53% | 2.081% | 74.1% | 0% | 51.05% | 0% | 63.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.95% | 0.7115% | CZ 7 | 18.22% | 46.53% | 2.081% | 74.1% | 0% | 51.05% | 0% | 63.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 51.57% | 0.7115% | CZ 7 | 18.22% | 46.53% | 0% | 0% | 0% | 51.05% | 0% | 63.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 34.59% | 0.7115% | CZ 7 | 0% | 0% | 2.081% | 74.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 68.63% | 0.7115% | CZ 7 | 18.22% | 46.53% | 2.081% | 74.1% | 0% | 51.05% | 0% | 63.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 43.5% | 0.7115%
CZ 8 | 17.36% | 45.81% | 2.023% | 64.55% | 0% | 48.87% | 0% | 70.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.64% | 0.0892% | CZ 8 | 17.36% | 45.81% | 2.023% | 64.55% | 0% | 48.87% | 0% | 70.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 51.29% | 0.0892% | CZ 8 | 17.36% | 45.81% | 0% | 0% | 0% | 48.87% | 0% | 70.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 36.62% | 0.0892% | CZ 8 | 0% | 0% | 2.023% | 64.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 61.22% | 0.0892% | CZ 8 | 17.36% | 45.81% | 2.023% | 64.55% | 0% | 48.87% | 0% | 70.23% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 45.11% | 0.0892%
Us Weighted | 24.37% | 46.66% | 2.143% | 73.65% | 0% | 50.39% | 0% | 54.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.07% | 100% | Us Weighted | 24.37% | 46.66% | 2.143% | 73.65% | 0% | 50.39% | 0% | 54.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 42.26% | 100% | Us Weighted | 24.37% | 46.66% | 0% | 0% | 0% | 50.39% | 0% | 54.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 35.29% | 100% | Us Weighted | 0% | 0% | 2.143% | 73.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 61.36% | 100% | Us Weighted | 24.37% | 46.66% | 2.143% | 73.65% | 0% | 50.39% | 0% | 54.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 38.29% | 100%

## StripMall
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Strip Mall |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Strip Mall | [14 empty] | Prototype Floor Area: | 22500 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.6179 | 0.090451 | 0.079876 | 0.10856 | 0 | 0.20011 | 0 | 0.18267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4428 |  | STD2013 | 20.4348 | 2.9913 | 2.6416 | 10.9653 | 0 | 6.6179 | 0 | 6.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.0919 |  | STD2013 | 5.9874 | 0.87646 | 0.77398 | 0 | 0 | 1.939 | 0 | 1.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.929 |  | STD2013 | 0 | 0 | 0 | 0.10965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10965 |  | STD2013 | 62.6816 | 9.1756 | 8.1028 | 11.9851 | 0 | 20.2997 | 0 | 18.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 147.3385
STD2010 | 0.69371 | 0.090451 | 0.079914 | 0.1062 | 0 | 0.23519 | 0 | 0.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.6083 |  | STD2010 | 22.9419 | 2.9913 | 2.6429 | 10.7269 | 0 | 7.7781 | 0 | 7.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.4048 |  | STD2010 | 6.7219 | 0.87646 | 0.77435 | 0 | 0 | 2.279 | 0 | 2.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.5555 |  | STD2010 | 0 | 0 | 0 | 0.10727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10727 |  | STD2010 | 70.3717 | 9.1756 | 8.1067 | 11.7245 | 0 | 23.8584 | 0 | 24.3061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 164.1059
STD2007 | 0.784 | 0.18327 | 0.087005 | 0.11092 | 0 | 0.34256 | 0 | 0.30227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.974 |  | STD2007 | 25.928 | 6.0611 | 2.8774 | 11.2041 | 0 | 11.3289 | 0 | 9.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.8197 |  | STD2007 | 7.5968 | 1.7759 | 0.84306 | 0 | 0 | 3.3193 | 0 | 2.9289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.0532 |  | STD2007 | 0 | 0 | 0 | 0.11204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11204 |  | STD2007 | 79.5314 | 18.5919 | 8.826 | 12.2461 | 0 | 34.7502 | 0 | 30.6631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 201.2452
STD2004 | 0.80528 | 0.18327 | 0.087108 | 0.17871 | 0 | 0.39462 | 0 | 0.34947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1625 |  | STD2004 | 26.6317 | 6.0611 | 2.8808 | 18.0517 | 0 | 13.0507 | 0 | 11.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 83.6572 |  | STD2004 | 7.803 | 1.7759 | 0.84406 | 0 | 0 | 3.8238 | 0 | 3.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2223 |  | STD2004 | 0 | 0 | 0 | 0.18052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18052 |  | STD2004 | 81.6898 | 18.5919 | 8.8365 | 19.7305 | 0 | 40.0315 | 0 | 35.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 220.9682
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0.021277 | 0 | 0.00010334 | 0.067791 | 0 | 0.052062 | 0 | 0.047203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18844 |  | 2004-2007 | 0.70366 | 0 | 0.0034175 | 6.8476 | 0 | 1.7218 | 0 | 1.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8375 |  | 2004-2007 | 0.20617 | 0 | 0.0010013 | 0 | 0 | 0.50448 | 0 | 0.45739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.169 |  | 2004-2007 | 0 | 0 | 0 | 0.068476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068476 |  | 2004-2007 | 2.1584 | 0 | 0.010483 | 7.4844 | 0 | 5.2813 | 0 | 4.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7231
2007-2010 | 0.090294 | 0.092823 | 0.0070908 | 0.0047244 | 0 | 0.10737 | 0 | 0.062666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.36569 |  | 2007-2010 | 2.9861 | 3.0698 | 0.2345 | 0.47721 | 0 | 3.5508 | 0 | 2.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 12.4149 |  | 2007-2010 | 0.87493 | 0.89944 | 0.068709 | 0 | 0 | 1.0404 | 0 | 0.60723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 3.4977 |  | 2007-2010 | 0 | 0 | 0 | 0.0047721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047721 |  | 2007-2010 | 9.1596 | 9.4162 | 0.71931 | 0.5216 | 0 | 10.8917 | 0 | 6.3571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 37.1393
2010-2013 | 0.075807 | 0 | 3.8384e-05 | -0.0023602 | 0 | 0.035081 | 0 | 0.056931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1655 |  | 2010-2013 | 2.5071 | 0 | 0.0012694 | -0.2384 | 0 | 1.1602 | 0 | 1.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3129 |  | 2010-2013 | 0.73456 | 0 | 0.00037194 | 0 | 0 | 0.33993 | 0 | 0.55165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6265 |  | 2010-2013 | 0 | 0 | 0 | -0.002384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.002384 |  | 2010-2013 | 7.6901 | 0 | 0.0038938 | -0.26057 | 0 | 3.5587 | 0 | 5.7752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7674
2004-2013 | 0.18738 | 0.092823 | 0.0072325 | 0.070155 | 0 | 0.19451 | 0 | 0.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.71963 |  | 2004-2013 | 6.1969 | 3.0698 | 0.23919 | 7.0864 | 0 | 6.4328 | 0 | 5.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 28.5653 |  | 2004-2013 | 1.8157 | 0.89944 | 0.070082 | 0 | 0 | 1.8848 | 0 | 1.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.2933 |  | 2004-2013 | 0 | 0 | 0 | 0.070864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070864 |  | 2004-2013 | 19.0082 | 9.4162 | 0.73369 | 7.7454 | 0 | 19.7318 | 0 | 16.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 73.6297
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 2.642% | 0% | 0.1186% | 37.93% |  | 13.19% |  | 13.51% | [7 empty] | 0% | 8.714% |  | 2004-2007 | 2.642% | 0% | 0.1186% | 37.93% |  | 13.19% |  | 13.51% | [7 empty] | 0% | 12.95% |  | 2004-2007 | 2.642% | 0% | 0.1186% |  |  | 13.19% |  | 13.51% | [7 empty] | 0% | 6.082% |  | 2004-2007 |  |  |  | 37.93% | [12 empty] | 37.93% |  | 2004-2007 | 2.642% | 0% | 0.1186% | 37.93% |  | 13.19% |  | 13.51% | [7 empty] | 0% | 8.926%
2007-2010 | 11.52% | 50.65% | 8.15% | 4.259% |  | 31.34% |  | 20.73% | [7 empty] | 0.4428% | 18.53% |  | 2007-2010 | 11.52% | 50.65% | 8.15% | 4.259% |  | 31.34% |  | 20.73% | [7 empty] | 0.4428% | 17.05% |  | 2007-2010 | 11.52% | 50.65% | 8.15% |  |  | 31.34% |  | 20.73% | [7 empty] | 0.4428% | 19.37% |  | 2007-2010 |  |  |  | 4.259% | [12 empty] | 4.259% |  | 2007-2010 | 11.52% | 50.65% | 8.15% | 4.259% |  | 31.34% |  | 20.73% | [7 empty] | 0.4428% | 18.45%
2010-2013 | 10.93% | 0% | 0.04803% | -2.222% |  | 14.92% |  | 23.76% | [7 empty] | 0% | 10.29% |  | 2010-2013 | 10.93% | 0% | 0.04803% | -2.222% |  | 14.92% |  | 23.76% | [7 empty] | 0% | 8.795% |  | 2010-2013 | 10.93% | 0% | 0.04803% |  |  | 14.92% |  | 23.76% | [7 empty] | 0% | 11.17% |  | 2010-2013 |  |  |  | -2.222% | [12 empty] | -2.222% |  | 2010-2013 | 10.93% | 0% | 0.04803% | -2.222% |  | 14.92% |  | 23.76% | [7 empty] | 0% | 10.22%
2004-2013 | 23.27% | 50.65% | 8.303% | 39.26% |  | 49.29% |  | 47.73% | [7 empty] | 0.4428% | 33.28% |  | 2004-2013 | 23.27% | 50.65% | 8.303% | 39.26% |  | 49.29% |  | 47.73% | [7 empty] | 0.4428% | 34.15% |  | 2004-2013 | 23.27% | 50.65% | 8.303% |  |  | 49.29% |  | 47.73% | [7 empty] | 0.4428% | 32.74% |  | 2004-2013 |  |  |  | 39.26% | [12 empty] | 39.26% |  | 2004-2013 | 23.27% | 50.65% | 8.303% | 39.26% |  | 49.29% |  | 47.73% | [7 empty] | 0.4428% | 33.32%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.6179 | 0.090434 | 0.075158 | 0.0026691 | 0 | 0.43492 | 0 | 0.11671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5011 | 2.424% | CZ 1A | 20.4348 | 2.9908 | 2.4856 | 0.2696 | 0 | 14.3833 | 0 | 3.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.8234 | 2.424% | CZ 1A | 5.9874 | 0.87629 | 0.72826 | 0 | 0 | 4.2143 | 0 | 1.1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.5191 | 2.424% | CZ 1A | 0 | 0 | 0 | 0.002696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002696 | 2.424% | CZ 1A | 62.6816 | 9.1739 | 7.6242 | 0.29467 | 0 | 44.1193 | 0 | 11.8389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 152.2954 | 2.424%
CZ 1B | 0.6179 | 0.090421 | 0.074329 | 0.0078445 | 0 | 0.47194 | 0 | 0.18542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.6111 | 0% | CZ 1B | 20.4348 | 2.9904 | 2.4582 | 0.79238 | 0 | 15.6078 | 0 | 6.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 53.8152 | 0% | CZ 1B | 5.9874 | 0.87616 | 0.72024 | 0 | 0 | 4.573 | 0 | 1.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.5355 | 0% | CZ 1B | 0 | 0 | 0 | 0.0079238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079238 | 0% | CZ 1B | 62.6816 | 9.1726 | 7.5402 | 0.86607 | 0 | 47.8752 | 0 | 18.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 163.5076 | 0%
CZ 2A | 0.6179 | 0.090383 | 0.0774 | 0.036462 | 0 | 0.3283 | 0 | 0.16337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4771 | 17.47% | CZ 2A | 20.4348 | 2.9891 | 2.5597 | 3.683 | 0 | 10.8575 | 0 | 5.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.3268 | 17.47% | CZ 2A | 5.9874 | 0.87579 | 0.74999 | 0 | 0 | 3.1812 | 0 | 1.5831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.9595 | 17.47% | CZ 2A | 0 | 0 | 0 | 0.03683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03683 | 17.47% | CZ 2A | 62.6816 | 9.1687 | 7.8517 | 4.0255 | 0 | 33.304 | 0 | 16.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 150.1676 | 17.47%
CZ 2B | 0.6179 | 0.090357 | 0.0761 | 0.014521 | 0 | 0.39062 | 0 | 0.21903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5718 | 4.471% | CZ 2B | 20.4348 | 2.9882 | 2.5167 | 1.4668 | 0 | 12.9183 | 0 | 7.2435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.9681 | 4.471% | CZ 2B | 5.9874 | 0.87555 | 0.7374 | 0 | 0 | 3.785 | 0 | 2.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 15.0897 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.014668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014668 | 4.471% | CZ 2B | 62.6816 | 9.1661 | 7.7198 | 1.6032 | 0 | 39.6255 | 0 | 22.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 159.5777 | 4.471%
CZ 3A | 0.6179 | 0.090408 | 0.07912 | 0.094547 | 0 | 0.21985 | 0 | 0.15769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4228 | 18% | CZ 3A | 20.4348 | 2.9899 | 2.6166 | 9.5502 | 0 | 7.2709 | 0 | 5.2151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 53.4772 | 18% | CZ 3A | 5.9874 | 0.87604 | 0.76666 | 0 | 0 | 2.1304 | 0 | 1.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8705 | 18% | CZ 3A | 0 | 0 | 0 | 0.095502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095502 | 18% | CZ 3A | 62.6816 | 9.1713 | 8.0262 | 10.4384 | 0 | 22.3026 | 0 | 15.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 145.1796 | 18%
CZ 3B | 0.6179 | 0.090357 | 0.078521 | 0.029848 | 0 | 0.1851 | 0 | 0.22663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.3916 | 11.03% | CZ 3B | 20.4348 | 2.9882 | 2.5968 | 3.0149 | 0 | 6.1214 | 0 | 7.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.0509 | 11.03% | CZ 3B | 5.9874 | 0.87555 | 0.76086 | 0 | 0 | 1.7936 | 0 | 2.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.1954 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.030149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030149 | 11.03% | CZ 3B | 62.6816 | 9.1661 | 7.9654 | 3.2953 | 0 | 18.7768 | 0 | 22.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 141.4383 | 11.03%
CZ 3C | 0.6179 | 0.09037 | 0.081006 | 0.038589 | 0 | 0.02794 | 0 | 0.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.1688 | 1.823% | CZ 3C | 20.4348 | 2.9887 | 2.679 | 3.8978 | 0 | 0.92403 | 0 | 4.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 41.2749 | 1.823% | CZ 3C | 5.9874 | 0.87567 | 0.78493 | 0 | 0 | 0.27074 | 0 | 1.4506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 10.9514 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.038978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038978 | 1.823% | CZ 3C | 62.6816 | 9.1674 | 8.2174 | 4.2603 | 0 | 2.8344 | 0 | 15.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 118.9104 | 1.823%
CZ 4A | 0.6179 | 0.090396 | 0.081159 | 0.13414 | 0 | 0.14702 | 0 | 0.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4199 | 17.78% | CZ 4A | 20.4348 | 2.9895 | 2.684 | 13.5496 | 0 | 4.862 | 0 | 6.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 56.071 | 17.78% | CZ 4A | 5.9874 | 0.87592 | 0.78641 | 0 | 0 | 1.4246 | 0 | 1.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.4587 | 17.78% | CZ 4A | 0 | 0 | 0 | 0.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1355 | 17.78% | CZ 4A | 62.6816 | 9.17 | 8.233 | 14.8097 | 0 | 14.9137 | 0 | 18.8686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 145.2393 | 17.78%
CZ 4B | 0.6179 | 0.090332 | 0.080789 | 0.047205 | 0 | 0.13427 | 0 | 0.22281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.3566 | 0.3973% | CZ 4B | 20.4348 | 2.9874 | 2.6718 | 4.7682 | 0 | 4.4407 | 0 | 7.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.0711 | 0.3973% | CZ 4B | 5.9874 | 0.8753 | 0.78283 | 0 | 0 | 1.3011 | 0 | 2.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.6877 | 0.3973% | CZ 4B | 0 | 0 | 0 | 0.047682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047682 | 0.3973% | CZ 4B | 62.6816 | 9.1635 | 8.1955 | 5.2116 | 0 | 13.6212 | 0 | 22.6025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 138.0387 | 0.3973%
CZ 4C | 0.6179 | 0.090485 | 0.08205 | 0.11083 | 0 | 0.07252 | 0 | 0.18912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.3262 | 1.882% | CZ 4C | 20.4348 | 2.9925 | 2.7135 | 11.1952 | 0 | 2.3983 | 0 | 6.2546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.3886 | 1.882% | CZ 4C | 5.9874 | 0.87678 | 0.79505 | 0 | 0 | 0.70271 | 0 | 1.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.7766 | 1.882% | CZ 4C | 0 | 0 | 0 | 0.11195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11195 | 1.882% | CZ 4C | 62.6816 | 9.179 | 8.3234 | 12.2363 | 0 | 7.3567 | 0 | 19.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 135.5252 | 1.882%
CZ 5A | 0.6179 | 0.090714 | 0.082611 | 0.22795 | 0 | 0.11319 | 0 | 0.19172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4874 | 18.04% | CZ 5A | 20.4348 | 3 | 2.7321 | 23.0256 | 0 | 3.7433 | 0 | 6.3405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 64.6761 | 18.04% | CZ 5A | 5.9874 | 0.879 | 0.80049 | 0 | 0 | 1.0968 | 0 | 1.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2035 | 18.04% | CZ 5A | 0 | 0 | 0 | 0.23026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23026 | 18.04% | CZ 5A | 62.6816 | 9.2023 | 8.3803 | 25.167 | 0 | 11.4822 | 0 | 19.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 152.9251 | 18.04%
CZ 5B | 0.6179 | 0.090166 | 0.082305 | 0.12885 | 0 | 0.10024 | 0 | 0.21361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.3963 | 3.55% | CZ 5B | 20.4348 | 2.9819 | 2.7219 | 13.015 | 0 | 3.3152 | 0 | 7.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.933 | 3.55% | CZ 5B | 5.9874 | 0.8737 | 0.79752 | 0 | 0 | 0.97135 | 0 | 2.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2819 | 3.55% | CZ 5B | 0 | 0 | 0 | 0.13015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13015 | 3.55% | CZ 5B | 62.6816 | 9.1467 | 8.3493 | 14.2254 | 0 | 10.1691 | 0 | 21.6693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 142.8042 | 3.55%
CZ 5C | 0.6179 | 0.090587 | 0.0827 | 0.16428 | 0 | 0.028641 | 0 | 0.15807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.3055 | 0% | CZ 5C | 20.4348 | 2.9958 | 2.735 | 16.594 | 0 | 0.9472 | 0 | 5.2277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.3342 | 0% | CZ 5C | 5.9874 | 0.87777 | 0.80135 | 0 | 0 | 0.27753 | 0 | 1.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.0578 | 0% | CZ 5C | 0 | 0 | 0 | 0.16594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16594 | 0% | CZ 5C | 62.6816 | 9.1894 | 8.3893 | 18.1372 | 0 | 2.9054 | 0 | 16.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 133.9013 | 0%
CZ 6A | 0.6179 | 0.090765 | 0.08386 | 0.27759 | 0 | 0.072762 | 0 | 0.17922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4854 | 2.692% | CZ 6A | 20.4348 | 3.0017 | 2.7734 | 28.039 | 0 | 2.4064 | 0 | 5.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 67.9821 | 2.692% | CZ 6A | 5.9874 | 0.8795 | 0.81259 | 0 | 0 | 0.70506 | 0 | 1.7367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.7032 | 2.692% | CZ 6A | 0 | 0 | 0 | 0.28039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28039 | 2.692% | CZ 6A | 62.6816 | 9.2075 | 8.507 | 30.6466 | 0 | 7.3812 | 0 | 18.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 153.1677 | 2.692%
CZ 6B | 0.6179 | 0.090332 | 0.084025 | 0.20631 | 0 | 0.063551 | 0 | 0.20636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4317 | 0.2819% | CZ 6B | 20.4348 | 2.9874 | 2.7788 | 20.8389 | 0 | 2.1017 | 0 | 6.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 61.366 | 0.2819% | CZ 6B | 5.9874 | 0.8753 | 0.81419 | 0 | 0 | 0.6158 | 0 | 1.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.8743 | 0.2819% | CZ 6B | 0 | 0 | 0 | 0.20839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20839 | 0.2819% | CZ 6B | 62.6816 | 9.1635 | 8.5238 | 22.7769 | 0 | 6.4468 | 0 | 20.9339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 147.0894 | 0.2819%
CZ 7 | 0.6179 | 0.090548 | 0.085834 | 0.3617 | 0 | 0.047548 | 0 | 0.18712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5539 | 0.121% | CZ 7 | 20.4348 | 2.9946 | 2.8387 | 36.5352 | 0 | 1.5725 | 0 | 6.1884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 75.9638 | 0.121% | CZ 7 | 5.9874 | 0.8774 | 0.83172 | 0 | 0 | 0.46074 | 0 | 1.8132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.5525 | 0.121% | CZ 7 | 0 | 0 | 0 | 0.36535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36535 | 0.121% | CZ 7 | 62.6816 | 9.1855 | 8.7073 | 39.933 | 0 | 4.8235 | 0 | 18.9823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 160.876 | 0.121%
CZ 8 | 0.6179 | 0.091122 | 0.08823 | 0.57701 | 0 | 0.022118 | 0 | 0.22903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.7887 | 0.02367% | CZ 8 | 20.4348 | 3.0135 | 2.9179 | 58.2836 | 0 | 0.73147 | 0 | 7.5743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 98.3552 | 0.02367% | CZ 8 | 5.9874 | 0.88295 | 0.85493 | 0 | 0 | 0.21432 | 0 | 2.2192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 11.7409 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.58284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58284 | 0.02367% | CZ 8 | 62.6816 | 9.2437 | 8.9503 | 63.704 | 0 | 2.2437 | 0 | 23.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 186.6192 | 0.02367%
Us Weighted | 0.6179 | 0.090451 | 0.079876 | 0.10856 | 0 | 0.20011 | 0 | 0.18267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4428 | 100% | Us Weighted | 20.4348 | 2.9913 | 2.6416 | 10.9653 | 0 | 6.6179 | 0 | 6.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.0919 | 100% | Us Weighted | 5.9874 | 0.87646 | 0.77398 | 0 | 0 | 1.939 | 0 | 1.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.929 | 100% | Us Weighted | 0 | 0 | 0 | 0.10965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10965 | 100% | Us Weighted | 62.6816 | 9.1756 | 8.1028 | 11.9851 | 0 | 20.2997 | 0 | 18.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 147.3385 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.69371 | 0.090434 | 0.075221 | 0.0019517 | 0 | 0.54696 | 0 | 0.25177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.8233 | 2.424% | CZ 1A | 22.9419 | 2.9908 | 2.4877 | 0.19715 | 0 | 18.0887 | 0 | 8.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.4323 | 2.424% | CZ 1A | 6.7219 | 0.87629 | 0.72888 | 0 | 0 | 5.3 | 0 | 2.4396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 17.6487 | 2.424% | CZ 1A | 0 | 0 | 0 | 0.0019715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019715 | 2.424% | CZ 1A | 70.3717 | 9.1739 | 7.6307 | 0.21548 | 0 | 55.4852 | 0 | 25.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 184.98 | 2.424%
CZ 1B | 0.69371 | 0.090421 | 0.074304 | 0.0047668 | 0 | 0.543 | 0 | 0.33309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.9026 | 0% | CZ 1B | 22.9419 | 2.9904 | 2.4573 | 0.48149 | 0 | 17.9577 | 0 | 11.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 63.2443 | 0% | CZ 1B | 6.7219 | 0.87616 | 0.71999 | 0 | 0 | 5.2616 | 0 | 3.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 18.3893 | 0% | CZ 1B | 0 | 0 | 0 | 0.0048149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048149 | 0% | CZ 1B | 70.3717 | 9.1726 | 7.5376 | 0.52627 | 0 | 55.0832 | 0 | 33.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 193.0443 | 0%
CZ 2A | 0.69371 | 0.090383 | 0.077451 | 0.029677 | 0 | 0.39159 | 0 | 0.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.7116 | 17.47% | CZ 2A | 22.9419 | 2.9891 | 2.5614 | 2.9976 | 0 | 12.9503 | 0 | 8.7806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.6206 | 17.47% | CZ 2A | 6.7219 | 0.87579 | 0.75049 | 0 | 0 | 3.7944 | 0 | 2.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 16.2974 | 17.47% | CZ 2A | 0 | 0 | 0 | 0.029976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029976 | 17.47% | CZ 2A | 70.3717 | 9.1687 | 7.8568 | 3.2764 | 0 | 39.7237 | 0 | 26.9335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 173.8937 | 17.47%
CZ 2B | 0.69371 | 0.090357 | 0.076062 | 0.010101 | 0 | 0.44138 | 0 | 0.31916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.794 | 4.471% | CZ 2B | 22.9419 | 2.9882 | 2.5155 | 1.0203 | 0 | 14.597 | 0 | 10.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.0174 | 4.471% | CZ 2B | 6.7219 | 0.87555 | 0.73703 | 0 | 0 | 4.2769 | 0 | 3.0926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 17.286 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.010203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010203 | 4.471% | CZ 2B | 70.3717 | 9.1661 | 7.716 | 1.1152 | 0 | 44.7746 | 0 | 32.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 182.0825 | 4.471%
CZ 3A | 0.69371 | 0.090408 | 0.079158 | 0.083533 | 0 | 0.25879 | 0 | 0.22259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5915 | 18% | CZ 3A | 22.9419 | 2.9899 | 2.6179 | 8.4377 | 0 | 8.5585 | 0 | 7.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.3071 | 18% | CZ 3A | 6.7219 | 0.87604 | 0.76703 | 0 | 0 | 2.5076 | 0 | 2.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.6116 | 18% | CZ 3A | 0 | 0 | 0 | 0.084377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084377 | 18% | CZ 3A | 70.3717 | 9.1713 | 8.03 | 9.2224 | 0 | 26.2524 | 0 | 22.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 162.1912 | 18%
CZ 3B | 0.69371 | 0.090357 | 0.078496 | 0.019326 | 0 | 0.2039 | 0 | 0.25876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5078 | 11.03% | CZ 3B | 22.9419 | 2.9882 | 2.596 | 1.9521 | 0 | 6.7434 | 0 | 8.5577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.1789 | 11.03% | CZ 3B | 6.7219 | 0.87555 | 0.76061 | 0 | 0 | 1.9758 | 0 | 2.5074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.4233 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.019521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019521 | 11.03% | CZ 3B | 70.3717 | 9.1661 | 7.9628 | 2.1336 | 0 | 20.6845 | 0 | 26.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 153.1314 | 11.03%
CZ 3C | 0.69371 | 0.09037 | 0.080967 | 0.02966 | 0 | 0.038452 | 0 | 0.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.2966 | 1.823% | CZ 3C | 22.9419 | 2.9887 | 2.6777 | 2.9959 | 0 | 1.2716 | 0 | 6.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 44.8962 | 1.823% | CZ 3C | 6.7219 | 0.87567 | 0.78456 | 0 | 0 | 0.37259 | 0 | 1.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.2767 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.029959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029959 | 1.823% | CZ 3C | 70.3717 | 9.1674 | 8.2136 | 3.2746 | 0 | 3.9006 | 0 | 20.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 131.7991 | 1.823%
CZ 4A | 0.69371 | 0.090396 | 0.081209 | 0.13602 | 0 | 0.17506 | 0 | 0.22104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5607 | 17.78% | CZ 4A | 22.9419 | 2.9895 | 2.6857 | 13.7396 | 0 | 5.7894 | 0 | 7.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.8558 | 17.78% | CZ 4A | 6.7219 | 0.87592 | 0.78691 | 0 | 0 | 1.6963 | 0 | 2.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.8049 | 17.78% | CZ 4A | 0 | 0 | 0 | 0.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1374 | 17.78% | CZ 4A | 70.3717 | 9.17 | 8.2381 | 15.0173 | 0 | 17.7584 | 0 | 22.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 159.5412 | 17.78%
CZ 4B | 0.69371 | 0.090332 | 0.080853 | 0.04685 | 0 | 0.15477 | 0 | 0.27482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5046 | 0.3973% | CZ 4B | 22.9419 | 2.9874 | 2.6739 | 4.7323 | 0 | 5.1186 | 0 | 9.0886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.9424 | 0.3973% | CZ 4B | 6.7219 | 0.8753 | 0.78345 | 0 | 0 | 1.4997 | 0 | 2.6629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.1254 | 0.3973% | CZ 4B | 0 | 0 | 0 | 0.047323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047323 | 0.3973% | CZ 4B | 70.3717 | 9.1635 | 8.2019 | 5.1725 | 0 | 15.7008 | 0 | 27.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 153.0516 | 0.3973%
CZ 4C | 0.69371 | 0.090485 | 0.082089 | 0.10359 | 0 | 0.089555 | 0 | 0.25171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4744 | 1.882% | CZ 4C | 22.9419 | 2.9925 | 2.7148 | 10.4639 | 0 | 2.9617 | 0 | 8.3243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.7987 | 1.882% | CZ 4C | 6.7219 | 0.87678 | 0.79542 | 0 | 0 | 0.86777 | 0 | 2.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.283 | 1.882% | CZ 4C | 0 | 0 | 0 | 0.10464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10464 | 1.882% | CZ 4C | 70.3717 | 9.179 | 8.3273 | 11.437 | 0 | 9.0847 | 0 | 25.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 150.4964 | 1.882%
CZ 5A | 0.69371 | 0.090714 | 0.082675 | 0.23825 | 0 | 0.13306 | 0 | 0.21672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.6184 | 18.04% | CZ 5A | 22.9419 | 3 | 2.7342 | 24.0661 | 0 | 4.4006 | 0 | 7.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 69.7097 | 18.04% | CZ 5A | 6.7219 | 0.879 | 0.8011 | 0 | 0 | 1.2894 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.3735 | 18.04% | CZ 5A | 0 | 0 | 0 | 0.24066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24066 | 18.04% | CZ 5A | 70.3717 | 9.2023 | 8.3868 | 26.3043 | 0 | 13.4984 | 0 | 21.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 166.311 | 18.04%
CZ 5B | 0.69371 | 0.090166 | 0.082382 | 0.13167 | 0 | 0.11347 | 0 | 0.26401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5387 | 3.55% | CZ 5B | 22.9419 | 2.9819 | 2.7245 | 13.3002 | 0 | 3.7526 | 0 | 8.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 59.832 | 3.55% | CZ 5B | 6.7219 | 0.8737 | 0.79826 | 0 | 0 | 1.0995 | 0 | 2.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.6337 | 3.55% | CZ 5B | 0 | 0 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.133 | 3.55% | CZ 5B | 70.3717 | 9.1467 | 8.357 | 14.5371 | 0 | 11.5106 | 0 | 26.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 157.2684 | 3.55%
CZ 5C | 0.69371 | 0.090587 | 0.082738 | 0.16255 | 0 | 0.037598 | 0 | 0.20829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.4387 | 0% | CZ 5C | 22.9419 | 2.9958 | 2.7363 | 16.4187 | 0 | 1.2434 | 0 | 6.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.6241 | 0% | CZ 5C | 6.7219 | 0.87777 | 0.80172 | 0 | 0 | 0.36432 | 0 | 2.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.3661 | 0% | CZ 5C | 0 | 0 | 0 | 0.16419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16419 | 0% | CZ 5C | 70.3717 | 9.1894 | 8.3932 | 17.9457 | 0 | 3.814 | 0 | 21.1291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 147.4059 | 0%
CZ 6A | 0.69371 | 0.090765 | 0.083923 | 0.28343 | 0 | 0.082726 | 0 | 0.21635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.6142 | 2.692% | CZ 6A | 22.9419 | 3.0017 | 2.7755 | 28.6291 | 0 | 2.7359 | 0 | 7.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 72.6387 | 2.692% | CZ 6A | 6.7219 | 0.8795 | 0.8132 | 0 | 0 | 0.8016 | 0 | 2.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8947 | 2.692% | CZ 6A | 0 | 0 | 0 | 0.28629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28629 | 2.692% | CZ 6A | 70.3717 | 9.2075 | 8.5134 | 31.2916 | 0 | 8.3919 | 0 | 21.9472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 166.2862 | 2.692%
CZ 6B | 0.69371 | 0.090332 | 0.084089 | 0.20383 | 0 | 0.077808 | 0 | 0.28147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.5945 | 0.2819% | CZ 6B | 22.9419 | 2.9874 | 2.7809 | 20.5887 | 0 | 2.5732 | 0 | 9.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 66.5803 | 0.2819% | CZ 6B | 6.7219 | 0.8753 | 0.81481 | 0 | 0 | 0.75394 | 0 | 2.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 13.4754 | 0.2819% | CZ 6B | 0 | 0 | 0 | 0.20589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20589 | 0.2819% | CZ 6B | 70.3717 | 9.1635 | 8.5302 | 22.5034 | 0 | 7.893 | 0 | 28.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 163.5778 | 0.2819%
CZ 7 | 0.69371 | 0.090548 | 0.085924 | 0.38453 | 0 | 0.054696 | 0 | 0.22731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.7 | 0.121% | CZ 7 | 22.9419 | 2.9946 | 2.8416 | 38.8415 | 0 | 1.8089 | 0 | 7.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 82.3455 | 0.121% | CZ 7 | 6.7219 | 0.8774 | 0.83259 | 0 | 0 | 0.53 | 0 | 2.2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.7466 | 0.121% | CZ 7 | 0 | 0 | 0 | 0.38842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38842 | 0.121% | CZ 7 | 70.3717 | 9.1855 | 8.7163 | 42.4538 | 0 | 5.5485 | 0 | 23.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 175.8975 | 0.121%
CZ 8 | 0.69371 | 0.091122 | 0.088344 | 0.63529 | 0 | 0.022003 | 0 | 0.26842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.9622 | 0.02367% | CZ 8 | 22.9419 | 3.0135 | 2.9217 | 64.171 | 0 | 0.72768 | 0 | 8.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 108.0525 | 0.02367% | CZ 8 | 6.7219 | 0.88295 | 0.85604 | 0 | 0 | 0.21321 | 0 | 2.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 12.8572 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.64171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64171 | 0.02367% | CZ 8 | 70.3717 | 9.2437 | 8.9619 | 70.1389 | 0 | 2.2321 | 0 | 27.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 204.7406 | 0.02367%
Us Weighted | 0.69371 | 0.090451 | 0.079914 | 0.1062 | 0 | 0.23519 | 0 | 0.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16327 | 1.6083 | 100% | Us Weighted | 22.9419 | 2.9913 | 2.6429 | 10.7269 | 0 | 7.7781 | 0 | 7.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.4048 | 100% | Us Weighted | 6.7219 | 0.87646 | 0.77435 | 0 | 0 | 2.279 | 0 | 2.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 14.5555 | 100% | Us Weighted | 0 | 0 | 0 | 0.10727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10727 | 100% | Us Weighted | 70.3717 | 9.1756 | 8.1067 | 11.7245 | 0 | 23.8584 | 0 | 24.3061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5628 | 164.1059 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.784 | 0.18349 | 0.082089 | 0.0014471 | 0 | 0.77395 | 0 | 0.3343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.3233 | 2.424% | CZ 1A | 25.928 | 6.0683 | 2.7148 | 0.14617 | 0 | 25.5956 | 0 | 11.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 76.9325 | 2.424% | CZ 1A | 7.5968 | 1.778 | 0.79542 | 0 | 0 | 7.4994 | 0 | 3.2394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.4982 | 2.424% | CZ 1A | 0 | 0 | 0 | 0.0014617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014617 | 2.424% | CZ 1A | 79.5314 | 18.614 | 8.3273 | 0.15977 | 0 | 78.5116 | 0 | 33.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 235.6933 | 2.424%
CZ 1B | 0.784 | 0.18347 | 0.081082 | 0.0027399 | 0 | 0.71811 | 0 | 0.41465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.348 | 0% | CZ 1B | 25.928 | 6.0675 | 2.6815 | 0.27676 | 0 | 23.7488 | 0 | 13.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 77.8392 | 0% | CZ 1B | 7.5968 | 1.7778 | 0.78567 | 0 | 0 | 6.9583 | 0 | 4.0179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.7256 | 0% | CZ 1B | 0 | 0 | 0 | 0.0027676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027676 | 0% | CZ 1B | 79.5314 | 18.6114 | 8.2252 | 0.3025 | 0 | 72.8468 | 0 | 42.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 238.2168 | 0%
CZ 2A | 0.784 | 0.18342 | 0.08442 | 0.028963 | 0 | 0.57383 | 0 | 0.33963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1583 | 17.47% | CZ 2A | 25.928 | 6.0658 | 2.7919 | 2.9256 | 0 | 18.9774 | 0 | 11.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 73.3444 | 17.47% | CZ 2A | 7.5968 | 1.7773 | 0.81802 | 0 | 0 | 5.5603 | 0 | 3.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 20.6325 | 17.47% | CZ 2A | 0 | 0 | 0 | 0.029256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029256 | 17.47% | CZ 2A | 79.5314 | 18.6062 | 8.5638 | 3.1977 | 0 | 58.211 | 0 | 34.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 219.1996 | 17.47%
CZ 2B | 0.784 | 0.18336 | 0.082879 | 0.0099172 | 0 | 0.6049 | 0 | 0.39286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.2219 | 4.471% | CZ 2B | 25.928 | 6.0641 | 2.7409 | 1.0017 | 0 | 20.0051 | 0 | 12.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 74.156 | 4.471% | CZ 2B | 7.5968 | 1.7768 | 0.80308 | 0 | 0 | 5.8614 | 0 | 3.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 21.434 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.010017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010017 | 4.471% | CZ 2B | 79.5314 | 18.601 | 8.4074 | 1.0949 | 0 | 61.3633 | 0 | 39.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 225.4875 | 4.471%
CZ 3A | 0.784 | 0.18329 | 0.086217 | 0.083896 | 0 | 0.39909 | 0 | 0.29634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.9968 | 18% | CZ 3A | 25.928 | 6.0616 | 2.8513 | 8.4743 | 0 | 13.1985 | 0 | 9.8003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 71.7377 | 18% | CZ 3A | 7.5968 | 1.776 | 0.83542 | 0 | 0 | 3.8671 | 0 | 2.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.536 | 18% | CZ 3A | 0 | 0 | 0 | 0.084743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084743 | 18% | CZ 3A | 79.5314 | 18.5933 | 8.7461 | 9.2624 | 0 | 40.4849 | 0 | 30.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 203.3159 | 18%
CZ 3B | 0.784 | 0.18336 | 0.085439 | 0.019213 | 0 | 0.28138 | 0 | 0.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.8338 | 11.03% | CZ 3B | 25.928 | 6.0641 | 2.8256 | 1.9407 | 0 | 9.3056 | 0 | 10.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 61.9517 | 11.03% | CZ 3B | 7.5968 | 1.7768 | 0.82789 | 0 | 0 | 2.7265 | 0 | 3.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.5831 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.019407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019407 | 11.03% | CZ 3B | 79.5314 | 18.601 | 8.6672 | 2.1212 | 0 | 28.5439 | 0 | 32.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 186.1981 | 11.03%
CZ 3C | 0.784 | 0.18329 | 0.088051 | 0.023625 | 0 | 0.059894 | 0 | 0.22817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.531 | 1.823% | CZ 3C | 25.928 | 6.0616 | 2.912 | 2.3864 | 0 | 1.9808 | 0 | 7.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 52.2385 | 1.823% | CZ 3C | 7.5968 | 1.776 | 0.8532 | 0 | 0 | 0.58037 | 0 | 2.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 14.6065 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.023864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023864 | 1.823% | CZ 3C | 79.5314 | 18.5933 | 8.9322 | 2.6083 | 0 | 6.0758 | 0 | 23.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 155.5241 | 1.823%
CZ 4A | 0.784 | 0.18319 | 0.088395 | 0.14385 | 0 | 0.25642 | 0 | 0.27928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.8991 | 17.78% | CZ 4A | 25.928 | 6.0582 | 2.9234 | 14.5302 | 0 | 8.4802 | 0 | 9.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.5798 | 17.78% | CZ 4A | 7.5968 | 1.775 | 0.85654 | 0 | 0 | 2.4847 | 0 | 2.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.0084 | 17.78% | CZ 4A | 0 | 0 | 0 | 0.1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1453 | 17.78% | CZ 4A | 79.5314 | 18.583 | 8.9671 | 15.8816 | 0 | 26.012 | 0 | 28.3307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 193.9421 | 17.78%
CZ 4B | 0.784 | 0.18324 | 0.087962 | 0.049507 | 0 | 0.20567 | 0 | 0.32395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.7983 | 0.3973% | CZ 4B | 25.928 | 6.0599 | 2.909 | 5.0007 | 0 | 6.8019 | 0 | 10.7134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 62.8366 | 0.3973% | CZ 4B | 7.5968 | 1.7755 | 0.85234 | 0 | 0 | 1.9929 | 0 | 3.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.9458 | 0.3973% | CZ 4B | 0 | 0 | 0 | 0.050007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050007 | 0.3973% | CZ 4B | 79.5314 | 18.5881 | 8.9231 | 5.4657 | 0 | 20.8641 | 0 | 32.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 182.871 | 0.3973%
CZ 4C | 0.784 | 0.1831 | 0.089287 | 0.10873 | 0 | 0.10965 | 0 | 0.26976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.7085 | 1.882% | CZ 4C | 25.928 | 6.0553 | 2.9529 | 10.9833 | 0 | 3.6262 | 0 | 8.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 63.8906 | 1.882% | CZ 4C | 7.5968 | 1.7742 | 0.86518 | 0 | 0 | 1.0625 | 0 | 2.6139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.5017 | 1.882% | CZ 4C | 0 | 0 | 0 | 0.10983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10983 | 1.882% | CZ 4C | 79.5314 | 18.5739 | 9.0575 | 12.0048 | 0 | 11.1229 | 0 | 27.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 174.2922 | 1.882%
CZ 5A | 0.784 | 0.1832 | 0.089937 | 0.25241 | 0 | 0.19381 | 0 | 0.27438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.9417 | 18.04% | CZ 5A | 25.928 | 6.0587 | 2.9743 | 25.4963 | 0 | 6.4096 | 0 | 9.0743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 81.3649 | 18.04% | CZ 5A | 7.5968 | 1.7752 | 0.87147 | 0 | 0 | 1.878 | 0 | 2.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.3694 | 18.04% | CZ 5A | 0 | 0 | 0 | 0.25496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25496 | 18.04% | CZ 5A | 79.5314 | 18.5842 | 9.1235 | 27.8674 | 0 | 19.6609 | 0 | 27.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 199.2382 | 18.04%
CZ 5B | 0.784 | 0.18305 | 0.089593 | 0.13211 | 0 | 0.15388 | 0 | 0.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.8184 | 3.55% | CZ 5B | 25.928 | 6.0536 | 2.963 | 13.344 | 0 | 5.0891 | 0 | 10.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 69.1132 | 3.55% | CZ 5B | 7.5968 | 1.7737 | 0.86814 | 0 | 0 | 1.4911 | 0 | 3.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.3402 | 3.55% | CZ 5B | 0 | 0 | 0 | 0.13344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13344 | 3.55% | CZ 5B | 79.5314 | 18.5687 | 9.0886 | 14.585 | 0 | 15.6103 | 0 | 31.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 185.6508 | 3.55%
CZ 5C | 0.784 | 0.18291 | 0.090013 | 0.16654 | 0 | 0.04695 | 0 | 0.22538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.6598 | 0% | CZ 5C | 25.928 | 6.049 | 2.9769 | 16.8227 | 0 | 1.5527 | 0 | 7.4538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 66.2067 | 0% | CZ 5C | 7.5968 | 1.7723 | 0.87221 | 0 | 0 | 0.45493 | 0 | 2.1839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 14.4694 | 0% | CZ 5C | 0 | 0 | 0 | 0.16823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16823 | 0% | CZ 5C | 79.5314 | 18.5545 | 9.1312 | 18.3872 | 0 | 4.7627 | 0 | 22.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 169.8671 | 0%
CZ 6A | 0.784 | 0.1831 | 0.091236 | 0.31061 | 0 | 0.11846 | 0 | 0.25924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.9106 | 2.692% | CZ 6A | 25.928 | 6.0553 | 3.0173 | 31.3749 | 0 | 3.9178 | 0 | 8.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 84.2902 | 2.692% | CZ 6A | 7.5968 | 1.7742 | 0.88407 | 0 | 0 | 1.1479 | 0 | 2.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.5041 | 2.692% | CZ 6A | 0 | 0 | 0 | 0.31375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31375 | 2.692% | CZ 6A | 79.5314 | 18.5739 | 9.2553 | 34.2927 | 0 | 12.0173 | 0 | 26.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 196.6047 | 2.692%
CZ 6B | 0.784 | 0.18305 | 0.091377 | 0.21406 | 0 | 0.10153 | 0 | 0.30247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.8405 | 0.2819% | CZ 6B | 25.928 | 6.0536 | 3.022 | 21.622 | 0 | 3.3578 | 0 | 10.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.41 | 0.2819% | CZ 6B | 7.5968 | 1.7737 | 0.88542 | 0 | 0 | 0.98382 | 0 | 2.9308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.7597 | 0.2819% | CZ 6B | 0 | 0 | 0 | 0.21622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21622 | 0.2819% | CZ 6B | 79.5314 | 18.5687 | 9.2695 | 23.6329 | 0 | 10.2996 | 0 | 30.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 188.6215 | 0.2819%
CZ 7 | 0.784 | 0.18297 | 0.0933 | 0.44819 | 0 | 0.081579 | 0 | 0.27012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.0242 | 0.121% | CZ 7 | 25.928 | 6.0511 | 3.0856 | 45.2715 | 0 | 2.6979 | 0 | 8.9331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 97.3909 | 0.121% | CZ 7 | 7.5968 | 1.7729 | 0.90407 | 0 | 0 | 0.79049 | 0 | 2.6174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.2708 | 0.121% | CZ 7 | 0 | 0 | 0 | 0.45272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45272 | 0.121% | CZ 7 | 79.5314 | 18.561 | 9.4647 | 49.4818 | 0 | 8.2756 | 0 | 27.4014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 209.3523 | 0.121%
CZ 8 | 0.784 | 0.18181 | 0.095772 | 0.71952 | 0 | 0.051141 | 0 | 0.33462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.3309 | 0.02367% | CZ 8 | 25.928 | 6.0127 | 3.1673 | 72.679 | 0 | 1.6913 | 0 | 11.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 125.9685 | 0.02367% | CZ 8 | 7.5968 | 1.7617 | 0.92802 | 0 | 0 | 0.49555 | 0 | 3.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.6137 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.72679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72679 | 0.02367% | CZ 8 | 79.5314 | 18.4434 | 9.7154 | 79.4382 | 0 | 5.1879 | 0 | 33.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 242.8979 | 0.02367%
Us Weighted | 0.784 | 0.18327 | 0.087005 | 0.11092 | 0 | 0.34256 | 0 | 0.30227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.974 | 100% | Us Weighted | 25.928 | 6.0611 | 2.8774 | 11.2041 | 0 | 11.3289 | 0 | 9.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.8197 | 100% | Us Weighted | 7.5968 | 1.7759 | 0.84306 | 0 | 0 | 3.3193 | 0 | 2.9289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.0532 | 100% | Us Weighted | 0 | 0 | 0 | 0.11204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11204 | 100% | Us Weighted | 79.5314 | 18.5919 | 8.826 | 12.2461 | 0 | 34.7502 | 0 | 30.6631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 201.2452 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.80528 | 0.18349 | 0.082089 | 0.0021436 | 0 | 0.8192 | 0 | 0.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.3927 | 2.424% | CZ 1A | 26.6317 | 6.0683 | 2.7148 | 0.21652 | 0 | 27.0922 | 0 | 11.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.2756 | 2.424% | CZ 1A | 7.803 | 1.778 | 0.79542 | 0 | 0 | 7.938 | 0 | 3.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 23.1641 | 2.424% | CZ 1A | 0 | 0 | 0 | 0.0021652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021652 | 2.424% | CZ 1A | 81.6898 | 18.614 | 8.3273 | 0.23666 | 0 | 83.1024 | 0 | 34.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 242.7417 | 2.424%
CZ 1B | 0.80528 | 0.18347 | 0.081082 | 0.004454 | 0 | 0.75335 | 0 | 0.41657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.4082 | 0% | CZ 1B | 26.6317 | 6.0675 | 2.6815 | 0.4499 | 0 | 24.9143 | 0 | 13.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.9451 | 0% | CZ 1B | 7.803 | 1.7778 | 0.78567 | 0 | 0 | 7.2998 | 0 | 4.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 23.2919 | 0% | CZ 1B | 0 | 0 | 0 | 0.004499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004499 | 0% | CZ 1B | 81.6898 | 18.6114 | 8.2252 | 0.49174 | 0 | 76.4217 | 0 | 42.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 244.3345 | 0%
CZ 2A | 0.80528 | 0.18342 | 0.084471 | 0.043139 | 0 | 0.63207 | 0 | 0.35902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.2714 | 17.47% | CZ 2A | 26.6317 | 6.0658 | 2.7936 | 4.3574 | 0 | 20.9034 | 0 | 11.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.0489 | 17.47% | CZ 2A | 7.803 | 1.7773 | 0.81851 | 0 | 0 | 6.1246 | 0 | 3.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 21.5914 | 17.47% | CZ 2A | 0 | 0 | 0 | 0.043574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043574 | 17.47% | CZ 2A | 81.6898 | 18.6062 | 8.569 | 4.7627 | 0 | 64.1188 | 0 | 36.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 230.8031 | 17.47%
CZ 2B | 0.80528 | 0.18336 | 0.082917 | 0.01634 | 0 | 0.66503 | 0 | 0.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.3297 | 4.471% | CZ 2B | 26.6317 | 6.0641 | 2.7422 | 1.6505 | 0 | 21.9934 | 0 | 13.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.1574 | 4.471% | CZ 2B | 7.803 | 1.7768 | 0.80345 | 0 | 0 | 6.444 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 22.4163 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.016505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016505 | 4.471% | CZ 2B | 81.6898 | 18.601 | 8.4113 | 1.804 | 0 | 67.4624 | 0 | 41.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 236.4806 | 4.471%
CZ 3A | 0.80528 | 0.18329 | 0.086319 | 0.14172 | 0 | 0.4744 | 0 | 0.35368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.2087 | 18% | CZ 3A | 26.6317 | 6.0616 | 2.8547 | 14.3154 | 0 | 15.6891 | 0 | 11.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 82.673 | 18% | CZ 3A | 7.803 | 1.776 | 0.83641 | 0 | 0 | 4.5969 | 0 | 3.4271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 20.0286 | 18% | CZ 3A | 0 | 0 | 0 | 0.14315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14315 | 18% | CZ 3A | 81.6898 | 18.5933 | 8.7564 | 15.6467 | 0 | 48.1247 | 0 | 35.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 225.326 | 18%
CZ 3B | 0.80528 | 0.18336 | 0.085554 | 0.029209 | 0 | 0.34346 | 0 | 0.37771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.9886 | 11.03% | CZ 3B | 26.6317 | 6.0641 | 2.8294 | 2.9504 | 0 | 11.3589 | 0 | 12.4915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 67.7497 | 11.03% | CZ 3B | 7.803 | 1.7768 | 0.829 | 0 | 0 | 3.3281 | 0 | 3.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.986 | 11.03% | CZ 3B | 0 | 0 | 0 | 0.029504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029504 | 11.03% | CZ 3B | 81.6898 | 18.601 | 8.6789 | 3.2248 | 0 | 34.8421 | 0 | 38.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 201.9893 | 11.03%
CZ 3C | 0.80528 | 0.18329 | 0.088268 | 0.051859 | 0 | 0.068443 | 0 | 0.26384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.625 | 1.823% | CZ 3C | 26.6317 | 6.0616 | 2.9191 | 5.2383 | 0 | 2.2635 | 0 | 8.7254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 57.2633 | 1.823% | CZ 3C | 7.803 | 1.776 | 0.8553 | 0 | 0 | 0.6632 | 0 | 2.5565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 15.2432 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.052383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052383 | 1.823% | CZ 3C | 81.6898 | 18.5933 | 8.9541 | 5.7254 | 0 | 6.9431 | 0 | 26.7642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 165.3064 | 1.823%
CZ 4A | 0.80528 | 0.18319 | 0.088535 | 0.25051 | 0 | 0.30301 | 0 | 0.33569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1302 | 17.78% | CZ 4A | 26.6317 | 6.0582 | 2.928 | 25.3038 | 0 | 10.0211 | 0 | 11.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 87.4683 | 17.78% | CZ 4A | 7.803 | 1.775 | 0.85789 | 0 | 0 | 2.9361 | 0 | 3.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.214 | 17.78% | CZ 4A | 0 | 0 | 0 | 0.25304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25304 | 17.78% | CZ 4A | 81.6898 | 18.583 | 8.9813 | 27.657 | 0 | 30.7385 | 0 | 34.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 218.3397 | 17.78%
CZ 4B | 0.80528 | 0.18324 | 0.08814 | 0.084396 | 0 | 0.24385 | 0 | 0.38519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.9541 | 0.3973% | CZ 4B | 26.6317 | 6.0599 | 2.9149 | 8.5249 | 0 | 8.0643 | 0 | 12.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 70.3582 | 0.3973% | CZ 4B | 7.803 | 1.7755 | 0.85407 | 0 | 0 | 2.3628 | 0 | 3.7324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 18.117 | 0.3973% | CZ 4B | 0 | 0 | 0 | 0.085249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085249 | 0.3973% | CZ 4B | 81.6898 | 18.5881 | 8.9412 | 9.3177 | 0 | 24.7363 | 0 | 39.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 198.9845 | 0.3973%
CZ 4C | 0.80528 | 0.1831 | 0.089465 | 0.196 | 0 | 0.13531 | 0 | 0.31663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.8898 | 1.882% | CZ 4C | 26.6317 | 6.0553 | 2.9587 | 19.7984 | 0 | 4.4748 | 0 | 10.4715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.8141 | 1.882% | CZ 4C | 7.803 | 1.7742 | 0.86691 | 0 | 0 | 1.3111 | 0 | 3.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.4124 | 1.882% | CZ 4C | 0 | 0 | 0 | 0.19798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19798 | 1.882% | CZ 4C | 81.6898 | 18.5739 | 9.0756 | 21.6397 | 0 | 13.7259 | 0 | 32.1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 193.4616 | 1.882%
CZ 5A | 0.80528 | 0.1832 | 0.090052 | 0.38877 | 0 | 0.23127 | 0 | 0.32833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1909 | 18.04% | CZ 5A | 26.6317 | 6.0587 | 2.9781 | 39.2695 | 0 | 7.6484 | 0 | 10.8583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 98.8684 | 18.04% | CZ 5A | 7.803 | 1.7752 | 0.87258 | 0 | 0 | 2.241 | 0 | 3.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.4623 | 18.04% | CZ 5A | 0 | 0 | 0 | 0.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3927 | 18.04% | CZ 5A | 81.6898 | 18.5842 | 9.1351 | 42.9216 | 0 | 23.4607 | 0 | 33.3066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 225.7345 | 18.04%
CZ 5B | 0.80528 | 0.18305 | 0.089708 | 0.2095 | 0 | 0.18744 | 0 | 0.36753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.0065 | 3.55% | CZ 5B | 26.6317 | 6.0536 | 2.9668 | 21.1612 | 0 | 6.199 | 0 | 12.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 80.5907 | 3.55% | CZ 5B | 7.803 | 1.7737 | 0.86925 | 0 | 0 | 1.8163 | 0 | 3.5613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.4127 | 3.55% | CZ 5B | 0 | 0 | 0 | 0.21161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21161 | 3.55% | CZ 5B | 81.6898 | 18.5687 | 9.1002 | 23.1292 | 0 | 19.0146 | 0 | 37.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 205.4225 | 3.55%
CZ 5C | 0.80528 | 0.18291 | 0.090166 | 0.28844 | 0 | 0.047153 | 0 | 0.23201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 1.81 | 0% | CZ 5C | 26.6317 | 6.049 | 2.9819 | 29.1355 | 0 | 1.5594 | 0 | 7.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.454 | 0% | CZ 5C | 7.803 | 1.7723 | 0.8737 | 0 | 0 | 0.45691 | 0 | 2.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 14.7432 | 0% | CZ 5C | 0 | 0 | 0 | 0.29135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29135 | 0% | CZ 5C | 81.6898 | 18.5545 | 9.1467 | 31.8451 | 0 | 4.7834 | 0 | 23.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 186.1916 | 0%
CZ 6A | 0.80528 | 0.1831 | 0.091364 | 0.47158 | 0 | 0.14126 | 0 | 0.32953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1861 | 2.692% | CZ 6A | 26.6317 | 6.0553 | 3.0215 | 47.6339 | 0 | 4.6716 | 0 | 10.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 104.3356 | 2.692% | CZ 6A | 7.803 | 1.7742 | 0.8853 | 0 | 0 | 1.3688 | 0 | 3.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.6134 | 2.692% | CZ 6A | 0 | 0 | 0 | 0.47634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47634 | 2.692% | CZ 6A | 81.6898 | 18.5739 | 9.2682 | 52.0639 | 0 | 14.3295 | 0 | 33.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 225.9899 | 2.692%
CZ 6B | 0.80528 | 0.18305 | 0.091529 | 0.32035 | 0 | 0.11394 | 0 | 0.37242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.0506 | 0.2819% | CZ 6B | 26.6317 | 6.0536 | 3.027 | 32.3589 | 0 | 3.7682 | 0 | 12.3166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 89.5796 | 0.2819% | CZ 6B | 7.803 | 1.7737 | 0.88691 | 0 | 0 | 1.1041 | 0 | 3.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.7655 | 0.2819% | CZ 6B | 0 | 0 | 0 | 0.32359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32359 | 0.2819% | CZ 6B | 81.6898 | 18.5687 | 9.285 | 35.3683 | 0 | 11.5584 | 0 | 37.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 210.8866 | 0.2819%
CZ 7 | 0.80528 | 0.18297 | 0.093428 | 0.62026 | 0 | 0.097339 | 0 | 0.39031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.3536 | 0.121% | CZ 7 | 26.6317 | 6.0511 | 3.0898 | 62.6528 | 0 | 3.2191 | 0 | 12.9082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 119.9764 | 0.121% | CZ 7 | 7.803 | 1.7729 | 0.9053 | 0 | 0 | 0.9432 | 0 | 3.7821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 16.7957 | 0.121% | CZ 7 | 0 | 0 | 0 | 0.62653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62653 | 0.121% | CZ 7 | 81.6898 | 18.561 | 9.4776 | 68.4795 | 0 | 9.8744 | 0 | 39.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 244.3132 | 0.121%
CZ 8 | 0.80528 | 0.18181 | 0.095823 | 0.91528 | 0 | 0.050746 | 0 | 0.45732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.6703 | 0.02367% | CZ 8 | 26.6317 | 6.0127 | 3.169 | 92.4526 | 0 | 1.6783 | 0 | 15.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 150.492 | 0.02367% | CZ 8 | 7.803 | 1.7617 | 0.92851 | 0 | 0 | 0.49172 | 0 | 4.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 17.0054 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.92453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92453 | 0.02367% | CZ 8 | 81.6898 | 18.4434 | 9.7206 | 101.0507 | 0 | 5.1479 | 0 | 46.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 279.0802 | 0.02367%
Us Weighted | 0.80528 | 0.18327 | 0.087108 | 0.17871 | 0 | 0.39462 | 0 | 0.34947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 2.1625 | 100% | Us Weighted | 26.6317 | 6.0611 | 2.8808 | 18.0517 | 0 | 13.0507 | 0 | 11.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 83.6572 | 100% | Us Weighted | 7.803 | 1.7759 | 0.84406 | 0 | 0 | 3.8238 | 0 | 3.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5891 | 19.2223 | 100% | Us Weighted | 0 | 0 | 0 | 0.18052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18052 | 100% | Us Weighted | 81.6898 | 18.5919 | 8.8365 | 19.7305 | 0 | 40.0315 | 0 | 35.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6365 | 220.9682 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Strip Mall |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 22500 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 22500 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.18738 | 0.093058 | 0.006931 | -0.00052547 | 0 | 0.38429 | 0 | 0.21979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.89164 | 2.424% | CZ 1A | 6.1969 | 3.0776 | 0.22922 | -0.053078 | 0 | 12.7089 | 0 | 7.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.4523 | 2.424% | CZ 1A | 1.8157 | 0.90172 | 0.06716 | 0 | 0 | 3.7237 | 0 | 2.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 8.645 | 2.424% | CZ 1A | 0 | 0 | 0 | -0.00053078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00053078 | 2.424% | CZ 1A | 19.0082 | 9.4401 | 0.7031 | -0.058014 | 0 | 38.9831 | 0 | 22.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 90.4463 | 2.424%
CZ 1B | 0.18738 | 0.093046 | 0.0067526 | -0.0033905 | 0 | 0.2814 | 0 | 0.23116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.79707 | 0% | CZ 1B | 6.1969 | 3.0771 | 0.22332 | -0.34248 | 0 | 9.3065 | 0 | 7.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 26.1299 | 0% | CZ 1B | 1.8157 | 0.9016 | 0.065432 | 0 | 0 | 2.7268 | 0 | 2.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.7563 | 0% | CZ 1B | 0 | 0 | 0 | -0.0034248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0034248 | 0% | CZ 1B | 19.0082 | 9.4388 | 0.685 | -0.37433 | 0 | 28.5465 | 0 | 23.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 80.8269 | 0%
CZ 2A | 0.18738 | 0.093033 | 0.0070711 | 0.0066768 | 0 | 0.30376 | 0 | 0.19565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.7943 | 17.47% | CZ 2A | 6.1969 | 3.0767 | 0.23385 | 0.67442 | 0 | 10.0459 | 0 | 6.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 26.7221 | 17.47% | CZ 2A | 1.8157 | 0.90147 | 0.068518 | 0 | 0 | 2.9434 | 0 | 1.8958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.6319 | 17.47% | CZ 2A | 0 | 0 | 0 | 0.0067442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067442 | 17.47% | CZ 2A | 19.0082 | 9.4375 | 0.71731 | 0.73715 | 0 | 30.8148 | 0 | 19.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 80.6356 | 17.47%
CZ 2B | 0.18738 | 0.093007 | 0.0068163 | 0.0018183 | 0 | 0.27441 | 0 | 0.19377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.75793 | 4.471% | CZ 2B | 6.1969 | 3.0759 | 0.22542 | 0.18367 | 0 | 9.0751 | 0 | 6.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 25.1894 | 4.471% | CZ 2B | 1.8157 | 0.90123 | 0.066049 | 0 | 0 | 2.659 | 0 | 1.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.3266 | 4.471% | CZ 2B | 0 | 0 | 0 | 0.0018367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018367 | 4.471% | CZ 2B | 19.0082 | 9.4349 | 0.69146 | 0.20075 | 0 | 27.8369 | 0 | 19.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 76.9029 | 4.471%
CZ 3A | 0.18738 | 0.09288 | 0.0071985 | 0.047176 | 0 | 0.25455 | 0 | 0.19599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.7859 | 18% | CZ 3A | 6.1969 | 3.0717 | 0.23807 | 4.7652 | 0 | 8.4182 | 0 | 6.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.1957 | 18% | CZ 3A | 1.8157 | 0.89999 | 0.069752 | 0 | 0 | 2.4665 | 0 | 1.8991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 7.1581 | 18% | CZ 3A | 0 | 0 | 0 | 0.047652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047652 | 18% | CZ 3A | 19.0082 | 9.422 | 0.73024 | 5.2084 | 0 | 25.822 | 0 | 19.8819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 80.1463 | 18%
CZ 3B | 0.18738 | 0.093007 | 0.0070329 | -0.00063807 | 0 | 0.15837 | 0 | 0.15108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.59695 | 11.03% | CZ 3B | 6.1969 | 3.0759 | 0.23259 | -0.064452 | 0 | 5.2374 | 0 | 4.9964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 19.6987 | 11.03% | CZ 3B | 1.8157 | 0.90123 | 0.068148 | 0 | 0 | 1.5346 | 0 | 1.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.7906 | 11.03% | CZ 3B | 0 | 0 | 0 | -0.00064452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00064452 | 11.03% | CZ 3B | 19.0082 | 9.4349 | 0.71344 | -0.070446 | 0 | 16.0652 | 0 | 15.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 60.551 | 11.03%
CZ 3C | 0.18738 | 0.092918 | 0.0072622 | 0.01327 | 0 | 0.040503 | 0 | 0.11413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.45619 | 1.823% | CZ 3C | 6.1969 | 3.0729 | 0.24017 | 1.3404 | 0 | 1.3395 | 0 | 3.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 15.9884 | 1.823% | CZ 3C | 1.8157 | 0.90036 | 0.07037 | 0 | 0 | 0.39247 | 0 | 1.1059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 4.2918 | 1.823% | CZ 3C | 0 | 0 | 0 | 0.013404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013404 | 1.823% | CZ 3C | 19.0082 | 9.4259 | 0.7367 | 1.4651 | 0 | 4.1087 | 0 | 11.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 46.3961 | 1.823%
CZ 4A | 0.18738 | 0.092791 | 0.0073769 | 0.11637 | 0 | 0.156 | 0 | 0.14969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.71033 | 17.78% | CZ 4A | 6.1969 | 3.0687 | 0.24396 | 11.7542 | 0 | 5.1591 | 0 | 4.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 31.3973 | 17.78% | CZ 4A | 1.8157 | 0.89913 | 0.071481 | 0 | 0 | 1.5116 | 0 | 1.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.7554 | 17.78% | CZ 4A | 0 | 0 | 0 | 0.11754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11754 | 17.78% | CZ 4A | 19.0082 | 9.413 | 0.74833 | 12.8473 | 0 | 15.8248 | 0 | 15.1851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 73.1004 | 17.78%
CZ 4B | 0.18738 | 0.092905 | 0.0073514 | 0.037192 | 0 | 0.10957 | 0 | 0.16238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.5975 | 0.3973% | CZ 4B | 6.1969 | 3.0725 | 0.24312 | 3.7567 | 0 | 3.6236 | 0 | 5.3702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 22.287 | 0.3973% | CZ 4B | 1.8157 | 0.90024 | 0.071234 | 0 | 0 | 1.0617 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.4293 | 0.3973% | CZ 4B | 0 | 0 | 0 | 0.037567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037567 | 0.3973% | CZ 4B | 19.0082 | 9.4246 | 0.74575 | 4.1061 | 0 | 11.1151 | 0 | 16.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 60.9458 | 0.3973%
CZ 4C | 0.18738 | 0.092612 | 0.0074151 | 0.085172 | 0 | 0.062786 | 0 | 0.12751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.5636 | 1.882% | CZ 4C | 6.1969 | 3.0628 | 0.24523 | 8.6032 | 0 | 2.0764 | 0 | 4.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 24.4255 | 1.882% | CZ 4C | 1.8157 | 0.8974 | 0.071851 | 0 | 0 | 0.60839 | 0 | 1.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 4.6359 | 1.882% | CZ 4C | 0 | 0 | 0 | 0.086032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086032 | 1.882% | CZ 4C | 19.0082 | 9.3949 | 0.75221 | 9.4033 | 0 | 6.3692 | 0 | 12.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 57.9364 | 1.882%
CZ 5A | 0.18738 | 0.092485 | 0.0074406 | 0.16081 | 0 | 0.11808 | 0 | 0.13661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.70353 | 18.04% | CZ 5A | 6.1969 | 3.0586 | 0.24607 | 16.2439 | 0 | 3.9051 | 0 | 4.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 34.1923 | 18.04% | CZ 5A | 1.8157 | 0.89616 | 0.072098 | 0 | 0 | 1.1442 | 0 | 1.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.2588 | 18.04% | CZ 5A | 0 | 0 | 0 | 0.16244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16244 | 18.04% | CZ 5A | 19.0082 | 9.3819 | 0.7548 | 17.7546 | 0 | 11.9785 | 0 | 13.8577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 72.8094 | 18.04%
CZ 5B | 0.18738 | 0.09288 | 0.0074024 | 0.080647 | 0 | 0.087198 | 0 | 0.15392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.61015 | 3.55% | CZ 5B | 6.1969 | 3.0717 | 0.24481 | 8.1462 | 0 | 2.8837 | 0 | 5.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 25.6577 | 3.55% | CZ 5B | 1.8157 | 0.89999 | 0.071728 | 0 | 0 | 0.84493 | 0 | 1.4915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.1308 | 3.55% | CZ 5B | 0 | 0 | 0 | 0.081462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081462 | 3.55% | CZ 5B | 19.0082 | 9.422 | 0.75092 | 8.9038 | 0 | 8.8456 | 0 | 15.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 62.6183 | 3.55%
CZ 5C | 0.18738 | 0.092319 | 0.0074661 | 0.12416 | 0 | 0.018512 | 0 | 0.073935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.5045 | 0% | CZ 5C | 6.1969 | 3.0531 | 0.24691 | 12.5415 | 0 | 0.61223 | 0 | 2.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 25.1198 | 0% | CZ 5C | 1.8157 | 0.89456 | 0.072345 | 0 | 0 | 0.17938 | 0 | 0.71641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 3.6854 | 0% | CZ 5C | 0 | 0 | 0 | 0.12542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12542 | 0% | CZ 5C | 19.0082 | 9.3651 | 0.75738 | 13.7079 | 0 | 1.8779 | 0 | 7.5001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 52.2903 | 0%
CZ 6A | 0.18738 | 0.092332 | 0.0075043 | 0.19399 | 0 | 0.068494 | 0 | 0.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.70073 | 2.692% | CZ 6A | 6.1969 | 3.0536 | 0.24818 | 19.595 | 0 | 2.2652 | 0 | 4.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.3535 | 2.692% | CZ 6A | 1.8157 | 0.89468 | 0.072715 | 0 | 0 | 0.6637 | 0 | 1.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 4.9102 | 2.692% | CZ 6A | 0 | 0 | 0 | 0.19595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19595 | 2.692% | CZ 6A | 19.0082 | 9.3664 | 0.76126 | 21.4173 | 0 | 6.9483 | 0 | 15.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 72.8222 | 2.692%
CZ 6B | 0.18738 | 0.092714 | 0.0075043 | 0.11405 | 0 | 0.05039 | 0 | 0.16606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.61882 | 0.2819% | CZ 6B | 6.1969 | 3.0662 | 0.24818 | 11.52 | 0 | 1.6665 | 0 | 5.4919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 28.2136 | 0.2819% | CZ 6B | 1.8157 | 0.89839 | 0.072715 | 0 | 0 | 0.48827 | 0 | 1.6091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 4.8912 | 0.2819% | CZ 6B | 0 | 0 | 0 | 0.1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1152 | 0.2819% | CZ 6B | 19.0082 | 9.4052 | 0.76126 | 12.5913 | 0 | 5.1117 | 0 | 16.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 63.7972 | 0.2819%
CZ 7 | 0.18738 | 0.092421 | 0.0075935 | 0.25856 | 0 | 0.049791 | 0 | 0.20319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.79966 | 0.121% | CZ 7 | 6.1969 | 3.0565 | 0.25113 | 26.1176 | 0 | 1.6467 | 0 | 6.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 44.0125 | 0.121% | CZ 7 | 1.8157 | 0.89555 | 0.07358 | 0 | 0 | 0.48246 | 0 | 1.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.2432 | 0.121% | CZ 7 | 0 | 0 | 0 | 0.26118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26118 | 0.121% | CZ 7 | 19.0082 | 9.3755 | 0.7703 | 28.5466 | 0 | 5.0509 | 0 | 20.6121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 83.4372 | 0.121%
CZ 8 | 0.18738 | 0.090689 | 0.0075935 | 0.33827 | 0 | 0.028628 | 0 | 0.22829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.88158 | 0.02367% | CZ 8 | 6.1969 | 2.9992 | 0.25113 | 34.169 | 0 | 0.94678 | 0 | 7.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 52.1368 | 0.02367% | CZ 8 | 1.8157 | 0.87876 | 0.07358 | 0 | 0 | 0.2774 | 0 | 2.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 5.2645 | 0.02367% | CZ 8 | 0 | 0 | 0 | 0.34169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34169 | 0.02367% | CZ 8 | 19.0082 | 9.1997 | 0.7703 | 37.3467 | 0 | 2.9042 | 0 | 23.1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 92.461 | 0.02367%
Us Weighted | 0.18738 | 0.092823 | 0.0072325 | 0.070155 | 0 | 0.19451 | 0 | 0.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00072622 | 0.71963 | 100% | Us Weighted | 6.1969 | 3.0698 | 0.23919 | 7.0864 | 0 | 6.4328 | 0 | 5.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 28.5653 | 100% | Us Weighted | 1.8157 | 0.89944 | 0.070082 | 0 | 0 | 1.8848 | 0 | 1.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007037 | 6.2933 | 100% | Us Weighted | 0 | 0 | 0 | 0.070864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070864 | 100% | Us Weighted | 19.0082 | 9.4162 | 0.73369 | 7.7454 | 0 | 19.7318 | 0 | 16.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07367 | 73.6297 | 100%
Building Type: | Strip Mall |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 22500 | [17 empty] | Prototype Floor Area: | 22500 | [17 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 23.27% | 50.72% | 8.443% | -24.51% | 0% | 46.91% | 0% | 65.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.27% | 2.424% | CZ 1A | 23.27% | 50.72% | 8.443% | -24.51% | 0% | 46.91% | 0% | 65.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.15% | 2.424% | CZ 1A | 23.27% | 50.72% | 8.443% | 0% | 0% | 46.91% | 0% | 65.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.32% | 2.424% | CZ 1A | 0% | 0% | 0% | -24.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -24.51% | 2.424% | CZ 1A | 23.27% | 50.72% | 8.443% | -24.51% | 0% | 46.91% | 0% | 65.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 37.26% | 2.424%
CZ 1B | 23.27% | 50.72% | 8.328% | -76.12% | 0% | 37.35% | 0% | 55.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.1% | 0% | CZ 1B | 23.27% | 50.72% | 8.328% | -76.12% | 0% | 37.35% | 0% | 55.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.68% | 0% | CZ 1B | 23.27% | 50.72% | 8.328% | 0% | 0% | 37.35% | 0% | 55.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.3% | 0% | CZ 1B | 0% | 0% | 0% | -76.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -76.12% | 0% | CZ 1B | 23.27% | 50.72% | 8.328% | -76.12% | 0% | 37.35% | 0% | 55.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.08% | 0%
CZ 2A | 23.27% | 50.72% | 8.371% | 15.48% | 0% | 48.06% | 0% | 54.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.97% | 17.47% | CZ 2A | 23.27% | 50.72% | 8.371% | 15.48% | 0% | 48.06% | 0% | 54.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.24% | 17.47% | CZ 2A | 23.27% | 50.72% | 8.371% | 0% | 0% | 48.06% | 0% | 54.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.35% | 17.47% | CZ 2A | 0% | 0% | 0% | 15.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.48% | 17.47% | CZ 2A | 23.27% | 50.72% | 8.371% | 15.48% | 0% | 48.06% | 0% | 54.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.94% | 17.47%
CZ 2B | 23.27% | 50.72% | 8.221% | 11.13% | 0% | 41.26% | 0% | 46.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.53% | 4.471% | CZ 2B | 23.27% | 50.72% | 8.221% | 11.13% | 0% | 41.26% | 0% | 46.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.23% | 4.471% | CZ 2B | 23.27% | 50.72% | 8.221% | 0% | 0% | 41.26% | 0% | 46.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.68% | 4.471% | CZ 2B | 0% | 0% | 0% | 11.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.13% | 4.471% | CZ 2B | 23.27% | 50.72% | 8.221% | 11.13% | 0% | 41.26% | 0% | 46.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.52% | 4.471%
CZ 3A | 23.27% | 50.67% | 8.339% | 33.29% | 0% | 53.66% | 0% | 55.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.58% | 18% | CZ 3A | 23.27% | 50.67% | 8.339% | 33.29% | 0% | 53.66% | 0% | 55.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.31% | 18% | CZ 3A | 23.27% | 50.67% | 8.339% | 0% | 0% | 53.66% | 0% | 55.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.74% | 18% | CZ 3A | 0% | 0% | 0% | 33.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.29% | 18% | CZ 3A | 23.27% | 50.67% | 8.339% | 33.29% | 0% | 53.66% | 0% | 55.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.57% | 18%
CZ 3B | 23.27% | 50.72% | 8.22% | -2.184% | 0% | 46.11% | 0% | 40% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.02% | 11.03% | CZ 3B | 23.27% | 50.72% | 8.22% | -2.184% | 0% | 46.11% | 0% | 40% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.08% | 11.03% | CZ 3B | 23.27% | 50.72% | 8.22% | 0% | 0% | 46.11% | 0% | 40% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.5% | 11.03% | CZ 3B | 0% | 0% | 0% | -2.184% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -2.184% | 11.03% | CZ 3B | 23.27% | 50.72% | 8.22% | -2.184% | 0% | 46.11% | 0% | 40% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.98% | 11.03%
CZ 3C | 23.27% | 50.7% | 8.227% | 25.59% | 0% | 59.18% | 0% | 43.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 28.07% | 1.823% | CZ 3C | 23.27% | 50.7% | 8.227% | 25.59% | 0% | 59.18% | 0% | 43.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 27.92% | 1.823% | CZ 3C | 23.27% | 50.7% | 8.227% | 0% | 0% | 59.18% | 0% | 43.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 28.16% | 1.823% | CZ 3C | 0% | 0% | 0% | 25.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 25.59% | 1.823% | CZ 3C | 23.27% | 50.7% | 8.227% | 25.59% | 0% | 59.18% | 0% | 43.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 28.07% | 1.823%
CZ 4A | 23.27% | 50.65% | 8.332% | 46.45% | 0% | 51.48% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.35% | 17.78% | CZ 4A | 23.27% | 50.65% | 8.332% | 46.45% | 0% | 51.48% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 35.9% | 17.78% | CZ 4A | 23.27% | 50.65% | 8.332% | 0% | 0% | 51.48% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.6% | 17.78% | CZ 4A | 0% | 0% | 0% | 46.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 46.45% | 17.78% | CZ 4A | 23.27% | 50.65% | 8.332% | 46.45% | 0% | 51.48% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.48% | 17.78%
CZ 4B | 23.27% | 50.7% | 8.341% | 44.07% | 0% | 44.93% | 0% | 42.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.58% | 0.3973% | CZ 4B | 23.27% | 50.7% | 8.341% | 44.07% | 0% | 44.93% | 0% | 42.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.68% | 0.3973% | CZ 4B | 23.27% | 50.7% | 8.341% | 0% | 0% | 44.93% | 0% | 42.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.97% | 0.3973% | CZ 4B | 0% | 0% | 0% | 44.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.07% | 0.3973% | CZ 4B | 23.27% | 50.7% | 8.341% | 44.07% | 0% | 44.93% | 0% | 42.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.63% | 0.3973%
CZ 4C | 23.27% | 50.58% | 8.288% | 43.45% | 0% | 46.4% | 0% | 40.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.82% | 1.882% | CZ 4C | 23.27% | 50.58% | 8.288% | 43.45% | 0% | 46.4% | 0% | 40.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.22% | 1.882% | CZ 4C | 23.27% | 50.58% | 8.288% | 0% | 0% | 46.4% | 0% | 40.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 28.25% | 1.882% | CZ 4C | 0% | 0% | 0% | 43.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.45% | 1.882% | CZ 4C | 23.27% | 50.58% | 8.288% | 43.45% | 0% | 46.4% | 0% | 40.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.95% | 1.882%
CZ 5A | 23.27% | 50.48% | 8.263% | 41.37% | 0% | 51.06% | 0% | 41.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.11% | 18.04% | CZ 5A | 23.27% | 50.48% | 8.263% | 41.37% | 0% | 51.06% | 0% | 41.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.58% | 18.04% | CZ 5A | 23.27% | 50.48% | 8.263% | 0% | 0% | 51.06% | 0% | 41.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.12% | 18.04% | CZ 5A | 0% | 0% | 0% | 41.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.37% | 18.04% | CZ 5A | 23.27% | 50.48% | 8.263% | 41.37% | 0% | 51.06% | 0% | 41.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.25% | 18.04%
CZ 5B | 23.27% | 50.74% | 8.252% | 38.5% | 0% | 46.52% | 0% | 41.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.41% | 3.55% | CZ 5B | 23.27% | 50.74% | 8.252% | 38.5% | 0% | 46.52% | 0% | 41.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.84% | 3.55% | CZ 5B | 23.27% | 50.74% | 8.252% | 0% | 0% | 46.52% | 0% | 41.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.47% | 3.55% | CZ 5B | 0% | 0% | 0% | 38.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.5% | 3.55% | CZ 5B | 23.27% | 50.74% | 8.252% | 38.5% | 0% | 46.52% | 0% | 41.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.48% | 3.55%
CZ 5C | 23.27% | 50.47% | 8.28% | 43.05% | 0% | 39.26% | 0% | 31.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 27.87% | 0% | CZ 5C | 23.27% | 50.47% | 8.28% | 43.05% | 0% | 39.26% | 0% | 31.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.62% | 0% | CZ 5C | 23.27% | 50.47% | 8.28% | 0% | 0% | 39.26% | 0% | 31.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 25% | 0% | CZ 5C | 0% | 0% | 0% | 43.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.05% | 0% | CZ 5C | 23.27% | 50.47% | 8.28% | 43.05% | 0% | 39.26% | 0% | 31.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 28.08% | 0%
CZ 6A | 23.27% | 50.43% | 8.214% | 41.14% | 0% | 48.49% | 0% | 45.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.05% | 2.692% | CZ 6A | 23.27% | 50.43% | 8.214% | 41.14% | 0% | 48.49% | 0% | 45.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.84% | 2.692% | CZ 6A | 23.27% | 50.43% | 8.214% | 0% | 0% | 48.49% | 0% | 45.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.56% | 2.692% | CZ 6A | 0% | 0% | 0% | 41.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.14% | 2.692% | CZ 6A | 23.27% | 50.43% | 8.214% | 41.14% | 0% | 48.49% | 0% | 45.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.22% | 2.692%
CZ 6B | 23.27% | 50.65% | 8.199% | 35.6% | 0% | 44.22% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.18% | 0.2819% | CZ 6B | 23.27% | 50.65% | 8.199% | 35.6% | 0% | 44.22% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.5% | 0.2819% | CZ 6B | 23.27% | 50.65% | 8.199% | 0% | 0% | 44.22% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 29.17% | 0.2819% | CZ 6B | 0% | 0% | 0% | 35.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.6% | 0.2819% | CZ 6B | 23.27% | 50.65% | 8.199% | 35.6% | 0% | 44.22% | 0% | 44.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.25% | 0.2819%
CZ 7 | 23.27% | 50.51% | 8.128% | 41.69% | 0% | 51.15% | 0% | 52.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.98% | 0.121% | CZ 7 | 23.27% | 50.51% | 8.128% | 41.69% | 0% | 51.15% | 0% | 52.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 36.68% | 0.121% | CZ 7 | 23.27% | 50.51% | 8.128% | 0% | 0% | 51.15% | 0% | 52.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 31.22% | 0.121% | CZ 7 | 0% | 0% | 0% | 41.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.69% | 0.121% | CZ 7 | 23.27% | 50.51% | 8.128% | 41.69% | 0% | 51.15% | 0% | 52.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.15% | 0.121%
CZ 8 | 23.27% | 49.88% | 7.924% | 36.96% | 0% | 56.41% | 0% | 49.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.01% | 0.02367% | CZ 8 | 23.27% | 49.88% | 7.924% | 36.96% | 0% | 56.41% | 0% | 49.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.64% | 0.02367% | CZ 8 | 23.27% | 49.88% | 7.924% | 0% | 0% | 56.41% | 0% | 49.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 30.96% | 0.02367% | CZ 8 | 0% | 0% | 0% | 36.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.96% | 0.02367% | CZ 8 | 23.27% | 49.88% | 7.924% | 36.96% | 0% | 56.41% | 0% | 49.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.13% | 0.02367%
Us Weighted | 23.27% | 50.65% | 8.303% | 39.26% | 0% | 49.29% | 0% | 47.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.28% | 100% | Us Weighted | 23.27% | 50.65% | 8.303% | 39.26% | 0% | 49.29% | 0% | 47.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 34.15% | 100% | Us Weighted | 23.27% | 50.65% | 8.303% | 0% | 0% | 49.29% | 0% | 47.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 32.74% | 100% | Us Weighted | 0% | 0% | 0% | 39.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.26% | 100% | Us Weighted | 23.27% | 50.65% | 8.303% | 39.26% | 0% | 49.29% | 0% | 47.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 33.32% | 100%

## PrSchool
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Primary School |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Primary School | [14 empty] | Prototype Floor Area: | 73959 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.27405 | 0.017771 | 0.024515 | 0.099364 | 0 | 0.21633 | 0 | 0.12348 | 0.032338 | 0.00047268 | 0.047498 | 0 | 0.0093797 | 0.10384 | 0 | 0.36238 | 1.3114 |  | STD2013 | 9.0631 | 0.58772 | 1.7959 | 10.0368 | 0 | 7.1542 | 0 | 4.0836 | 1.0695 | 0.015632 | 1.5708 | 0 | 0.3102 | 6.547 | 0 | 11.9836 | 54.2181 |  | STD2013 | 2.6555 | 0.1722 | 0.097041 | 0 | 0 | 2.0962 | 0 | 1.1965 | 0.31335 | 0.0045802 | 0.46025 | 0 | 0.090888 | 0.56229 | 0 | 3.5115 | 11.1602 |  | STD2013 | 0 | 0 | 0.014647 | 0.10037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.16129 |  | STD2013 | 27.8001 | 1.8028 | 2.6168 | 10.9702 | 0 | 21.9447 | 0 | 12.526 | 3.2805 | 0.04795 | 4.8184 | 0 | 0.9515 | 10.9449 | 0 | 36.7621 | 134.4659
STD2010 | 0.3114 | 0.017771 | 0.024519 | 0.096358 | 0 | 0.26397 | 0 | 0.15254 | 0.040915 | 0.00052073 | 0.052735 | 0 | 0.010512 | 0.10384 | 0 | 0.42046 | 1.4955 |  | STD2010 | 10.2983 | 0.58772 | 1.7964 | 9.7332 | 0 | 8.73 | 0 | 5.0447 | 1.3531 | 0.017221 | 1.744 | 0 | 0.34763 | 6.547 | 0 | 13.9042 | 60.1035 |  | STD2010 | 3.0174 | 0.1722 | 0.097031 | 0 | 0 | 2.5579 | 0 | 1.4781 | 0.39646 | 0.0050458 | 0.511 | 0 | 0.10186 | 0.56229 | 0 | 4.0742 | 12.9734 |  | STD2010 | 0 | 0 | 0.014652 | 0.097332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15826 |  | STD2010 | 31.5889 | 1.8028 | 2.6173 | 10.6383 | 0 | 26.7783 | 0 | 15.4741 | 4.1505 | 0.052825 | 5.3496 | 0 | 1.0663 | 10.9449 | 0 | 42.6533 | 153.1171
STD2007 | 0.46913 | 0.03293 | 0.025394 | 0.13371 | 0 | 0.36826 | 0 | 0.17158 | 0.042295 | 0.00040613 | 0.05275 | 0 | 0.018616 | 0.10384 | 0 | 0.42505 | 1.844 |  | STD2007 | 15.5148 | 1.089 | 1.8286 | 13.5057 | 0 | 12.179 | 0 | 5.6745 | 1.3988 | 0.013431 | 1.7445 | 0 | 0.61566 | 6.547 | 0 | 14.0563 | 74.1673 |  | STD2007 | 4.5458 | 0.31909 | 0.10503 | 0 | 0 | 3.5684 | 0 | 1.6626 | 0.40983 | 0.0039353 | 0.51114 | 0 | 0.18039 | 0.56229 | 0 | 4.1188 | 15.9873 |  | STD2007 | 0 | 0 | 0.014701 | 0.13506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.19604 |  | STD2007 | 47.5899 | 3.3405 | 2.7064 | 14.7617 | 0 | 37.3577 | 0 | 17.4059 | 4.2905 | 0.041199 | 5.3511 | 0 | 1.8885 | 10.9449 | 0 | 43.1196 | 188.7981
STD2004 | 0.46913 | 0.03293 | 0.025408 | 0.17128 | 0 | 0.39782 | 0 | 0.19641 | 0.051919 | 0.000486 | 0.052753 | 0 | 0.018613 | 0.10384 | 0 | 0.42505 | 1.9457 |  | STD2004 | 15.5148 | 1.089 | 1.83 | 17.3012 | 0 | 13.1565 | 0 | 6.4956 | 1.717 | 0.016073 | 1.7446 | 0 | 0.61557 | 6.547 | 0 | 14.0563 | 80.0837 |  | STD2004 | 4.5458 | 0.31909 | 0.10505 | 0 | 0 | 3.8548 | 0 | 1.9032 | 0.50309 | 0.0047092 | 0.51117 | 0 | 0.18036 | 0.56229 | 0 | 4.1188 | 16.6084 |  | STD2004 | 0 | 0 | 0.014714 | 0.17301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23401 |  | STD2004 | 47.5899 | 3.3405 | 2.708 | 18.9102 | 0 | 40.3561 | 0 | 19.9247 | 5.2669 | 0.049301 | 5.3514 | 0 | 1.8882 | 10.9449 | 0 | 43.1196 | 199.4497
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 1.467e-05 | 0.037576 | 0 | 0.029557 | 0 | 0.02483 | 0.0096245 | 7.9866e-05 | 2.8424e-06 | 0 | -2.7453e-06 | 0 | 0 | 0 | 0.10168 |  | 2004-2007 | 0 | 0 | 0.0013728 | 3.7955 | 0 | 0.97749 | 0 | 0.82115 | 0.3183 | 0.0026413 | 9.4003e-05 | 0 | -9.0789e-05 | 0 | 0 | 0 | 5.9165 |  | 2004-2007 | 0 | 0 | 1.5546e-05 | 0 | 0 | 0.2864 | 0 | 0.2406 | 0.09326 | 0.00077389 | 2.7543e-05 | 0 | -2.6601e-05 | 0 | 0 | 0 | 0.62105 |  | 2004-2007 | 0 | 0 | 1.3198e-05 | 0.037955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037968 |  | 2004-2007 | 0 | 0 | 0.0016053 | 4.1485 | 0 | 2.9983 | 0 | 2.5188 | 0.97633 | 0.0081018 | 0.00028835 | 0 | -0.00027849 | 0 | 0 | 0 | 10.6517
2007-2010 | 0.15773 | 0.015159 | 0.00087448 | 0.037348 | 0 | 0.10429 | 0 | 0.019043 | 0.00138 | -0.0001146 | 1.456e-05 | 0 | 0.0081045 | 0 | 0 | 0.004597 | 0.34843 |  | 2007-2010 | 5.2165 | 0.50133 | 0.032215 | 3.7725 | 0 | 3.449 | 0 | 0.62979 | 0.045639 | -0.0037901 | 0.00048152 | 0 | 0.26803 | 0 | 0 | 0.15203 | 14.0638 |  | 2007-2010 | 1.5284 | 0.14689 | 0.0080037 | 0 | 0 | 1.0106 | 0 | 0.18453 | 0.013372 | -0.0011105 | 0.00014109 | 0 | 0.078531 | 0 | 0 | 0.044544 | 3.0139 |  | 2007-2010 | 0 | 0 | 4.8983e-05 | 0.037725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037774 |  | 2007-2010 | 16.0011 | 1.5378 | 0.089145 | 4.1234 | 0 | 10.5795 | 0 | 1.9318 | 0.13999 | -0.011626 | 0.001477 | 0 | 0.82215 | 0 | 0 | 0.46633 | 35.6809
2010-2013 | 0.037349 | 0 | 4.2241e-06 | -0.003006 | 0 | 0.047648 | 0 | 0.029062 | 0.0085765 | 4.8051e-05 | 0.0052368 | 0 | 0.0011319 | 0 | 0 | 0.058074 | 0.18412 |  | 2010-2013 | 1.2352 | 0 | 0.00050158 | -0.30364 | 0 | 1.5758 | 0 | 0.96111 | 0.28364 | 0.0015891 | 0.17319 | 0 | 0.037435 | 0 | 0 | 1.9206 | 5.8854 |  | 2010-2013 | 0.3619 | 0 | -1.0684e-05 | 0 | 0 | 0.4617 | 0 | 0.2816 | 0.083104 | 0.00046561 | 0.050744 | 0 | 0.010968 | 0 | 0 | 0.56273 | 1.8132 |  | 2010-2013 | 0 | 0 | 5.3805e-06 | -0.0030364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.003031 |  | 2010-2013 | 3.7887 | 0 | 0.00047623 | -0.33188 | 0 | 4.8336 | 0 | 2.9481 | 0.87002 | 0.0048745 | 0.53123 | 0 | 0.11483 | 0 | 0 | 5.8912 | 18.6512
2004-2013 | 0.19508 | 0.015159 | 0.00089338 | 0.071918 | 0 | 0.1815 | 0 | 0.072935 | 0.019581 | 1.3314e-05 | 0.0052542 | 0 | 0.0092337 | 0 | 0 | 0.062671 | 0.63424 |  | 2004-2013 | 6.4517 | 0.50133 | 0.034089 | 7.2644 | 0 | 6.0023 | 0 | 2.4121 | 0.64757 | 0.0004403 | 0.17376 | 0 | 0.30537 | 0 | 0 | 2.0726 | 25.8656 |  | 2004-2013 | 1.8903 | 0.14689 | 0.0080086 | 0 | 0 | 1.7587 | 0 | 0.70673 | 0.18974 | 0.00012901 | 0.050912 | 0 | 0.089473 | 0 | 0 | 0.60728 | 5.4481 |  | 2004-2013 | 0 | 0 | 6.7561e-05 | 0.072644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072712 |  | 2004-2013 | 19.7898 | 1.5378 | 0.091226 | 7.94 | 0 | 18.4114 | 0 | 7.3987 | 1.9863 | 0.0013506 | 0.533 | 0 | 0.93669 | 0 | 0 | 6.3576 | 64.9839
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.05774% | 21.94% |  | 7.43% |  | 12.64% | 18.54% | 16.43% | 0.005388% |  | -0.01475% | 0% |  | 0% | 5.226% |  | 2004-2007 | 0% | 0% | 0.07502% | 21.94% |  | 7.43% |  | 12.64% | 18.54% | 16.43% | 0.005388% |  | -0.01475% | 0% |  | 0% | 7.388% |  | 2004-2007 | 0% | 0% | 0.0148% |  |  | 7.43% |  | 12.64% | 18.54% | 16.43% | 0.005388% |  | -0.01475% | 0% |  | 0% | 3.739% |  | 2004-2007 |  |  | 0.08969% | 21.94% | [9 empty] | 0% |  |  | 16.23% |  | 2004-2007 | 0% | 0% | 0.05928% | 21.94% |  | 7.43% |  | 12.64% | 18.54% | 16.43% | 0.005388% |  | -0.01475% | 0% |  | 0% | 5.341%
2007-2010 | 33.62% | 46.03% | 3.444% | 27.93% |  | 28.32% |  | 11.1% | 3.263% | -28.22% | 0.0276% |  | 43.53% | 0% |  | 1.082% | 18.9% |  | 2007-2010 | 33.62% | 46.03% | 1.762% | 27.93% |  | 28.32% |  | 11.1% | 3.263% | -28.22% | 0.0276% |  | 43.53% | 0% |  | 1.082% | 18.96% |  | 2007-2010 | 33.62% | 46.03% | 7.62% |  |  | 28.32% |  | 11.1% | 3.263% | -28.22% | 0.0276% |  | 43.53% | 0% |  | 1.081% | 18.85% |  | 2007-2010 |  |  | 0.3332% | 27.93% | [9 empty] | 0% |  |  | 19.27% |  | 2007-2010 | 33.62% | 46.03% | 3.294% | 27.93% |  | 28.32% |  | 11.1% | 3.263% | -28.22% | 0.0276% |  | 43.53% | 0% |  | 1.081% | 18.9%
2010-2013 | 11.99% | 0% | 0.01723% | -3.12% |  | 18.05% |  | 19.05% | 20.96% | 9.228% | 9.93% |  | 10.77% | 0% |  | 13.81% | 12.31% |  | 2010-2013 | 11.99% | 0% | 0.02792% | -3.12% |  | 18.05% |  | 19.05% | 20.96% | 9.228% | 9.93% |  | 10.77% | 0% |  | 13.81% | 9.792% |  | 2010-2013 | 11.99% | 0% | -0.01101% |  |  | 18.05% |  | 19.05% | 20.96% | 9.228% | 9.93% |  | 10.77% | 0% |  | 13.81% | 13.98% |  | 2010-2013 |  |  | 0.03672% | -3.12% | [9 empty] | 0% |  |  | -1.915% |  | 2010-2013 | 11.99% | 0% | 0.0182% | -3.12% |  | 18.05% |  | 19.05% | 20.96% | 9.228% | 9.93% |  | 10.77% | 0% |  | 13.81% | 12.18%
2004-2013 | 41.58% | 46.03% | 3.516% | 41.99% |  | 45.62% |  | 37.13% | 37.71% | 2.739% | 9.96% |  | 49.61% | 0% |  | 14.74% | 32.6% |  | 2004-2013 | 41.58% | 46.03% | 1.863% | 41.99% |  | 45.62% |  | 37.13% | 37.71% | 2.739% | 9.96% |  | 49.61% | 0% |  | 14.75% | 32.3% |  | 2004-2013 | 41.58% | 46.03% | 7.624% |  |  | 45.62% |  | 37.13% | 37.71% | 2.739% | 9.96% |  | 49.61% | 0% |  | 14.74% | 32.8% |  | 2004-2013 |  |  | 0.4592% | 41.99% | [9 empty] | 0% |  |  | 31.07% |  | 2004-2013 | 41.58% | 46.03% | 3.369% | 41.99% |  | 45.62% |  | 37.13% | 37.71% | 2.739% | 9.96% |  | 49.61% | 0% |  | 14.74% | 32.58%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.27365 | 0.017768 | 0.021425 | 0.017312 | 0 | 0.43482 | 0 | 0.13098 | 0.051508 | 6.9768e-05 | 0.048132 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.4713 | 1.275% | CZ 1A | 9.0502 | 0.5876 | 1.484 | 1.7487 | 0 | 14.38 | 0 | 4.3316 | 1.7035 | 0.0023073 | 1.5918 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 53.7204 | 1.275% | CZ 1A | 2.6517 | 0.17217 | 0.097012 | 0 | 0 | 4.2133 | 0 | 1.2692 | 0.49911 | 0.00067604 | 0.4664 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 13.5342 | 1.275% | CZ 1A | 0 | 0 | 0.011529 | 0.017487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.075295 | 1.275% | CZ 1A | 27.7603 | 1.8024 | 2.2757 | 1.9113 | 0 | 44.109 | 0 | 13.2868 | 5.2252 | 0.0070775 | 4.8827 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 149.9189 | 1.275%
CZ 1B | 0.27544 | 0.017764 | 0.021207 | 0.017687 | 0 | 0.39597 | 0 | 0.12177 | 0.04583 | 7.3644e-05 | 0.04716 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.4185 | 0% | CZ 1B | 9.1091 | 0.58747 | 1.4619 | 1.7866 | 0 | 13.0954 | 0 | 4.0272 | 1.5157 | 0.0024355 | 1.5596 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 51.9864 | 0% | CZ 1B | 2.6689 | 0.17213 | 0.097012 | 0 | 0 | 3.8369 | 0 | 1.18 | 0.44409 | 0.0007136 | 0.45697 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 13.0215 | 0% | CZ 1B | 0 | 0 | 0.011308 | 0.017866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.075454 | 0% | CZ 1B | 27.9412 | 1.802 | 2.2516 | 1.9528 | 0 | 40.1688 | 0 | 12.353 | 4.6491 | 0.0074707 | 4.784 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 144.5687 | 0%
CZ 2A | 0.27788 | 0.01776 | 0.022888 | 0.057966 | 0 | 0.31938 | 0 | 0.12428 | 0.038814 | 0.00012016 | 0.047908 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.3826 | 18.69% | CZ 2A | 9.1897 | 0.58735 | 1.6317 | 5.8551 | 0 | 10.5625 | 0 | 4.11 | 1.2836 | 0.0039737 | 1.5844 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 53.6494 | 18.69% | CZ 2A | 2.6926 | 0.17209 | 0.097012 | 0 | 0 | 3.0948 | 0 | 1.2042 | 0.37611 | 0.0011643 | 0.46422 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 12.2669 | 18.69% | CZ 2A | 0 | 0 | 0.013006 | 0.058551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.11784 | 18.69% | CZ 2A | 28.1885 | 1.8016 | 2.4372 | 6.3996 | 0 | 32.3992 | 0 | 12.607 | 3.9375 | 0.012189 | 4.8599 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 141.3015 | 18.69%
CZ 2B | 0.27797 | 0.017752 | 0.022254 | 0.025055 | 0 | 0.35013 | 0 | 0.13214 | 0.034834 | 0.00010465 | 0.047179 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.383 | 3.29% | CZ 2B | 9.1928 | 0.58709 | 1.5677 | 2.5308 | 0 | 11.5793 | 0 | 4.3701 | 1.152 | 0.003461 | 1.5603 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 51.3844 | 3.29% | CZ 2B | 2.6935 | 0.17202 | 0.097012 | 0 | 0 | 3.3927 | 0 | 1.2804 | 0.33753 | 0.0010141 | 0.45716 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 12.596 | 3.29% | CZ 2B | 0 | 0 | 0.012366 | 0.025308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.083953 | 3.29% | CZ 2B | 28.198 | 1.8008 | 2.3672 | 2.7662 | 0 | 35.5181 | 0 | 13.4048 | 3.5336 | 0.010616 | 4.786 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 141.044 | 3.29%
CZ 3A | 0.27991 | 0.017764 | 0.023962 | 0.094957 | 0 | 0.24186 | 0 | 0.1284 | 0.037989 | 0.0002752 | 0.047656 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.3484 | 18.91% | CZ 3A | 9.2569 | 0.58747 | 1.7399 | 9.5916 | 0 | 7.9986 | 0 | 4.2464 | 1.2563 | 0.0091012 | 1.576 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 55.1032 | 18.91% | CZ 3A | 2.7123 | 0.17213 | 0.09705 | 0 | 0 | 2.3436 | 0 | 1.2442 | 0.36811 | 0.0026666 | 0.46178 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 11.5664 | 18.91% | CZ 3A | 0 | 0 | 0.014087 | 0.095916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15628 | 18.91% | CZ 3A | 28.3946 | 1.802 | 2.5557 | 10.4836 | 0 | 24.535 | 0 | 13.0254 | 3.8537 | 0.027917 | 4.8344 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 138.1705 | 18.91%
CZ 3B | 0.27752 | 0.017752 | 0.023623 | 0.053037 | 0 | 0.20218 | 0 | 0.095505 | 0 | 0.00031396 | 0.047163 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.1927 | 8.934% | CZ 3B | 9.1778 | 0.58709 | 1.7057 | 5.3572 | 0 | 6.6863 | 0 | 3.1585 | 0 | 0.010383 | 1.5598 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 47.0837 | 8.934% | CZ 3B | 2.6891 | 0.17202 | 0.09705 | 0 | 0 | 1.9591 | 0 | 0.92543 | 0 | 0.0030422 | 0.45701 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 10.4674 | 8.934% | CZ 3B | 0 | 0 | 0.013745 | 0.053572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.1136 | 8.934% | CZ 3B | 28.152 | 1.8008 | 2.5183 | 5.8555 | 0 | 20.5094 | 0 | 9.6883 | 0 | 0.031849 | 4.7844 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 121.9993 | 8.934%
CZ 3C | 0.27941 | 0.017756 | 0.024781 | 0.063982 | 0 | 0.070261 | 0 | 0.086951 | 0 | 0.00026745 | 0.047156 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.0662 | 0.953% | CZ 3C | 9.2404 | 0.58722 | 1.8227 | 6.4628 | 0 | 2.3236 | 0 | 2.8756 | 0 | 0.0088448 | 1.5595 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 43.7215 | 0.953% | CZ 3C | 2.7074 | 0.17205 | 0.09705 | 0 | 0 | 0.68081 | 0 | 0.84254 | 0 | 0.0025915 | 0.45693 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 9.1241 | 0.953% | CZ 3C | 0 | 0 | 0.014915 | 0.064628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.12582 | 0.953% | CZ 3C | 28.3438 | 1.8012 | 2.6462 | 7.0639 | 0 | 7.1274 | 0 | 8.8205 | 0 | 0.02713 | 4.7836 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 109.2722 | 0.953%
CZ 4A | 0.26855 | 0.01776 | 0.025188 | 0.11707 | 0 | 0.18856 | 0 | 0.13241 | 0.039268 | 0.00049225 | 0.047462 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.3124 | 17.92% | CZ 4A | 8.8815 | 0.58735 | 1.8638 | 11.8253 | 0 | 6.2358 | 0 | 4.3789 | 1.2986 | 0.01628 | 1.5696 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 55.4981 | 17.92% | CZ 4A | 2.6022 | 0.17209 | 0.09705 | 0 | 0 | 1.8271 | 0 | 1.283 | 0.3805 | 0.0047699 | 0.4599 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 10.9913 | 17.92% | CZ 4A | 0 | 0 | 0.015326 | 0.11825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17986 | 17.92% | CZ 4A | 27.2429 | 1.8016 | 2.6911 | 12.9251 | 0 | 19.1277 | 0 | 13.4319 | 3.9835 | 0.049936 | 4.8147 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 134.7268 | 17.92%
CZ 4B | 0.26744 | 0.017748 | 0.024979 | 0.08231 | 0 | 0.1394 | 0 | 0.10465 | 0 | 0.00053489 | 0.047121 | 0 | 0.0093708 | 0.10384 | 0 | 0.36238 | 1.1598 | 0.6023% | CZ 4B | 8.8445 | 0.58696 | 1.8427 | 8.3141 | 0 | 4.6101 | 0 | 3.4609 | 0 | 0.01769 | 1.5584 | 0 | 0.30991 | 6.547 | 0 | 11.9836 | 48.0759 | 0.6023% | CZ 4B | 2.5914 | 0.17198 | 0.09705 | 0 | 0 | 1.3507 | 0 | 1.014 | 0 | 0.005183 | 0.45659 | 0 | 0.090802 | 0.56229 | 0 | 3.5115 | 9.8516 | 0.6023% | CZ 4B | 0 | 0 | 0.015115 | 0.083141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.14454 | 0.6023% | CZ 4B | 27.1297 | 1.8004 | 2.668 | 9.0874 | 0 | 14.1409 | 0 | 10.6159 | 0 | 0.054261 | 4.7801 | 0 | 0.9506 | 10.9449 | 0 | 36.7621 | 118.9341 | 0.6023%
CZ 4C | 0.27211 | 0.017775 | 0.025509 | 0.12028 | 0 | 0.094978 | 0 | 0.081869 | 0 | 0.00082947 | 0.047105 | 0 | 0.0093747 | 0.10384 | 0 | 0.36238 | 1.1361 | 1.875% | CZ 4C | 8.999 | 0.58786 | 1.8963 | 12.149 | 0 | 3.1411 | 0 | 2.7075 | 0 | 0.027432 | 1.5578 | 0 | 0.31003 | 6.547 | 0 | 11.9836 | 49.9067 | 1.875% | CZ 4C | 2.6367 | 0.17224 | 0.09705 | 0 | 0 | 0.92032 | 0 | 0.7933 | 0 | 0.0080374 | 0.45644 | 0 | 0.090839 | 0.56229 | 0 | 3.5115 | 9.2487 | 1.875% | CZ 4C | 0 | 0 | 0.01565 | 0.12149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.18342 | 1.875% | CZ 4C | 27.6035 | 1.8032 | 2.7266 | 13.2789 | 0 | 9.6348 | 0 | 8.3051 | 0 | 0.084144 | 4.7785 | 0 | 0.951 | 10.9449 | 0 | 36.7621 | 116.8726 | 1.875%
CZ 5A | 0.26908 | 0.017818 | 0.026051 | 0.14452 | 0 | 0.15804 | 0 | 0.13374 | 0.039435 | 0.00087598 | 0.047388 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.3126 | 18.43% | CZ 5A | 8.8989 | 0.58927 | 1.951 | 14.5982 | 0 | 5.2266 | 0 | 4.423 | 1.3042 | 0.02897 | 1.5672 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 57.4281 | 18.43% | CZ 5A | 2.6074 | 0.17265 | 0.09705 | 0 | 0 | 1.5314 | 0 | 1.2959 | 0.38212 | 0.0084881 | 0.45919 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 10.7189 | 18.43% | CZ 5A | 0 | 0 | 0.016197 | 0.14598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.20846 | 18.43% | CZ 5A | 27.2964 | 1.8075 | 2.7864 | 15.9558 | 0 | 16.0321 | 0 | 13.5672 | 4.0004 | 0.088862 | 4.8072 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 135.0002 | 18.43%
CZ 5B | 0.27079 | 0.017713 | 0.025886 | 0.13008 | 0 | 0.10648 | 0 | 0.086753 | 0 | 0.001 | 0.047036 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.1614 | 4.478% | CZ 5B | 8.9556 | 0.58581 | 1.9343 | 13.1395 | 0 | 3.5215 | 0 | 2.869 | 0 | 0.033072 | 1.5555 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 51.4352 | 4.478% | CZ 5B | 2.624 | 0.17164 | 0.09705 | 0 | 0 | 1.0318 | 0 | 0.84062 | 0 | 0.00969 | 0.45577 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 9.3952 | 4.478% | CZ 5B | 0 | 0 | 0.016031 | 0.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.19371 | 4.478% | CZ 5B | 27.4702 | 1.7969 | 2.7682 | 14.3615 | 0 | 10.8018 | 0 | 8.8005 | 0 | 0.10144 | 4.7714 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 119.5303 | 4.478%
CZ 5C | 0.28091 | 0.017795 | 0.025866 | 0.093055 | 0 | 0.072559 | 0 | 0.1323 | 0.031093 | 0.000469 | 0.047074 | 0 | 0.0093786 | 0.10384 | 0 | 0.36238 | 1.1767 | 0% | CZ 5C | 9.2901 | 0.5885 | 1.9323 | 9.3995 | 0 | 2.3996 | 0 | 4.3754 | 1.0283 | 0.01551 | 1.5568 | 0 | 0.31016 | 6.547 | 0 | 11.9836 | 49.4268 | 0% | CZ 5C | 2.722 | 0.17243 | 0.09705 | 0 | 0 | 0.70309 | 0 | 1.282 | 0.30129 | 0.0045445 | 0.45614 | 0 | 0.090877 | 0.56229 | 0 | 3.5115 | 9.9032 | 0% | CZ 5C | 0 | 0 | 0.01601 | 0.093995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15628 | 0% | CZ 5C | 28.4964 | 1.8052 | 2.7659 | 10.2736 | 0 | 7.3606 | 0 | 13.4209 | 3.1542 | 0.047577 | 4.7754 | 0 | 0.95139 | 10.9449 | 0 | 36.7621 | 120.7582 | 0%
CZ 6A | 0.27092 | 0.01783 | 0.026783 | 0.17166 | 0 | 0.11087 | 0 | 0.13038 | 0.03783 | 0.0010194 | 0.04726 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.2902 | 3.366% | CZ 6A | 8.9597 | 0.58965 | 2.0249 | 17.3398 | 0 | 3.6666 | 0 | 4.3118 | 1.2511 | 0.033713 | 1.563 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 58.5811 | 3.366% | CZ 6A | 2.6252 | 0.17277 | 0.09705 | 0 | 0 | 1.0743 | 0 | 1.2633 | 0.36657 | 0.0098778 | 0.45795 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 10.2317 | 3.366% | CZ 6A | 0 | 0 | 0.016937 | 0.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23661 | 3.366% | CZ 6A | 27.4827 | 1.8087 | 2.8672 | 18.9524 | 0 | 11.2469 | 0 | 13.2259 | 3.8376 | 0.10341 | 4.7942 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 132.9779 | 3.366%
CZ 6B | 0.27102 | 0.017748 | 0.026876 | 0.13 | 0 | 0.086493 | 0 | 0.1396 | 0.041566 | 0.00099226 | 0.047051 | 0 | 0.0093747 | 0.10384 | 0 | 0.36238 | 1.2369 | 0.7502% | CZ 6B | 8.963 | 0.58696 | 2.0343 | 13.1308 | 0 | 2.8605 | 0 | 4.6167 | 1.3747 | 0.032815 | 1.5561 | 0 | 0.31003 | 6.547 | 0 | 11.9836 | 53.9964 | 0.7502% | CZ 6B | 2.6261 | 0.17198 | 0.09705 | 0 | 0 | 0.83811 | 0 | 1.3527 | 0.40277 | 0.0096148 | 0.45592 | 0 | 0.090839 | 0.56229 | 0 | 3.5115 | 10.1189 | 0.7502% | CZ 6B | 0 | 0 | 0.01703 | 0.13131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.19462 | 0.7502% | CZ 6B | 27.493 | 1.8004 | 2.8774 | 14.352 | 0 | 8.7741 | 0 | 14.1613 | 4.2166 | 0.10066 | 4.773 | 0 | 0.951 | 10.9449 | 0 | 36.7621 | 127.2065 | 0.7502%
CZ 7 | 0.26097 | 0.017787 | 0.027952 | 0.21206 | 0 | 0.084214 | 0 | 0.13739 | 0.039051 | 0.0014303 | 0.047156 | 0 | 0.0093669 | 0.10384 | 0 | 0.36238 | 1.3036 | 0.4665% | CZ 7 | 8.6307 | 0.58824 | 2.1427 | 21.4201 | 0 | 2.7851 | 0 | 4.5437 | 1.2915 | 0.0473 | 1.5595 | 0 | 0.30978 | 6.547 | 0 | 11.9836 | 61.8492 | 0.4665% | CZ 7 | 2.5288 | 0.17235 | 0.097087 | 0 | 0 | 0.81602 | 0 | 1.3313 | 0.3784 | 0.013859 | 0.45693 | 0 | 0.090764 | 0.56229 | 0 | 3.5115 | 9.9593 | 0.4665% | CZ 7 | 0 | 0 | 0.018113 | 0.2142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.27859 | 0.4665% | CZ 7 | 26.4738 | 1.8044 | 2.9962 | 23.4122 | 0 | 8.5429 | 0 | 13.9372 | 3.9614 | 0.14509 | 4.7836 | 0 | 0.95021 | 10.9449 | 0 | 36.7621 | 134.714 | 0.4665%
CZ 8 | 0.27612 | 0.017892 | 0.0293 | 0.38812 | 0 | 0.049059 | 0 | 0.14569 | 0.041911 | 0.0025233 | 0.046942 | 0 | 0.0093825 | 0.10384 | 0 | 0.36238 | 1.4732 | 0.06613% | CZ 8 | 9.1317 | 0.5917 | 2.2787 | 39.2041 | 0 | 1.6224 | 0 | 4.8181 | 1.3861 | 0.083449 | 1.5525 | 0 | 0.31029 | 6.547 | 0 | 11.9836 | 79.5096 | 0.06613% | CZ 8 | 2.6756 | 0.17337 | 0.097125 | 0 | 0 | 0.47537 | 0 | 1.4117 | 0.40611 | 0.02445 | 0.45487 | 0 | 0.090914 | 0.56229 | 0 | 3.5115 | 9.8833 | 0.06613% | CZ 8 | 0 | 0 | 0.019472 | 0.39204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.45779 | 0.06613% | CZ 8 | 28.0104 | 1.815 | 3.1451 | 42.8501 | 0 | 4.9767 | 0 | 14.779 | 4.2516 | 0.25597 | 4.762 | 0 | 0.95178 | 10.9449 | 0 | 36.7621 | 153.5045 | 0.06613%
Us Weighted | 0.27405 | 0.017771 | 0.024515 | 0.099364 | 0 | 0.21633 | 0 | 0.12348 | 0.032338 | 0.00047268 | 0.047498 | 0 | 0.0093797 | 0.10384 | 0 | 0.36238 | 1.3114 | 100% | Us Weighted | 9.0631 | 0.58772 | 1.7959 | 10.0368 | 0 | 7.1542 | 0 | 4.0836 | 1.0695 | 0.015632 | 1.5708 | 0 | 0.3102 | 6.547 | 0 | 11.9836 | 54.2181 | 100% | Us Weighted | 2.6555 | 0.1722 | 0.097041 | 0 | 0 | 2.0962 | 0 | 1.1965 | 0.31335 | 0.0045802 | 0.46025 | 0 | 0.090888 | 0.56229 | 0 | 3.5115 | 11.1602 | 100% | Us Weighted | 0 | 0 | 0.014647 | 0.10037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.16129 | 100% | Us Weighted | 27.8001 | 1.8028 | 2.6168 | 10.9702 | 0 | 21.9447 | 0 | 12.526 | 3.2805 | 0.04795 | 4.8184 | 0 | 0.9515 | 10.9449 | 0 | 36.7621 | 134.4659 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.31521 | 0.017768 | 0.02143 | 0.018395 | 0 | 0.58619 | 0 | 0.17187 | 0.070354 | 8.9148e-05 | 0.053229 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.7893 | 1.275% | CZ 1A | 10.4244 | 0.5876 | 1.4845 | 1.8581 | 0 | 19.3861 | 0 | 5.6841 | 2.3267 | 0.0029483 | 1.7604 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 64.3138 | 1.275% | CZ 1A | 3.0543 | 0.17217 | 0.097012 | 0 | 0 | 5.6801 | 0 | 1.6654 | 0.68172 | 0.00086383 | 0.51579 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 16.6058 | 1.275% | CZ 1A | 0 | 0 | 0.011534 | 0.018581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.076394 | 1.275% | CZ 1A | 31.9758 | 1.8024 | 2.2763 | 2.0309 | 0 | 59.4648 | 0 | 17.4354 | 7.1369 | 0.0090435 | 5.3998 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 182.1957 | 1.275%
CZ 1B | 0.31855 | 0.017764 | 0.021203 | 0.024141 | 0 | 0.46644 | 0 | 0.14925 | 0.048516 | 8.9148e-05 | 0.052559 | 0 | 0.010518 | 0.10384 | 0 | 0.42046 | 1.6333 | 0% | CZ 1B | 10.5351 | 0.58747 | 1.4616 | 2.4385 | 0 | 15.426 | 0 | 4.9359 | 1.6045 | 0.0029483 | 1.7382 | 0 | 0.34785 | 6.547 | 0 | 13.9042 | 59.5292 | 0% | CZ 1B | 3.0867 | 0.17213 | 0.097012 | 0 | 0 | 4.5198 | 0 | 1.4462 | 0.47011 | 0.00086383 | 0.50929 | 0 | 0.10192 | 0.56229 | 0 | 4.0742 | 15.0406 | 0% | CZ 1B | 0 | 0 | 0.011304 | 0.024385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.081969 | 0% | CZ 1B | 32.3151 | 1.802 | 2.2512 | 2.6653 | 0 | 47.3175 | 0 | 15.1404 | 4.9216 | 0.0090435 | 5.3317 | 0 | 1.067 | 10.9449 | 0 | 42.6533 | 166.419 | 0%
CZ 2A | 0.31911 | 0.01776 | 0.022887 | 0.05955 | 0 | 0.39909 | 0 | 0.1496 | 0.043849 | 0.00019768 | 0.053047 | 0 | 0.010514 | 0.10384 | 0 | 0.42046 | 1.5999 | 18.69% | CZ 2A | 10.5535 | 0.58735 | 1.6316 | 6.0152 | 0 | 13.1985 | 0 | 4.9473 | 1.4502 | 0.0065375 | 1.7544 | 0 | 0.34772 | 6.547 | 0 | 13.9042 | 60.9435 | 18.69% | CZ 2A | 3.0922 | 0.17209 | 0.097012 | 0 | 0 | 3.8671 | 0 | 1.4496 | 0.42489 | 0.0019155 | 0.51402 | 0 | 0.10188 | 0.56229 | 0 | 4.0742 | 14.3572 | 18.69% | CZ 2A | 0 | 0 | 0.013005 | 0.060152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.11944 | 18.69% | CZ 2A | 32.3717 | 1.8016 | 2.4371 | 6.5746 | 0 | 40.4849 | 0 | 15.1754 | 4.4482 | 0.020053 | 5.3813 | 0 | 1.0666 | 10.9449 | 0 | 42.6533 | 163.3596 | 18.69%
CZ 2B | 0.32138 | 0.017752 | 0.022252 | 0.031834 | 0 | 0.40472 | 0 | 0.14785 | 0.034876 | 0.00012403 | 0.052578 | 0 | 0.010518 | 0.10384 | 0 | 0.42046 | 1.5682 | 3.29% | CZ 2B | 10.6285 | 0.58709 | 1.5675 | 3.2155 | 0 | 13.3847 | 0 | 4.8895 | 1.1534 | 0.0041019 | 1.7388 | 0 | 0.34785 | 6.547 | 0 | 13.9042 | 57.9684 | 3.29% | CZ 2B | 3.1141 | 0.17202 | 0.097012 | 0 | 0 | 3.9217 | 0 | 1.4326 | 0.33795 | 0.0012019 | 0.50948 | 0 | 0.10192 | 0.56229 | 0 | 4.0742 | 14.3245 | 3.29% | CZ 2B | 0 | 0 | 0.012364 | 0.032155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.090799 | 3.29% | CZ 2B | 32.6017 | 1.8008 | 2.367 | 3.5146 | 0 | 41.0562 | 0 | 14.998 | 3.538 | 0.012582 | 5.3337 | 0 | 1.067 | 10.9449 | 0 | 42.6533 | 159.8879 | 3.29%
CZ 3A | 0.31236 | 0.017764 | 0.023958 | 0.092522 | 0 | 0.29265 | 0 | 0.15107 | 0.040012 | 0.00036047 | 0.052838 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.5183 | 18.91% | CZ 3A | 10.3302 | 0.58747 | 1.7398 | 9.3457 | 0 | 9.6783 | 0 | 4.9962 | 1.3233 | 0.011921 | 1.7474 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 60.559 | 18.91% | CZ 3A | 3.0267 | 0.17213 | 0.097012 | 0 | 0 | 2.8357 | 0 | 1.4639 | 0.38771 | 0.0034929 | 0.51199 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 13.237 | 18.91% | CZ 3A | 0 | 0 | 0.014087 | 0.093457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15382 | 18.91% | CZ 3A | 31.6868 | 1.802 | 2.5553 | 10.2148 | 0 | 29.687 | 0 | 15.3252 | 4.0589 | 0.036567 | 5.3601 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 155.391 | 18.91%
CZ 3B | 0.31202 | 0.017752 | 0.023618 | 0.046612 | 0 | 0.24399 | 0 | 0.15353 | 0.035411 | 0.0001938 | 0.052559 | 0 | 0.010514 | 0.10384 | 0 | 0.42046 | 1.4205 | 8.934% | CZ 3B | 10.3189 | 0.58709 | 1.7054 | 4.7083 | 0 | 8.069 | 0 | 5.0773 | 1.1711 | 0.0064093 | 1.7382 | 0 | 0.34772 | 6.547 | 0 | 13.9042 | 54.1807 | 8.934% | CZ 3B | 3.0234 | 0.17202 | 0.097012 | 0 | 0 | 2.3642 | 0 | 1.4876 | 0.34313 | 0.0018779 | 0.50929 | 0 | 0.10188 | 0.56229 | 0 | 4.0742 | 12.737 | 8.934% | CZ 3B | 0 | 0 | 0.013743 | 0.047083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.10711 | 8.934% | CZ 3B | 31.6522 | 1.8008 | 2.5178 | 5.1461 | 0 | 24.7508 | 0 | 15.5741 | 3.5922 | 0.01966 | 5.3317 | 0 | 1.0666 | 10.9449 | 0 | 42.6533 | 145.0502 | 8.934%
CZ 3C | 0.313 | 0.017756 | 0.024782 | 0.057698 | 0 | 0.12762 | 0 | 0.15003 | 0.029717 | 0.00014341 | 0.052543 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.3081 | 0.953% | CZ 3C | 10.3512 | 0.58722 | 1.8228 | 5.8281 | 0 | 4.2206 | 0 | 4.9618 | 0.9828 | 0.0047429 | 1.7377 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 51.2959 | 0.953% | CZ 3C | 3.0329 | 0.17205 | 0.09705 | 0 | 0 | 1.2366 | 0 | 1.4538 | 0.28796 | 0.0013896 | 0.50914 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 11.5293 | 0.953% | CZ 3C | 0 | 0 | 0.014916 | 0.058281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.11948 | 0.953% | CZ 3C | 31.7513 | 1.8012 | 2.6463 | 6.3701 | 0 | 12.9463 | 0 | 15.2198 | 3.0146 | 0.014548 | 5.3302 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 133.7587 | 0.953%
CZ 4A | 0.30672 | 0.01776 | 0.025196 | 0.11209 | 0 | 0.22296 | 0 | 0.1555 | 0.042322 | 0.0005814 | 0.052683 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.4706 | 17.92% | CZ 4A | 10.1437 | 0.58735 | 1.8646 | 11.3226 | 0 | 7.3735 | 0 | 5.1427 | 1.3997 | 0.019228 | 1.7423 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 60.3944 | 17.92% | CZ 4A | 2.9721 | 0.17209 | 0.09705 | 0 | 0 | 2.1604 | 0 | 1.5068 | 0.4101 | 0.0056337 | 0.51049 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 12.573 | 17.92% | CZ 4A | 0 | 0 | 0.015334 | 0.11323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17484 | 17.92% | CZ 4A | 31.1147 | 1.8016 | 2.692 | 12.3756 | 0 | 22.6173 | 0 | 15.7746 | 4.2933 | 0.058979 | 5.3443 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 150.7368 | 17.92%
CZ 4B | 0.30683 | 0.017748 | 0.024989 | 0.067542 | 0 | 0.19308 | 0 | 0.16467 | 0.033311 | 0.00033721 | 0.052508 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.3958 | 0.6023% | CZ 4B | 10.1473 | 0.58696 | 1.844 | 6.8224 | 0 | 6.3856 | 0 | 5.446 | 1.1016 | 0.011152 | 1.7365 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 54.8803 | 0.6023% | CZ 4B | 2.9731 | 0.17198 | 0.097012 | 0 | 0 | 1.871 | 0 | 1.5957 | 0.32277 | 0.0032675 | 0.5088 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 12.2819 | 0.6023% | CZ 4B | 0 | 0 | 0.015129 | 0.068224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.12963 | 0.6023% | CZ 4B | 31.1257 | 1.8004 | 2.6692 | 7.4569 | 0 | 19.587 | 0 | 16.7049 | 3.3791 | 0.034208 | 5.3266 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 142.7484 | 0.6023%
CZ 4C | 0.30864 | 0.017775 | 0.025523 | 0.096983 | 0 | 0.14041 | 0 | 0.15495 | 0.035442 | 0.00044962 | 0.052489 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.3675 | 1.875% | CZ 4C | 10.2072 | 0.58786 | 1.8977 | 9.7963 | 0 | 4.6435 | 0 | 5.1245 | 1.1721 | 0.01487 | 1.7359 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 55.9786 | 1.875% | CZ 4C | 2.9907 | 0.17224 | 0.09705 | 0 | 0 | 1.3605 | 0 | 1.5015 | 0.34343 | 0.0043567 | 0.50861 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 11.7167 | 1.875% | CZ 4C | 0 | 0 | 0.015664 | 0.097963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15991 | 1.875% | CZ 4C | 31.3093 | 1.8032 | 2.7281 | 10.7073 | 0 | 14.2435 | 0 | 15.7187 | 3.5954 | 0.045611 | 5.3247 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 140.1402 | 1.875%
CZ 5A | 0.30671 | 0.017818 | 0.026066 | 0.14506 | 0 | 0.18711 | 0 | 0.15499 | 0.042097 | 0.0010426 | 0.052621 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.4683 | 18.43% | CZ 5A | 10.1433 | 0.58927 | 1.9525 | 14.6521 | 0 | 6.1879 | 0 | 5.1256 | 1.3922 | 0.034482 | 1.7403 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 62.6166 | 18.43% | CZ 5A | 2.972 | 0.17265 | 0.09705 | 0 | 0 | 1.813 | 0 | 1.5018 | 0.40792 | 0.010103 | 0.50989 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 12.2228 | 18.43% | CZ 5A | 0 | 0 | 0.016213 | 0.14652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.20901 | 18.43% | CZ 5A | 31.1135 | 1.8075 | 2.7881 | 16.0148 | 0 | 18.9807 | 0 | 15.7223 | 4.2705 | 0.10577 | 5.338 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 150.8056 | 18.43%
CZ 5B | 0.30842 | 0.017713 | 0.025899 | 0.096333 | 0 | 0.14014 | 0 | 0.14456 | 0.034489 | 0.0005659 | 0.052427 | 0 | 0.010506 | 0.10384 | 0 | 0.42046 | 1.3554 | 4.478% | CZ 5B | 10.1998 | 0.58581 | 1.9356 | 9.7306 | 0 | 4.6345 | 0 | 4.7808 | 1.1406 | 0.018715 | 1.7338 | 0 | 0.34746 | 6.547 | 0 | 13.9042 | 55.5591 | 4.478% | CZ 5B | 2.9885 | 0.17164 | 0.09705 | 0 | 0 | 1.3579 | 0 | 1.4008 | 0.33419 | 0.0054835 | 0.50801 | 0 | 0.10181 | 0.56229 | 0 | 4.0742 | 11.6019 | 4.478% | CZ 5B | 0 | 0 | 0.016044 | 0.097306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15963 | 4.478% | CZ 5B | 31.2869 | 1.7969 | 2.7696 | 10.6356 | 0 | 14.216 | 0 | 14.6646 | 3.4986 | 0.057406 | 5.3184 | 0 | 1.0658 | 10.9449 | 0 | 42.6533 | 138.9079 | 4.478%
CZ 5C | 0.31428 | 0.017795 | 0.025879 | 0.10997 | 0 | 0.083238 | 0 | 0.16508 | 0.033462 | 0.00052326 | 0.052458 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.3375 | 0% | CZ 5C | 10.3938 | 0.5885 | 1.9335 | 11.1083 | 0 | 2.7528 | 0 | 5.4595 | 1.1066 | 0.017305 | 1.7349 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 55.8941 | 0% | CZ 5C | 3.0454 | 0.17243 | 0.09705 | 0 | 0 | 0.80656 | 0 | 1.5996 | 0.32424 | 0.0050703 | 0.50831 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 11.297 | 0% | CZ 5C | 0 | 0 | 0.016023 | 0.11108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17339 | 0% | CZ 5C | 31.8818 | 1.8052 | 2.7673 | 12.1414 | 0 | 8.4439 | 0 | 16.7466 | 3.3945 | 0.053081 | 5.3215 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 137.2195 | 0%
CZ 6A | 0.30788 | 0.01783 | 0.026795 | 0.17331 | 0 | 0.13366 | 0 | 0.15122 | 0.040849 | 0.0012442 | 0.052516 | 0 | 0.010514 | 0.10384 | 0 | 0.42046 | 1.4401 | 3.366% | CZ 6A | 10.1819 | 0.58965 | 2.0261 | 17.5056 | 0 | 4.4205 | 0 | 5.0009 | 1.3509 | 0.041148 | 1.7368 | 0 | 0.34772 | 6.547 | 0 | 13.9042 | 63.6525 | 3.366% | CZ 6A | 2.9833 | 0.17277 | 0.09705 | 0 | 0 | 1.2952 | 0 | 1.4653 | 0.39582 | 0.012056 | 0.50888 | 0 | 0.10188 | 0.56229 | 0 | 4.0742 | 11.6687 | 3.366% | CZ 6A | 0 | 0 | 0.016948 | 0.17506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23828 | 3.366% | CZ 6A | 31.2319 | 1.8087 | 2.8685 | 19.1337 | 0 | 13.5593 | 0 | 15.3397 | 4.1439 | 0.12622 | 5.3274 | 0 | 1.0666 | 10.9449 | 0 | 42.6533 | 148.204 | 3.366%
CZ 6B | 0.30862 | 0.017748 | 0.026885 | 0.14995 | 0 | 0.10078 | 0 | 0.14453 | 0.04119 | 0.0010194 | 0.052423 | 0 | 0.01051 | 0.10384 | 0 | 0.42046 | 1.378 | 0.7502% | CZ 6B | 10.2066 | 0.58696 | 2.0352 | 15.147 | 0 | 3.333 | 0 | 4.7797 | 1.3622 | 0.033713 | 1.7337 | 0 | 0.34759 | 6.547 | 0 | 13.9042 | 60.0168 | 0.7502% | CZ 6B | 2.9905 | 0.17198 | 0.09705 | 0 | 0 | 0.97655 | 0 | 1.4004 | 0.39913 | 0.0098778 | 0.50797 | 0 | 0.10184 | 0.56229 | 0 | 4.0742 | 11.2919 | 0.7502% | CZ 6B | 0 | 0 | 0.017039 | 0.15147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.21479 | 0.7502% | CZ 6B | 31.3077 | 1.8004 | 2.8784 | 16.5556 | 0 | 10.2235 | 0 | 14.6611 | 4.1785 | 0.10341 | 5.318 | 0 | 1.0662 | 10.9449 | 0 | 42.6533 | 141.691 | 0.7502%
CZ 7 | 0.30616 | 0.017787 | 0.027971 | 0.24296 | 0 | 0.09666 | 0 | 0.15769 | 0.042706 | 0.0017093 | 0.052512 | 0 | 0.010506 | 0.10384 | 0 | 0.42046 | 1.481 | 0.4665% | CZ 7 | 10.1251 | 0.58824 | 2.1446 | 24.5412 | 0 | 3.1967 | 0 | 5.2151 | 1.4123 | 0.05653 | 1.7367 | 0 | 0.34746 | 6.547 | 0 | 13.9042 | 69.8152 | 0.4665% | CZ 7 | 2.9666 | 0.17235 | 0.097087 | 0 | 0 | 0.93662 | 0 | 1.528 | 0.41381 | 0.016563 | 0.50884 | 0 | 0.10181 | 0.56229 | 0 | 4.0742 | 11.3783 | 0.4665% | CZ 7 | 0 | 0 | 0.018133 | 0.24541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.30982 | 0.4665% | CZ 7 | 31.0577 | 1.8044 | 2.9983 | 26.8235 | 0 | 9.8055 | 0 | 15.9967 | 4.3322 | 0.1734 | 5.327 | 0 | 1.0658 | 10.9449 | 0 | 42.6533 | 152.9827 | 0.4665%
CZ 8 | 0.31764 | 0.017892 | 0.02933 | 0.44308 | 0 | 0.056102 | 0 | 0.1672 | 0.043586 | 0.0032248 | 0.052299 | 0 | 0.010514 | 0.10384 | 0 | 0.42046 | 1.6652 | 0.06613% | CZ 8 | 10.5049 | 0.5917 | 2.2816 | 44.7556 | 0 | 1.8554 | 0 | 5.5295 | 1.4414 | 0.10665 | 1.7296 | 0 | 0.34772 | 6.547 | 0 | 13.9042 | 89.5954 | 0.06613% | CZ 8 | 3.0779 | 0.17337 | 0.097125 | 0 | 0 | 0.54361 | 0 | 1.6201 | 0.42234 | 0.031248 | 0.50677 | 0 | 0.10188 | 0.56229 | 0 | 4.0742 | 11.2109 | 0.06613% | CZ 8 | 0 | 0 | 0.019501 | 0.44756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.51334 | 0.06613% | CZ 8 | 32.2227 | 1.815 | 3.1483 | 48.9179 | 0 | 5.6911 | 0 | 16.9612 | 4.4215 | 0.32714 | 5.3054 | 0 | 1.0666 | 10.9449 | 0 | 42.6533 | 173.475 | 0.06613%
Us Weighted | 0.3114 | 0.017771 | 0.024519 | 0.096358 | 0 | 0.26397 | 0 | 0.15254 | 0.040915 | 0.00052073 | 0.052735 | 0 | 0.010512 | 0.10384 | 0 | 0.42046 | 1.4955 | 100% | Us Weighted | 10.2983 | 0.58772 | 1.7964 | 9.7332 | 0 | 8.73 | 0 | 5.0447 | 1.3531 | 0.017221 | 1.744 | 0 | 0.34763 | 6.547 | 0 | 13.9042 | 60.1035 | 100% | Us Weighted | 3.0174 | 0.1722 | 0.097031 | 0 | 0 | 2.5579 | 0 | 1.4781 | 0.39646 | 0.0050458 | 0.511 | 0 | 0.10186 | 0.56229 | 0 | 4.0742 | 12.9734 | 100% | Us Weighted | 0 | 0 | 0.014652 | 0.097332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15826 | 100% | Us Weighted | 31.5889 | 1.8028 | 2.6173 | 10.6383 | 0 | 26.7783 | 0 | 15.4741 | 4.1505 | 0.052825 | 5.3496 | 0 | 1.0663 | 10.9449 | 0 | 42.6533 | 153.1171 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.46913 | 0.032969 | 0.022298 | 0.020684 | 0 | 0.76431 | 0 | 0.20149 | 0.053431 | 7.3644e-05 | 0.053489 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 2.1654 | 1.275% | CZ 1A | 15.5148 | 1.0903 | 1.5165 | 2.0893 | 0 | 25.2769 | 0 | 6.6635 | 1.767 | 0.0024355 | 1.769 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 76.9088 | 1.275% | CZ 1A | 4.5458 | 0.31947 | 0.10494 | 0 | 0 | 7.4061 | 0 | 1.9524 | 0.51774 | 0.0007136 | 0.5183 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 20.2269 | 1.275% | CZ 1A | 0 | 0 | 0.011584 | 0.020893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.078756 | 1.275% | CZ 1A | 47.5899 | 3.3445 | 2.3647 | 2.2836 | 0 | 77.5341 | 0 | 20.4394 | 5.4202 | 0.0074707 | 5.4261 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 220.3633 | 1.275%
CZ 1B | 0.46913 | 0.032966 | 0.022069 | 0.033167 | 0 | 0.71538 | 0 | 0.20255 | 0 | 9.3025e-05 | 0.05266 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 2.0755 | 0% | CZ 1B | 15.5148 | 1.0902 | 1.4935 | 3.3502 | 0 | 23.6586 | 0 | 6.6985 | 0 | 0.0030765 | 1.7415 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 74.7691 | 0% | CZ 1B | 4.5458 | 0.31943 | 0.10494 | 0 | 0 | 6.9319 | 0 | 1.9626 | 0 | 0.00090139 | 0.51027 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 19.2373 | 0% | CZ 1B | 0 | 0 | 0.011353 | 0.033502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.091135 | 0% | CZ 1B | 47.5899 | 3.3441 | 2.3395 | 3.6618 | 0 | 72.57 | 0 | 20.5468 | 0 | 0.0094367 | 5.342 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 211.356 | 0%
CZ 2A | 0.46913 | 0.032958 | 0.023755 | 0.069417 | 0 | 0.57879 | 0 | 0.18227 | 0.050202 | 0.00014729 | 0.053195 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 2.0074 | 18.69% | CZ 2A | 15.5148 | 1.09 | 1.6635 | 7.0118 | 0 | 19.1414 | 0 | 6.0281 | 1.6603 | 0.004871 | 1.7592 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 75.0929 | 18.69% | CZ 2A | 4.5458 | 0.31936 | 0.10497 | 0 | 0 | 5.6084 | 0 | 1.7662 | 0.48645 | 0.0014272 | 0.51545 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 18.2095 | 18.69% | CZ 2A | 0 | 0 | 0.013053 | 0.070118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.12945 | 18.69% | CZ 2A | 47.5899 | 3.3433 | 2.5256 | 7.6639 | 0 | 58.7142 | 0 | 18.4904 | 5.0927 | 0.014941 | 5.3962 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 204.7841 | 18.69%
CZ 2B | 0.46913 | 0.03295 | 0.023119 | 0.050974 | 0 | 0.53736 | 0 | 0.18192 | 0.024756 | 0.00010853 | 0.052714 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.9205 | 3.29% | CZ 2B | 15.5148 | 1.0897 | 1.5992 | 5.1489 | 0 | 17.7711 | 0 | 6.0165 | 0.81872 | 0.0035892 | 1.7433 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 70.9247 | 3.29% | CZ 2B | 4.5458 | 0.31928 | 0.10497 | 0 | 0 | 5.2069 | 0 | 1.7628 | 0.23988 | 0.0010516 | 0.51079 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 17.5529 | 3.29% | CZ 2B | 0 | 0 | 0.012409 | 0.051489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.11018 | 3.29% | CZ 2B | 47.5899 | 3.3425 | 2.4553 | 5.6277 | 0 | 54.5109 | 0 | 18.455 | 2.5113 | 0.011009 | 5.3475 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 195.8041 | 3.29%
CZ 3A | 0.46913 | 0.032935 | 0.02483 | 0.11044 | 0 | 0.43135 | 0 | 0.17636 | 0.049008 | 0.0002907 | 0.052869 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.8947 | 18.91% | CZ 3A | 15.5148 | 1.0892 | 1.7718 | 11.156 | 0 | 14.2654 | 0 | 5.8324 | 1.6208 | 0.0096139 | 1.7485 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 74.2274 | 18.91% | CZ 3A | 4.5458 | 0.31913 | 0.10501 | 0 | 0 | 4.1797 | 0 | 1.7089 | 0.47488 | 0.0028169 | 0.51229 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 16.71 | 18.91% | CZ 3A | 0 | 0 | 0.014134 | 0.11156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17197 | 18.91% | CZ 3A | 47.5899 | 3.341 | 2.6442 | 12.1935 | 0 | 43.7575 | 0 | 17.8904 | 4.9716 | 0.02949 | 5.3632 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 193.7336 | 18.91%
CZ 3B | 0.46913 | 0.03295 | 0.024481 | 0.075871 | 0 | 0.32361 | 0 | 0.16707 | 0.035481 | 0.00013954 | 0.052601 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 1.7289 | 8.934% | CZ 3B | 15.5148 | 1.0897 | 1.7366 | 7.6638 | 0 | 10.7023 | 0 | 5.5252 | 1.1734 | 0.0046147 | 1.7396 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 66.369 | 8.934% | CZ 3B | 4.5458 | 0.31928 | 0.10501 | 0 | 0 | 3.1358 | 0 | 1.6189 | 0.34381 | 0.0013521 | 0.5097 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 15.4411 | 8.934% | CZ 3B | 0 | 0 | 0.013782 | 0.076638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.1367 | 8.934% | CZ 3B | 47.5899 | 3.3425 | 2.6057 | 8.3765 | 0 | 32.8282 | 0 | 16.9479 | 3.5993 | 0.014155 | 5.3361 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 176.5936 | 8.934%
CZ 3C | 0.46913 | 0.032935 | 0.025651 | 0.11126 | 0 | 0.13909 | 0 | 0.12831 | 0 | 0.00018993 | 0.052675 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.5067 | 0.953% | CZ 3C | 15.5148 | 1.0892 | 1.8545 | 11.238 | 0 | 4.5998 | 0 | 4.2433 | 0 | 0.0062811 | 1.742 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 61.5068 | 0.953% | CZ 3C | 4.5458 | 0.31913 | 0.10505 | 0 | 0 | 1.3477 | 0 | 1.2433 | 0 | 0.0018403 | 0.51042 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 12.9347 | 0.953% | CZ 3C | 0 | 0 | 0.014959 | 0.11238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17362 | 0.953% | CZ 3C | 47.5899 | 3.341 | 2.7348 | 12.2831 | 0 | 14.1094 | 0 | 13.0159 | 0 | 0.019267 | 5.3435 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 154.3899 | 0.953%
CZ 4A | 0.46913 | 0.032915 | 0.026075 | 0.15692 | 0 | 0.31578 | 0 | 0.16329 | 0.04645 | 0.00042249 | 0.05264 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 1.8111 | 17.92% | CZ 4A | 15.5148 | 1.0886 | 1.8973 | 15.85 | 0 | 10.4434 | 0 | 5.4003 | 1.5362 | 0.013972 | 1.7409 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 74.7044 | 17.92% | CZ 4A | 4.5458 | 0.31894 | 0.10505 | 0 | 0 | 3.0599 | 0 | 1.5823 | 0.4501 | 0.0040938 | 0.51008 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 15.4377 | 17.92% | CZ 4A | 0 | 0 | 0.015387 | 0.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.22017 | 17.92% | CZ 4A | 47.5899 | 3.339 | 2.7816 | 17.3241 | 0 | 32.034 | 0 | 16.5649 | 4.712 | 0.042858 | 5.34 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 185.6817 | 17.92%
CZ 4B | 0.46913 | 0.032923 | 0.025869 | 0.10977 | 0 | 0.2531 | 0 | 0.17331 | 0.03538 | 0.00025969 | 0.052446 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 1.6997 | 0.6023% | CZ 4B | 15.5148 | 1.0888 | 1.8765 | 11.0875 | 0 | 8.3703 | 0 | 5.7317 | 1.1701 | 0.0085884 | 1.7345 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 67.8015 | 0.6023% | CZ 4B | 4.5458 | 0.31902 | 0.10505 | 0 | 0 | 2.4525 | 0 | 1.6794 | 0.34283 | 0.0025164 | 0.5082 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 14.8167 | 0.6023% | CZ 4B | 0 | 0 | 0.01518 | 0.11088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.17233 | 0.6023% | CZ 4B | 47.5899 | 3.3398 | 2.7589 | 12.1187 | 0 | 25.6748 | 0 | 17.5813 | 3.5891 | 0.026344 | 5.3203 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 173.9517 | 0.6023%
CZ 4C | 0.46913 | 0.0329 | 0.0264 | 0.17581 | 0 | 0.18546 | 0 | 0.1644 | 0.035489 | 0.00037597 | 0.052512 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.69 | 1.875% | CZ 4C | 15.5148 | 1.088 | 1.9298 | 17.7582 | 0 | 6.1335 | 0 | 5.437 | 1.1737 | 0.012434 | 1.7367 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 72.0031 | 1.875% | CZ 4C | 4.5458 | 0.31879 | 0.10509 | 0 | 0 | 1.7971 | 0 | 1.593 | 0.34388 | 0.0036431 | 0.50884 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 14.0776 | 1.875% | CZ 4C | 0 | 0 | 0.015712 | 0.17758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23957 | 1.875% | CZ 4C | 47.5899 | 3.3374 | 2.8175 | 19.4097 | 0 | 18.814 | 0 | 16.6774 | 3.6001 | 0.03814 | 5.327 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 173.564 | 1.875%
CZ 5A | 0.46913 | 0.032919 | 0.026948 | 0.20923 | 0 | 0.23527 | 0 | 0.16963 | 0.035489 | 0.00082947 | 0.052551 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7795 | 18.43% | CZ 5A | 15.5148 | 1.0887 | 1.9852 | 21.1342 | 0 | 7.7807 | 0 | 5.6098 | 1.1737 | 0.027432 | 1.7379 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 77.2713 | 18.43% | CZ 5A | 4.5458 | 0.31898 | 0.10509 | 0 | 0 | 2.2797 | 0 | 1.6437 | 0.34388 | 0.0080374 | 0.50921 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 14.6158 | 18.43% | CZ 5A | 0 | 0 | 0.016265 | 0.21134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.27389 | 18.43% | CZ 5A | 47.5899 | 3.3394 | 2.878 | 23.0997 | 0 | 23.8665 | 0 | 17.2074 | 3.6001 | 0.084144 | 5.331 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 182.949 | 18.43%
CZ 5B | 0.46913 | 0.032888 | 0.02678 | 0.16982 | 0 | 0.1894 | 0 | 0.15703 | 0.035473 | 0.00043799 | 0.052315 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.6808 | 4.478% | CZ 5B | 15.5148 | 1.0877 | 1.9683 | 17.1537 | 0 | 6.2637 | 0 | 5.193 | 1.1732 | 0.014485 | 1.7301 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 71.3178 | 4.478% | CZ 5B | 4.5458 | 0.31868 | 0.10509 | 0 | 0 | 1.8352 | 0 | 1.5215 | 0.34373 | 0.0042441 | 0.50692 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 14.0427 | 4.478% | CZ 5B | 0 | 0 | 0.016096 | 0.17154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23391 | 4.478% | CZ 5B | 47.5899 | 3.3363 | 2.8595 | 18.749 | 0 | 19.2131 | 0 | 15.9291 | 3.5985 | 0.044431 | 5.307 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 172.5797 | 4.478%
CZ 5C | 0.46913 | 0.032865 | 0.026754 | 0.215 | 0 | 0.13229 | 0 | 0.18016 | 0.035489 | 0.00053101 | 0.052431 | 0 | 0.018607 | 0.10384 | 0 | 0.42505 | 1.6922 | 0% | CZ 5C | 15.5148 | 1.0869 | 1.9653 | 21.7176 | 0 | 4.3751 | 0 | 5.9582 | 1.1737 | 0.017561 | 1.734 | 0 | 0.61537 | 6.547 | 0 | 14.0563 | 74.7617 | 0% | CZ 5C | 4.5458 | 0.31845 | 0.10512 | 0 | 0 | 1.2819 | 0 | 1.7457 | 0.34388 | 0.0051454 | 0.50805 | 0 | 0.1803 | 0.56229 | 0 | 4.1188 | 13.7155 | 0% | CZ 5C | 0 | 0 | 0.016065 | 0.21718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.27952 | 0% | CZ 5C | 47.5899 | 3.3339 | 2.8565 | 23.7373 | 0 | 13.4201 | 0 | 18.2761 | 3.6001 | 0.053868 | 5.3188 | 0 | 1.8876 | 10.9449 | 0 | 43.1196 | 174.1387 | 0%
CZ 6A | 0.46913 | 0.0329 | 0.027677 | 0.24821 | 0 | 0.17052 | 0 | 0.16906 | 0.035489 | 0.001 | 0.052404 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7539 | 3.366% | CZ 6A | 15.5148 | 1.088 | 2.0586 | 25.0716 | 0 | 5.6393 | 0 | 5.5912 | 1.1737 | 0.033072 | 1.7331 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 79.1223 | 3.366% | CZ 6A | 4.5458 | 0.31879 | 0.10512 | 0 | 0 | 1.6523 | 0 | 1.6382 | 0.34388 | 0.00969 | 0.50779 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.983 | 3.366% | CZ 6A | 0 | 0 | 0.016998 | 0.25072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.31399 | 3.366% | CZ 6A | 47.5899 | 3.3374 | 2.9585 | 27.4033 | 0 | 17.2978 | 0 | 17.1504 | 3.6001 | 0.10144 | 5.316 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 180.7078 | 3.366%
CZ 6B | 0.46913 | 0.032888 | 0.027766 | 0.2183 | 0 | 0.13884 | 0 | 0.15784 | 0.035473 | 0.0007752 | 0.052241 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 1.6808 | 0.7502% | CZ 6B | 15.5148 | 1.0877 | 2.0676 | 22.0508 | 0 | 4.5916 | 0 | 5.2201 | 1.1732 | 0.025637 | 1.7277 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 74.6778 | 0.7502% | CZ 6B | 4.5458 | 0.31868 | 0.10512 | 0 | 0 | 1.3453 | 0 | 1.5295 | 0.34373 | 0.0075116 | 0.50621 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 13.5633 | 0.7502% | CZ 6B | 0 | 0 | 0.017088 | 0.22051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.28387 | 0.7502% | CZ 6B | 47.5899 | 3.3363 | 2.9683 | 24.1015 | 0 | 14.0842 | 0 | 16.0121 | 3.5985 | 0.078639 | 5.2995 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 173.0214 | 0.7502%
CZ 7 | 0.46913 | 0.032876 | 0.028854 | 0.31702 | 0 | 0.12903 | 0 | 0.17172 | 0.035489 | 0.0014419 | 0.052307 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 1.7854 | 0.4665% | CZ 7 | 15.5148 | 1.0873 | 2.1772 | 32.0222 | 0 | 4.2673 | 0 | 5.6789 | 1.1737 | 0.047685 | 1.7299 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 84.9176 | 0.4665% | CZ 7 | 4.5458 | 0.31857 | 0.10516 | 0 | 0 | 1.2503 | 0 | 1.6639 | 0.34388 | 0.013972 | 0.50685 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 13.6098 | 0.4665% | CZ 7 | 0 | 0 | 0.018183 | 0.32022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.38468 | 0.4665% | CZ 7 | 47.5899 | 3.3351 | 3.0883 | 35.0003 | 0 | 13.0895 | 0 | 17.4193 | 3.6001 | 0.14627 | 5.3062 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 184.5274 | 0.4665%
CZ 8 | 0.46913 | 0.032667 | 0.030218 | 0.55482 | 0 | 0.086358 | 0 | 0.17527 | 0.035489 | 0.002845 | 0.052152 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 1.9865 | 0.06613% | CZ 8 | 15.5148 | 1.0803 | 2.3144 | 56.0423 | 0 | 2.856 | 0 | 5.7963 | 1.1737 | 0.094088 | 1.7247 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 107.8157 | 0.06613% | CZ 8 | 4.5458 | 0.31654 | 0.10524 | 0 | 0 | 0.83679 | 0 | 1.6983 | 0.34388 | 0.027568 | 0.50534 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 13.2409 | 0.06613% | CZ 8 | 0 | 0 | 0.019553 | 0.56042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.62625 | 0.06613% | CZ 8 | 47.5899 | 3.3138 | 3.2388 | 61.2542 | 0 | 8.7604 | 0 | 17.7795 | 3.6001 | 0.2886 | 5.2905 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 207.0691 | 0.06613%
Us Weighted | 0.46913 | 0.03293 | 0.025394 | 0.13371 | 0 | 0.36826 | 0 | 0.17158 | 0.042295 | 0.00040613 | 0.05275 | 0 | 0.018616 | 0.10384 | 0 | 0.42505 | 1.844 | 100% | Us Weighted | 15.5148 | 1.089 | 1.8286 | 13.5057 | 0 | 12.179 | 0 | 5.6745 | 1.3988 | 0.013431 | 1.7445 | 0 | 0.61566 | 6.547 | 0 | 14.0563 | 74.1673 | 100% | Us Weighted | 4.5458 | 0.31909 | 0.10503 | 0 | 0 | 3.5684 | 0 | 1.6626 | 0.40983 | 0.0039353 | 0.51114 | 0 | 0.18039 | 0.56229 | 0 | 4.1188 | 15.9873 | 100% | Us Weighted | 0 | 0 | 0.014701 | 0.13506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.19604 | 100% | Us Weighted | 47.5899 | 3.3405 | 2.7064 | 14.7617 | 0 | 37.3577 | 0 | 17.4059 | 4.2905 | 0.041199 | 5.3511 | 0 | 1.8885 | 10.9449 | 0 | 43.1196 | 188.7981 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.46913 | 0.032969 | 0.0223 | 0.022238 | 0 | 0.80481 | 0 | 0.23564 | 0.068501 | 7.752e-05 | 0.053489 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 2.2567 | 1.275% | CZ 1A | 15.5148 | 1.0903 | 1.5168 | 2.2463 | 0 | 26.6162 | 0 | 7.793 | 2.2654 | 0.0025637 | 1.769 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 80.0333 | 1.275% | CZ 1A | 4.5458 | 0.31947 | 0.10494 | 0 | 0 | 7.7985 | 0 | 2.2833 | 0.66376 | 0.00075116 | 0.5183 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 21.0963 | 1.275% | CZ 1A | 0 | 0 | 0.011586 | 0.022463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.080329 | 1.275% | CZ 1A | 47.5899 | 3.3445 | 2.365 | 2.4552 | 0 | 81.6422 | 0 | 23.9043 | 6.9489 | 0.0078639 | 5.4261 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 229.6369 | 1.275%
CZ 1B | 0.46913 | 0.032966 | 0.022071 | 0.034526 | 0 | 0.74958 | 0 | 0.23322 | 0.014485 | 9.3025e-05 | 0.052656 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 2.1562 | 0% | CZ 1B | 15.5148 | 1.0902 | 1.4936 | 3.4875 | 0 | 24.7895 | 0 | 7.713 | 0.47903 | 0.0030765 | 1.7414 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 77.5311 | 0% | CZ 1B | 4.5458 | 0.31943 | 0.10494 | 0 | 0 | 7.2633 | 0 | 2.2599 | 0.14035 | 0.00090139 | 0.51023 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 20.0063 | 0% | CZ 1B | 0 | 0 | 0.011354 | 0.034875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.092508 | 0% | CZ 1B | 47.5899 | 3.3441 | 2.3396 | 3.8118 | 0 | 76.0391 | 0 | 23.6589 | 1.4694 | 0.0094367 | 5.3416 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 219.5568 | 0%
CZ 2A | 0.46913 | 0.032958 | 0.023766 | 0.078387 | 0 | 0.62635 | 0 | 0.2086 | 0.064842 | 0.00017442 | 0.053198 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 2.1049 | 18.69% | CZ 2A | 15.5148 | 1.09 | 1.6646 | 7.9179 | 0 | 20.7141 | 0 | 6.8987 | 2.1444 | 0.0057683 | 1.7594 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 78.9283 | 18.69% | CZ 2A | 4.5458 | 0.31936 | 0.10497 | 0 | 0 | 6.0692 | 0 | 2.0213 | 0.62831 | 0.0016901 | 0.51549 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 19.0675 | 18.69% | CZ 2A | 0 | 0 | 0.013063 | 0.079179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.13852 | 18.69% | CZ 2A | 47.5899 | 3.3433 | 2.5267 | 8.6543 | 0 | 63.5383 | 0 | 21.161 | 6.5778 | 0.017694 | 5.3966 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 214.7581 | 18.69%
CZ 2B | 0.46913 | 0.03295 | 0.023126 | 0.062281 | 0 | 0.6189 | 0 | 0.2164 | 0.0076823 | 0.00014729 | 0.052714 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 2.0308 | 3.29% | CZ 2B | 15.5148 | 1.0897 | 1.6 | 6.291 | 0 | 20.468 | 0 | 7.1566 | 0.25406 | 0.004871 | 1.7433 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 75.3412 | 3.29% | CZ 2B | 4.5458 | 0.31928 | 0.10497 | 0 | 0 | 5.9971 | 0 | 2.0969 | 0.07444 | 0.0014272 | 0.51079 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 18.5121 | 3.29% | CZ 2B | 0 | 0 | 0.012417 | 0.06291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.12161 | 3.29% | CZ 2B | 47.5899 | 3.3425 | 2.4561 | 6.876 | 0 | 62.7834 | 0 | 21.9521 | 0.77931 | 0.014941 | 5.3475 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 207.0947 | 3.29%
CZ 3A | 0.46913 | 0.032935 | 0.024842 | 0.13174 | 0 | 0.46848 | 0 | 0.20298 | 0.063838 | 0.00034884 | 0.052869 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 1.9947 | 18.91% | CZ 3A | 15.5148 | 1.0892 | 1.773 | 13.3073 | 0 | 15.4934 | 0 | 6.7127 | 2.1112 | 0.011537 | 1.7485 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 78.9806 | 18.91% | CZ 3A | 4.5458 | 0.31913 | 0.10501 | 0 | 0 | 4.5395 | 0 | 1.9668 | 0.61858 | 0.0033802 | 0.51229 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 17.472 | 18.91% | CZ 3A | 0 | 0 | 0.014146 | 0.13307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.1935 | 18.91% | CZ 3A | 47.5899 | 3.341 | 2.6455 | 14.5449 | 0 | 47.5243 | 0 | 20.5904 | 6.4759 | 0.035388 | 5.3632 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 204.0638 | 18.91%
CZ 3B | 0.46913 | 0.03295 | 0.024493 | 0.094343 | 0 | 0.35243 | 0 | 0.19153 | 0.040927 | 0.00016279 | 0.052598 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 1.8061 | 8.934% | CZ 3B | 15.5148 | 1.0897 | 1.7377 | 9.5296 | 0 | 11.6554 | 0 | 6.3343 | 1.3535 | 0.0053838 | 1.7395 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 70.1786 | 8.934% | CZ 3B | 4.5458 | 0.31928 | 0.10501 | 0 | 0 | 3.415 | 0 | 1.8559 | 0.39657 | 0.0015774 | 0.50966 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 16.0103 | 8.934% | CZ 3B | 0 | 0 | 0.013793 | 0.095296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.15537 | 8.934% | CZ 3B | 47.5899 | 3.3425 | 2.607 | 10.4158 | 0 | 35.7516 | 0 | 19.4297 | 4.1517 | 0.016514 | 5.3357 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 184.593 | 8.934%
CZ 3C | 0.46913 | 0.032935 | 0.02566 | 0.14936 | 0 | 0.1549 | 0 | 0.1517 | 0 | 0.00023644 | 0.052667 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.5841 | 0.953% | CZ 3C | 15.5148 | 1.0892 | 1.8554 | 15.0872 | 0 | 5.1228 | 0 | 5.0168 | 0 | 0.0078193 | 1.7418 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 66.6547 | 0.953% | CZ 3C | 4.5458 | 0.31913 | 0.10505 | 0 | 0 | 1.501 | 0 | 1.4699 | 0 | 0.002291 | 0.51034 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.3149 | 0.953% | CZ 3C | 0 | 0 | 0.014968 | 0.15087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.21212 | 0.953% | CZ 3C | 47.5899 | 3.341 | 2.7358 | 16.4903 | 0 | 15.7136 | 0 | 15.3885 | 0 | 0.023985 | 5.3428 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 162.5788 | 0.953%
CZ 4A | 0.46913 | 0.032915 | 0.026096 | 0.19053 | 0 | 0.33835 | 0 | 0.18638 | 0.061819 | 0.00055427 | 0.052648 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.9059 | 17.92% | CZ 4A | 15.5148 | 1.0886 | 1.8992 | 19.2456 | 0 | 11.1898 | 0 | 6.1639 | 2.0444 | 0.018331 | 1.7412 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 80.1247 | 17.92% | CZ 4A | 4.5458 | 0.31894 | 0.10509 | 0 | 0 | 3.2786 | 0 | 1.806 | 0.59901 | 0.0053708 | 0.51015 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 16.0304 | 17.92% | CZ 4A | 0 | 0 | 0.015405 | 0.19246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.25414 | 17.92% | CZ 4A | 47.5899 | 3.339 | 2.784 | 21.0354 | 0 | 34.3235 | 0 | 18.9072 | 6.2711 | 0.056227 | 5.3408 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 195.6 | 17.92%
CZ 4B | 0.46913 | 0.032923 | 0.025881 | 0.1516 | 0 | 0.26902 | 0 | 0.19422 | 0.028462 | 0.00041861 | 0.052443 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7716 | 0.6023% | CZ 4B | 15.5148 | 1.0888 | 1.8777 | 15.3129 | 0 | 8.897 | 0 | 6.423 | 0.94127 | 0.013844 | 1.7344 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 73.0225 | 0.6023% | CZ 4B | 4.5458 | 0.31902 | 0.10505 | 0 | 0 | 2.6068 | 0 | 1.8819 | 0.27579 | 0.0040563 | 0.50816 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 15.108 | 0.6023% | CZ 4B | 0 | 0 | 0.015191 | 0.15313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.2146 | 0.6023% | CZ 4B | 47.5899 | 3.3398 | 2.7602 | 16.737 | 0 | 27.2905 | 0 | 19.7018 | 2.8872 | 0.042465 | 5.3199 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 181.6217 | 0.6023%
CZ 4C | 0.46913 | 0.0329 | 0.026415 | 0.22709 | 0 | 0.19343 | 0 | 0.18265 | 0.037768 | 0.00042636 | 0.052512 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7698 | 1.875% | CZ 4C | 15.5148 | 1.088 | 1.9314 | 22.9382 | 0 | 6.3971 | 0 | 6.0404 | 1.249 | 0.0141 | 1.7367 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 78.1286 | 1.875% | CZ 4C | 4.5458 | 0.31879 | 0.10509 | 0 | 0 | 1.8743 | 0 | 1.7698 | 0.36597 | 0.0041314 | 0.50884 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 14.3542 | 1.875% | CZ 4C | 0 | 0 | 0.015727 | 0.22938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.29139 | 1.875% | CZ 4C | 47.5899 | 3.3374 | 2.8191 | 25.0715 | 0 | 19.6224 | 0 | 18.5281 | 3.8313 | 0.043251 | 5.327 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 182.123 | 1.875%
CZ 5A | 0.46913 | 0.032919 | 0.026966 | 0.29198 | 0 | 0.24923 | 0 | 0.19305 | 0.040094 | 0.00097288 | 0.052555 | 0 | 0.018607 | 0.10384 | 0 | 0.42505 | 1.9044 | 18.43% | CZ 5A | 15.5148 | 1.0887 | 1.9867 | 29.4927 | 0 | 8.2425 | 0 | 6.3845 | 1.326 | 0.032175 | 1.7381 | 0 | 0.61537 | 6.547 | 0 | 14.0563 | 87.0247 | 18.43% | CZ 5A | 4.5458 | 0.31898 | 0.10512 | 0 | 0 | 2.415 | 0 | 1.8707 | 0.3885 | 0.0094271 | 0.50925 | 0 | 0.1803 | 0.56229 | 0 | 4.1188 | 15.0241 | 18.43% | CZ 5A | 0 | 0 | 0.016279 | 0.29493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.35749 | 18.43% | CZ 5A | 47.5899 | 3.3394 | 2.8799 | 32.2355 | 0 | 25.2828 | 0 | 19.5839 | 4.0672 | 0.098692 | 5.3313 | 0 | 1.8876 | 10.9449 | 0 | 43.1196 | 196.3608 | 18.43%
CZ 5B | 0.46913 | 0.032888 | 0.026792 | 0.22574 | 0 | 0.20128 | 0 | 0.17745 | 0.039958 | 0.00049613 | 0.052322 | 0 | 0.018619 | 0.10384 | 0 | 0.42505 | 1.7736 | 4.478% | CZ 5B | 15.5148 | 1.0877 | 1.9694 | 22.8019 | 0 | 6.6567 | 0 | 5.8685 | 1.3215 | 0.016408 | 1.7304 | 0 | 0.61576 | 6.547 | 0 | 14.0563 | 78.1862 | 4.478% | CZ 5B | 4.5458 | 0.31868 | 0.10509 | 0 | 0 | 1.9504 | 0 | 1.7194 | 0.38719 | 0.0048074 | 0.507 | 0 | 0.18042 | 0.56229 | 0 | 4.1188 | 14.3999 | 4.478% | CZ 5B | 0 | 0 | 0.016108 | 0.22802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.29041 | 4.478% | CZ 5B | 47.5899 | 3.3363 | 2.8607 | 24.9224 | 0 | 20.4186 | 0 | 18.0008 | 4.0534 | 0.050329 | 5.3078 | 0 | 1.8888 | 10.9449 | 0 | 43.1196 | 182.4936 | 4.478%
CZ 5C | 0.46913 | 0.032865 | 0.026772 | 0.27766 | 0 | 0.13596 | 0 | 0.20351 | 0.036609 | 0.00059691 | 0.052439 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7831 | 0% | CZ 5C | 15.5148 | 1.0869 | 1.9671 | 28.0465 | 0 | 4.4965 | 0 | 6.7305 | 1.2107 | 0.019741 | 1.7342 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 82.0259 | 0% | CZ 5C | 4.5458 | 0.31845 | 0.10512 | 0 | 0 | 1.3175 | 0 | 1.972 | 0.35474 | 0.0057839 | 0.50812 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.989 | 0% | CZ 5C | 0 | 0 | 0.016083 | 0.28046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.34283 | 0% | CZ 5C | 47.5899 | 3.3339 | 2.8585 | 30.6548 | 0 | 13.7925 | 0 | 20.6451 | 3.7137 | 0.060552 | 5.3196 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 183.9214 | 0%
CZ 6A | 0.46913 | 0.0329 | 0.027702 | 0.34266 | 0 | 0.17772 | 0 | 0.19232 | 0.039121 | 0.001093 | 0.052408 | 0 | 0.018611 | 0.10384 | 0 | 0.42505 | 1.8826 | 3.366% | CZ 6A | 15.5148 | 1.088 | 2.0608 | 34.6125 | 0 | 5.8776 | 0 | 6.3602 | 1.2938 | 0.036148 | 1.7332 | 0 | 0.6155 | 6.547 | 0 | 14.0563 | 89.7957 | 3.366% | CZ 6A | 4.5458 | 0.31879 | 0.10516 | 0 | 0 | 1.7221 | 0 | 1.8635 | 0.37907 | 0.010591 | 0.50782 | 0 | 0.18034 | 0.56229 | 0 | 4.1188 | 14.3143 | 3.366% | CZ 6A | 0 | 0 | 0.017019 | 0.34612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.40942 | 3.366% | CZ 6A | 47.5899 | 3.3374 | 2.9611 | 37.8314 | 0 | 18.0288 | 0 | 19.5091 | 3.9685 | 0.11088 | 5.3164 | 0 | 1.888 | 10.9449 | 0 | 43.1196 | 194.6061 | 3.366%
CZ 6B | 0.46913 | 0.032888 | 0.027795 | 0.29734 | 0 | 0.14425 | 0 | 0.1789 | 0.038915 | 0.00086435 | 0.052249 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.7898 | 0.7502% | CZ 6B | 15.5148 | 1.0877 | 2.0703 | 30.0345 | 0 | 4.7704 | 0 | 5.9164 | 1.287 | 0.028585 | 1.7279 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 83.6565 | 0.7502% | CZ 6B | 4.5458 | 0.31868 | 0.10516 | 0 | 0 | 1.3977 | 0 | 1.7335 | 0.37708 | 0.0083754 | 0.50628 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.854 | 0.7502% | CZ 6B | 0 | 0 | 0.017114 | 0.30035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.36374 | 0.7502% | CZ 6B | 47.5899 | 3.3363 | 2.9715 | 32.8277 | 0 | 14.6327 | 0 | 18.1479 | 3.9477 | 0.087682 | 5.3003 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 184.7946 | 0.7502%
CZ 7 | 0.46913 | 0.032876 | 0.028888 | 0.44698 | 0 | 0.13785 | 0 | 0.19333 | 0.038334 | 0.0017597 | 0.052291 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 1.9489 | 0.4665% | CZ 7 | 15.5148 | 1.0873 | 2.1801 | 45.1494 | 0 | 4.5589 | 0 | 6.3936 | 1.2678 | 0.058196 | 1.7294 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 99.1584 | 0.4665% | CZ 7 | 4.5458 | 0.31857 | 0.10524 | 0 | 0 | 1.3358 | 0 | 1.8733 | 0.37145 | 0.017051 | 0.5067 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.9353 | 0.4665% | CZ 7 | 0 | 0 | 0.018209 | 0.45149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.51598 | 0.4665% | CZ 7 | 47.5899 | 3.3351 | 3.092 | 49.3483 | 0 | 13.984 | 0 | 19.6118 | 3.8887 | 0.17851 | 5.3046 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 202.2858 | 0.4665%
CZ 8 | 0.46913 | 0.032667 | 0.030224 | 0.70699 | 0 | 0.092625 | 0 | 0.2057 | 0.037663 | 0.0030388 | 0.052144 | 0 | 0.018615 | 0.10384 | 0 | 0.42505 | 2.1777 | 0.06613% | CZ 8 | 15.5148 | 1.0803 | 2.3151 | 71.4134 | 0 | 3.0632 | 0 | 6.8029 | 1.2456 | 0.1005 | 1.7245 | 0 | 0.61563 | 6.547 | 0 | 14.0563 | 124.4793 | 0.06613% | CZ 8 | 4.5458 | 0.31654 | 0.10524 | 0 | 0 | 0.89752 | 0 | 1.9932 | 0.36495 | 0.029445 | 0.50527 | 0 | 0.18038 | 0.56229 | 0 | 4.1188 | 13.6195 | 0.06613% | CZ 8 | 0 | 0 | 0.019559 | 0.71413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.77997 | 0.06613% | CZ 8 | 47.5899 | 3.3138 | 3.2395 | 78.0548 | 0 | 9.3962 | 0 | 20.8672 | 3.8207 | 0.30826 | 5.2897 | 0 | 1.8884 | 10.9449 | 0 | 43.1196 | 227.8331 | 0.06613%
Us Weighted | 0.46913 | 0.03293 | 0.025408 | 0.17128 | 0 | 0.39782 | 0 | 0.19641 | 0.051919 | 0.000486 | 0.052753 | 0 | 0.018613 | 0.10384 | 0 | 0.42505 | 1.9457 | 100% | Us Weighted | 15.5148 | 1.089 | 1.83 | 17.3012 | 0 | 13.1565 | 0 | 6.4956 | 1.717 | 0.016073 | 1.7446 | 0 | 0.61557 | 6.547 | 0 | 14.0563 | 80.0837 | 100% | Us Weighted | 4.5458 | 0.31909 | 0.10505 | 0 | 0 | 3.8548 | 0 | 1.9032 | 0.50309 | 0.0047092 | 0.51117 | 0 | 0.18036 | 0.56229 | 0 | 4.1188 | 16.6084 | 100% | Us Weighted | 0 | 0 | 0.014714 | 0.17301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046279 | 0 | 0 | 0.23401 | 100% | Us Weighted | 47.5899 | 3.3405 | 2.708 | 18.9102 | 0 | 40.3561 | 0 | 19.9247 | 5.2669 | 0.049301 | 5.3514 | 0 | 1.8882 | 10.9449 | 0 | 43.1196 | 199.4497 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Primary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 73959 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 73959 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.19548 | 0.015202 | 0.00087493 | 0.0049265 | 0 | 0.36999 | 0 | 0.10466 | 0.016992 | 7.752e-06 | 0.0053567 | 0 | 0.0092366 | 0 | 0 | 0.062671 | 0.7854 | 1.275% | CZ 1A | 6.4646 | 0.50274 | 0.032814 | 0.49762 | 0 | 12.2362 | 0 | 3.4614 | 0.56197 | 0.00025637 | 0.17715 | 0 | 0.30547 | 0 | 0 | 2.0726 | 26.3129 | 1.275% | CZ 1A | 1.8941 | 0.1473 | 0.0079247 | 0 | 0 | 3.5852 | 0 | 1.0142 | 0.16465 | 7.5116e-05 | 0.051905 | 0 | 0.089501 | 0 | 0 | 0.60728 | 7.5621 | 1.275% | CZ 1A | 0 | 0 | 5.7669e-05 | 0.0049762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0050339 | 1.275% | CZ 1A | 19.8296 | 1.5421 | 0.089267 | 0.5439 | 0 | 37.5332 | 0 | 10.6174 | 1.7238 | 0.00078639 | 0.5434 | 0 | 0.93698 | 0 | 0 | 6.3576 | 79.718 | 1.275%
CZ 1B | 0.19369 | 0.015202 | 0.00086351 | 0.016839 | 0 | 0.3536 | 0 | 0.11145 | -0.031345 | 1.938e-05 | 0.0054962 | 0 | 0.0092327 | 0 | 0 | 0.062671 | 0.73772 | 0% | CZ 1B | 6.4057 | 0.50274 | 0.031661 | 1.7009 | 0 | 11.6941 | 0 | 3.6858 | -1.0366 | 0.00064093 | 0.18177 | 0 | 0.30534 | 0 | 0 | 2.0726 | 25.5446 | 0% | CZ 1B | 1.8768 | 0.1473 | 0.0079247 | 0 | 0 | 3.4263 | 0 | 1.0799 | -0.30373 | 0.00018779 | 0.053257 | 0 | 0.089463 | 0 | 0 | 0.60728 | 6.9848 | 0% | CZ 1B | 0 | 0 | 4.6136e-05 | 0.017009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017055 | 0% | CZ 1B | 19.6487 | 1.5421 | 0.088007 | 1.859 | 0 | 35.8704 | 0 | 11.3059 | -3.1798 | 0.001966 | 0.55755 | 0 | 0.93659 | 0 | 0 | 6.3576 | 74.9881 | 0%
CZ 2A | 0.19125 | 0.015198 | 0.00087754 | 0.020421 | 0 | 0.30696 | 0 | 0.084323 | 0.026027 | 5.4264e-05 | 0.0052908 | 0 | 0.0092288 | 0 | 0 | 0.062671 | 0.72231 | 18.69% | CZ 2A | 6.3251 | 0.50262 | 0.032814 | 2.0628 | 0 | 10.1516 | 0 | 2.7887 | 0.86077 | 0.0017946 | 0.17497 | 0 | 0.30521 | 0 | 0 | 2.0726 | 25.279 | 18.69% | CZ 2A | 1.8532 | 0.14726 | 0.0079623 | 0 | 0 | 2.9744 | 0 | 0.81707 | 0.2522 | 0.00052581 | 0.051267 | 0 | 0.089426 | 0 | 0 | 0.60728 | 6.8006 | 18.69% | CZ 2A | 0 | 0 | 5.6388e-05 | 0.020628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020684 | 18.69% | CZ 2A | 19.4014 | 1.5417 | 0.08952 | 2.2546 | 0 | 31.1391 | 0 | 8.554 | 2.6403 | 0.0055047 | 0.53671 | 0 | 0.9362 | 0 | 0 | 6.3576 | 73.4566 | 18.69%
CZ 2B | 0.19116 | 0.015198 | 0.00087247 | 0.037226 | 0 | 0.26877 | 0 | 0.084257 | -0.027152 | 4.2636e-05 | 0.005535 | 0 | 0.0092327 | 0 | 0 | 0.062671 | 0.64782 | 3.29% | CZ 2B | 6.322 | 0.50262 | 0.032301 | 3.7602 | 0 | 8.8888 | 0 | 2.7865 | -0.89794 | 0.00141 | 0.18305 | 0 | 0.30534 | 0 | 0 | 2.0726 | 23.9568 | 3.29% | CZ 2B | 1.8523 | 0.14726 | 0.0079623 | 0 | 0 | 2.6044 | 0 | 0.81644 | -0.26309 | 0.00041314 | 0.053633 | 0 | 0.089463 | 0 | 0 | 0.60728 | 5.9161 | 3.29% | CZ 2B | 0 | 0 | 5.1262e-05 | 0.037602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037653 | 3.29% | CZ 2B | 19.392 | 1.5417 | 0.08896 | 4.1099 | 0 | 27.2653 | 0 | 8.5473 | -2.7543 | 0.0043251 | 0.56148 | 0 | 0.93659 | 0 | 0 | 6.3576 | 66.0507 | 3.29%
CZ 3A | 0.18922 | 0.015171 | 0.00088008 | 0.036786 | 0 | 0.22662 | 0 | 0.074575 | 0.025849 | 7.3644e-05 | 0.0052132 | 0 | 0.0092404 | 0 | 0 | 0.062671 | 0.64631 | 18.91% | CZ 3A | 6.2579 | 0.50172 | 0.03307 | 3.7157 | 0 | 7.4947 | 0 | 2.4663 | 0.85487 | 0.0024355 | 0.17241 | 0 | 0.30559 | 0 | 0 | 2.0726 | 23.8774 | 18.91% | CZ 3A | 1.8335 | 0.147 | 0.0079623 | 0 | 0 | 2.1959 | 0 | 0.72262 | 0.25047 | 0.0007136 | 0.050516 | 0 | 0.089538 | 0 | 0 | 0.60728 | 5.9056 | 18.91% | CZ 3A | 0 | 0 | 5.8951e-05 | 0.037157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037216 | 18.91% | CZ 3A | 19.1954 | 1.539 | 0.089801 | 4.0613 | 0 | 22.9893 | 0 | 7.5651 | 2.6222 | 0.0074707 | 0.52885 | 0 | 0.93738 | 0 | 0 | 6.3576 | 65.8933 | 18.91%
CZ 3B | 0.19161 | 0.015198 | 0.00086993 | 0.041306 | 0 | 0.15025 | 0 | 0.096028 | 0.040927 | -0.00015116 | 0.0054342 | 0 | 0.0092288 | 0 | 0 | 0.062671 | 0.61338 | 8.934% | CZ 3B | 6.337 | 0.50262 | 0.032045 | 4.1723 | 0 | 4.9691 | 0 | 3.1758 | 1.3535 | -0.0049992 | 0.17972 | 0 | 0.30521 | 0 | 0 | 2.0726 | 23.0949 | 8.934% | CZ 3B | 1.8567 | 0.14726 | 0.0079623 | 0 | 0 | 1.4559 | 0 | 0.9305 | 0.39657 | -0.0014648 | 0.052656 | 0 | 0.089426 | 0 | 0 | 0.60728 | 5.5428 | 8.934% | CZ 3B | 0 | 0 | 4.8699e-05 | 0.041723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041772 | 8.934% | CZ 3B | 19.438 | 1.5417 | 0.08868 | 4.5603 | 0 | 15.2422 | 0 | 9.7414 | 4.1517 | -0.015335 | 0.55126 | 0 | 0.9362 | 0 | 0 | 6.3576 | 62.5937 | 8.934%
CZ 3C | 0.18972 | 0.015178 | 0.00087888 | 0.085382 | 0 | 0.084641 | 0 | 0.064745 | 0 | -3.1008e-05 | 0.0055117 | 0 | 0.0092366 | 0 | 0 | 0.062671 | 0.51794 | 0.953% | CZ 3C | 6.2744 | 0.50197 | 0.032686 | 8.6244 | 0 | 2.7992 | 0 | 2.1412 | 0 | -0.0010255 | 0.18228 | 0 | 0.30547 | 0 | 0 | 2.0726 | 22.9332 | 0.953% | CZ 3C | 1.8384 | 0.14708 | 0.0079999 | 0 | 0 | 0.82015 | 0 | 0.62737 | 0 | -0.00030046 | 0.053407 | 0 | 0.089501 | 0 | 0 | 0.60728 | 4.1909 | 0.953% | CZ 3C | 0 | 0 | 5.3825e-05 | 0.086244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086298 | 0.953% | CZ 3C | 19.2461 | 1.5398 | 0.089634 | 9.4265 | 0 | 8.5862 | 0 | 6.5679 | 0 | -0.0031456 | 0.55912 | 0 | 0.93698 | 0 | 0 | 6.3576 | 53.3066 | 0.953%
CZ 4A | 0.20058 | 0.015155 | 0.00090813 | 0.073461 | 0 | 0.1498 | 0 | 0.053974 | 0.022551 | 6.2016e-05 | 0.0051861 | 0 | 0.0092366 | 0 | 0 | 0.062671 | 0.59358 | 17.92% | CZ 4A | 6.6333 | 0.50121 | 0.035377 | 7.4203 | 0 | 4.954 | 0 | 1.785 | 0.74578 | 0.002051 | 0.17151 | 0 | 0.30547 | 0 | 0 | 2.0726 | 24.6266 | 17.92% | CZ 4A | 1.9436 | 0.14685 | 0.0080374 | 0 | 0 | 1.4515 | 0 | 0.523 | 0.21851 | 0.00060093 | 0.050253 | 0 | 0.089501 | 0 | 0 | 0.60728 | 5.0391 | 17.92% | CZ 4A | 0 | 0 | 7.9456e-05 | 0.074203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074282 | 17.92% | CZ 4A | 20.347 | 1.5374 | 0.092828 | 8.1104 | 0 | 15.1958 | 0 | 5.4752 | 2.2876 | 0.0062911 | 0.52609 | 0 | 0.93698 | 0 | 0 | 6.3576 | 60.8732 | 17.92%
CZ 4B | 0.20169 | 0.015175 | 0.00090172 | 0.069288 | 0 | 0.12963 | 0 | 0.089567 | 0.028462 | -0.00011628 | 0.0053218 | 0 | 0.0092443 | 0 | 0 | 0.062671 | 0.61183 | 0.6023% | CZ 4B | 6.6703 | 0.50185 | 0.034993 | 6.9988 | 0 | 4.2869 | 0 | 2.9621 | 0.94127 | -0.0038456 | 0.176 | 0 | 0.30572 | 0 | 0 | 2.0726 | 24.9467 | 0.6023% | CZ 4B | 1.9544 | 0.14704 | 0.0079999 | 0 | 0 | 1.2561 | 0 | 0.86789 | 0.27579 | -0.0011267 | 0.051567 | 0 | 0.089576 | 0 | 0 | 0.60728 | 5.2564 | 0.6023% | CZ 4B | 0 | 0 | 7.6893e-05 | 0.069988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070065 | 0.6023% | CZ 4B | 20.4603 | 1.5394 | 0.092155 | 7.6497 | 0 | 13.1496 | 0 | 9.0859 | 2.8872 | -0.011796 | 0.53986 | 0 | 0.93777 | 0 | 0 | 6.3576 | 62.6876 | 0.6023%
CZ 4C | 0.19702 | 0.015124 | 0.00090559 | 0.10681 | 0 | 0.098455 | 0 | 0.10078 | 0.037768 | -0.00040311 | 0.005407 | 0 | 0.0092404 | 0 | 0 | 0.062671 | 0.63378 | 1.875% | CZ 4C | 6.5158 | 0.50018 | 0.035121 | 10.7892 | 0 | 3.256 | 0 | 3.3328 | 1.249 | -0.013331 | 0.17882 | 0 | 0.30559 | 0 | 0 | 2.0726 | 28.2219 | 1.875% | CZ 4C | 1.9091 | 0.14655 | 0.0080374 | 0 | 0 | 0.95401 | 0 | 0.97651 | 0.36597 | -0.003906 | 0.052393 | 0 | 0.089538 | 0 | 0 | 0.60728 | 5.1055 | 1.875% | CZ 4C | 0 | 0 | 7.6893e-05 | 0.10789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10797 | 1.875% | CZ 4C | 19.9865 | 1.5342 | 0.092548 | 11.7926 | 0 | 9.9875 | 0 | 10.2231 | 3.8313 | -0.040892 | 0.54851 | 0 | 0.93738 | 0 | 0 | 6.3576 | 65.2503 | 1.875%
CZ 5A | 0.20005 | 0.015101 | 0.00091454 | 0.14746 | 0 | 0.091191 | 0 | 0.059311 | 0.00065892 | 9.6901e-05 | 0.0051667 | 0 | 0.0092288 | 0 | 0 | 0.062671 | 0.59184 | 18.43% | CZ 5A | 6.6159 | 0.49941 | 0.035762 | 14.8945 | 0 | 3.0158 | 0 | 1.9615 | 0.021792 | 0.0032046 | 0.17087 | 0 | 0.30521 | 0 | 0 | 2.0726 | 29.5966 | 18.43% | CZ 5A | 1.9384 | 0.14633 | 0.008075 | 0 | 0 | 0.88363 | 0 | 0.57471 | 0.0063849 | 0.00093895 | 0.050065 | 0 | 0.089426 | 0 | 0 | 0.60728 | 4.3053 | 18.43% | CZ 5A | 0 | 0 | 8.2019e-05 | 0.14894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14903 | 18.43% | CZ 5A | 20.2936 | 1.5319 | 0.093502 | 16.2797 | 0 | 9.2507 | 0 | 6.0167 | 0.066843 | 0.0098299 | 0.52413 | 0 | 0.9362 | 0 | 0 | 6.3576 | 61.3606 | 18.43%
CZ 5B | 0.19834 | 0.015175 | 0.00090559 | 0.095657 | 0 | 0.0948 | 0 | 0.090695 | 0.039958 | -0.00050388 | 0.0052869 | 0 | 0.0092404 | 0 | 0 | 0.062671 | 0.61222 | 4.478% | CZ 5B | 6.5593 | 0.50185 | 0.035121 | 9.6623 | 0 | 3.1352 | 0 | 2.9994 | 1.3215 | -0.016664 | 0.17484 | 0 | 0.30559 | 0 | 0 | 2.0726 | 26.751 | 4.478% | CZ 5B | 1.9218 | 0.14704 | 0.0080374 | 0 | 0 | 0.91859 | 0 | 0.87882 | 0.38719 | -0.0048825 | 0.051229 | 0 | 0.089538 | 0 | 0 | 0.60728 | 5.0047 | 4.478% | CZ 5B | 0 | 0 | 7.6893e-05 | 0.096623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0967 | 4.478% | CZ 5B | 20.1198 | 1.5394 | 0.092548 | 10.5609 | 0 | 9.6168 | 0 | 9.2004 | 4.0534 | -0.051115 | 0.53632 | 0 | 0.93738 | 0 | 0 | 6.3576 | 62.9633 | 4.478%
CZ 5C | 0.18822 | 0.01507 | 0.00090566 | 0.18461 | 0 | 0.063404 | 0 | 0.071214 | 0.0055156 | 0.00012791 | 0.0053644 | 0 | 0.0092366 | 0 | 0 | 0.062671 | 0.60633 | 0% | CZ 5C | 6.2247 | 0.49839 | 0.034865 | 18.647 | 0 | 2.0969 | 0 | 2.3552 | 0.18241 | 0.0042301 | 0.17741 | 0 | 0.30547 | 0 | 0 | 2.0726 | 32.5991 | 0% | CZ 5C | 1.8238 | 0.14603 | 0.008075 | 0 | 0 | 0.61437 | 0 | 0.69005 | 0.053445 | 0.0012394 | 0.05198 | 0 | 0.089501 | 0 | 0 | 0.60728 | 4.0858 | 0% | CZ 5C | 0 | 0 | 7.3048e-05 | 0.18647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18654 | 0% | CZ 5C | 19.0935 | 1.5287 | 0.092521 | 20.3811 | 0 | 6.4319 | 0 | 7.2242 | 0.55952 | 0.012975 | 0.54418 | 0 | 0.93698 | 0 | 0 | 6.3576 | 63.1632 | 0%
CZ 6A | 0.19821 | 0.01507 | 0.00091842 | 0.171 | 0 | 0.066854 | 0 | 0.061939 | 0.0012907 | 7.3644e-05 | 0.0051474 | 0 | 0.0092288 | 0 | 0 | 0.062671 | 0.5924 | 3.366% | CZ 6A | 6.5551 | 0.49839 | 0.03589 | 17.2726 | 0 | 2.2109 | 0 | 2.0484 | 0.042686 | 0.0024355 | 0.17023 | 0 | 0.30521 | 0 | 0 | 2.0726 | 31.2146 | 3.366% | CZ 6A | 1.9206 | 0.14603 | 0.0081125 | 0 | 0 | 0.6478 | 0 | 0.60018 | 0.012507 | 0.0007136 | 0.049877 | 0 | 0.089426 | 0 | 0 | 0.60728 | 4.0826 | 3.366% | CZ 6A | 0 | 0 | 8.2019e-05 | 0.17273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17281 | 3.366% | CZ 6A | 20.1072 | 1.5287 | 0.093895 | 18.879 | 0 | 6.7818 | 0 | 6.2833 | 0.13093 | 0.0074707 | 0.52216 | 0 | 0.9362 | 0 | 0 | 6.3576 | 61.6282 | 3.366%
CZ 6B | 0.19811 | 0.01514 | 0.00091969 | 0.16735 | 0 | 0.057753 | 0 | 0.039299 | -0.0026512 | -0.00012791 | 0.0051977 | 0 | 0.0092404 | 0 | 0 | 0.062671 | 0.5529 | 0.7502% | CZ 6B | 6.5518 | 0.50069 | 0.036018 | 16.9037 | 0 | 1.91 | 0 | 1.2997 | -0.087679 | -0.0042301 | 0.1719 | 0 | 0.30559 | 0 | 0 | 2.0726 | 29.6601 | 0.7502% | CZ 6B | 1.9197 | 0.1467 | 0.0081125 | 0 | 0 | 0.55961 | 0 | 0.3808 | -0.02569 | -0.0012394 | 0.050365 | 0 | 0.089538 | 0 | 0 | 0.60728 | 3.7351 | 0.7502% | CZ 6B | 0 | 0 | 8.33e-05 | 0.16904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16912 | 0.7502% | CZ 6B | 20.097 | 1.5358 | 0.094035 | 18.4757 | 0 | 5.8586 | 0 | 3.9866 | -0.26895 | -0.012975 | 0.52727 | 0 | 0.93738 | 0 | 0 | 6.3576 | 57.5881 | 0.7502%
CZ 7 | 0.20816 | 0.015089 | 0.00093625 | 0.23492 | 0 | 0.053636 | 0 | 0.055939 | -0.00071706 | 0.00032946 | 0.0051357 | 0 | 0.0092482 | 0 | 0 | 0.062671 | 0.64535 | 0.4665% | CZ 7 | 6.8841 | 0.49903 | 0.037428 | 23.7293 | 0 | 1.7738 | 0 | 1.85 | -0.023714 | 0.010896 | 0.16985 | 0 | 0.30585 | 0 | 0 | 2.0726 | 37.3092 | 0.4665% | CZ 7 | 2.017 | 0.14621 | 0.0081501 | 0 | 0 | 0.51973 | 0 | 0.54204 | -0.0069482 | 0.0031924 | 0.049764 | 0 | 0.089613 | 0 | 0 | 0.60728 | 3.976 | 0.4665% | CZ 7 | 0 | 0 | 9.6116e-05 | 0.23729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23739 | 0.4665% | CZ 7 | 21.1161 | 1.5307 | 0.095829 | 25.9362 | 0 | 5.441 | 0 | 5.6746 | -0.072741 | 0.033422 | 0.52098 | 0 | 0.93816 | 0 | 0 | 6.3576 | 67.5718 | 0.4665%
CZ 8 | 0.19301 | 0.014775 | 0.00092349 | 0.31887 | 0 | 0.043566 | 0 | 0.060016 | -0.0042481 | 0.00051551 | 0.0052016 | 0 | 0.0092327 | 0 | 0 | 0.062671 | 0.70454 | 0.06613% | CZ 8 | 6.3831 | 0.48864 | 0.036403 | 32.2093 | 0 | 1.4408 | 0 | 1.9848 | -0.14049 | 0.017049 | 0.17202 | 0 | 0.30534 | 0 | 0 | 2.0726 | 44.9697 | 0.06613% | CZ 8 | 1.8702 | 0.14317 | 0.0081125 | 0 | 0 | 0.42215 | 0 | 0.58155 | -0.041164 | 0.0049952 | 0.050403 | 0 | 0.089463 | 0 | 0 | 0.60728 | 3.7362 | 0.06613% | CZ 8 | 0 | 0 | 8.7145e-05 | 0.32209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32218 | 0.06613% | CZ 8 | 19.5795 | 1.4989 | 0.094455 | 35.2048 | 0 | 4.4195 | 0 | 6.0882 | -0.43094 | 0.052295 | 0.52767 | 0 | 0.93659 | 0 | 0 | 6.3576 | 74.3285 | 0.06613%
Us Weighted | 0.19508 | 0.015159 | 0.00089338 | 0.071918 | 0 | 0.1815 | 0 | 0.072935 | 0.019581 | 1.3314e-05 | 0.0052542 | 0 | 0.0092337 | 0 | 0 | 0.062671 | 0.63424 | 100% | Us Weighted | 6.4517 | 0.50133 | 0.034089 | 7.2644 | 0 | 6.0023 | 0 | 2.4121 | 0.64757 | 0.0004403 | 0.17376 | 0 | 0.30537 | 0 | 0 | 2.0726 | 25.8656 | 100% | Us Weighted | 1.8903 | 0.14689 | 0.0080086 | 0 | 0 | 1.7587 | 0 | 0.70673 | 0.18974 | 0.00012901 | 0.050912 | 0 | 0.089473 | 0 | 0 | 0.60728 | 5.4481 | 100% | Us Weighted | 0 | 0 | 6.7561e-05 | 0.072644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072712 | 100% | Us Weighted | 19.7898 | 1.5378 | 0.091226 | 7.94 | 0 | 18.4114 | 0 | 7.3987 | 1.9863 | 0.0013506 | 0.533 | 0 | 0.93669 | 0 | 0 | 6.3576 | 64.9839 | 100%
Building Type: | Primary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 73959 | [17 empty] | Prototype Floor Area: | 73959 | [17 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 41.67% | 46.11% | 3.923% | 22.15% | 0% | 45.97% | 0% | 44.42% | 24.81% | 10% | 10.01% | 0% | 49.62% | 0% | 0% | 14.74% | 34.8% | 1.275% | CZ 1A | 41.67% | 46.11% | 2.163% | 22.15% | 0% | 45.97% | 0% | 44.42% | 24.81% | 10% | 10.01% | 0% | 49.62% | 0% | 0% | 14.75% | 32.88% | 1.275% | CZ 1A | 41.67% | 46.11% | 7.552% | 0% | 0% | 45.97% | 0% | 44.42% | 24.81% | 10% | 10.01% | 0% | 49.62% | 0% | 0% | 14.74% | 35.85% | 1.275% | CZ 1A | 0% | 0% | 0.4977% | 22.15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.267% | 1.275% | CZ 1A | 41.67% | 46.11% | 3.775% | 22.15% | 0% | 45.97% | 0% | 44.42% | 24.81% | 10% | 10.01% | 0% | 49.62% | 0% | 0% | 14.74% | 34.71% | 1.275%
CZ 1B | 41.29% | 46.11% | 3.913% | 48.77% | 0% | 47.17% | 0% | 47.79% | -216.4% | 20.83% | 10.44% | 0% | 49.6% | 0% | 0% | 14.74% | 34.21% | 0% | CZ 1B | 41.29% | 46.11% | 2.12% | 48.77% | 0% | 47.17% | 0% | 47.79% | -216.4% | 20.83% | 10.44% | 0% | 49.6% | 0% | 0% | 14.75% | 32.95% | 0% | CZ 1B | 41.29% | 46.11% | 7.552% | 0% | 0% | 47.17% | 0% | 47.79% | -216.4% | 20.83% | 10.44% | 0% | 49.6% | 0% | 0% | 14.74% | 34.91% | 0% | CZ 1B | 0% | 0% | 0.4063% | 48.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.44% | 0% | CZ 1B | 41.29% | 46.11% | 3.762% | 48.77% | 0% | 47.17% | 0% | 47.79% | -216.4% | 20.83% | 10.44% | 0% | 49.6% | 0% | 0% | 14.74% | 34.15% | 0%
CZ 2A | 40.77% | 46.11% | 3.692% | 26.05% | 0% | 49.01% | 0% | 40.42% | 40.14% | 31.11% | 9.945% | 0% | 49.59% | 0% | 0% | 14.74% | 34.32% | 18.69% | CZ 2A | 40.77% | 46.11% | 1.971% | 26.05% | 0% | 49.01% | 0% | 40.42% | 40.14% | 31.11% | 9.945% | 0% | 49.59% | 0% | 0% | 14.75% | 32.03% | 18.69% | CZ 2A | 40.77% | 46.11% | 7.585% | 0% | 0% | 49.01% | 0% | 40.42% | 40.14% | 31.11% | 9.945% | 0% | 49.59% | 0% | 0% | 14.74% | 35.67% | 18.69% | CZ 2A | 0% | 0% | 0.4317% | 26.05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 14.93% | 18.69% | CZ 2A | 40.77% | 46.11% | 3.543% | 26.05% | 0% | 49.01% | 0% | 40.42% | 40.14% | 31.11% | 9.945% | 0% | 49.59% | 0% | 0% | 14.74% | 34.2% | 18.69%
CZ 2B | 40.75% | 46.12% | 3.773% | 59.77% | 0% | 43.43% | 0% | 38.94% | -353.4% | 28.95% | 10.5% | 0% | 49.6% | 0% | 0% | 14.74% | 31.9% | 3.29% | CZ 2B | 40.75% | 46.12% | 2.019% | 59.77% | 0% | 43.43% | 0% | 38.94% | -353.4% | 28.95% | 10.5% | 0% | 49.6% | 0% | 0% | 14.75% | 31.8% | 3.29% | CZ 2B | 40.75% | 46.12% | 7.585% | 0% | 0% | 43.43% | 0% | 38.94% | -353.4% | 28.95% | 10.5% | 0% | 49.6% | 0% | 0% | 14.74% | 31.96% | 3.29% | CZ 2B | 0% | 0% | 0.4128% | 59.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.96% | 3.29% | CZ 2B | 40.75% | 46.12% | 3.622% | 59.77% | 0% | 43.43% | 0% | 38.94% | -353.4% | 28.95% | 10.5% | 0% | 49.6% | 0% | 0% | 14.74% | 31.89% | 3.29%
CZ 3A | 40.33% | 46.06% | 3.543% | 27.92% | 0% | 48.37% | 0% | 36.74% | 40.49% | 21.11% | 9.861% | 0% | 49.63% | 0% | 0% | 14.74% | 32.4% | 18.91% | CZ 3A | 40.33% | 46.06% | 1.865% | 27.92% | 0% | 48.37% | 0% | 36.74% | 40.49% | 21.11% | 9.861% | 0% | 49.63% | 0% | 0% | 14.75% | 30.23% | 18.91% | CZ 3A | 40.33% | 46.06% | 7.582% | 0% | 0% | 48.37% | 0% | 36.74% | 40.49% | 21.11% | 9.861% | 0% | 49.63% | 0% | 0% | 14.74% | 33.8% | 18.91% | CZ 3A | 0% | 0% | 0.4167% | 27.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.23% | 18.91% | CZ 3A | 40.33% | 46.06% | 3.394% | 27.92% | 0% | 48.37% | 0% | 36.74% | 40.49% | 21.11% | 9.861% | 0% | 49.63% | 0% | 0% | 14.74% | 32.29% | 18.91%
CZ 3B | 40.84% | 46.12% | 3.552% | 43.78% | 0% | 42.63% | 0% | 50.14% | 100% | -92.86% | 10.33% | 0% | 49.59% | 0% | 0% | 14.74% | 33.96% | 8.934% | CZ 3B | 40.84% | 46.12% | 1.844% | 43.78% | 0% | 42.63% | 0% | 50.14% | 100% | -92.86% | 10.33% | 0% | 49.59% | 0% | 0% | 14.75% | 32.91% | 8.934% | CZ 3B | 40.84% | 46.12% | 7.582% | 0% | 0% | 42.63% | 0% | 50.14% | 100% | -92.86% | 10.33% | 0% | 49.59% | 0% | 0% | 14.74% | 34.62% | 8.934% | CZ 3B | 0% | 0% | 0.3531% | 43.78% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.89% | 8.934% | CZ 3B | 40.84% | 46.12% | 3.402% | 43.78% | 0% | 42.63% | 0% | 50.14% | 100% | -92.86% | 10.33% | 0% | 49.59% | 0% | 0% | 14.74% | 33.91% | 8.934%
CZ 3C | 40.44% | 46.09% | 3.425% | 57.16% | 0% | 54.64% | 0% | 42.68% | 0% | -13.11% | 10.47% | 0% | 49.62% | 0% | 0% | 14.74% | 32.7% | 0.953% | CZ 3C | 40.44% | 46.09% | 1.762% | 57.16% | 0% | 54.64% | 0% | 42.68% | 0% | -13.11% | 10.47% | 0% | 49.62% | 0% | 0% | 14.75% | 34.41% | 0.953% | CZ 3C | 40.44% | 46.09% | 7.615% | 0% | 0% | 54.64% | 0% | 42.68% | 0% | -13.11% | 10.47% | 0% | 49.62% | 0% | 0% | 14.74% | 31.47% | 0.953% | CZ 3C | 0% | 0% | 0.3596% | 57.16% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.68% | 0.953% | CZ 3C | 40.44% | 46.09% | 3.276% | 57.16% | 0% | 54.64% | 0% | 42.68% | 0% | -13.11% | 10.47% | 0% | 49.62% | 0% | 0% | 14.74% | 32.79% | 0.953%
CZ 4A | 42.75% | 46.04% | 3.48% | 38.56% | 0% | 44.27% | 0% | 28.96% | 36.48% | 11.19% | 9.851% | 0% | 49.62% | 0% | 0% | 14.74% | 31.14% | 17.92% | CZ 4A | 42.75% | 46.04% | 1.863% | 38.56% | 0% | 44.27% | 0% | 28.96% | 36.48% | 11.19% | 9.851% | 0% | 49.62% | 0% | 0% | 14.75% | 30.74% | 17.92% | CZ 4A | 42.75% | 46.04% | 7.648% | 0% | 0% | 44.27% | 0% | 28.96% | 36.48% | 11.19% | 9.851% | 0% | 49.62% | 0% | 0% | 14.74% | 31.43% | 17.92% | CZ 4A | 0% | 0% | 0.5158% | 38.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.23% | 17.92% | CZ 4A | 42.75% | 46.04% | 3.334% | 38.56% | 0% | 44.27% | 0% | 28.96% | 36.48% | 11.19% | 9.851% | 0% | 49.62% | 0% | 0% | 14.74% | 31.12% | 17.92%
CZ 4B | 42.99% | 46.09% | 3.484% | 45.71% | 0% | 48.18% | 0% | 46.12% | 100% | -27.78% | 10.15% | 0% | 49.66% | 0% | 0% | 14.74% | 34.54% | 0.6023% | CZ 4B | 42.99% | 46.09% | 1.864% | 45.71% | 0% | 48.18% | 0% | 46.12% | 100% | -27.78% | 10.15% | 0% | 49.66% | 0% | 0% | 14.75% | 34.16% | 0.6023% | CZ 4B | 42.99% | 46.09% | 7.615% | 0% | 0% | 48.18% | 0% | 46.12% | 100% | -27.78% | 10.15% | 0% | 49.66% | 0% | 0% | 14.74% | 34.79% | 0.6023% | CZ 4B | 0% | 0% | 0.5062% | 45.71% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.65% | 0.6023% | CZ 4B | 42.99% | 46.09% | 3.339% | 45.71% | 0% | 48.18% | 0% | 46.12% | 100% | -27.78% | 10.15% | 0% | 49.66% | 0% | 0% | 14.74% | 34.52% | 0.6023%
CZ 4C | 42% | 45.97% | 3.428% | 47.04% | 0% | 50.9% | 0% | 55.18% | 100% | -94.55% | 10.3% | 0% | 49.64% | 0% | 0% | 14.74% | 35.81% | 1.875% | CZ 4C | 42% | 45.97% | 1.818% | 47.04% | 0% | 50.9% | 0% | 55.18% | 100% | -94.55% | 10.3% | 0% | 49.64% | 0% | 0% | 14.75% | 36.12% | 1.875% | CZ 4C | 42% | 45.97% | 7.648% | 0% | 0% | 50.9% | 0% | 55.18% | 100% | -94.55% | 10.3% | 0% | 49.64% | 0% | 0% | 14.74% | 35.57% | 1.875% | CZ 4C | 0% | 0% | 0.4889% | 47.04% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.05% | 1.875% | CZ 4C | 42% | 45.97% | 3.283% | 47.04% | 0% | 50.9% | 0% | 55.18% | 100% | -94.55% | 10.3% | 0% | 49.64% | 0% | 0% | 14.74% | 35.83% | 1.875%
CZ 5A | 42.64% | 45.87% | 3.392% | 50.5% | 0% | 36.59% | 0% | 30.72% | 1.643% | 9.96% | 9.831% | 0% | 49.6% | 0% | 0% | 14.74% | 31.08% | 18.43% | CZ 5A | 42.64% | 45.87% | 1.8% | 50.5% | 0% | 36.59% | 0% | 30.72% | 1.643% | 9.96% | 9.831% | 0% | 49.6% | 0% | 0% | 14.75% | 34.01% | 18.43% | CZ 5A | 42.64% | 45.87% | 7.681% | 0% | 0% | 36.59% | 0% | 30.72% | 1.643% | 9.96% | 9.831% | 0% | 49.6% | 0% | 0% | 14.74% | 28.66% | 18.43% | CZ 5A | 0% | 0% | 0.5038% | 50.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.69% | 18.43% | CZ 5A | 42.64% | 45.87% | 3.247% | 50.5% | 0% | 36.59% | 0% | 30.72% | 1.643% | 9.96% | 9.831% | 0% | 49.6% | 0% | 0% | 14.74% | 31.25% | 18.43%
CZ 5B | 42.28% | 46.14% | 3.38% | 42.38% | 0% | 47.1% | 0% | 51.11% | 100% | -101.6% | 10.1% | 0% | 49.63% | 0% | 0% | 14.74% | 34.52% | 4.478% | CZ 5B | 42.28% | 46.14% | 1.783% | 42.38% | 0% | 47.1% | 0% | 51.11% | 100% | -101.6% | 10.1% | 0% | 49.63% | 0% | 0% | 14.75% | 34.21% | 4.478% | CZ 5B | 42.28% | 46.14% | 7.648% | 0% | 0% | 47.1% | 0% | 51.11% | 100% | -101.6% | 10.1% | 0% | 49.63% | 0% | 0% | 14.74% | 34.76% | 4.478% | CZ 5B | 0% | 0% | 0.4774% | 42.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.3% | 4.478% | CZ 5B | 42.28% | 46.14% | 3.235% | 42.38% | 0% | 47.1% | 0% | 51.11% | 100% | -101.6% | 10.1% | 0% | 49.63% | 0% | 0% | 14.74% | 34.5% | 4.478%
CZ 5C | 40.12% | 45.85% | 3.383% | 66.49% | 0% | 46.63% | 0% | 34.99% | 15.07% | 21.43% | 10.23% | 0% | 49.62% | 0% | 0% | 14.74% | 34.01% | 0% | CZ 5C | 40.12% | 45.85% | 1.772% | 66.49% | 0% | 46.63% | 0% | 34.99% | 15.07% | 21.43% | 10.23% | 0% | 49.62% | 0% | 0% | 14.75% | 39.74% | 0% | CZ 5C | 40.12% | 45.85% | 7.681% | 0% | 0% | 46.63% | 0% | 34.99% | 15.07% | 21.43% | 10.23% | 0% | 49.62% | 0% | 0% | 14.74% | 29.21% | 0% | CZ 5C | 0% | 0% | 0.4542% | 66.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.41% | 0% | CZ 5C | 40.12% | 45.85% | 3.237% | 66.49% | 0% | 46.63% | 0% | 34.99% | 15.07% | 21.43% | 10.23% | 0% | 49.62% | 0% | 0% | 14.74% | 34.34% | 0%
CZ 6A | 42.25% | 45.81% | 3.315% | 49.9% | 0% | 37.62% | 0% | 32.21% | 3.299% | 6.738% | 9.822% | 0% | 49.59% | 0% | 0% | 14.74% | 31.47% | 3.366% | CZ 6A | 42.25% | 45.81% | 1.742% | 49.9% | 0% | 37.62% | 0% | 32.21% | 3.299% | 6.738% | 9.822% | 0% | 49.59% | 0% | 0% | 14.75% | 34.76% | 3.366% | CZ 6A | 42.25% | 45.81% | 7.714% | 0% | 0% | 37.62% | 0% | 32.21% | 3.299% | 6.738% | 9.822% | 0% | 49.59% | 0% | 0% | 14.74% | 28.52% | 3.366% | CZ 6A | 0% | 0% | 0.4819% | 49.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.21% | 3.366% | CZ 6A | 42.25% | 45.81% | 3.171% | 49.9% | 0% | 37.62% | 0% | 32.21% | 3.299% | 6.738% | 9.822% | 0% | 49.59% | 0% | 0% | 14.74% | 31.67% | 3.366%
CZ 6B | 42.23% | 46.03% | 3.309% | 56.28% | 0% | 40.04% | 0% | 21.97% | -6.813% | -14.8% | 9.948% | 0% | 49.64% | 0% | 0% | 14.74% | 30.89% | 0.7502% | CZ 6B | 42.23% | 46.03% | 1.74% | 56.28% | 0% | 40.04% | 0% | 21.97% | -6.813% | -14.8% | 9.948% | 0% | 49.64% | 0% | 0% | 14.75% | 35.45% | 0.7502% | CZ 6B | 42.23% | 46.03% | 7.714% | 0% | 0% | 40.04% | 0% | 21.97% | -6.813% | -14.8% | 9.948% | 0% | 49.64% | 0% | 0% | 14.74% | 26.96% | 0.7502% | CZ 6B | 0% | 0% | 0.4867% | 56.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 46.5% | 0.7502% | CZ 6B | 42.23% | 46.03% | 3.165% | 56.28% | 0% | 40.04% | 0% | 21.97% | -6.813% | -14.8% | 9.948% | 0% | 49.64% | 0% | 0% | 14.74% | 31.16% | 0.7502%
CZ 7 | 44.37% | 45.9% | 3.241% | 52.56% | 0% | 38.91% | 0% | 28.93% | -1.871% | 18.72% | 9.821% | 0% | 49.68% | 0% | 0% | 14.74% | 33.11% | 0.4665% | CZ 7 | 44.37% | 45.9% | 1.717% | 52.56% | 0% | 38.91% | 0% | 28.93% | -1.871% | 18.72% | 9.821% | 0% | 49.68% | 0% | 0% | 14.75% | 37.63% | 0.4665% | CZ 7 | 44.37% | 45.9% | 7.744% | 0% | 0% | 38.91% | 0% | 28.93% | -1.871% | 18.72% | 9.821% | 0% | 49.68% | 0% | 0% | 14.74% | 28.53% | 0.4665% | CZ 7 | 0% | 0% | 0.5278% | 52.56% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 46.01% | 0.4665% | CZ 7 | 44.37% | 45.9% | 3.099% | 52.56% | 0% | 38.91% | 0% | 28.93% | -1.871% | 18.72% | 9.821% | 0% | 49.68% | 0% | 0% | 14.74% | 33.4% | 0.4665%
CZ 8 | 41.14% | 45.23% | 3.056% | 45.1% | 0% | 47.04% | 0% | 29.18% | -11.28% | 16.96% | 9.975% | 0% | 49.6% | 0% | 0% | 14.74% | 32.35% | 0.06613% | CZ 8 | 41.14% | 45.23% | 1.572% | 45.1% | 0% | 47.04% | 0% | 29.18% | -11.28% | 16.96% | 9.975% | 0% | 49.6% | 0% | 0% | 14.75% | 36.13% | 0.06613% | CZ 8 | 41.14% | 45.23% | 7.709% | 0% | 0% | 47.04% | 0% | 29.18% | -11.28% | 16.96% | 9.975% | 0% | 49.6% | 0% | 0% | 14.74% | 27.43% | 0.06613% | CZ 8 | 0% | 0% | 0.4456% | 45.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.31% | 0.06613% | CZ 8 | 41.14% | 45.23% | 2.916% | 45.1% | 0% | 47.04% | 0% | 29.18% | -11.28% | 16.96% | 9.975% | 0% | 49.6% | 0% | 0% | 14.74% | 32.62% | 0.06613%
Us Weighted | 41.58% | 46.03% | 3.516% | 41.99% | 0% | 45.62% | 0% | 37.13% | 37.71% | 2.739% | 9.96% | 0% | 49.61% | 0% | 0% | 14.74% | 32.6% | 100% | Us Weighted | 41.58% | 46.03% | 1.863% | 41.99% | 0% | 45.62% | 0% | 37.13% | 37.71% | 2.739% | 9.96% | 0% | 49.61% | 0% | 0% | 14.75% | 32.3% | 100% | Us Weighted | 41.58% | 46.03% | 7.624% | 0% | 0% | 45.62% | 0% | 37.13% | 37.71% | 2.739% | 9.96% | 0% | 49.61% | 0% | 0% | 14.74% | 32.8% | 100% | Us Weighted | 0% | 0% | 0.4592% | 41.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.07% | 100% | Us Weighted | 41.58% | 46.03% | 3.369% | 41.99% | 0% | 45.62% | 0% | 37.13% | 37.71% | 2.739% | 9.96% | 0% | 49.61% | 0% | 0% | 14.74% | 32.58% | 100%

## SecSchool
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Secondary School |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Secondary School | [14 empty] | Prototype Floor Area: | 210887 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.25199 | 0.015699 | 0.042364 | 0.035029 | 0 | 0.22937 | 0 | 0.11089 | 0.031537 | 0.0066751 | 0.026107 | 0.0089444 | 0.0055594 | 0.07308 | 0 | 0.25915 | 1.0964 |  | STD2013 | 8.3336 | 0.5192 | 2.8532 | 3.5382 | 0 | 7.5856 | 0 | 3.6671 | 1.043 | 0.22076 | 0.86339 | 0.29581 | 0.18386 | 4.0631 | 0 | 8.57 | 41.737 |  | STD2013 | 2.4417 | 0.15212 | 0.20338 | 0 | 0 | 2.2226 | 0 | 1.0745 | 0.30559 | 0.064681 | 0.25297 | 0.086671 | 0.053869 | 0.47333 | 0 | 2.5112 | 9.8425 |  | STD2013 | 0 | 0 | 0.021591 | 0.035382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.08145 |  | STD2013 | 25.5623 | 1.5926 | 4.489 | 3.8673 | 0 | 23.2681 | 0 | 11.2486 | 3.1992 | 0.67714 | 2.6483 | 0.90736 | 0.56396 | 7.6306 | 0 | 26.2895 | 111.944
STD2010 | 0.2902 | 0.015699 | 0.042397 | 0.035366 | 0 | 0.312 | 0 | 0.13711 | 0.038582 | 0.0099102 | 0.028707 | 0.0089676 | 0.0060306 | 0.07308 | 0 | 0.2872 | 1.2853 |  | STD2010 | 9.5974 | 0.5192 | 2.8555 | 3.5723 | 0 | 10.3183 | 0 | 4.5344 | 1.276 | 0.32774 | 0.94938 | 0.29657 | 0.19944 | 4.0631 | 0 | 9.4978 | 48.0071 |  | STD2010 | 2.812 | 0.15212 | 0.20354 | 0 | 0 | 3.0232 | 0 | 1.3286 | 0.37385 | 0.096028 | 0.27817 | 0.086895 | 0.058435 | 0.47333 | 0 | 2.783 | 11.6692 |  | STD2010 | 0 | 0 | 0.021608 | 0.035723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.081807 |  | STD2010 | 29.4389 | 1.5926 | 4.4926 | 3.9045 | 0 | 31.6503 | 0 | 13.9087 | 3.9138 | 1.0053 | 2.9121 | 0.9097 | 0.61176 | 7.6306 | 0 | 29.1354 | 131.1063
STD2007 | 0.4479 | 0.030025 | 0.042419 | 0.084078 | 0 | 0.42944 | 0 | 0.18602 | 0.047893 | 0.028042 | 0.028726 | 0.010297 | 0.010788 | 0.07308 | 0 | 0.2885 | 1.7072 |  | STD2007 | 14.8126 | 0.99297 | 2.8577 | 8.4927 | 0 | 14.2023 | 0 | 6.152 | 1.5839 | 0.92739 | 0.95003 | 0.34054 | 0.35677 | 4.0631 | 0 | 9.5406 | 65.2726 |  | STD2007 | 4.3401 | 0.29094 | 0.20354 | 0 | 0 | 4.1612 | 0 | 1.8025 | 0.46408 | 0.27172 | 0.27835 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 15.2856 |  | STD2007 | 0 | 0 | 0.02163 | 0.084927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.13103 |  | STD2007 | 45.436 | 3.0458 | 4.495 | 9.2825 | 0 | 43.5639 | 0 | 18.8705 | 4.8584 | 2.8447 | 2.9141 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 174.3471
STD2004 | 0.4479 | 0.030025 | 0.042426 | 0.11526 | 0 | 0.47537 | 0 | 0.24849 | 0.073976 | 0.030176 | 0.02872 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.875 |  | STD2004 | 14.8126 | 0.99297 | 2.8583 | 11.6425 | 0 | 15.7211 | 0 | 8.218 | 2.4465 | 0.99798 | 0.94983 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 72.9409 |  | STD2004 | 4.3401 | 0.29094 | 0.20354 | 0 | 0 | 4.6063 | 0 | 2.4079 | 0.71681 | 0.2924 | 0.2783 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 16.6094 |  | STD2004 | 0 | 0 | 0.021636 | 0.11643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.16254 |  | STD2004 | 45.436 | 3.0458 | 4.4957 | 12.7253 | 0 | 48.2229 | 0 | 25.2079 | 7.5043 | 3.0612 | 2.9135 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 191.6487
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 6.0786e-06 | 0.031183 | 0 | 0.045927 | 0 | 0.062473 | 0.026083 | 0.0021343 | -5.9229e-06 | 0 | -5.0708e-07 | 0 | 0 | 0 | 0.1678 |  | 2004-2007 | 0 | 0 | 0.00061184 | 3.1498 | 0 | 1.5189 | 0 | 2.0661 | 0.86259 | 0.070585 | -0.00019588 | 0 | -1.677e-05 | 0 | 0 | 0 | 7.6683 |  | 2004-2007 | 0 | 0 | 3.0837e-07 | 0 | 0 | 0.44502 | 0 | 0.60535 | 0.25274 | 0.020681 | -5.7392e-05 | 0 | -4.9135e-06 | 0 | 0 | 0 | 1.3237 |  | 2004-2007 | 0 | 0 | 6.1078e-06 | 0.031498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031504 |  | 2004-2007 | 0 | 0 | 0.00067082 | 3.4428 | 0 | 4.6589 | 0 | 6.3374 | 2.6459 | 0.21651 | -0.00060084 | 0 | -5.1439e-05 | 0 | 0 | 0 | 17.3016
2007-2010 | 0.1577 | 0.014326 | 2.2166e-05 | 0.048712 | 0 | 0.11744 | 0 | 0.048912 | 0.0093112 | 0.018132 | 1.953e-05 | 0.0013294 | 0.0047572 | 0 | 0 | 0.0012941 | 0.42195 |  | 2007-2010 | 5.2152 | 0.47377 | 0.002239 | 4.9204 | 0 | 3.884 | 0 | 1.6176 | 0.30793 | 0.59965 | 0.00064588 | 0.043967 | 0.15733 | 0 | 0 | 0.042797 | 17.2655 |  | 2007-2010 | 1.528 | 0.13881 | 0 | 0 | 0 | 1.138 | 0 | 0.47395 | 0.090224 | 0.17569 | 0.00018924 | 0.012882 | 0.046097 | 0 | 0 | 0.012539 | 3.6164 |  | 2007-2010 | 0 | 0 | 2.239e-05 | 0.049204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049226 |  | 2007-2010 | 15.9971 | 1.4532 | 0.0024472 | 5.378 | 0 | 11.9137 | 0 | 4.9617 | 0.94455 | 1.8393 | 0.0019812 | 0.13486 | 0.48259 | 0 | 0 | 0.13127 | 43.2408
2010-2013 | 0.038214 | 0 | 3.3772e-05 | 0.00033708 | 0 | 0.08263 | 0 | 0.026223 | 0.0070445 | 0.0032351 | 0.0026002 | 2.3109e-05 | 0.00047123 | 0 | 0 | 0.028054 | 0.18887 |  | 2010-2013 | 1.2638 | 0 | 0.0022501 | 0.034049 | 0 | 2.7327 | 0 | 0.86724 | 0.23297 | 0.10699 | 0.085994 | 0.00076425 | 0.015584 | 0 | 0 | 0.92779 | 6.2701 |  | 2010-2013 | 0.37029 | 0 | 0.00016562 | 0 | 0 | 0.80067 | 0 | 0.2541 | 0.06826 | 0.031348 | 0.025196 | 0.00022392 | 0.0045661 | 0 | 0 | 0.27184 | 1.8267 |  | 2010-2013 | 0 | 0 | 1.6848e-05 | 0.00034049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00035734 |  | 2010-2013 | 3.8766 | 0 | 0.0035754 | 0.037215 | 0 | 8.3822 | 0 | 2.6602 | 0.71461 | 0.32818 | 0.26378 | 0.0023442 | 0.047803 | 0 | 0 | 2.8459 | 19.1623
2004-2013 | 0.19591 | 0.014326 | 6.2016e-05 | 0.080232 | 0 | 0.246 | 0 | 0.13761 | 0.042438 | 0.023501 | 0.0026138 | 0.0013525 | 0.0052279 | 0 | 0 | 0.029348 | 0.77862 |  | 2004-2013 | 6.479 | 0.47377 | 0.0051009 | 8.1043 | 0 | 8.1355 | 0 | 4.5509 | 1.4035 | 0.77722 | 0.086444 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 31.204 |  | 2004-2013 | 1.8983 | 0.13881 | 0.00016592 | 0 | 0 | 2.3837 | 0 | 1.3334 | 0.41122 | 0.22772 | 0.025328 | 0.013106 | 0.050658 | 0 | 0 | 0.28438 | 6.7668 |  | 2004-2013 | 0 | 0 | 4.5346e-05 | 0.081043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081088 |  | 2004-2013 | 19.8737 | 1.4532 | 0.0066934 | 8.858 | 0 | 24.9548 | 0 | 13.9594 | 4.3051 | 2.384 | 0.26516 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 79.7047
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.01433% | 27.05% |  | 9.661% |  | 25.14% | 35.26% | 7.073% | -0.02062% | 0% | -0.004701% | 0% |  | 0% | 8.949% |  | 2004-2007 | 0% | 0% | 0.02141% | 27.05% |  | 9.661% |  | 25.14% | 35.26% | 7.073% | -0.02062% | 0% | -0.004701% | 0% |  | 0% | 10.51% |  | 2004-2007 | 0% | 0% | 0.0001515% |  |  | 9.661% |  | 25.14% | 35.26% | 7.073% | -0.02062% | 0% | -0.004701% | 0% |  | 0% | 7.97% |  | 2004-2007 |  |  | 0.02823% | 27.05% | [9 empty] | 0% |  |  | 19.38% |  | 2004-2007 | 0% | 0% | 0.01492% | 27.05% |  | 9.661% |  | 25.14% | 35.26% | 7.073% | -0.02062% | 0% | -0.004701% | 0% |  | 0% | 9.028%
2007-2010 | 35.21% | 47.71% | 0.05225% | 57.94% |  | 27.35% |  | 26.29% | 19.44% | 64.66% | 0.06799% | 12.91% | 44.1% | 0% |  | 0.4486% | 24.72% |  | 2007-2010 | 35.21% | 47.71% | 0.07835% | 57.94% |  | 27.35% |  | 26.29% | 19.44% | 64.66% | 0.06799% | 12.91% | 44.1% | 0% |  | 0.4486% | 26.45% |  | 2007-2010 | 35.21% | 47.71% | 0% |  |  | 27.35% |  | 26.29% | 19.44% | 64.66% | 0.06799% | 12.91% | 44.1% | 0% |  | 0.4485% | 23.66% |  | 2007-2010 |  |  | 0.1035% | 57.94% | [9 empty] | 0% |  |  | 37.57% |  | 2007-2010 | 35.21% | 47.71% | 0.05444% | 57.94% |  | 27.35% |  | 26.29% | 19.44% | 64.66% | 0.06799% | 12.91% | 44.1% | 0% |  | 0.4485% | 24.8%
2010-2013 | 13.17% | 0% | 0.07965% | 0.9531% |  | 26.48% |  | 19.13% | 18.26% | 32.64% | 9.058% | 0.2577% | 7.814% | 0% |  | 9.768% | 14.69% |  | 2010-2013 | 13.17% | 0% | 0.0788% | 0.9531% |  | 26.48% |  | 19.13% | 18.26% | 32.64% | 9.058% | 0.2577% | 7.814% | 0% |  | 9.768% | 13.06% |  | 2010-2013 | 13.17% | 0% | 0.08137% |  |  | 26.48% |  | 19.13% | 18.26% | 32.64% | 9.058% | 0.2577% | 7.814% | 0% |  | 9.768% | 15.65% |  | 2010-2013 |  |  | 0.07797% | 0.9531% | [9 empty] | 0% |  |  | 0.4368% |  | 2010-2013 | 13.17% | 0% | 0.07958% | 0.9531% |  | 26.48% |  | 19.13% | 18.26% | 32.64% | 9.058% | 0.2577% | 7.814% | 0% |  | 9.768% | 14.62%
2004-2013 | 43.74% | 47.71% | 0.1462% | 69.61% |  | 51.75% |  | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% |  | 10.17% | 41.53% |  | 2004-2013 | 43.74% | 47.71% | 0.1785% | 69.61% |  | 51.75% |  | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% |  | 10.17% | 42.78% |  | 2004-2013 | 43.74% | 47.71% | 0.08152% |  |  | 51.75% |  | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% |  | 10.17% | 40.74% |  | 2004-2013 |  |  | 0.2096% | 69.61% | [9 empty] | 0% |  |  | 49.89% |  | 2004-2013 | 43.74% | 47.71% | 0.1489% | 69.61% |  | 51.75% |  | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% |  | 10.17% | 41.59%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.24645 | 0.015694 | 0.037167 | 0.00093795 | 0 | 0.48653 | 0 | 0.10535 | 0.051276 | 0.011684 | 0.026432 | 0.0089444 | 0.0055578 | 0.07308 | 0 | 0.25915 | 1.3283 | 1.546% | CZ 1A | 8.1506 | 0.51901 | 2.3284 | 0.094743 | 0 | 16.0903 | 0 | 3.484 | 1.6958 | 0.38639 | 0.87416 | 0.29581 | 0.18381 | 4.0631 | 0 | 8.57 | 46.7361 | 1.546% | CZ 1A | 2.3881 | 0.15207 | 0.20337 | 0 | 0 | 4.7144 | 0 | 1.0208 | 0.49685 | 0.11321 | 0.25613 | 0.086671 | 0.053855 | 0.47333 | 0 | 2.5112 | 12.47 | 1.546% | CZ 1A | 0 | 0 | 0.016343 | 0.00094743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.041767 | 1.546% | CZ 1A | 25.0009 | 1.592 | 3.9154 | 0.10355 | 0 | 49.3553 | 0 | 10.6867 | 5.2015 | 1.1852 | 2.6814 | 0.90736 | 0.5638 | 7.6306 | 0 | 26.2895 | 135.1133 | 1.546%
CZ 1B | 0.24803 | 0.015691 | 0.0368 | 0.011422 | 0 | 0.45211 | 0 | 0.12371 | 0.047362 | 0.011091 | 0.025887 | 0.0089444 | 0.0055578 | 0.07308 | 0 | 0.25915 | 1.3188 | 0% | CZ 1B | 8.2028 | 0.51892 | 2.2912 | 1.1538 | 0 | 14.952 | 0 | 4.0914 | 1.5663 | 0.36679 | 0.85613 | 0.29581 | 0.18381 | 4.0631 | 0 | 8.57 | 47.1121 | 0% | CZ 1B | 2.4034 | 0.15204 | 0.20337 | 0 | 0 | 4.3809 | 0 | 1.1988 | 0.45893 | 0.10747 | 0.25084 | 0.086671 | 0.053855 | 0.47333 | 0 | 2.5112 | 12.2807 | 0% | CZ 1B | 0 | 0 | 0.015971 | 0.011538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.051986 | 0% | CZ 1B | 25.161 | 1.5917 | 3.8748 | 1.2611 | 0 | 45.8636 | 0 | 12.55 | 4.8045 | 1.1251 | 2.6261 | 0.90736 | 0.5638 | 7.6306 | 0 | 26.2895 | 134.2492 | 0%
CZ 2A | 0.25057 | 0.015687 | 0.039479 | 0.010466 | 0 | 0.35623 | 0 | 0.10196 | 0.035055 | 0.0094189 | 0.026343 | 0.0089444 | 0.0055592 | 0.07308 | 0 | 0.25915 | 1.1919 | 14.7% | CZ 2A | 8.2868 | 0.51878 | 2.5619 | 1.0572 | 0 | 11.781 | 0 | 3.3719 | 1.1593 | 0.31149 | 0.87119 | 0.29581 | 0.18385 | 4.0631 | 0 | 8.57 | 43.0323 | 14.7% | CZ 2A | 2.428 | 0.152 | 0.20337 | 0 | 0 | 3.4518 | 0 | 0.98796 | 0.33967 | 0.091267 | 0.25526 | 0.086671 | 0.053868 | 0.47333 | 0 | 2.5112 | 11.0344 | 14.7% | CZ 2A | 0 | 0 | 0.018678 | 0.010572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.053726 | 14.7% | CZ 2A | 25.4188 | 1.5913 | 4.1706 | 1.1555 | 0 | 36.1369 | 0 | 10.343 | 3.556 | 0.95548 | 2.6723 | 0.90736 | 0.56394 | 7.6306 | 0 | 26.2895 | 121.3912 | 14.7%
CZ 2B | 0.25174 | 0.015681 | 0.038481 | 0.016126 | 0 | 0.38425 | 0 | 0.11908 | 0.03332 | 0.0082362 | 0.025918 | 0.0089444 | 0.0055592 | 0.07308 | 0 | 0.25915 | 1.2396 | 2.216% | CZ 2B | 8.3255 | 0.5186 | 2.461 | 1.6289 | 0 | 12.7078 | 0 | 3.9383 | 1.1019 | 0.27238 | 0.85716 | 0.29581 | 0.18385 | 4.0631 | 0 | 8.57 | 44.9244 | 2.216% | CZ 2B | 2.4393 | 0.15195 | 0.20337 | 0 | 0 | 3.7233 | 0 | 1.1539 | 0.32287 | 0.079808 | 0.25115 | 0.086671 | 0.053868 | 0.47333 | 0 | 2.5112 | 11.4508 | 2.216% | CZ 2B | 0 | 0 | 0.017669 | 0.016289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.058435 | 2.216% | CZ 2B | 25.5375 | 1.5908 | 4.0604 | 1.7804 | 0 | 38.9796 | 0 | 12.0803 | 3.3801 | 0.83551 | 2.6293 | 0.90736 | 0.56394 | 7.6306 | 0 | 26.2895 | 126.2652 | 2.216%
CZ 3A | 0.25324 | 0.015689 | 0.041174 | 0.026765 | 0 | 0.27609 | 0 | 0.1041 | 0.037118 | 0.007543 | 0.026194 | 0.0089444 | 0.0055592 | 0.07308 | 0 | 0.25915 | 1.1346 | 18.27% | CZ 3A | 8.3749 | 0.51887 | 2.7331 | 2.7035 | 0 | 9.1305 | 0 | 3.4427 | 1.2275 | 0.24946 | 0.86629 | 0.29581 | 0.18385 | 4.0631 | 0 | 8.57 | 42.3597 | 18.27% | CZ 3A | 2.4538 | 0.15203 | 0.20337 | 0 | 0 | 2.6752 | 0 | 1.0087 | 0.35967 | 0.07309 | 0.25382 | 0.086671 | 0.053868 | 0.47333 | 0 | 2.5112 | 10.3048 | 18.27% | CZ 3A | 0 | 0 | 0.020389 | 0.027035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.071901 | 18.27% | CZ 3A | 25.689 | 1.5916 | 4.3577 | 2.9549 | 0 | 28.0069 | 0 | 10.5601 | 3.7654 | 0.76518 | 2.6572 | 0.90736 | 0.56394 | 7.6306 | 0 | 26.2895 | 115.7395 | 18.27%
CZ 3B | 0.25082 | 0.015681 | 0.04065 | 0.043865 | 0 | 0.23272 | 0 | 0.1088 | 0 | 0.0074872 | 0.025913 | 0.0089444 | 0.0055606 | 0.07308 | 0 | 0.25915 | 1.0727 | 7.906% | CZ 3B | 8.2949 | 0.5186 | 2.6801 | 4.4308 | 0 | 7.6965 | 0 | 3.5981 | 0 | 0.24761 | 0.85698 | 0.29581 | 0.1839 | 4.0631 | 0 | 8.57 | 41.4364 | 7.906% | CZ 3B | 2.4304 | 0.15195 | 0.20337 | 0 | 0 | 2.255 | 0 | 1.0542 | 0 | 0.07255 | 0.25109 | 0.086671 | 0.053881 | 0.47333 | 0 | 2.5112 | 9.5437 | 7.906% | CZ 3B | 0 | 0 | 0.01986 | 0.044308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.088644 | 7.906% | CZ 3B | 25.4436 | 1.5908 | 4.2998 | 4.8429 | 0 | 23.6081 | 0 | 11.0369 | 0 | 0.75953 | 2.6287 | 0.90736 | 0.56408 | 7.6306 | 0 | 26.2895 | 109.6017 | 7.906%
CZ 3C | 0.25266 | 0.015684 | 0.042485 | 0.047832 | 0 | 0.074969 | 0 | 0.087997 | 0 | 0.0027173 | 0.025932 | 0.0089444 | 0.0055606 | 0.07308 | 0 | 0.25915 | 0.89701 | 1.057% | CZ 3C | 8.3558 | 0.51869 | 2.8655 | 4.8315 | 0 | 2.4793 | 0 | 2.9102 | 0 | 0.089865 | 0.85761 | 0.29581 | 0.1839 | 4.0631 | 0 | 8.57 | 36.0213 | 1.057% | CZ 3C | 2.4482 | 0.15198 | 0.20337 | 0 | 0 | 0.72644 | 0 | 0.85267 | 0 | 0.02633 | 0.25128 | 0.086671 | 0.053881 | 0.47333 | 0 | 2.5112 | 7.7853 | 1.057% | CZ 3C | 0 | 0 | 0.021714 | 0.048315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.094506 | 1.057% | CZ 3C | 25.6304 | 1.591 | 4.5025 | 5.2808 | 0 | 7.6051 | 0 | 8.9266 | 0 | 0.27565 | 2.6306 | 0.90736 | 0.56408 | 7.6306 | 0 | 26.2895 | 91.8343 | 1.057%
CZ 4A | 0.25171 | 0.015687 | 0.043137 | 0.021047 | 0 | 0.20501 | 0 | 0.11525 | 0.039833 | 0.006151 | 0.026099 | 0.0089444 | 0.0055606 | 0.07308 | 0 | 0.25915 | 1.0707 | 19.43% | CZ 4A | 8.3244 | 0.51878 | 2.9314 | 2.1259 | 0 | 6.7798 | 0 | 3.8115 | 1.3173 | 0.20342 | 0.86314 | 0.29581 | 0.1839 | 4.0631 | 0 | 8.57 | 39.9886 | 19.43% | CZ 4A | 2.439 | 0.152 | 0.20337 | 0 | 0 | 1.9865 | 0 | 1.1168 | 0.38597 | 0.059602 | 0.2529 | 0.086671 | 0.053881 | 0.47333 | 0 | 2.5112 | 9.7212 | 19.43% | CZ 4A | 0 | 0 | 0.022373 | 0.021259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.068108 | 19.43% | CZ 4A | 25.5342 | 1.5913 | 4.5745 | 2.3236 | 0 | 20.7964 | 0 | 11.6913 | 4.0407 | 0.62398 | 2.6476 | 0.90736 | 0.56408 | 7.6306 | 0 | 26.2895 | 109.2151 | 19.43%
CZ 4B | 0.25085 | 0.015676 | 0.04282 | 0.075517 | 0 | 0.16226 | 0 | 0.11547 | 0 | 0.0059335 | 0.025889 | 0.0089444 | 0.0055592 | 0.07308 | 0 | 0.25915 | 1.0411 | 0.6104% | CZ 4B | 8.296 | 0.51842 | 2.8994 | 7.628 | 0 | 5.366 | 0 | 3.8188 | 0 | 0.19623 | 0.85617 | 0.29581 | 0.18385 | 4.0631 | 0 | 8.57 | 42.6919 | 0.6104% | CZ 4B | 2.4307 | 0.1519 | 0.20337 | 0 | 0 | 1.5722 | 0 | 1.1189 | 0 | 0.057495 | 0.25086 | 0.086671 | 0.053868 | 0.47333 | 0 | 2.5112 | 8.9105 | 0.6104% | CZ 4B | 0 | 0 | 0.022053 | 0.07628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.12281 | 0.6104% | CZ 4B | 25.4472 | 1.5902 | 4.5395 | 8.3374 | 0 | 16.4597 | 0 | 11.7138 | 0 | 0.60191 | 2.6262 | 0.90736 | 0.56394 | 7.6306 | 0 | 26.2895 | 106.7073 | 0.6104%
CZ 4C | 0.25555 | 0.0157 | 0.043653 | 0.1074 | 0 | 0.10415 | 0 | 0.091375 | 0 | 0.0042765 | 0.025916 | 0.0089444 | 0.0055619 | 0.07308 | 0 | 0.25915 | 0.99475 | 2.341% | CZ 4C | 8.4514 | 0.51923 | 2.9835 | 10.8483 | 0 | 3.4443 | 0 | 3.0219 | 0 | 0.14143 | 0.85707 | 0.29581 | 0.18394 | 4.0631 | 0 | 8.57 | 43.38 | 2.341% | CZ 4C | 2.4762 | 0.15213 | 0.20337 | 0 | 0 | 1.0092 | 0 | 0.88541 | 0 | 0.041438 | 0.25112 | 0.086671 | 0.053894 | 0.47333 | 0 | 2.5112 | 8.1439 | 2.341% | CZ 4C | 0 | 0 | 0.022894 | 0.10848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.15585 | 2.341% | CZ 4C | 25.9236 | 1.5927 | 4.6314 | 11.8572 | 0 | 10.5651 | 0 | 9.2693 | 0 | 0.43382 | 2.629 | 0.90736 | 0.56422 | 7.6306 | 0 | 26.2895 | 102.2938 | 2.341%
CZ 5A | 0.25207 | 0.015738 | 0.044506 | 0.038999 | 0 | 0.16709 | 0 | 0.12122 | 0.037284 | 0.0053381 | 0.026068 | 0.0089444 | 0.0055578 | 0.07308 | 0 | 0.25915 | 1.0551 | 22.02% | CZ 5A | 8.3363 | 0.52049 | 3.0696 | 3.9393 | 0 | 5.526 | 0 | 4.009 | 1.233 | 0.17654 | 0.86211 | 0.29581 | 0.18381 | 4.0631 | 0 | 8.57 | 40.7851 | 22.02% | CZ 5A | 2.4425 | 0.1525 | 0.20339 | 0 | 0 | 1.6191 | 0 | 1.1746 | 0.36127 | 0.051725 | 0.2526 | 0.086671 | 0.053855 | 0.47333 | 0 | 2.5112 | 9.3828 | 22.02% | CZ 5A | 0 | 0 | 0.023754 | 0.039393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.087624 | 22.02% | CZ 5A | 25.5707 | 1.5965 | 4.7256 | 4.3057 | 0 | 16.9503 | 0 | 12.2971 | 3.7822 | 0.54151 | 2.6444 | 0.90736 | 0.5638 | 7.6306 | 0 | 26.2895 | 107.8054 | 22.02%
CZ 5B | 0.25469 | 0.015647 | 0.044249 | 0.12966 | 0 | 0.12764 | 0 | 0.10079 | 0 | 0.0047645 | 0.025861 | 0.0089444 | 0.0055619 | 0.07308 | 0 | 0.25915 | 1.05 | 4.225% | CZ 5B | 8.4229 | 0.51748 | 3.0437 | 13.0974 | 0 | 4.2212 | 0 | 3.3331 | 0 | 0.15757 | 0.85528 | 0.29581 | 0.18394 | 4.0631 | 0 | 8.57 | 46.7614 | 4.225% | CZ 5B | 2.4679 | 0.15162 | 0.20337 | 0 | 0 | 1.2368 | 0 | 0.97659 | 0 | 0.046167 | 0.25059 | 0.086671 | 0.053894 | 0.47333 | 0 | 2.5112 | 8.4581 | 4.225% | CZ 5B | 0 | 0 | 0.023496 | 0.13097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.17895 | 4.225% | CZ 5B | 25.8362 | 1.5873 | 4.6972 | 14.3155 | 0 | 12.9479 | 0 | 10.224 | 0 | 0.48332 | 2.6235 | 0.90736 | 0.56422 | 7.6306 | 0 | 26.2895 | 108.1065 | 4.225%
CZ 5C | 0.26388 | 0.015717 | 0.044204 | 0.04938 | 0 | 0.063858 | 0 | 0.11459 | 0.032836 | 0.0019887 | 0.025882 | 0.0089444 | 0.005566 | 0.07308 | 0 | 0.25915 | 0.95908 | 0% | CZ 5C | 8.7268 | 0.51977 | 3.0392 | 4.9879 | 0 | 2.1119 | 0 | 3.7898 | 1.0859 | 0.065769 | 0.85595 | 0.29581 | 0.18408 | 4.0631 | 0 | 8.57 | 38.296 | 0% | CZ 5C | 2.5569 | 0.15229 | 0.20337 | 0 | 0 | 0.61877 | 0 | 1.1104 | 0.31818 | 0.01927 | 0.25079 | 0.086671 | 0.053934 | 0.47333 | 0 | 2.5112 | 8.3551 | 0% | CZ 5C | 0 | 0 | 0.023451 | 0.049879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.097806 | 0% | CZ 5C | 26.7685 | 1.5943 | 4.6923 | 5.4518 | 0 | 6.4779 | 0 | 11.6248 | 3.331 | 0.20174 | 2.6255 | 0.90736 | 0.56463 | 7.6306 | 0 | 26.2895 | 98.16 | 0%
CZ 6A | 0.25375 | 0.015747 | 0.045665 | 0.049741 | 0 | 0.11292 | 0 | 0.11867 | 0.035795 | 0.0039475 | 0.025993 | 0.0089444 | 0.0055578 | 0.07308 | 0 | 0.25915 | 1.009 | 4.008% | CZ 6A | 8.3917 | 0.52076 | 3.1866 | 5.0244 | 0 | 3.7344 | 0 | 3.9247 | 1.1838 | 0.13055 | 0.85964 | 0.29581 | 0.18381 | 4.0631 | 0 | 8.57 | 40.0694 | 4.008% | CZ 6A | 2.4588 | 0.15258 | 0.20339 | 0 | 0 | 1.0942 | 0 | 1.1499 | 0.34685 | 0.038251 | 0.25187 | 0.086671 | 0.053855 | 0.47333 | 0 | 2.5112 | 8.8208 | 4.008% | CZ 6A | 0 | 0 | 0.024925 | 0.050244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.099645 | 4.008% | CZ 6A | 25.7407 | 1.5974 | 4.8535 | 5.4916 | 0 | 11.4548 | 0 | 12.0387 | 3.6312 | 0.40045 | 2.6368 | 0.90736 | 0.5638 | 7.6306 | 0 | 26.2895 | 103.2365 | 4.008%
CZ 6B | 0.2547 | 0.015676 | 0.045811 | 0.038137 | 0 | 0.085475 | 0 | 0.1271 | 0.04249 | 0.0040141 | 0.025887 | 0.0089444 | 0.0055619 | 0.07308 | 0 | 0.25915 | 0.98603 | 0.8296% | CZ 6B | 8.4234 | 0.51842 | 3.2014 | 3.8523 | 0 | 2.8268 | 0 | 4.2032 | 1.4052 | 0.13275 | 0.85613 | 0.29581 | 0.18394 | 4.0631 | 0 | 8.57 | 38.5326 | 0.8296% | CZ 6B | 2.468 | 0.1519 | 0.20339 | 0 | 0 | 0.82824 | 0 | 1.2315 | 0.41172 | 0.038896 | 0.25084 | 0.086671 | 0.053894 | 0.47333 | 0 | 2.5112 | 8.7096 | 0.8296% | CZ 6B | 0 | 0 | 0.025073 | 0.038523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.088072 | 0.8296% | CZ 6B | 25.838 | 1.5902 | 4.8697 | 4.2105 | 0 | 8.6708 | 0 | 12.8929 | 4.3103 | 0.4072 | 2.6261 | 0.90736 | 0.56422 | 7.6306 | 0 | 26.2895 | 100.8074 | 0.8296%
CZ 7 | 0.23905 | 0.015711 | 0.047519 | 0.074748 | 0 | 0.085289 | 0 | 0.12674 | 0.039657 | 0.0034215 | 0.025897 | 0.0089444 | 0.0055524 | 0.07308 | 0 | 0.25915 | 1.0048 | 0.7271% | CZ 7 | 7.9056 | 0.51959 | 3.3739 | 7.5503 | 0 | 2.8206 | 0 | 4.1915 | 1.3115 | 0.11315 | 0.85644 | 0.29581 | 0.18363 | 4.0631 | 0 | 8.57 | 41.7553 | 0.7271% | CZ 7 | 2.3163 | 0.15224 | 0.20339 | 0 | 0 | 0.82644 | 0 | 1.2281 | 0.38427 | 0.033153 | 0.25094 | 0.086671 | 0.053802 | 0.47333 | 0 | 2.5112 | 8.5198 | 0.7271% | CZ 7 | 0 | 0 | 0.026798 | 0.075503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.12678 | 0.7271% | CZ 7 | 24.2495 | 1.5938 | 5.0582 | 8.2525 | 0 | 8.652 | 0 | 12.8571 | 4.023 | 0.34708 | 2.627 | 0.90736 | 0.56325 | 7.6306 | 0 | 26.2895 | 103.0509 | 0.7271%
CZ 8 | 0.25403 | 0.015801 | 0.049635 | 0.22799 | 0 | 0.042421 | 0 | 0.13786 | 0.040568 | 0.0037504 | 0.02573 | 0.0089444 | 0.0055633 | 0.07308 | 0 | 0.25915 | 1.1445 | 0.1192% | CZ 8 | 8.4011 | 0.52256 | 3.5875 | 23.029 | 0 | 1.4029 | 0 | 4.5591 | 1.3416 | 0.12403 | 0.85091 | 0.29581 | 0.18399 | 4.0631 | 0 | 8.57 | 56.9318 | 0.1192% | CZ 8 | 2.4615 | 0.15311 | 0.2034 | 0 | 0 | 0.41105 | 0 | 1.3358 | 0.3931 | 0.036341 | 0.24932 | 0.086671 | 0.053907 | 0.47333 | 0 | 2.5112 | 8.3687 | 0.1192% | CZ 8 | 0 | 0 | 0.028933 | 0.23029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.2837 | 0.1192% | CZ 8 | 25.7694 | 1.6029 | 5.2918 | 25.1707 | 0 | 4.3033 | 0 | 13.9846 | 4.1153 | 0.38045 | 2.6101 | 0.90736 | 0.56436 | 7.6306 | 0 | 26.2895 | 118.6205 | 0.1192%
Us Weighted | 0.25199 | 0.015699 | 0.042364 | 0.035029 | 0 | 0.22937 | 0 | 0.11089 | 0.031537 | 0.0066751 | 0.026107 | 0.0089444 | 0.0055594 | 0.07308 | 0 | 0.25915 | 1.0964 | 100% | Us Weighted | 8.3336 | 0.5192 | 2.8532 | 3.5382 | 0 | 7.5856 | 0 | 3.6671 | 1.043 | 0.22076 | 0.86339 | 0.29581 | 0.18386 | 4.0631 | 0 | 8.57 | 41.737 | 100% | Us Weighted | 2.4417 | 0.15212 | 0.20338 | 0 | 0 | 2.2226 | 0 | 1.0745 | 0.30559 | 0.064681 | 0.25297 | 0.086671 | 0.053869 | 0.47333 | 0 | 2.5112 | 9.8425 | 100% | Us Weighted | 0 | 0 | 0.021591 | 0.035382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.08145 | 100% | Us Weighted | 25.5623 | 1.5926 | 4.489 | 3.8673 | 0 | 23.2681 | 0 | 11.2486 | 3.1992 | 0.67714 | 2.6483 | 0.90736 | 0.56396 | 7.6306 | 0 | 26.2895 | 111.944 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.29248 | 0.015694 | 0.037211 | 0.0028495 | 0 | 0.76843 | 0 | 0.14365 | 0.080073 | 0.019848 | 0.028928 | 0.0089676 | 0.0060336 | 0.07308 | 0 | 0.2872 | 1.7644 | 1.546% | CZ 1A | 9.6727 | 0.51901 | 2.3315 | 0.28782 | 0 | 25.4129 | 0 | 4.7506 | 2.6481 | 0.65639 | 0.95669 | 0.29657 | 0.19954 | 4.0631 | 0 | 9.4978 | 61.2928 | 1.546% | CZ 1A | 2.8341 | 0.15207 | 0.20356 | 0 | 0 | 7.4459 | 0 | 1.3919 | 0.7759 | 0.19232 | 0.28031 | 0.086895 | 0.058465 | 0.47333 | 0 | 2.783 | 16.6778 | 1.546% | CZ 1A | 0 | 0 | 0.016368 | 0.0028782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.043723 | 1.546% | CZ 1A | 29.6699 | 1.592 | 3.92 | 0.31459 | 0 | 77.9513 | 0 | 14.5719 | 8.1229 | 2.0134 | 2.9346 | 0.9097 | 0.61207 | 7.6306 | 0 | 29.1354 | 179.3783 | 1.546%
CZ 1B | 0.29614 | 0.015691 | 0.036799 | 0.0157 | 0 | 0.54335 | 0 | 0.13964 | 0.049729 | 0.012806 | 0.029572 | 0.0089676 | 0.0060363 | 0.07308 | 0 | 0.2872 | 1.5147 | 0% | CZ 1B | 9.7937 | 0.51892 | 2.2912 | 1.5859 | 0 | 17.9693 | 0 | 4.618 | 1.6446 | 0.42352 | 0.978 | 0.29657 | 0.19963 | 4.0631 | 0 | 9.4978 | 53.8802 | 0% | CZ 1B | 2.8695 | 0.15204 | 0.20337 | 0 | 0 | 5.265 | 0 | 1.3531 | 0.48186 | 0.12409 | 0.28655 | 0.086895 | 0.058491 | 0.47333 | 0 | 2.783 | 14.1372 | 0% | CZ 1B | 0 | 0 | 0.015971 | 0.015859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.056306 | 0% | CZ 1B | 30.0411 | 1.5917 | 3.8747 | 1.7333 | 0 | 55.1189 | 0 | 14.1651 | 5.0446 | 1.2991 | 2.9999 | 0.9097 | 0.61234 | 7.6306 | 0 | 29.1354 | 154.1566 | 0%
CZ 2A | 0.29681 | 0.015687 | 0.039518 | 0.017808 | 0 | 0.51989 | 0 | 0.13318 | 0.041588 | 0.015261 | 0.028825 | 0.0089676 | 0.0060336 | 0.07308 | 0 | 0.2872 | 1.4839 | 14.7% | CZ 2A | 9.8161 | 0.51878 | 2.5646 | 1.7988 | 0 | 17.1934 | 0 | 4.4046 | 1.3754 | 0.50471 | 0.95328 | 0.29657 | 0.19954 | 4.0631 | 0 | 9.4978 | 53.1866 | 14.7% | CZ 2A | 2.8761 | 0.152 | 0.20356 | 0 | 0 | 5.0376 | 0 | 1.2905 | 0.40298 | 0.14788 | 0.27931 | 0.086895 | 0.058465 | 0.47333 | 0 | 2.783 | 13.7917 | 14.7% | CZ 2A | 0 | 0 | 0.018698 | 0.017988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.061163 | 14.7% | CZ 2A | 30.1097 | 1.5913 | 4.1747 | 1.9661 | 0 | 52.7388 | 0 | 13.5106 | 4.2188 | 1.5481 | 2.9241 | 0.9097 | 0.61207 | 7.6306 | 0 | 29.1354 | 151.0699 | 14.7%
CZ 2B | 0.29914 | 0.015681 | 0.03848 | 0.019619 | 0 | 0.45654 | 0 | 0.14051 | 0.029638 | 0.009843 | 0.029606 | 0.0089676 | 0.006035 | 0.07308 | 0 | 0.2872 | 1.4143 | 2.216% | CZ 2B | 9.893 | 0.5186 | 2.4609 | 1.9817 | 0 | 15.0983 | 0 | 4.647 | 0.98016 | 0.32552 | 0.97913 | 0.29657 | 0.19958 | 4.0631 | 0 | 9.4978 | 50.9415 | 2.216% | CZ 2B | 2.8986 | 0.15195 | 0.20337 | 0 | 0 | 4.4238 | 0 | 1.3616 | 0.28718 | 0.095377 | 0.28688 | 0.086895 | 0.058478 | 0.47333 | 0 | 2.783 | 13.1104 | 2.216% | CZ 2B | 0 | 0 | 0.017668 | 0.019817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.061961 | 2.216% | CZ 2B | 30.3456 | 1.5908 | 4.0602 | 2.166 | 0 | 46.3125 | 0 | 14.2542 | 3.0065 | 0.9985 | 3.0034 | 0.9097 | 0.6122 | 7.6306 | 0 | 29.1354 | 144.0256 | 2.216%
CZ 3A | 0.29289 | 0.015689 | 0.041212 | 0.029907 | 0 | 0.38077 | 0 | 0.1299 | 0.03579 | 0.012581 | 0.028663 | 0.0089676 | 0.0060336 | 0.07308 | 0 | 0.2872 | 1.3427 | 18.27% | CZ 3A | 9.6863 | 0.51887 | 2.7357 | 3.0209 | 0 | 12.5926 | 0 | 4.2959 | 1.1836 | 0.41606 | 0.94793 | 0.29657 | 0.19954 | 4.0631 | 0 | 9.4978 | 49.4549 | 18.27% | CZ 3A | 2.8381 | 0.15203 | 0.20356 | 0 | 0 | 3.6896 | 0 | 1.2587 | 0.3468 | 0.1219 | 0.27774 | 0.086895 | 0.058465 | 0.47333 | 0 | 2.783 | 12.2901 | 18.27% | CZ 3A | 0 | 0 | 0.020409 | 0.030209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.075095 | 18.27% | CZ 3A | 29.7116 | 1.5916 | 4.3618 | 3.3018 | 0 | 38.6264 | 0 | 13.1773 | 3.6306 | 1.2762 | 2.9077 | 0.9097 | 0.61207 | 7.6306 | 0 | 29.1354 | 136.8726 | 18.27%
CZ 3B | 0.29175 | 0.015681 | 0.040649 | 0.026502 | 0 | 0.25505 | 0 | 0.1318 | 0.030406 | 0.0075035 | 0.0296 | 0.0089676 | 0.0060309 | 0.07308 | 0 | 0.2872 | 1.2042 | 7.906% | CZ 3B | 9.6484 | 0.5186 | 2.6801 | 2.677 | 0 | 8.4349 | 0 | 4.3588 | 1.0056 | 0.24815 | 0.9789 | 0.29657 | 0.19945 | 4.0631 | 0 | 9.4978 | 44.6074 | 7.906% | CZ 3B | 2.827 | 0.15195 | 0.20337 | 0 | 0 | 2.4714 | 0 | 1.2771 | 0.29463 | 0.072708 | 0.28682 | 0.086895 | 0.058438 | 0.47333 | 0 | 2.783 | 10.9867 | 7.906% | CZ 3B | 0 | 0 | 0.01986 | 0.02677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.071106 | 7.906% | CZ 3B | 29.5955 | 1.5908 | 4.2997 | 2.9259 | 0 | 25.8733 | 0 | 13.3702 | 3.0844 | 0.76118 | 3.0027 | 0.9097 | 0.61179 | 7.6306 | 0 | 29.1354 | 122.7911 | 7.906%
CZ 3C | 0.29292 | 0.015684 | 0.042512 | 0.022874 | 0 | 0.10576 | 0 | 0.11148 | 0.021275 | 0.0036131 | 0.028573 | 0.0089676 | 0.0060336 | 0.07308 | 0 | 0.2872 | 1.02 | 1.057% | CZ 3C | 9.6872 | 0.51869 | 2.8669 | 2.3105 | 0 | 3.4977 | 0 | 3.6867 | 0.70359 | 0.11949 | 0.94496 | 0.29657 | 0.19954 | 4.0631 | 0 | 9.4978 | 38.3929 | 1.057% | CZ 3C | 2.8383 | 0.15198 | 0.20356 | 0 | 0 | 1.0248 | 0 | 1.0802 | 0.20615 | 0.035011 | 0.27687 | 0.086895 | 0.058465 | 0.47333 | 0 | 2.783 | 9.2186 | 1.057% | CZ 3C | 0 | 0 | 0.021722 | 0.023105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.069304 | 1.057% | CZ 3C | 29.7145 | 1.591 | 4.5052 | 2.5254 | 0 | 10.7289 | 0 | 11.3085 | 2.1582 | 0.36653 | 2.8986 | 0.9097 | 0.61207 | 7.6306 | 0 | 29.1354 | 104.0846 | 1.057%
CZ 4A | 0.28644 | 0.015687 | 0.043175 | 0.027421 | 0 | 0.27709 | 0 | 0.13867 | 0.042331 | 0.0092258 | 0.028553 | 0.0089676 | 0.0060282 | 0.07308 | 0 | 0.2872 | 1.2439 | 19.43% | CZ 4A | 9.473 | 0.51878 | 2.9339 | 2.7698 | 0 | 9.1639 | 0 | 4.5861 | 1.4 | 0.30511 | 0.94429 | 0.29657 | 0.19936 | 4.0631 | 0 | 9.4978 | 46.1516 | 19.43% | CZ 4A | 2.7756 | 0.152 | 0.20356 | 0 | 0 | 2.685 | 0 | 1.3437 | 0.41018 | 0.089397 | 0.27667 | 0.086895 | 0.058412 | 0.47333 | 0 | 2.783 | 11.3377 | 19.43% | CZ 4A | 0 | 0 | 0.022391 | 0.027698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.074566 | 19.43% | CZ 4A | 29.0573 | 1.5913 | 4.5784 | 3.0274 | 0 | 28.1092 | 0 | 14.0672 | 4.2942 | 0.93589 | 2.8965 | 0.9097 | 0.61152 | 7.6306 | 0 | 29.1354 | 126.8446 | 19.43%
CZ 4B | 0.28623 | 0.015676 | 0.042859 | 0.033094 | 0 | 0.2126 | 0 | 0.16133 | 0.028957 | 0.0071338 | 0.028489 | 0.0089676 | 0.0060295 | 0.07308 | 0 | 0.2872 | 1.1917 | 0.6104% | CZ 4B | 9.466 | 0.51842 | 2.902 | 3.3428 | 0 | 7.031 | 0 | 5.3356 | 0.95764 | 0.23592 | 0.94217 | 0.29657 | 0.19941 | 4.0631 | 0 | 9.4978 | 44.7884 | 0.6104% | CZ 4B | 2.7735 | 0.1519 | 0.20356 | 0 | 0 | 2.0601 | 0 | 1.5633 | 0.28058 | 0.069125 | 0.27605 | 0.086895 | 0.058425 | 0.47333 | 0 | 2.783 | 10.7798 | 0.6104% | CZ 4B | 0 | 0 | 0.022072 | 0.033428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.079977 | 0.6104% | CZ 4B | 29.0359 | 1.5902 | 4.5435 | 3.6537 | 0 | 21.5668 | 0 | 16.3662 | 2.9374 | 0.72367 | 2.89 | 0.9097 | 0.61165 | 7.6306 | 0 | 29.1354 | 121.5948 | 0.6104%
CZ 4C | 0.28887 | 0.0157 | 0.043686 | 0.052592 | 0 | 0.13196 | 0 | 0.13507 | 0.026605 | 0.00474 | 0.028504 | 0.0089676 | 0.0060282 | 0.07308 | 0 | 0.2872 | 1.103 | 2.341% | CZ 4C | 9.5534 | 0.51923 | 2.9855 | 5.3123 | 0 | 4.3642 | 0 | 4.4669 | 0.87986 | 0.15676 | 0.94267 | 0.29657 | 0.19936 | 4.0631 | 0 | 9.4978 | 43.2378 | 2.341% | CZ 4C | 2.7991 | 0.15213 | 0.20356 | 0 | 0 | 1.2787 | 0 | 1.3088 | 0.2578 | 0.04593 | 0.2762 | 0.086895 | 0.058412 | 0.47333 | 0 | 2.783 | 9.7239 | 2.341% | CZ 4C | 0 | 0 | 0.022908 | 0.053123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.10051 | 2.341% | CZ 4C | 29.304 | 1.5927 | 4.6349 | 5.8064 | 0 | 13.3867 | 0 | 13.7017 | 2.6989 | 0.48084 | 2.8915 | 0.9097 | 0.61152 | 7.6306 | 0 | 29.1354 | 112.7848 | 2.341%
CZ 5A | 0.28653 | 0.015738 | 0.044544 | 0.049985 | 0 | 0.22524 | 0 | 0.14273 | 0.039532 | 0.0078298 | 0.028538 | 0.0089676 | 0.0060282 | 0.07308 | 0 | 0.2872 | 1.2159 | 22.02% | CZ 5A | 9.476 | 0.52049 | 3.0721 | 5.049 | 0 | 7.4489 | 0 | 4.7202 | 1.3074 | 0.25894 | 0.94379 | 0.29657 | 0.19936 | 4.0631 | 0 | 9.4978 | 46.8536 | 22.02% | CZ 5A | 2.7764 | 0.1525 | 0.20357 | 0 | 0 | 2.1825 | 0 | 1.383 | 0.38306 | 0.075869 | 0.27653 | 0.086895 | 0.058412 | 0.47333 | 0 | 2.783 | 10.8351 | 22.02% | CZ 5A | 0 | 0 | 0.023773 | 0.05049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.098739 | 22.02% | CZ 5A | 29.0665 | 1.5965 | 4.7295 | 5.5186 | 0 | 22.8485 | 0 | 14.4787 | 4.0103 | 0.79428 | 2.895 | 0.9097 | 0.61152 | 7.6306 | 0 | 29.1354 | 124.2251 | 22.02%
CZ 5B | 0.28851 | 0.015647 | 0.044286 | 0.060822 | 0 | 0.16434 | 0 | 0.14913 | 0.030601 | 0.0056195 | 0.028409 | 0.0089676 | 0.0060295 | 0.07308 | 0 | 0.2872 | 1.1626 | 4.225% | CZ 5B | 9.5415 | 0.51748 | 3.0461 | 6.1436 | 0 | 5.4351 | 0 | 4.9318 | 1.012 | 0.18584 | 0.93952 | 0.29657 | 0.19941 | 4.0631 | 0 | 9.4978 | 45.8099 | 4.225% | CZ 5B | 2.7956 | 0.15162 | 0.20356 | 0 | 0 | 1.5925 | 0 | 1.445 | 0.29652 | 0.054452 | 0.27528 | 0.086895 | 0.058425 | 0.47333 | 0 | 2.783 | 10.2162 | 4.225% | CZ 5B | 0 | 0 | 0.023514 | 0.061436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.10943 | 4.225% | CZ 5B | 29.2676 | 1.5873 | 4.7011 | 6.715 | 0 | 16.6715 | 0 | 15.1278 | 3.1043 | 0.57006 | 2.8819 | 0.9097 | 0.61165 | 7.6306 | 0 | 29.1354 | 118.9138 | 4.225%
CZ 5C | 0.2947 | 0.015717 | 0.04424 | 0.066259 | 0 | 0.078937 | 0 | 0.13533 | 0.032746 | 0.0029185 | 0.028471 | 0.0089676 | 0.006035 | 0.07308 | 0 | 0.2872 | 1.0746 | 0% | CZ 5C | 9.7462 | 0.51977 | 3.0415 | 6.6928 | 0 | 2.6105 | 0 | 4.4757 | 1.083 | 0.096519 | 0.94159 | 0.29657 | 0.19958 | 4.0631 | 0 | 9.4978 | 43.2647 | 0% | CZ 5C | 2.8556 | 0.15229 | 0.20356 | 0 | 0 | 0.76488 | 0 | 1.3114 | 0.31731 | 0.02828 | 0.27588 | 0.086895 | 0.058478 | 0.47333 | 0 | 2.783 | 9.3109 | 0% | CZ 5C | 0 | 0 | 0.023468 | 0.066928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.11487 | 0% | CZ 5C | 29.8954 | 1.5943 | 4.696 | 7.3152 | 0 | 8.0076 | 0 | 13.7286 | 3.3219 | 0.29606 | 2.8882 | 0.9097 | 0.6122 | 7.6306 | 0 | 29.1354 | 110.0312 | 0%
CZ 6A | 0.28768 | 0.015747 | 0.045701 | 0.063617 | 0 | 0.1572 | 0 | 0.13972 | 0.043859 | 0.0056739 | 0.028452 | 0.0089676 | 0.0060295 | 0.07308 | 0 | 0.2872 | 1.1629 | 4.008% | CZ 6A | 9.514 | 0.52076 | 3.1889 | 6.426 | 0 | 5.1988 | 0 | 4.6207 | 1.4505 | 0.18764 | 0.94096 | 0.29657 | 0.19941 | 4.0631 | 0 | 9.4978 | 46.1053 | 4.008% | CZ 6A | 2.7876 | 0.15258 | 0.20357 | 0 | 0 | 1.5232 | 0 | 1.3539 | 0.42499 | 0.054979 | 0.2757 | 0.086895 | 0.058425 | 0.47333 | 0 | 2.783 | 10.1782 | 4.008% | CZ 6A | 0 | 0 | 0.024941 | 0.06426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.11368 | 4.008% | CZ 6A | 29.1832 | 1.5974 | 4.8573 | 7.0236 | 0 | 15.9469 | 0 | 14.1736 | 4.4492 | 0.57557 | 2.8863 | 0.9097 | 0.61165 | 7.6306 | 0 | 29.1354 | 118.9802 | 4.008%
CZ 6B | 0.28878 | 0.015676 | 0.045845 | 0.061125 | 0 | 0.10447 | 0 | 0.14384 | 0.035318 | 0.0045742 | 0.02835 | 0.0089676 | 0.0060309 | 0.07308 | 0 | 0.2872 | 1.1033 | 0.8296% | CZ 6B | 9.5504 | 0.51842 | 3.2036 | 6.1743 | 0 | 3.4551 | 0 | 4.757 | 1.168 | 0.15127 | 0.93759 | 0.29657 | 0.19945 | 4.0631 | 0 | 9.4978 | 43.9727 | 0.8296% | CZ 6B | 2.7982 | 0.1519 | 0.20356 | 0 | 0 | 1.0123 | 0 | 1.3938 | 0.34223 | 0.044323 | 0.27471 | 0.086895 | 0.058438 | 0.47333 | 0 | 2.783 | 9.6228 | 0.8296% | CZ 6B | 0 | 0 | 0.025089 | 0.061743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.11131 | 0.8296% | CZ 6B | 29.2949 | 1.5902 | 4.8732 | 6.7485 | 0 | 10.5981 | 0 | 14.5916 | 3.5828 | 0.46402 | 2.8759 | 0.9097 | 0.61179 | 7.6306 | 0 | 29.1354 | 112.9067 | 0.8296%
CZ 7 | 0.27938 | 0.015711 | 0.047555 | 0.10118 | 0 | 0.10473 | 0 | 0.14783 | 0.039551 | 0.0045946 | 0.028388 | 0.0089676 | 0.0060241 | 0.07308 | 0 | 0.2872 | 1.1442 | 0.7271% | CZ 7 | 9.2395 | 0.51959 | 3.3762 | 10.22 | 0 | 3.4636 | 0 | 4.889 | 1.308 | 0.15195 | 0.93885 | 0.29657 | 0.19923 | 4.0631 | 0 | 9.4978 | 48.1635 | 0.7271% | CZ 7 | 2.7071 | 0.15224 | 0.20357 | 0 | 0 | 1.0148 | 0 | 1.4325 | 0.38325 | 0.044521 | 0.27508 | 0.086895 | 0.058372 | 0.47333 | 0 | 2.783 | 9.6147 | 0.7271% | CZ 7 | 0 | 0 | 0.026814 | 0.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.15349 | 0.7271% | CZ 7 | 28.341 | 1.5938 | 5.062 | 11.1705 | 0 | 10.6243 | 0 | 14.9965 | 4.0122 | 0.46609 | 2.8798 | 0.9097 | 0.6111 | 7.6306 | 0 | 29.1354 | 117.4329 | 0.7271%
CZ 8 | 0.29921 | 0.015801 | 0.049668 | 0.28432 | 0 | 0.050537 | 0 | 0.15483 | 0.039694 | 0.0043852 | 0.02825 | 0.0089676 | 0.0060377 | 0.07308 | 0 | 0.2872 | 1.302 | 0.1192% | CZ 8 | 9.8953 | 0.52256 | 3.5897 | 28.7189 | 0 | 1.6713 | 0 | 5.1203 | 1.3127 | 0.14503 | 0.93426 | 0.29657 | 0.19967 | 4.0631 | 0 | 9.4978 | 65.9674 | 0.1192% | CZ 8 | 2.8993 | 0.15311 | 0.20357 | 0 | 0 | 0.4897 | 0 | 1.5002 | 0.38463 | 0.042492 | 0.27374 | 0.086895 | 0.058504 | 0.47333 | 0 | 2.783 | 9.3485 | 0.1192% | CZ 8 | 0 | 0 | 0.028949 | 0.28719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.34061 | 0.1192% | CZ 8 | 30.3528 | 1.6029 | 5.2953 | 31.3898 | 0 | 5.1267 | 0 | 15.706 | 4.0267 | 0.44485 | 2.8657 | 0.9097 | 0.61248 | 7.6306 | 0 | 29.1354 | 135.0988 | 0.1192%
Us Weighted | 0.2902 | 0.015699 | 0.042397 | 0.035366 | 0 | 0.312 | 0 | 0.13711 | 0.038582 | 0.0099102 | 0.028707 | 0.0089676 | 0.0060306 | 0.07308 | 0 | 0.2872 | 1.2853 | 100% | Us Weighted | 9.5974 | 0.5192 | 2.8555 | 3.5723 | 0 | 10.3183 | 0 | 4.5344 | 1.276 | 0.32774 | 0.94938 | 0.29657 | 0.19944 | 4.0631 | 0 | 9.4978 | 48.0071 | 100% | Us Weighted | 2.812 | 0.15212 | 0.20354 | 0 | 0 | 3.0232 | 0 | 1.3286 | 0.37385 | 0.096028 | 0.27817 | 0.086895 | 0.058435 | 0.47333 | 0 | 2.783 | 11.6692 | 100% | Us Weighted | 0 | 0 | 0.021608 | 0.035723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.081807 | 100% | Us Weighted | 29.4389 | 1.5926 | 4.4926 | 3.9045 | 0 | 31.6503 | 0 | 13.9087 | 3.9138 | 1.0053 | 2.9121 | 0.9097 | 0.61176 | 7.6306 | 0 | 29.1354 | 131.1063 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.4479 | 0.030064 | 0.037235 | 0.0053167 | 0 | 0.97784 | 0 | 0.20996 | 0.06675 | 0.059138 | 0.029144 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 2.246 | 1.546% | CZ 1A | 14.8126 | 0.99427 | 2.3339 | 0.53704 | 0 | 32.3385 | 0 | 6.9437 | 2.2075 | 1.9558 | 0.96384 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 77.3883 | 1.546% | CZ 1A | 4.3401 | 0.29132 | 0.20356 | 0 | 0 | 9.4751 | 0 | 2.0345 | 0.6468 | 0.57304 | 0.2824 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 21.3199 | 1.546% | CZ 1A | 0 | 0 | 0.016392 | 0.0053704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.046239 | 1.546% | CZ 1A | 45.436 | 3.0498 | 3.9227 | 0.58698 | 0 | 99.1947 | 0 | 21.2991 | 6.7713 | 5.9991 | 2.9565 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 228.2525 | 1.546%
CZ 1B | 0.4479 | 0.03006 | 0.036815 | 0.021861 | 0 | 0.70852 | 0 | 0.20396 | 0.036793 | 0.033917 | 0.029654 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.9321 | 0% | CZ 1B | 14.8126 | 0.99414 | 2.2928 | 2.2082 | 0 | 23.4318 | 0 | 6.7454 | 1.2168 | 1.1217 | 0.9807 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 68.1051 | 0% | CZ 1B | 4.3401 | 0.29128 | 0.20337 | 0 | 0 | 6.8654 | 0 | 1.9764 | 0.35652 | 0.32865 | 0.28734 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 18.1222 | 0% | CZ 1B | 0 | 0 | 0.015987 | 0.022082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.062545 | 0% | CZ 1B | 45.436 | 3.0494 | 3.8764 | 2.4135 | 0 | 71.8744 | 0 | 20.6908 | 3.7324 | 3.4406 | 3.0082 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 196.5579 | 0%
CZ 2A | 0.4479 | 0.030052 | 0.03954 | 0.030449 | 0 | 0.72956 | 0 | 0.18854 | 0.060435 | 0.045345 | 0.028959 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.9834 | 14.7% | CZ 2A | 14.8126 | 0.99387 | 2.5667 | 3.0756 | 0 | 24.1276 | 0 | 6.2353 | 1.9987 | 1.4996 | 0.95773 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 70.5688 | 14.7% | CZ 2A | 4.3401 | 0.2912 | 0.20356 | 0 | 0 | 7.0693 | 0 | 1.8269 | 0.5856 | 0.43938 | 0.28061 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 18.5099 | 14.7% | CZ 2A | 0 | 0 | 0.01872 | 0.030756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.073953 | 14.7% | CZ 2A | 45.436 | 3.0486 | 4.1771 | 3.3617 | 0 | 74.0089 | 0 | 19.1262 | 6.1307 | 4.5999 | 2.9377 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 201.8629 | 14.7%
CZ 2B | 0.4479 | 0.030044 | 0.038494 | 0.027998 | 0 | 0.57654 | 0 | 0.19009 | 0.040308 | 0.028339 | 0.029688 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.7921 | 2.216% | CZ 2B | 14.8126 | 0.9936 | 2.4624 | 2.828 | 0 | 19.067 | 0 | 6.2865 | 1.3331 | 0.93723 | 0.98182 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 64.0032 | 2.216% | CZ 2B | 4.3401 | 0.29112 | 0.20337 | 0 | 0 | 5.5866 | 0 | 1.8419 | 0.39058 | 0.2746 | 0.28767 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 16.6891 | 2.216% | CZ 2B | 0 | 0 | 0.017682 | 0.02828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.070439 | 2.216% | CZ 2B | 45.436 | 3.0478 | 4.0618 | 3.091 | 0 | 58.4859 | 0 | 19.2831 | 4.089 | 2.8748 | 3.0116 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 182.4172 | 2.216%
CZ 3A | 0.4479 | 0.030032 | 0.041231 | 0.05845 | 0 | 0.54875 | 0 | 0.18055 | 0.05787 | 0.035956 | 0.028728 | 0.010297 | 0.01079 | 0.07308 | 0 | 0.2885 | 1.8121 | 18.27% | CZ 3A | 14.8126 | 0.9932 | 2.7376 | 5.9041 | 0 | 18.1478 | 0 | 5.9709 | 1.9138 | 1.1891 | 0.95009 | 0.34054 | 0.35684 | 4.0631 | 0 | 9.5406 | 66.9204 | 18.27% | CZ 3A | 4.3401 | 0.291 | 0.20356 | 0 | 0 | 5.3173 | 0 | 1.7495 | 0.56075 | 0.34841 | 0.27837 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 16.5621 | 18.27% | CZ 3A | 0 | 0 | 0.020429 | 0.059041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.10395 | 18.27% | CZ 3A | 45.436 | 3.0465 | 4.3639 | 6.4531 | 0 | 55.6665 | 0 | 18.3151 | 5.8705 | 3.6475 | 2.9143 | 1.0446 | 1.0946 | 7.6306 | 0 | 29.2667 | 184.7497 | 18.27%
CZ 3B | 0.4479 | 0.030044 | 0.040663 | 0.035502 | 0 | 0.31875 | 0 | 0.17927 | 0.025228 | 0.017519 | 0.029601 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.5071 | 7.906% | CZ 3B | 14.8126 | 0.9936 | 2.6815 | 3.586 | 0 | 10.5416 | 0 | 5.9289 | 0.83432 | 0.57938 | 0.97895 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 55.238 | 7.906% | CZ 3B | 4.3401 | 0.29112 | 0.20337 | 0 | 0 | 3.0887 | 0 | 1.7371 | 0.24445 | 0.16976 | 0.28683 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 13.8346 | 7.906% | CZ 3B | 0 | 0 | 0.019874 | 0.03586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.080211 | 7.906% | CZ 3B | 45.436 | 3.0478 | 4.3013 | 3.9195 | 0 | 32.3353 | 0 | 18.1862 | 2.5592 | 1.7772 | 3.0028 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 153.6015 | 7.906%
CZ 3C | 0.4479 | 0.03003 | 0.042531 | 0.04277 | 0 | 0.13582 | 0 | 0.14776 | 0 | 0.010928 | 0.028649 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.269 | 1.057% | CZ 3C | 14.8126 | 0.99315 | 2.8689 | 4.3202 | 0 | 4.4919 | 0 | 4.8865 | 0 | 0.36139 | 0.94748 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 47.9832 | 1.057% | CZ 3C | 4.3401 | 0.29099 | 0.20356 | 0 | 0 | 1.3161 | 0 | 1.4317 | 0 | 0.10589 | 0.27761 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 11.4391 | 1.057% | CZ 3C | 0 | 0 | 0.021741 | 0.043202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.08942 | 1.057% | CZ 3C | 45.436 | 3.0464 | 4.5074 | 4.722 | 0 | 13.7783 | 0 | 14.9889 | 0 | 1.1085 | 2.9063 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 129.53 | 1.057%
CZ 4A | 0.4479 | 0.030014 | 0.043199 | 0.093016 | 0 | 0.38819 | 0 | 0.17459 | 0.056377 | 0.026866 | 0.028565 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.6714 | 19.43% | CZ 4A | 14.8126 | 0.99261 | 2.9363 | 9.3956 | 0 | 12.838 | 0 | 5.774 | 1.8645 | 0.88849 | 0.94469 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 64.7479 | 19.43% | CZ 4A | 4.3401 | 0.29083 | 0.20356 | 0 | 0 | 3.7615 | 0 | 1.6918 | 0.54629 | 0.26033 | 0.27679 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 14.8443 | 19.43% | CZ 4A | 0 | 0 | 0.022416 | 0.093956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.14085 | 19.43% | CZ 4A | 45.436 | 3.0447 | 4.5811 | 10.2694 | 0 | 39.3793 | 0 | 17.7111 | 5.7191 | 2.7254 | 2.8977 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 170.7999 | 19.43%
CZ 4B | 0.4479 | 0.030022 | 0.042883 | 0.047083 | 0 | 0.26132 | 0 | 0.21118 | 0.026493 | 0.017019 | 0.028441 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.495 | 0.6104% | CZ 4B | 14.8126 | 0.99288 | 2.9044 | 4.7559 | 0 | 8.6421 | 0 | 6.9841 | 0.87618 | 0.56284 | 0.9406 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 55.7727 | 0.6104% | CZ 4B | 4.3401 | 0.29091 | 0.20356 | 0 | 0 | 2.5321 | 0 | 2.0463 | 0.25672 | 0.16491 | 0.27559 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 13.5834 | 0.6104% | CZ 4B | 0 | 0 | 0.022097 | 0.047559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.094132 | 0.6104% | CZ 4B | 45.436 | 3.0456 | 4.5462 | 5.1982 | 0 | 26.5088 | 0 | 21.423 | 2.6876 | 1.7264 | 2.8852 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 152.4932 | 0.6104%
CZ 4C | 0.4479 | 0.029999 | 0.043707 | 0.086506 | 0 | 0.16657 | 0 | 0.1752 | 0.023741 | 0.012534 | 0.028507 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.3973 | 2.341% | CZ 4C | 14.8126 | 0.99212 | 2.9876 | 8.738 | 0 | 5.5086 | 0 | 5.794 | 0.78514 | 0.41453 | 0.94276 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 55.2764 | 2.341% | CZ 4C | 4.3401 | 0.29069 | 0.20356 | 0 | 0 | 1.614 | 0 | 1.6976 | 0.23004 | 0.12146 | 0.27623 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.2468 | 2.341% | CZ 4C | 0 | 0 | 0.022929 | 0.08738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.13479 | 2.341% | CZ 4C | 45.436 | 3.0432 | 4.6371 | 9.5507 | 0 | 16.897 | 0 | 17.7723 | 2.4083 | 1.2715 | 2.8918 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 142.9442 | 2.341%
CZ 5A | 0.4479 | 0.030017 | 0.044569 | 0.1396 | 0 | 0.29984 | 0 | 0.19724 | 0.040574 | 0.021352 | 0.028478 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.6322 | 22.02% | CZ 5A | 14.8126 | 0.9927 | 3.0746 | 14.1012 | 0 | 9.9163 | 0 | 6.523 | 1.3418 | 0.70616 | 0.94181 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 66.7113 | 22.02% | CZ 5A | 4.3401 | 0.29086 | 0.20357 | 0 | 0 | 2.9054 | 0 | 1.9112 | 0.39315 | 0.2069 | 0.27595 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 14.0003 | 22.02% | CZ 5A | 0 | 0 | 0.023798 | 0.14101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.18929 | 22.02% | CZ 5A | 45.436 | 3.045 | 4.7323 | 15.4126 | 0 | 30.417 | 0 | 20.0087 | 4.1159 | 2.1661 | 2.8889 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 167.2587 | 22.02%
CZ 5B | 0.4479 | 0.02999 | 0.044311 | 0.091504 | 0 | 0.23223 | 0 | 0.19514 | 0.039547 | 0.015468 | 0.028338 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.5071 | 4.225% | CZ 5B | 14.8126 | 0.9918 | 3.0486 | 9.2428 | 0 | 7.6802 | 0 | 6.4535 | 1.3079 | 0.51155 | 0.93718 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 59.2872 | 4.225% | CZ 5B | 4.3401 | 0.2906 | 0.20356 | 0 | 0 | 2.2503 | 0 | 1.8908 | 0.38321 | 0.14988 | 0.27459 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 13.2562 | 4.225% | CZ 5B | 0 | 0 | 0.023539 | 0.092428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.14044 | 4.225% | CZ 5B | 45.436 | 3.0422 | 4.7038 | 10.1024 | 0 | 23.5581 | 0 | 19.7953 | 4.0118 | 1.5691 | 2.8747 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 154.1296 | 4.225%
CZ 5C | 0.4479 | 0.029968 | 0.044259 | 0.10938 | 0 | 0.10617 | 0 | 0.17554 | 0.032612 | 0.0087664 | 0.028441 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.3657 | 0% | CZ 5C | 14.8126 | 0.99108 | 3.0433 | 11.0488 | 0 | 3.5113 | 0 | 5.8053 | 1.0785 | 0.28992 | 0.9406 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 55.8226 | 0% | CZ 5C | 4.3401 | 0.29038 | 0.20357 | 0 | 0 | 1.0288 | 0 | 1.7009 | 0.316 | 0.084945 | 0.27559 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 11.7135 | 0% | CZ 5C | 0 | 0 | 0.023486 | 0.11049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.15845 | 0% | CZ 5C | 45.436 | 3.04 | 4.6982 | 12.0764 | 0 | 10.7704 | 0 | 17.8071 | 3.3082 | 0.88929 | 2.8852 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 139.9471 | 0%
CZ 6A | 0.4479 | 0.029999 | 0.045726 | 0.16647 | 0 | 0.20454 | 0 | 0.19318 | 0.039376 | 0.015049 | 0.028379 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.5533 | 4.008% | CZ 6A | 14.8126 | 0.99212 | 3.1915 | 16.8147 | 0 | 6.7645 | 0 | 6.3887 | 1.3022 | 0.4977 | 0.93853 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 66.0037 | 4.008% | CZ 6A | 4.3401 | 0.29069 | 0.20357 | 0 | 0 | 1.982 | 0 | 1.8719 | 0.38155 | 0.14582 | 0.27499 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.9637 | 4.008% | CZ 6A | 0 | 0 | 0.024967 | 0.16815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.21759 | 4.008% | CZ 6A | 45.436 | 3.0432 | 4.8601 | 18.3785 | 0 | 20.7492 | 0 | 19.5967 | 3.9944 | 1.5266 | 2.8788 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 159.4998 | 4.008%
CZ 6B | 0.4479 | 0.02999 | 0.045869 | 0.1308 | 0 | 0.15717 | 0 | 0.19667 | 0.039762 | 0.011495 | 0.02828 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.4706 | 0.8296% | CZ 6B | 14.8126 | 0.9918 | 3.206 | 13.212 | 0 | 5.1978 | 0 | 6.5042 | 1.315 | 0.38014 | 0.93525 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 60.8558 | 0.8296% | CZ 6B | 4.3401 | 0.2906 | 0.20356 | 0 | 0 | 1.5229 | 0 | 1.9057 | 0.38529 | 0.11138 | 0.27403 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.5067 | 0.8296% | CZ 6B | 0 | 0 | 0.025113 | 0.13212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.18171 | 0.8296% | CZ 6B | 45.436 | 3.0422 | 4.8759 | 14.4407 | 0 | 15.9436 | 0 | 19.9509 | 4.0336 | 1.166 | 2.8688 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 150.7939 | 0.8296%
CZ 7 | 0.4479 | 0.029979 | 0.047585 | 0.23032 | 0 | 0.14932 | 0 | 0.20963 | 0.03952 | 0.011775 | 0.028308 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.577 | 0.7271% | CZ 7 | 14.8126 | 0.99144 | 3.3793 | 23.2642 | 0 | 4.9381 | 0 | 6.9329 | 1.307 | 0.3894 | 0.93619 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 71.2521 | 0.7271% | CZ 7 | 4.3401 | 0.29049 | 0.20357 | 0 | 0 | 1.4469 | 0 | 2.0313 | 0.38294 | 0.11409 | 0.2743 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 12.5568 | 0.7271% | CZ 7 | 0 | 0 | 0.026845 | 0.23264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.28396 | 0.7271% | CZ 7 | 45.436 | 3.0411 | 5.0654 | 25.4278 | 0 | 15.1471 | 0 | 21.2658 | 4.009 | 1.1944 | 2.8717 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 162.4944 | 0.7271%
CZ 8 | 0.4479 | 0.02979 | 0.049701 | 0.45257 | 0 | 0.083987 | 0 | 0.20653 | 0.039721 | 0.0080745 | 0.028157 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 1.7291 | 0.1192% | CZ 8 | 14.8126 | 0.98519 | 3.593 | 45.7143 | 0 | 2.7776 | 0 | 6.8301 | 1.3136 | 0.26703 | 0.9312 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 91.5256 | 0.1192% | CZ 8 | 4.3401 | 0.28866 | 0.20357 | 0 | 0 | 0.81382 | 0 | 2.0012 | 0.38489 | 0.07824 | 0.27284 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 11.8564 | 0.1192% | CZ 8 | 0 | 0 | 0.028982 | 0.45714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.5106 | 0.1192% | CZ 8 | 45.436 | 3.022 | 5.2989 | 49.9657 | 0 | 8.5199 | 0 | 20.9505 | 4.0294 | 0.8191 | 2.8564 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 179.9339 | 0.1192%
Us Weighted | 0.4479 | 0.030025 | 0.042419 | 0.084078 | 0 | 0.42944 | 0 | 0.18602 | 0.047893 | 0.028042 | 0.028726 | 0.010297 | 0.010788 | 0.07308 | 0 | 0.2885 | 1.7072 | 100% | Us Weighted | 14.8126 | 0.99297 | 2.8577 | 8.4927 | 0 | 14.2023 | 0 | 6.152 | 1.5839 | 0.92739 | 0.95003 | 0.34054 | 0.35677 | 4.0631 | 0 | 9.5406 | 65.2726 | 100% | Us Weighted | 4.3401 | 0.29094 | 0.20354 | 0 | 0 | 4.1612 | 0 | 1.8025 | 0.46408 | 0.27172 | 0.27835 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 15.2856 | 100% | Us Weighted | 0 | 0 | 0.02163 | 0.084927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.13103 | 100% | Us Weighted | 45.436 | 3.0458 | 4.495 | 9.2825 | 0 | 43.5639 | 0 | 18.8705 | 4.8584 | 2.8447 | 2.9141 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 174.3471 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.4479 | 0.030064 | 0.037235 | 0.0084705 | 0 | 1.1447 | 0 | 0.27904 | 0.1016 | 0.064399 | 0.029144 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 2.5252 | 1.546% | CZ 1A | 14.8126 | 0.99427 | 2.3339 | 0.8556 | 0 | 37.857 | 0 | 9.2283 | 3.3601 | 2.1298 | 0.96384 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 86.8364 | 1.546% | CZ 1A | 4.3401 | 0.29132 | 0.20356 | 0 | 0 | 11.092 | 0 | 2.7039 | 0.98451 | 0.62401 | 0.2824 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 23.9949 | 1.546% | CZ 1A | 0 | 0 | 0.016392 | 0.008556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.049424 | 1.546% | CZ 1A | 45.436 | 3.0498 | 3.9226 | 0.93518 | 0 | 116.122 | 0 | 28.3068 | 10.3068 | 6.5328 | 2.9565 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 256.6046 | 1.546%
CZ 1B | 0.4479 | 0.03006 | 0.036817 | 0.022192 | 0 | 0.7226 | 0 | 0.24272 | 0.077845 | 0.035536 | 0.029654 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 2.028 | 0% | CZ 1B | 14.8126 | 0.99414 | 2.293 | 2.2416 | 0 | 23.8973 | 0 | 8.027 | 2.5745 | 1.1752 | 0.9807 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 71.2971 | 0% | CZ 1B | 4.3401 | 0.29128 | 0.20337 | 0 | 0 | 7.0019 | 0 | 2.3519 | 0.75431 | 0.34434 | 0.28734 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 19.0476 | 0% | CZ 1B | 0 | 0 | 0.015989 | 0.022416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.062882 | 0% | CZ 1B | 45.436 | 3.0494 | 3.8767 | 2.4501 | 0 | 73.3024 | 0 | 24.622 | 7.8968 | 3.6049 | 3.0082 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 206.2825 | 0%
CZ 2A | 0.4479 | 0.030052 | 0.039542 | 0.041028 | 0 | 0.81683 | 0 | 0.25113 | 0.09208 | 0.048704 | 0.028957 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 2.1789 | 14.7% | CZ 2A | 14.8126 | 0.99387 | 2.5669 | 4.1443 | 0 | 27.0138 | 0 | 8.3051 | 3.0452 | 1.6107 | 0.95764 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 77.7512 | 14.7% | CZ 2A | 4.3401 | 0.2912 | 0.20356 | 0 | 0 | 7.915 | 0 | 2.4334 | 0.89224 | 0.47193 | 0.28059 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 20.3011 | 14.7% | CZ 2A | 0 | 0 | 0.018722 | 0.041443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.084641 | 14.7% | CZ 2A | 45.436 | 3.0486 | 4.1773 | 4.5297 | 0 | 82.8617 | 0 | 25.4749 | 9.3409 | 4.9406 | 2.9374 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 221.7835 | 14.7%
CZ 2B | 0.4479 | 0.030044 | 0.038499 | 0.034808 | 0 | 0.6449 | 0 | 0.2379 | 0.063557 | 0.031031 | 0.029687 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.941 | 2.216% | CZ 2B | 14.8126 | 0.9936 | 2.4628 | 3.5159 | 0 | 21.3278 | 0 | 7.8677 | 2.1019 | 1.0262 | 0.98178 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 69.3914 | 2.216% | CZ 2B | 4.3401 | 0.29112 | 0.20337 | 0 | 0 | 6.249 | 0 | 2.3052 | 0.61586 | 0.30068 | 0.28766 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 18.0661 | 2.216% | CZ 2B | 0 | 0 | 0.017687 | 0.035159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.077323 | 2.216% | CZ 2B | 45.436 | 3.0478 | 4.0623 | 3.8429 | 0 | 65.4206 | 0 | 24.1332 | 6.4474 | 3.1479 | 3.0115 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 197.5857 | 2.216%
CZ 3A | 0.4479 | 0.030032 | 0.041236 | 0.080902 | 0 | 0.61119 | 0 | 0.24379 | 0.088719 | 0.038728 | 0.028726 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.9939 | 18.27% | CZ 3A | 14.8126 | 0.9932 | 2.7381 | 8.172 | 0 | 20.2129 | 0 | 8.0624 | 2.934 | 1.2808 | 0.95 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 74.4569 | 18.27% | CZ 3A | 4.3401 | 0.291 | 0.20356 | 0 | 0 | 5.9223 | 0 | 2.3623 | 0.85967 | 0.37526 | 0.27835 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 18.1057 | 18.27% | CZ 3A | 0 | 0 | 0.020433 | 0.08172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.12663 | 18.27% | CZ 3A | 45.436 | 3.0465 | 4.3644 | 8.9319 | 0 | 62.0007 | 0 | 24.7305 | 8.9999 | 3.9286 | 2.914 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 203.3887 | 18.27%
CZ 3B | 0.4479 | 0.030044 | 0.040667 | 0.046632 | 0 | 0.36298 | 0 | 0.22708 | 0.039142 | 0.019346 | 0.029597 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.626 | 7.906% | CZ 3B | 14.8126 | 0.9936 | 2.6819 | 4.7103 | 0 | 12.0043 | 0 | 7.5098 | 1.2945 | 0.6398 | 0.97881 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 59.9267 | 7.906% | CZ 3B | 4.3401 | 0.29112 | 0.20337 | 0 | 0 | 3.5172 | 0 | 2.2004 | 0.37928 | 0.18746 | 0.28679 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 14.8789 | 7.906% | CZ 3B | 0 | 0 | 0.019878 | 0.047103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.091457 | 7.906% | CZ 3B | 45.436 | 3.0478 | 4.3018 | 5.1484 | 0 | 36.8219 | 0 | 23.0355 | 3.9707 | 1.9625 | 3.0024 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 165.7632 | 7.906%
CZ 3C | 0.4479 | 0.03003 | 0.042536 | 0.085924 | 0 | 0.14397 | 0 | 0.20677 | 0 | 0.012352 | 0.02864 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.3808 | 1.057% | CZ 3C | 14.8126 | 0.99315 | 2.8693 | 8.6792 | 0 | 4.7613 | 0 | 6.8383 | 0 | 0.40851 | 0.94716 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 54.6106 | 1.057% | CZ 3C | 4.3401 | 0.29099 | 0.20356 | 0 | 0 | 1.395 | 0 | 2.0036 | 0 | 0.11969 | 0.27752 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 12.1037 | 1.057% | CZ 3C | 0 | 0 | 0.021746 | 0.086792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.13301 | 1.057% | CZ 3C | 45.436 | 3.0464 | 4.5079 | 9.4864 | 0 | 14.6046 | 0 | 20.9758 | 0 | 1.2531 | 2.9053 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 141.2517 | 1.057%
CZ 4A | 0.4479 | 0.030014 | 0.043208 | 0.1384 | 0 | 0.424 | 0 | 0.23933 | 0.087592 | 0.028754 | 0.028556 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.8504 | 19.43% | CZ 4A | 14.8126 | 0.99261 | 2.9373 | 13.9802 | 0 | 14.0224 | 0 | 7.9149 | 2.8968 | 0.95094 | 0.94438 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 73.7532 | 19.43% | CZ 4A | 4.3401 | 0.29083 | 0.20356 | 0 | 0 | 4.1085 | 0 | 2.3191 | 0.84875 | 0.27862 | 0.2767 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 16.1393 | 19.43% | CZ 4A | 0 | 0 | 0.022425 | 0.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.1867 | 19.43% | CZ 4A | 45.436 | 3.0447 | 4.5821 | 15.2804 | 0 | 43.0121 | 0 | 24.2782 | 8.8855 | 2.9169 | 2.8968 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 189.3689 | 19.43%
CZ 4B | 0.4479 | 0.030022 | 0.042889 | 0.078096 | 0 | 0.28923 | 0 | 0.27469 | 0.041138 | 0.018399 | 0.028433 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.6335 | 0.6104% | CZ 4B | 14.8126 | 0.99288 | 2.905 | 7.8885 | 0 | 9.5653 | 0 | 9.0842 | 1.3605 | 0.60847 | 0.94033 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 62.4588 | 0.6104% | CZ 4B | 4.3401 | 0.29091 | 0.20356 | 0 | 0 | 2.8026 | 0 | 2.6617 | 0.39862 | 0.17828 | 0.27551 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 14.6244 | 0.6104% | CZ 4B | 0 | 0 | 0.022103 | 0.078885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.12546 | 0.6104% | CZ 4B | 45.436 | 3.0456 | 4.5469 | 8.6221 | 0 | 29.3405 | 0 | 27.8649 | 4.1731 | 1.8664 | 2.8844 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 166.8159 | 0.6104%
CZ 4C | 0.4479 | 0.029999 | 0.043713 | 0.12256 | 0 | 0.18981 | 0 | 0.23812 | 0.048542 | 0.014351 | 0.028497 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 1.5462 | 2.341% | CZ 4C | 14.8126 | 0.99212 | 2.9882 | 12.3802 | 0 | 6.2773 | 0 | 7.8751 | 1.6054 | 0.47459 | 0.94244 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 62.6489 | 2.341% | CZ 4C | 4.3401 | 0.29069 | 0.20357 | 0 | 0 | 1.8392 | 0 | 2.3074 | 0.47036 | 0.13905 | 0.27613 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 13.3397 | 2.341% | CZ 4C | 0 | 0 | 0.022934 | 0.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.17121 | 2.341% | CZ 4C | 45.436 | 3.0432 | 4.6379 | 13.5315 | 0 | 19.2548 | 0 | 24.1561 | 4.9242 | 1.4558 | 2.8908 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 158.3664 | 2.341%
CZ 5A | 0.4479 | 0.030017 | 0.044577 | 0.18267 | 0 | 0.32241 | 0 | 0.26186 | 0.0617 | 0.022723 | 0.028471 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 1.785 | 22.02% | CZ 5A | 14.8126 | 0.9927 | 3.0754 | 18.4516 | 0 | 10.6624 | 0 | 8.66 | 2.0405 | 0.75147 | 0.94159 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 74.6893 | 22.02% | CZ 5A | 4.3401 | 0.29086 | 0.20357 | 0 | 0 | 3.1241 | 0 | 2.5374 | 0.59787 | 0.22018 | 0.27588 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 15.063 | 22.02% | CZ 5A | 0 | 0 | 0.023806 | 0.18452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.2328 | 22.02% | CZ 5A | 45.436 | 3.045 | 4.7332 | 20.1676 | 0 | 32.7058 | 0 | 26.5637 | 6.2591 | 2.3051 | 2.8882 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 183.1396 | 22.02%
CZ 5B | 0.4479 | 0.02999 | 0.044315 | 0.12824 | 0 | 0.24659 | 0 | 0.26095 | 0.062709 | 0.016581 | 0.028329 | 0.010297 | 0.01079 | 0.07308 | 0 | 0.2885 | 1.6483 | 4.225% | CZ 5B | 14.8126 | 0.9918 | 3.0491 | 12.9534 | 0 | 8.1552 | 0 | 8.63 | 2.0739 | 0.54836 | 0.93687 | 0.34054 | 0.35684 | 4.0631 | 0 | 9.5406 | 66.4523 | 4.225% | CZ 5B | 4.3401 | 0.2906 | 0.20356 | 0 | 0 | 2.3894 | 0 | 2.5286 | 0.60764 | 0.16067 | 0.2745 | 0.099777 | 0.10455 | 0.47333 | 0 | 2.7956 | 14.2682 | 4.225% | CZ 5B | 0 | 0 | 0.023543 | 0.12953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.17755 | 4.225% | CZ 5B | 45.436 | 3.0422 | 4.7043 | 14.1581 | 0 | 25.0151 | 0 | 26.4715 | 6.3614 | 1.682 | 2.8737 | 1.0446 | 1.0946 | 7.6306 | 0 | 29.2667 | 168.7808 | 4.225%
CZ 5C | 0.4479 | 0.029968 | 0.044267 | 0.14634 | 0 | 0.10749 | 0 | 0.2357 | 0.052256 | 0.0093849 | 0.028433 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.4844 | 0% | CZ 5C | 14.8126 | 0.99108 | 3.0441 | 14.7815 | 0 | 3.5549 | 0 | 7.795 | 1.7282 | 0.31037 | 0.94033 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 62.2591 | 0% | CZ 5C | 4.3401 | 0.29038 | 0.20357 | 0 | 0 | 1.0416 | 0 | 2.2839 | 0.50635 | 0.090938 | 0.27551 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 12.5055 | 0% | CZ 5C | 0 | 0 | 0.023493 | 0.14782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.19578 | 0% | CZ 5C | 45.436 | 3.04 | 4.699 | 16.1562 | 0 | 10.9042 | 0 | 23.9103 | 5.301 | 0.95203 | 2.8844 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 152.3194 | 0%
CZ 6A | 0.4479 | 0.029999 | 0.045736 | 0.21816 | 0 | 0.2194 | 0 | 0.2577 | 0.061487 | 0.016207 | 0.028369 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.7076 | 4.008% | CZ 6A | 14.8126 | 0.99212 | 3.1925 | 22.036 | 0 | 7.2558 | 0 | 8.5224 | 2.0335 | 0.536 | 0.93822 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 74.6201 | 4.008% | CZ 6A | 4.3401 | 0.29069 | 0.20357 | 0 | 0 | 2.1259 | 0 | 2.497 | 0.5958 | 0.15705 | 0.2749 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 13.9582 | 4.008% | CZ 6A | 0 | 0 | 0.024977 | 0.22036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.26981 | 4.008% | CZ 6A | 45.436 | 3.0432 | 4.8611 | 24.0853 | 0 | 22.2564 | 0 | 26.1415 | 6.2374 | 1.6441 | 2.8779 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 175.6191 | 4.008%
CZ 6B | 0.4479 | 0.02999 | 0.045879 | 0.1826 | 0 | 0.16347 | 0 | 0.26403 | 0.062926 | 0.012407 | 0.028267 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.6201 | 0.8296% | CZ 6B | 14.8126 | 0.9918 | 3.2071 | 18.4445 | 0 | 5.4062 | 0 | 8.7317 | 2.0811 | 0.41031 | 0.93485 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 69.3212 | 0.8296% | CZ 6B | 4.3401 | 0.2906 | 0.20356 | 0 | 0 | 1.584 | 0 | 2.5584 | 0.60975 | 0.12022 | 0.27391 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 13.4537 | 0.8296% | CZ 6B | 0 | 0 | 0.025123 | 0.18445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.23405 | 0.8296% | CZ 6B | 45.436 | 3.0422 | 4.877 | 20.1599 | 0 | 16.583 | 0 | 26.7835 | 6.3834 | 1.2586 | 2.8675 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 166.4275 | 0.8296%
CZ 7 | 0.4479 | 0.029979 | 0.047595 | 0.29883 | 0 | 0.16482 | 0 | 0.28049 | 0.062933 | 0.013437 | 0.028299 | 0.010297 | 0.010789 | 0.07308 | 0 | 0.2885 | 1.7569 | 0.7271% | CZ 7 | 14.8126 | 0.99144 | 3.3803 | 30.1849 | 0 | 5.4507 | 0 | 9.2763 | 2.0813 | 0.44438 | 0.93588 | 0.34054 | 0.35679 | 4.0631 | 0 | 9.5406 | 81.8589 | 0.7271% | CZ 7 | 4.3401 | 0.29049 | 0.20357 | 0 | 0 | 1.597 | 0 | 2.7179 | 0.60981 | 0.1302 | 0.27421 | 0.099777 | 0.10454 | 0.47333 | 0 | 2.7956 | 13.6365 | 0.7271% | CZ 7 | 0 | 0 | 0.026855 | 0.30185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.35318 | 0.7271% | CZ 7 | 45.436 | 3.0411 | 5.0664 | 32.9921 | 0 | 16.7194 | 0 | 28.4541 | 6.3841 | 1.3631 | 2.8707 | 1.0446 | 1.0944 | 7.6306 | 0 | 29.2667 | 181.3633 | 0.7271%
CZ 8 | 0.4479 | 0.02979 | 0.049704 | 0.53942 | 0 | 0.091036 | 0 | 0.27627 | 0.063054 | 0.0091103 | 0.028156 | 0.010297 | 0.010786 | 0.07308 | 0 | 0.2885 | 1.9171 | 0.1192% | CZ 8 | 14.8126 | 0.98519 | 3.5933 | 54.4869 | 0 | 3.0107 | 0 | 9.1368 | 2.0853 | 0.30129 | 0.93116 | 0.34054 | 0.3567 | 4.0631 | 0 | 9.5406 | 103.6442 | 0.1192% | CZ 8 | 4.3401 | 0.28866 | 0.20357 | 0 | 0 | 0.88213 | 0 | 2.6771 | 0.61099 | 0.088277 | 0.27283 | 0.099777 | 0.10451 | 0.47333 | 0 | 2.7956 | 12.8367 | 0.1192% | CZ 8 | 0 | 0 | 0.028985 | 0.54487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.59833 | 0.1192% | CZ 8 | 45.436 | 3.022 | 5.2993 | 59.5542 | 0 | 9.235 | 0 | 28.0261 | 6.3964 | 0.92417 | 2.8562 | 1.0446 | 1.0941 | 7.6306 | 0 | 29.2667 | 199.7853 | 0.1192%
Us Weighted | 0.4479 | 0.030025 | 0.042426 | 0.11526 | 0 | 0.47537 | 0 | 0.24849 | 0.073976 | 0.030176 | 0.02872 | 0.010297 | 0.010787 | 0.07308 | 0 | 0.2885 | 1.875 | 100% | Us Weighted | 14.8126 | 0.99297 | 2.8583 | 11.6425 | 0 | 15.7211 | 0 | 8.218 | 2.4465 | 0.99798 | 0.94983 | 0.34054 | 0.35675 | 4.0631 | 0 | 9.5406 | 72.9409 | 100% | Us Weighted | 4.3401 | 0.29094 | 0.20354 | 0 | 0 | 4.6063 | 0 | 2.4079 | 0.71681 | 0.2924 | 0.2783 | 0.099777 | 0.10453 | 0.47333 | 0 | 2.7956 | 16.6094 | 100% | Us Weighted | 0 | 0 | 0.021636 | 0.11643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024477 | 0 | 0 | 0.16254 | 100% | Us Weighted | 45.436 | 3.0458 | 4.4957 | 12.7253 | 0 | 48.2229 | 0 | 25.2079 | 7.5043 | 3.0612 | 2.9135 | 1.0446 | 1.0943 | 7.6306 | 0 | 29.2667 | 191.6487 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Secondary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 210887 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 210887 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.20144 | 0.014371 | 6.753e-05 | 0.0075325 | 0 | 0.65817 | 0 | 0.17369 | 0.050327 | 0.052715 | 0.0027119 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 1.197 | 1.546% | CZ 1A | 6.662 | 0.47527 | 0.0055283 | 0.76086 | 0 | 21.7666 | 0 | 5.7443 | 1.6644 | 1.7434 | 0.089686 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 40.1003 | 1.546% | CZ 1A | 1.952 | 0.13925 | 0.0001844 | 0 | 0 | 6.3776 | 0 | 1.6831 | 0.48766 | 0.5108 | 0.026278 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 11.5249 | 1.546% | CZ 1A | 0 | 0 | 4.8989e-05 | 0.0076086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0076576 | 1.546% | CZ 1A | 20.4351 | 1.4578 | 0.0072851 | 0.83162 | 0 | 66.7668 | 0 | 17.6201 | 5.1053 | 5.3476 | 0.2751 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 121.4914 | 1.546%
CZ 1B | 0.19987 | 0.01437 | 1.7353e-05 | 0.01077 | 0 | 0.27049 | 0 | 0.119 | 0.030483 | 0.024445 | 0.0037667 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.70913 | 0% | CZ 1B | 6.6099 | 0.47522 | 0.0017528 | 1.0879 | 0 | 8.9453 | 0 | 3.9356 | 1.0081 | 0.80843 | 0.12457 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 24.185 | 0% | CZ 1B | 1.9367 | 0.13924 | 0 | 0 | 0 | 2.621 | 0 | 1.1531 | 0.29538 | 0.23687 | 0.036499 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 6.7669 | 0% | CZ 1B | 0 | 0 | 1.7528e-05 | 0.010879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010896 | 0% | CZ 1B | 20.275 | 1.4577 | 0.0019158 | 1.189 | 0 | 27.4388 | 0 | 12.072 | 3.0923 | 2.4798 | 0.38211 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 72.0334 | 0%
CZ 2A | 0.19733 | 0.014365 | 6.3081e-05 | 0.030562 | 0 | 0.4606 | 0 | 0.14917 | 0.057026 | 0.039285 | 0.002614 | 0.0013525 | 0.0052294 | 0 | 0 | 0.029348 | 0.98694 | 14.7% | CZ 2A | 6.5258 | 0.47509 | 0.0050789 | 3.0871 | 0 | 15.2328 | 0 | 4.9332 | 1.8859 | 1.2992 | 0.086449 | 0.044731 | 0.17294 | 0 | 0 | 0.97058 | 34.7188 | 14.7% | CZ 2A | 1.9121 | 0.1392 | 0.0001844 | 0 | 0 | 4.4632 | 0 | 1.4454 | 0.55257 | 0.38066 | 0.025329 | 0.013106 | 0.050672 | 0 | 0 | 0.28438 | 9.2667 | 14.7% | CZ 2A | 0 | 0 | 4.4495e-05 | 0.030871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030915 | 14.7% | CZ 2A | 20.0173 | 1.4573 | 0.0067938 | 3.3742 | 0 | 46.7248 | 0 | 15.1319 | 5.7848 | 3.9852 | 0.26517 | 0.13721 | 0.53048 | 0 | 0 | 2.9772 | 100.3923 | 14.7%
CZ 2B | 0.19616 | 0.014363 | 1.7798e-05 | 0.018682 | 0 | 0.26065 | 0 | 0.11881 | 0.030237 | 0.022795 | 0.0037681 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.70141 | 2.216% | CZ 2B | 6.4871 | 0.475 | 0.0017978 | 1.8871 | 0 | 8.62 | 0 | 3.9294 | 0.99998 | 0.75385 | 0.12462 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 24.467 | 2.216% | CZ 2B | 1.9007 | 0.13917 | 0 | 0 | 0 | 2.5256 | 0 | 1.1513 | 0.29299 | 0.22088 | 0.036512 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 6.6153 | 2.216% | CZ 2B | 0 | 0 | 1.7978e-05 | 0.018871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018889 | 2.216% | CZ 2B | 19.8985 | 1.457 | 0.001965 | 2.0626 | 0 | 26.441 | 0 | 12.0529 | 3.0673 | 2.3124 | 0.38225 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 71.3206 | 2.216%
CZ 3A | 0.19466 | 0.014342 | 6.2636e-05 | 0.054138 | 0 | 0.3351 | 0 | 0.13969 | 0.0516 | 0.031185 | 0.0025311 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.85924 | 18.27% | CZ 3A | 6.4377 | 0.47432 | 0.0050339 | 5.4685 | 0 | 11.0823 | 0 | 4.6197 | 1.7065 | 1.0313 | 0.083707 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 32.0973 | 18.27% | CZ 3A | 1.8862 | 0.13898 | 0.0001844 | 0 | 0 | 3.2471 | 0 | 1.3536 | 0.5 | 0.30217 | 0.024526 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 7.8009 | 18.27% | CZ 3A | 0 | 0 | 4.4045e-05 | 0.054685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054729 | 18.27% | CZ 3A | 19.747 | 1.4549 | 0.0067447 | 5.977 | 0 | 33.9938 | 0 | 14.1704 | 5.2345 | 3.1635 | 0.25676 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 87.6493 | 18.27%
CZ 3B | 0.19708 | 0.014363 | 1.7798e-05 | 0.0027671 | 0 | 0.13026 | 0 | 0.11828 | 0.039142 | 0.011859 | 0.0036838 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.55338 | 7.906% | CZ 3B | 6.5177 | 0.475 | 0.0017978 | 0.27951 | 0 | 4.3078 | 0 | 3.9117 | 1.2945 | 0.39219 | 0.12183 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 18.4903 | 7.906% | CZ 3B | 1.9097 | 0.13917 | 0 | 0 | 0 | 1.2622 | 0 | 1.1461 | 0.37928 | 0.11491 | 0.035695 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 5.3352 | 7.906% | CZ 3B | 0 | 0 | 1.7978e-05 | 0.0027951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028131 | 7.906% | CZ 3B | 19.9925 | 1.457 | 0.001965 | 0.3055 | 0 | 13.2138 | 0 | 11.9987 | 3.9707 | 1.203 | 0.3737 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 56.1615 | 7.906%
CZ 3C | 0.19524 | 0.014346 | 5.0177e-05 | 0.038093 | 0 | 0.069 | 0 | 0.11878 | 0 | 0.009635 | 0.0027078 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.48378 | 1.057% | CZ 3C | 6.4568 | 0.47446 | 0.0037755 | 3.8478 | 0 | 2.2819 | 0 | 3.9281 | 0 | 0.31864 | 0.089551 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 18.5893 | 1.057% | CZ 3C | 1.8918 | 0.13901 | 0.0001844 | 0 | 0 | 0.6686 | 0 | 1.1509 | 0 | 0.093361 | 0.026238 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 4.3183 | 1.057% | CZ 3C | 0 | 0 | 3.1461e-05 | 0.038478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038509 | 1.057% | CZ 3C | 19.8056 | 1.4553 | 0.0053692 | 4.2056 | 0 | 6.9996 | 0 | 12.0491 | 0 | 0.9774 | 0.27469 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 49.4174 | 1.057%
CZ 4A | 0.19619 | 0.014327 | 7.109e-05 | 0.11736 | 0 | 0.219 | 0 | 0.12408 | 0.047759 | 0.022603 | 0.0024563 | 0.0013525 | 0.0052267 | 0 | 0 | 0.029348 | 0.77977 | 19.43% | CZ 4A | 6.4882 | 0.47383 | 0.0058879 | 11.8543 | 0 | 7.2426 | 0 | 4.1035 | 1.5795 | 0.74752 | 0.081234 | 0.044731 | 0.17285 | 0 | 0 | 0.97058 | 33.7646 | 19.43% | CZ 4A | 1.901 | 0.13883 | 0.0001844 | 0 | 0 | 2.122 | 0 | 1.2023 | 0.46278 | 0.21902 | 0.023801 | 0.013106 | 0.050645 | 0 | 0 | 0.28438 | 6.4181 | 19.43% | CZ 4A | 0 | 0 | 5.2585e-05 | 0.11854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1186 | 19.43% | CZ 4A | 19.9019 | 1.4534 | 0.0076781 | 12.9567 | 0 | 22.2157 | 0 | 12.5869 | 4.8448 | 2.2929 | 0.24918 | 0.13721 | 0.53021 | 0 | 0 | 2.9772 | 80.1538 | 19.43%
CZ 4B | 0.19705 | 0.014346 | 6.842e-05 | 0.0025789 | 0 | 0.12698 | 0 | 0.15921 | 0.041138 | 0.012465 | 0.0025447 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.5923 | 0.6104% | CZ 4B | 6.5166 | 0.47446 | 0.0056182 | 0.2605 | 0 | 4.1993 | 0 | 5.2654 | 1.3605 | 0.41224 | 0.084156 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 19.7669 | 0.6104% | CZ 4B | 1.9093 | 0.13901 | 0.0001844 | 0 | 0 | 1.2304 | 0 | 1.5428 | 0.39862 | 0.12079 | 0.024658 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 5.7139 | 0.6104% | CZ 4B | 0 | 0 | 4.9888e-05 | 0.002605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026549 | 0.6104% | CZ 4B | 19.9889 | 1.4553 | 0.0073833 | 0.28472 | 0 | 12.8808 | 0 | 16.1511 | 4.1731 | 1.2645 | 0.25814 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 60.1087 | 0.6104%
CZ 4C | 0.19235 | 0.014299 | 6.0435e-05 | 0.015166 | 0 | 0.085661 | 0 | 0.14675 | 0.048542 | 0.010074 | 0.0025814 | 0.0013525 | 0.0052239 | 0 | 0 | 0.029348 | 0.55141 | 2.341% | CZ 4C | 6.3613 | 0.47288 | 0.0047193 | 1.5319 | 0 | 2.8329 | 0 | 4.8532 | 1.6054 | 0.33316 | 0.08537 | 0.044731 | 0.17276 | 0 | 0 | 0.97058 | 19.2689 | 2.341% | CZ 4C | 1.8638 | 0.13855 | 0.00019758 | 0 | 0 | 0.83004 | 0 | 1.422 | 0.47036 | 0.097616 | 0.025013 | 0.013106 | 0.050619 | 0 | 0 | 0.28438 | 5.1957 | 2.341% | CZ 4C | 0 | 0 | 4.045e-05 | 0.015319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015359 | 2.341% | CZ 4C | 19.5124 | 1.4505 | 0.0064896 | 1.6743 | 0 | 8.6897 | 0 | 14.8867 | 4.9242 | 1.0219 | 0.26186 | 0.13721 | 0.52993 | 0 | 0 | 2.9772 | 56.0726 | 2.341%
CZ 5A | 0.19583 | 0.014278 | 7.02e-05 | 0.14367 | 0 | 0.15531 | 0 | 0.14064 | 0.024416 | 0.017385 | 0.0024033 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.72993 | 22.02% | CZ 5A | 6.4763 | 0.47221 | 0.005798 | 14.5122 | 0 | 5.1364 | 0 | 4.6511 | 0.80749 | 0.57493 | 0.079481 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 33.9042 | 22.02% | CZ 5A | 1.8975 | 0.13836 | 0.0001844 | 0 | 0 | 1.505 | 0 | 1.3628 | 0.23659 | 0.16845 | 0.023288 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 5.6803 | 22.02% | CZ 5A | 0 | 0 | 5.1686e-05 | 0.14512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14517 | 22.02% | CZ 5A | 19.8653 | 1.4485 | 0.0075798 | 15.8619 | 0 | 15.7555 | 0 | 14.2666 | 2.4769 | 1.7635 | 0.2438 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 75.3343 | 22.02%
CZ 5B | 0.19321 | 0.014342 | 6.6195e-05 | -0.0014252 | 0 | 0.11896 | 0 | 0.16016 | 0.062709 | 0.011817 | 0.0024672 | 0.0013525 | 0.005228 | 0 | 0 | 0.029348 | 0.59824 | 4.225% | CZ 5B | 6.3898 | 0.47432 | 0.0053935 | -0.14396 | 0 | 3.934 | 0 | 5.2968 | 2.0739 | 0.3908 | 0.081594 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 19.6909 | 4.225% | CZ 5B | 1.8722 | 0.13898 | 0.0001844 | 0 | 0 | 1.1527 | 0 | 1.552 | 0.60764 | 0.1145 | 0.023907 | 0.013106 | 0.050659 | 0 | 0 | 0.28438 | 5.8102 | 4.225% | CZ 5B | 0 | 0 | 4.7641e-05 | -0.0014396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0013919 | 4.225% | CZ 5B | 19.5999 | 1.4549 | 0.0071377 | -0.15734 | 0 | 12.0672 | 0 | 16.2475 | 6.3614 | 1.1987 | 0.25028 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 60.6744 | 4.225%
CZ 5C | 0.18402 | 0.014251 | 6.266e-05 | 0.096957 | 0 | 0.043633 | 0 | 0.12111 | 0.019419 | 0.0073962 | 0.0025515 | 0.0013525 | 0.0052226 | 0 | 0 | 0.029348 | 0.52532 | 0% | CZ 5C | 6.0858 | 0.47131 | 0.004944 | 9.7936 | 0 | 1.443 | 0 | 4.0052 | 0.64223 | 0.2446 | 0.084381 | 0.044731 | 0.17272 | 0 | 0 | 0.97058 | 23.9631 | 0% | CZ 5C | 1.7831 | 0.13809 | 0.00019758 | 0 | 0 | 0.4228 | 0 | 1.1735 | 0.18817 | 0.071668 | 0.024723 | 0.013106 | 0.050606 | 0 | 0 | 0.28438 | 4.1504 | 0% | CZ 5C | 0 | 0 | 4.2697e-05 | 0.097936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097979 | 0% | CZ 5C | 18.6676 | 1.4457 | 0.0067352 | 10.7044 | 0 | 4.4263 | 0 | 12.2855 | 1.97 | 0.75029 | 0.25883 | 0.13721 | 0.52979 | 0 | 0 | 2.9772 | 54.1594 | 0%
CZ 6A | 0.19415 | 0.014253 | 7.0645e-05 | 0.16841 | 0 | 0.10648 | 0 | 0.13902 | 0.025691 | 0.01226 | 0.0023761 | 0.0013525 | 0.0052294 | 0 | 0 | 0.029348 | 0.69865 | 4.008% | CZ 6A | 6.4209 | 0.47136 | 0.0058429 | 17.0116 | 0 | 3.5214 | 0 | 4.5977 | 0.84965 | 0.40545 | 0.078582 | 0.044731 | 0.17294 | 0 | 0 | 0.97058 | 34.5507 | 4.008% | CZ 6A | 1.8813 | 0.13811 | 0.0001844 | 0 | 0 | 1.0318 | 0 | 1.3471 | 0.24895 | 0.1188 | 0.023024 | 0.013106 | 0.050672 | 0 | 0 | 0.28438 | 5.1374 | 4.008% | CZ 6A | 0 | 0 | 5.2135e-05 | 0.17012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17017 | 4.008% | CZ 6A | 19.6953 | 1.4458 | 0.0076289 | 18.5937 | 0 | 10.8016 | 0 | 14.1028 | 2.6062 | 1.2437 | 0.24104 | 0.13721 | 0.53048 | 0 | 0 | 2.9772 | 72.3826 | 4.008%
CZ 6B | 0.19319 | 0.014314 | 6.7951e-05 | 0.14446 | 0 | 0.077996 | 0 | 0.13693 | 0.020436 | 0.0083926 | 0.0023802 | 0.0013525 | 0.0052267 | 0 | 0 | 0.029348 | 0.6341 | 0.8296% | CZ 6B | 6.3892 | 0.47338 | 0.0056631 | 14.5922 | 0 | 2.5794 | 0 | 4.5285 | 0.67586 | 0.27755 | 0.078717 | 0.044731 | 0.17285 | 0 | 0 | 0.97058 | 30.7887 | 0.8296% | CZ 6B | 1.872 | 0.1387 | 0.00017123 | 0 | 0 | 0.75577 | 0 | 1.3268 | 0.19802 | 0.081322 | 0.023064 | 0.013106 | 0.050645 | 0 | 0 | 0.28438 | 4.744 | 0.8296% | CZ 6B | 0 | 0 | 5.0787e-05 | 0.14592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14597 | 0.8296% | CZ 6B | 19.5981 | 1.452 | 0.0073437 | 15.9493 | 0 | 7.9121 | 0 | 13.8906 | 2.0731 | 0.85136 | 0.24145 | 0.13721 | 0.53021 | 0 | 0 | 2.9772 | 65.62 | 0.8296%
CZ 7 | 0.20885 | 0.014268 | 7.5539e-05 | 0.22408 | 0 | 0.079527 | 0 | 0.15375 | 0.023276 | 0.010016 | 0.0024019 | 0.0013525 | 0.0052362 | 0 | 0 | 0.029348 | 0.75219 | 0.7271% | CZ 7 | 6.907 | 0.47185 | 0.0063373 | 22.6346 | 0 | 2.6301 | 0 | 5.0848 | 0.76977 | 0.33123 | 0.079436 | 0.044731 | 0.17317 | 0 | 0 | 0.97058 | 40.1035 | 0.7271% | CZ 7 | 2.0237 | 0.13825 | 0.0001844 | 0 | 0 | 0.7706 | 0 | 1.4898 | 0.22554 | 0.09705 | 0.023274 | 0.013106 | 0.050738 | 0 | 0 | 0.28438 | 5.1167 | 0.7271% | CZ 7 | 0 | 0 | 5.7079e-05 | 0.22635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2264 | 0.7271% | CZ 7 | 21.1865 | 1.4473 | 0.0081693 | 24.7396 | 0 | 8.0674 | 0 | 15.597 | 2.3612 | 1.016 | 0.24366 | 0.13721 | 0.53117 | 0 | 0 | 2.9772 | 78.3124 | 0.7271%
CZ 8 | 0.19387 | 0.013989 | 6.9285e-05 | 0.31143 | 0 | 0.048615 | 0 | 0.13842 | 0.022486 | 0.0053599 | 0.0024264 | 0.0013525 | 0.0052226 | 0 | 0 | 0.029348 | 0.77259 | 0.1192% | CZ 8 | 6.4115 | 0.46263 | 0.005798 | 31.4579 | 0 | 1.6078 | 0 | 4.5777 | 0.74365 | 0.17726 | 0.080245 | 0.044731 | 0.17272 | 0 | 0 | 0.97058 | 46.7124 | 0.1192% | CZ 8 | 1.8786 | 0.13555 | 0.00017123 | 0 | 0 | 0.47107 | 0 | 1.3412 | 0.21789 | 0.051936 | 0.023512 | 0.013106 | 0.050606 | 0 | 0 | 0.28438 | 4.468 | 0.1192% | CZ 8 | 0 | 0 | 5.2135e-05 | 0.31458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31463 | 0.1192% | CZ 8 | 19.6666 | 1.4191 | 0.007491 | 34.3835 | 0 | 4.9317 | 0 | 14.0414 | 2.2811 | 0.54372 | 0.24614 | 0.13721 | 0.52979 | 0 | 0 | 2.9772 | 81.1648 | 0.1192%
Us Weighted | 0.19591 | 0.014326 | 6.2016e-05 | 0.080232 | 0 | 0.246 | 0 | 0.13761 | 0.042438 | 0.023501 | 0.0026138 | 0.0013525 | 0.0052279 | 0 | 0 | 0.029348 | 0.77862 | 100% | Us Weighted | 6.479 | 0.47377 | 0.0051009 | 8.1043 | 0 | 8.1355 | 0 | 4.5509 | 1.4035 | 0.77722 | 0.086444 | 0.044731 | 0.1729 | 0 | 0 | 0.97058 | 31.204 | 100% | Us Weighted | 1.8983 | 0.13881 | 0.00016592 | 0 | 0 | 2.3837 | 0 | 1.3334 | 0.41122 | 0.22772 | 0.025328 | 0.013106 | 0.050658 | 0 | 0 | 0.28438 | 6.7668 | 100% | Us Weighted | 0 | 0 | 4.5346e-05 | 0.081043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081088 | 100% | Us Weighted | 19.8737 | 1.4532 | 0.0066934 | 8.858 | 0 | 24.9548 | 0 | 13.9594 | 4.3051 | 2.384 | 0.26516 | 0.13721 | 0.53034 | 0 | 0 | 2.9772 | 79.7047 | 100%
Building Type: | Secondary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 210887 | [17 empty] | Prototype Floor Area: | 210887 | [17 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 44.98% | 47.8% | 0.1814% | 88.93% | 0% | 57.5% | 0% | 62.25% | 49.53% | 81.86% | 9.305% | 13.14% | 48.47% | 0% | 0% | 10.17% | 47.4% | 1.546% | CZ 1A | 44.98% | 47.8% | 0.2369% | 88.93% | 0% | 57.5% | 0% | 62.25% | 49.53% | 81.86% | 9.305% | 13.14% | 48.47% | 0% | 0% | 10.17% | 46.18% | 1.546% | CZ 1A | 44.98% | 47.8% | 0.09059% | 0% | 0% | 57.5% | 0% | 62.25% | 49.53% | 81.86% | 9.305% | 13.14% | 48.47% | 0% | 0% | 10.17% | 48.03% | 1.546% | CZ 1A | 0% | 0% | 0.2989% | 88.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.49% | 1.546% | CZ 1A | 44.98% | 47.8% | 0.1857% | 88.93% | 0% | 57.5% | 0% | 62.25% | 49.53% | 81.86% | 9.305% | 13.14% | 48.47% | 0% | 0% | 10.17% | 47.35% | 1.546%
CZ 1B | 44.62% | 47.8% | 0.04713% | 48.53% | 0% | 37.43% | 0% | 49.03% | 39.16% | 68.79% | 12.7% | 13.14% | 48.47% | 0% | 0% | 10.17% | 34.97% | 0% | CZ 1B | 44.62% | 47.8% | 0.07644% | 48.53% | 0% | 37.43% | 0% | 49.03% | 39.16% | 68.79% | 12.7% | 13.14% | 48.47% | 0% | 0% | 10.17% | 33.92% | 0% | CZ 1B | 44.62% | 47.8% | 0% | 0% | 0% | 37.43% | 0% | 49.03% | 39.16% | 68.79% | 12.7% | 13.14% | 48.47% | 0% | 0% | 10.17% | 35.53% | 0% | CZ 1B | 0% | 0% | 0.1096% | 48.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.33% | 0% | CZ 1B | 44.62% | 47.8% | 0.04942% | 48.53% | 0% | 37.43% | 0% | 49.03% | 39.16% | 68.79% | 12.7% | 13.14% | 48.47% | 0% | 0% | 10.17% | 34.92% | 0%
CZ 2A | 44.06% | 47.8% | 0.1595% | 74.49% | 0% | 56.39% | 0% | 59.4% | 61.93% | 80.66% | 9.027% | 13.14% | 48.47% | 0% | 0% | 10.17% | 45.3% | 14.7% | CZ 2A | 44.06% | 47.8% | 0.1979% | 74.49% | 0% | 56.39% | 0% | 59.4% | 61.93% | 80.66% | 9.027% | 13.14% | 48.47% | 0% | 0% | 10.17% | 44.65% | 14.7% | CZ 2A | 44.06% | 47.8% | 0.09059% | 0% | 0% | 56.39% | 0% | 59.4% | 61.93% | 80.66% | 9.027% | 13.14% | 48.47% | 0% | 0% | 10.17% | 45.65% | 14.7% | CZ 2A | 0% | 0% | 0.2377% | 74.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.53% | 14.7% | CZ 2A | 44.06% | 47.8% | 0.1626% | 74.49% | 0% | 56.39% | 0% | 59.4% | 61.93% | 80.66% | 9.027% | 13.14% | 48.47% | 0% | 0% | 10.17% | 45.27% | 14.7%
CZ 2B | 43.79% | 47.81% | 0.04623% | 53.67% | 0% | 40.42% | 0% | 49.94% | 47.57% | 73.46% | 12.69% | 13.14% | 48.46% | 0% | 0% | 10.17% | 36.14% | 2.216% | CZ 2B | 43.79% | 47.81% | 0.073% | 53.67% | 0% | 40.42% | 0% | 49.94% | 47.57% | 73.46% | 12.69% | 13.14% | 48.46% | 0% | 0% | 10.17% | 35.26% | 2.216% | CZ 2B | 43.79% | 47.81% | 0% | 0% | 0% | 40.42% | 0% | 49.94% | 47.57% | 73.46% | 12.69% | 13.14% | 48.46% | 0% | 0% | 10.17% | 36.62% | 2.216% | CZ 2B | 0% | 0% | 0.1016% | 53.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 24.43% | 2.216% | CZ 2B | 43.79% | 47.81% | 0.04837% | 53.67% | 0% | 40.42% | 0% | 49.94% | 47.57% | 73.46% | 12.69% | 13.14% | 48.46% | 0% | 0% | 10.17% | 36.1% | 2.216%
CZ 3A | 43.46% | 47.76% | 0.1519% | 66.92% | 0% | 54.83% | 0% | 57.3% | 58.16% | 80.52% | 8.811% | 13.14% | 48.46% | 0% | 0% | 10.17% | 43.09% | 18.27% | CZ 3A | 43.46% | 47.76% | 0.1838% | 66.92% | 0% | 54.83% | 0% | 57.3% | 58.16% | 80.52% | 8.811% | 13.14% | 48.46% | 0% | 0% | 10.17% | 43.11% | 18.27% | CZ 3A | 43.46% | 47.76% | 0.09059% | 0% | 0% | 54.83% | 0% | 57.3% | 58.16% | 80.52% | 8.811% | 13.14% | 48.46% | 0% | 0% | 10.17% | 43.09% | 18.27% | CZ 3A | 0% | 0% | 0.2156% | 66.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.22% | 18.27% | CZ 3A | 43.46% | 47.76% | 0.1545% | 66.92% | 0% | 54.83% | 0% | 57.3% | 58.16% | 80.52% | 8.811% | 13.14% | 48.46% | 0% | 0% | 10.17% | 43.09% | 18.27%
CZ 3B | 44% | 47.81% | 0.04376% | 5.934% | 0% | 35.89% | 0% | 52.09% | 100% | 61.3% | 12.45% | 13.14% | 48.46% | 0% | 0% | 10.17% | 34.03% | 7.906% | CZ 3B | 44% | 47.81% | 0.06703% | 5.934% | 0% | 35.89% | 0% | 52.09% | 100% | 61.3% | 12.45% | 13.14% | 48.46% | 0% | 0% | 10.17% | 30.85% | 7.906% | CZ 3B | 44% | 47.81% | 0% | 0% | 0% | 35.89% | 0% | 52.09% | 100% | 61.3% | 12.45% | 13.14% | 48.46% | 0% | 0% | 10.17% | 35.86% | 7.906% | CZ 3B | 0% | 0% | 0.09044% | 5.934% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.076% | 7.906% | CZ 3B | 44% | 47.81% | 0.04568% | 5.934% | 0% | 35.89% | 0% | 52.09% | 100% | 61.3% | 12.45% | 13.14% | 48.46% | 0% | 0% | 10.17% | 33.88% | 7.906%
CZ 3C | 43.59% | 47.77% | 0.118% | 44.33% | 0% | 47.93% | 0% | 57.44% | 0% | 78% | 9.455% | 13.14% | 48.46% | 0% | 0% | 10.17% | 35.04% | 1.057% | CZ 3C | 43.59% | 47.77% | 0.1316% | 44.33% | 0% | 47.93% | 0% | 57.44% | 0% | 78% | 9.455% | 13.14% | 48.46% | 0% | 0% | 10.17% | 34.04% | 1.057% | CZ 3C | 43.59% | 47.77% | 0.09059% | 0% | 0% | 47.93% | 0% | 57.44% | 0% | 78% | 9.455% | 13.14% | 48.46% | 0% | 0% | 10.17% | 35.68% | 1.057% | CZ 3C | 0% | 0% | 0.1447% | 44.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.95% | 1.057% | CZ 3C | 43.59% | 47.77% | 0.1191% | 44.33% | 0% | 47.93% | 0% | 57.44% | 0% | 78% | 9.455% | 13.14% | 48.46% | 0% | 0% | 10.17% | 34.99% | 1.057%
CZ 4A | 43.8% | 47.74% | 0.1645% | 84.79% | 0% | 51.65% | 0% | 51.84% | 54.52% | 78.61% | 8.602% | 13.14% | 48.45% | 0% | 0% | 10.17% | 42.14% | 19.43% | CZ 4A | 43.8% | 47.74% | 0.2005% | 84.79% | 0% | 51.65% | 0% | 51.84% | 54.52% | 78.61% | 8.602% | 13.14% | 48.45% | 0% | 0% | 10.17% | 45.78% | 19.43% | CZ 4A | 43.8% | 47.74% | 0.09059% | 0% | 0% | 51.65% | 0% | 51.84% | 54.52% | 78.61% | 8.602% | 13.14% | 48.45% | 0% | 0% | 10.17% | 39.77% | 19.43% | CZ 4A | 0% | 0% | 0.2345% | 84.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 63.52% | 19.43% | CZ 4A | 43.8% | 47.74% | 0.1676% | 84.79% | 0% | 51.65% | 0% | 51.84% | 54.52% | 78.61% | 8.602% | 13.14% | 48.45% | 0% | 0% | 10.17% | 42.33% | 19.43%
CZ 4B | 43.99% | 47.79% | 0.1595% | 3.302% | 0% | 43.9% | 0% | 57.96% | 100% | 67.75% | 8.95% | 13.14% | 48.46% | 0% | 0% | 10.17% | 36.26% | 0.6104% | CZ 4B | 43.99% | 47.79% | 0.1934% | 3.302% | 0% | 43.9% | 0% | 57.96% | 100% | 67.75% | 8.95% | 13.14% | 48.46% | 0% | 0% | 10.17% | 31.65% | 0.6104% | CZ 4B | 43.99% | 47.79% | 0.09059% | 0% | 0% | 43.9% | 0% | 57.96% | 100% | 67.75% | 8.95% | 13.14% | 48.46% | 0% | 0% | 10.17% | 39.07% | 0.6104% | CZ 4B | 0% | 0% | 0.2257% | 3.302% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.116% | 0.6104% | CZ 4B | 43.99% | 47.79% | 0.1624% | 3.302% | 0% | 43.9% | 0% | 57.96% | 100% | 67.75% | 8.95% | 13.14% | 48.46% | 0% | 0% | 10.17% | 36.03% | 0.6104%
CZ 4C | 42.94% | 47.66% | 0.1383% | 12.37% | 0% | 45.13% | 0% | 61.63% | 100% | 70.2% | 9.058% | 13.14% | 48.43% | 0% | 0% | 10.17% | 35.66% | 2.341% | CZ 4C | 42.94% | 47.66% | 0.1579% | 12.37% | 0% | 45.13% | 0% | 61.63% | 100% | 70.2% | 9.058% | 13.14% | 48.43% | 0% | 0% | 10.17% | 30.76% | 2.341% | CZ 4C | 42.94% | 47.66% | 0.09706% | 0% | 0% | 45.13% | 0% | 61.63% | 100% | 70.2% | 9.058% | 13.14% | 48.43% | 0% | 0% | 10.17% | 38.95% | 2.341% | CZ 4C | 0% | 0% | 0.1764% | 12.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.971% | 2.341% | CZ 4C | 42.94% | 47.66% | 0.1399% | 12.37% | 0% | 45.13% | 0% | 61.63% | 100% | 70.2% | 9.058% | 13.14% | 48.43% | 0% | 0% | 10.17% | 35.41% | 2.341%
CZ 5A | 43.72% | 47.57% | 0.1575% | 78.65% | 0% | 48.17% | 0% | 53.71% | 39.57% | 76.51% | 8.441% | 13.14% | 48.47% | 0% | 0% | 10.17% | 40.89% | 22.02% | CZ 5A | 43.72% | 47.57% | 0.1885% | 78.65% | 0% | 48.17% | 0% | 53.71% | 39.57% | 76.51% | 8.441% | 13.14% | 48.47% | 0% | 0% | 10.17% | 45.39% | 22.02% | CZ 5A | 43.72% | 47.57% | 0.09059% | 0% | 0% | 48.17% | 0% | 53.71% | 39.57% | 76.51% | 8.441% | 13.14% | 48.47% | 0% | 0% | 10.17% | 37.71% | 22.02% | CZ 5A | 0% | 0% | 0.2171% | 78.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.36% | 22.02% | CZ 5A | 43.72% | 47.57% | 0.1601% | 78.65% | 0% | 48.17% | 0% | 53.71% | 39.57% | 76.51% | 8.441% | 13.14% | 48.47% | 0% | 0% | 10.17% | 41.13% | 22.02%
CZ 5B | 43.14% | 47.82% | 0.1494% | -1.111% | 0% | 48.24% | 0% | 61.38% | 100% | 71.27% | 8.709% | 13.14% | 48.45% | 0% | 0% | 10.17% | 36.29% | 4.225% | CZ 5B | 43.14% | 47.82% | 0.1769% | -1.111% | 0% | 48.24% | 0% | 61.38% | 100% | 71.27% | 8.709% | 13.14% | 48.45% | 0% | 0% | 10.17% | 29.63% | 4.225% | CZ 5B | 43.14% | 47.82% | 0.09059% | 0% | 0% | 48.24% | 0% | 61.38% | 100% | 71.27% | 8.709% | 13.14% | 48.45% | 0% | 0% | 10.17% | 40.72% | 4.225% | CZ 5B | 0% | 0% | 0.2024% | -1.111% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.7839% | 4.225% | CZ 5B | 43.14% | 47.82% | 0.1517% | -1.111% | 0% | 48.24% | 0% | 61.38% | 100% | 71.27% | 8.709% | 13.14% | 48.45% | 0% | 0% | 10.17% | 35.95% | 4.225%
CZ 5C | 41.09% | 47.56% | 0.1416% | 66.26% | 0% | 40.59% | 0% | 51.38% | 37.16% | 78.81% | 8.974% | 13.14% | 48.41% | 0% | 0% | 10.17% | 35.39% | 0% | CZ 5C | 41.09% | 47.56% | 0.1624% | 66.26% | 0% | 40.59% | 0% | 51.38% | 37.16% | 78.81% | 8.974% | 13.14% | 48.41% | 0% | 0% | 10.17% | 38.49% | 0% | CZ 5C | 41.09% | 47.56% | 0.09706% | 0% | 0% | 40.59% | 0% | 51.38% | 37.16% | 78.81% | 8.974% | 13.14% | 48.41% | 0% | 0% | 10.17% | 33.19% | 0% | CZ 5C | 0% | 0% | 0.1817% | 66.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50.04% | 0% | CZ 5C | 41.09% | 47.56% | 0.1433% | 66.26% | 0% | 40.59% | 0% | 51.38% | 37.16% | 78.81% | 8.974% | 13.14% | 48.41% | 0% | 0% | 10.17% | 35.56% | 0%
CZ 6A | 43.35% | 47.51% | 0.1545% | 77.2% | 0% | 48.53% | 0% | 53.95% | 41.78% | 75.64% | 8.376% | 13.14% | 48.48% | 0% | 0% | 10.17% | 40.91% | 4.008% | CZ 6A | 43.35% | 47.51% | 0.183% | 77.2% | 0% | 48.53% | 0% | 53.95% | 41.78% | 75.64% | 8.376% | 13.14% | 48.48% | 0% | 0% | 10.17% | 46.3% | 4.008% | CZ 6A | 43.35% | 47.51% | 0.09059% | 0% | 0% | 48.53% | 0% | 53.95% | 41.78% | 75.64% | 8.376% | 13.14% | 48.48% | 0% | 0% | 10.17% | 36.81% | 4.008% | CZ 6A | 0% | 0% | 0.2087% | 77.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 63.07% | 4.008% | CZ 6A | 43.35% | 47.51% | 0.1569% | 77.2% | 0% | 48.53% | 0% | 53.95% | 41.78% | 75.64% | 8.376% | 13.14% | 48.48% | 0% | 0% | 10.17% | 41.22% | 4.008%
CZ 6B | 43.13% | 47.73% | 0.1481% | 79.11% | 0% | 47.71% | 0% | 51.86% | 32.48% | 67.65% | 8.42% | 13.14% | 48.45% | 0% | 0% | 10.17% | 39.14% | 0.8296% | CZ 6B | 43.13% | 47.73% | 0.1766% | 79.11% | 0% | 47.71% | 0% | 51.86% | 32.48% | 67.65% | 8.42% | 13.14% | 48.45% | 0% | 0% | 10.17% | 44.41% | 0.8296% | CZ 6B | 43.13% | 47.73% | 0.08412% | 0% | 0% | 47.71% | 0% | 51.86% | 32.48% | 67.65% | 8.42% | 13.14% | 48.45% | 0% | 0% | 10.17% | 35.26% | 0.8296% | CZ 6B | 0% | 0% | 0.2022% | 79.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.37% | 0.8296% | CZ 6B | 43.13% | 47.73% | 0.1506% | 79.11% | 0% | 47.71% | 0% | 51.86% | 32.48% | 67.65% | 8.42% | 13.14% | 48.45% | 0% | 0% | 10.17% | 39.43% | 0.8296%
CZ 7 | 46.63% | 47.59% | 0.1587% | 74.99% | 0% | 48.25% | 0% | 54.81% | 36.99% | 74.54% | 8.488% | 13.14% | 48.53% | 0% | 0% | 10.17% | 42.81% | 0.7271% | CZ 7 | 46.63% | 47.59% | 0.1875% | 74.99% | 0% | 48.25% | 0% | 54.81% | 36.99% | 74.54% | 8.488% | 13.14% | 48.53% | 0% | 0% | 10.17% | 48.99% | 0.7271% | CZ 7 | 46.63% | 47.59% | 0.09059% | 0% | 0% | 48.25% | 0% | 54.81% | 36.99% | 74.54% | 8.488% | 13.14% | 48.53% | 0% | 0% | 10.17% | 37.52% | 0.7271% | CZ 7 | 0% | 0% | 0.2125% | 74.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 64.1% | 0.7271% | CZ 7 | 46.63% | 47.59% | 0.1612% | 74.99% | 0% | 48.25% | 0% | 54.81% | 36.99% | 74.54% | 8.488% | 13.14% | 48.53% | 0% | 0% | 10.17% | 43.18% | 0.7271%
CZ 8 | 43.28% | 46.96% | 0.1394% | 57.73% | 0% | 53.4% | 0% | 50.1% | 35.66% | 58.83% | 8.618% | 13.14% | 48.42% | 0% | 0% | 10.17% | 40.3% | 0.1192% | CZ 8 | 43.28% | 46.96% | 0.1614% | 57.73% | 0% | 53.4% | 0% | 50.1% | 35.66% | 58.83% | 8.618% | 13.14% | 48.42% | 0% | 0% | 10.17% | 45.07% | 0.1192% | CZ 8 | 43.28% | 46.96% | 0.08412% | 0% | 0% | 53.4% | 0% | 50.1% | 35.66% | 58.83% | 8.618% | 13.14% | 48.42% | 0% | 0% | 10.17% | 34.81% | 0.1192% | CZ 8 | 0% | 0% | 0.1799% | 57.73% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 52.58% | 0.1192% | CZ 8 | 43.28% | 46.96% | 0.1414% | 57.73% | 0% | 53.4% | 0% | 50.1% | 35.66% | 58.83% | 8.618% | 13.14% | 48.42% | 0% | 0% | 10.17% | 40.63% | 0.1192%
Us Weighted | 43.74% | 47.71% | 0.1462% | 69.61% | 0% | 51.75% | 0% | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% | 0% | 10.17% | 41.53% | 100% | Us Weighted | 43.74% | 47.71% | 0.1785% | 69.61% | 0% | 51.75% | 0% | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% | 0% | 10.17% | 42.78% | 100% | Us Weighted | 43.74% | 47.71% | 0.08152% | 0% | 0% | 51.75% | 0% | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% | 0% | 10.17% | 40.74% | 100% | Us Weighted | 0% | 0% | 0.2096% | 69.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 49.89% | 100% | Us Weighted | 43.74% | 47.71% | 0.1489% | 69.61% | 0% | 51.75% | 0% | 55.38% | 57.37% | 77.88% | 9.101% | 13.14% | 48.46% | 0% | 0% | 10.17% | 41.59% | 100%

## Warehouse
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Warehouse |  |  |  | End Use Cost Summary for Standard 90.1 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [5 empty] | US Average Weighted Results | [18 empty] | US Average Weighted Results | [18 empty] | Building Type: | Warehouse | [14 empty] | Prototype Floor Area: | 52045 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total
End Cost by 90.1 version: | [18 empty] | End Use by 90.1 version: | [18 empty] | End Electric Use by 90.1 version: | [18 empty] | End Gas Use by 90.1 version: | [18 empty] | End Use by 90.1 version:
STD2013 | 0.16999 | 0.045491 | 0.013738 | 0.059903 | 0 | 0.011858 | 0 | 0.018947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.39511 |  | STD2013 | 5.6218 | 1.5044 | 0.45433 | 6.0508 | 0 | 0.39217 | 0 | 0.62661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.1366 |  | STD2013 | 1.6472 | 0.4408 | 0.13312 | 0 | 0 | 0.1149 | 0 | 0.18359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2481 |  | STD2013 | 0 | 0 | 0 | 0.060508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060508 |  | STD2013 | 17.2442 | 4.6147 | 1.3936 | 6.6135 | 0 | 1.2029 | 0 | 1.9221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.6179
STD2010 | 0.18375 | 0.045491 | 0.013739 | 0.06358 | 0 | 0.014655 | 0 | 0.02391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.42062 |  | STD2010 | 6.077 | 1.5044 | 0.45438 | 6.4223 | 0 | 0.48465 | 0 | 0.79075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 18.2301 |  | STD2010 | 1.7805 | 0.4408 | 0.13313 | 0 | 0 | 0.142 | 0 | 0.23169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.4597 |  | STD2010 | 0 | 0 | 0 | 0.064223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064223 |  | STD2010 | 18.6404 | 4.6147 | 1.3938 | 7.0195 | 0 | 1.4866 | 0 | 2.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.2389
STD2007 | 0.26547 | 0.067996 | 0.01419 | 0.072587 | 0 | 0.021665 | 0 | 0.037948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.55657 |  | STD2007 | 8.7793 | 2.2487 | 0.4693 | 7.332 | 0 | 0.7165 | 0 | 1.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.338 |  | STD2007 | 2.5723 | 0.65887 | 0.1375 | 0 | 0 | 0.20993 | 0 | 0.36771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6897 |  | STD2007 | 0 | 0 | 0 | 0.07332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07332 |  | STD2007 | 26.9297 | 6.8978 | 1.4395 | 8.0139 | 0 | 2.1978 | 0 | 3.8495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 57.1104
STD2004 | 0.26547 | 0.067996 | 0.01419 | 0.094171 | 0 | 0.022072 | 0 | 0.038342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.57895 |  | STD2004 | 8.7793 | 2.2487 | 0.4693 | 9.5122 | 0 | 0.72994 | 0 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.5447 |  | STD2004 | 2.5723 | 0.65887 | 0.1375 | 0 | 0 | 0.21387 | 0 | 0.37152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6975 |  | STD2004 | 0 | 0 | 0 | 0.095122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095122 |  | STD2004 | 26.9297 | 6.8978 | 1.4395 | 10.3969 | 0 | 2.239 | 0 | 3.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 59.5746
Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions: | [18 empty] | Savings between versions:
2004-2007 | 0 | 0 | 1.4934e-08 | 0.021585 | 0 | 0.00040665 | 0 | 0.00039395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022385 |  | 2004-2007 | 0 | 0 | 4.9389e-07 | 2.1803 | 0 | 0.013449 | 0 | 0.013028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2067 |  | 2004-2007 | 0 | 0 | 1.4471e-07 | 0 | 0 | 0.0039404 | 0 | 0.0038173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077578 |  | 2004-2007 | 0 | 0 | 0 | 0.021803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021803 |  | 2004-2007 | 0 | 0 | 1.515e-06 | 2.383 | 0 | 0.041252 | 0 | 0.039963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4642
2007-2010 | 0.081713 | 0.022506 | 0.00045096 | 0.0090064 | 0 | 0.0070103 | 0 | 0.014037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012228 | 0.13595 |  | 2007-2010 | 2.7024 | 0.7443 | 0.014914 | 0.90973 | 0 | 0.23184 | 0 | 0.46423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040439 | 5.1078 |  | 2007-2010 | 0.79179 | 0.21808 | 0.0043698 | 0 | 0 | 0.067929 | 0 | 0.13602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011849 | 1.23 |  | 2007-2010 | 0 | 0 | 0 | 0.0090973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090973 |  | 2007-2010 | 8.2892 | 2.2831 | 0.045747 | 0.99434 | 0 | 0.71114 | 0 | 1.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12404 | 13.8715
2010-2013 | 0.013764 | 0 | 1.6984e-06 | 0.0036776 | 0 | 0.0027966 | 0 | 0.0049632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030845 | 0.025512 |  | 2010-2013 | 0.4552 | 0 | 5.6169e-05 | 0.37147 | 0 | 0.092489 | 0 | 0.16414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010201 | 1.0936 |  | 2010-2013 | 0.13337 | 0 | 1.6457e-05 | 0 | 0 | 0.027099 | 0 | 0.048093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029888 | 0.21157 |  | 2010-2013 | 0 | 0 | 0 | 0.0037147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037147 |  | 2010-2013 | 1.3963 | 0 | 0.00017229 | 0.40602 | 0 | 0.2837 | 0 | 0.50348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03129 | 2.6209
2004-2013 | 0.095477 | 0.022506 | 0.00045268 | 0.034268 | 0 | 0.010214 | 0 | 0.019394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.18384 |  | 2004-2013 | 3.1576 | 0.7443 | 0.014971 | 3.4615 | 0 | 0.33778 | 0 | 0.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 8.4081 |  | 2004-2013 | 0.92516 | 0.21808 | 0.0043864 | 0 | 0 | 0.098968 | 0 | 0.18793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.4494 |  | 2004-2013 | 0 | 0 | 0 | 0.034615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034615 |  | 2004-2013 | 9.6855 | 2.2831 | 0.045921 | 3.7834 | 0 | 1.0361 | 0 | 1.9674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 18.9567
Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions: | [18 empty] | Percentage savings between versions:
2004-2007 | 0% | 0% | 0.0001052% | 22.92% |  | 1.842% |  | 1.027% | [7 empty] | 0% | 3.866% |  | 2004-2007 | 0% | 0% | 0.0001052% | 22.92% |  | 1.842% |  | 1.027% | [7 empty] | 0% | 8.639% |  | 2004-2007 | 0% | 0% | 0.0001052% |  |  | 1.842% |  | 1.027% | [7 empty] | 0% | 0.1651% |  | 2004-2007 |  |  |  | 22.92% | [12 empty] | 22.92% |  | 2004-2007 | 0% | 0% | 0.0001052% | 22.92% |  | 1.842% |  | 1.027% | [7 empty] | 0% | 4.136%
2007-2010 | 30.78% | 33.1% | 3.178% | 12.41% |  | 32.36% |  | 36.99% | [7 empty] | 1.594% | 24.43% |  | 2007-2010 | 30.78% | 33.1% | 3.178% | 12.41% |  | 32.36% |  | 36.99% | [7 empty] | 1.594% | 21.89% |  | 2007-2010 | 30.78% | 33.1% | 3.178% |  |  | 32.36% |  | 36.99% | [7 empty] | 1.594% | 26.23% |  | 2007-2010 |  |  |  | 12.41% | [12 empty] | 12.41% |  | 2007-2010 | 30.78% | 33.1% | 3.178% | 12.41% |  | 32.36% |  | 36.99% | [7 empty] | 1.594% | 24.29%
2010-2013 | 7.491% | 0% | 0.01236% | 5.784% |  | 19.08% |  | 20.76% | [7 empty] | 0.4086% | 6.065% |  | 2010-2013 | 7.491% | 0% | 0.01236% | 5.784% |  | 19.08% |  | 20.76% | [7 empty] | 0.4086% | 5.999% |  | 2010-2013 | 7.491% | 0% | 0.01236% |  |  | 19.08% |  | 20.76% | [7 empty] | 0.4086% | 6.115% |  | 2010-2013 |  |  |  | 5.784% | [12 empty] | 5.784% |  | 2010-2013 | 7.491% | 0% | 0.01236% | 5.784% |  | 19.08% |  | 20.76% | [7 empty] | 0.4086% | 6.062%
2004-2013 | 35.97% | 33.1% | 3.19% | 36.39% |  | 46.27% |  | 50.58% | [7 empty] | 1.996% | 31.75% |  | 2004-2013 | 35.97% | 33.1% | 3.19% | 36.39% |  | 46.27% |  | 50.58% | [7 empty] | 1.996% | 32.92% |  | 2004-2013 | 35.97% | 33.1% | 3.19% |  |  | 46.27% |  | 50.58% | [7 empty] | 1.996% | 30.85% |  | 2004-2013 |  |  |  | 36.39% | [12 empty] | 36.39% |  | 2004-2013 | 35.97% | 33.1% | 3.19% | 36.39% |  | 46.27% |  | 50.58% | [7 empty] | 1.996% | 31.82%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.1593 | 0.045508 | 0.012558 | 0.00021996 | 0 | 0.032856 | 0 | 0.014563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.34019 | 2.089% | CZ 1A | 5.2684 | 1.505 | 0.41532 | 0.022218 | 0 | 1.0866 | 0 | 0.48163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.2656 | 2.089% | CZ 1A | 1.5436 | 0.44096 | 0.12169 | 0 | 0 | 0.31836 | 0 | 0.14112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2943 | 2.089% | CZ 1A | 0 | 0 | 0 | 0.00022218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00022218 | 2.089% | CZ 1A | 16.1602 | 4.6164 | 1.274 | 0.024284 | 0 | 3.333 | 0 | 1.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 34.5122 | 2.089%
CZ 1B | 0.16339 | 0.045463 | 0.012338 | 0.0035175 | 0 | 0.13 | 0 | 0.071869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.50176 | 0% | CZ 1B | 5.4036 | 1.5035 | 0.40804 | 0.35531 | 0 | 4.2991 | 0 | 2.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 16.8329 | 0% | CZ 1B | 1.5832 | 0.44053 | 0.11955 | 0 | 0 | 1.2596 | 0 | 0.6964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 4.8279 | 0% | CZ 1B | 0 | 0 | 0 | 0.0035531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0035531 | 0% | CZ 1B | 16.5748 | 4.6119 | 1.2516 | 0.38835 | 0 | 13.1871 | 0 | 7.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 50.9315 | 0%
CZ 2A | 0.16366 | 0.045414 | 0.013098 | 0.015579 | 0 | 0.021189 | 0 | 0.020396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.35452 | 15.5% | CZ 2A | 5.4123 | 1.5019 | 0.43317 | 1.5737 | 0 | 0.70077 | 0 | 0.67454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.7828 | 15.5% | CZ 2A | 1.5858 | 0.44005 | 0.12692 | 0 | 0 | 0.20532 | 0 | 0.19764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2843 | 15.5% | CZ 2A | 0 | 0 | 0 | 0.015737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015737 | 15.5% | CZ 2A | 16.6017 | 4.6069 | 1.3287 | 1.72 | 0 | 2.1495 | 0 | 2.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 36.1029 | 15.5%
CZ 2B | 0.17098 | 0.045381 | 0.01279 | 0.010879 | 0 | 0.072629 | 0 | 0.064499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.45234 | 3.472% | CZ 2B | 5.6546 | 1.5008 | 0.42297 | 1.0989 | 0 | 2.4019 | 0 | 2.1331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.6987 | 3.472% | CZ 2B | 1.6568 | 0.43973 | 0.12393 | 0 | 0 | 0.70376 | 0 | 0.62499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 4.2777 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.010989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010989 | 3.472% | CZ 2B | 17.3448 | 4.6036 | 1.2974 | 1.2011 | 0 | 7.3677 | 0 | 6.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 45.9846 | 3.472%
CZ 3A | 0.16722 | 0.045502 | 0.013511 | 0.043871 | 0 | 0.013792 | 0 | 0.019107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.37819 | 17.75% | CZ 3A | 5.5302 | 1.5048 | 0.44684 | 4.4314 | 0 | 0.45613 | 0 | 0.63191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.4877 | 17.75% | CZ 3A | 1.6203 | 0.44091 | 0.13092 | 0 | 0 | 0.13364 | 0 | 0.18515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2395 | 17.75% | CZ 3A | 0 | 0 | 0 | 0.044314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044314 | 17.75% | CZ 3A | 16.9632 | 4.6159 | 1.3706 | 4.8435 | 0 | 1.3991 | 0 | 1.9383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 38.7576 | 17.75%
CZ 3B | 0.16843 | 0.045452 | 0.013374 | 0.026206 | 0 | 0.013704 | 0 | 0.025062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.36741 | 13.75% | CZ 3B | 5.5702 | 1.5032 | 0.44228 | 2.647 | 0 | 0.45321 | 0 | 0.82882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 13.9312 | 13.75% | CZ 3B | 1.6321 | 0.44043 | 0.12959 | 0 | 0 | 0.13279 | 0 | 0.24284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.3062 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.02647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02647 | 13.75% | CZ 3B | 17.0861 | 4.6108 | 1.3567 | 2.8932 | 0 | 1.3902 | 0 | 2.5423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 37.5063 | 13.75%
CZ 3C | 0.1684 | 0.045419 | 0.013985 | 0.045135 | 0 | 3.8556e-05 | 0 | 0.01095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.35912 | 0.9199% | CZ 3C | 5.5693 | 1.5021 | 0.4625 | 4.5591 | 0 | 0.0012751 | 0 | 0.36213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.9429 | 0.9199% | CZ 3C | 1.6318 | 0.44011 | 0.13551 | 0 | 0 | 0.0003736 | 0 | 0.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.0424 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.045591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045591 | 0.9199% | CZ 3C | 17.0833 | 4.6075 | 1.4187 | 4.9831 | 0 | 0.0039113 | 0 | 1.1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 36.8342 | 0.9199%
CZ 4A | 0.17025 | 0.045497 | 0.014012 | 0.073349 | 0 | 0.0036408 | 0 | 0.012129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.39407 | 14.63% | CZ 4A | 5.6305 | 1.5046 | 0.46341 | 7.409 | 0 | 0.12041 | 0 | 0.40111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.0156 | 14.63% | CZ 4A | 1.6497 | 0.44085 | 0.13578 | 0 | 0 | 0.035279 | 0 | 0.11753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.1077 | 14.63% | CZ 4A | 0 | 0 | 0 | 0.07409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07409 | 14.63% | CZ 4A | 17.2711 | 4.6153 | 1.4215 | 8.098 | 0 | 0.36934 | 0 | 1.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.6325 | 14.63%
CZ 4B | 0.17251 | 0.045441 | 0.013941 | 0.048056 | 0 | 0.0038446 | 0 | 0.020655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.37963 | 0.4058% | CZ 4B | 5.705 | 1.5028 | 0.46104 | 4.8541 | 0 | 0.12715 | 0 | 0.6831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.8197 | 0.4058% | CZ 4B | 1.6716 | 0.44032 | 0.13508 | 0 | 0 | 0.037254 | 0 | 0.20015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2129 | 0.4058% | CZ 4B | 0 | 0 | 0 | 0.048541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048541 | 0.4058% | CZ 4B | 17.4996 | 4.6097 | 1.4142 | 5.3055 | 0 | 0.39001 | 0 | 2.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 38.9413 | 0.4058%
CZ 4C | 0.17402 | 0.04553 | 0.014238 | 0.061947 | 0 | 0.00025888 | 0 | 0.013555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.38474 | 2.605% | CZ 4C | 5.7551 | 1.5057 | 0.47088 | 6.2573 | 0 | 0.0085615 | 0 | 0.44829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 16.9324 | 2.605% | CZ 4C | 1.6862 | 0.44117 | 0.13797 | 0 | 0 | 0.0025085 | 0 | 0.13135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.1278 | 2.605% | CZ 4C | 0 | 0 | 0 | 0.062573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062573 | 2.605% | CZ 4C | 17.6532 | 4.6187 | 1.4444 | 6.8392 | 0 | 0.026261 | 0 | 1.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 39.5838 | 2.605%
CZ 5A | 0.16921 | 0.045585 | 0.014365 | 0.12046 | 0 | 0.0018672 | 0 | 0.014657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.44133 | 21.41% | CZ 5A | 5.5959 | 1.5075 | 0.47507 | 12.1676 | 0 | 0.061752 | 0 | 0.48473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 22.7791 | 21.41% | CZ 5A | 1.6396 | 0.44171 | 0.13919 | 0 | 0 | 0.018093 | 0 | 0.14202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.1091 | 21.41% | CZ 5A | 0 | 0 | 0 | 0.12168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12168 | 21.41% | CZ 5A | 17.1649 | 4.6242 | 1.4572 | 13.2992 | 0 | 0.18942 | 0 | 1.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 45.8488 | 21.41%
CZ 5B | 0.17744 | 0.045331 | 0.014304 | 0.070286 | 0 | 0.0015643 | 0 | 0.013104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.39722 | 4.118% | CZ 5B | 5.8683 | 1.4992 | 0.47307 | 7.0996 | 0 | 0.051733 | 0 | 0.43336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.9116 | 4.118% | CZ 5B | 1.7194 | 0.43925 | 0.13861 | 0 | 0 | 0.015158 | 0 | 0.12697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.1679 | 4.118% | CZ 5B | 0 | 0 | 0 | 0.070996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070996 | 4.118% | CZ 5B | 18.0002 | 4.5985 | 1.4511 | 7.7598 | 0 | 0.15869 | 0 | 1.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.9246 | 4.118%
CZ 5C | 0.18193 | 0.045546 | 0.014387 | 0.073185 | 0 | 7.7113e-05 | 0 | 0.015367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.40567 | 0% | CZ 5C | 6.0165 | 1.5063 | 0.4758 | 7.3924 | 0 | 0.0025502 | 0 | 0.50822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.3883 | 0% | CZ 5C | 1.7628 | 0.44133 | 0.13941 | 0 | 0 | 0.00074721 | 0 | 0.14891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2218 | 0% | CZ 5C | 0 | 0 | 0 | 0.073924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073924 | 0% | CZ 5C | 18.455 | 4.6203 | 1.4595 | 8.0799 | 0 | 0.0078225 | 0 | 1.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 41.8085 | 0%
CZ 6A | 0.21753 | 0.045634 | 0.014673 | 0.11787 | 0 | 0.0004792 | 0 | 0.011391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.48276 | 2.787% | CZ 6A | 7.194 | 1.5092 | 0.48527 | 11.9063 | 0 | 0.015848 | 0 | 0.3767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 23.9738 | 2.787% | CZ 6A | 2.1078 | 0.44219 | 0.14218 | 0 | 0 | 0.0046434 | 0 | 0.11037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.5357 | 2.787% | CZ 6A | 0 | 0 | 0 | 0.11906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11906 | 2.787% | CZ 6A | 22.0668 | 4.6293 | 1.4885 | 13.0136 | 0 | 0.048611 | 0 | 1.1555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 50.0293 | 2.787%
CZ 6B | 0.21877 | 0.045414 | 0.014723 | 0.084026 | 0 | 0.00029743 | 0 | 0.018088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.45651 | 0.2931% | CZ 6B | 7.2352 | 1.5019 | 0.48691 | 8.4875 | 0 | 0.0098366 | 0 | 0.59821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 20.806 | 0.2931% | CZ 6B | 2.1199 | 0.44005 | 0.14266 | 0 | 0 | 0.0028821 | 0 | 0.17527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.6093 | 0.2931% | CZ 6B | 0 | 0 | 0 | 0.084875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084875 | 0.2931% | CZ 6B | 22.1931 | 4.6069 | 1.4935 | 9.2768 | 0 | 0.030173 | 0 | 1.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 47.0625 | 0.2931%
CZ 7 | 0.21747 | 0.04553 | 0.015164 | 0.19911 | 0 | 0.00014872 | 0 | 0.016464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.56908 | 0.2579% | CZ 7 | 7.1922 | 1.5057 | 0.50148 | 20.1124 | 0 | 0.0049183 | 0 | 0.54447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 32.3477 | 0.2579% | CZ 7 | 2.1073 | 0.44117 | 0.14693 | 0 | 0 | 0.001441 | 0 | 0.15953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.5849 | 0.2579% | CZ 7 | 0 | 0 | 0 | 0.20112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20112 | 0.2579% | CZ 7 | 22.0612 | 4.6187 | 1.5382 | 21.9829 | 0 | 0.015086 | 0 | 1.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 59.5132 | 0.2579%
CZ 8 | 0.22036 | 0.045766 | 0.015759 | 0.19875 | 0 | 0.00012118 | 0 | 0.017543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.57349 | 0.01321% | CZ 8 | 7.2876 | 1.5136 | 0.52116 | 20.0758 | 0 | 0.0040075 | 0 | 0.58018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 32.4688 | 0.01321% | CZ 8 | 2.1353 | 0.44347 | 0.1527 | 0 | 0 | 0.0011742 | 0 | 0.16999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.6311 | 0.01321% | CZ 8 | 0 | 0 | 0 | 0.20076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20076 | 0.01321% | CZ 8 | 22.354 | 4.6427 | 1.5986 | 21.9429 | 0 | 0.012293 | 0 | 1.7796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 59.957 | 0.01321%
Us Weighted | 0.16999 | 0.045491 | 0.013738 | 0.059903 | 0 | 0.011858 | 0 | 0.018947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075185 | 0.39511 | 100% | Us Weighted | 5.6218 | 1.5044 | 0.45433 | 6.0508 | 0 | 0.39217 | 0 | 0.62661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.1366 | 100% | Us Weighted | 1.6472 | 0.4408 | 0.13312 | 0 | 0 | 0.1149 | 0 | 0.18359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72853 | 3.2481 | 100% | Us Weighted | 0 | 0 | 0 | 0.060508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060508 | 100% | Us Weighted | 17.2442 | 4.6147 | 1.3936 | 6.6135 | 0 | 1.2029 | 0 | 1.9221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.627 | 40.6179 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.17479 | 0.045508 | 0.012569 | 0.00021635 | 0 | 0.042979 | 0 | 0.024566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.37612 | 2.089% | CZ 1A | 5.7805 | 1.505 | 0.41569 | 0.021854 | 0 | 1.4214 | 0 | 0.81243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.4535 | 2.089% | CZ 1A | 1.6937 | 0.44096 | 0.1218 | 0 | 0 | 0.41646 | 0 | 0.23804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.6424 | 2.089% | CZ 1A | 0 | 0 | 0 | 0.00021854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00021854 | 2.089% | CZ 1A | 17.7309 | 4.6164 | 1.2751 | 0.023886 | 0 | 4.3599 | 0 | 2.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 38.1565 | 2.089%
CZ 1B | 0.18264 | 0.045463 | 0.012338 | 0.0040548 | 0 | 0.13766 | 0 | 0.075851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.5335 | 0% | CZ 1B | 6.0402 | 1.5035 | 0.40804 | 0.40958 | 0 | 4.5525 | 0 | 2.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 17.9191 | 0% | CZ 1B | 1.7698 | 0.44053 | 0.11955 | 0 | 0 | 1.3339 | 0 | 0.73499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 5.1302 | 0% | CZ 1B | 0 | 0 | 0 | 0.0040958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040958 | 0% | CZ 1B | 18.5277 | 4.6119 | 1.2516 | 0.44767 | 0 | 13.9644 | 0 | 7.6946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 54.1561 | 0%
CZ 2A | 0.17975 | 0.045414 | 0.013104 | 0.01599 | 0 | 0.02683 | 0 | 0.025508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.38209 | 15.5% | CZ 2A | 5.9446 | 1.5019 | 0.43336 | 1.6152 | 0 | 0.8873 | 0 | 0.84358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 13.7226 | 15.5% | CZ 2A | 1.7417 | 0.44005 | 0.12697 | 0 | 0 | 0.25998 | 0 | 0.24717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.5474 | 15.5% | CZ 2A | 0 | 0 | 0 | 0.016152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016152 | 15.5% | CZ 2A | 18.2343 | 4.6069 | 1.3293 | 1.7654 | 0 | 2.7217 | 0 | 2.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 38.9035 | 15.5%
CZ 2B | 0.1885 | 0.045381 | 0.012784 | 0.010527 | 0 | 0.078886 | 0 | 0.075268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.48684 | 3.472% | CZ 2B | 6.2338 | 1.5008 | 0.42279 | 1.0634 | 0 | 2.6089 | 0 | 2.4892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 16.8156 | 3.472% | CZ 2B | 1.8265 | 0.43973 | 0.12388 | 0 | 0 | 0.7644 | 0 | 0.72933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 4.6154 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.010634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010634 | 3.472% | CZ 2B | 19.1216 | 4.6036 | 1.2969 | 1.1623 | 0 | 8.0025 | 0 | 7.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 49.4804 | 3.472%
CZ 3A | 0.18261 | 0.045502 | 0.013511 | 0.044956 | 0 | 0.017328 | 0 | 0.022605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.402 | 17.75% | CZ 3A | 6.0391 | 1.5048 | 0.44684 | 4.541 | 0 | 0.57307 | 0 | 0.74758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 16.3491 | 17.75% | CZ 3A | 1.7694 | 0.44091 | 0.13092 | 0 | 0 | 0.16791 | 0 | 0.21904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.4597 | 17.75% | CZ 3A | 0 | 0 | 0 | 0.04541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04541 | 17.75% | CZ 3A | 18.5243 | 4.6159 | 1.3706 | 4.9634 | 0 | 1.7578 | 0 | 2.2931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 41.1834 | 17.75%
CZ 3B | 0.18487 | 0.045452 | 0.013374 | 0.02745 | 0 | 0.01637 | 0 | 0.02743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.39044 | 13.75% | CZ 3B | 6.1138 | 1.5032 | 0.44228 | 2.7727 | 0 | 0.54138 | 0 | 0.90715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 14.7772 | 13.75% | CZ 3B | 1.7913 | 0.44043 | 0.12959 | 0 | 0 | 0.15862 | 0 | 0.26579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.5173 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.027727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027727 | 13.75% | CZ 3B | 18.7534 | 4.6108 | 1.3567 | 3.0306 | 0 | 1.6606 | 0 | 2.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 39.8529 | 13.75%
CZ 3C | 0.18586 | 0.045419 | 0.013985 | 0.045998 | 0 | 4.9572e-05 | 0 | 0.011589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.3784 | 0.9199% | CZ 3C | 6.1468 | 1.5021 | 0.4625 | 4.6463 | 0 | 0.0016394 | 0 | 0.38326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.6392 | 0.9199% | CZ 3C | 1.801 | 0.44011 | 0.13551 | 0 | 0 | 0.00048035 | 0 | 0.11229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.2209 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.046463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046463 | 0.9199% | CZ 3C | 18.8546 | 4.6075 | 1.4187 | 5.0784 | 0 | 0.0050288 | 0 | 1.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 38.798 | 0.9199%
CZ 4A | 0.182 | 0.045497 | 0.014018 | 0.078448 | 0 | 0.005453 | 0 | 0.021531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.42244 | 14.63% | CZ 4A | 6.0191 | 1.5046 | 0.46359 | 7.924 | 0 | 0.18034 | 0 | 0.71206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.3004 | 14.63% | CZ 4A | 1.7636 | 0.44085 | 0.13583 | 0 | 0 | 0.052838 | 0 | 0.20863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.3332 | 14.63% | CZ 4A | 0 | 0 | 0 | 0.07924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07924 | 14.63% | CZ 4A | 18.4629 | 4.6153 | 1.422 | 8.6609 | 0 | 0.55317 | 0 | 2.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.5567 | 14.63%
CZ 4B | 0.18466 | 0.045441 | 0.013941 | 0.051276 | 0 | 0.0061194 | 0 | 0.027281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.40421 | 0.4058% | CZ 4B | 6.1069 | 1.5028 | 0.46104 | 5.1793 | 0 | 0.20238 | 0 | 0.90223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 16.8514 | 0.4058% | CZ 4B | 1.7893 | 0.44032 | 0.13508 | 0 | 0 | 0.059296 | 0 | 0.26435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.4199 | 0.4058% | CZ 4B | 0 | 0 | 0 | 0.051793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051793 | 0.4058% | CZ 4B | 18.7322 | 4.6097 | 1.4142 | 5.661 | 0 | 0.62077 | 0 | 2.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 41.4637 | 0.4058%
CZ 4C | 0.18584 | 0.04553 | 0.014238 | 0.066649 | 0 | 0.00040209 | 0 | 0.015494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.40365 | 2.605% | CZ 4C | 6.146 | 1.5057 | 0.47088 | 6.7322 | 0 | 0.013298 | 0 | 0.51241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 17.8773 | 2.605% | CZ 4C | 1.8008 | 0.44117 | 0.13797 | 0 | 0 | 0.0038962 | 0 | 0.15014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.2655 | 2.605% | CZ 4C | 0 | 0 | 0 | 0.067322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067322 | 2.605% | CZ 4C | 18.8523 | 4.6187 | 1.4444 | 7.3583 | 0 | 0.040789 | 0 | 1.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 41.5445 | 2.605%
CZ 5A | 0.18093 | 0.045585 | 0.014365 | 0.12993 | 0 | 0.0026824 | 0 | 0.016943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.46592 | 21.41% | CZ 5A | 5.9836 | 1.5075 | 0.47507 | 13.1239 | 0 | 0.088711 | 0 | 0.56032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 24.2358 | 21.41% | CZ 5A | 1.7532 | 0.44171 | 0.13919 | 0 | 0 | 0.025992 | 0 | 0.16417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.2558 | 21.41% | CZ 5A | 0 | 0 | 0 | 0.13124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13124 | 21.41% | CZ 5A | 18.3539 | 4.6242 | 1.4572 | 14.3445 | 0 | 0.27211 | 0 | 1.7187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 48.4289 | 21.41%
CZ 5B | 0.18945 | 0.045331 | 0.014304 | 0.073612 | 0 | 0.0025502 | 0 | 0.023668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.42441 | 4.118% | CZ 5B | 6.2654 | 1.4992 | 0.47307 | 7.4356 | 0 | 0.08434 | 0 | 0.78274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.0369 | 4.118% | CZ 5B | 1.8357 | 0.43925 | 0.13861 | 0 | 0 | 0.024711 | 0 | 0.22934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.3992 | 4.118% | CZ 5B | 0 | 0 | 0 | 0.074356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074356 | 4.118% | CZ 5B | 19.2183 | 4.5985 | 1.4511 | 8.1271 | 0 | 0.2587 | 0 | 2.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.7129 | 4.118%
CZ 5C | 0.19251 | 0.045546 | 0.014387 | 0.079576 | 0 | 8.8129e-05 | 0 | 0.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.425 | 0% | CZ 5C | 6.3666 | 1.5063 | 0.4758 | 8.038 | 0 | 0.0029145 | 0 | 0.57544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.4617 | 0% | CZ 5C | 1.8654 | 0.44133 | 0.13941 | 0 | 0 | 0.00085395 | 0 | 0.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.3471 | 0% | CZ 5C | 0 | 0 | 0 | 0.08038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08038 | 0% | CZ 5C | 19.529 | 4.6203 | 1.4595 | 8.7855 | 0 | 0.00894 | 0 | 1.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.8266 | 0%
CZ 6A | 0.22098 | 0.045634 | 0.014673 | 0.12376 | 0 | 0.00068851 | 0 | 0.020215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.50145 | 2.787% | CZ 6A | 7.3082 | 1.5092 | 0.48527 | 12.5015 | 0 | 0.02277 | 0 | 0.66852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 24.9921 | 2.787% | CZ 6A | 2.1413 | 0.44219 | 0.14218 | 0 | 0 | 0.0066715 | 0 | 0.19588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.6597 | 2.787% | CZ 6A | 0 | 0 | 0 | 0.12501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12501 | 2.787% | CZ 6A | 22.4172 | 4.6293 | 1.4885 | 13.6641 | 0 | 0.069844 | 0 | 2.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 51.9778 | 2.787%
CZ 6B | 0.22214 | 0.045414 | 0.014723 | 0.090704 | 0 | 0.00041861 | 0 | 0.021162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.47005 | 0.2931% | CZ 6B | 7.3465 | 1.5019 | 0.48691 | 9.162 | 0 | 0.013844 | 0 | 0.69986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 21.7077 | 0.2931% | CZ 6B | 2.1525 | 0.44005 | 0.14266 | 0 | 0 | 0.0040563 | 0 | 0.20506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.6758 | 0.2931% | CZ 6B | 0 | 0 | 0 | 0.09162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09162 | 0.2931% | CZ 6B | 22.5345 | 4.6069 | 1.4935 | 10.0141 | 0 | 0.042465 | 0 | 2.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 48.4965 | 0.2931%
CZ 7 | 0.21726 | 0.04553 | 0.015164 | 0.20766 | 0 | 0.0002038 | 0 | 0.017631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.57894 | 0.2579% | CZ 7 | 7.1851 | 1.5057 | 0.50148 | 20.9758 | 0 | 0.0067399 | 0 | 0.58309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 33.2546 | 0.2579% | CZ 7 | 2.1052 | 0.44117 | 0.14693 | 0 | 0 | 0.0019748 | 0 | 0.17084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.5977 | 0.2579% | CZ 7 | 0 | 0 | 0 | 0.20976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20976 | 0.2579% | CZ 7 | 22.0394 | 4.6187 | 1.5382 | 22.9266 | 0 | 0.020674 | 0 | 1.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 60.5904 | 0.2579%
CZ 8 | 0.22431 | 0.045766 | 0.015759 | 0.21982 | 0 | 9.3637e-05 | 0 | 0.02071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.60195 | 0.01321% | CZ 8 | 7.4182 | 1.5136 | 0.52116 | 22.2038 | 0 | 0.0030967 | 0 | 0.68492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 34.8415 | 0.01321% | CZ 8 | 2.1735 | 0.44347 | 0.1527 | 0 | 0 | 0.00090733 | 0 | 0.20068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.7028 | 0.01321% | CZ 8 | 0 | 0 | 0 | 0.22204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22204 | 0.01321% | CZ 8 | 22.7547 | 4.6427 | 1.5986 | 24.2688 | 0 | 0.0094988 | 0 | 2.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 63.0334 | 0.01321%
Us Weighted | 0.18375 | 0.045491 | 0.013739 | 0.06358 | 0 | 0.014655 | 0 | 0.02391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075493 | 0.42062 | 100% | Us Weighted | 6.077 | 1.5044 | 0.45438 | 6.4223 | 0 | 0.48465 | 0 | 0.79075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 18.2301 | 100% | Us Weighted | 1.7805 | 0.4408 | 0.13313 | 0 | 0 | 0.142 | 0 | 0.23169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73152 | 3.4597 | 100% | Us Weighted | 0 | 0 | 0 | 0.064223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064223 | 100% | Us Weighted | 18.6404 | 4.6147 | 1.3938 | 7.0195 | 0 | 1.4866 | 0 | 2.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6583 | 43.2389 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.26547 | 0.068124 | 0.012982 | 0.00022897 | 0 | 0.068994 | 0 | 0.04906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.54157 | 2.089% | CZ 1A | 8.7793 | 2.2529 | 0.42935 | 0.023129 | 0 | 2.2817 | 0 | 1.6225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.9261 | 2.089% | CZ 1A | 2.5723 | 0.66011 | 0.1258 | 0 | 0 | 0.66854 | 0 | 0.47539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.2455 | 2.089% | CZ 1A | 0 | 0 | 0 | 0.00023129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00023129 | 2.089% | CZ 1A | 26.9297 | 6.9107 | 1.317 | 0.02528 | 0 | 6.9989 | 0 | 4.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 54.9406 | 2.089%
CZ 1B | 0.26547 | 0.068063 | 0.012746 | 0.0027693 | 0 | 0.19486 | 0 | 0.17412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.79473 | 0% | CZ 1B | 8.7793 | 2.2509 | 0.42152 | 0.27973 | 0 | 6.4442 | 0 | 5.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 26.4711 | 0% | CZ 1B | 2.5723 | 0.65952 | 0.1235 | 0 | 0 | 1.8881 | 0 | 1.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 7.674 | 0% | CZ 1B | 0 | 0 | 0 | 0.0027973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027973 | 0% | CZ 1B | 26.9297 | 6.9045 | 1.293 | 0.30574 | 0 | 19.767 | 0 | 17.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 80.6449 | 0%
CZ 2A | 0.26547 | 0.068002 | 0.013539 | 0.01857 | 0 | 0.039641 | 0 | 0.039201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.52114 | 15.5% | CZ 2A | 8.7793 | 2.2489 | 0.44775 | 1.8758 | 0 | 1.311 | 0 | 1.2964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.4963 | 15.5% | CZ 2A | 2.5723 | 0.65893 | 0.13119 | 0 | 0 | 0.38412 | 0 | 0.37985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.8698 | 15.5% | CZ 2A | 0 | 0 | 0 | 0.018758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018758 | 15.5% | CZ 2A | 26.9297 | 6.8984 | 1.3734 | 2.0502 | 0 | 4.0213 | 0 | 3.9766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 53.032 | 15.5%
CZ 2B | 0.26547 | 0.067958 | 0.013208 | 0.006651 | 0 | 0.1032 | 0 | 0.12182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.65502 | 3.472% | CZ 2B | 8.7793 | 2.2475 | 0.43682 | 0.67182 | 0 | 3.4129 | 0 | 4.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.1141 | 3.472% | CZ 2B | 2.5723 | 0.65851 | 0.12799 | 0 | 0 | 0.99998 | 0 | 1.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 6.2825 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.0067182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067182 | 3.472% | CZ 2B | 26.9297 | 6.8939 | 1.3399 | 0.7343 | 0 | 10.4688 | 0 | 12.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 66.5062 | 3.472%
CZ 3A | 0.26547 | 0.068046 | 0.013963 | 0.054304 | 0 | 0.027067 | 0 | 0.036805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.54237 | 17.75% | CZ 3A | 8.7793 | 2.2504 | 0.46177 | 5.4853 | 0 | 0.89513 | 0 | 1.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.6262 | 17.75% | CZ 3A | 2.5723 | 0.65936 | 0.1353 | 0 | 0 | 0.26227 | 0 | 0.35663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7293 | 17.75% | CZ 3A | 0 | 0 | 0 | 0.054853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054853 | 17.75% | CZ 3A | 26.9297 | 6.9028 | 1.4164 | 5.9954 | 0 | 2.7457 | 0 | 3.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 55.506 | 17.75%
CZ 3B | 0.26547 | 0.068052 | 0.013814 | 0.025189 | 0 | 0.023619 | 0 | 0.046785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.51964 | 13.75% | CZ 3B | 8.7793 | 2.2506 | 0.45685 | 2.5443 | 0 | 0.7811 | 0 | 1.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.8966 | 13.75% | CZ 3B | 2.5723 | 0.65941 | 0.13386 | 0 | 0 | 0.22886 | 0 | 0.45334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7912 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.025443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025443 | 13.75% | CZ 3B | 26.9297 | 6.9034 | 1.4014 | 2.781 | 0 | 2.3959 | 0 | 4.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 52.9396 | 13.75%
CZ 3C | 0.26547 | 0.067953 | 0.014459 | 0.045604 | 0 | 6.6097e-05 | 0 | 0.012052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.48232 | 0.9199% | CZ 3C | 8.7793 | 2.2473 | 0.47817 | 4.6064 | 0 | 0.0021859 | 0 | 0.39856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.0491 | 0.9199% | CZ 3C | 2.5723 | 0.65845 | 0.1401 | 0 | 0 | 0.00064047 | 0 | 0.11678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2317 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.046064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046064 | 0.9199% | CZ 3C | 26.9297 | 6.8933 | 1.4667 | 5.0348 | 0 | 0.006705 | 0 | 1.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 49.3361 | 0.9199%
CZ 4A | 0.26547 | 0.068013 | 0.014475 | 0.094187 | 0 | 0.0080913 | 0 | 0.025348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.5523 | 14.63% | CZ 4A | 8.7793 | 2.2493 | 0.47871 | 9.5139 | 0 | 0.26759 | 0 | 0.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 24.6642 | 14.63% | CZ 4A | 2.5723 | 0.65904 | 0.14026 | 0 | 0 | 0.078404 | 0 | 0.24562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.439 | 14.63% | CZ 4A | 0 | 0 | 0 | 0.095139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095139 | 14.63% | CZ 4A | 26.9297 | 6.8995 | 1.4684 | 10.3987 | 0 | 0.82081 | 0 | 2.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 56.8707 | 14.63%
CZ 4B | 0.26547 | 0.067997 | 0.014398 | 0.053791 | 0 | 0.0084989 | 0 | 0.033136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.52 | 0.4058% | CZ 4B | 8.7793 | 2.2488 | 0.47616 | 5.4334 | 0 | 0.28107 | 0 | 1.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.8517 | 0.4058% | CZ 4B | 2.5723 | 0.65888 | 0.13951 | 0 | 0 | 0.082353 | 0 | 0.32109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5175 | 0.4058% | CZ 4B | 0 | 0 | 0 | 0.054334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054334 | 0.4058% | CZ 4B | 26.9297 | 6.8978 | 1.4606 | 5.9387 | 0 | 0.86216 | 0 | 3.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 53.2327 | 0.4058%
CZ 4C | 0.26547 | 0.06798 | 0.014712 | 0.07109 | 0 | 0.00064444 | 0 | 0.017053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.51366 | 2.605% | CZ 4C | 8.7793 | 2.2482 | 0.48655 | 7.1808 | 0 | 0.021313 | 0 | 0.56396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.8173 | 2.605% | CZ 4C | 2.5723 | 0.65872 | 0.14256 | 0 | 0 | 0.0062445 | 0 | 0.16524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2885 | 2.605% | CZ 4C | 0 | 0 | 0 | 0.071808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071808 | 2.605% | CZ 4C | 26.9297 | 6.8961 | 1.4924 | 7.8486 | 0 | 0.065374 | 0 | 1.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 52.7444 | 2.605%
CZ 5A | 0.26547 | 0.067931 | 0.014828 | 0.14458 | 0 | 0.0047479 | 0 | 0.033318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.60759 | 21.41% | CZ 5A | 8.7793 | 2.2466 | 0.49037 | 14.6042 | 0 | 0.15702 | 0 | 1.1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 29.9165 | 21.41% | CZ 5A | 2.5723 | 0.65824 | 0.14368 | 0 | 0 | 0.046007 | 0 | 0.32285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4865 | 21.41% | CZ 5A | 0 | 0 | 0 | 0.14604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14604 | 21.41% | CZ 5A | 26.9297 | 6.8911 | 1.5042 | 15.9623 | 0 | 0.48164 | 0 | 3.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 62.9311 | 21.41%
CZ 5B | 0.26547 | 0.067898 | 0.014767 | 0.079609 | 0 | 0.0038116 | 0 | 0.027937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.5362 | 4.118% | CZ 5B | 8.7793 | 2.2455 | 0.48837 | 8.0413 | 0 | 0.12605 | 0 | 0.92391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.1415 | 4.118% | CZ 5B | 2.5723 | 0.65792 | 0.14309 | 0 | 0 | 0.036934 | 0 | 0.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4243 | 4.118% | CZ 5B | 0 | 0 | 0 | 0.080413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080413 | 4.118% | CZ 5B | 26.9297 | 6.8877 | 1.498 | 8.7891 | 0 | 0.38666 | 0 | 2.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 55.1075 | 4.118%
CZ 5C | 0.26547 | 0.067859 | 0.014861 | 0.086 | 0 | 9.9145e-05 | 0 | 0.019559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.53056 | 0% | CZ 5C | 8.7793 | 2.2442 | 0.49147 | 8.6869 | 0 | 0.0032789 | 0 | 0.64685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.3891 | 0% | CZ 5C | 2.5723 | 0.65754 | 0.144 | 0 | 0 | 0.0009607 | 0 | 0.18952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3077 | 0% | CZ 5C | 0 | 0 | 0 | 0.086869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086869 | 0% | CZ 5C | 26.9297 | 6.8838 | 1.5075 | 9.4948 | 0 | 0.010058 | 0 | 1.9841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 54.5923 | 0%
CZ 6A | 0.26547 | 0.067936 | 0.015147 | 0.17063 | 0 | 0.0012063 | 0 | 0.028113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.62522 | 2.787% | CZ 6A | 8.7793 | 2.2468 | 0.50094 | 17.2354 | 0 | 0.039893 | 0 | 0.92974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 32.2691 | 2.787% | CZ 6A | 2.5723 | 0.65829 | 0.14677 | 0 | 0 | 0.011688 | 0 | 0.27241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4049 | 2.787% | CZ 6A | 0 | 0 | 0 | 0.17235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17235 | 2.787% | CZ 6A | 26.9297 | 6.8917 | 1.5366 | 18.8382 | 0 | 0.12237 | 0 | 2.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 64.9527 | 2.787%
CZ 6B | 0.26547 | 0.067887 | 0.015191 | 0.12169 | 0 | 0.0007546 | 0 | 0.028361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.57607 | 0.2931% | CZ 6B | 8.7793 | 2.2451 | 0.50239 | 12.292 | 0 | 0.024956 | 0 | 0.93794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.3189 | 0.2931% | CZ 6B | 2.5723 | 0.65781 | 0.1472 | 0 | 0 | 0.007312 | 0 | 0.27481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4028 | 0.2931% | CZ 6B | 0 | 0 | 0 | 0.12292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12292 | 0.2931% | CZ 6B | 26.9297 | 6.8866 | 1.541 | 13.4352 | 0 | 0.076549 | 0 | 2.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 59.5284 | 0.2931%
CZ 7 | 0.26547 | 0.067887 | 0.015637 | 0.27582 | 0 | 0.00040209 | 0 | 0.038843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.74077 | 0.2579% | CZ 7 | 8.7793 | 2.2451 | 0.51715 | 27.8603 | 0 | 0.013298 | 0 | 1.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 43.2369 | 0.2579% | CZ 7 | 2.5723 | 0.65781 | 0.15152 | 0 | 0 | 0.0038962 | 0 | 0.37638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5053 | 0.2579% | CZ 7 | 0 | 0 | 0 | 0.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2786 | 0.2579% | CZ 7 | 26.9297 | 6.8866 | 1.5863 | 30.4513 | 0 | 0.040789 | 0 | 3.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 77.6173 | 0.2579%
CZ 8 | 0.26547 | 0.067474 | 0.016238 | 0.29331 | 0 | 7.7113e-05 | 0 | 0.024114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.74339 | 0.01321% | CZ 8 | 8.7793 | 2.2314 | 0.537 | 29.6268 | 0 | 0.0025502 | 0 | 0.79749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 44.5118 | 0.01321% | CZ 8 | 2.5723 | 0.65381 | 0.15734 | 0 | 0 | 0.00074721 | 0 | 0.23366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3613 | 0.01321% | CZ 8 | 0 | 0 | 0 | 0.29627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29627 | 0.01321% | CZ 8 | 26.9297 | 6.8447 | 1.6472 | 32.3821 | 0 | 0.0078225 | 0 | 2.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 78.04 | 0.01321%
Us Weighted | 0.26547 | 0.067996 | 0.01419 | 0.072587 | 0 | 0.021665 | 0 | 0.037948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.55657 | 100% | Us Weighted | 8.7793 | 2.2487 | 0.4693 | 7.332 | 0 | 0.7165 | 0 | 1.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.338 | 100% | Us Weighted | 2.5723 | 0.65887 | 0.1375 | 0 | 0 | 0.20993 | 0 | 0.36771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6897 | 100% | Us Weighted | 0 | 0 | 0 | 0.07332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07332 | 100% | Us Weighted | 26.9297 | 6.8978 | 1.4395 | 8.0139 | 0 | 2.1978 | 0 | 3.8495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 57.1104 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtus/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  |  | Natural Gas Rate, $/therm: | 0.99 | [43 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.26547 | 0.068124 | 0.012982 | 0.01019 | 0 | 0.067622 | 0 | 0.04906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.55016 | 2.089% | CZ 1A | 8.7793 | 2.2529 | 0.42935 | 1.0293 | 0 | 2.2364 | 0 | 1.6225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.8869 | 2.089% | CZ 1A | 2.5723 | 0.66011 | 0.1258 | 0 | 0 | 0.65525 | 0 | 0.47539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 5.2322 | 2.089% | CZ 1A | 0 | 0 | 0 | 0.010293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010293 | 2.089% | CZ 1A | 26.9297 | 6.9107 | 1.317 | 1.125 | 0 | 6.8598 | 0 | 4.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 55.9013 | 2.089%
CZ 1B | 0.26547 | 0.068063 | 0.012746 | 0.015439 | 0 | 0.19686 | 0 | 0.18603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.82132 | 0% | CZ 1B | 8.7793 | 2.2509 | 0.42152 | 1.5595 | 0 | 6.5105 | 0 | 6.1522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 28.2111 | 0% | CZ 1B | 2.5723 | 0.65952 | 0.1235 | 0 | 0 | 1.9076 | 0 | 1.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 7.8089 | 0% | CZ 1B | 0 | 0 | 0 | 0.015595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015595 | 0% | CZ 1B | 26.9297 | 6.9045 | 1.293 | 1.7045 | 0 | 19.9704 | 0 | 18.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 83.4556 | 0%
CZ 2A | 0.26547 | 0.068002 | 0.013539 | 0.035291 | 0 | 0.039328 | 0 | 0.039085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.53743 | 15.5% | CZ 2A | 8.7793 | 2.2489 | 0.44775 | 3.5647 | 0 | 1.3006 | 0 | 1.2926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.1711 | 15.5% | CZ 2A | 2.5723 | 0.65893 | 0.13119 | 0 | 0 | 0.38108 | 0 | 0.37873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.8656 | 15.5% | CZ 2A | 0 | 0 | 0 | 0.035647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035647 | 15.5% | CZ 2A | 26.9297 | 6.8984 | 1.3734 | 3.8962 | 0 | 3.9895 | 0 | 3.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 54.8344 | 15.5%
CZ 2B | 0.26547 | 0.067958 | 0.013208 | 0.016331 | 0 | 0.1041 | 0 | 0.12997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.67375 | 3.472% | CZ 2B | 8.7793 | 2.2475 | 0.43682 | 1.6496 | 0 | 3.4426 | 0 | 4.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.3914 | 3.472% | CZ 2B | 2.5723 | 0.65851 | 0.12799 | 0 | 0 | 1.0087 | 0 | 1.2594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 6.3703 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.016496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016496 | 3.472% | CZ 2B | 26.9297 | 6.8939 | 1.3399 | 1.803 | 0 | 10.5599 | 0 | 13.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 68.4935 | 3.472%
CZ 3A | 0.26547 | 0.068046 | 0.013963 | 0.076509 | 0 | 0.027314 | 0 | 0.03692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.56494 | 17.75% | CZ 3A | 8.7793 | 2.2504 | 0.46177 | 7.7282 | 0 | 0.90333 | 0 | 1.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.8812 | 17.75% | CZ 3A | 2.5723 | 0.65936 | 0.1353 | 0 | 0 | 0.26467 | 0 | 0.35775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7328 | 17.75% | CZ 3A | 0 | 0 | 0 | 0.077282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077282 | 17.75% | CZ 3A | 26.9297 | 6.9028 | 1.4164 | 8.447 | 0 | 2.7709 | 0 | 3.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 57.9944 | 17.75%
CZ 3B | 0.26547 | 0.068052 | 0.013814 | 0.038419 | 0 | 0.023685 | 0 | 0.046967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.53312 | 13.75% | CZ 3B | 8.7793 | 2.2506 | 0.45685 | 3.8807 | 0 | 0.78328 | 0 | 1.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.2411 | 13.75% | CZ 3B | 2.5723 | 0.65941 | 0.13386 | 0 | 0 | 0.2295 | 0 | 0.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.7936 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.038807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038807 | 13.75% | CZ 3B | 26.9297 | 6.9034 | 1.4014 | 4.2416 | 0 | 2.4026 | 0 | 4.7645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 54.4254 | 13.75%
CZ 3C | 0.26547 | 0.067953 | 0.014459 | 0.056917 | 0 | 0.00012669 | 0 | 0.012156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.49379 | 0.9199% | CZ 3C | 8.7793 | 2.2473 | 0.47817 | 5.7492 | 0 | 0.0041897 | 0 | 0.40203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.1973 | 0.9199% | CZ 3C | 2.5723 | 0.65845 | 0.1401 | 0 | 0 | 0.0012276 | 0 | 0.11779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2333 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.057492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057492 | 0.9199% | CZ 3C | 26.9297 | 6.8933 | 1.4667 | 6.2839 | 0 | 0.012851 | 0 | 1.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 50.6019 | 0.9199%
CZ 4A | 0.26547 | 0.068013 | 0.014475 | 0.1212 | 0 | 0.009259 | 0 | 0.025376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.58051 | 14.63% | CZ 4A | 8.7793 | 2.2493 | 0.47871 | 12.2429 | 0 | 0.30621 | 0 | 0.83921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.4327 | 14.63% | CZ 4A | 2.5723 | 0.65904 | 0.14026 | 0 | 0 | 0.089719 | 0 | 0.24589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4506 | 14.63% | CZ 4A | 0 | 0 | 0 | 0.12243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12243 | 14.63% | CZ 4A | 26.9297 | 6.8995 | 1.4684 | 13.3814 | 0 | 0.93926 | 0 | 2.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 59.9747 | 14.63%
CZ 4B | 0.26547 | 0.067997 | 0.014398 | 0.075677 | 0 | 0.0094849 | 0 | 0.033153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.54289 | 0.4058% | CZ 4B | 8.7793 | 2.2488 | 0.47616 | 7.6441 | 0 | 0.31368 | 0 | 1.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.0956 | 0.4058% | CZ 4B | 2.5723 | 0.65888 | 0.13951 | 0 | 0 | 0.091907 | 0 | 0.32125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5272 | 0.4058% | CZ 4B | 0 | 0 | 0 | 0.076441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076441 | 0.4058% | CZ 4B | 26.9297 | 6.8978 | 1.4606 | 8.355 | 0 | 0.96217 | 0 | 3.3631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 55.7506 | 0.4058%
CZ 4C | 0.26547 | 0.06798 | 0.014712 | 0.088818 | 0 | 0.00080968 | 0 | 0.017058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.53156 | 2.605% | CZ 4C | 8.7793 | 2.2482 | 0.48655 | 8.9715 | 0 | 0.026777 | 0 | 0.56415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.6137 | 2.605% | CZ 4C | 2.5723 | 0.65872 | 0.14256 | 0 | 0 | 0.0078457 | 0 | 0.16529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.2901 | 2.605% | CZ 4C | 0 | 0 | 0 | 0.089715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089715 | 2.605% | CZ 4C | 26.9297 | 6.8961 | 1.4924 | 9.8059 | 0 | 0.082137 | 0 | 1.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 54.719 | 2.605%
CZ 5A | 0.26547 | 0.067931 | 0.014828 | 0.17276 | 0 | 0.0056072 | 0 | 0.033533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.63684 | 21.41% | CZ 5A | 8.7793 | 2.2466 | 0.49037 | 17.4503 | 0 | 0.18544 | 0 | 1.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 32.7981 | 21.41% | CZ 5A | 2.5723 | 0.65824 | 0.14368 | 0 | 0 | 0.054333 | 0 | 0.32493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4969 | 21.41% | CZ 5A | 0 | 0 | 0 | 0.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1745 | 21.41% | CZ 5A | 26.9297 | 6.8911 | 1.5042 | 19.0731 | 0 | 0.56881 | 0 | 3.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 66.1508 | 21.41%
CZ 5B | 0.26547 | 0.067898 | 0.014767 | 0.10709 | 0 | 0.004445 | 0 | 0.028422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.56481 | 4.118% | CZ 5B | 8.7793 | 2.2455 | 0.48837 | 10.8176 | 0 | 0.147 | 0 | 0.93994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.9549 | 4.118% | CZ 5B | 2.5723 | 0.65792 | 0.14309 | 0 | 0 | 0.043071 | 0 | 0.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4352 | 4.118% | CZ 5B | 0 | 0 | 0 | 0.10818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10818 | 4.118% | CZ 5B | 26.9297 | 6.8877 | 1.498 | 11.8237 | 0 | 0.45091 | 0 | 2.8832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 58.2555 | 4.118%
CZ 5C | 0.26547 | 0.067859 | 0.014861 | 0.10499 | 0 | 0.00011567 | 0 | 0.019565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.54957 | 0% | CZ 5C | 8.7793 | 2.2442 | 0.49147 | 10.6049 | 0 | 0.0038253 | 0 | 0.64703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.3079 | 0% | CZ 5C | 2.5723 | 0.65754 | 0.144 | 0 | 0 | 0.0011208 | 0 | 0.18958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3079 | 0% | CZ 5C | 0 | 0 | 0 | 0.10605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10605 | 0% | CZ 5C | 26.9297 | 6.8838 | 1.5075 | 11.5912 | 0 | 0.011734 | 0 | 1.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 56.6909 | 0%
CZ 6A | 0.26547 | 0.067936 | 0.015147 | 0.19702 | 0 | 0.0015312 | 0 | 0.028482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.6523 | 2.787% | CZ 6A | 8.7793 | 2.2468 | 0.50094 | 19.9012 | 0 | 0.05064 | 0 | 0.94194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 34.9579 | 2.787% | CZ 6A | 2.5723 | 0.65829 | 0.14677 | 0 | 0 | 0.014837 | 0 | 0.27599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4116 | 2.787% | CZ 6A | 0 | 0 | 0 | 0.19901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19901 | 2.787% | CZ 6A | 26.9297 | 6.8917 | 1.5366 | 21.752 | 0 | 0.15533 | 0 | 2.8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 67.9368 | 2.787%
CZ 6B | 0.26547 | 0.067887 | 0.015191 | 0.15891 | 0 | 0.00098594 | 0 | 0.028796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.61396 | 0.2931% | CZ 6B | 8.7793 | 2.2451 | 0.50239 | 16.0518 | 0 | 0.032606 | 0 | 0.95233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 31.1007 | 0.2931% | CZ 6B | 2.5723 | 0.65781 | 0.1472 | 0 | 0 | 0.0095536 | 0 | 0.27903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.4093 | 0.2931% | CZ 6B | 0 | 0 | 0 | 0.16052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16052 | 0.2931% | CZ 6B | 26.9297 | 6.8866 | 1.541 | 17.5446 | 0 | 0.10002 | 0 | 2.9212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 63.7054 | 0.2931%
CZ 7 | 0.26547 | 0.067887 | 0.015643 | 0.30224 | 0 | 0.00046818 | 0 | 0.038986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.76741 | 0.2579% | CZ 7 | 8.7793 | 2.2451 | 0.51733 | 30.5294 | 0 | 0.015484 | 0 | 1.2893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 45.9131 | 0.2579% | CZ 7 | 2.5723 | 0.65781 | 0.15158 | 0 | 0 | 0.0045366 | 0 | 0.37777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.5074 | 0.2579% | CZ 7 | 0 | 0 | 0 | 0.30529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30529 | 0.2579% | CZ 7 | 26.9297 | 6.8866 | 1.5869 | 33.3686 | 0 | 0.047494 | 0 | 3.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 80.5564 | 0.2579%
CZ 8 | 0.26547 | 0.067474 | 0.016243 | 0.3189 | 0 | 8.8129e-05 | 0 | 0.024191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.76908 | 0.01321% | CZ 8 | 8.7793 | 2.2314 | 0.53719 | 32.2125 | 0 | 0.0029145 | 0 | 0.80004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 47.1005 | 0.01321% | CZ 8 | 2.5723 | 0.65381 | 0.15739 | 0 | 0 | 0.00085395 | 0 | 0.23441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.3622 | 0.01321% | CZ 8 | 0 | 0 | 0 | 0.32212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32212 | 0.01321% | CZ 8 | 26.9297 | 6.8447 | 1.6478 | 35.2082 | 0 | 0.00894 | 0 | 2.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 80.8757 | 0.01321%
Us Weighted | 0.26547 | 0.067996 | 0.01419 | 0.094171 | 0 | 0.022072 | 0 | 0.038342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076716 | 0.57895 | 100% | Us Weighted | 8.7793 | 2.2487 | 0.4693 | 9.5122 | 0 | 0.72994 | 0 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.5447 | 100% | Us Weighted | 2.5723 | 0.65887 | 0.1375 | 0 | 0 | 0.21387 | 0 | 0.37152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74337 | 4.6975 | 100% | Us Weighted | 0 | 0 | 0 | 0.095122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095122 | 100% | Us Weighted | 26.9297 | 6.8978 | 1.4395 | 10.3969 | 0 | 2.239 | 0 | 3.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7823 | 59.5746 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Warehouse |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 52045 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 52045 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 0.10616 | 0.022616 | 0.00042412 | 0.0099702 | 0 | 0.034767 | 0 | 0.034497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.20997 | 2.089% | CZ 1A | 3.5109 | 0.74795 | 0.014026 | 1.0071 | 0 | 1.1498 | 0 | 1.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 7.6213 | 2.089% | CZ 1A | 1.0287 | 0.21915 | 0.0041097 | 0 | 0 | 0.33688 | 0 | 0.33427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.9379 | 2.089% | CZ 1A | 0 | 0 | 0 | 0.010071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010071 | 2.089% | CZ 1A | 10.7694 | 2.2942 | 0.043024 | 1.1008 | 0 | 3.5268 | 0 | 3.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 21.3891 | 2.089%
CZ 1B | 0.10208 | 0.0226 | 0.0004076 | 0.011921 | 0 | 0.066868 | 0 | 0.11416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.31956 | 0% | CZ 1B | 3.3758 | 0.7474 | 0.01348 | 1.2041 | 0 | 2.2114 | 0 | 3.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.3783 | 0% | CZ 1B | 0.98909 | 0.21899 | 0.0039495 | 0 | 0 | 0.64794 | 0 | 1.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 2.981 | 0% | CZ 1B | 0 | 0 | 0 | 0.012041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012041 | 0% | CZ 1B | 10.3548 | 2.2926 | 0.041348 | 1.3161 | 0 | 6.7833 | 0 | 11.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 32.5242 | 0%
CZ 2A | 0.10181 | 0.022589 | 0.00044064 | 0.019712 | 0 | 0.018138 | 0 | 0.018689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.18291 | 15.5% | CZ 2A | 3.367 | 0.74703 | 0.014573 | 1.9911 | 0 | 0.59985 | 0 | 0.61807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 7.3883 | 15.5% | CZ 2A | 0.98653 | 0.21888 | 0.0042698 | 0 | 0 | 0.17575 | 0 | 0.18109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.5814 | 15.5% | CZ 2A | 0 | 0 | 0 | 0.019911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019911 | 15.5% | CZ 2A | 10.328 | 2.2914 | 0.0447 | 2.1762 | 0 | 1.84 | 0 | 1.8958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 18.7315 | 15.5%
CZ 2B | 0.094485 | 0.022578 | 0.00041861 | 0.0054521 | 0 | 0.031468 | 0 | 0.065474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.22141 | 3.472% | CZ 2B | 3.1248 | 0.74667 | 0.013844 | 0.55072 | 0 | 1.0407 | 0 | 2.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 7.6926 | 3.472% | CZ 2B | 0.91555 | 0.21877 | 0.0040563 | 0 | 0 | 0.30491 | 0 | 0.63443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 2.0926 | 3.472% | CZ 2B | 0 | 0 | 0 | 0.0055072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055072 | 3.472% | CZ 2B | 9.5848 | 2.2903 | 0.042465 | 0.60193 | 0 | 3.1922 | 0 | 6.6419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 22.509 | 3.472%
CZ 3A | 0.098247 | 0.022544 | 0.00045166 | 0.032639 | 0 | 0.013522 | 0 | 0.017813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.18675 | 17.75% | CZ 3A | 3.2492 | 0.74558 | 0.014937 | 3.2968 | 0 | 0.4472 | 0 | 0.5891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 8.3935 | 17.75% | CZ 3A | 0.952 | 0.21845 | 0.0043765 | 0 | 0 | 0.13103 | 0 | 0.17261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.4933 | 17.75% | CZ 3A | 0 | 0 | 0 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032968 | 17.75% | CZ 3A | 9.9665 | 2.287 | 0.045818 | 3.6034 | 0 | 1.3717 | 0 | 1.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 19.2368 | 17.75%
CZ 3B | 0.097035 | 0.0226 | 0.00044064 | 0.012213 | 0 | 0.0099806 | 0 | 0.021906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.16571 | 13.75% | CZ 3B | 3.2091 | 0.7474 | 0.014573 | 1.2336 | 0 | 0.33007 | 0 | 0.72445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 6.3099 | 13.75% | CZ 3B | 0.94026 | 0.21899 | 0.0042698 | 0 | 0 | 0.09671 | 0 | 0.21226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.4873 | 13.75% | CZ 3B | 0 | 0 | 0 | 0.012336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012336 | 13.75% | CZ 3B | 9.8435 | 2.2926 | 0.0447 | 1.3484 | 0 | 1.0125 | 0 | 2.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 16.9191 | 13.75%
CZ 3C | 0.097063 | 0.022533 | 0.00047369 | 0.011782 | 0 | 8.8129e-05 | 0 | 0.0012063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.13468 | 0.9199% | CZ 3C | 3.21 | 0.74521 | 0.015666 | 1.1901 | 0 | 0.0029145 | 0 | 0.039893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 5.2545 | 0.9199% | CZ 3C | 0.94052 | 0.21835 | 0.00459 | 0 | 0 | 0.00085395 | 0 | 0.011688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.1908 | 0.9199% | CZ 3C | 0 | 0 | 0 | 0.011901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011901 | 0.9199% | CZ 3C | 9.8463 | 2.2859 | 0.048053 | 1.3008 | 0 | 0.00894 | 0 | 0.12237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 13.7677 | 0.9199%
CZ 4A | 0.095212 | 0.022517 | 0.00046268 | 0.047855 | 0 | 0.0056182 | 0 | 0.013247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.18644 | 14.63% | CZ 4A | 3.1488 | 0.74467 | 0.015301 | 4.8339 | 0 | 0.1858 | 0 | 0.43809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.4172 | 14.63% | CZ 4A | 0.92259 | 0.21819 | 0.0044833 | 0 | 0 | 0.05444 | 0 | 0.12836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.3429 | 14.63% | CZ 4A | 0 | 0 | 0 | 0.048339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048339 | 14.63% | CZ 4A | 9.6586 | 2.2842 | 0.046935 | 5.2834 | 0 | 0.56993 | 0 | 1.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 19.3422 | 14.63%
CZ 4B | 0.092959 | 0.022555 | 0.00045717 | 0.027621 | 0 | 0.0056402 | 0 | 0.012498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.16326 | 0.4058% | CZ 4B | 3.0743 | 0.74594 | 0.015119 | 2.79 | 0 | 0.18653 | 0 | 0.41332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 7.2759 | 0.4058% | CZ 4B | 0.90076 | 0.21856 | 0.0044299 | 0 | 0 | 0.054653 | 0 | 0.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.3143 | 0.4058% | CZ 4B | 0 | 0 | 0 | 0.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0279 | 0.4058% | CZ 4B | 9.4301 | 2.2881 | 0.046376 | 3.0495 | 0 | 0.57216 | 0 | 1.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 16.8093 | 0.4058%
CZ 4C | 0.091445 | 0.022451 | 0.00047369 | 0.026871 | 0 | 0.00055081 | 0 | 0.0035031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.14683 | 2.605% | CZ 4C | 3.0242 | 0.74248 | 0.015666 | 2.7142 | 0 | 0.018216 | 0 | 0.11585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 6.6813 | 2.605% | CZ 4C | 0.88608 | 0.21754 | 0.00459 | 0 | 0 | 0.0053372 | 0 | 0.033945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.1623 | 2.605% | CZ 4C | 0 | 0 | 0 | 0.027142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027142 | 2.605% | CZ 4C | 9.2764 | 2.2775 | 0.048053 | 2.9667 | 0 | 0.055875 | 0 | 0.35537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 15.1352 | 2.605%
CZ 5A | 0.096259 | 0.022346 | 0.00046268 | 0.052298 | 0 | 0.00374 | 0 | 0.018876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.19551 | 21.41% | CZ 5A | 3.1834 | 0.73902 | 0.015301 | 5.2826 | 0 | 0.12369 | 0 | 0.62426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.0189 | 21.41% | CZ 5A | 0.93273 | 0.21653 | 0.0044833 | 0 | 0 | 0.03624 | 0 | 0.18291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.3877 | 21.41% | CZ 5A | 0 | 0 | 0 | 0.052826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052826 | 21.41% | CZ 5A | 9.7648 | 2.2669 | 0.046935 | 5.7739 | 0 | 0.37939 | 0 | 1.9148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 20.302 | 21.41%
CZ 5B | 0.088024 | 0.022566 | 0.00046268 | 0.036809 | 0 | 0.0028807 | 0 | 0.015318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.16759 | 4.118% | CZ 5B | 2.9111 | 0.74631 | 0.015301 | 3.7181 | 0 | 0.095269 | 0 | 0.50658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 8.0432 | 4.118% | CZ 5B | 0.85294 | 0.21867 | 0.0044833 | 0 | 0 | 0.027914 | 0 | 0.14843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.2673 | 4.118% | CZ 5B | 0 | 0 | 0 | 0.037181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037181 | 4.118% | CZ 5B | 8.9294 | 2.2892 | 0.046935 | 4.0638 | 0 | 0.29223 | 0 | 1.5539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 17.3309 | 4.118%
CZ 5C | 0.083541 | 0.022313 | 0.00047369 | 0.031804 | 0 | 3.8556e-05 | 0 | 0.0041971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.1439 | 0% | CZ 5C | 2.7628 | 0.73793 | 0.015666 | 3.2125 | 0 | 0.0012751 | 0 | 0.13881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 6.9196 | 0% | CZ 5C | 0.8095 | 0.21621 | 0.00459 | 0 | 0 | 0.0003736 | 0 | 0.04067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.0862 | 0% | CZ 5C | 0 | 0 | 0 | 0.032125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032125 | 0% | CZ 5C | 8.4746 | 2.2635 | 0.048053 | 3.5113 | 0 | 0.0039113 | 0 | 0.42577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 14.8824 | 0%
CZ 6A | 0.047937 | 0.022302 | 0.00047369 | 0.079149 | 0 | 0.001052 | 0 | 0.017091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.16954 | 2.787% | CZ 6A | 1.5853 | 0.73756 | 0.015666 | 7.9948 | 0 | 0.034792 | 0 | 0.56524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.9841 | 2.787% | CZ 6A | 0.4645 | 0.2161 | 0.00459 | 0 | 0 | 0.010194 | 0 | 0.16561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 0.87584 | 2.787% | CZ 6A | 0 | 0 | 0 | 0.079948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079948 | 2.787% | CZ 6A | 4.8628 | 2.2624 | 0.048053 | 8.7384 | 0 | 0.10672 | 0 | 1.7338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 17.9075 | 2.787%
CZ 6B | 0.046692 | 0.022473 | 0.00046818 | 0.074887 | 0 | 0.00068851 | 0 | 0.010708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.15745 | 0.2931% | CZ 6B | 1.5442 | 0.74321 | 0.015484 | 7.5643 | 0 | 0.02277 | 0 | 0.35412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.2947 | 0.2931% | CZ 6B | 0.45244 | 0.21776 | 0.0045366 | 0 | 0 | 0.0066715 | 0 | 0.10376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 0.79999 | 0.2931% | CZ 6B | 0 | 0 | 0 | 0.075643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075643 | 0.2931% | CZ 6B | 4.7365 | 2.2797 | 0.047494 | 8.2678 | 0 | 0.069844 | 0 | 1.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 16.643 | 0.2931%
CZ 7 | 0.047992 | 0.022357 | 0.0004792 | 0.10313 | 0 | 0.00031947 | 0 | 0.022522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.19833 | 0.2579% | CZ 7 | 1.5872 | 0.73938 | 0.015848 | 10.417 | 0 | 0.010565 | 0 | 0.74485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 13.5654 | 0.2579% | CZ 7 | 0.46503 | 0.21664 | 0.0046434 | 0 | 0 | 0.0030956 | 0 | 0.21824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 0.92248 | 0.2579% | CZ 7 | 0 | 0 | 0 | 0.10417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10417 | 0.2579% | CZ 7 | 4.8684 | 2.268 | 0.048611 | 11.3858 | 0 | 0.032408 | 0 | 2.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 21.0432 | 0.2579%
CZ 8 | 0.045105 | 0.021707 | 0.00048471 | 0.12015 | 0 | -3.3048e-05 | 0 | 0.0066482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.1956 | 0.01321% | CZ 8 | 1.4917 | 0.71789 | 0.01603 | 12.1367 | 0 | -0.001093 | 0 | 0.21987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 14.6317 | 0.01321% | CZ 8 | 0.43706 | 0.21034 | 0.0046967 | 0 | 0 | -0.00032023 | 0 | 0.06442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 0.73104 | 0.01321% | CZ 8 | 0 | 0 | 0 | 0.12137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12137 | 0.01321% | CZ 8 | 4.5756 | 2.202 | 0.04917 | 13.2654 | 0 | -0.0033525 | 0 | 0.67441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 20.9186 | 0.01321%
Us Weighted | 0.095477 | 0.022506 | 0.00045268 | 0.034268 | 0 | 0.010214 | 0 | 0.019394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015312 | 0.18384 | 100% | Us Weighted | 3.1576 | 0.7443 | 0.014971 | 3.4615 | 0 | 0.33778 | 0 | 0.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 8.4081 | 100% | Us Weighted | 0.92516 | 0.21808 | 0.0043864 | 0 | 0 | 0.098968 | 0 | 0.18793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014837 | 1.4494 | 100% | Us Weighted | 0 | 0 | 0 | 0.034615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034615 | 100% | Us Weighted | 9.6855 | 2.2831 | 0.045921 | 3.7834 | 0 | 1.0361 | 0 | 1.9674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15533 | 18.9567 | 100%
Building Type: | Warehouse |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Energy Use Index Site kBtus/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2013 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2013 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1032 |  |  |  | Natural Gas Rate, $/therm: | 0.99 |  |  |  |  | Prototype Floor Area: | 52045 | [17 empty] | Prototype Floor Area: | 52045 | [17 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight | 2004-2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | Data.Ctr | Equip | Total | Weight
CZ 1A | 39.99% | 33.2% | 3.267% | 97.84% | 0% | 51.41% | 0% | 70.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 38.16% | 2.089% | CZ 1A | 39.99% | 33.2% | 3.267% | 97.84% | 0% | 51.41% | 0% | 70.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 40.35% | 2.089% | CZ 1A | 39.99% | 33.2% | 3.267% | 0% | 0% | 51.41% | 0% | 70.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 37.04% | 2.089% | CZ 1A | 0% | 0% | 0% | 97.84% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.84% | 2.089% | CZ 1A | 39.99% | 33.2% | 3.267% | 97.84% | 0% | 51.41% | 0% | 70.32% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 38.26% | 2.089%
CZ 1B | 38.45% | 33.2% | 3.198% | 77.22% | 0% | 33.97% | 0% | 61.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 38.91% | 0% | CZ 1B | 38.45% | 33.2% | 3.198% | 77.22% | 0% | 33.97% | 0% | 61.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 40.33% | 0% | CZ 1B | 38.45% | 33.2% | 3.198% | 0% | 0% | 33.97% | 0% | 61.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 38.17% | 0% | CZ 1B | 0% | 0% | 0% | 77.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 77.22% | 0% | CZ 1B | 38.45% | 33.2% | 3.198% | 77.22% | 0% | 33.97% | 0% | 61.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 38.97% | 0%
CZ 2A | 38.35% | 33.22% | 3.255% | 55.85% | 0% | 46.12% | 0% | 47.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 34.03% | 15.5% | CZ 2A | 38.35% | 33.22% | 3.255% | 55.85% | 0% | 46.12% | 0% | 47.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 36.63% | 15.5% | CZ 2A | 38.35% | 33.22% | 3.255% | 0% | 0% | 46.12% | 0% | 47.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.5% | 15.5% | CZ 2A | 0% | 0% | 0% | 55.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 55.85% | 15.5% | CZ 2A | 38.35% | 33.22% | 3.255% | 55.85% | 0% | 46.12% | 0% | 47.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 34.16% | 15.5%
CZ 2B | 35.59% | 33.22% | 3.169% | 33.38% | 0% | 30.23% | 0% | 50.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.86% | 3.472% | CZ 2B | 35.59% | 33.22% | 3.169% | 33.38% | 0% | 30.23% | 0% | 50.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.89% | 3.472% | CZ 2B | 35.59% | 33.22% | 3.169% | 0% | 0% | 30.23% | 0% | 50.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.85% | 3.472% | CZ 2B | 0% | 0% | 0% | 33.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.38% | 3.472% | CZ 2B | 35.59% | 33.22% | 3.169% | 33.38% | 0% | 30.23% | 0% | 50.38% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.86% | 3.472%
CZ 3A | 37.01% | 33.13% | 3.235% | 42.66% | 0% | 49.51% | 0% | 48.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 33.06% | 17.75% | CZ 3A | 37.01% | 33.13% | 3.235% | 42.66% | 0% | 49.51% | 0% | 48.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 35.15% | 17.75% | CZ 3A | 37.01% | 33.13% | 3.235% | 0% | 0% | 49.51% | 0% | 48.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.55% | 17.75% | CZ 3A | 0% | 0% | 0% | 42.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.66% | 17.75% | CZ 3A | 37.01% | 33.13% | 3.235% | 42.66% | 0% | 49.51% | 0% | 48.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 33.17% | 17.75%
CZ 3B | 36.55% | 33.21% | 3.19% | 31.79% | 0% | 42.14% | 0% | 46.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.08% | 13.75% | CZ 3B | 36.55% | 33.21% | 3.19% | 31.79% | 0% | 42.14% | 0% | 46.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.17% | 13.75% | CZ 3B | 36.55% | 33.21% | 3.19% | 0% | 0% | 42.14% | 0% | 46.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.03% | 13.75% | CZ 3B | 0% | 0% | 0% | 31.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.79% | 13.75% | CZ 3B | 36.55% | 33.21% | 3.19% | 31.79% | 0% | 42.14% | 0% | 46.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.09% | 13.75%
CZ 3C | 36.56% | 33.16% | 3.276% | 20.7% | 0% | 69.57% | 0% | 9.923% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.27% | 0.9199% | CZ 3C | 36.56% | 33.16% | 3.276% | 20.7% | 0% | 69.57% | 0% | 9.923% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.02% | 0.9199% | CZ 3C | 36.56% | 33.16% | 3.276% | 0% | 0% | 69.57% | 0% | 9.923% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 28.13% | 0.9199% | CZ 3C | 0% | 0% | 0% | 20.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20.7% | 0.9199% | CZ 3C | 36.56% | 33.16% | 3.276% | 20.7% | 0% | 69.57% | 0% | 9.923% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.21% | 0.9199%
CZ 4A | 35.87% | 33.11% | 3.196% | 39.48% | 0% | 60.68% | 0% | 52.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.12% | 14.63% | CZ 4A | 35.87% | 33.11% | 3.196% | 39.48% | 0% | 60.68% | 0% | 52.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 34.33% | 14.63% | CZ 4A | 35.87% | 33.11% | 3.196% | 0% | 0% | 60.68% | 0% | 52.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.17% | 14.63% | CZ 4A | 0% | 0% | 0% | 39.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.48% | 14.63% | CZ 4A | 35.87% | 33.11% | 3.196% | 39.48% | 0% | 60.68% | 0% | 52.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.25% | 14.63%
CZ 4B | 35.02% | 33.17% | 3.175% | 36.5% | 0% | 59.47% | 0% | 37.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.07% | 0.4058% | CZ 4B | 35.02% | 33.17% | 3.175% | 36.5% | 0% | 59.47% | 0% | 37.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.5% | 0.4058% | CZ 4B | 35.02% | 33.17% | 3.175% | 0% | 0% | 59.47% | 0% | 37.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 29.03% | 0.4058% | CZ 4B | 0% | 0% | 0% | 36.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.5% | 0.4058% | CZ 4B | 35.02% | 33.17% | 3.175% | 36.5% | 0% | 59.47% | 0% | 37.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.15% | 0.4058%
CZ 4C | 34.45% | 33.03% | 3.22% | 30.25% | 0% | 68.03% | 0% | 20.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.62% | 2.605% | CZ 4C | 34.45% | 33.03% | 3.22% | 30.25% | 0% | 68.03% | 0% | 20.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 28.29% | 2.605% | CZ 4C | 34.45% | 33.03% | 3.22% | 0% | 0% | 68.03% | 0% | 20.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.09% | 2.605% | CZ 4C | 0% | 0% | 0% | 30.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.25% | 2.605% | CZ 4C | 34.45% | 33.03% | 3.22% | 30.25% | 0% | 68.03% | 0% | 20.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.66% | 2.605%
CZ 5A | 36.26% | 32.9% | 3.12% | 30.27% | 0% | 66.7% | 0% | 56.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.7% | 21.41% | CZ 5A | 36.26% | 32.9% | 3.12% | 30.27% | 0% | 66.7% | 0% | 56.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.55% | 21.41% | CZ 5A | 36.26% | 32.9% | 3.12% | 0% | 0% | 66.7% | 0% | 56.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.86% | 21.41% | CZ 5A | 0% | 0% | 0% | 30.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.27% | 21.41% | CZ 5A | 36.26% | 32.9% | 3.12% | 30.27% | 0% | 66.7% | 0% | 56.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.69% | 21.41%
CZ 5B | 33.16% | 33.24% | 3.133% | 34.37% | 0% | 64.81% | 0% | 53.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 29.67% | 4.118% | CZ 5B | 33.16% | 33.24% | 3.133% | 34.37% | 0% | 64.81% | 0% | 53.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.99% | 4.118% | CZ 5B | 33.16% | 33.24% | 3.133% | 0% | 0% | 64.81% | 0% | 53.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 28.57% | 4.118% | CZ 5B | 0% | 0% | 0% | 34.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.37% | 4.118% | CZ 5B | 33.16% | 33.24% | 3.133% | 34.37% | 0% | 64.81% | 0% | 53.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 29.75% | 4.118%
CZ 5C | 31.47% | 32.88% | 3.188% | 30.29% | 0% | 33.33% | 0% | 21.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.18% | 0% | CZ 5C | 31.47% | 32.88% | 3.188% | 30.29% | 0% | 33.33% | 0% | 21.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 27.34% | 0% | CZ 5C | 31.47% | 32.88% | 3.188% | 0% | 0% | 33.33% | 0% | 21.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.21% | 0% | CZ 5C | 0% | 0% | 0% | 30.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 30.29% | 0% | CZ 5C | 31.47% | 32.88% | 3.188% | 30.29% | 0% | 33.33% | 0% | 21.45% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.25% | 0%
CZ 6A | 18.06% | 32.83% | 3.127% | 40.17% | 0% | 68.71% | 0% | 60.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.99% | 2.787% | CZ 6A | 18.06% | 32.83% | 3.127% | 40.17% | 0% | 68.71% | 0% | 60.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.42% | 2.787% | CZ 6A | 18.06% | 32.83% | 3.127% | 0% | 0% | 68.71% | 0% | 60.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 19.85% | 2.787% | CZ 6A | 0% | 0% | 0% | 40.17% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.17% | 2.787% | CZ 6A | 18.06% | 32.83% | 3.127% | 40.17% | 0% | 68.71% | 0% | 60.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.36% | 2.787%
CZ 6B | 17.59% | 33.1% | 3.082% | 47.12% | 0% | 69.83% | 0% | 37.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.64% | 0.2931% | CZ 6B | 17.59% | 33.1% | 3.082% | 47.12% | 0% | 69.83% | 0% | 37.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 33.1% | 0.2931% | CZ 6B | 17.59% | 33.1% | 3.082% | 0% | 0% | 69.83% | 0% | 37.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 18.14% | 0.2931% | CZ 6B | 0% | 0% | 0% | 47.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 47.12% | 0.2931% | CZ 6B | 17.59% | 33.1% | 3.082% | 47.12% | 0% | 69.83% | 0% | 37.18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.12% | 0.2931%
CZ 7 | 18.08% | 32.93% | 3.063% | 34.12% | 0% | 68.24% | 0% | 57.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.84% | 0.2579% | CZ 7 | 18.08% | 32.93% | 3.063% | 34.12% | 0% | 68.24% | 0% | 57.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 29.55% | 0.2579% | CZ 7 | 18.08% | 32.93% | 3.063% | 0% | 0% | 68.24% | 0% | 57.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 20.47% | 0.2579% | CZ 7 | 0% | 0% | 0% | 34.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.12% | 0.2579% | CZ 7 | 18.08% | 32.93% | 3.063% | 34.12% | 0% | 68.24% | 0% | 57.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 26.12% | 0.2579%
CZ 8 | 16.99% | 32.17% | 2.984% | 37.68% | 0% | -37.5% | 0% | 27.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.43% | 0.01321% | CZ 8 | 16.99% | 32.17% | 2.984% | 37.68% | 0% | -37.5% | 0% | 27.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.06% | 0.01321% | CZ 8 | 16.99% | 32.17% | 2.984% | 0% | 0% | -37.5% | 0% | 27.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 16.76% | 0.01321% | CZ 8 | 0% | 0% | 0% | 37.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.68% | 0.01321% | CZ 8 | 16.99% | 32.17% | 2.984% | 37.68% | 0% | -37.5% | 0% | 27.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 25.87% | 0.01321%
Us Weighted | 35.97% | 33.1% | 3.19% | 36.39% | 0% | 46.27% | 0% | 50.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.75% | 100% | Us Weighted | 35.97% | 33.1% | 3.19% | 36.39% | 0% | 46.27% | 0% | 50.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 32.92% | 100% | Us Weighted | 35.97% | 33.1% | 3.19% | 0% | 0% | 46.27% | 0% | 50.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 30.85% | 100% | Us Weighted | 0% | 0% | 0% | 36.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 36.39% | 100% | Us Weighted | 35.97% | 33.1% | 3.19% | 36.39% | 0% | 46.27% | 0% | 50.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 31.82% | 100%