5MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.434; 2: 4
6MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.424; 2: 4
6MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.73; 2: 0
7MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 7 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.54; 2: 2
8MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 8 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.52; 2: 2
1PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | PS | 1: 0.51; 2: 2
1PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | PS
2PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 2 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt insulation | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | PS
3PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 3 | Above Ground Wall | Steel-framed | 0.084 |  | 0.084 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.7228 | 7.2721 | 0 | 12.9949 | 0.974 | 1.039 | 0 | 1 | 5.574 | 7.5557 | 0 | 12.9949 | PS
4PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
5PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
5PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
5PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
6PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
6PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
7PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 7 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
8PSAbove Ground Wall - Steel-framed2010 | 2010 | Primary School | 8 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
1SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SH
1SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SH
2SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 2 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
3SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 3 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
4SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
5SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
5SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
5SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
6SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
6SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
7SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 7 | Above Ground Wall | Steel-framed | 0.042 |  | 0.042 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
8SHAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel | 8 | Above Ground Wall | Steel-framed | 0.037 |  | 0.037 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
1SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SHNR
2SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 2 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt insulation | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SHNR
3SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 3 | Above Ground Wall | Steel-framed | 0.084 |  | 0.084 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.7228 | 7.2721 | 0 | 12.9949 | 0.974 | 1.039 | 0 | 1 | 5.574 | 7.5557 | 0 | 12.9949 | SHNR
4SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
5SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
6SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 6 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
7SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 7 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
8SHNRAbove Ground Wall - Steel-framed2010 | 2010 | Small Hotel - Non-res | 8 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
1SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 1 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 |  | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
1SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 1 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 |  | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
2SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 2 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
3SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 3 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
4SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 4 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
5SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.064 |  | 0.064 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt + Polyiso insulation | 5.0866 | 7.4601 | 0 | 12.5467 | 1.089 | 1.041 | 0 | 1 | 5.5394 | 7.7659 | 0 | 12.5467 | SO
5SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.064 |  | 0.064 |  | 4.6605 | 6.0105 | 0 | 10.671 | 1.089 | 1.041 | 0 | 1 | 5.0753 | 6.2569 | 0 | 10.671 | SO
5SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.064 |  | 0.064 |  | 4.6605 | 6.0105 | 0 | 10.671 | 1.089 | 1.041 | 0 | 1 | 5.0753 | 6.2569 | 0 | 10.671 | SO
6SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 6 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
6SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 6 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
7SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 7 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
8SOAbove Ground Wall - Wood-framed2010 | 2010 | Small Office | 8 | Above Ground Wall | Wood-framed | 0.036 |  | 0.036 |  | 7.4129 | 8.5125 | 0 | 15.9254 | 1.089 | 1.041 | 0 | 1 | 8.0727 | 8.8615 | 0 | 15.9254 | SO
1SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | SR
1SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | SR
2SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 2 | Above Ground Wall | Mass | 0.151 |  | 0.151 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 5.8312 | 8.4749 | 0.63208 | 14.9382 | 1.047 | 1.046 | 0 | 1 | 6.1052 | 8.8648 | 0 | 14.9382 | SR
3SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 3 | Above Ground Wall | Mass | 0.123 |  | 0.123 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.0047 | 8.4749 | 0.63208 | 15.1117 | 1.047 | 1.046 | 0 | 1 | 6.2869 | 8.8648 | 0 | 15.1117 | SR
4SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 4 | Above Ground Wall | Mass | 0.104 |  | 0.104 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.1782 | 8.4749 | 0.63208 | 15.2853 | 1.047 | 1.046 | 0 | 1 | 6.4686 | 8.8648 | 0 | 15.2853 | SR
5SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.090 |  | 0.090 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
5SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
5SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
6SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | SR
6SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | SR
7SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 7 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | SR
8SRAbove Ground Wall - Mass2010 | 2010 | Stand-alone Retail | 8 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | SR
1LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | LO
1LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | LO
2LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 2 | Above Ground Wall | Mass | 0.151 |  | 0.151 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 5.8312 | 8.4749 | 0.63208 | 14.9382 | 1.047 | 1.046 | 0 | 1 | 6.1052 | 8.8648 | 0 | 14.9382 | LO
3LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 3 | Above Ground Wall | Mass | 0.123 |  | 0.123 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.0047 | 8.4749 | 0.63208 | 15.1117 | 1.047 | 1.046 | 0 | 1 | 6.2869 | 8.8648 | 0 | 15.1117 | LO
4LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 4 | Above Ground Wall | Mass | 0.104 |  | 0.104 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.1782 | 8.4749 | 0.63208 | 15.2853 | 1.047 | 1.046 | 0 | 1 | 6.4686 | 8.8648 | 0 | 15.2853 | LO
5LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 5 | Above Ground Wall | Mass | 0.090 |  | 0.090 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO
5LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO
5LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO
6LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | LO
6LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | LO
7LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 7 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | LO
8LOAbove Ground Wall - Mass2013 | 2013 | Large Office | 8 | Above Ground Wall | Mass | 0.048 |  | 0.048 |  | 7.0459 | 8.4749 | 0.63208 | 16.1529 | 1.047 | 1.046 | 0 | 1 | 7.3771 | 8.8648 | 0 | 16.1529 | LO
1MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | MA
1MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | MA
2MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 2 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA
3MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 3 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA
4MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA
5MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | MA
5MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | MA
5MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | MA
6MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | MA
6MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | MA
7MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 7 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | MA
8MAAbove Ground Wall - Steel-framed2013 | 2013 | Mid-rise Apartment | 8 | Above Ground Wall | Steel-framed | 0.037 |  | 0.037 |  | 8.5624 | 7.3327 | 0 | 15.8951 | 0.974 | 1.039 | 0 | 1 | 8.3397 | 7.6187 | 0 | 15.8951 | MA
1PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | PS
1PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | PS
2PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 2 | Above Ground Wall | Steel-framed | 0.084 |  | 0.084 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.7228 | 7.2721 | 0 | 12.9949 | 0.974 | 1.039 | 0 | 1 | 5.574 | 7.5557 | 0 | 12.9949 | PS
3PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 3 | Above Ground Wall | Steel-framed | 0.077 |  | 0.077 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.8631 | 7.2721 | 0 | 13.1352 | 0.974 | 1.039 | 0 | 1 | 5.7107 | 7.5557 | 0 | 13.1352 | PS
4PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | PS
5PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | PS
5PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | PS
5PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | PS
6PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | PS
6PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | PS
7PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 7 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | PS
8PSAbove Ground Wall - Steel-framed2013 | 2013 | Primary School | 8 | Above Ground Wall | Steel-framed | 0.037 |  | 0.037 |  | 8.5624 | 7.3327 | 0 | 15.8951 | 0.974 | 1.039 | 0 | 1 | 8.3397 | 7.6187 | 0 | 15.8951 | PS
1SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SH
1SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SH
2SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 2 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
3SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 3 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
4SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SH
5SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | SH
5SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | SH
5SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 |  | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | SH
6SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | SH
6SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | SH
7SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 7 | Above Ground Wall | Steel-framed | 0.042 |  | 0.042 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | SH
8SHAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel | 8 | Above Ground Wall | Steel-framed | 0.037 |  | 0.037 |  | 8.5624 | 7.3327 | 0 | 15.8951 | 0.974 | 1.039 | 0 | 1 | 8.3397 | 7.6187 | 0 | 15.8951 | SH
1SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | SHNR
2SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 2 | Above Ground Wall | Steel-framed | 0.084 |  | 0.084 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.7228 | 7.2721 | 0 | 12.9949 | 0.974 | 1.039 | 0 | 1 | 5.574 | 7.5557 | 0 | 12.9949 | SHNR
3SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 3 | Above Ground Wall | Steel-framed | 0.077 |  | 0.077 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 5.8631 | 7.2721 | 0 | 13.1352 | 0.974 | 1.039 | 0 | 1 | 5.7107 | 7.5557 | 0 | 13.1352 | SHNR
4SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | SHNR
5SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 5 | Above Ground Wall | Steel-framed | 0.055 |  | 0.055 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.4213 | 7.3327 | 0 | 13.754 | 0.974 | 1.039 | 0 | 1 | 6.2543 | 7.6187 | 0 | 13.754 | SHNR
6SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 6 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | SHNR
7SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 7 | Above Ground Wall | Steel-framed | 0.049 |  | 0.049 |  | 7.0033 | 7.3327 | 0 | 14.336 | 0.974 | 1.039 | 0 | 1 | 6.8212 | 7.6187 | 0 | 14.336 | SHNR
8SHNRAbove Ground Wall - Steel-framed2013 | 2013 | Small Hotel - Non-res | 8 | Above Ground Wall | Steel-framed | 0.037 |  | 0.037 |  | 8.5624 | 7.3327 | 0 | 15.8951 | 0.974 | 1.039 | 0 | 1 | 8.3397 | 7.6187 | 0 | 15.8951 | SHNR
1SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 1 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 |  | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
1SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 1 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 |  | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
2SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 2 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
3SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 3 | Above Ground Wall | Wood-framed | 0.089 |  | 0.089 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 3.4964 | 5.4956 | 0 | 8.992 | 1.089 | 1.041 | 0 | 1 | 3.8076 | 5.7209 | 0 | 8.992 | SO
4SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 4 | Above Ground Wall | Wood-framed | 0.064 |  | 0.064 | 2 x 6 Nominal Wood Framing, Single Row Studs, Cavity Batt insulation | 4.6605 | 6.0105 | 0 | 10.671 | 1.089 | 1.041 | 0 | 1 | 5.0753 | 6.2569 | 0 | 10.671 | SO
5SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 | 2 x 4 Nominal Wood Framing, Single Row Studs, Cavity Batt + Polyiso insulation | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
5SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
5SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 5 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
6SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 6 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
6SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 6 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
7SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 7 | Above Ground Wall | Wood-framed | 0.051 |  | 0.051 |  | 5.4499 | 7.4903 | 0 | 12.9402 | 1.089 | 1.041 | 0 | 1 | 5.935 | 7.7974 | 0 | 12.9402 | SO
8SOAbove Ground Wall - Wood-framed2013 | 2013 | Small Office | 8 | Above Ground Wall | Wood-framed | 0.032 |  | 0.032 |  | 8.2018 | 8.5125 | 0 | 16.7142 | 1.089 | 1.041 | 0 | 1 | 8.9317 | 8.8615 | 0 | 16.7142 | SO
1SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | SR
1SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | SR
2SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 2 | Above Ground Wall | Mass | 0.151 |  | 0.151 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 5.8312 | 8.4749 | 0.63208 | 14.9382 | 1.047 | 1.046 | 0 | 1 | 6.1052 | 8.8648 | 0 | 14.9382 | SR
3SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 3 | Above Ground Wall | Mass | 0.123 |  | 0.123 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.0047 | 8.4749 | 0.63208 | 15.1117 | 1.047 | 1.046 | 0 | 1 | 6.2869 | 8.8648 | 0 | 15.1117 | SR
4SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 4 | Above Ground Wall | Mass | 0.104 |  | 0.104 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.1782 | 8.4749 | 0.63208 | 15.2853 | 1.047 | 1.046 | 0 | 1 | 6.4686 | 8.8648 | 0 | 15.2853 | SR
5SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.090 |  | 0.090 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
5SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
5SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | SR
6SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | SR
6SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | SR
7SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 7 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | SR
8SRAbove Ground Wall - Mass2013 | 2013 | Stand-alone Retail | 8 | Above Ground Wall | Mass | 0.048 |  | 0.048 |  | 7.0459 | 8.4749 | 0.63208 | 16.1529 | 1.047 | 1.046 | 0 | 1 | 7.3771 | 8.8648 | 0 | 16.1529 | SR
1LOBelow Grade Wall2010 | 2010 | Large Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
1LOBelow Grade Wall2010 | 2010 | Large Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
2LOBelow Grade Wall2010 | 2010 | Large Office | 2 | Below Grade Wall |  | 1.140 |  | 1.140 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill insulation | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
3LOBelow Grade Wall2010 | 2010 | Large Office | 3 | Below Grade Wall |  | 1.140 |  | 1.140 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill insulation | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
4LOBelow Grade Wall2010 | 2010 | Large Office | 4 | Below Grade Wall |  | 1.140 |  | 1.140 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill insulation | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
5LOBelow Grade Wall2010 | 2010 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill + XPS (interpolated) insulation | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
5LOBelow Grade Wall2010 | 2010 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
5LOBelow Grade Wall2010 | 2010 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
6LOBelow Grade Wall2010 | 2010 | Large Office | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
6LOBelow Grade Wall2010 | 2010 | Large Office | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
7LOBelow Grade Wall2010 | 2010 | Large Office | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
8LOBelow Grade Wall2010 | 2010 | Large Office | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
1MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | MA
1MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | MA
5MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
5MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
6MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
6MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
7MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
8MABelow Grade Wall2010 | 2010 | Mid-rise Apartment | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
1PSBelow Grade Wall2010 | 2010 | Primary School | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | PS
1PSBelow Grade Wall2010 | 2010 | Primary School | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | PS
5PSBelow Grade Wall2010 | 2010 | Primary School | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
5PSBelow Grade Wall2010 | 2010 | Primary School | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
6PSBelow Grade Wall2010 | 2010 | Primary School | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
6PSBelow Grade Wall2010 | 2010 | Primary School | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
7PSBelow Grade Wall2010 | 2010 | Primary School | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
8PSBelow Grade Wall2010 | 2010 | Primary School | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
1SHBelow Grade Wall2010 | 2010 | Small Hotel | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SH
1SHBelow Grade Wall2010 | 2010 | Small Hotel | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SH
5SHBelow Grade Wall2010 | 2010 | Small Hotel | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
5SHBelow Grade Wall2010 | 2010 | Small Hotel | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
6SHBelow Grade Wall2010 | 2010 | Small Hotel | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
6SHBelow Grade Wall2010 | 2010 | Small Hotel | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
7SHBelow Grade Wall2010 | 2010 | Small Hotel | 7 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
8SHBelow Grade Wall2010 | 2010 | Small Hotel | 8 | Below Grade Wall |  | 0.075 |  | 0.075 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
1SHNRBelow Grade Wall2010 | 2010 | Small Hotel - Non-res | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SHNR
6SHNRBelow Grade Wall2010 | 2010 | Small Hotel - Non-res | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SHNR
7SHNRBelow Grade Wall2010 | 2010 | Small Hotel - Non-res | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SHNR
8SHNRBelow Grade Wall2010 | 2010 | Small Hotel - Non-res | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SHNR
1SOBelow Grade Wall2010 | 2010 | Small Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SO
1SOBelow Grade Wall2010 | 2010 | Small Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SO
5SOBelow Grade Wall2010 | 2010 | Small Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
5SOBelow Grade Wall2010 | 2010 | Small Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
6SOBelow Grade Wall2010 | 2010 | Small Office | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
6SOBelow Grade Wall2010 | 2010 | Small Office | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
7SOBelow Grade Wall2010 | 2010 | Small Office | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
8SOBelow Grade Wall2010 | 2010 | Small Office | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
1SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SR
1SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SR
5SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
5SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
6SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
6SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 6 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
7SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 7 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
8SRBelow Grade Wall2010 | 2010 | Stand-alone Retail | 8 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
1LOBelow Grade Wall2013 | 2013 | Large Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
1LOBelow Grade Wall2013 | 2013 | Large Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
2LOBelow Grade Wall2013 | 2013 | Large Office | 2 | Below Grade Wall |  | 1.140 |  | 1.140 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill insulation | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
3LOBelow Grade Wall2013 | 2013 | Large Office | 3 | Below Grade Wall |  | 1.140 |  | 1.140 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill insulation | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | LO
4LOBelow Grade Wall2013 | 2013 | Large Office | 4 | Below Grade Wall |  | 0.119 |  | 0.119 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill + XPS (interpolated) insulation | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
5LOBelow Grade Wall2013 | 2013 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 | Concrete Masonry Units (CMU), 8"x16"x8" (Single Wythe), No cavity fill + XPS (interpolated) insulation | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
5LOBelow Grade Wall2013 | 2013 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
5LOBelow Grade Wall2013 | 2013 | Large Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | LO
6LOBelow Grade Wall2013 | 2013 | Large Office | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | LO
6LOBelow Grade Wall2013 | 2013 | Large Office | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | LO
7LOBelow Grade Wall2013 | 2013 | Large Office | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | LO
8LOBelow Grade Wall2013 | 2013 | Large Office | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | LO
1MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | MA
1MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | MA
5MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
5MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | MA
6MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | MA
6MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | MA
7MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | MA
8MABelow Grade Wall2013 | 2013 | Mid-rise Apartment | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | MA
1PSBelow Grade Wall2013 | 2013 | Primary School | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | PS
1PSBelow Grade Wall2013 | 2013 | Primary School | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | PS
5PSBelow Grade Wall2013 | 2013 | Primary School | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
5PSBelow Grade Wall2013 | 2013 | Primary School | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | PS
6PSBelow Grade Wall2013 | 2013 | Primary School | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | PS
6PSBelow Grade Wall2013 | 2013 | Primary School | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | PS
7PSBelow Grade Wall2013 | 2013 | Primary School | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | PS
8PSBelow Grade Wall2013 | 2013 | Primary School | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | PS
1SHBelow Grade Wall2013 | 2013 | Small Hotel | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SH
1SHBelow Grade Wall2013 | 2013 | Small Hotel | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SH
5SHBelow Grade Wall2013 | 2013 | Small Hotel | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
5SHBelow Grade Wall2013 | 2013 | Small Hotel | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SH
6SHBelow Grade Wall2013 | 2013 | Small Hotel | 6 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SH
6SHBelow Grade Wall2013 | 2013 | Small Hotel | 6 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SH
7SHBelow Grade Wall2013 | 2013 | Small Hotel | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SH
8SHBelow Grade Wall2013 | 2013 | Small Hotel | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SH
1SHNRBelow Grade Wall2013 | 2013 | Small Hotel - Non-res | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SHNR
6SHNRBelow Grade Wall2013 | 2013 | Small Hotel - Non-res | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SHNR
7SHNRBelow Grade Wall2013 | 2013 | Small Hotel - Non-res | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SHNR
8SHNRBelow Grade Wall2013 | 2013 | Small Hotel - Non-res | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SHNR
1SOBelow Grade Wall2013 | 2013 | Small Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SO
1SOBelow Grade Wall2013 | 2013 | Small Office | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SO
5SOBelow Grade Wall2013 | 2013 | Small Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
5SOBelow Grade Wall2013 | 2013 | Small Office | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SO
6SOBelow Grade Wall2013 | 2013 | Small Office | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SO
6SOBelow Grade Wall2013 | 2013 | Small Office | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SO
7SOBelow Grade Wall2013 | 2013 | Small Office | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SO
8SOBelow Grade Wall2013 | 2013 | Small Office | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SO
1SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SR
1SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 1 | Below Grade Wall |  | 1.14 |  | 1.14 |  | 4.6884 | 6.0839 | 0 | 10.7723 | 1.047 | 1.046 | 0 | 1 | 4.9088 | 6.3637 | 0 | 10.7723 | SR
5SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
5SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 5 | Below Grade Wall |  | 0.119 |  | 0.119 |  | 8.5556 | 10.7685 | 0 | 19.3241 | 1.047 | 1.046 | 0 | 1 | 8.9577 | 11.2638 | 0 | 19.3241 | SR
6SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SR
6SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 6 | Below Grade Wall |  | 0.092 |  | 0.092 |  | 8.8825 | 10.7685 | 0 | 19.651 | 1.047 | 1.046 | 0 | 1 | 9.3 | 11.2638 | 0 | 19.651 | SR
7SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 7 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SR
8SRBelow Grade Wall2013 | 2013 | Stand-alone Retail | 8 | Below Grade Wall |  | 0.063 |  | 0.063 |  | 9.5683 | 10.7685 | 0 | 20.3367 | 1.047 | 1.046 | 0 | 1 | 10.018 | 11.2638 | 0 | 20.3367 | SR
1LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | LO
1LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | LO
2LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
3LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
4LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
5LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
5LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
5LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
6LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
6LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
7LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
8LORoof - Insulation Entirely Above Deck2010 | 2010 | Large Office | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
1MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | MA
1MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | MA
2MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
3MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
4MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
5MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
5MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
5MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
6MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
6MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
7MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
8MARoof - Insulation Entirely Above Deck2010 | 2010 | Mid-rise Apartment | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
1PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | PS
1PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | PS
2PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
3PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
4PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
5PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
5PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
5PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
6PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
6PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
7PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
8PSRoof - Insulation Entirely Above Deck2010 | 2010 | Primary School | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
1SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | SH
1SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | SH
2SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
3SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
4SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
5SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
5SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
5SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
6SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
6SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
7SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
8SHRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
1SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | SHNR
2SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
3SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
4SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
5SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
6SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
7SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
8SHNRRoof - Insulation Entirely Above Deck2010 | 2010 | Small Hotel - Non-res | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
1SORoof - Attic and other2010 | 2010 | Small Office | 1 | Roof | Attic and other | 0.034 |  | 0.034 |  | 4.5826 | 2.404 | 0.121 | 7.1076 | 1.081 | 1.038 | 1.2333 | 1 | 4.9538 | 2.4954 | 0.14923 | 7.1076 | SO
1SORoof - Attic and other2010 | 2010 | Small Office | 1 | Roof | Attic and other | 0.034 |  | 0.034 |  | 4.5826 | 2.404 | 0.121 | 7.1076 | 1.081 | 1.038 | 1.2333 | 1 | 4.9538 | 2.4954 | 0.14923 | 7.1076 | SO
2SORoof - Attic and other2010 | 2010 | Small Office | 2 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
3SORoof - Attic and other2010 | 2010 | Small Office | 3 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
4SORoof - Attic and other2010 | 2010 | Small Office | 4 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
5SORoof - Attic and other2010 | 2010 | Small Office | 5 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
5SORoof - Attic and other2010 | 2010 | Small Office | 5 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
5SORoof - Attic and other2010 | 2010 | Small Office | 5 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
6SORoof - Attic and other2010 | 2010 | Small Office | 6 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
6SORoof - Attic and other2010 | 2010 | Small Office | 6 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
7SORoof - Attic and other2010 | 2010 | Small Office | 7 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
8SORoof - Attic and other2010 | 2010 | Small Office | 8 | Roof | Attic and other | 0.021 |  | 0.021 |  | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
1SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | SR
1SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 1 | Roof | Insulation Entirely Above Deck | 0.063 |  | 0.063 |  | 16.3337 | 8.3534 | 0 | 24.6871 | 1.103 | 1.047 | 0 | 1 | 18.0161 | 8.746 | 0 | 24.6871 | SR
2SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 2 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
3SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 3 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
4SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 4 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
5SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 | Concrete or Metal Deck, Polyiso insulation | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
5SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
5SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
6SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
6SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 6 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
7SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 7 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
8SRRoof - Insulation Entirely Above Deck2010 | 2010 | Stand-alone Retail | 8 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
1LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
1LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | LO
2LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | LO
3LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | LO
4LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
5LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
5LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
5LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
6LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
6LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | LO
7LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | LO
8LORoof - Insulation Entirely Above Deck2013 | 2013 | Large Office | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | LO
1MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
1MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | MA
2MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | MA
3MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | MA
4MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
5MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
5MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
5MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
6MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
6MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | MA
7MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | MA
8MARoof - Insulation Entirely Above Deck2013 | 2013 | Mid-rise Apartment | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | MA
1PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
1PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | PS
2PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | PS
3PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | PS
4PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
5PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
5PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
5PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
6PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
6PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | PS
7PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | PS
8PSRoof - Insulation Entirely Above Deck2013 | 2013 | Primary School | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | PS
1SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 1 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
1SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 1 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SH
2SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SH
3SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SH
4SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
5SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
5SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
5SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
6SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
6SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SH
7SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SH
8SHRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SH
1SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SHNR
2SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SHNR
3SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SHNR
4SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SHNR
5SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SHNR
6SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SHNR
7SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SHNR
8SHNRRoof - Insulation Entirely Above Deck2013 | 2013 | Small Hotel - Non-res | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SHNR
1SORoof - Attic and other2013 | 2013 | Small Office | 1 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
1SORoof - Attic and other2013 | 2013 | Small Office | 1 | Roof | Attic and other | 0.027 |  | 0.027 |  | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
2SORoof - Attic and other2013 | 2013 | Small Office | 2 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
3SORoof - Attic and other2013 | 2013 | Small Office | 3 | Roof | Attic and other | 0.027 |  | 0.027 | Engineered Truss, 24" OC, Blown in insulation | 4.767 | 2.5957 | 0.176 | 7.5386 | 1.081 | 1.038 | 1.2333 | 1 | 5.1531 | 2.6943 | 0.21707 | 7.5386 | SO
4SORoof - Attic and other2013 | 2013 | Small Office | 4 | Roof | Attic and other | 0.021 |  | 0.021 | Engineered Truss, 24" OC, Blown in insulation | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
5SORoof - Attic and other2013 | 2013 | Small Office | 5 | Roof | Attic and other | 0.021 |  | 0.021 | Engineered Truss, 24" OC, Blown in insulation | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
5SORoof - Attic and other2013 | 2013 | Small Office | 5 | Roof | Attic and other | 0.021 |  | 0.021 |  | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
5SORoof - Attic and other2013 | 2013 | Small Office | 5 | Roof | Attic and other | 0.021 |  | 0.021 |  | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
6SORoof - Attic and other2013 | 2013 | Small Office | 6 | Roof | Attic and other | 0.021 |  | 0.021 |  | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
6SORoof - Attic and other2013 | 2013 | Small Office | 6 | Roof | Attic and other | 0.021 |  | 0.021 |  | 5.0435 | 2.6852 | 0.209 | 7.9377 | 1.081 | 1.038 | 1.2333 | 1 | 5.452 | 2.7872 | 0.25777 | 7.9377 | SO
7SORoof - Attic and other2013 | 2013 | Small Office | 7 | Roof | Attic and other | 0.017 |  | 0.017 |  | 5.3355 | 2.8129 | 0.242 | 8.3904 | 1.081 | 1.038 | 1.2333 | 1 | 5.7676 | 2.9198 | 0.29847 | 8.3904 | SO
8SORoof - Attic and other2013 | 2013 | Small Office | 8 | Roof | Attic and other | 0.017 |  | 0.017 |  | 5.3355 | 2.8129 | 0.242 | 8.3904 | 1.081 | 1.038 | 1.2333 | 1 | 5.7676 | 2.9198 | 0.29847 | 8.3904 | SO
1SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
1SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 1 | Roof | Insulation Entirely Above Deck | 0.048 |  | 0.048 |  | 16.93 | 8.3662 | 0 | 25.2962 | 1.103 | 1.047 | 0 | 1 | 18.6738 | 8.7594 | 0 | 25.2962 | SR
2SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 2 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SR
3SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 3 | Roof | Insulation Entirely Above Deck | 0.039 |  | 0.039 | Concrete or Metal Deck, Polyiso insulation | 17.5153 | 8.3694 | 0 | 25.8847 | 1.103 | 1.047 | 0 | 1 | 19.3194 | 8.7628 | 0 | 25.8847 | SR
4SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 4 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
5SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 | Concrete or Metal Deck, Polyiso insulation | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
5SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
5SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 5 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
6SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
6SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 6 | Roof | Insulation Entirely Above Deck | 0.032 |  | 0.032 |  | 17.8596 | 8.3856 | 0 | 26.2452 | 1.103 | 1.047 | 0 | 1 | 19.6991 | 8.7797 | 0 | 26.2452 | SR
7SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 7 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SR
8SRRoof - Insulation Entirely Above Deck2013 | 2013 | Stand-alone Retail | 8 | Roof | Insulation Entirely Above Deck | 0.028 |  | 0.028 |  | 18.2941 | 8.3856 | 0 | 26.6797 | 1.103 | 1.047 | 0 | 1 | 20.1784 | 8.7797 | 0 | 26.6797 | SR
2PSSkylights2010 | 2010 | Primary School | 2 | Skylights |  | 1.98 | 0.19 | 1.98, 0.19 |  | 38.1774 | 17.1196 | 0 | 55.2971 | 1.123 | 1.195 | 0 | 1 | 42.8733 | 20.458 | 0 | 55.2971 | PS
3PSSkylights2010 | 2010 | Primary School | 3 | Skylights |  | 1.17 | 0.19 | 1.17, 0.19 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | PS
4PSSkylights2010 | 2010 | Primary School | 4 | Skylights |  | 1.17 | 0.39 | 1.17, 0.39 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | PS
5PSSkylights2010 | 2010 | Primary School | 5 | Skylights |  | 1.17 | 0.39 | 1.17, 0.39 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | PS
6PSSkylights2010 | 2010 | Primary School | 6 | Skylights |  | 1.17 | 0.39 | 1.17, 0.39 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | PS
2SRSkylights2010 | 2010 | Stand-alone Retail | 2 | Skylights |  | 1.98 | 0.36 | 1.98, 0.36 |  | 38.1774 | 17.1196 | 0 | 55.2971 | 1.123 | 1.195 | 0 | 1 | 42.8733 | 20.458 | 0 | 55.2971 | SR
3SRSkylights2010 | 2010 | Stand-alone Retail | 3 | Skylights |  | 1.17 | 0.39 | 1.17, 0.39 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | SR
4SRSkylights2010 | 2010 | Stand-alone Retail | 4 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | SR
5SRSkylights2010 | 2010 | Stand-alone Retail | 5 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | SR
6SRSkylights2010 | 2010 | Stand-alone Retail | 6 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 54.9593 | 22.4271 | 0 | 77.3864 | 1.123 | 1.195 | 0 | 1 | 61.7193 | 26.8003 | 0 | 77.3864 | SR
2PSSkylights2013 | 2013 | Primary School | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 58.0553 | 22.4271 | 0 | 80.4824 | 1.123 | 1.195 | 0 | 1 | 65.1961 | 26.8003 | 0 | 80.4824 | PS
3PSSkylights2013 | 2013 | Primary School | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 78.9717 | 27.5518 | 0 | 106.5235 | 1.123 | 1.195 | 0 | 1 | 88.6852 | 32.9244 | 0 | 106.5235 | PS
4PSSkylights2013 | 2013 | Primary School | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | PS
5PSSkylights2013 | 2013 | Primary School | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | PS
6PSSkylights2013 | 2013 | Primary School | 6 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | PS
2SRSkylights2013 | 2013 | Stand-alone Retail | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 58.0553 | 22.4271 | 0 | 80.4824 | 1.123 | 1.195 | 0 | 1 | 65.1961 | 26.8003 | 0 | 80.4824 | SR
3SRSkylights2013 | 2013 | Stand-alone Retail | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 78.9717 | 27.5518 | 0 | 106.5235 | 1.123 | 1.195 | 0 | 1 | 88.6852 | 32.9244 | 0 | 106.5235 | SR
4SRSkylights2013 | 2013 | Stand-alone Retail | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | SR
5SRSkylights2013 | 2013 | Stand-alone Retail | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | SR
6SRSkylights2013 | 2013 | Stand-alone Retail | 6 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 79.8117 | 27.5518 | 0 | 107.3635 | 1.123 | 1.195 | 0 | 1 | 89.6286 | 32.9244 | 0 | 107.3635 | SR
1LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
1LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
2LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
3LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
4LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 4 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
5LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 5 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
5LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
5LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
6LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | LO
6LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | LO
7LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
8LOSlab-on-grade - Unheated2010 | 2010 | Large Office | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
1MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
1MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
2MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
3MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
4MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 4 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | MA
5MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | MA
5MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
5MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
6MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | MA
6MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | MA
7MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | MA
8MASlab-on-grade - Unheated2010 | 2010 | Mid-rise Apartment | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | MA
1PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
1PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
2PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
3PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
4PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 4 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
5PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 5 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
5PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
5PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
6PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | PS
6PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | PS
7PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
8PSSlab-on-grade - Unheated2010 | 2010 | Primary School | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
1SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
1SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
2SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
3SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
4SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 4 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SH
5SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SH
5SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
5SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
6SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 6 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SH
6SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 6 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SH
7SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SH
8SHSlab-on-grade - Unheated2010 | 2010 | Small Hotel | 8 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SH
1SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
2SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
3SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
4SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 4 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
5SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 5 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
6SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SHNR
7SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SHNR
8SHNRSlab-on-grade - Unheated2010 | 2010 | Small Hotel - Non-res | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SHNR
1SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
1SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
2SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
3SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
4SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 4 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
5SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 5 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
5SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
5SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
6SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SO
6SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SO
7SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
8SOSlab-on-grade - Unheated2010 | 2010 | Small Office | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
1SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
1SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
2SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
3SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
4SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 4 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
5SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
5SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
5SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
6SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SR
6SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 6 | Slab-on-grade | Unheated | 0.54 |  | 0.54 |  | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SR
7SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 7 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
8SRSlab-on-grade - Unheated2010 | 2010 | Stand-alone Retail | 8 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
1LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
1LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
2LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
3LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | LO
4LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
5LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 5 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
5LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
5LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | LO
6LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | LO
6LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | LO
7LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | LO
8LOSlab-on-grade - Unheated2013 | 2013 | Large Office | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | LO
1MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
1MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
2MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | MA
3MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 3 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | MA
4MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | MA
5MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.510 |  | 0.510 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | MA
5MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | MA
5MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | MA
6MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | MA
6MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | MA
7MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | MA
8MASlab-on-grade - Unheated2013 | 2013 | Mid-rise Apartment | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | MA
1PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
1PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
2PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
3PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | PS
4PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
5PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 5 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
5PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
5PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | PS
6PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | PS
6PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | PS
7PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | PS
8PSSlab-on-grade - Unheated2013 | 2013 | Primary School | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | PS
1SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
1SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
2SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SH
3SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 3 | Slab-on-grade | Unheated | 0.540 |  | 0.540 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 6.8938 | 5.7874 | 0 | 12.68 | 1.03 | 0.988 | 0 | 1 | 7.1007 | 5.7179 | 0 | 12.68 | SH
4SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SH
5SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.510 |  | 0.510 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SH
5SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SH
5SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SH
6SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 6 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SH
6SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 6 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SH
7SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 7 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SH
8SHSlab-on-grade - Unheated2013 | 2013 | Small Hotel | 8 | Slab-on-grade | Unheated | 0.424 |  | 0.424 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | SH
1SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
2SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
3SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SHNR
4SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SHNR
5SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 5 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SHNR
6SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SHNR
7SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SHNR
8SHNRSlab-on-grade - Unheated2013 | 2013 | Small Hotel - Non-res | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | SHNR
1SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
1SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
2SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
3SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SO
4SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
5SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 5 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
5SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
5SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SO
6SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SO
6SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SO
7SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SO
8SOSlab-on-grade - Unheated2013 | 2013 | Small Office | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | SO
1SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
1SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 1 | Slab-on-grade | Unheated | 0.73 |  | 0.73 |  | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
2SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 2 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
3SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 3 | Slab-on-grade | Unheated | 0.730 |  | 0.730 | Base slab 6 in. concrete poured directly onto insulation, No insulation | 3.2907 | 1.292 | 0 | 4.5828 | 1.03 | 0.988 | 0 | 1 | 3.3895 | 1.2765 | 0 | 4.5828 | SR
4SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 4 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
5SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.520 |  | 0.520 | Base slab 6 in. concrete poured directly onto insulation, vertical XPS insulation | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
5SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
5SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 5 | Slab-on-grade | Unheated | 0.52 |  | 0.52 |  | 7.4829 | 5.7874 | 0 | 13.27 | 1.03 | 0.988 | 0 | 1 | 7.7074 | 5.7179 | 0 | 13.27 | SR
6SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SR
6SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 6 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SR
7SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 7 | Slab-on-grade | Unheated | 0.51 |  | 0.51 |  | 8.0309 | 5.7874 | 0 | 13.82 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.82 | SR
8SRSlab-on-grade - Unheated2013 | 2013 | Stand-alone Retail | 8 | Slab-on-grade | Unheated | 0.434 |  | 0.434 |  | 8.0309 | 5.7874 | 0 | 13.8183 | 1.03 | 0.988 | 0 | 1 | 8.2719 | 5.7179 | 0 | 13.8183 | SR
1MAWindows2010 | 2010 | Mid-rise Apartment | 1 | Windows |  | 1.2003 | 0.25007 | 1.20, 0.25 |  | 21.3228 | 24.9548 |  | 46.2776 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 29.9458 | 0 | 46.2776 | MA
2MAWindows2010 | 2010 | Mid-rise Apartment | 2 | Windows |  | 0.74771 | 0.25007 | 0.75, 0.25 |  | 21.3228 | 24.9548 |  | 46.2776 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 29.9458 | 0 | 46.2776 | MA
3MAWindows2010 | 2010 | Mid-rise Apartment | 3 | Windows |  | 0.64768 | 0.25007 | 0.65, 0.25 |  | 21.3228 | 24.9548 |  | 46.2776 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 29.9458 | 0 | 46.2776 | MA
4MAWindows2010 | 2010 | Mid-rise Apartment | 4 | Windows |  | 0.49979 | 0.40011 | 0.50, 0.40 |  | 21.3228 | 22.6785 |  | 44.0013 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 27.2142 | 0 | 44.0013 | MA
5MAWindows2010 | 2010 | Mid-rise Apartment | 5 | Windows |  | 0.48135 | 0.40011 | 0.48, 0.40 |  | 21.3228 | 22.809 |  | 44.1317 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 27.3708 | 0 | 44.1317 | MA
6MAWindows2010 | 2010 | Mid-rise Apartment | 6 | Windows |  | 0.48135 | 0.40011 | 0.48, 0.40 |  | 21.3228 | 22.809 |  | 44.1317 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 27.3708 | 0 | 44.1317 | MA
7MAWindows2010 | 2010 | Mid-rise Apartment | 7 | Windows |  | 0.41572 | 0.45012 | 0.42, 0.45 |  | 21.3228 | 24.1846 |  | 45.5074 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 29.0215 | 0 | 45.5074 | MA
8MAWindows2010 | 2010 | Mid-rise Apartment | 8 | Windows |  | 0.41572 | 0.45012 | 0.42, 0.45 |  | 21.3228 | 24.1846 |  | 45.5074 | 1.088 | 1.2 | 0 | 1 | 23.1992 | 29.0215 | 0 | 45.5074 | MA
1SHWindows2010 | 2010 | Small Hotel | 1 | Windows |  | 1.2009 | 0.25019 | 1.20, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SH
2SHWindows2010 | 2010 | Small Hotel | 2 | Windows |  | 0.7403 | 0.25019 | 0.74, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SH
3SHWindows2010 | 2010 | Small Hotel | 3 | Windows |  | 0.64022 | 0.25019 | 0.64, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SH
4SHWindows2010 | 2010 | Small Hotel | 4 | Windows |  | 0.52291 | 0.4003 | 0.52, 0.40 |  | 25.9648 | 15.2108 |  | 41.1755 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.2529 | 0 | 41.1755 | SH
5SHWindows2010 | 2010 | Small Hotel | 5 | Windows |  | 0.5069 | 0.4003 | 0.51, 0.40 |  | 25.9648 | 15.46 |  | 41.4248 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.552 | 0 | 41.4248 | SH
6SHWindows2010 | 2010 | Small Hotel | 6 | Windows |  | 0.5069 | 0.4003 | 0.51, 0.40 |  | 25.9648 | 15.46 |  | 41.4248 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.552 | 0 | 41.4248 | SH
7SHWindows2010 | 2010 | Small Hotel | 7 | Windows |  | 0.42858 | 0.45034 | 0.43, 0.45 |  | 25.9648 | 16.9793 |  | 42.944 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 20.3751 | 0 | 42.944 | SH
8SHWindows2010 | 2010 | Small Hotel | 8 | Windows |  | 0.42858 | 0.45034 | 0.43, 0.45 |  | 25.9648 | 16.9793 |  | 42.944 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 20.3751 | 0 | 42.944 | SH
1SHNRWindows2010 | 2010 | Small Hotel - Non-res | 1 | Windows |  | 1.2009 | 0.25019 | 1.20, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SHNR
2SHNRWindows2010 | 2010 | Small Hotel - Non-res | 2 | Windows |  | 0.7403 | 0.25019 | 0.74, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SHNR
3SHNRWindows2010 | 2010 | Small Hotel - Non-res | 3 | Windows |  | 0.64022 | 0.25019 | 0.64, 0.25 |  | 25.9648 | 17.8022 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 21.3627 | 0 | 43.767 | SHNR
4SHNRWindows2010 | 2010 | Small Hotel - Non-res | 4 | Windows |  | 0.52291 | 0.4003 | 0.52, 0.40 |  | 25.9648 | 15.2108 |  | 41.1755 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.2529 | 0 | 41.1755 | SHNR
5SHNRWindows2010 | 2010 | Small Hotel - Non-res | 5 | Windows |  | 0.5069 | 0.4003 | 0.51, 0.40 |  | 25.9648 | 15.46 |  | 41.4248 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.552 | 0 | 41.4248 | SHNR
6SHNRWindows2010 | 2010 | Small Hotel - Non-res | 6 | Windows |  | 0.5069 | 0.4003 | 0.51, 0.40 |  | 25.9648 | 15.46 |  | 41.4248 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 18.552 | 0 | 41.4248 | SHNR
7SHNRWindows2010 | 2010 | Small Hotel - Non-res | 7 | Windows |  | 0.42858 | 0.45034 | 0.43, 0.45 |  | 25.9648 | 16.9793 |  | 42.944 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 20.3751 | 0 | 42.944 | SHNR
8SHNRWindows2010 | 2010 | Small Hotel - Non-res | 8 | Windows |  | 0.42858 | 0.45034 | 0.43, 0.45 |  | 25.9648 | 16.9793 |  | 42.944 | 1.088 | 1.2 | 0 | 1 | 28.2497 | 20.3751 | 0 | 42.944 | SHNR
1SOWindows2010 | 2010 | Small Office | 1 | Windows |  | 1.201 | 0.25021 | 1.20, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | SO
2SOWindows2010 | 2010 | Small Office | 2 | Windows |  | 0.71951 | 0.25021 | 0.72, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | SO
3SOWindows2010 | 2010 | Small Office | 3 | Windows |  | 0.61942 | 0.25021 | 0.62, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | SO
4SOWindows2010 | 2010 | Small Office | 4 | Windows |  | 0.5169 | 0.40033 | 0.52, 0.40 |  | 28.2043 | 11.9683 |  | 40.1726 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 14.3619 | 0 | 40.1726 | SO
5SOWindows2010 | 2010 | Small Office | 5 | Windows |  | 0.48497 | 0.40033 | 0.48, 0.40 |  | 28.2043 | 12.6442 |  | 40.8485 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 15.173 | 0 | 40.8485 | SO
6SOWindows2010 | 2010 | Small Office | 6 | Windows |  | 0.48497 | 0.40033 | 0.48, 0.40 |  | 28.2043 | 12.6442 |  | 40.8485 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 15.173 | 0 | 40.8485 | SO
7SOWindows2010 | 2010 | Small Office | 7 | Windows |  | 0.41763 | 0.45037 | 0.42, 0.45 |  | 28.2043 | 13.5761 |  | 41.7804 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 16.2913 | 0 | 41.7804 | SO
8SOWindows2010 | 2010 | Small Office | 8 | Windows |  | 0.41763 | 0.45037 | 0.42, 0.45 |  | 28.2043 | 13.5761 |  | 41.7804 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 16.2913 | 0 | 41.7804 | SO
1LOWindows2010 | 2010 | Large Office | 1 | Windows |  | 1.201 | 0.25021 | 1.20, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | LO
2LOWindows2010 | 2010 | Large Office | 2 | Windows |  | 0.71951 | 0.25021 | 0.72, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | LO
3LOWindows2010 | 2010 | Large Office | 3 | Windows |  | 0.61942 | 0.25021 | 0.62, 0.25 |  | 28.2043 | 14.3424 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 17.2109 | 0 | 42.5467 | LO
4LOWindows2010 | 2010 | Large Office | 4 | Windows |  | 0.5169 | 0.40033 | 0.52, 0.40 |  | 28.2043 | 11.9683 |  | 40.1726 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 14.3619 | 0 | 40.1726 | LO
5LOWindows2010 | 2010 | Large Office | 5 | Windows |  | 0.48497 | 0.40033 | 0.48, 0.40 |  | 28.2043 | 12.6442 |  | 40.8485 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 15.173 | 0 | 40.8485 | LO
6LOWindows2010 | 2010 | Large Office | 6 | Windows |  | 0.48497 | 0.40033 | 0.48, 0.40 |  | 28.2043 | 12.6442 |  | 40.8485 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 15.173 | 0 | 40.8485 | LO
7LOWindows2010 | 2010 | Large Office | 7 | Windows |  | 0.41763 | 0.45037 | 0.42, 0.45 |  | 28.2043 | 13.5761 |  | 41.7804 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 16.2913 | 0 | 41.7804 | LO
8LOWindows2010 | 2010 | Large Office | 8 | Windows |  | 0.41763 | 0.45037 | 0.42, 0.45 |  | 28.2043 | 13.5761 |  | 41.7804 | 1.088 | 1.2 | 0 | 1 | 30.6863 | 16.2913 | 0 | 41.7804 | LO
1SRWindows2010 | 2010 | Stand-alone Retail | 1 | Windows |  | 1.2084 | 0.25176 | 1.21, 0.25 |  | 26.4984 | 17.3414 |  | 43.8398 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 20.8096 | 0 | 43.8398 | SR
2SRWindows2010 | 2010 | Stand-alone Retail | 2 | Windows |  | 0.72407 | 0.25176 | 0.72, 0.25 |  | 26.4984 | 17.3414 |  | 43.8398 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 20.8096 | 0 | 43.8398 | SR
3SRWindows2010 | 2010 | Stand-alone Retail | 3 | Windows |  | 0.62337 | 0.25176 | 0.62, 0.25 |  | 26.4984 | 17.3414 |  | 43.8398 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 20.8096 | 0 | 43.8398 | SR
4SRWindows2010 | 2010 | Stand-alone Retail | 4 | Windows |  | 0.50776 | 0.40282 | 0.51, 0.40 |  | 26.4984 | 15.1461 |  | 41.6445 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 18.1753 | 0 | 41.6445 | SR
5SRWindows2010 | 2010 | Stand-alone Retail | 5 | Windows |  | 0.47159 | 0.40282 | 0.47, 0.40 |  | 26.4984 | 15.844 |  | 42.3424 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 19.0128 | 0 | 42.3424 | SR
6SRWindows2010 | 2010 | Stand-alone Retail | 6 | Windows |  | 0.47159 | 0.40282 | 0.47, 0.40 |  | 26.4984 | 15.844 |  | 42.3424 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 19.0128 | 0 | 42.3424 | SR
7SRWindows2010 | 2010 | Stand-alone Retail | 7 | Windows |  | 0.41203 | 0.45317 | 0.41, 0.45 |  | 26.4984 | 16.6063 |  | 43.1047 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 19.9275 | 0 | 43.1047 | SR
8SRWindows2010 | 2010 | Stand-alone Retail | 8 | Windows |  | 0.41203 | 0.45317 | 0.41, 0.45 |  | 26.4984 | 16.6063 |  | 43.1047 | 1.088 | 1.2 | 0 | 1 | 28.8303 | 19.9275 | 0 | 43.1047 | SR
1PSWindows2010 | 2010 | Primary School | 1 | Windows |  | 1.1997 | 0.24993 | 1.20, 0.25 |  | 23.6415 | 21.3368 |  | 44.9783 | 1.088 | 1.2 | 0 | 1 | 25.722 | 25.6042 | 0 | 44.9783 | PS
2PSWindows2010 | 2010 | Primary School | 2 | Windows |  | 0.72752 | 0.24993 | 0.73, 0.25 |  | 23.6415 | 21.3368 |  | 44.9783 | 1.088 | 1.2 | 0 | 1 | 25.722 | 25.6042 | 0 | 44.9783 | PS
3PSWindows2010 | 2010 | Primary School | 3 | Windows |  | 0.62755 | 0.24993 | 0.63, 0.25 |  | 23.6415 | 21.3368 |  | 44.9783 | 1.088 | 1.2 | 0 | 1 | 25.722 | 25.6042 | 0 | 44.9783 | PS
4PSWindows2010 | 2010 | Primary School | 4 | Windows |  | 0.49516 | 0.39989 | 0.50, 0.40 |  | 23.6415 | 19.2466 |  | 42.8881 | 1.088 | 1.2 | 0 | 1 | 25.722 | 23.096 | 0 | 42.8881 | PS
5PSWindows2010 | 2010 | Primary School | 5 | Windows |  | 0.46208 | 0.39989 | 0.46, 0.40 |  | 23.6415 | 19.7796 |  | 43.4211 | 1.088 | 1.2 | 0 | 1 | 25.722 | 23.7355 | 0 | 43.4211 | PS
6PSWindows2010 | 2010 | Primary School | 6 | Windows |  | 0.46208 | 0.39989 | 0.46, 0.40 |  | 23.6415 | 19.7796 |  | 43.4211 | 1.088 | 1.2 | 0 | 1 | 25.722 | 23.7355 | 0 | 43.4211 | PS
7PSWindows2010 | 2010 | Primary School | 7 | Windows |  | 0.40599 | 0.44988 | 0.41, 0.45 |  | 23.6415 | 20.6169 |  | 44.2584 | 1.088 | 1.2 | 0 | 1 | 25.722 | 24.7403 | 0 | 44.2584 | PS
8PSWindows2010 | 2010 | Primary School | 8 | Windows |  | 0.40599 | 0.44988 | 0.41, 0.45 |  | 23.6415 | 20.6169 |  | 44.2584 | 1.088 | 1.2 | 0 | 1 | 25.722 | 24.7403 | 0 | 44.2584 | PS
1MAWindows2013 | 2013 | Mid-rise Apartment | 1 | Windows |  | 0.59832 | 0.25007 | 0.60, 0.25 |  | 24.9548 | 21.3228 |  | 46.2776 | 1.088 | 1.2 | 0 | 1 | 27.1509 | 25.5873 | 0 | 46.2776 | MA
2MAWindows2013 | 2013 | Mid-rise Apartment | 2 | Windows |  | 0.56642 | 0.25007 | 0.57, 0.25 |  | 24.9548 | 21.3228 |  | 46.2776 | 1.088 | 1.2 | 0 | 1 | 27.1509 | 25.5873 | 0 | 46.2776 | MA
3MAWindows2013 | 2013 | Mid-rise Apartment | 3 | Windows |  | 0.51541 | 0.25007 | 0.52, 0.25 |  | 25.0039 | 21.3228 |  | 46.3267 | 1.088 | 1.2 | 0 | 1 | 27.2042 | 25.5873 | 0 | 46.3267 | MA
4MAWindows2013 | 2013 | Mid-rise Apartment | 4 | Windows |  | 0.44828 | 0.40011 | 0.45, 0.40 |  | 23.5028 | 21.3228 |  | 44.8256 | 1.088 | 1.2 | 0 | 1 | 25.571 | 25.5873 | 0 | 44.8256 | MA
5MAWindows2013 | 2013 | Mid-rise Apartment | 5 | Windows |  | 0.43871 | 0.40011 | 0.44, 0.40 |  | 23.7335 | 21.3228 |  | 45.0562 | 1.088 | 1.2 | 0 | 1 | 25.822 | 25.5873 | 0 | 45.0562 | MA
6MAWindows2013 | 2013 | Mid-rise Apartment | 6 | Windows |  | 0.43871 | 0.40011 | 0.44, 0.40 |  | 23.7335 | 21.3228 |  | 45.0562 | 1.088 | 1.2 | 0 | 1 | 25.822 | 25.5873 | 0 | 45.0562 | MA
7MAWindows2013 | 2013 | Mid-rise Apartment | 7 | Windows |  | 0.37358 | 0.45012 | 0.37, 0.45 |  | 24.6167 | 21.3228 |  | 45.9395 | 1.088 | 1.2 | 0 | 1 | 26.783 | 25.5873 | 0 | 45.9395 | MA
8MAWindows2013 | 2013 | Mid-rise Apartment | 8 | Windows |  | 0.37358 | 0.45012 | 0.37, 0.45 |  | 24.6167 | 21.3228 |  | 45.9395 | 1.088 | 1.2 | 0 | 1 | 26.783 | 25.5873 | 0 | 45.9395 | MA
1SHWindows2013 | 2013 | Small Hotel | 1 | Windows |  | 0.61682 | 0.25019 | 0.62, 0.25 |  | 17.8022 | 25.9648 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 19.3688 | 31.1577 | 0 | 43.767 | SH
2SHWindows2013 | 2013 | Small Hotel | 2 | Windows |  | 0.60533 | 0.25019 | 0.61, 0.25 |  | 17.8022 | 25.9648 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 19.3688 | 31.1577 | 0 | 43.767 | SH
3SHWindows2013 | 2013 | Small Hotel | 3 | Windows |  | 0.55119 | 0.25019 | 0.55, 0.25 |  | 18.0042 | 25.9648 |  | 43.969 | 1.088 | 1.2 | 0 | 1 | 19.5886 | 31.1577 | 0 | 43.969 | SH
4SHWindows2013 | 2013 | Small Hotel | 4 | Windows |  | 0.46671 | 0.4003 | 0.47, 0.40 |  | 16.2443 | 25.9648 |  | 42.209 | 1.088 | 1.2 | 0 | 1 | 17.6738 | 31.1577 | 0 | 42.209 | SH
5SHWindows2013 | 2013 | Small Hotel | 5 | Windows |  | 0.46326 | 0.4003 | 0.46, 0.40 |  | 16.3274 | 25.9648 |  | 42.2922 | 1.088 | 1.2 | 0 | 1 | 17.7642 | 31.1577 | 0 | 42.2922 | SH
6SHWindows2013 | 2013 | Small Hotel | 6 | Windows |  | 0.46326 | 0.4003 | 0.46, 0.40 |  | 16.3274 | 25.9648 |  | 42.2922 | 1.088 | 1.2 | 0 | 1 | 17.7642 | 31.1577 | 0 | 42.2922 | SH
7SHWindows2013 | 2013 | Small Hotel | 7 | Windows |  | 0.387 | 0.45034 | 0.39, 0.45 |  | 17.4309 | 25.9648 |  | 43.3957 | 1.088 | 1.2 | 0 | 1 | 18.9649 | 31.1577 | 0 | 43.3957 | SH
8SHWindows2013 | 2013 | Small Hotel | 8 | Windows |  | 0.387 | 0.45034 | 0.39, 0.45 |  | 17.4309 | 25.9648 |  | 43.3957 | 1.088 | 1.2 | 0 | 1 | 18.9649 | 31.1577 | 0 | 43.3957 | SH
1SHNRWindows2013 | 2013 | Small Hotel - Non-res | 1 | Windows |  | 0.61682 | 0.25019 | 0.62, 0.25 |  | 17.8022 | 25.9648 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 19.3688 | 31.1577 | 0 | 43.767 | SHNR
2SHNRWindows2013 | 2013 | Small Hotel - Non-res | 2 | Windows |  | 0.60533 | 0.25019 | 0.61, 0.25 |  | 17.8022 | 25.9648 |  | 43.767 | 1.088 | 1.2 | 0 | 1 | 19.3688 | 31.1577 | 0 | 43.767 | SHNR
3SHNRWindows2013 | 2013 | Small Hotel - Non-res | 3 | Windows |  | 0.55119 | 0.25019 | 0.55, 0.25 |  | 18.0042 | 25.9648 |  | 43.969 | 1.088 | 1.2 | 0 | 1 | 19.5886 | 31.1577 | 0 | 43.969 | SHNR
4SHNRWindows2013 | 2013 | Small Hotel - Non-res | 4 | Windows |  | 0.46671 | 0.4003 | 0.47, 0.40 |  | 16.2443 | 25.9648 |  | 42.209 | 1.088 | 1.2 | 0 | 1 | 17.6738 | 31.1577 | 0 | 42.209 | SHNR
5SHNRWindows2013 | 2013 | Small Hotel - Non-res | 5 | Windows |  | 0.46326 | 0.4003 | 0.46, 0.40 |  | 16.3274 | 25.9648 |  | 42.2922 | 1.088 | 1.2 | 0 | 1 | 17.7642 | 31.1577 | 0 | 42.2922 | SHNR
6SHNRWindows2013 | 2013 | Small Hotel - Non-res | 6 | Windows |  | 0.46326 | 0.4003 | 0.46, 0.40 |  | 16.3274 | 25.9648 |  | 42.2922 | 1.088 | 1.2 | 0 | 1 | 17.7642 | 31.1577 | 0 | 42.2922 | SHNR
7SHNRWindows2013 | 2013 | Small Hotel - Non-res | 7 | Windows |  | 0.387 | 0.45034 | 0.39, 0.45 |  | 17.4309 | 25.9648 |  | 43.3957 | 1.088 | 1.2 | 0 | 1 | 18.9649 | 31.1577 | 0 | 43.3957 | SHNR
8SHNRWindows2013 | 2013 | Small Hotel - Non-res | 8 | Windows |  | 0.387 | 0.45034 | 0.39, 0.45 |  | 17.4309 | 25.9648 |  | 43.3957 | 1.088 | 1.2 | 0 | 1 | 18.9649 | 31.1577 | 0 | 43.3957 | SHNR
1SOWindows2013 | 2013 | Small Office | 1 | Windows |  | 0.59832 | 0.25021 | 0.60, 0.25 |  | 14.3424 | 28.2043 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 15.6045 | 33.8452 | 0 | 42.5467 | SO
2SOWindows2013 | 2013 | Small Office | 2 | Windows |  | 0.59669 | 0.25021 | 0.60, 0.25 |  | 14.3424 | 28.2043 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 15.6045 | 33.8452 | 0 | 42.5467 | SO
3SOWindows2013 | 2013 | Small Office | 3 | Windows |  | 0.5342 | 0.25021 | 0.53, 0.25 |  | 14.9547 | 28.2043 |  | 43.159 | 1.088 | 1.2 | 0 | 1 | 16.2707 | 33.8452 | 0 | 43.159 | SO
4SOWindows2013 | 2013 | Small Office | 4 | Windows |  | 0.44819 | 0.40033 | 0.45, 0.40 |  | 13.1848 | 28.2043 |  | 41.3891 | 1.088 | 1.2 | 0 | 1 | 14.3451 | 33.8452 | 0 | 41.3891 | SO
5SOWindows2013 | 2013 | Small Office | 5 | Windows |  | 0.4477 | 0.40033 | 0.45, 0.40 |  | 13.1966 | 28.2043 |  | 41.4009 | 1.088 | 1.2 | 0 | 1 | 14.3579 | 33.8452 | 0 | 41.4009 | SO
6SOWindows2013 | 2013 | Small Office | 6 | Windows |  | 0.4477 | 0.40033 | 0.45, 0.40 |  | 13.1966 | 28.2043 |  | 41.4009 | 1.088 | 1.2 | 0 | 1 | 14.3579 | 33.8452 | 0 | 41.4009 | SO
7SOWindows2013 | 2013 | Small Office | 7 | Windows |  | 0.38658 | 0.45037 | 0.39, 0.45 |  | 14.2971 | 28.2043 |  | 42.5014 | 1.088 | 1.2 | 0 | 1 | 15.5552 | 33.8452 | 0 | 42.5014 | SO
8SOWindows2013 | 2013 | Small Office | 8 | Windows |  | 0.38658 | 0.45037 | 0.39, 0.45 |  | 14.2971 | 28.2043 |  | 42.5014 | 1.088 | 1.2 | 0 | 1 | 15.5552 | 33.8452 | 0 | 42.5014 | SO
1LOWindows2013 | 2013 | Large Office | 1 | Windows |  | 0.59832 | 0.25021 | 0.60, 0.25 |  | 14.3424 | 28.2043 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 15.6045 | 33.8452 | 0 | 42.5467 | LO
2LOWindows2013 | 2013 | Large Office | 2 | Windows |  | 0.59669 | 0.25021 | 0.60, 0.25 |  | 14.3424 | 28.2043 |  | 42.5467 | 1.088 | 1.2 | 0 | 1 | 15.6045 | 33.8452 | 0 | 42.5467 | LO
3LOWindows2013 | 2013 | Large Office | 3 | Windows |  | 0.5342 | 0.25021 | 0.53, 0.25 |  | 14.9547 | 28.2043 |  | 43.159 | 1.088 | 1.2 | 0 | 1 | 16.2707 | 33.8452 | 0 | 43.159 | LO
4LOWindows2013 | 2013 | Large Office | 4 | Windows |  | 0.44819 | 0.40033 | 0.45, 0.40 |  | 13.1848 | 28.2043 |  | 41.3891 | 1.088 | 1.2 | 0 | 1 | 14.3451 | 33.8452 | 0 | 41.3891 | LO
5LOWindows2013 | 2013 | Large Office | 5 | Windows |  | 0.4477 | 0.40033 | 0.45, 0.40 |  | 13.1966 | 28.2043 |  | 41.4009 | 1.088 | 1.2 | 0 | 1 | 14.3579 | 33.8452 | 0 | 41.4009 | LO
6LOWindows2013 | 2013 | Large Office | 6 | Windows |  | 0.4477 | 0.40033 | 0.45, 0.40 |  | 13.1966 | 28.2043 |  | 41.4009 | 1.088 | 1.2 | 0 | 1 | 14.3579 | 33.8452 | 0 | 41.4009 | LO
7LOWindows2013 | 2013 | Large Office | 7 | Windows |  | 0.38658 | 0.45037 | 0.39, 0.45 |  | 14.2971 | 28.2043 |  | 42.5014 | 1.088 | 1.2 | 0 | 1 | 15.5552 | 33.8452 | 0 | 42.5014 | LO
8LOWindows2013 | 2013 | Large Office | 8 | Windows |  | 0.38658 | 0.45037 | 0.39, 0.45 |  | 14.2971 | 28.2043 |  | 42.5014 | 1.088 | 1.2 | 0 | 1 | 15.5552 | 33.8452 | 0 | 42.5014 | LO
1SRWindows2013 | 2013 | Stand-alone Retail | 1 | Windows |  | 0.58974 | 0.25176 | 0.59, 0.25 |  | 17.3414 | 26.4984 |  | 43.8398 | 1.088 | 1.2 | 0 | 1 | 18.8674 | 31.7981 | 0 | 43.8398 | SR
2SRWindows2013 | 2013 | Stand-alone Retail | 2 | Windows |  | 0.57981 | 0.25176 | 0.58, 0.25 |  | 17.3414 | 26.4984 |  | 43.8398 | 1.088 | 1.2 | 0 | 1 | 18.8674 | 31.7981 | 0 | 43.8398 | SR
3SRWindows2013 | 2013 | Stand-alone Retail | 3 | Windows |  | 0.51698 | 0.25176 | 0.52, 0.25 |  | 17.9555 | 26.4984 |  | 44.4539 | 1.088 | 1.2 | 0 | 1 | 19.5356 | 31.7981 | 0 | 44.4539 | SR
4SRWindows2013 | 2013 | Stand-alone Retail | 4 | Windows |  | 0.43869 | 0.40282 | 0.44, 0.40 |  | 16.3 | 26.4984 |  | 42.7984 | 1.088 | 1.2 | 0 | 1 | 17.7344 | 31.7981 | 0 | 42.7984 | SR
5SRWindows2013 | 2013 | Stand-alone Retail | 5 | Windows |  | 0.43571 | 0.40282 | 0.44, 0.40 |  | 16.3719 | 26.4984 |  | 42.8703 | 1.088 | 1.2 | 0 | 1 | 17.8126 | 31.7981 | 0 | 42.8703 | SR
6SRWindows2013 | 2013 | Stand-alone Retail | 6 | Windows |  | 0.43571 | 0.40282 | 0.44, 0.40 |  | 16.3719 | 26.4984 |  | 42.8703 | 1.088 | 1.2 | 0 | 1 | 17.8126 | 31.7981 | 0 | 42.8703 | SR
7SRWindows2013 | 2013 | Stand-alone Retail | 7 | Windows |  | 0.38239 | 0.45317 | 0.38, 0.45 |  | 17.3703 | 26.4984 |  | 43.8687 | 1.088 | 1.2 | 0 | 1 | 18.8989 | 31.7981 | 0 | 43.8687 | SR
8SRWindows2013 | 2013 | Stand-alone Retail | 8 | Windows |  | 0.38239 | 0.45317 | 0.38, 0.45 |  | 17.3703 | 26.4984 |  | 43.8687 | 1.088 | 1.2 | 0 | 1 | 18.8989 | 31.7981 | 0 | 43.8687 | SR
1PSWindows2013 | 2013 | Primary School | 1 | Windows |  | 0.58177 | 0.24993 | 0.58, 0.25 |  | 21.3368 | 23.6415 |  | 44.9783 | 1.088 | 1.2 | 0 | 1 | 23.2145 | 28.3698 | 0 | 44.9783 | PS
2PSWindows2013 | 2013 | Primary School | 2 | Windows |  | 0.56015 | 0.24993 | 0.56, 0.25 |  | 21.3368 | 23.6415 |  | 44.9783 | 1.088 | 1.2 | 0 | 1 | 23.2145 | 28.3698 | 0 | 44.9783 | PS
3PSWindows2013 | 2013 | Primary School | 3 | Windows |  | 0.50126 | 0.24993 | 0.50, 0.25 |  | 21.7752 | 23.6415 |  | 45.4167 | 1.088 | 1.2 | 0 | 1 | 23.6914 | 28.3698 | 0 | 45.4167 | PS
4PSWindows2013 | 2013 | Primary School | 4 | Windows |  | 0.43181 | 0.39989 | 0.43, 0.40 |  | 20.2517 | 23.6415 |  | 43.8932 | 1.088 | 1.2 | 0 | 1 | 22.0339 | 28.3698 | 0 | 43.8932 | PS
5PSWindows2013 | 2013 | Primary School | 5 | Windows |  | 0.42532 | 0.39989 | 0.43, 0.40 |  | 20.408 | 23.6415 |  | 44.0495 | 1.088 | 1.2 | 0 | 1 | 22.2039 | 28.3698 | 0 | 44.0495 | PS
6PSWindows2013 | 2013 | Primary School | 6 | Windows |  | 0.42532 | 0.39989 | 0.43, 0.40 |  | 20.408 | 23.6415 |  | 44.0495 | 1.088 | 1.2 | 0 | 1 | 22.2039 | 28.3698 | 0 | 44.0495 | PS
7PSWindows2013 | 2013 | Primary School | 7 | Windows |  | 0.37369 | 0.44988 | 0.37, 0.45 |  | 21.2998 | 23.6415 |  | 44.9413 | 1.088 | 1.2 | 0 | 1 | 23.1741 | 28.3698 | 0 | 44.9413 | PS
8PSWindows2013 | 2013 | Primary School | 8 | Windows |  | 0.37369 | 0.44988 | 0.37, 0.45 |  | 21.2998 | 23.6415 |  | 44.9413 | 1.088 | 1.2 | 0 | 1 | 23.1741 | 28.3698 | 0 | 44.9413 | PS
1LOWindows2016 | 2016 | Large Office | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 14.399 | 28.204 |  | 42.603 | 1.088 | 1.2 | 0 | 1 | 15.6661 | 33.8448 | 0 | 49.5109 | LO
2LOWindows2016 | 2016 | Large Office | 2 | Windows |  | 0.54 | 0.25 | 0.54, 0.25 |  | 14.659 | 28.204 |  | 42.863 | 1.088 | 1.2 | 0 | 1 | 15.949 | 33.8448 | 0 | 49.7938 | LO
3LOWindows2016 | 2016 | Large Office | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 15.438 | 28.204 |  | 43.642 | 1.088 | 1.2 | 0 | 1 | 16.7965 | 33.8448 | 0 | 50.6413 | LO
4LOWindows2016 | 2016 | Large Office | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 14.476 | 28.204 |  | 42.68 | 1.088 | 1.2 | 0 | 1 | 15.7499 | 33.8448 | 0 | 49.5947 | LO
5LOWindows2016 | 2016 | Large Office | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 14.191 | 28.204 |  | 42.395 | 1.088 | 1.2 | 0 | 1 | 15.4398 | 33.8448 | 0 | 49.2846 | LO
6LOWindows2016 | 2016 | Large Office | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 14.079 | 28.204 |  | 42.283 | 1.088 | 1.2 | 0 | 1 | 15.318 | 33.8448 | 0 | 49.1628 | LO
7LOWindows2016 | 2016 | Large Office | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 13.626 | 28.204 |  | 41.83 | 1.088 | 1.2 | 0 | 1 | 14.8251 | 33.8448 | 0 | 48.6699 | LO
8LOWindows2016 | 2016 | Large Office | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 13.972 | 28.204 |  | 42.176 | 1.088 | 1.2 | 0 | 1 | 15.2015 | 33.8448 | 0 | 49.0463 | LO
1LOWindows2019 | 2019 | Large Office | 1 | Windows |  | 0.5 | 0.23 | 0.5, 0.23 |  | 15.291 | 28.204 |  | 43.495 | 1.088 | 1.2 | 0 | 1 | 16.6366 | 33.8448 | 0 | 50.4814 | LO
2LOWindows2019 | 2019 | Large Office | 2 | Windows |  | 0.46 | 0.25 | 0.46, 0.25 |  | 15.352 | 28.204 |  | 43.556 | 1.088 | 1.2 | 0 | 1 | 16.703 | 33.8448 | 0 | 50.5478 | LO
3LOWindows2019 | 2019 | Large Office | 3 | Windows |  | 0.42 | 0.25 | 0.42, 0.25 |  | 15.698 | 28.204 |  | 43.902 | 1.088 | 1.2 | 0 | 1 | 17.0794 | 33.8448 | 0 | 50.9242 | LO
4LOWindows2019 | 2019 | Large Office | 4 | Windows |  | 0.36 | 0.36 | 0.36, 0.36 |  | 14.649 | 28.204 |  | 42.853 | 1.088 | 1.2 | 0 | 1 | 15.9381 | 33.8448 | 0 | 49.7829 | LO
5LOWindows2019 | 2019 | Large Office | 5 | Windows |  | 0.36 | 0.38 | 0.36, 0.38 |  | 14.364 | 28.204 |  | 42.568 | 1.088 | 1.2 | 0 | 1 | 15.628 | 33.8448 | 0 | 49.4728 | LO
6LOWindows2019 | 2019 | Large Office | 6 | Windows |  | 0.34 | 0.38 | 0.34, 0.38 |  | 14.537 | 28.204 |  | 42.741 | 1.088 | 1.2 | 0 | 1 | 15.8163 | 33.8448 | 0 | 49.6611 | LO
7LOWindows2019 | 2019 | Large Office | 7 | Windows |  | 0.29 | 0.4 | 0.29, 0.4 |  | 14.685 | 28.204 |  | 42.889 | 1.088 | 1.2 | 0 | 1 | 15.9773 | 33.8448 | 0 | 49.8221 | LO
8LOWindows2019 | 2019 | Large Office | 8 | Windows |  | 0.26 | 0.4 | 0.26, 0.4 |  | 14.945 | 28.204 |  | 43.149 | 1.088 | 1.2 | 0 | 1 | 16.2602 | 33.8448 | 0 | 50.105 | LO
1MAWindows2016 | 2016 | Mid-rise Apartment | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 24.803 | 21.323 |  | 46.126 | 1.088 | 1.2 | 0 | 1 | 26.9857 | 25.5876 | 0 | 52.5733 | MA
2MAWindows2016 | 2016 | Mid-rise Apartment | 2 | Windows |  | 0.53 | 0.25 | 0.53, 0.25 |  | 25.041 | 21.323 |  | 46.364 | 1.088 | 1.2 | 0 | 1 | 27.2446 | 25.5876 | 0 | 52.8322 | MA
3MAWindows2016 | 2016 | Mid-rise Apartment | 3 | Windows |  | 0.48 | 0.25 | 0.48, 0.25 |  | 25.338 | 21.323 |  | 46.661 | 1.088 | 1.2 | 0 | 1 | 27.5677 | 25.5876 | 0 | 53.1553 | MA
4MAWindows2016 | 2016 | Mid-rise Apartment | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 24.343 | 21.323 |  | 45.666 | 1.088 | 1.2 | 0 | 1 | 26.4852 | 25.5876 | 0 | 52.0728 | MA
5MAWindows2016 | 2016 | Mid-rise Apartment | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 24.054 | 21.323 |  | 45.377 | 1.088 | 1.2 | 0 | 1 | 26.1708 | 25.5876 | 0 | 51.7584 | MA
6MAWindows2016 | 2016 | Mid-rise Apartment | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 23.884 | 21.323 |  | 45.207 | 1.088 | 1.2 | 0 | 1 | 25.9858 | 25.5876 | 0 | 51.5734 | MA
7MAWindows2016 | 2016 | Mid-rise Apartment | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 23.339 | 21.323 |  | 44.662 | 1.088 | 1.2 | 0 | 1 | 25.3928 | 25.5876 | 0 | 50.9804 | MA
8MAWindows2016 | 2016 | Mid-rise Apartment | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 23.577 | 21.323 |  | 44.9 | 1.088 | 1.2 | 0 | 1 | 25.6518 | 25.5876 | 0 | 51.2394 | MA
1MAWindows2019 | 2019 | Mid-rise Apartment | 1 | Windows |  | 0.53 | 0.23 | 0.53, 0.23 |  | 25.33 | 21.323 |  | 46.653 | 1.088 | 1.2 | 0 | 1 | 27.559 | 25.5876 | 0 | 53.1466 | MA
2MAWindows2019 | 2019 | Mid-rise Apartment | 2 | Windows |  | 0.49 | 0.25 | 0.49, 0.25 |  | 25.278 | 21.323 |  | 46.601 | 1.088 | 1.2 | 0 | 1 | 27.5025 | 25.5876 | 0 | 53.0901 | MA
3MAWindows2019 | 2019 | Mid-rise Apartment | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 25.516 | 21.323 |  | 46.839 | 1.088 | 1.2 | 0 | 1 | 27.7614 | 25.5876 | 0 | 53.349 | MA
4MAWindows2019 | 2019 | Mid-rise Apartment | 4 | Windows |  | 0.38 | 0.35 | 0.38, 0.35 |  | 24.487 | 21.323 |  | 45.81 | 1.088 | 1.2 | 0 | 1 | 26.6419 | 25.5876 | 0 | 52.2295 | MA
5MAWindows2019 | 2019 | Mid-rise Apartment | 5 | Windows |  | 0.38 | 0.37 | 0.38, 0.37 |  | 24.198 | 21.323 |  | 45.521 | 1.088 | 1.2 | 0 | 1 | 26.3274 | 25.5876 | 0 | 51.915 | MA
6MAWindows2019 | 2019 | Mid-rise Apartment | 6 | Windows |  | 0.36 | 0.37 | 0.36, 0.37 |  | 24.317 | 21.323 |  | 45.64 | 1.088 | 1.2 | 0 | 1 | 26.4569 | 25.5876 | 0 | 52.0445 | MA
7MAWindows2019 | 2019 | Mid-rise Apartment | 7 | Windows |  | 0.31 | 0.39 | 0.31, 0.39 |  | 24.325 | 21.323 |  | 45.648 | 1.088 | 1.2 | 0 | 1 | 26.4656 | 25.5876 | 0 | 52.0532 | MA
8MAWindows2019 | 2019 | Mid-rise Apartment | 8 | Windows |  | 0.28 | 0.39 | 0.28, 0.39 |  | 24.504 | 21.323 |  | 45.827 | 1.088 | 1.2 | 0 | 1 | 26.6604 | 25.5876 | 0 | 52.248 | MA
1PSWindows2016 | 2016 | Primary School | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 21.089 | 23.642 |  | 44.731 | 1.088 | 1.2 | 0 | 1 | 22.9448 | 28.3704 | 0 | 51.3152 | PS
2PSWindows2016 | 2016 | Primary School | 2 | Windows |  | 0.53 | 0.25 | 0.53, 0.25 |  | 21.407 | 23.642 |  | 45.049 | 1.088 | 1.2 | 0 | 1 | 23.2908 | 28.3704 | 0 | 51.6612 | PS
3PSWindows2016 | 2016 | Primary School | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 22.042 | 23.642 |  | 45.684 | 1.088 | 1.2 | 0 | 1 | 23.9817 | 28.3704 | 0 | 52.3521 | PS
4PSWindows2016 | 2016 | Primary School | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 21.178 | 23.642 |  | 44.82 | 1.088 | 1.2 | 0 | 1 | 23.0417 | 28.3704 | 0 | 51.4121 | PS
5PSWindows2016 | 2016 | Primary School | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 20.92 | 23.642 |  | 44.562 | 1.088 | 1.2 | 0 | 1 | 22.761 | 28.3704 | 0 | 51.1314 | PS
6PSWindows2016 | 2016 | Primary School | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 20.821 | 23.642 |  | 44.463 | 1.088 | 1.2 | 0 | 1 | 22.6532 | 28.3704 | 0 | 51.0236 | PS
7PSWindows2016 | 2016 | Primary School | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 20.413 | 23.642 |  | 44.055 | 1.088 | 1.2 | 0 | 1 | 22.2093 | 28.3704 | 0 | 50.5797 | PS
8PSWindows2016 | 2016 | Primary School | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 20.731 | 23.642 |  | 44.373 | 1.088 | 1.2 | 0 | 1 | 22.5553 | 28.3704 | 0 | 50.9257 | PS
1PSWindows2019 | 2019 | Primary School | 1 | Windows |  | 0.51 | 0.23 | 0.51, 0.23 |  | 21.824 | 23.642 |  | 45.466 | 1.088 | 1.2 | 0 | 1 | 23.7445 | 28.3704 | 0 | 52.1149 | PS
2PSWindows2019 | 2019 | Primary School | 2 | Windows |  | 0.47 | 0.25 | 0.47, 0.25 |  | 21.883 | 23.642 |  | 45.525 | 1.088 | 1.2 | 0 | 1 | 23.8087 | 28.3704 | 0 | 52.1791 | PS
3PSWindows2019 | 2019 | Primary School | 3 | Windows |  | 0.43 | 0.25 | 0.43, 0.25 |  | 22.201 | 23.642 |  | 45.843 | 1.088 | 1.2 | 0 | 1 | 24.1547 | 28.3704 | 0 | 52.5251 | PS
4PSWindows2019 | 2019 | Primary School | 4 | Windows |  | 0.37 | 0.36 | 0.37, 0.36 |  | 21.258 | 23.642 |  | 44.9 | 1.088 | 1.2 | 0 | 1 | 23.1287 | 28.3704 | 0 | 51.4991 | PS
5PSWindows2019 | 2019 | Primary School | 5 | Windows |  | 0.37 | 0.38 | 0.37, 0.38 |  | 20.999 | 23.642 |  | 44.641 | 1.088 | 1.2 | 0 | 1 | 22.8469 | 28.3704 | 0 | 51.2173 | PS
6PSWindows2019 | 2019 | Primary School | 6 | Windows |  | 0.35 | 0.38 | 0.35, 0.38 |  | 21.158 | 23.642 |  | 44.8 | 1.088 | 1.2 | 0 | 1 | 23.0199 | 28.3704 | 0 | 51.3903 | PS
7PSWindows2019 | 2019 | Primary School | 7 | Windows |  | 0.3 | 0.4 | 0.3, 0.4 |  | 21.297 | 23.642 |  | 44.939 | 1.088 | 1.2 | 0 | 1 | 23.1711 | 28.3704 | 0 | 51.5415 | PS
8PSWindows2019 | 2019 | Primary School | 8 | Windows |  | 0.27 | 0.4 | 0.27, 0.4 |  | 21.536 | 23.642 |  | 45.178 | 1.088 | 1.2 | 0 | 1 | 23.4312 | 28.3704 | 0 | 51.8016 | PS
1SHWindows2016 | 2016 | Small Hotel | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 17.917 | 25.965 |  | 43.882 | 1.088 | 1.2 | 0 | 1 | 19.4937 | 31.158 | 0 | 50.6517 | SH
2SHWindows2016 | 2016 | Small Hotel | 2 | Windows |  | 0.54 | 0.25 | 0.54, 0.25 |  | 18.126 | 25.965 |  | 44.091 | 1.088 | 1.2 | 0 | 1 | 19.7211 | 31.158 | 0 | 50.8791 | SH
3SHWindows2016 | 2016 | Small Hotel | 3 | Windows |  | 0.49 | 0.25 | 0.49, 0.25 |  | 18.475 | 25.965 |  | 44.44 | 1.088 | 1.2 | 0 | 1 | 20.1008 | 31.158 | 0 | 51.2588 | SH
4SHWindows2016 | 2016 | Small Hotel | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 17.455 | 25.965 |  | 43.42 | 1.088 | 1.2 | 0 | 1 | 18.991 | 31.158 | 0 | 50.149 | SH
5SHWindows2016 | 2016 | Small Hotel | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 17.131 | 25.965 |  | 43.096 | 1.088 | 1.2 | 0 | 1 | 18.6385 | 31.158 | 0 | 49.7965 | SH
6SHWindows2016 | 2016 | Small Hotel | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 16.945 | 25.965 |  | 42.91 | 1.088 | 1.2 | 0 | 1 | 18.4362 | 31.158 | 0 | 49.5942 | SH
7SHWindows2016 | 2016 | Small Hotel | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 16.343 | 25.965 |  | 42.308 | 1.088 | 1.2 | 0 | 1 | 17.7812 | 31.158 | 0 | 48.9392 | SH
8SHWindows2016 | 2016 | Small Hotel | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 16.621 | 25.965 |  | 42.586 | 1.088 | 1.2 | 0 | 1 | 18.0836 | 31.158 | 0 | 49.2416 | SH
1SHWindows2019 | 2019 | Small Hotel | 1 | Windows |  | 0.51 | 0.23 | 0.51, 0.23 |  | 18.66 | 25.965 |  | 44.625 | 1.088 | 1.2 | 0 | 1 | 20.3021 | 31.158 | 0 | 51.4601 | SH
2SHWindows2019 | 2019 | Small Hotel | 2 | Windows |  | 0.46 | 0.25 | 0.46, 0.25 |  | 18.684 | 25.965 |  | 44.649 | 1.088 | 1.2 | 0 | 1 | 20.3282 | 31.158 | 0 | 51.4862 | SH
3SHWindows2019 | 2019 | Small Hotel | 3 | Windows |  | 0.43 | 0.25 | 0.43, 0.25 |  | 18.893 | 25.965 |  | 44.858 | 1.088 | 1.2 | 0 | 1 | 20.5556 | 31.158 | 0 | 51.7136 | SH
4SHWindows2019 | 2019 | Small Hotel | 4 | Windows |  | 0.37 | 0.36 | 0.37, 0.36 |  | 17.525 | 25.965 |  | 43.49 | 1.088 | 1.2 | 0 | 1 | 19.0672 | 31.158 | 0 | 50.2252 | SH
5SHWindows2019 | 2019 | Small Hotel | 5 | Windows |  | 0.37 | 0.38 | 0.37, 0.38 |  | 17.2 | 25.965 |  | 43.165 | 1.088 | 1.2 | 0 | 1 | 18.7136 | 31.158 | 0 | 49.8716 | SH
6SHWindows2019 | 2019 | Small Hotel | 6 | Windows |  | 0.35 | 0.38 | 0.35, 0.38 |  | 17.34 | 25.965 |  | 43.305 | 1.088 | 1.2 | 0 | 1 | 18.8659 | 31.158 | 0 | 50.0239 | SH
7SHWindows2019 | 2019 | Small Hotel | 7 | Windows |  | 0.3 | 0.4 | 0.3, 0.4 |  | 17.363 | 25.965 |  | 43.328 | 1.088 | 1.2 | 0 | 1 | 18.8909 | 31.158 | 0 | 50.0489 | SH
8SHWindows2019 | 2019 | Small Hotel | 8 | Windows |  | 0.27 | 0.4 | 0.27, 0.4 |  | 17.572 | 25.965 |  | 43.537 | 1.088 | 1.2 | 0 | 1 | 19.1183 | 31.158 | 0 | 50.2763 | SH
1SHNRWindows2016 | 2016 | Small Hotel - Non-res | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 17.917 | 25.965 |  | 43.882 | 1.088 | 1.2 | 0 | 1 | 19.4937 | 31.158 | 0 | 50.6517 | SHNR
2SHNRWindows2016 | 2016 | Small Hotel - Non-res | 2 | Windows |  | 0.54 | 0.25 | 0.54, 0.25 |  | 18.126 | 25.965 |  | 44.091 | 1.088 | 1.2 | 0 | 1 | 19.7211 | 31.158 | 0 | 50.8791 | SHNR
3SHNRWindows2016 | 2016 | Small Hotel - Non-res | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 18.753 | 25.965 |  | 44.718 | 1.088 | 1.2 | 0 | 1 | 20.4033 | 31.158 | 0 | 51.5613 | SHNR
4SHNRWindows2016 | 2016 | Small Hotel - Non-res | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 17.455 | 25.965 |  | 43.42 | 1.088 | 1.2 | 0 | 1 | 18.991 | 31.158 | 0 | 50.149 | SHNR
5SHNRWindows2016 | 2016 | Small Hotel - Non-res | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 17.131 | 25.965 |  | 43.096 | 1.088 | 1.2 | 0 | 1 | 18.6385 | 31.158 | 0 | 49.7965 | SHNR
6SHNRWindows2016 | 2016 | Small Hotel - Non-res | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 16.945 | 25.965 |  | 42.91 | 1.088 | 1.2 | 0 | 1 | 18.4362 | 31.158 | 0 | 49.5942 | SHNR
7SHNRWindows2016 | 2016 | Small Hotel - Non-res | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 16.343 | 25.965 |  | 42.308 | 1.088 | 1.2 | 0 | 1 | 17.7812 | 31.158 | 0 | 48.9392 | SHNR
8SHNRWindows2016 | 2016 | Small Hotel - Non-res | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 16.621 | 25.965 |  | 42.586 | 1.088 | 1.2 | 0 | 1 | 18.0836 | 31.158 | 0 | 49.2416 | SHNR
1SHNRWindows2019 | 2019 | Small Hotel - Non-res | 1 | Windows |  | 0.51 | 0.23 | 0.51, 0.23 |  | 18.66 | 25.965 |  | 44.625 | 1.088 | 1.2 | 0 | 1 | 20.3021 | 31.158 | 0 | 51.4601 | SHNR
2SHNRWindows2019 | 2019 | Small Hotel - Non-res | 2 | Windows |  | 0.46 | 0.25 | 0.46, 0.25 |  | 18.684 | 25.965 |  | 44.649 | 1.088 | 1.2 | 0 | 1 | 20.3282 | 31.158 | 0 | 51.4862 | SHNR
3SHNRWindows2019 | 2019 | Small Hotel - Non-res | 3 | Windows |  | 0.43 | 0.25 | 0.43, 0.25 |  | 18.893 | 25.965 |  | 44.858 | 1.088 | 1.2 | 0 | 1 | 20.5556 | 31.158 | 0 | 51.7136 | SHNR
4SHNRWindows2019 | 2019 | Small Hotel - Non-res | 4 | Windows |  | 0.37 | 0.36 | 0.37, 0.36 |  | 17.525 | 25.965 |  | 43.49 | 1.088 | 1.2 | 0 | 1 | 19.0672 | 31.158 | 0 | 50.2252 | SHNR
5SHNRWindows2019 | 2019 | Small Hotel - Non-res | 5 | Windows |  | 0.37 | 0.38 | 0.37, 0.38 |  | 17.2 | 25.965 |  | 43.165 | 1.088 | 1.2 | 0 | 1 | 18.7136 | 31.158 | 0 | 49.8716 | SHNR
6SHNRWindows2019 | 2019 | Small Hotel - Non-res | 6 | Windows |  | 0.35 | 0.38 | 0.35, 0.38 |  | 17.34 | 25.965 |  | 43.305 | 1.088 | 1.2 | 0 | 1 | 18.8659 | 31.158 | 0 | 50.0239 | SHNR
7SHNRWindows2019 | 2019 | Small Hotel - Non-res | 7 | Windows |  | 0.3 | 0.4 | 0.3, 0.4 |  | 17.363 | 25.965 |  | 43.328 | 1.088 | 1.2 | 0 | 1 | 18.8909 | 31.158 | 0 | 50.0489 | SHNR
8SHNRWindows2019 | 2019 | Small Hotel - Non-res | 8 | Windows |  | 0.27 | 0.4 | 0.27, 0.4 |  | 17.572 | 25.965 |  | 43.537 | 1.088 | 1.2 | 0 | 1 | 19.1183 | 31.158 | 0 | 50.2763 | SHNR
1SOWindows2016 | 2016 | Small Office | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 14.399 | 28.204 |  | 42.603 | 1.088 | 1.2 | 0 | 1 | 15.6661 | 33.8448 | 0 | 49.5109 | SO
2SOWindows2016 | 2016 | Small Office | 2 | Windows |  | 0.54 | 0.25 | 0.54, 0.25 |  | 14.659 | 28.204 |  | 42.863 | 1.088 | 1.2 | 0 | 1 | 15.949 | 33.8448 | 0 | 49.7938 | SO
3SOWindows2016 | 2016 | Small Office | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 15.438 | 28.204 |  | 43.642 | 1.088 | 1.2 | 0 | 1 | 16.7965 | 33.8448 | 0 | 50.6413 | SO
4SOWindows2016 | 2016 | Small Office | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 14.476 | 28.204 |  | 42.68 | 1.088 | 1.2 | 0 | 1 | 15.7499 | 33.8448 | 0 | 49.5947 | SO
5SOWindows2016 | 2016 | Small Office | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 14.191 | 28.204 |  | 42.395 | 1.088 | 1.2 | 0 | 1 | 15.4398 | 33.8448 | 0 | 49.2846 | SO
6SOWindows2016 | 2016 | Small Office | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 14.079 | 28.204 |  | 42.283 | 1.088 | 1.2 | 0 | 1 | 15.318 | 33.8448 | 0 | 49.1628 | SO
7SOWindows2016 | 2016 | Small Office | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 13.626 | 28.204 |  | 41.83 | 1.088 | 1.2 | 0 | 1 | 14.8251 | 33.8448 | 0 | 48.6699 | SO
8SOWindows2016 | 2016 | Small Office | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 13.972 | 28.204 |  | 42.176 | 1.088 | 1.2 | 0 | 1 | 15.2015 | 33.8448 | 0 | 49.0463 | SO
1SOWindows2019 | 2019 | Small Office | 1 | Windows |  | 0.5 | 0.23 | 0.5, 0.23 |  | 15.291 | 28.204 |  | 43.495 | 1.088 | 1.2 | 0 | 1 | 16.6366 | 33.8448 | 0 | 50.4814 | SO
2SOWindows2019 | 2019 | Small Office | 2 | Windows |  | 0.46 | 0.25 | 0.46, 0.25 |  | 15.352 | 28.204 |  | 43.556 | 1.088 | 1.2 | 0 | 1 | 16.703 | 33.8448 | 0 | 50.5478 | SO
3SOWindows2019 | 2019 | Small Office | 3 | Windows |  | 0.42 | 0.25 | 0.42, 0.25 |  | 15.698 | 28.204 |  | 43.902 | 1.088 | 1.2 | 0 | 1 | 17.0794 | 33.8448 | 0 | 50.9242 | SO
4SOWindows2019 | 2019 | Small Office | 4 | Windows |  | 0.36 | 0.36 | 0.36, 0.36 |  | 14.649 | 28.204 |  | 42.853 | 1.088 | 1.2 | 0 | 1 | 15.9381 | 33.8448 | 0 | 49.7829 | SO
5SOWindows2019 | 2019 | Small Office | 5 | Windows |  | 0.36 | 0.38 | 0.36, 0.38 |  | 14.364 | 28.204 |  | 42.568 | 1.088 | 1.2 | 0 | 1 | 15.628 | 33.8448 | 0 | 49.4728 | SO
6SOWindows2019 | 2019 | Small Office | 6 | Windows |  | 0.34 | 0.38 | 0.34, 0.38 |  | 14.537 | 28.204 |  | 42.741 | 1.088 | 1.2 | 0 | 1 | 15.8163 | 33.8448 | 0 | 49.6611 | SO
7SOWindows2019 | 2019 | Small Office | 7 | Windows |  | 0.29 | 0.4 | 0.29, 0.4 |  | 14.685 | 28.204 |  | 42.889 | 1.088 | 1.2 | 0 | 1 | 15.9773 | 33.8448 | 0 | 49.8221 | SO
8SOWindows2019 | 2019 | Small Office | 8 | Windows |  | 0.26 | 0.4 | 0.26, 0.4 |  | 14.945 | 28.204 |  | 43.149 | 1.088 | 1.2 | 0 | 1 | 16.2602 | 33.8448 | 0 | 50.105 | SO
1SRWindows2016 | 2016 | Stand-alone Retail | 1 | Windows |  | 0.57 | 0.25 | 0.57, 0.25 |  | 17.257 | 26.498 |  | 43.755 | 1.088 | 1.2 | 0 | 1 | 18.7756 | 31.7976 | 0 | 50.5732 | SR
2SRWindows2016 | 2016 | Stand-alone Retail | 2 | Windows |  | 0.54 | 0.25 | 0.54, 0.25 |  | 17.519 | 26.498 |  | 44.017 | 1.088 | 1.2 | 0 | 1 | 19.0607 | 31.7976 | 0 | 50.8583 | SR
3SRWindows2016 | 2016 | Stand-alone Retail | 3 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 18.305 | 26.498 |  | 44.803 | 1.088 | 1.2 | 0 | 1 | 19.9158 | 31.7976 | 0 | 51.7134 | SR
4SRWindows2016 | 2016 | Stand-alone Retail | 4 | Windows |  | 0.38 | 0.36 | 0.38, 0.36 |  | 17.47 | 26.498 |  | 43.968 | 1.088 | 1.2 | 0 | 1 | 19.0074 | 31.7976 | 0 | 50.805 | SR
5SRWindows2016 | 2016 | Stand-alone Retail | 5 | Windows |  | 0.38 | 0.38 | 0.38, 0.38 |  | 17.207 | 26.498 |  | 43.705 | 1.088 | 1.2 | 0 | 1 | 18.7212 | 31.7976 | 0 | 50.5188 | SR
6SRWindows2016 | 2016 | Stand-alone Retail | 6 | Windows |  | 0.36 | 0.4 | 0.36, 0.4 |  | 17.119 | 26.498 |  | 43.617 | 1.088 | 1.2 | 0 | 1 | 18.6255 | 31.7976 | 0 | 50.4231 | SR
7SRWindows2016 | 2016 | Stand-alone Retail | 7 | Windows |  | 0.33 | 0.45 | 0.33, 0.45 |  | 16.724 | 26.498 |  | 43.222 | 1.088 | 1.2 | 0 | 1 | 18.1957 | 31.7976 | 0 | 49.9933 | SR
8SRWindows2016 | 2016 | Stand-alone Retail | 8 | Windows |  | 0.29 | 0.45 | 0.29, 0.45 |  | 17.073 | 26.498 |  | 43.571 | 1.088 | 1.2 | 0 | 1 | 18.5754 | 31.7976 | 0 | 50.373 | SR
1SRWindows2019 | 2019 | Stand-alone Retail | 1 | Windows |  | 0.5 | 0.23 | 0.5, 0.23 |  | 18.131 | 26.498 |  | 44.629 | 1.088 | 1.2 | 0 | 1 | 19.7265 | 31.7976 | 0 | 51.5241 | SR
2SRWindows2019 | 2019 | Stand-alone Retail | 2 | Windows |  | 0.45 | 0.25 | 0.45, 0.25 |  | 18.305 | 26.498 |  | 44.803 | 1.088 | 1.2 | 0 | 1 | 19.9158 | 31.7976 | 0 | 51.7134 | SR
3SRWindows2019 | 2019 | Stand-alone Retail | 3 | Windows |  | 0.42 | 0.25 | 0.42, 0.25 |  | 18.567 | 26.498 |  | 45.065 | 1.088 | 1.2 | 0 | 1 | 20.2009 | 31.7976 | 0 | 51.9985 | SR
4SRWindows2019 | 2019 | Stand-alone Retail | 4 | Windows |  | 0.36 | 0.36 | 0.36, 0.36 |  | 17.645 | 26.498 |  | 44.143 | 1.088 | 1.2 | 0 | 1 | 19.1978 | 31.7976 | 0 | 50.9954 | SR
5SRWindows2019 | 2019 | Stand-alone Retail | 5 | Windows |  | 0.36 | 0.38 | 0.36, 0.38 |  | 17.382 | 26.498 |  | 43.88 | 1.088 | 1.2 | 0 | 1 | 18.9116 | 31.7976 | 0 | 50.7092 | SR
6SRWindows2019 | 2019 | Stand-alone Retail | 6 | Windows |  | 0.34 | 0.38 | 0.34, 0.38 |  | 17.557 | 26.498 |  | 44.055 | 1.088 | 1.2 | 0 | 1 | 19.102 | 31.7976 | 0 | 50.8996 | SR
7SRWindows2019 | 2019 | Stand-alone Retail | 7 | Windows |  | 0.29 | 0.4 | 0.29, 0.4 |  | 17.731 | 26.498 |  | 44.229 | 1.088 | 1.2 | 0 | 1 | 19.2913 | 31.7976 | 0 | 51.0889 | SR
8SRWindows2019 | 2019 | Stand-alone Retail | 8 | Windows |  | 0.26 | 0.4 | 0.26, 0.4 |  | 17.993 | 26.498 |  | 44.491 | 1.088 | 1.2 | 0 | 1 | 19.5764 | 31.7976 | 0 | 51.374 | SR
1PSSkylights2016 | 2016 | Primary School | 1 | Skylights |  | 0.75 | 0.35 | 0.75, 0.35 |  | 25.179 | 38.177 |  | 63.356 | 1.123 | 1.195 | 0 | 1 | 28.276 | 45.6215 | 0 | 73.8975 | PS
2PSSkylights2016 | 2016 | Primary School | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 25.834 | 38.177 |  | 64.011 | 1.123 | 1.195 | 0 | 1 | 29.0116 | 45.6215 | 0 | 74.6331 | PS
3PSSkylights2016 | 2016 | Primary School | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 26.49 | 54.959 |  | 81.449 | 1.123 | 1.195 | 0 | 1 | 29.7483 | 65.676 | 0 | 95.4243 | PS
4PSSkylights2016 | 2016 | Primary School | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
5PSSkylights2016 | 2016 | Primary School | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
6PSSkylights2016 | 2016 | Primary School | 6 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
7PSSkylights2016 | 2016 | Primary School | 7 | Skylights |  | 0.5 | 0.55 | 0.5, 0.55 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
8PSSkylights2016 | 2016 | Primary School | 8 | Skylights |  | 0.41 | 0.55 | 0.41, 0.55 |  | 27.407 | 54.959 |  | 82.366 | 1.123 | 1.195 | 0 | 1 | 30.7781 | 65.676 | 0 | 96.4541 | PS
1PSSkylights2019 | 2019 | Primary School | 1 | Skylights |  | 0.7 | 0.3 | 0.7, 0.3 |  | 25.507 | 38.177 |  | 63.684 | 1.123 | 1.195 | 0 | 1 | 28.6444 | 45.6215 | 0 | 74.2659 | PS
2PSSkylights2019 | 2019 | Primary School | 2 | Skylights |  | 0.65 | 0.3 | 0.65, 0.3 |  | 25.834 | 38.177 |  | 64.011 | 1.123 | 1.195 | 0 | 1 | 29.0116 | 45.6215 | 0 | 74.6331 | PS
3PSSkylights2019 | 2019 | Primary School | 3 | Skylights |  | 0.55 | 0.3 | 0.55, 0.3 |  | 26.49 | 54.959 |  | 81.449 | 1.123 | 1.195 | 0 | 1 | 29.7483 | 65.676 | 0 | 95.4243 | PS
4PSSkylights2019 | 2019 | Primary School | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
5PSSkylights2019 | 2019 | Primary School | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 26.817 | 54.959 |  | 81.776 | 1.123 | 1.195 | 0 | 1 | 30.1155 | 65.676 | 0 | 95.7915 | PS
6PSSkylights2019 | 2019 | Primary School | 6 | Skylights |  | 0.47 | 0.4 | 0.47, 0.4 |  | 27.014 | 54.959 |  | 81.973 | 1.123 | 1.195 | 0 | 1 | 30.3367 | 65.676 | 0 | 96.0127 | PS
7PSSkylights2019 | 2019 | Primary School | 7 | Skylights |  | 0.44 | 0.55 | 0.44, 0.55 |  | 27.21 | 54.959 |  | 82.169 | 1.123 | 1.195 | 0 | 1 | 30.5568 | 65.676 | 0 | 96.2328 | PS
8PSSkylights2019 | 2019 | Primary School | 8 | Skylights |  | 0.41 | 0.55 | 0.41, 0.55 |  | 27.407 | 54.959 |  | 82.366 | 1.123 | 1.195 | 0 | 1 | 30.7781 | 65.676 | 0 | 96.4541 | PS
1SRSkylights2016 | 2016 | Stand-alone Retail | 1 | Skylights |  | 0.75 | 0.35 | 0.75, 0.35 |  | 17.302 | 57.815 |  | 75.117 | 1.123 | 1.195 | 0 | 1 | 19.4301 | 69.0889 | 0 | 88.5191 | SR
2SRSkylights2016 | 2016 | Stand-alone Retail | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 22.427 | 58.055 |  | 80.482 | 1.123 | 1.195 | 0 | 1 | 25.1855 | 69.3757 | 0 | 94.5612 | SR
3SRSkylights2016 | 2016 | Stand-alone Retail | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 27.552 | 78.972 |  | 106.524 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 94.3715 | 0 | 125.3124 | SR
4SRSkylights2016 | 2016 | Stand-alone Retail | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 27.552 | 79.812 |  | 107.364 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 95.3753 | 0 | 126.3162 | SR
5SRSkylights2016 | 2016 | Stand-alone Retail | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 27.552 | 79.812 |  | 107.364 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 95.3753 | 0 | 126.3162 | SR
6SRSkylights2016 | 2016 | Stand-alone Retail | 6 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 27.552 | 79.812 |  | 107.364 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 95.3753 | 0 | 126.3162 | SR
7SRSkylights2016 | 2016 | Stand-alone Retail | 7 | Skylights |  | 0.5 | 0.55 | 0.5, 0.55 |  | 19.865 | 79.812 |  | 99.677 | 1.123 | 1.195 | 0 | 1 | 22.3084 | 95.3753 | 0 | 117.6837 | SR
8SRSkylights2016 | 2016 | Stand-alone Retail | 8 | Skylights |  | 0.41 | 0.55 | 0.41, 0.55 |  | 24.477 | 79.812 |  | 104.289 | 1.123 | 1.195 | 0 | 1 | 27.4877 | 95.3753 | 0 | 122.863 | SR
1SRSkylights2019 | 2019 | Stand-alone Retail | 1 | Skylights |  | 0.7 | 0.3 | 0.7, 0.3 |  | 22.427 | 57.815 |  | 80.242 | 1.123 | 1.195 | 0 | 1 | 25.1855 | 69.0889 | 0 | 94.2744 | SR
2SRSkylights2019 | 2019 | Stand-alone Retail | 2 | Skylights |  | 0.65 | 0.3 | 0.65, 0.3 |  | 24.989 | 58.055 |  | 83.044 | 1.123 | 1.195 | 0 | 1 | 28.0626 | 69.3757 | 0 | 97.4384 | SR
3SRSkylights2019 | 2019 | Stand-alone Retail | 3 | Skylights |  | 0.55 | 0.3 | 0.55, 0.3 |  | 30.114 | 78.972 |  | 109.086 | 1.123 | 1.195 | 0 | 1 | 33.818 | 94.3715 | 0 | 128.1896 | SR
4SRSkylights2019 | 2019 | Stand-alone Retail | 4 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 27.552 | 79.812 |  | 107.364 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 95.3753 | 0 | 126.3162 | SR
5SRSkylights2019 | 2019 | Stand-alone Retail | 5 | Skylights |  | 0.5 | 0.4 | 0.5, 0.4 |  | 27.552 | 79.812 |  | 107.364 | 1.123 | 1.195 | 0 | 1 | 30.9409 | 95.3753 | 0 | 126.3162 | SR
6SRSkylights2019 | 2019 | Stand-alone Retail | 6 | Skylights |  | 0.47 | 0.4 | 0.47, 0.4 |  | 29.089 | 79.812 |  | 108.901 | 1.123 | 1.195 | 0 | 1 | 32.6669 | 95.3753 | 0 | 128.0423 | SR
7SRSkylights2019 | 2019 | Stand-alone Retail | 7 | Skylights |  | 0.44 | 0.55 | 0.44, 0.55 |  | 22.94 | 79.812 |  | 102.752 | 1.123 | 1.195 | 0 | 1 | 25.7616 | 95.3753 | 0 | 121.137 | SR
8SRSkylights2019 | 2019 | Stand-alone Retail | 8 | Skylights |  | 0.41 | 0.55 | 0.41, 0.55 |  | 24.477 | 79.812 |  | 104.289 | 1.123 | 1.195 | 0 | 1 | 27.4877 | 95.3753 | 0 | 122.863 | SR
1SRSkylights2013 | 2013 | Stand-alone Retail | 1 | Skylights |  | 0.75 | 0.35 | 0.75, 0.35 |  | 22.4271 | 57.8153 |  | 80.2424 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 69.0893 | 0 | 80.2424 | SR
2SRSkylights2013 | 2013 | Stand-alone Retail | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 22.4271 | 58.0553 |  | 80.4824 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 69.3761 | 0 | 80.4824 | SR
3SRSkylights2013 | 2013 | Stand-alone Retail | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 27.5518 | 78.9717 |  | 106.5235 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 94.3712 | 0 | 106.5235 | SR
4SRSkylights2013 | 2013 | Stand-alone Retail | 4 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | SR
5SRSkylights2013 | 2013 | Stand-alone Retail | 5 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | SR
6SRSkylights2013 | 2013 | Stand-alone Retail | 6 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | SR
7SRSkylights2013 | 2013 | Stand-alone Retail | 7 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | SR
8SRSkylights2013 | 2013 | Stand-alone Retail | 8 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | SR
1PSSkylights2010 | 2010 | Primary School | 1 | Skylights |  | 1.98 | 0.36 | 1.98, 0.36 |  | 17.1196 | 38.1774 |  | 55.2971 | 1.123 | 1.195 | 0 | 1 | 19.2254 | 45.622 | 0 | 55.2971 | PS
2PSSkylights2010 | 2010 | Primary School | 2 | Skylights |  | 1.98 | 0.36 | 1.98, 0.36 |  | 17.1196 | 38.1774 |  | 55.2971 | 1.123 | 1.195 | 0 | 1 | 19.2254 | 45.622 | 0 | 55.2971 | PS
3PSSkylights2010 | 2010 | Primary School | 3 | Skylights |  | 1.17 | 0.39 | 1.17, 0.39 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
4PSSkylights2010 | 2010 | Primary School | 4 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
5PSSkylights2010 | 2010 | Primary School | 5 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
6PSSkylights2010 | 2010 | Primary School | 6 | Skylights |  | 1.17 | 0.49 | 1.17, 0.49 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
7PSSkylights2010 | 2010 | Primary School | 7 | Skylights |  | 1.17 | 0.68 | 1.17, 0.68 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
8PSSkylights2010 | 2010 | Primary School | 8 | Skylights |  | 1.17 | 0.68 | 1.17, 0.68 |  | 22.4271 | 54.9593 |  | 77.3864 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 65.6764 | 0 | 77.3864 | PS
1PSSkylights2013 | 2013 | Primary School | 1 | Skylights |  | 0.75 | 0.35 | 0.75, 0.35 |  | 22.4271 | 57.8153 |  | 80.2424 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 69.0893 | 0 | 80.2424 | PS
2PSSkylights2013 | 2013 | Primary School | 2 | Skylights |  | 0.65 | 0.35 | 0.65, 0.35 |  | 22.4271 | 58.0553 |  | 80.4824 | 1.123 | 1.195 | 0 | 1 | 25.1856 | 69.3761 | 0 | 80.4824 | PS
3PSSkylights2013 | 2013 | Primary School | 3 | Skylights |  | 0.55 | 0.35 | 0.55, 0.35 |  | 27.5518 | 78.9717 |  | 106.5235 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 94.3712 | 0 | 106.5235 | PS
4PSSkylights2013 | 2013 | Primary School | 4 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | PS
5PSSkylights2013 | 2013 | Primary School | 5 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | PS
6PSSkylights2013 | 2013 | Primary School | 6 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | PS
7PSSkylights2013 | 2013 | Primary School | 7 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | PS
8PSSkylights2013 | 2013 | Primary School | 8 | Skylights |  | 0.5 | 0.4 | 0.50, 0.40 |  | 27.5518 | 79.8117 |  | 107.3635 | 1.123 | 1.195 | 0 | 1 | 30.9407 | 95.375 | 0 | 107.3635 | PS
21sf_Door_0.7unins |  |  |  | Doors |  | 0.7 |  |  |  | 455 | 47.5 |  | 502.5 | 1 | 1 | 1 |  | 455 | 47.5 | 0 | 502.5
21sf_Door_0.5_insPS |  |  |  | Doors |  | 0.5 |  |  |  | 476.33 | 47.5 |  | 523.83 | 1 | 1 | 1 |  | 476.33 | 47.5 | 0 | 523.83
21sf_Door_0.37_insPU |  |  |  | Doors |  | 0.37 |  |  |  | 483.3689 | 47.5 |  | 530.8689 | 1 | 1 | 1 |  | 483.3689 | 47.5 | 0 | 530.8689
80sf_RU_Door_0.5_insPS |  |  |  | Doors |  | 0.5 |  |  |  | 925 | 585 |  | 1510 | 1 | 1 | 1 |  | 925 | 585 | 0 | 1510
80sf_RU_Door_0.31_insPU |  |  |  | Doors |  | 0.31 |  |  |  | 1006.27 | 666.27 |  | 1672.54 | 1 | 1 | 1 |  | 1006.27 | 666.27 | 0 | 1672.54

## Env_Summary
Envelope, Power and Other Items - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
CZ_1 | 2A | [6 empty] | CZ_1 | 2A | [6 empty] | CZ_1 | 2A | [6 empty] | CZ_1 | 2A | [6 empty] | CZ_1 | 2A | [6 empty] | CZ_1 | 2A
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 4388 | 4388 | 4388 | 4388 | New Construction | 0 | 0 | New Construction | 600594 | 600594 | 600594 | 600594 | New Construction | 0 | 0 | New Construction | 35588 | 35588 | 35588 | 35588 | New Construction | 0 | 0 | New Construction | 94496 | 94496 | 94496 | 94496 | New Construction | 0 | 0 | New Construction | 69719 | 69719 | 69719 | 69719 | New Construction | 0 | 0 | New Construction | 45405 | 45405 | 45405 | 45405
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
CZ_2 | 3A | [6 empty] | CZ_2 | 3A | [6 empty] | CZ_2 | 3A | [6 empty] | CZ_2 | 3A | [6 empty] | CZ_2 | 3A | [6 empty] | CZ_2 | 3A
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 4388 | 4388 | 4388 | 4388 | New Construction | 0 | 0 | New Construction | 600594 | 600594 | 600594 | 600594 | New Construction | 0 | 0 | New Construction | 35588 | 35588 | 35588 | 35588 | New Construction | 0 | 0 | New Construction | 94496 | 94496 | 94496 | 94496 | New Construction | 0 | 0 | New Construction | 66558 | 66558 | 66558 | 66558 | New Construction | 0 | 0 | New Construction | 45405 | 45405 | 45405 | 45405
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
CZ_3 | 3B | [6 empty] | CZ_3 | 3B | [6 empty] | CZ_3 | 3B | [6 empty] | CZ_3 | 3B | [6 empty] | CZ_3 | 3B | [6 empty] | CZ_3 | 3B
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 4388 | 4388 | 4388 | 4388 | New Construction | 0 | 0 | New Construction | 600594 | 600594 | 600594 | 600594 | New Construction | 0 | 0 | New Construction | 35588 | 35588 | 35588 | 35588 | New Construction | 0 | 0 | New Construction | 94496 | 94496 | 94496 | 94496 | New Construction | 0 | 0 | New Construction | 66558 | 66558 | 66558 | 66558 | New Construction | 0 | 0 | New Construction | 45405 | 45405 | 45405 | 45405
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
CZ_4 | 4A | [6 empty] | CZ_4 | 4A | [6 empty] | CZ_4 | 4A | [6 empty] | CZ_4 | 4A | [6 empty] | CZ_4 | 4A | [6 empty] | CZ_4 | 4A
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 6148 | 6148 | 6148 | 6148 | New Construction | 0 | 0 | New Construction | 628852 | 628852 | 628852 | 628852 | New Construction | 0 | 0 | New Construction | 38691 | 38691 | 38691 | 38691 | New Construction | 0 | 0 | New Construction | 117289 | 117289 | 117289 | 117289 | New Construction | 0 | 0 | New Construction | 70715 | 70715 | 70715 | 70715 | New Construction | 0 | 0 | New Construction | 50460 | 50460 | 50460 | 50460
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
CZ_5 | 5A | [6 empty] | CZ_5 | 5A | [6 empty] | CZ_5 | 5A | [6 empty] | CZ_5 | 5A | [6 empty] | CZ_5 | 5A | [6 empty] | CZ_5 | 5A
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 6148 | 6148 | 6148 | 6148 | New Construction | 0 | 0 | New Construction | 628852 | 628852 | 628852 | 628852 | New Construction | 0 | 0 | New Construction | 38691 | 38691 | 38691 | 38691 | New Construction | 0 | 0 | New Construction | 117289 | 117289 | 117289 | 117289 | New Construction | 0 | 0 | New Construction | 70715 | 70715 | 70715 | 70715 | New Construction | 0 | 0 | New Construction | 50460 | 50460 | 50460 | 50460
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year |  |  |  |  | Replacement - Year |  |  | Replacement - Year
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0

## General Cost Parameters
Labor | Value |  | Materials
Base Rate and Fringe | Varies with Crew Type |  | Materials | Varies by component
Payroll, Taxes and Insurance including Worker's Comp, FICA, Unemployment Compensation Insuruance and Contractors Liability Insurance | 0.16 |  | Waste | 0 | 0.1 | 0% except for envelope costs which include 10% waste, or other value as described in F&G envelope cost report
Small Tools | 0.03 |  | Profit on Materials | 0.1 | 0.1
Sub-total % Multiplier | 0.19 |  | Sales Taxes | 0.0656 | 0.0656 | Varies by State, National average
Home Office Overhead | 0.15 |  | Material Cost % adjustment | 0.1656 | 0.28216 | Material_Cost_Adj
Profit | 0.1
Contingency for wage rate changes, applied after OHP | 0.0256
Labor Cost % OHP etc. | 0.526 | Labor_Cost_Adj
Replacement Home Office Overhead (intead of 15% for new construction) | 0.23 | F&G - from mechanical cost est. | Replacement Material - Added factor | 0.1 | 0.1 | F&G - from mechanical cost est.
Replacement Labor Cost % total adjustment | 0.623 | Replace_Labor_Cost_Adj | Replacement Material % adjustment | 0.28216 | 0.39872 | Replace_Material_Cost_Adj
Replacement labor added | 0.65 | Added labor cost for replacement for additional items for example demolition, protection, logistics, clean-up, lost productivity, etc. Added prior to calculating OH&P etc.. Faithful+Gould
Project Adjustment to Total Labor and Material
General Conditions (see F&G envelope cost report) | 0.12 | Sub-contractor
General Contractor Markup | 0.1
Contingency | 0.05
Project Markup Multiplier | 0.288 | Project_Cost_Adj
Location Index (multiplier) 1.00 is national average | 1 | Loc_Cost_Adj
Other Factors
General mechanical maintenance labor rate per hour | 72.55 | RS Means Mechanical Cost Data 2023, 1 Steamfitter (from Crew Q-5)
General electrical labor rate per hour | 67.35 | RS Means Electrical Costs Data 2023, 1 Electrician (from Crew R-1)
Fully loaded commissioning labor rate | 100 | Solarc. For occupancy sensors a different approach than an hourly commissioning rate is used, see occupancy sensor costs methodology.

## Crews (hidden)
Means 2023 Crew Data |  |  |  | 45002
Means Crew | $/hour | Count | Crew$/hr | Comment | Rates for crew labor (no equipment); enter crew staffing at right |  |  | Matching crew quantities (Overwrite formula if not 1)
Q1 | 64.85 | 2 | 129.7 |  | 72.05 | 57.65 |  | 1 | 1
Q2 | 67.25 | 3 | 201.75 |  | 72.05 | 57.65 |  | 2 | 1
Q5 | 65.3 | 2 | 130.6 |  | 72.55 | 58.05 |  | 1 | 1
Q6 | 67.72 | 3 | 203.15 |  | 72.55 | 58.05 |  | 2 | 1
Q7 | 69.05 | 4 | 276.2 |  | 73.05 | 72.55 | 58.05 | 1 | 2 | 1
Q9 | 63.13 | 2 | 126.25 |  | 70.15 | 56.1 |  | 1 | 1
Q10 | 65.47 | 3 | 196.4 |  | 70.15 | 56.1 |  | 2 | 1
Q14 | 58.73 | 2 | 117.45 |  | 65.25 | 52.2 |  | 1 | 1
Q20 | 63.97 | 2.5 | 159.925 |  | 70.15 | 56.1 | 67.35 | 1 | 1 | 0.5
R-1A | 60.63 | 2 | 121.25 |  | 67.35 | 53.9 |  | 1 | 1
R3 | 67.34 | 2.5 | 168.35 |  | 67.85 | 67.35 | 66.3 | 1 | 1 | 0.5
Elec | 67.85 | 1 | 67.85 | From R-1 | 67.85 |  |  | 1
1 Elec | 67.85 | 1 | 67.85 | From R-1 | 67.85 |  |  | 1
2 Elec | 67.6 | 2 | 135.2 | From R-1 | 67.85 | 67.35 |  | 1 | 1
Elec. | 67.85 | 1 | 67.85 | From R-1 | 67.85 |  |  | 1
Q-1 | 64.85 | 2 | 129.7 | These are repeats from rows 3-17 | 72.05 | 57.65 |  | 1 | 1
Q-2 | 67.25 | 3 | 201.75 |  | 72.05 | 57.65 |  | 2 | 1
Q-5 | 65.3 | 2 | 130.6 |  | 72.55 | 58.05 |  | 1 | 1
Q-6 | 67.72 | 3 | 203.15 |  | 72.55 | 58.05 |  | 2 | 1
Q-7 | 69.05 | 4 | 276.2 |  | 73.05 | 72.55 | 58.05 | 1 | 2 | 1
Q-9 | 63.13 | 2 | 126.25 |  | 70.15 | 56.1 |  | 1 | 1
Q-10 | 65.47 | 3 | 196.4 |  | 70.15 | 56.1 |  | 2 | 1
Q-14 | 58.73 | 2 | 117.45 |  | 65.25 | 52.2 |  | 1 | 1
Q-20 | 63.97 | 2.5 | 159.925 |  | 70.15 | 56.1 | 67.35 | 1 | 1 | 0.5
1 Shee | 63.13 | 2 | 126.25 | Use Q-10 | 70.15 | 56.1 |  | 1 | 1
R-3 | 67.34 | 2.5 | 168.35 |  | 67.85 | 67.35 | 66.3 | 1 | 1 | 0.5
NA | 0 | 0 | 0 | No labor required
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
| #DIV/0! | 0 | 0
CrewRate (lookup above)

## Cost_Inflation (hidden)
PNNL is conducting a cost effectiveness analysis for ASHRAE Standard 90.1-2019 compared to ASHRAE Standard 90.1-2016. The methodology and cost data are based on the previous analysis for the cost-effectiveness of 90.1-2013 to 90.1-2016. In an earlier analysis, PNNL worked with cost estimating consulting firms to develop cost information. For the current 90.1-2019 cost effectiveness analysis, PNNL decided to use the cost data developed in the previous study and adjusted them with inflation factors. The following approach is used for developing the inflation factors
The first step was to select representative cost parameters (e.g. size) for each cost item. In the previous study, the parameters usually have ranges that are applicable to the designs in the 90.1 models. The representative item costs within these ranges were collected from the 2012 and 2014 RS Means handbooks. The second step was to develop an inflation factor for the cost item individually. It used the ratio of item cost in the year 2020 to that in 2012.
The factor is defined as:
Inflation factor = Item cost in year 2020 / Item cost in year 2012
It was found that the inflation factors for certain component vary significantly within the range. Instead of taking the simple average of the inflation factors, we removed some of the inflation factor outliners if their difference from the simple average is more than two times the standard deviation.
The final inflation factor for each component is the average of the inflation factors for the cost items excluding the outliners.
2012 to 2023
2012 to 2020
HVAC Inflation Factor | Means | [5 empty] | 2012 to 2018
| 2012 to 2023 |  | 2014 to 2018 |  |  |  | 2012 to 2014 |  | 2014 to 2018 |  | 2020 to 2023
Type | Inflation Factor |  | Inflation Factor |  |  |  | Inflation Factor |  | Inflation Factor |  | Inflation Factor
| Mat. | Lab. | Mat. | Lab. |  |  | Mat. | Lab. | Mat. | Lab. | Mat. | Lab.
Pump | 1.838 |  | 1.105 |  |  | This factor not used | 1.838 |  | 1.1053 |  | 1.433
Cooling Tower | 1.384 | [5 empty] | 1.3839 |  | 1.1114
VFD | 1.463 | [5 empty] | 1.4628
Chiller | 1.104 |  | 0.985 |  |  |  | 1.1043 |  | 0.98549 |  | Note: use 2102-18 for F&G & new Means # from 2018
Ducts | 1.537 | 1.344 | Applied to regression of earlier price |  |  |  | 1.5374 | 1.344
Energy Recovery | 1.235 | [5 empty] | 1.2354
Packaged CAV_DX Units | 0.793 | [5 empty] | 0.79334
packaged VAV_DX Units | 1.147 | [5 empty] | 1.1473
Packaged Heat Pump | 1.217 | [5 empty] | 1.2174
CAV_AHU | 1.239 | [5 empty] | 1.2391
VAV_AHU | 1.242 | [5 empty] | 1.2416
Boilers | 1.314 | 1.301 |  |  |  |  | 1.3144 | 1.3009
Chilled Water and Condenser Water Piping | 0.619 | 1.137 | Applied to regression of earlier price |  |  |  | 0.61874 | 1.1374
Split Systems | 1.042 | 1.321 | Applied to regression of earlier price |  |  |  | 1.0418 | 1.321
Dry Transformers | 1.4 | [5 empty] | 1.4003
General Controls | 1.451 | 1.316 |  |  |  |  | 1.4511 | 1.3159
Lighting controls | 1.063 | 1.264 |  |  |  |  | 1.0627 | 1.2641
Summary Envelope Inflation Factors | [6 empty] | 2012 to 2020
| 2012 to 2020 | Grey not used (2012-2014) |  |  |  |  | 2012 to 2014
Type | Inflation Factor | [5 empty] | Inflation Factor
| Mat. | Lab. | Equip |  |  |  | Mat. | Lab.
Roof - Insulation entirely above deck | 1.103 | 1.047 |  |  | Not used 2016 |  | 1.1026 | 1.0466
Roof - Attic and other | 1.081 | 1.038 | 1.2333 |  | Not used 2016 |  | 1.0809 | 1.0377
Above ground wall - Mass | 1.047 | 1.046 |  |  | Not used 2016 |  | 1.0467 | 1.0464
Above ground wall - Steel-framed | 0.974 | 1.039 |  |  | Not used 2016 |  | 0.9744 | 1.0388
Above ground wall - Wood-framed | 1.089 | 1.041 |  |  | Not used 2016 |  | 1.0894 | 1.0413
Below grade wall - | 1.047 | 1.046 |  |  | Not used 2016
Slab-on-grade - Unheated | 1.03 | 0.988 |  |  | Not used 2016 |  | 1.0302 | 0.98824
Windows - | 1.088 | 1.2 |  |  |  |  | 1.0885 | 1.1996
Skylights - | 1.123 | 1.195 |  |  |  |  | 1.1225 | 1.1947
Doors | 1.029 | 1.203 | Note: using new costs |  |  |  | 1.0291 | 1.2029
Summary Insulated Heating WaterPiping Inflation Factors | [6 empty] | 2012 to 2020
| 2012 to 2020 | [5 empty] | 2012 to 2014 |  | 2014 to 2018 |  | 2014 to 2023
Type | Inflation Factor | [5 empty] | Inflation Factor |  | Inflation Factor |  | Inflation Factor
Note: These factors are applied to 2012 costs before regressions are run. | Mat. | Lab. |  |  |  |  | Mat. | Lab. | Mat. | Lab. | Mat. | Lab.
Steel Piping | 0.749 | 1.193 |  |  |  |  | 0.74921 | 1.1925
Piping Insulation | 1.33 | 1.235 |  |  |  |  | 1.3298 | 1.2355
2014 to 2018
Note: These factors are applied after regressions are run from 2014 to 2018. |  |  | Mat. | Lab.
Insulated steel piping |  |  | 1.096 | 1.05 | regression |  |  |  | 1.0965 | 1.05
|  |  | 2014 to 2023 | [7 empty] | 1.8174 | 0.9729
|  |  | Mat. | Lab.
|  |  | 1.817 | 0.973
Note on H7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Alex updated on 3/17/2023.

## Construction Weights
State Commercial Energy Code Adoption Cost Effectiveness - Construction Weights
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| State | Abbreviation | Climate zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment
1 | Alabama | AL | 2A | 0.027733 | 0.008261 | 0.07481 | 0.038836 | 0.020135 | 0.025978 | Wt_CZandPR_Look | [6 empty] | National contribution by CZ AND Building Type, Fraction | [9 empty] | % weights by building type
2 | Alabama | AL | 3A | 0.12952 | 0.054528 | 0.31218 | 0.10826 | 0.060368 | 0.13939 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
3 | [9 empty] | CZ | ClimateZone | 1A | 2B | 2A | 3B | 3C | 3A | 4B | 4C | 4A | 5B | 5C | 5A | 6B | 6A | 7 | 8 |  | US
4 | [11 empty] | 1_moist | 2_dry | 2_moist | 3_dry | 3_marine | 3_moist | 4_dry | 4_marine | 4_moist | 5_dry | 5_marine | 5_moist | 6_dry | 6_moist | 7 | 8 |  |  |  | Principal Building Activities
5 | [10 empty] | OfficeLarge | 0.0010917 | 0.00066659 | 0.0054449 | 0.0025673 | 0.0022943 | 0.0054317 | 7.7661e-06 | 0.0023844 | 0.011264 | 0.0015416 | 1.051e-05 | 0.0048227 | 3.5187e-05 | 0.00090541 | 8.3829e-05 | 0 |  | 0.038552 |  | 0.038552 | Office
6 | Arkansas | AR | 3A | 0.097466 | 0.015132 | 0.28848 | 0.15464 | 0.056896 | 0.042947 |  | OfficeMedium | 0.001414 | 0.0019359 | 0.0077729 | 0.0044555 | 0.0016462 | 0.0072567 | 0.00025435 | 0.0017011 | 0.0095084 | 0.0031253 | 2.3771e-05 | 0.0087887 | 0.0002591 | 0.0017191 | 0.00020532 | 2.3027e-05 |  | 0.050089 |  | 0.050089
7 | Arkansas | AR | 4A | 0.0474 | 0.016042 | 0.13886 | 0.068578 | 0.023153 | 0.050412 |  | OfficeSmall | 0.0011107 | 0.0015445 | 0.0076675 | 0.0027497 | 0.00046808 | 0.0069679 | 0.00030929 | 0.00092729 | 0.0057679 | 0.0020617 | 2.2561e-05 | 0.0066987 | 0.00021776 | 0.0013025 | 0.00015684 | 7.9797e-06 |  | 0.037981 |  | 0.037981
8 | [10 empty] | RetailStandalone | 0.0029007 | 0.0030753 | 0.017927 | 0.0085352 | 0.0012167 | 0.017781 | 0.000819 | 0.0026467 | 0.019184 | 0.0053695 | 0.000113 | 0.023661 | 0.00062068 | 0.0049341 | 0.00057878 | 6.3333e-05 |  | 0.10943 |  | 0.10943 | Retail
9 | [10 empty] | RetailStripmall | 0.0015619 | 0.0013841 | 0.0063313 | 0.0042407 | 0.00088755 | 0.0069625 | 0.00017215 | 0.0008752 | 0.0066053 | 0.0012468 | 2.0755e-05 | 0.006072 | 8.2664e-05 | 0.00058786 | 8.0373e-05 | 9.2352e-06 |  | 0.03712 |  | 0.03712
10 | [10 empty] | SchoolPrimary | 0.0013081 | 0.0011998 | 0.0097606 | 0.0035846 | 0.00043897 | 0.0093858 | 0.00032441 | 0.0011527 | 0.0088178 | 0.0023189 | 1.7836e-05 | 0.0077229 | 0.00047263 | 0.0015686 | 0.00019099 | 1.317e-05 |  | 0.048278 |  | 0.048278 | School
11 | Colorado | CO | 4B | 0.000197 | 0 | 0.000442 | 0.000384 | 0.000335 | 2.5e-05 |  | SchoolSecondary | 0.0026285 | 0.0019224 | 0.018595 | 0.0076738 | 0.0013513 | 0.021631 | 0.00071077 | 0.0027077 | 0.019767 | 0.0050656 | 8.7783e-05 | 0.021776 | 0.00094597 | 0.0036665 | 0.00060435 | 6.5171e-05 |  | 0.1092 |  | 0.1092
12 | Colorado | CO | 5B | 0.078121 | 0.089428 | 0.22912 | 0.066277 | 0.038024 | 0.4461 |  | Hospital | 0.00092915 | 0.0010853 | 0.0074838 | 0.0031507 | 0.00098456 | 0.0063127 | 0.00025618 | 0.0012901 | 0.0092124 | 0.0023417 | 6.8096e-05 | 0.0094709 | 0.00032055 | 0.0019684 | 0.00032924 | 2.2858e-05 |  | 0.045227
13 | Colorado | CO | 6B | 0.001395 | 0 | 0.004867 | 0.003289 | 0.002577 | 0.014843 |  | OutPatientHealthCare | 0.0005475 | 0.00088916 | 0.0054185 | 0.0017477 | 0.00044062 | 0.005305 | 0.00020753 | 0.00098403 | 0.0061938 | 0.0020241 | 3.7368e-05 | 0.008005 | 0.00026967 | 0.0018086 | 0.000288 | 2.0839e-05 |  | 0.034187
14 | Colorado | CO | 7 | 0.001439 | 0 | 0.004532 | 0.001548 | 0.001125 | 0.015923 |  | RestaurantSitDown | 0.00031106 | 0.00027323 | 0.0017695 | 0.00084031 | 0.00012835 | 0.0016807 | 7.5668e-05 | 0.00021129 | 0.0016343 | 0.00044958 | 6.4135e-06 | 0.0019495 | 4.4286e-05 | 0.00029168 | 4.3322e-05 | 8.491e-06 |  | 0.0097177
15 | [10 empty] | RestaurantFastFood | 7.9079e-05 | 9.4908e-05 | 0.00067244 | 0.00020241 | 1.8982e-05 | 0.00064962 | 2.005e-05 | 4.573e-05 | 0.00055112 | 0.00017441 | 8.4133e-07 | 0.00067646 | 1.805e-05 | 0.00010596 | 8.9958e-06 | 2.7181e-07 |  | 0.0033193
16 | Connecticut | CT | 5A | 0.069659 | 0.053126 | 0.32216 | 0.13814 | 0.02258 | 0.39434 |  | HotelLarge | 0.0017913 | 0.0010479 | 0.0070561 | 0.0054743 | 0.00091124 | 0.0056219 | 0.00023729 | 0.001341 | 0.0081564 | 0.0019235 | 2.1137e-05 | 0.0065019 | 0.00041749 | 0.0014355 | 0.00024311 | 5.5787e-06 |  | 0.042186 |  | 0.042186 | Hotel
17 | [10 empty] | HotelSmall | 0.00032729 | 0.0002425 | 0.0030366 | 0.0010619 | 0.0001526 | 0.0026795 | 0.00013672 | 0.00025961 | 0.0030428 | 0.00095109 | 2.0638e-05 | 0.0027267 | 0.00025413 | 0.00082193 | 0.0001577 | 1.02e-05 |  | 0.015882 |  | 0.015882
18 | [10 empty] | Warehouse | 0.0053343 | 0.0062522 | 0.035257 | 0.022325 | 0.0018279 | 0.027749 | 0.00052515 | 0.0054116 | 0.036938 | 0.0081514 | 3.0249e-05 | 0.031371 | 0.00030199 | 0.0037065 | 0.00036487 | 2.0464e-05 |  | 0.18557
19 | [10 empty] | ApartmentHighRise | 0.014412 | 0.00083553 | 0.011915 | 0.0063132 | 0.0029247 | 0.005691 | 0 | 0.0049429 | 0.03263 | 0.0018651 | 0 | 0.013569 | 8.8857e-05 | 0.0011319 | 4.0895e-05 | 0 |  | 0.09636 |  | 0.09636 | Apartment
20 | [10 empty] | ApartmentMidRise | 0.0036221 | 0.0027031 | 0.022442 | 0.011765 | 0.0049247 | 0.017784 | 0.00025922 | 0.0070595 | 0.030166 | 0.0072879 | 6.6096e-05 | 0.022186 | 0.00051692 | 0.0057142 | 0.00041255 | 1.1002e-07 |  | 0.13691 |  | 0.13691
21 | Delaware | DE | 4A | 0.073056 | 0.09402 | 0.30912 | 0.17601 | 0.052608 | 0.29518 |  | %weight by Zone | 0.039369 | 0.025152 | 0.16855 | 0.086687 | 0.020617 | 0.14889 | 0.0043155 | 0.033941 | 0.20944 | 0.045898 | 0.00054706 | 0.176 | 0.0048659 | 0.031669 | 0.0037892 | 0.00027073 | 0 | 1 |  | 0.72198
22
23
24
25 | [9 empty] | Wt_CZandPR_Look 1: Wt_CZandPR_Look; National contribution by CZ AND Building Type, Fraction 8: National contribution by CZ AND Building Type, Fraction; % weights by building type 18: % weights by building type
26 | District of Columbia | DC | 4A | 0.011769 | 0.56078 | 0.048577 | 0.028181 | 0.002749 | 0.34795 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
27 | [9 empty] | CZ | ClimateZone | 1A | 2B | 2A | 3B | 3C | 3A | 4B | 4C | 4A | 5B | 5C | 5A | 6B | 6A | 7 | 8 |  | US
28 | [11 empty] | 1_moist | 2_dry | 2_moist | 3_dry | 3_marine | 3_moist | 4_dry | 4_marine | 4_moist | 5_dry | 5_marine | 5_moist | 6_dry | 6_moist | 7 | 8
29 | [9 empty] | Wt_CZandPR_Look 2: OfficeLarge; Wt_CZandPR_Look 5: 0.0054449; Wt_CZandPR_Look 6: 0.0025673; National contribution by CZ AND Building Type, Fraction 8: 0.0054317; National contribution by CZ AND Building Type, Fraction 11: 0.011264; National contribution by CZ AND Building Type, Fraction 14: 0.0048227; % weights by building type 20: 0.029531
30 | [9 empty] | Wt_CZandPR_Look 2: OfficeMedium
31 | Georgia | GA | 2A | 0.011825 | 0.000451 | 0.026201 | 0.030544 | 0.010185 | 0.011918 | Wt_CZandPR_Look 2: OfficeSmall; Wt_CZandPR_Look 5: 0.0076675; Wt_CZandPR_Look 6: 0.0027497; National contribution by CZ AND Building Type, Fraction 8: 0.0069679; National contribution by CZ AND Building Type, Fraction 11: 0.0057679; National contribution by CZ AND Building Type, Fraction 14: 0.0066987; % weights by building type 20: 0.029852
32 | Georgia | GA | 3A | 0.090817 | 0.08534 | 0.23142 | 0.15085 | 0.028482 | 0.32197 | Wt_CZandPR_Look 2: RetailStandalone; Wt_CZandPR_Look 5: 0.017927; Wt_CZandPR_Look 6: 0.0085352; National contribution by CZ AND Building Type, Fraction 8: 0.017781; National contribution by CZ AND Building Type, Fraction 11: 0.019184; National contribution by CZ AND Building Type, Fraction 14: 0.023661; % weights by building type 20: 0.087089
33 | [9 empty] | Wt_CZandPR_Look 2: RetailStripmall
34 | [9 empty] | Wt_CZandPR_Look 2: SchoolPrimary; Wt_CZandPR_Look 5: 0.0097606; Wt_CZandPR_Look 6: 0.0035846; National contribution by CZ AND Building Type, Fraction 8: 0.0093858; National contribution by CZ AND Building Type, Fraction 11: 0.0088178; National contribution by CZ AND Building Type, Fraction 14: 0.0077229; % weights by building type 20: 0.039272
35 | [9 empty] | Wt_CZandPR_Look 2: SchoolSecondary
36 | Iowa | IA | 5A | 0.15651 | 0.042768 | 0.31205 | 0.16343 | 0.057989 | 0.23767 | Wt_CZandPR_Look 2: Hospital
37 | Iowa | IA | 6A | 0.003529 | 0 | 0.012305 | 0.004457 | 0.005338 | 0.003964 | Wt_CZandPR_Look 2: OutPatientHealthCare
38 | [9 empty] | Wt_CZandPR_Look 2: RestaurantSitDown
39 | [9 empty] | Wt_CZandPR_Look 2: RestaurantFastFood
40 | [9 empty] | Wt_CZandPR_Look 2: HotelLarge
41 | Kentucky | KY | 4A | 0.14028 | 0.030764 | 0.39182 | 0.19486 | 0.07278 | 0.1695 | Wt_CZandPR_Look 2: HotelSmall; Wt_CZandPR_Look 5: 0.0030366; Wt_CZandPR_Look 6: 0.0010619; National contribution by CZ AND Building Type, Fraction 8: 0.0026795; National contribution by CZ AND Building Type, Fraction 11: 0.0030428; National contribution by CZ AND Building Type, Fraction 14: 0.0027267; % weights by building type 20: 0.012547
42 | [9 empty] | Wt_CZandPR_Look 2: Warehouse
43 | [9 empty] | Wt_CZandPR_Look 2: ApartmentHighRise
44 | [9 empty] | Wt_CZandPR_Look 2: ApartmentMidRise; Wt_CZandPR_Look 5: 0.022442; Wt_CZandPR_Look 6: 0.011765; National contribution by CZ AND Building Type, Fraction 8: 0.017784; National contribution by CZ AND Building Type, Fraction 11: 0.030166; National contribution by CZ AND Building Type, Fraction 14: 0.022186; % weights by building type 20: 0.10434 |  | 0.30263 | of building type
45 | [9 empty] | Wt_CZandPR_Look 2: %weight by Zone; Wt_CZandPR_Look 5: 0.066278; Wt_CZandPR_Look 6: 0.030264; National contribution by CZ AND Building Type, Fraction 8: 0.06003; National contribution by CZ AND Building Type, Fraction 11: 0.078243; National contribution by CZ AND Building Type, Fraction 14: 0.067818; % weights by building type 20: 0.30263 |  | 0.23482 | of climate zones
46 | Massachusetts | MA | 5A | 0.040534 | 0.11127 | 0.18855 | 0.06479 | 0.018912 | 0.57594 | Wt_CZandPR_Look 5: 2A; Wt_CZandPR_Look 6: 3B; Wt_CZandPR_Look 7: 3C; National contribution by CZ AND Building Type, Fraction 8: 3A; National contribution by CZ AND Building Type, Fraction 9: 4B; National contribution by CZ AND Building Type, Fraction 10: 4C; National contribution by CZ AND Building Type, Fraction 11: 4A; National contribution by CZ AND Building Type, Fraction 12: 5B; National contribution by CZ AND Building Type, Fraction 13: 5C; National contribution by CZ AND Building Type, Fraction 14: 5A |  | 0.30263 | of total building stock
47 | [9 empty] | 2 | OfficeLarge |  |  | 0.017992 | 0.0084833 | 0 | 0.017948 | 0 | 0 | 0.037221 | 0 | 0 | 0.015936
48 | [10 empty] | OfficeMedium |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 2A | 3A | 3B | 4A | 5A
49 | [9 empty] | 1 | OfficeSmall |  |  | 0.025336 | 0.0090861 | 0 | 0.023024 | 0 | 0 | 0.019059 | 0 | 0 | 0.022135 |  |  |  |  | OfficeSmall | 0.025336 | 0.023024 | 0.0090861 | 0.019059 | 0.022135
50 | [9 empty] | 3 | RetailStandalone |  |  | 0.059235 | 0.028203 | 0 | 0.058756 | 0 | 0 | 0.063391 | 0 | 0 | 0.078184 |  |  |  |  | OfficeLarge | 0.017992 | 0.017948 | 0.0084833 | 0.037221 | 0.015936
51 | Montana | MT | 6B | 0.13919 | 0.027612 | 0.41765 | 0.1651 | 0.13539 | 0.11506 |  | RetailStripmall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | RetailStandalone | 0.059235 | 0.058756 | 0.028203 | 0.063391 | 0.078184
52 | [9 empty] | 4 | SchoolPrimary |  |  | 0.032252 | 0.011845 | 0 | 0.031014 | 0 | 0 | 0.029137 | 0 | 0 | 0.025519 |  |  |  |  | SchoolPrimary | 0.032252 | 0.031014 | 0.011845 | 0.029137 | 0.025519
53 | [10 empty] | SchoolSecondary |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | HotelSmall | 0.010034 | 0.0088539 | 0.003509 | 0.010054 | 0.0090099
54 | [10 empty] | Hospital |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | ApartmentMidRise | 0.074155 | 0.058763 | 0.038875 | 0.099679 | 0.07331
55 | [9 empty] | Wt_CZandPR_Look 2: OutPatientHealthCare; Wt_CZandPR_Look 5: 0; Wt_CZandPR_Look 6: 0; Wt_CZandPR_Look 7: 0; National contribution by CZ AND Building Type, Fraction 8: 0; National contribution by CZ AND Building Type, Fraction 9: 0; National contribution by CZ AND Building Type, Fraction 10: 0; National contribution by CZ AND Building Type, Fraction 11: 0; National contribution by CZ AND Building Type, Fraction 12: 0; National contribution by CZ AND Building Type, Fraction 13: 0; National contribution by CZ AND Building Type, Fraction 14: 0
56 | Nebraska | NE | 5A | 0.12903 | 0.048961 | 0.35637 | 0.1628 | 0.061145 | 0.24169 | Wt_CZandPR_Look 2: RestaurantSitDown; Wt_CZandPR_Look 5: 0; Wt_CZandPR_Look 6: 0; Wt_CZandPR_Look 7: 0; National contribution by CZ AND Building Type, Fraction 8: 0; National contribution by CZ AND Building Type, Fraction 9: 0; National contribution by CZ AND Building Type, Fraction 10: 0; National contribution by CZ AND Building Type, Fraction 11: 0; National contribution by CZ AND Building Type, Fraction 12: 0; National contribution by CZ AND Building Type, Fraction 13: 0; National contribution by CZ AND Building Type, Fraction 14: 0
57 | [10 empty] | RestaurantFastFood |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | OfficeSmall | OfficeLarge | RetailStandalone | SchoolPrimary | HotelSmall | ApartmentMidRise
58 | [10 empty] | HotelLarge |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2A | 0.025336 | 0.017992 | 0.059235 | 0.032252 | 0.010034 | 0.074155
59 | [9 empty] | 5 | HotelSmall |  |  | 0.010034 | 0.003509 | 0 | 0.0088539 | 0 | 0 | 0.010054 | 0 | 0 | 0.0090099 |  |  | 3A | 0.023024 | 0.017948 | 0.058756 | 0.031014 | 0.0088539 | 0.058763
60 | [10 empty] | Warehouse |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3B | 0.0090861 | 0.0084833 | 0.028203 | 0.011845 | 0.003509 | 0.038875
61 | New Jersey | NJ | 4A | 0.026127 | 0.029221 | 0.14514 | 0.09347 | 0.013562 | 0.40846 |  | ApartmentHighRise |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4A | 0.019059 | 0.037221 | 0.063391 | 0.029137 | 0.010054 | 0.099679
62 | New Jersey | NJ | 5A | 0.011216 | 0.015203 | 0.065188 | 0.033236 | 0.004791 | 0.15439 | 6 | ApartmentMidRise |  |  | 0.074155 | 0.038875 | 0 | 0.058763 | 0 | 0 | 0.099679 | 0 | 0 | 0.07331 |  |  | 5A | 0.022135 | 0.015936 | 0.078184 | 0.025519 | 0.0090099 | 0.07331
63 | [32 empty] | 1
64
65
66 | New York | NY | 4A | 0.012886 | 0.18625 | 0.081569 | 0.031634 | 0.030624 | 0.31621 | bar: National contribution by CZ AND Building Type, Fraction 14
67 | New York | NY | 5A | 0.03012 | 0.012416 | 0.10889 | 0.012853 | 0.019296 | 0.10848
68 | New York | NY | 6A | 0.002612 | 2e-05 | 0.025921 | 0.002094 | 0.006817 | 0.011315 | Wt_CZandPR_Look 4: State; Wt_CZandPR_Look 5: Abbreviation; Wt_CZandPR_Look 6: Climate zone; Wt_CZandPR_Look 7: Small Office; National contribution by CZ AND Building Type, Fraction 8: Large Office; National contribution by CZ AND Building Type, Fraction 9: Stand-Alone Retail; National contribution by CZ AND Building Type, Fraction 10: Primary School; National contribution by CZ AND Building Type, Fraction 11: Small Hotel; National contribution by CZ AND Building Type, Fraction 12: Mid-rise Apartment
69 | [9 empty] | Wt_CZandPR_Look 4: US National; Wt_CZandPR_Look 5: US; Wt_CZandPR_Look 6: 2A; Wt_CZandPR_Look 7: 0.025336; National contribution by CZ AND Building Type, Fraction 8: 0.017992; National contribution by CZ AND Building Type, Fraction 9: 0.059235; National contribution by CZ AND Building Type, Fraction 10: 0.032252; National contribution by CZ AND Building Type, Fraction 11: 0.010034; National contribution by CZ AND Building Type, Fraction 12: 0.074155
70 | [9 empty] | Wt_CZandPR_Look 4: US National; Wt_CZandPR_Look 5: US; Wt_CZandPR_Look 6: 3A; Wt_CZandPR_Look 7: 0.023024; National contribution by CZ AND Building Type, Fraction 8: 0.017948; National contribution by CZ AND Building Type, Fraction 9: 0.058756; National contribution by CZ AND Building Type, Fraction 10: 0.031014; National contribution by CZ AND Building Type, Fraction 11: 0.0088539; National contribution by CZ AND Building Type, Fraction 12: 0.058763
71 | North Carolina | NC | 3A | 0.10018 | 0.11082 | 0.24283 | 0.11869 | 0.02586 | 0.33226 | Wt_CZandPR_Look 4: US National; Wt_CZandPR_Look 5: US; Wt_CZandPR_Look 6: 3B; Wt_CZandPR_Look 7: 0.0090861; National contribution by CZ AND Building Type, Fraction 8: 0.0084833; National contribution by CZ AND Building Type, Fraction 9: 0.028203; National contribution by CZ AND Building Type, Fraction 10: 0.011845; National contribution by CZ AND Building Type, Fraction 11: 0.003509; National contribution by CZ AND Building Type, Fraction 12: 0.038875
72 | North Carolina | NC | 4A | 0.006774 | 0.000367 | 0.023438 | 0.007919 | 0.003797 | 0.019588 | Wt_CZandPR_Look 4: US National; Wt_CZandPR_Look 5: US; Wt_CZandPR_Look 6: 4A; Wt_CZandPR_Look 7: 0.019059; National contribution by CZ AND Building Type, Fraction 8: 0.037221; National contribution by CZ AND Building Type, Fraction 9: 0.063391; National contribution by CZ AND Building Type, Fraction 10: 0.029137; National contribution by CZ AND Building Type, Fraction 11: 0.010054; National contribution by CZ AND Building Type, Fraction 12: 0.099679
73 | North Carolina | NC | 5A | 0.00044 | 0 | 0.004302 | 0.001068 | 0.000328 | 0.001337 | Wt_CZandPR_Look 4: US National; Wt_CZandPR_Look 5: US; Wt_CZandPR_Look 6: 5A; Wt_CZandPR_Look 7: 0.022135; National contribution by CZ AND Building Type, Fraction 8: 0.015936; National contribution by CZ AND Building Type, Fraction 9: 0.078184; National contribution by CZ AND Building Type, Fraction 10: 0.025519; National contribution by CZ AND Building Type, Fraction 11: 0.0090099; National contribution by CZ AND Building Type, Fraction 12: 0.07331
74
75
76 | Oklahoma | OK | 3A | 0.15237 | 0.066247 | 0.31859 | 0.20222 | 0.078857 | 0.11662
77 | Oklahoma | OK | 4A | 0.007284 | 0.001651 | 0.016455 | 0.015516 | 0.006977 | 0.011955
78 | Oklahoma | OK | 4B | 0.001832 | 0 | 0.002807 | 0.000162 | 0.000417 | 4.4e-05
79
80
81 | Rhode Island | RI | 5A | 0.053515 | 0.048978 | 0.3999 | 0.061222 | 0.050685 | 0.3857
82
83
84
85
86 | South Carolina | SC | 2A | 0.006559 | 0 | 0.014657 | 0.005971 | 0.004267 | 0.00768
87 | South Carolina | SC | 3A | 0.10763 | 0.031851 | 0.31291 | 0.15336 | 0.036765 | 0.31835
88
89
90
91 | Texas | TX | 1A | 0.005956 | 0.00027 | 0.014492 | 0.008116 | 0.002053 | 0.000812
92 | Texas | TX | 2A | 0.066281 | 0.094658 | 0.18461 | 0.11824 | 0.031348 | 0.27214
93 | Texas | TX | 2B | 0.000646 | 0 | 0.003255 | 0.003906 | 0.001068 | 0.000109
94 | Texas | TX | 3A | 0.01287 | 0.016119 | 0.041589 | 0.030187 | 0.006054 | 0.040315
95 | Texas | TX | 3B | 0.00623 | 0.001475 | 0.016384 | 0.011033 | 0.005422 | 0.00436
96 | US National | US | 2A | 0.025336 | 0.017992 | 0.059235 | 0.032252 | 0.010034 | 0.074155
97 | US National | US | 3A | 0.023024 | 0.017948 | 0.058756 | 0.031014 | 0.008854 | 0.058763
98 | US National | US | 3B | 0.009086 | 0.008483 | 0.028203 | 0.011845 | 0.003509 | 0.038875
99 | US National | US | 4A | 0.019059 | 0.037221 | 0.063391 | 0.029137 | 0.010054 | 0.099679
100 | US National | US | 5A | 0.022135 | 0.015936 | 0.078184 | 0.025519 | 0.00901 | 0.07331
101 | Utah | UT | 3B | 0.005428 | 0 | 0.009686 | 0.010459 | 0.007206 | 0.009104
102 | Utah | UT | 5B | 0.086936 | 0.090212 | 0.23913 | 0.14448 | 0.028873 | 0.31847
103 | Utah | UT | 6B | 0.003068 | 0 | 0.010505 | 0.010209 | 0.004529 | 0.021715
104
105
106 | Virginia | VA | 3A | 0.025022 | 0.012166 | 0.044178 | 0.018118 | 0.006363 | 0.070402
107 | Virginia | VA | 4A | 0.067379 | 0.14629 | 0.16448 | 0.075581 | 0.021736 | 0.3479
108 | Virginia | VA | 5A | 2.3e-05 | 0 | 7.7e-05 | 7.8e-05 | 0.000209 | 0
109
110
111 | Wisconsin | WI | 5A | 0.072216 | 0.065529 | 0.28444 | 0.062414 | 0.026574 | 0.30086
112 | Wisconsin | WI | 6A | 0.025121 | 0.006813 | 0.084413 | 0.029066 | 0.012115 | 0.030441
113
114
115
116 | California | CA | 2B | 0.000284 | 0 | 0.00303 | 0.00038 | 0.000278 | 0
117 | California | CA | 3B | 0.053013 | 0.067797 | 0.17887 | 0.071871 | 0.017737 | 0.31567
118 | California | CA | 3C | 0.013865 | 0.067959 | 0.03604 | 0.013002 | 0.00452 | 0.14587
119 | California | CA | 4B | 0.001632 | 0 | 0.002978 | 0.000478 | 0.000281 | 0.001825
120 | California | CA | 5B | 0.000356 | 0 | 0.000664 | 0.000116 | 0.000425 | 0.00105
121 | Arizona | AZ | 2B | 0.15377 | 0.068142 | 0.28809 | 0.10234 | 0.018637 | 0.27579
122 | Arizona | AZ | 3B | 0.004211 | 0 | 0.025498 | 0.002687 | 0.004827 | 0.000913
123 | Arizona | AZ | 4B | 0.001711 | 0 | 0.01388 | 0.002089 | 0.001491 | 0.00217
124 | Arizona | AZ | 5B | 0.003968 | 0 | 0.010701 | 0.003801 | 0.006145 | 0.00914
125
126 | Florida | FL | 1A | 0.023798 | 0.033984 | 0.064311 | 0.027014 | 0.006838 | 0.10647
127 | Florida | FL | 2A | 0.10275 | 0.026041 | 0.21508 | 0.090196 | 0.028859 | 0.27466
128
129
130
131 | Hawaii | HI | 1A | 0.12194 | 0.043341 | 0.29842 | 0.11664 | 0.024715 | 0.39494
132
133
134
135
136 | Idaho | ID | 5B | 0.16959 | 0.043719 | 0.24424 | 0.10588 | 0.034112 | 0.18508
137 | Idaho | ID | 6B | 0.028402 | 0.008211 | 0.058977 | 0.045715 | 0.011563 | 0.06452
138
139
140
141 | Illinois | IL | 4A | 0.006867 | 0.000407 | 0.036976 | 0.011466 | 0.004755 | 0.00732
142 | Illinois | IL | 5A | 0.078675 | 0.10851 | 0.31901 | 0.090527 | 0.019006 | 0.31648
143
144
145
146 | Indiana | IN | 4A | 0.071108 | 0.009522 | 0.17172 | 0.051867 | 0.026116 | 0.13147
147 | Indiana | IN | 5A | 0.10488 | 0.014782 | 0.22465 | 0.068621 | 0.033965 | 0.091301
148
149
150
151 | Kansas | KS | 4A | 0.11331 | 0.044783 | 0.34232 | 0.17486 | 0.077658 | 0.23654
152 | Kansas | KS | 5A | 0.001125 | 0 | 0.003223 | 0.001532 | 0.003959 | 0.000679
153
154
155
156 | Louisiana | LA | 2A | 0.18241 | 0.020215 | 0.31908 | 0.12385 | 0.070808 | 0.13701
157 | Louisiana | LA | 3A | 0.01849 | 0.002054 | 0.07871 | 0.017745 | 0.017673 | 0.011962
158
159
160
161 | Maine | ME | 6A | 0.088934 | 0.034586 | 0.41622 | 0.19128 | 0.091407 | 0.15328
162 | Maine | ME | 7 | 0.001257 | 0 | 0.011419 | 0.008086 | 0.003327 | 0.000205
163
164
165
166 | Maryland | MD | 4A | 0.068002 | 0.1475 | 0.13784 | 0.083179 | 0.016445 | 0.54222
167 | Maryland | MD | 5A | 0.000729 | 0 | 0.002895 | 0.000214 | 0.000519 | 0.000468
168
169
170
171 | Michigan | MI | 7 | 0.00084 | 0 | 0.005273 | 0.000468 | 0.000985 | 0.002041
172 | Michigan | MI | 5A | 0.1152 | 0.03648 | 0.4069 | 0.09366 | 0.03596 | 0.19669
173 | Michigan | MI | 6A | 0.011626 | 0 | 0.069088 | 0.008971 | 0.005901 | 0.009928
174
175
176 | Minnesota | MN | 5A | 0.0002 | 0 | 0.00081 | 6.5e-05 | 0.000368 | 0.000492
177 | Minnesota | MN | 6A | 0.064084 | 0.090092 | 0.21579 | 0.077664 | 0.018015 | 0.47791
178 | Minnesota | MN | 7 | 0.004923 | 0.001472 | 0.021211 | 0.007513 | 0.005806 | 0.01358
179
180
181 | Mississippi | MS | 2A | 0.061169 | 0 | 0.073925 | 0.036541 | 0.018594 | 0.021467
182 | Mississippi | MS | 3A | 0.11718 | 0.028975 | 0.34325 | 0.13482 | 0.091374 | 0.072706
183
184
185
186 | Missouri | MO | 3A | 0.000397 | 0 | 6.3e-05 | 0.000606 | 0 | 0
187 | Missouri | MO | 4A | 0.077616 | 0.088128 | 0.36633 | 0.10827 | 0.041698 | 0.29991
188 | Missouri | MO | 5A | 0.001486 | 0 | 0.009404 | 0.003642 | 0.001226 | 0.001224
189
190
191 | Nevada | NV | 3B | 0.12923 | 0.051374 | 0.30603 | 0.10594 | 0.010284 | 0.20305
192 | Nevada | NV | 4B | 0.01305 | 0.001915 | 0.022402 | 0.003588 | 0.002113 | 0.000453
193 | Nevada | NV | 5B | 0.027642 | 1.8e-05 | 0.061344 | 0.011629 | 0.008428 | 0.041502
194
195
196 | New Hampshire | NH | 5A | 0.043446 | 0.013584 | 0.34964 | 0.043325 | 0.032648 | 0.25203
197 | New Hampshire | NH | 6A | 0.008933 | 0.002479 | 0.1332 | 0.007991 | 0.027109 | 0.085613
198
199
200
201 | New Mexico | NM | 3B | 0.037316 | 0 | 0.094324 | 0.065282 | 0.041711 | 0.00986
202 | New Mexico | NM | 4B | 0.074843 | 0 | 0.15844 | 0.11886 | 0.026184 | 0.076621
203 | New Mexico | NM | 5B | 0.040512 | 0.009646 | 0.096902 | 0.097726 | 0.02759 | 0.024177
204
205
206 | North Dakota | ND | 6A | 0.087008 | 0.009801 | 0.25868 | 0.11774 | 0.10113 | 0.19541
207 | North Dakota | ND | 7 | 0.028384 | 0 | 0.084202 | 0.022205 | 0.031317 | 0.064129
208
209
210
211 | Ohio | OH | 4A | 0.042986 | 0.038193 | 0.1315 | 0.069104 | 0.015781 | 0.12363
212 | Ohio | OH | 5A | 0.077098 | 0.019362 | 0.24748 | 0.11908 | 0.029418 | 0.08637
213
214
215
216 | Oregon | OR | 4C | 0.076649 | 0.079385 | 0.22522 | 0.074177 | 0.029637 | 0.4197
217 | Oregon | OR | 5B | 0.012634 | 0 | 0.037717 | 0.019056 | 0.01255 | 0.013278
218
219
220
221 | Pennsylvania | PA | 4A | 0.032115 | 0.061312 | 0.14412 | 0.086268 | 0.015006 | 0.22591
222 | Pennsylvania | PA | 5A | 0.035221 | 0.047092 | 0.15876 | 0.068075 | 0.0267 | 0.099413
223
224
225
226 | South Dakota | SD | 5A | 0.008543 | 0 | 0.036692 | 0.011445 | 0.003566 | 0.00493
227 | South Dakota | SD | 6A | 0.15069 | 0.011487 | 0.33657 | 0.17088 | 0.075419 | 0.18979
228
229
230
231 | Tennessee | TN | 3A | 0.080073 | 0.095604 | 0.17894 | 0.068665 | 0.025171 | 0.21951
232 | Tennessee | TN | 4A | 0.042975 | 0.005661 | 0.14318 | 0.048818 | 0.024217 | 0.067184
233
234
235
236 | Vermont | VT | 6A | 0.09014 | 0 | 0.25469 | 0.032768 | 0.094321 | 0.52808
237
238
239
240
241 | Washington | WA | 4C | 0.049602 | 0.1739 | 0.1373 | 0.069805 | 0.01025 | 0.44206
242 | Washington | WA | 5B | 0.010668 | 0.002298 | 0.036451 | 0.020058 | 0.007772 | 0.017987
243 | Washington | WA | 5C | 0.001903 | 0.000904 | 0.009721 | 0.001178 | 0.001599 | 0.005639
244 | Washington | WA | 6B | 0.0003 | 0 | 9.9e-05 | 0.000419 | 2.7e-05 | 5.5e-05
245
246 | West Virginia | WV | 4A | 0.034589 | 0.00339 | 0.34738 | 0.15127 | 0.0407 | 0.012636
247 | West Virginia | WV | 5A | 0.023501 | 0.036673 | 0.1946 | 0.076405 | 0.029804 | 0.049055
248
249
250
251 | Wyoming | WY | 5B | 0.023566 | 0 | 0.097031 | 0.06555 | 0.041078 | 0.001394
252 | Wyoming | WY | 6B | 0.050845 | 0 | 0.17936 | 0.26863 | 0.13883 | 0.027528
253 | Wyoming | WY | 7 | 0.005665 | 0 | 0.004032 | 0.059736 | 0.030734 | 0.006023
254
255
256 | Alaska | AK | 5C | 0.000846 | 0 | 0 | 0.007965 | 0.003945 | 0.001058
257 | Alaska | AK | 6A | 0.001195 | 0 | 0.013056 | 0.000137 | 0.000162 | 0.004991
258 | Alaska | AK | 7 | 0.10271 | 0.13632 | 0.36894 | 0.059255 | 0.050966 | 0.066163
259 | Alaska | AK | 8 | 0.015346 | 0 | 0.1218 | 0.025328 | 0.019615 | 0.000212
260

## Cost Est Summary
Commercial Energy Code Adoption Cost Effectiveness - Incremental Cost Summary by Prototype and Climate Zone with 29 Years of Replacement Costs and Residual Values in Year 30
First Cost Summary | [9 empty] | First Cost Summary Relative to Whole Building Cost
| Value | 2A | 3A | 3B | 4A | 5A |  |  |  | Prototype | Building First Cost,* $/ft2 | 2A | 3A | 3B | 4A | 5A
|  | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY |  | Building Areas |  |  |  | $/ft2 | $/ft2 | $/ft2 | $/ft2 | $/ft2
Small Office | First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 |  | 5502 |  | Small Office | 220 | 0.58745 | 0.56605 | 0.57979 | 0.82812 | 0.92122
| $/ft2 | 0.58745 | 0.56605 | 0.57979 | 0.82812 | 0.92122 | [5 empty] | 0.0026702 | 0.0025729 | 0.0026354 | 0.0037642 | 0.0041874
Large Office | First Cost | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 |  | 498588 |  | Large Office | 180 | 1.6873 | 1.136 | 1.1084 | 1.1821 | 1.1731
| $/ft2 | 1.6873 | 1.136 | 1.1084 | 1.1821 | 1.1731 | [5 empty] | 0.009374 | 0.0063111 | 0.0061576 | 0.0065675 | 0.0065173
Standalone Retail | First Cost | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 |  | 24692 |  | Standalone Retail | 116 | 1.1848 | 1.2556 | 1.2201 | 1.2856 | 1.1456
| $/ft2 | 1.1848 | 1.2556 | 1.2201 | 1.2856 | 1.1456 | [5 empty] | 0.010214 | 0.010824 | 0.010518 | 0.011083 | 0.0098757
Primary School | First Cost | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 |  | 73959 |  | Primary School | 225 | 1.3303 | 1.3494 | 1.2803 | 1.3678 | 1.3836
| $/ft2 | 1.3303 | 1.3494 | 1.2803 | 1.3678 | 1.3836 | [5 empty] | 0.0059126 | 0.0059972 | 0.0056904 | 0.0060792 | 0.0061491
Small Hotel | First Cost | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 |  | 43202 |  | Small Hotel | 197 | 1.6698 | 1.6064 | 1.5844 | 1.5882 | 1.5893
| $/ft2 | 1.6698 | 1.6064 | 1.5844 | 1.5882 | 1.5893 | [5 empty] | 0.0084759 | 0.0081543 | 0.0080425 | 0.008062 | 0.0080675
Mid-rise Apartment | First Cost | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794 |  | 33741 |  | Mid-rise Apartment | 218 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991
| $/ft2 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991 | [5 empty] | 0.0044317 | 0.0043889 | 0.0038316 | 0.0036643 | 0.0038528
* Building first costs are from 2020 RS Means Building Construction Costs, p. 897
Cost Location Index |  | 1 | (set to a value of 1 if you want to see costs without this adjustment summary without index adjustment) | [9 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Small Office |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Small Office | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | -1155.8408 | -1273.5984 | -1197.9729 | -1591.6563 | -1079.4222 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 4388 | 4388 | 4388 | 6148 | 6148 | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778
Maintenance | 0 | 0 | 0 | 0 | 0 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replacement (Year) | [11 empty] | Replacement (Year)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -1620.9765 | -1857.3665 | -1718.8944 | -2333.3577 | -1625.6601 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -1620.9765 | -1857.3665 | -1718.8944 | -2333.3577 | -1625.6601
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 824.4091 | 1016.8392 | 913.8651 | 1289.1364 | 939.6037 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 824.4091 | 1016.8392 | 913.8651 | 1289.1364 | 939.6037
Resid 30:
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note - all envelope & lighting columns same with ref col 8 to proto tab (no CZ diff) (except sm office first cost)
Large Office |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Large Office | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | 240685.0162 | -34202.2068 | -47978.4667 | -39447.227 | -43950.3141 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 600594 | 600594 | 600594 | 628852 | 628852 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859
Maintenance | 400 | 400 | 400 | 400 | 400 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400
Replacement (Year) | [11 empty] | Replacement (Year)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -81021.5631 | -84518.309 | -158303.2592 | -93634.8139 | -98349.8608 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -81021.5631 | -84518.309 | -158303.2592 | -93634.8139 | -98349.8608
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | -273.2549 | -392.9906 | -400.285 | -3822.2039 | -7011.3539 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | -273.2549 | -392.9906 | -400.285 | -3822.2039 | -7011.3539
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 50649.2979 | 52904.3621 | 100092.1844 | 63752.9825 | 70679.3371 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 50649.2979 | 52904.3621 | 100092.1844 | 63752.9825 | 70679.3371
Resid 30:
30 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902
Standalone Retail |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Standalone Retail | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | -6331.8683 | -4584.6419 | -5460.3332 | -6947.6598 | -10404.3859 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 35588 | 35588 | 35588 | 38691 | 38691 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141
Maintenance | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431
Replacement (Year) | [11 empty] | Replacement (Year)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -7878.9301 | -5890.7574 | -6965.3074 | -8743.0956 | -12960.4361 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -7878.9301 | -5890.7574 | -6965.3074 | -8743.0956 | -12960.4361
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 259496.806 | 0 | -265381.1643 | 5945.1779 | 8487.5129 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 259496.806 | 0 | -265381.1643 | 5945.1779 | 8487.5129
Resid 30:
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 |  |  |  | 5: 0.45188; 6: 1.3983
Primary School |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Primary School | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | 3893.5877 | 5302.1261 | 195.8378 | -16126.592 | -14962.7068 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 94496 | 94496 | 94496 | 117289 | 117289 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932
Maintenance | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462
Replacement (Year) | [11 empty] | Replacement (Year)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -110472.3773 | -1493.6383 | -6141.4228 | -31277.4541 | -30271.0718 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -110472.3773 | -1493.6383 | -6141.4228 | -31277.4541 | -30271.0718
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | -19.2259 | -56.426 | -56.5268 | -1470.335 | -1738.4059 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | -19.2259 | -56.426 | -56.5268 | -1470.335 | -1738.4059
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 74519.8252 | 1874.8645 | 3513.4311 | 19049.0932 | 18852.444 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 74519.8252 | 1874.8645 | 3513.4311 | 19049.0932 | 18852.444
Resid 30:
30 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572
[13 empty] | 0.28027 | 0.57093 | 0.54088 | 0.6505 | 1.4566
Small Hotel |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Small Hotel | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | 2417.55 | 2841.8577 | 1889.9802 | -2100.9186 | -2054.1797 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 69719 | 66558 | 66558 | 70715 | 70715 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203
Maintenance | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338
Replacement (Year) | [11 empty] | Replacement (Year)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 1305.2719 | 1985.9206 | 371.8465 | -4043.3792 | -4056.8571 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 1305.2719 | 1985.9206 | 371.8465 | -4043.3792 | -4056.8571
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 769.4745 | 323.5798 | 1409.1341 | 2771.37 | 2885.3686 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 769.4745 | 323.5798 | 1409.1341 | 2771.37 | 2885.3686
Resid 30:
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-2.2057
Mid-rise Apartment |  |  | HVAC |  |  |  |  | Lighting |  |  |  | Mid-rise Apartment | 2: Envelope, Power and Other; 9: Total
| 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A
New Construction | -22665.6583 | -22980.2112 | -27079.7846 | -33365.0007 | -31978.5206 | 9858 | 9858 | 9858 | 9858 | 9858 |  | New Construction | 45405 | 45405 | 45405 | 50460 | 50460 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Maintenance | 0 | 0 | 0 | 0 | 0 | [6 empty] | Maintenance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replacement (Year) | [11 empty] | Replacement (Year) | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 11307.8344 | 11459.9176 | 13498.9904 | 16629.2345 | 15928.9405 | 0 | 0 | 0 | 0 | 0 |  | 40 | 0 | 0 | 0 | 0 | 0 | 11307.8344 | 11459.9176 | 13498.9904 | 16629.2345 | 15928.9405
Resid 30:
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Energy_Data (hidden)
State Commercial Energy Code Adoption Cost Effectiveness - Energy Data | [19 empty] | 0
There are two table ranges in this sheet, upper table has current state data.
Current_Energy_Data - upper table starting in column B, one set of current state HVAC data (need to remove duplicate rows in energy summary - ask Yulong)
State_Energy_Data - lower table includes all state data - replacement data can be pasted in column B starting below Current_HVAC_ Data
Current State | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Lookup values |  |  |  | Energy Data for Current State | [15 empty] | B. Energy Usage, electricity in kWh, natural gas in kBtu | [18 empty] | C. Energy Cost | [18 empty] | D. Energy Usage mmBtu | [18 empty] | E. EUI kBtu/ft2
|  |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92
Lookup | CZ | Prototype | Fuel Type | Placeholder | A.case.name | A.building | A.std.year | A.climate.city | A.climate.zone | A.climates | A.standard | A.type.anal | A.state.abb | A.elec.price | A.gas.price/kbtu | A.filename | A.bldg | A.loc | A.fuel | B.htg | B.clg | B.intLgt | B.extLgt | B.intEqp | B.extEqp | B.fans | B.pumps | B.heatRej | B.humid | B.heatRec | B.swh | B.refrg | B.gentor | B.total | B.renew | B.sum | B.transLoss | B.extEqp.rev | C.htg | C.clg | C.intLgt | C.extLgt | C.intEqp | C.extEqp | C.fans | C.pumps | C.heatRej | C.humid | C.heatRec | C.swh | C.refrg | C.gentor | C.total | C.renew | C.sum | C.transLoss | C.extEqp.rev | D.htg | D.clg | D.intLgt | D.extLgt | D.intEqp | D.extEqp | D.fans | D.pumps | D.heatRej | D.humid | D.heatRec | D.swh | D.refrg | D.gentor | D.total | D.renew | D.sum | D.transLoss | D.extEqp.rev | E.intLgt | E.extLgt | E.plug | E.fans | E.pumps | E.heatRec | E.clg | E.htg | E.swh | E.humid | E.refrg | E.sum | E.total | E.add | F.code.comp
US_2A_SO_2022_EL | 2A | SO | EL | 0 | 0 | OfficeSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 77.7778 | 9777.7779 | 5391.6667 | 1927.7778 | 13416.6668 | 0 | 5150 | 0 | 0 | 0 | 0 | 6505.5556 | 0 | 0 | 42247.2226 | 805.8333 | 41441.3892 | 0 | 0 | 8.5478 | 1074.5778 | 592.5442 | 211.8628 | 1474.4917 | 0 | 565.985 | 0 | 0 | 0 | 0 | 714.9606 | 0 | 0 | 4642.9698 | 88.5611 | 4554.4087 | 0 | 0 | 0.26545 | 33.3713 | 18.4016 | 6.5794 | 45.7907 | 0 | 17.5768 | 0 | 0 | 0 | 0 | 22.2033 | 0 | 0 | 144.1885 | 2.7503 | 141.5434 | 0 | 0 | 3.3445 | 1.1958 | 8.3225 | 3.1946 | 0 | 0 | 6.0653 | 0.048247 | 4.0355 | 0 | 0 | 25.7258 | 26.2066 | 26.2066
US_2A_SO_2019_EL | 2A | SO | EL | 0 | 0 | OfficeSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 83.3333 | 10700.0001 | 7394.4445 | 2744.4445 | 13416.6668 | 0 | 5336.1112 | 0 | 0 | 0 | 0 | 6502.7778 | 0 | 0 | 46177.7781 | 0 | 46177.7781 | 0 | 0 | 9.1583 | 1175.93 | 812.6495 | 301.6144 | 1474.4917 | 0 | 586.4386 | 0 | 0 | 0 | 0 | 714.6553 | 0 | 0 | 5074.9378 | 0 | 5074.9378 | 0 | 0 | 0.28441 | 36.5188 | 25.237 | 9.3667 | 45.7907 | 0 | 18.212 | 0 | 0 | 0 | 0 | 22.1938 | 0 | 0 | 157.6033 | 0 | 157.5957 | 0 | 0 | 4.5869 | 1.7024 | 8.3225 | 3.3101 | 0 | 0 | 6.6374 | 0.051693 | 4.0338 | 0 | 0 | 28.6434 | 28.6447 | 28.6447
US_2A_SO_2022_NG | 2A | SO | NG | 0 | 0 | OfficeSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_2A_SO_2019_NG | 2A | SO | NG | 0 | 0 | OfficeSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_3A_SO_2022_EL | 3A | SO | EL | 0 | 0 | OfficeSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 1666.6667 | 5197.2223 | 5413.8889 | 1941.6667 | 13416.6668 | 0 | 4947.2223 | 0 | 0 | 0 | 0 | 6697.2223 | 0 | 0 | 39280.5559 | 779.7222 | 38500.8336 | 0 | 0 | 183.1667 | 571.1747 | 594.9864 | 213.3892 | 1474.4917 | 0 | 543.6997 | 0 | 0 | 0 | 0 | 736.0247 | 0 | 0 | 4316.9331 | 85.6915 | 4231.2416 | 0 | 0 | 5.6883 | 17.738 | 18.4774 | 6.6268 | 45.7907 | 0 | 16.8847 | 0 | 0 | 0 | 0 | 22.8574 | 0 | 0 | 134.0633 | 2.6612 | 131.5121 | 0 | 0 | 3.3583 | 1.2044 | 8.3225 | 3.0688 | 0 | 0 | 3.2239 | 1.0339 | 4.1544 | 0 | 0 | 23.9026 | 24.3663 | 24.3663
US_3A_SO_2019_EL | 3A | SO | EL | 0 | 0 | OfficeSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 1727.7778 | 5725 | 7427.7778 | 2766.6667 | 13416.6668 | 0 | 5163.8889 | 0 | 0 | 0 | 0 | 6694.4445 | 0 | 0 | 42922.2226 | 0 | 42922.2226 | 0 | 0 | 189.8828 | 629.1775 | 816.3128 | 304.0567 | 1474.4917 | 0 | 567.5114 | 0 | 0 | 0 | 0 | 735.7195 | 0 | 0 | 4717.1523 | 0 | 4717.1523 | 0 | 0 | 5.8969 | 19.5392 | 25.3508 | 9.4425 | 45.7907 | 0 | 17.6242 | 0 | 0 | 0 | 0 | 22.8479 | 0 | 0 | 146.4922 | 0 | 146.4998 | 0 | 0 | 4.6076 | 1.7162 | 8.3225 | 3.2032 | 0 | 0 | 3.5513 | 1.0718 | 4.1527 | 0 | 0 | 26.6266 | 26.6253 | 26.6253
US_3A_SO_2022_NG | 3A | SO | NG | 0 | 0 | OfficeSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 1516.5074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1516.5074 | 0 | 1516.5074 | 0 | 0 | 14.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9073 | 0 | 14.9073 | 0 | 0 | 1.5165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5165 | 0 | 1.5165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27563 | 0 | 0 | 0 | 0.27563 | 0.27563 | 0.27563
US_3A_SO_2019_NG | 3A | SO | NG | 0 | 0 | OfficeSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 1573.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3764 | 0 | 1573.3764 | 0 | 0 | 15.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4663 | 0 | 15.4663 | 0 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5734 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28596 | 0 | 0 | 0 | 0.28596 | 0.28596 | 0.28596
US_3B_SO_2022_EL | 3B | SO | EL | 0 | 0 | OfficeSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 702.7778 | 5880.5556 | 5458.3334 | 1911.1111 | 13416.6668 | 0 | 5855.5556 | 0 | 0 | 0 | 0 | 6644.4445 | 0 | 0 | 39869.4448 | 937.7778 | 38931.667 | 0 | 0 | 77.2353 | 646.2731 | 599.8708 | 210.0311 | 1474.4917 | 0 | 643.5256 | 0 | 0 | 0 | 0 | 730.2245 | 0 | 0 | 4381.652 | 103.0618 | 4278.5902 | 0 | 0 | 2.3986 | 20.0702 | 18.6291 | 6.5226 | 45.7907 | 0 | 19.9848 | 0 | 0 | 0 | 0 | 22.6773 | 0 | 0 | 136.0732 | 3.2006 | 133.0081 | 0 | 0 | 3.3859 | 1.1855 | 8.3225 | 3.6323 | 0 | 0 | 3.6478 | 0.43594 | 4.1216 | 0 | 0 | 24.1745 | 24.7316 | 24.7316
US_3B_SO_2019_EL | 3B | SO | EL | 0 | 0 | OfficeSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 702.7778 | 6463.8889 | 7444.4445 | 2722.2222 | 13416.6668 | 0 | 6102.7778 | 0 | 0 | 0 | 0 | 6644.4445 | 0 | 0 | 43497.2226 | 0 | 43497.2226 | 0 | 0 | 77.2353 | 710.3814 | 818.1445 | 299.1722 | 1474.4917 | 0 | 670.6953 | 0 | 0 | 0 | 0 | 730.2245 | 0 | 0 | 4780.3448 | 0 | 4780.3448 | 0 | 0 | 2.3986 | 22.0611 | 25.4077 | 9.2909 | 45.7907 | 0 | 20.8286 | 0 | 0 | 0 | 0 | 22.6773 | 0 | 0 | 148.4547 | 0 | 148.4585 | 0 | 0 | 4.6179 | 1.6886 | 8.3225 | 3.7856 | 0 | 0 | 4.0096 | 0.43594 | 4.1216 | 0 | 0 | 26.9826 | 26.9819 | 26.9819
US_3B_SO_2022_NG | 3B | SO | NG | 0 | 0 | OfficeSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 217.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217.9979 | 0 | 217.9979 | 0 | 0 | 2.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1429 | 0 | 2.1429 | 0 | 0 | 0.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.218 | 0 | 0.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039622 | 0 | 0 | 0 | 0.039622 | 0.039622 | 0.039622
US_3B_SO_2019_NG | 3B | SO | NG | 0 | 0 | OfficeSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 208.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.5198 | 0 | 208.5198 | 0 | 0 | 2.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0497 | 0 | 2.0497 | 0 | 0 | 0.20852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20852 | 0 | 0.20852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037899 | 0 | 0 | 0 | 0.037899 | 0.037899 | 0.037899
US_4A_SO_2022_EL | 4A | SO | EL | 0 | 0 | OfficeSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 2916.6667 | 3908.3334 | 5352.7778 | 1927.7778 | 13416.6668 | 0 | 4636.1111 | 0 | 0 | 0 | 0 | 6844.4445 | 0 | 0 | 39002.7781 | 676.1111 | 38326.667 | 0 | 0 | 320.5417 | 429.5258 | 588.2703 | 211.8628 | 1474.4917 | 0 | 509.5086 | 0 | 0 | 0 | 0 | 752.2045 | 0 | 0 | 4286.4053 | 74.3046 | 4212.1007 | 0 | 0 | 9.9545 | 13.339 | 18.2689 | 6.5794 | 45.7907 | 0 | 15.8229 | 0 | 0 | 0 | 0 | 23.3599 | 0 | 0 | 133.1153 | 2.3075 | 130.9139 | 0 | 0 | 3.3204 | 1.1958 | 8.3225 | 2.8758 | 0 | 0 | 2.4244 | 1.8092 | 4.2457 | 0 | 0 | 23.7939 | 24.194 | 24.194
US_4A_SO_2019_EL | 4A | SO | EL | 0 | 0 | OfficeSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 3341.6667 | 4291.6667 | 7344.4445 | 2744.4445 | 13416.6668 | 0 | 4922.2223 | 0 | 0 | 0 | 0 | 6844.4445 | 0 | 0 | 42905.5559 | 0 | 42905.5559 | 0 | 0 | 367.2492 | 471.6542 | 807.1545 | 301.6144 | 1474.4917 | 0 | 540.9522 | 0 | 0 | 0 | 0 | 752.2045 | 0 | 0 | 4715.3206 | 0 | 4715.3206 | 0 | 0 | 11.405 | 14.6473 | 25.0664 | 9.3667 | 45.7907 | 0 | 16.7994 | 0 | 0 | 0 | 0 | 23.3599 | 0 | 0 | 146.4353 | 0 | 146.4306 | 0 | 0 | 4.5559 | 1.7024 | 8.3225 | 3.0533 | 0 | 0 | 2.6622 | 2.0729 | 4.2457 | 0 | 0 | 26.6141 | 26.6149 | 26.6149
US_4A_SO_2022_NG | 4A | SO | NG | 0 | 0 | OfficeSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 2549.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2549.6281 | 0 | 2549.6281 | 0 | 0 | 25.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0628 | 0 | 25.0628 | 0 | 0 | 2.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5496 | 0 | 2.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4634 | 0 | 0 | 0 | 0.4634 | 0.4634 | 0.4634
US_4A_SO_2019_NG | 4A | SO | NG | 0 | 0 | OfficeSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 3004.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3004.5803 | 0 | 3004.5803 | 0 | 0 | 29.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.535 | 0 | 29.535 | 0 | 0 | 3.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0046 | 0 | 3.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54609 | 0 | 0 | 0 | 0.54609 | 0.54609 | 0.54609
US_5A_SO_2022_EL | 5A | SO | EL | 0 | 0 | OfficeSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 4813.8889 | 2219.4445 | 5347.2223 | 1938.8889 | 13416.6668 | 0 | 4625 | 0 | 0 | 0 | 0 | 6969.4445 | 0 | 0 | 39330.5559 | 651.1111 | 38679.4448 | 0 | 0 | 529.0464 | 243.9169 | 587.6597 | 213.0839 | 1474.4917 | 0 | 508.2875 | 0 | 0 | 0 | 0 | 765.942 | 0 | 0 | 4322.4281 | 71.5571 | 4250.871 | 0 | 0 | 16.4297 | 7.5749 | 18.2499 | 6.6174 | 45.7907 | 0 | 15.785 | 0 | 0 | 0 | 0 | 23.7865 | 0 | 0 | 134.234 | 2.2222 | 132.1217 | 0 | 0 | 3.317 | 1.2027 | 8.3225 | 2.869 | 0 | 0 | 1.3768 | 2.9861 | 4.3232 | 0 | 0 | 24.0134 | 24.3973 | 24.3973
US_5A_SO_2019_EL | 5A | SO | EL | 0 | 0 | OfficeSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 5533.3334 | 2558.3334 | 7336.1112 | 2763.8889 | 13416.6668 | 0 | 4941.6667 | 0 | 0 | 0 | 0 | 6969.4445 | 0 | 0 | 43519.4448 | 0 | 43519.4448 | 0 | 0 | 608.1133 | 281.1608 | 806.2386 | 303.7514 | 1474.4917 | 0 | 543.0892 | 0 | 0 | 0 | 0 | 765.942 | 0 | 0 | 4782.787 | 0 | 4782.787 | 0 | 0 | 18.8851 | 8.7315 | 25.0379 | 9.4331 | 45.7907 | 0 | 16.8658 | 0 | 0 | 0 | 0 | 23.7865 | 0 | 0 | 148.5305 | 0 | 148.5144 | 0 | 0 | 4.5507 | 1.7145 | 8.3225 | 3.0654 | 0 | 0 | 1.587 | 3.4324 | 4.3232 | 0 | 0 | 26.9928 | 26.9957 | 26.9957
US_5A_SO_2022_NG | 5A | SO | NG | 0 | 0 | OfficeSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 11440.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11440.1526 | 0 | 11440.1526 | 0 | 0 | 112.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4567 | 0 | 112.4567 | 0 | 0 | 11.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4402 | 0 | 11.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0793 | 0 | 0 | 0 | 2.0793 | 2.0793 | 2.0793
US_5A_SO_2019_NG | 5A | SO | NG | 0 | 0 | OfficeSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 13155.7016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13155.7016 | 0 | 13155.7016 | 0 | 0 | 129.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.3205 | 0 | 129.3205 | 0 | 0 | 13.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1557 | 0 | 13.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3911 | 0 | 0 | 0 | 2.3911 | 2.3911 | 2.3911
US_2A_LO_2022_EL | 2A | LO | EL | 0 | 0 | OfficeLarge | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 1191736.1206 | 475586.1149 | 73427.7784 | 4076777.8104 | 334358.336 | 563352.7823 | 179419.4459 | 431069.4479 | 94055.5563 | 14058.3334 | 0 | 0 | 0 | 7433841.7261 | 157366.6679 | 7276475.0582 | 0 | 334358.336 | 0 | 130971.7997 | 52266.914 | 8069.7128 | 448037.8814 | 36745.9811 | 61912.4708 | 19718.1971 | 47374.5323 | 10336.7056 | 1545.0108 | 0 | 0 | 0 | 816979.2057 | 17294.5968 | 799684.6089 | 0 | 36745.9811 | 0 | 4067.3584 | 1623.1607 | 250.6067 | 13913.9163 | 1141.1546 | 1922.7056 | 612.353 | 1471.2267 | 321.0087 | 47.9807 | 0 | 0 | 0 | 25371.4714 | 537.0876 | 24856.9559 | 0 | 1141.1546 | 3.2555 | 0.50263 | 30.1954 | 3.8563 | 1.2282 | 0.096233 | 11.1085 | 0 | 0 | 0.64384 | 0 | 49.8547 | 50.8866 | 50.8866
US_2A_LO_2019_EL | 2A | LO | EL | 0 | 0 | OfficeLarge | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 1278305.5658 | 682308.3388 | 97358.3341 | 4076777.8104 | 530358.3376 | 578358.338 | 186600.0015 | 441794.448 | 94158.3341 | 14030.5557 | 0 | 0 | 0 | 7980050.0638 | 0 | 7980050.0638 | 0 | 530358.3376 | 0 | 140485.7817 | 74985.6864 | 10699.6809 | 448037.8814 | 58286.3813 | 63561.5813 | 20507.3402 | 48553.2098 | 10348.0009 | 1541.9581 | 0 | 0 | 0 | 877007.502 | 0 | 877007.502 | 0 | 58286.3813 | 0 | 4362.8173 | 2328.6972 | 332.281 | 13913.9163 | 1810.0966 | 1973.9191 | 636.86 | 1507.8308 | 321.3595 | 47.8859 | 0 | 0 | 0 | 27235.6635 | 0 | 27235.6606 | 0 | 1810.0966 | 4.6706 | 0.66644 | 31.5371 | 3.959 | 1.2773 | 0.096043 | 11.7745 | 0 | 0 | 0.64454 | 0 | 54.6256 | 54.6256 | 54.6256
US_2A_LO_2022_NG | 2A | LO | NG | 0 | 0 | OfficeLarge | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 63503.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611228.3043 | 0 | 0 | 674732.0514 | 0 | 674732.0514 | 0 | 0 | 624.2418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6008.3742 | 0 | 0 | 6632.6161 | 0 | 6632.6161 | 0 | 0 | 63.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611.2283 | 0 | 0 | 674.7321 | 0 | 674.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12737 | 1.2259 | 0 | 0 | 1.3533 | 1.3533 | 1.3533
US_2A_LO_2019_NG | 2A | LO | NG | 0 | 0 | OfficeLarge | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 70925.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611218.8262 | 0 | 0 | 682143.9813 | 0 | 682143.9813 | 0 | 0 | 697.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6008.2811 | 0 | 0 | 6705.4753 | 0 | 6705.4753 | 0 | 0 | 70.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611.2188 | 0 | 0 | 682.144 | 0 | 682.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14225 | 1.2259 | 0 | 0 | 1.3682 | 1.3682 | 1.3682
US_3A_LO_2022_EL | 3A | LO | EL | 0 | 0 | OfficeLarge | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 748405.5615 | 476594.4483 | 73952.7784 | 4076777.8104 | 334358.336 | 624638.8939 | 127863.8899 | 281800.0023 | 266638.891 | 10869.4445 | 0 | 0 | 0 | 7021900.0562 | 152267.779 | 6869632.2772 | 0 | 334358.336 | 0 | 82249.7712 | 52377.7299 | 8127.4103 | 448037.8814 | 36745.9811 | 68647.8144 | 14052.2415 | 30969.8202 | 29303.6141 | 1194.552 | 0 | 0 | 0 | 771706.8162 | 16734.2289 | 754972.5873 | 0 | 36745.9811 | 0 | 2554.285 | 1626.6021 | 252.3985 | 13913.9163 | 1141.1546 | 2131.8732 | 436.3955 | 961.7747 | 910.0303 | 37.0971 | 0 | 0 | 0 | 23965.5272 | 519.6852 | 23468.0092 | 0 | 1141.1546 | 3.2624 | 0.50623 | 30.1954 | 4.2758 | 0.87526 | 0.074404 | 7.052 | 0 | 0 | 1.8252 | 0 | 47.0689 | 48.0668 | 48.0668
US_3A_LO_2019_EL | 3A | LO | EL | 0 | 0 | OfficeLarge | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 807900.0065 | 683780.561 | 98152.7786 | 4076777.8104 | 530358.3376 | 646741.6718 | 134530.5566 | 287894.4467 | 266897.2244 | 10752.7779 | 0 | 0 | 0 | 7543786.1715 | 0 | 7543786.1715 | 0 | 530358.3376 | 0 | 88788.2107 | 75147.4837 | 10786.9904 | 448037.8814 | 58286.3813 | 71076.9097 | 14784.9082 | 31639.5997 | 29332.005 | 1181.7303 | 0 | 0 | 0 | 829062.1002 | 0 | 829062.1002 | 0 | 58286.3813 | 0 | 2757.3377 | 2333.7219 | 334.9924 | 13913.9163 | 1810.0966 | 2207.3093 | 459.1486 | 982.5748 | 910.912 | 36.6989 | 0 | 0 | 0 | 25746.7083 | 0 | 25746.7083 | 0 | 1810.0966 | 4.6807 | 0.67188 | 31.5371 | 4.4271 | 0.9209 | 0.073606 | 7.501 | 0 | 0 | 1.827 | 0 | 51.6392 | 51.6392 | 51.6392
US_3A_LO_2022_NG | 3A | LO | NG | 0 | 0 | OfficeLarge | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 381600.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670372.0926 | 0 | 0 | 1051972.7433 | 0 | 1051972.7433 | 0 | 0 | 3751.1344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6589.7577 | 0 | 0 | 10340.8921 | 0 | 10340.8921 | 0 | 0 | 381.6007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670.3721 | 0 | 0 | 1051.9727 | 0 | 1051.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76536 | 1.3445 | 0 | 0 | 2.1099 | 2.1099 | 2.1099
US_3A_LO_2019_NG | 3A | LO | NG | 0 | 0 | OfficeLarge | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 418224.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670353.1363 | 0 | 0 | 1088577.4405 | 0 | 1088577.4405 | 0 | 0 | 4111.1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6589.5713 | 0 | 0 | 10700.7162 | 0 | 10700.7162 | 0 | 0 | 418.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670.3531 | 0 | 0 | 1088.5774 | 0 | 1088.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83882 | 1.3445 | 0 | 0 | 2.1833 | 2.1833 | 2.1833
US_3B_LO_2022_EL | 3B | LO | EL | 0 | 0 | OfficeLarge | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 815747.2287 | 490958.3373 | 72950.0006 | 4076777.8104 | 334363.8916 | 734255.5614 | 135425.0011 | 263938.891 | 496616.6706 | 0 | 0 | 0 | 0 | 7421033.3927 | 183140.557 | 7237892.8357 | 0 | 334363.8916 | 0 | 89650.6204 | 53956.3213 | 8017.2051 | 448037.8814 | 36746.5917 | 80694.6862 | 14883.2076 | 29006.8841 | 54578.1721 | 0 | 0 | 0 | 0 | 815571.5699 | 20127.1472 | 795444.4226 | 0 | 36746.5917 | 0 | 2784.12 | 1675.6256 | 248.9761 | 13913.9163 | 1141.1736 | 2505.9915 | 462.2013 | 900.8153 | 1694.9373 | 0 | 0 | 0 | 0 | 25327.7569 | 625.053 | 24728.4263 | 0 | 1141.1736 | 3.3607 | 0.49936 | 30.1955 | 5.0262 | 0.92702 | 0 | 7.3907 | 0 | 0 | 3.3995 | 0 | 49.5969 | 50.799 | 50.799
US_3B_LO_2019_EL | 3B | LO | EL | 0 | 0 | OfficeLarge | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 879747.2293 | 682994.4499 | 96608.3341 | 4076777.8104 | 530358.3376 | 758438.895 | 139966.6678 | 267875.0021 | 496619.4484 | 0 | 0 | 0 | 0 | 7929386.1745 | 0 | 7929386.1745 | 0 | 530358.3376 | 0 | 96684.2205 | 75061.09 | 10617.2559 | 448037.8814 | 58286.3813 | 83352.4346 | 15382.3368 | 29439.4627 | 54578.4774 | 0 | 0 | 0 | 0 | 871439.5406 | 0 | 871439.5406 | 0 | 58286.3813 | 0 | 3002.55 | 2331.0389 | 329.7212 | 13913.9163 | 1810.0966 | 2588.5284 | 477.7019 | 914.2491 | 1694.9468 | 0 | 0 | 0 | 0 | 27062.7492 | 0 | 27062.7369 | 0 | 1810.0966 | 4.6753 | 0.66131 | 31.5371 | 5.1917 | 0.95811 | 0 | 7.8558 | 0 | 0 | 3.3995 | 0 | 54.2788 | 54.2788 | 54.2788
US_3B_LO_2022_NG | 3B | LO | NG | 0 | 0 | OfficeLarge | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 328191.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655225.9751 | 0 | 0 | 983417.131 | 0 | 983417.131 | 0 | 0 | 3226.1191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6440.8713 | 0 | 0 | 9666.9904 | 0 | 9666.9904 | 0 | 0 | 328.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.226 | 0 | 0 | 983.4171 | 0 | 983.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65824 | 1.3142 | 0 | 0 | 1.9724 | 1.9724 | 1.9724
US_3B_LO_2019_NG | 3B | LO | NG | 0 | 0 | OfficeLarge | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 371563.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655216.4969 | 0 | 0 | 1026779.7643 | 0 | 1026779.7643 | 0 | 0 | 3652.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6440.7782 | 0 | 0 | 10093.2451 | 0 | 10093.2451 | 0 | 0 | 371.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.2165 | 0 | 0 | 1026.7798 | 0 | 1026.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74523 | 1.3141 | 0 | 0 | 2.0594 | 2.0594 | 2.0594
US_4A_LO_2022_EL | 4A | LO | EL | 0 | 0 | OfficeLarge | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 557408.3378 | 476997.226 | 73786.1117 | 4076777.8104 | 334358.336 | 599333.3381 | 108847.2231 | 198902.7794 | 350380.5584 | 12130.5557 | 0 | 0 | 0 | 6788922.2765 | 132035.2788 | 6656886.9977 | 0 | 334358.336 | 0 | 61259.1763 | 52421.9951 | 8109.0937 | 448037.8814 | 36745.9811 | 65866.7339 | 11962.3098 | 21859.4155 | 38506.8234 | 1333.1481 | 0 | 0 | 0 | 746102.5582 | 14510.6771 | 731591.881 | 0 | 36745.9811 | 0 | 1902.4174 | 1627.9767 | 251.8297 | 13913.9163 | 1141.1546 | 2045.5061 | 371.4922 | 678.849 | 1195.838 | 41.4012 | 0 | 0 | 0 | 23170.3813 | 450.6323 | 22739.803 | 0 | 1141.1546 | 3.2652 | 0.50509 | 30.1954 | 4.1026 | 0.74509 | 0.083037 | 5.1772 | 0 | 0 | 2.3984 | 0 | 45.6084 | 46.472 | 46.472
US_4A_LO_2019_EL | 4A | LO | EL | 0 | 0 | OfficeLarge | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 601619.4493 | 684355.561 | 97658.3341 | 4076777.8104 | 530358.3376 | 617022.2272 | 113919.4454 | 203600.0016 | 350750.0028 | 12013.889 | 0 | 0 | 0 | 7288075.0583 | 0 | 7288075.0583 | 0 | 530358.3376 | 0 | 66117.9775 | 75210.6762 | 10732.6509 | 448037.8814 | 58286.3813 | 67810.7428 | 12519.747 | 22375.6402 | 38547.4253 | 1320.3264 | 0 | 0 | 0 | 800959.4489 | 0 | 800959.4489 | 0 | 58286.3813 | 0 | 2053.3085 | 2335.6843 | 333.3049 | 13913.9163 | 1810.0966 | 2105.8777 | 388.8035 | 694.8805 | 1197.0989 | 41.003 | 0 | 0 | 0 | 24873.9742 | 0 | 24873.9581 | 0 | 1810.0966 | 4.6846 | 0.6685 | 31.5371 | 4.2237 | 0.77981 | 0.082238 | 5.5119 | 0 | 0 | 2.401 | 0 | 49.8888 | 49.8888 | 49.8888
US_4A_LO_2022_NG | 4A | LO | NG | 0 | 0 | OfficeLarge | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 690731.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716985.7386 | 0 | 0 | 1407716.943 | 0 | 1407716.943 | 0 | 0 | 6789.8877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7047.9698 | 0 | 0 | 13837.8575 | 0 | 13837.8575 | 0 | 0 | 690.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.9857 | 0 | 0 | 1407.7169 | 0 | 1407.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3854 | 1.438 | 0 | 0 | 2.8234 | 2.8234 | 2.8234
US_4A_LO_2019_NG | 4A | LO | NG | 0 | 0 | OfficeLarge | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 853575.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716957.3041 | 0 | 0 | 1570532.9678 | 0 | 1570532.9678 | 0 | 0 | 8390.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7047.6903 | 0 | 0 | 15438.3391 | 0 | 15438.3391 | 0 | 0 | 853.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.9573 | 0 | 0 | 1570.533 | 0 | 1570.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.712 | 1.438 | 0 | 0 | 3.15 | 3.15 | 3.15
US_5A_LO_2022_EL | 5A | LO | EL | 0 | 0 | OfficeLarge | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 387850.0031 | 476502.7816 | 74002.7784 | 4076777.8104 | 334358.336 | 603352.7826 | 85550.0007 | 142841.6678 | 401177.781 | 10480.5556 | 0 | 0 | 0 | 6592894.4972 | 127149.7232 | 6465744.7739 | 0 | 334358.336 | 0 | 42624.7153 | 52367.6557 | 8132.9053 | 448037.8814 | 36745.9811 | 66308.4708 | 9401.9451 | 15698.2993 | 44089.4381 | 1151.8131 | 0 | 0 | 0 | 724559.1052 | 13973.7546 | 710585.3507 | 0 | 36745.9811 | 0 | 1323.72 | 1626.2892 | 252.5692 | 13913.9163 | 1141.1546 | 2059.2243 | 291.9795 | 487.5142 | 1369.2073 | 35.7698 | 0 | 0 | 0 | 22501.3445 | 433.9581 | 22086.9068 | 0 | 1141.1546 | 3.2618 | 0.50657 | 30.1954 | 4.1301 | 0.58561 | 0.071742 | 3.6327 | 0 | 0 | 2.7462 | 0 | 44.2989 | 45.1301 | 45.1301
US_5A_LO_2019_EL | 5A | LO | EL | 0 | 0 | OfficeLarge | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 440350.0035 | 683655.561 | 98133.3341 | 4076777.8104 | 530358.3376 | 620355.5605 | 90044.4452 | 147002.779 | 401683.3365 | 10333.3334 | 0 | 0 | 0 | 7098694.5012 | 0 | 7098694.5012 | 0 | 530358.3376 | 0 | 48394.4654 | 75133.7462 | 10784.8534 | 448037.8814 | 58286.3813 | 68177.0761 | 9895.8845 | 16155.6054 | 44144.9987 | 1135.6333 | 0 | 0 | 0 | 780146.5257 | 0 | 780146.5257 | 0 | 58286.3813 | 0 | 1502.9009 | 2333.2952 | 334.926 | 13913.9163 | 1810.0966 | 2117.2543 | 307.3189 | 501.7159 | 1370.9328 | 35.2673 | 0 | 0 | 0 | 24227.6243 | 0 | 24227.6366 | 0 | 1810.0966 | 4.6798 | 0.67175 | 31.5371 | 4.2465 | 0.61638 | 0.070734 | 4.0206 | 0 | 0 | 2.7496 | 0 | 48.5925 | 48.5925 | 48.5925
US_5A_LO_2022_NG | 5A | LO | NG | 0 | 0 | OfficeLarge | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 1197235.1951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756519.1907 | 0 | 0 | 1953754.3858 | 0 | 1953754.3858 | 0 | 0 | 11768.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7436.5836 | 0 | 0 | 19205.4056 | 0 | 19205.4056 | 0 | 0 | 1197.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.5192 | 0 | 0 | 1953.7544 | 0 | 1953.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4013 | 1.5173 | 0 | 0 | 3.9186 | 3.9186 | 3.9186
US_5A_LO_2019_NG | 5A | LO | NG | 0 | 0 | OfficeLarge | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 1472301.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756481.278 | 0 | 0 | 2228782.4795 | 0 | 2228782.4795 | 0 | 0 | 14472.7208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7436.211 | 0 | 0 | 21908.9318 | 0 | 21908.9318 | 0 | 0 | 1472.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.4813 | 0 | 0 | 2228.7825 | 0 | 2228.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9529 | 1.5172 | 0 | 0 | 4.4702 | 4.4702 | 4.4702
US_2A_RS_2022_EL | 2A | RS | EL | 0 | 0 | RetailStandalone | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 84894.4451 | 46583.3337 | 8225.0001 | 53972.2227 | 0 | 32805.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226480.5574 | 21709.1668 | 204771.3905 | 0 | 0 | 0 | 9329.8995 | 5119.5084 | 903.9275 | 5931.5473 | 0 | 3605.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24890.2133 | 2385.8374 | 22504.3758 | 0 | 0 | 0 | 289.7421 | 158.9875 | 28.0717 | 184.2055 | 0 | 111.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772.9711 | 74.0927 | 701.9965 | 0 | 0 | 6.4388 | 1.1369 | 7.4601 | 4.5344 | 0 | 0 | 11.7343 | 0 | 0 | 0 | 0 | 28.4301 | 31.3045 | 31.3045
US_2A_RS_2019_EL | 2A | RS | EL | 0 | 0 | RetailStandalone | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 98269.4452 | 62308.3338 | 12102.7779 | 53972.2227 | 0 | 35091.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261744.4465 | 0 | 261744.4465 | 0 | 0 | 0 | 10799.812 | 6847.6859 | 1330.0953 | 5931.5473 | 0 | 3856.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28765.7147 | 0 | 28765.7147 | 0 | 0 | 0 | 335.3906 | 212.6564 | 41.3064 | 184.2055 | 0 | 119.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3257 | 0 | 893.3361 | 0 | 0 | 8.6124 | 1.6729 | 7.4601 | 4.8504 | 0 | 0 | 13.583 | 0 | 0 | 0 | 0 | 36.1792 | 36.1787 | 36.1787
US_2A_RS_2022_NG | 2A | RS | NG | 0 | 0 | RetailStandalone | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 9222.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83000.3452 | 0 | 0 | 92222.6058 | 0 | 92222.6058 | 0 | 0 | 90.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815.8934 | 0 | 0 | 906.5482 | 0 | 906.5482 | 0 | 0 | 9.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0003 | 0 | 0 | 92.2226 | 0 | 92.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37349 | 3.3614 | 0 | 0 | 3.7349 | 3.7349 | 3.7349
US_2A_RS_2019_NG | 2A | RS | NG | 0 | 0 | RetailStandalone | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 16198.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83000.3452 | 0 | 0 | 99198.5398 | 0 | 99198.5398 | 0 | 0 | 159.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815.8934 | 0 | 0 | 975.1216 | 0 | 975.1216 | 0 | 0 | 16.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0003 | 0 | 0 | 99.1985 | 0 | 99.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65601 | 3.3614 | 0 | 0 | 4.0174 | 4.0174 | 4.0174
US_3A_RS_2022_EL | 3A | RS | EL | 0 | 0 | RetailStandalone | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 46230.5559 | 40625.0003 | 8230.5556 | 53972.2227 | 0 | 35716.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184775.0015 | 21005.8335 | 163769.168 | 0 | 0 | 0 | 5080.7381 | 4464.6875 | 904.5381 | 5931.5473 | 0 | 3925.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20306.7727 | 2308.5411 | 17998.2316 | 0 | 0 | 0 | 157.7835 | 138.6519 | 28.0906 | 184.2055 | 0 | 121.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630.6314 | 71.6923 | 561.9946 | 0 | 0 | 5.6153 | 1.1376 | 7.4601 | 4.9368 | 0 | 0 | 6.3901 | 0 | 0 | 0 | 0 | 22.7602 | 25.5399 | 25.5399
US_3A_RS_2019_EL | 3A | RS | EL | 0 | 0 | RetailStandalone | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 54113.8893 | 62802.7783 | 12113.889 | 53972.2227 | 0 | 35272.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218275.0017 | 0 | 218275.0017 | 0 | 0 | 0 | 5947.1164 | 6902.0253 | 1331.3164 | 5931.5473 | 0 | 3876.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23988.4227 | 0 | 23988.4227 | 0 | 0 | 0 | 184.689 | 214.3439 | 41.3443 | 184.2055 | 0 | 120.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744.9658 | 0 | 744.9668 | 0 | 0 | 8.6807 | 1.6744 | 7.4601 | 4.8754 | 0 | 0 | 7.4797 | 0 | 0 | 0 | 0 | 30.1704 | 30.1703 | 30.1703
US_3A_RS_2022_NG | 3A | RS | NG | 0 | 0 | RetailStandalone | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 149271.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86564.1376 | 0 | 0 | 235835.8558 | 0 | 235835.8558 | 0 | 0 | 1467.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850.9255 | 0 | 0 | 2318.2665 | 0 | 2318.2665 | 0 | 0 | 149.2717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5641 | 0 | 0 | 235.8359 | 0 | 235.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0453 | 3.5058 | 0 | 0 | 9.5511 | 9.5511 | 9.5511
US_3A_RS_2019_NG | 3A | RS | NG | 0 | 0 | RetailStandalone | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 186511.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86564.1376 | 0 | 0 | 273075.5904 | 0 | 273075.5904 | 0 | 0 | 1833.4076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850.9255 | 0 | 0 | 2684.3331 | 0 | 2684.3331 | 0 | 0 | 186.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5641 | 0 | 0 | 273.0756 | 0 | 273.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5535 | 3.5058 | 0 | 0 | 11.0593 | 11.0593 | 11.0593
US_3B_RS_2022_EL | 3B | RS | EL | 0 | 0 | RetailStandalone | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 47222.2226 | 48436.1115 | 8230.5556 | 53972.2227 | 0 | 39683.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197544.446 | 25264.7224 | 172279.7236 | 0 | 0 | 0 | 5189.7223 | 5323.1287 | 904.5381 | 5931.5473 | 0 | 4361.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21710.1346 | 2776.593 | 18933.5416 | 0 | 0 | 0 | 161.168 | 165.3109 | 28.0906 | 184.2055 | 0 | 135.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.2131 | 86.2277 | 591.5358 | 0 | 0 | 6.6949 | 1.1376 | 7.4601 | 5.4851 | 0 | 0 | 6.5271 | 0 | 0 | 0 | 0 | 23.9566 | 27.3049 | 27.3049
US_3B_RS_2019_EL | 3B | RS | EL | 0 | 0 | RetailStandalone | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 54041.6671 | 64861.1116 | 12111.1112 | 53972.2227 | 0 | 38888.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223875.0018 | 0 | 223875.0018 | 0 | 0 | 0 | 5939.1792 | 7128.2362 | 1331.0111 | 5931.5473 | 0 | 4273.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24603.8627 | 0 | 24603.8627 | 0 | 0 | 0 | 184.4425 | 221.369 | 41.3348 | 184.2055 | 0 | 132.7266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0784 | 0 | 764.0822 | 0 | 0 | 8.9652 | 1.674 | 7.4601 | 5.3753 | 0 | 0 | 7.4697 | 0 | 0 | 0 | 0 | 30.9445 | 30.9444 | 30.9444
US_3B_RS_2022_NG | 3B | RS | NG | 0 | 0 | RetailStandalone | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 48130.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85625.7986 | 0 | 0 | 133755.952 | 0 | 133755.952 | 0 | 0 | 473.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.7016 | 0 | 0 | 1314.821 | 0 | 1314.821 | 0 | 0 | 48.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6258 | 0 | 0 | 133.756 | 0 | 133.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9492 | 3.4678 | 0 | 0 | 5.417 | 5.417 | 5.417
US_3B_RS_2019_NG | 3B | RS | NG | 0 | 0 | RetailStandalone | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 71332.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85625.7986 | 0 | 0 | 156958.5151 | 0 | 156958.5151 | 0 | 0 | 701.2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.7016 | 0 | 0 | 1542.9022 | 0 | 1542.9022 | 0 | 0 | 71.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6258 | 0 | 0 | 156.9585 | 0 | 156.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8889 | 3.4678 | 0 | 0 | 6.3567 | 6.3567 | 6.3567
US_4A_RS_2022_EL | 4A | RS | EL | 0 | 0 | RetailStandalone | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 31652.778 | 41841.667 | 8275.0001 | 53972.2227 | 0 | 36508.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172250.0014 | 18214.7224 | 154035.279 | 0 | 0 | 0 | 3478.6403 | 4598.3992 | 909.4225 | 5931.5473 | 0 | 4012.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18930.2752 | 2001.798 | 16928.4772 | 0 | 0 | 0 | 108.03 | 142.8043 | 28.2423 | 184.2055 | 0 | 124.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.8839 | 62.1663 | 528.4869 | 0 | 0 | 5.7834 | 1.1438 | 7.4601 | 5.0462 | 0 | 0 | 4.3751 | 0 | 0 | 0 | 0 | 21.4032 | 23.8087 | 23.8087
US_4A_RS_2019_EL | 4A | RS | EL | 0 | 0 | RetailStandalone | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 36305.5558 | 64775.0005 | 12175.0001 | 53972.2227 | 0 | 36750.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203977.7794 | 0 | 203977.7794 | 0 | 0 | 0 | 3989.9806 | 7118.7726 | 1338.0325 | 5931.5473 | 0 | 4038.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22417.158 | 0 | 22417.158 | 0 | 0 | 0 | 123.9097 | 221.0751 | 41.5529 | 184.2055 | 0 | 125.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.1698 | 0 | 696.167 | 0 | 0 | 8.9533 | 1.6828 | 7.4601 | 5.0796 | 0 | 0 | 5.0182 | 0 | 0 | 0 | 0 | 28.194 | 28.1941 | 28.1941
US_4A_RS_2022_NG | 4A | RS | NG | 0 | 0 | RetailStandalone | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 321992.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89360.1981 | 0 | 0 | 411352.6301 | 0 | 411352.6301 | 0 | 0 | 3165.1856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 878.4107 | 0 | 0 | 4043.5964 | 0 | 4043.5964 | 0 | 0 | 321.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3602 | 0 | 0 | 411.3526 | 0 | 411.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0404 | 3.619 | 0 | 0 | 16.6593 | 16.6593 | 16.6593
US_4A_RS_2019_NG | 4A | RS | NG | 0 | 0 | RetailStandalone | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 424792.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89360.1981 | 0 | 0 | 514152.8749 | 0 | 514152.8749 | 0 | 0 | 4175.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 878.4107 | 0 | 0 | 5054.1228 | 0 | 5054.1228 | 0 | 0 | 424.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3602 | 0 | 0 | 514.1529 | 0 | 514.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2037 | 3.619 | 0 | 0 | 20.8227 | 20.8227 | 20.8227
US_5A_RS_2022_EL | 5A | RS | EL | 0 | 0 | RetailStandalone | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 17355.5557 | 48336.1115 | 8247.2223 | 53972.2227 | 0 | 35841.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163752.7791 | 17540.8335 | 146211.9456 | 0 | 0 | 0 | 1907.3756 | 5312.1387 | 906.3697 | 5931.5473 | 0 | 3938.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17996.4304 | 1927.7376 | 16068.6928 | 0 | 0 | 0 | 59.234 | 164.9697 | 28.1475 | 184.2055 | 0 | 122.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.8832 | 59.8663 | 501.7074 | 0 | 0 | 6.6811 | 1.1399 | 7.4601 | 4.9541 | 0 | 0 | 2.3989 | 0 | 0 | 0 | 0 | 20.3186 | 22.6342 | 22.6342
US_5A_RS_2019_EL | 5A | RS | EL | 0 | 0 | RetailStandalone | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 20330.5557 | 64719.445 | 12133.3334 | 53972.2227 | 0 | 40625.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191780.5571 | 0 | 191780.5571 | 0 | 0 | 0 | 2234.3281 | 7112.667 | 1333.4533 | 5931.5473 | 0 | 4464.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21076.6832 | 0 | 21076.6832 | 0 | 0 | 0 | 69.3876 | 220.8855 | 41.4107 | 184.2055 | 0 | 138.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.5411 | 0 | 654.5439 | 0 | 0 | 8.9456 | 1.6771 | 7.4601 | 5.6153 | 0 | 0 | 2.8101 | 0 | 0 | 0 | 0 | 26.5083 | 26.5082 | 26.5082
US_5A_RS_2022_NG | 5A | RS | NG | 0 | 0 | RetailStandalone | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 485813.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91701.3064 | 0 | 0 | 577514.4494 | 0 | 577514.4494 | 0 | 0 | 4775.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901.4238 | 0 | 0 | 5676.967 | 0 | 5676.967 | 0 | 0 | 485.8131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7013 | 0 | 0 | 577.5144 | 0 | 577.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6749 | 3.7138 | 0 | 0 | 23.3887 | 23.3887 | 23.3887
US_5A_RS_2019_NG | 5A | RS | NG | 0 | 0 | RetailStandalone | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 642231.4023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91710.7845 | 0 | 0 | 733942.1869 | 0 | 733942.1869 | 0 | 0 | 6313.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901.517 | 0 | 0 | 7214.6517 | 0 | 7214.6517 | 0 | 0 | 642.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7108 | 0 | 0 | 733.9422 | 0 | 733.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0097 | 3.7142 | 0 | 0 | 29.7239 | 29.7239 | 29.7239
US_2A_PS_2022_EL | 2A | PS | EL | 0 | 0 | SchoolPrimary | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 274613.8911 | 68561.1117 | 5833.3334 | 312394.4469 | 4741.6667 | 72361.1117 | 122.2222 | 0 | 0 | 14944.4446 | 7177.7778 | 12555.5557 | 0 | 773305.5617 | 65034.7227 | 708270.839 | 0 | 4741.6667 | 0 | 30180.0666 | 7534.8662 | 641.0833 | 34332.1497 | 521.1092 | 7952.4862 | 13.4322 | 0 | 0 | 1642.3945 | 788.8378 | 1379.8556 | 0 | 84986.2812 | 7147.316 | 77838.9652 | 0 | 521.1092 | 0 | 937.2487 | 233.9969 | 19.909 | 1066.1926 | 16.1832 | 246.9662 | 0.41714 | 0 | 0 | 51.0049 | 24.4975 | 42.8517 | 0 | 2639.2679 | 221.9615 | 2426.6428 | 0 | 16.1832 | 3.1639 | 0.26919 | 14.6348 | 3.3392 | 0.0056402 | 0.68964 | 12.6725 | 0 | 0.33123 | 0 | 0.5794 | 32.8106 | 35.6856 | 35.6856
US_2A_PS_2019_EL | 2A | PS | EL | 0 | 0 | SchoolPrimary | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 301227.7802 | 78172.2228 | 8308.3334 | 312394.4469 | 4741.6667 | 72483.3339 | 119.4444 | 0 | 0 | 15058.3335 | 7177.7778 | 12555.5557 | 0 | 812238.8954 | 0 | 812238.8954 | 0 | 4741.6667 | 0 | 33104.933 | 8591.1273 | 913.0858 | 34332.1497 | 521.1092 | 7965.9184 | 13.1269 | 0 | 0 | 1654.9108 | 788.8378 | 1379.8556 | 0 | 89265.0546 | 0 | 89265.0546 | 0 | 521.1092 | 0 | 1028.0811 | 266.7994 | 28.3561 | 1066.1926 | 16.1832 | 247.3834 | 0.40766 | 0 | 0 | 51.3936 | 24.4975 | 42.8517 | 0 | 2772.1462 | 0 | 2772.1481 | 0 | 16.1832 | 3.6074 | 0.3834 | 14.6348 | 3.3449 | 0.005512 | 0.69489 | 13.9007 | 0 | 0.33123 | 0 | 0.5794 | 37.4822 | 37.4822 | 37.4822
US_2A_PS_2022_NG | 2A | PS | NG | 0 | 0 | SchoolPrimary | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 104857.008 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117595.6701 | 0 | 0 | 564643.0929 | 0 | 564643.0929 | 0 | 0 | 1030.7444 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.9654 | 0 | 0 | 5550.4416 | 0 | 5550.4416 | 0 | 0 | 104.857 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5957 | 0 | 0 | 564.6431 | 0 | 564.6431 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.4178 | 1.59 | 0 | 0 | 7.6345 | 7.6345 | 7.6345
US_2A_PS_2019_NG | 2A | PS | NG | 0 | 0 | SchoolPrimary | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 100914.0888 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117595.6701 | 0 | 0 | 560700.1737 | 0 | 560700.1737 | 0 | 0 | 991.9855 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.9654 | 0 | 0 | 5511.6827 | 0 | 5511.6827 | 0 | 0 | 100.9141 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5957 | 0 | 0 | 560.7002 | 0 | 560.7002 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.3645 | 1.59 | 0 | 0 | 7.5812 | 7.5812 | 7.5812
US_3A_PS_2022_EL | 3A | PS | EL | 0 | 0 | SchoolPrimary | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 155088.8901 | 69272.2228 | 5850 | 312394.4469 | 4741.6667 | 66327.7783 | 794.4445 | 0 | 0 | 11227.7779 | 7177.7778 | 12505.5557 | 0 | 645380.5607 | 62927.5005 | 582453.0602 | 0 | 4741.6667 | 0 | 17044.269 | 7613.0173 | 642.915 | 34332.1497 | 521.1092 | 7289.4228 | 87.3094 | 0 | 0 | 1233.9328 | 788.8378 | 1374.3606 | 0 | 70927.3236 | 6915.7323 | 64011.5913 | 0 | 521.1092 | 0 | 529.3136 | 236.4239 | 19.9659 | 1066.1926 | 16.1832 | 226.3747 | 2.7114 | 0 | 0 | 38.3201 | 24.4975 | 42.6811 | 0 | 2202.6638 | 214.7696 | 1997.0628 | 0 | 16.1832 | 3.1967 | 0.26996 | 14.6348 | 3.0608 | 0.036661 | 0.51813 | 7.1569 | 0 | 0.33123 | 0 | 0.57709 | 27.0023 | 29.7822 | 29.7822
US_3A_PS_2019_EL | 3A | PS | EL | 0 | 0 | SchoolPrimary | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 169541.668 | 79038.8895 | 8333.3334 | 312394.4469 | 4744.4445 | 66347.2228 | 386.1111 | 0 | 0 | 12025.0001 | 7177.7778 | 12505.5557 | 0 | 672494.4498 | 0 | 672494.4498 | 0 | 4744.4445 | 0 | 18632.6293 | 8686.374 | 915.8333 | 34332.1497 | 521.4144 | 7291.5598 | 42.4336 | 0 | 0 | 1321.5475 | 788.8378 | 1374.3606 | 0 | 73907.14 | 0 | 73907.14 | 0 | 521.4144 | 0 | 578.6405 | 269.7573 | 28.4414 | 1066.1926 | 16.1926 | 226.441 | 1.3178 | 0 | 0 | 41.041 | 24.4975 | 42.6811 | 0 | 2295.2027 | 0 | 2295.1866 | 0 | 16.1926 | 3.6474 | 0.38456 | 14.6349 | 3.0617 | 0.017818 | 0.55491 | 7.8238 | 0 | 0.33123 | 0 | 0.57709 | 31.0332 | 31.0334 | 31.0334
US_3A_PS_2022_NG | 3A | PS | NG | 0 | 0 | SchoolPrimary | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 405940.5943 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130419.6357 | 0 | 0 | 878550.6449 | 0 | 878550.6449 | 0 | 0 | 3990.396 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.025 | 0 | 0 | 8636.1528 | 0 | 8636.1528 | 0 | 0 | 405.9406 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4196 | 0 | 0 | 878.5506 | 0 | 878.5506 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.4887 | 1.7634 | 0 | 0 | 11.8789 | 11.8789 | 11.8789
US_3A_PS_2019_NG | 3A | PS | NG | 0 | 0 | SchoolPrimary | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 449369.5748 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130410.1575 | 0 | 0 | 921970.1471 | 0 | 921970.1471 | 0 | 0 | 4417.3029 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1281.9318 | 0 | 0 | 9062.9665 | 0 | 9062.9665 | 0 | 0 | 449.3696 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4102 | 0 | 0 | 921.9701 | 0 | 921.9701 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.0759 | 1.7633 | 0 | 0 | 12.466 | 12.466 | 12.466
US_3B_PS_2022_EL | 3B | PS | EL | 0 | 0 | SchoolPrimary | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 147066.6678 | 73866.6673 | 5819.4445 | 312394.4469 | 4741.6667 | 74288.8895 | 311.1111 | 0 | 0 | 0 | 7177.7778 | 12413.889 | 0 | 638080.5607 | 75686.3895 | 562394.1712 | 0 | 4741.6667 | 0 | 16162.6268 | 8117.9467 | 639.5569 | 34332.1497 | 521.1092 | 8164.349 | 34.1911 | 0 | 0 | 0 | 788.8378 | 1364.2864 | 0 | 70125.0536 | 8317.9342 | 61807.1194 | 0 | 521.1092 | 0 | 501.934 | 252.1046 | 19.8616 | 1066.1926 | 16.1832 | 253.5457 | 1.0618 | 0 | 0 | 0 | 24.4975 | 42.3682 | 0 | 2177.7492 | 258.3153 | 1930.0729 | 0 | 16.1832 | 3.4087 | 0.26855 | 14.6348 | 3.4282 | 0.014357 | 0 | 6.7867 | 0 | 0.33123 | 0 | 0.57286 | 26.0965 | 29.4454 | 29.4454
US_3B_PS_2019_EL | 3B | PS | EL | 0 | 0 | SchoolPrimary | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 155222.2235 | 80119.4451 | 8283.3334 | 312394.4469 | 4744.4445 | 74466.6673 | 163.8889 | 0 | 0 | 0 | 7177.7778 | 12411.1112 | 0 | 654983.3386 | 0 | 654983.3386 | 0 | 4744.4445 | 0 | 17058.9224 | 8805.127 | 910.3383 | 34332.1497 | 521.4144 | 8183.8867 | 18.0114 | 0 | 0 | 0 | 788.8378 | 1363.9811 | 0 | 71982.6689 | 0 | 71982.6689 | 0 | 521.4144 | 0 | 529.7686 | 273.4452 | 28.2708 | 1066.1926 | 16.1926 | 254.1524 | 0.55935 | 0 | 0 | 0 | 24.4975 | 42.3587 | 0 | 2235.4378 | 0 | 2235.4369 | 0 | 16.1926 | 3.6973 | 0.38225 | 14.6349 | 3.4364 | 0.0075629 | 0 | 7.163 | 0 | 0.33123 | 0 | 0.57273 | 30.2254 | 30.2254 | 30.2254
US_3B_PS_2022_NG | 3B | PS | NG | 0 | 0 | SchoolPrimary | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 137556.6986 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127225.492 | 0 | 0 | 606972.6055 | 0 | 606972.6055 | 0 | 0 | 1352.1823 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6266 | 0 | 0 | 5966.5407 | 0 | 5966.5407 | 0 | 0 | 137.5567 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2255 | 0 | 0 | 606.9726 | 0 | 606.9726 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.8599 | 1.7202 | 0 | 0 | 8.2069 | 8.2069 | 8.2069
US_3B_PS_2019_NG | 3B | PS | NG | 0 | 0 | SchoolPrimary | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 157053.2968 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127225.492 | 0 | 0 | 626469.2036 | 0 | 626469.2036 | 0 | 0 | 1543.8339 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6266 | 0 | 0 | 6158.1923 | 0 | 6158.1923 | 0 | 0 | 157.0533 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2255 | 0 | 0 | 626.4692 | 0 | 626.4692 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.1235 | 1.7202 | 0 | 0 | 8.4705 | 8.4705 | 8.4705
US_4A_PS_2022_EL | 4A | PS | EL | 0 | 0 | SchoolPrimary | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 97913.8897 | 69666.6672 | 5850 | 312394.4469 | 4741.6667 | 71430.5561 | 836.1111 | 0 | 0 | 13150.0001 | 7177.7778 | 12502.7779 | 0 | 595663.8937 | 54566.1115 | 541097.7821 | 0 | 4741.6667 | 0 | 10760.7365 | 7656.3667 | 642.915 | 34332.1497 | 521.1092 | 7850.2181 | 91.8886 | 0 | 0 | 1445.185 | 788.8378 | 1374.0553 | 0 | 65463.4619 | 5996.8157 | 59466.6463 | 0 | 521.1092 | 0 | 334.1771 | 237.7702 | 19.9659 | 1066.1926 | 16.1832 | 243.7903 | 2.8536 | 0 | 0 | 44.8805 | 24.4975 | 42.6716 | 0 | 2032.9824 | 186.2324 | 1855.0368 | 0 | 16.1832 | 3.2149 | 0.26996 | 14.6348 | 3.2963 | 0.038584 | 0.60683 | 4.5184 | 0 | 0.33123 | 0 | 0.57696 | 25.082 | 27.488 | 27.488
US_4A_PS_2019_EL | 4A | PS | EL | 0 | 0 | SchoolPrimary | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 108397.2231 | 79377.7784 | 8327.7778 | 312394.4469 | 4741.6667 | 70625.0006 | 441.6667 | 0 | 0 | 14147.2223 | 7177.7778 | 12502.7779 | 0 | 618133.3383 | 0 | 618133.3383 | 0 | 4741.6667 | 0 | 11912.8548 | 8723.6178 | 915.2228 | 34332.1497 | 521.1092 | 7761.6876 | 48.5392 | 0 | 0 | 1554.7797 | 788.8378 | 1374.0553 | 0 | 67932.8539 | 0 | 67932.8539 | 0 | 521.1092 | 0 | 369.9564 | 270.9139 | 28.4224 | 1066.1926 | 16.1832 | 241.0409 | 1.5074 | 0 | 0 | 48.284 | 24.4975 | 42.6716 | 0 | 2109.6699 | 0 | 2109.6832 | 0 | 16.1832 | 3.663 | 0.3843 | 14.6348 | 3.2591 | 0.020381 | 0.65285 | 5.0022 | 0 | 0.33123 | 0 | 0.57696 | 28.525 | 28.5249 | 28.5249
US_4A_PS_2022_NG | 4A | PS | NG | 0 | 0 | SchoolPrimary | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 459226.8728 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 139651.3745 | 0 | 0 | 941068.6621 | 0 | 941068.6621 | 0 | 0 | 4514.2002 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.773 | 0 | 0 | 9250.7049 | 0 | 9250.7049 | 0 | 0 | 459.2269 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 139.6514 | 0 | 0 | 941.0687 | 0 | 941.0687 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.2092 | 1.8882 | 0 | 0 | 12.7242 | 12.7242 | 12.7242
US_4A_PS_2019_NG | 4A | PS | NG | 0 | 0 | SchoolPrimary | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 564235.5315 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 139679.809 | 0 | 0 | 1046105.7553 | 0 | 1046105.7553 | 0 | 0 | 5546.4353 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.0525 | 0 | 0 | 10283.2196 | 0 | 10283.2196 | 0 | 0 | 564.2355 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 139.6798 | 0 | 0 | 1046.1058 | 0 | 1046.1058 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.629 | 1.8886 | 0 | 0 | 14.1444 | 14.1444 | 14.1444
US_5A_PS_2022_EL | 5A | PS | EL | 0 | 0 | SchoolPrimary | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 59258.3338 | 65497.2227 | 5850 | 312394.4469 | 4738.8889 | 68033.3339 | 1427.7778 | 0 | 0 | 12419.4445 | 7180.5556 | 12480.5557 | 0 | 549280.5599 | 52546.9449 | 496733.6151 | 0 | 4738.8889 | 0 | 6512.4909 | 7198.1448 | 642.915 | 34332.1497 | 520.8039 | 7476.8634 | 156.9128 | 0 | 0 | 1364.897 | 789.1431 | 1371.6131 | 0 | 60365.9335 | 5774.9092 | 54591.0243 | 0 | 520.8039 | 0 | 202.2469 | 223.54 | 19.9659 | 1066.1926 | 16.1737 | 232.1957 | 4.873 | 0 | 0 | 42.3872 | 24.507 | 42.5957 | 0 | 1874.6775 | 179.3411 | 1703.4081 | 0 | 16.1737 | 3.0225 | 0.26996 | 14.6347 | 3.1395 | 0.065887 | 0.57312 | 2.7346 | 0 | 0.33136 | 0 | 0.57594 | 23.0318 | 25.3475 | 25.3475
US_5A_PS_2019_EL | 5A | PS | EL | 0 | 0 | SchoolPrimary | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 64183.3338 | 78475.0006 | 8327.7778 | 312394.4469 | 4741.6667 | 67794.445 | 719.4445 | 0 | 0 | 13305.5557 | 7180.5556 | 12477.7779 | 0 | 569600.0046 | 0 | 569600.0046 | 0 | 4741.6667 | 0 | 7053.7484 | 8624.4026 | 915.2228 | 34332.1497 | 521.1092 | 7450.6095 | 79.0669 | 0 | 0 | 1462.2806 | 789.1431 | 1371.3078 | 0 | 62599.0405 | 0 | 62599.0405 | 0 | 521.1092 | 0 | 219.0557 | 267.8327 | 28.4224 | 1066.1926 | 16.1832 | 231.3803 | 2.4554 | 0 | 0 | 45.4114 | 24.507 | 42.5863 | 0 | 1944.0272 | 0 | 1944.0319 | 0 | 16.1832 | 3.6214 | 0.3843 | 14.6348 | 3.1285 | 0.0332 | 0.61401 | 2.9619 | 0 | 0.33136 | 0 | 0.57581 | 26.2853 | 26.2852 | 26.2852
US_5A_PS_2022_NG | 5A | PS | NG | 0 | 0 | SchoolPrimary | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 746841.9779 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 147319.215 | 0 | 0 | 1236351.6077 | 0 | 1236351.6077 | 0 | 0 | 7341.4566 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1448.1479 | 0 | 0 | 12153.3363 | 0 | 12153.3363 | 0 | 0 | 746.842 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 147.3192 | 0 | 0 | 1236.3516 | 0 | 1236.3516 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.0981 | 1.9919 | 0 | 0 | 16.7167 | 16.7167 | 16.7167
US_5A_PS_2019_NG | 5A | PS | NG | 0 | 0 | SchoolPrimary | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 943182.2943 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 147338.1713 | 0 | 0 | 1432710.8804 | 0 | 1432710.8804 | 0 | 0 | 9271.482 | 0 | 0 | 0 | 3363.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 1448.3342 | 0 | 0 | 14083.548 | 0 | 14083.548 | 0 | 0 | 943.1823 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 147.3382 | 0 | 0 | 1432.7109 | 0 | 1432.7109 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.7528 | 1.9922 | 0 | 0 | 19.3717 | 19.3717 | 19.3717
US_2A_SH_2022_EL | 2A | SH | EL | 0 | 0 | HotelSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 2000 | 127822.2232 | 43594.4448 | 10308.3334 | 105516.6675 | 0 | 68255.5561 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 357569.4473 | 28944.1669 | 328625.2804 | 0 | 0 | 219.8 | 14047.6623 | 4791.0295 | 1132.8858 | 11596.2818 | 0 | 7501.2856 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 39296.8823 | 3180.9639 | 36115.9183 | 0 | 0 | 6.8259 | 436.2533 | 148.7865 | 35.182 | 360.1251 | 0 | 232.9541 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.3734 | 98.7855 | 1125.7337 | 0 | 0 | 3.444 | 0.81436 | 8.3358 | 5.3922 | 0.0057056 | 0 | 10.098 | 0.158 | 0 | 0 | 0 | 26.0574 | 28.2481 | 28.2481
US_2A_SH_2019_EL | 2A | SH | EL | 0 | 0 | HotelSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 2116.6667 | 144080.5567 | 48975.0004 | 14488.889 | 122138.8899 | 0 | 71175.0006 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 403047.2254 | 0 | 403047.2254 | 0 | 0 | 232.6217 | 15834.4532 | 5382.3525 | 1592.3289 | 13423.064 | 0 | 7822.1326 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 44294.8901 | 0 | 44294.8901 | 0 | 0 | 7.2241 | 491.7425 | 167.1502 | 49.4501 | 416.8562 | 0 | 242.9181 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1375.5877 | 0 | 1375.5801 | 0 | 0 | 3.869 | 1.1446 | 9.649 | 5.6228 | 0.0057056 | 0 | 11.3824 | 0.16722 | 0 | 0 | 0 | 31.8407 | 31.8408 | 31.8408
US_2A_SH_2022_NG | 2A | SH | NG | 0 | 0 | HotelSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 37.9127 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 690683.8135 | 0 | 0 | 1090217.1641 | 0 | 1090217.1641 | 0 | 0 | 0.37268 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 6789.4219 | 0 | 0 | 10716.8347 | 0 | 10716.8347 | 0 | 0 | 0.037913 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 690.6838 | 0 | 0 | 1090.2172 | 0 | 1090.2172 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.00087757 | 15.9873 | 0 | 0 | 25.2353 | 25.2353 | 25.2353
US_2A_SH_2019_NG | 2A | SH | NG | 0 | 0 | HotelSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 3990.3101 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 815141.6795 | 0 | 0 | 1218627.4275 | 0 | 1218627.4275 | 0 | 0 | 39.2247 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 8012.8427 | 0 | 0 | 11979.1076 | 0 | 11979.1076 | 0 | 0 | 3.9903 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 815.1417 | 0 | 0 | 1218.6274 | 0 | 1218.6274 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.092364 | 18.8681 | 0 | 0 | 28.2077 | 28.2077 | 28.2077
US_3A_SH_2022_EL | 3A | SH | EL | 0 | 0 | HotelSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 14480.5557 | 88172.2229 | 45511.1115 | 10313.889 | 105516.6675 | 0 | 67102.7783 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 331169.4471 | 28006.3891 | 303163.058 | 0 | 0 | 1591.4131 | 9690.1273 | 5001.6712 | 1133.4964 | 11596.2818 | 0 | 7374.5953 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 36395.5222 | 3077.9022 | 33317.6201 | 0 | 0 | 49.4217 | 300.9291 | 155.328 | 35.201 | 360.1251 | 0 | 229.0197 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1130.2711 | 95.5849 | 1038.7504 | 0 | 0 | 3.5954 | 0.8148 | 8.3358 | 5.3011 | 0.0057056 | 0 | 6.9656 | 1.144 | 0 | 0 | 0 | 24.044 | 26.1625 | 26.1625
US_3A_SH_2019_EL | 3A | SH | EL | 0 | 0 | HotelSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 15588.889 | 95338.8897 | 49186.1115 | 14497.2223 | 122138.8899 | 0 | 69980.5561 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 366802.7807 | 0 | 366802.7807 | 0 | 0 | 1713.2189 | 10477.744 | 5405.5537 | 1593.2447 | 13423.064 | 0 | 7690.8631 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 40311.6256 | 0 | 40311.6256 | 0 | 0 | 53.2044 | 325.3887 | 167.8707 | 49.4786 | 416.8562 | 0 | 238.8415 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.8865 | 0 | 1251.8761 | 0 | 0 | 3.8857 | 1.1453 | 9.649 | 5.5285 | 0.0057056 | 0 | 7.5318 | 1.2315 | 0 | 0 | 0 | 28.9773 | 28.9775 | 28.9775
US_3A_SH_2022_NG | 3A | SH | NG | 0 | 0 | HotelSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 4141.9608 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 747770.8387 | 0 | 0 | 1151408.2374 | 0 | 1151408.2374 | 0 | 0 | 40.7155 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 7350.5873 | 0 | 0 | 11318.343 | 0 | 11318.343 | 0 | 0 | 4.142 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 747.7708 | 0 | 0 | 1151.4082 | 0 | 1151.4082 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.095874 | 17.3087 | 0 | 0 | 26.6517 | 26.6517 | 26.6517
US_3A_SH_2019_NG | 3A | SH | NG | 0 | 0 | HotelSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 28718.8587 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 882597.824 | 0 | 0 | 1310812.1206 | 0 | 1310812.1206 | 0 | 0 | 282.3064 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 8675.9366 | 0 | 0 | 12885.2831 | 0 | 12885.2831 | 0 | 0 | 28.7189 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 882.5978 | 0 | 0 | 1310.8121 | 0 | 1310.8121 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.66476 | 20.4296 | 0 | 0 | 30.3415 | 30.3415 | 30.3415
US_3B_SH_2022_EL | 3B | SH | EL | 0 | 0 | HotelSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 5727.7778 | 91583.3341 | 43819.4448 | 10313.889 | 105516.6675 | 0 | 77166.6673 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 334200.0027 | 33684.7225 | 300515.2802 | 0 | 0 | 629.4828 | 10065.0084 | 4815.757 | 1133.4964 | 11596.2818 | 0 | 8480.6167 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 36728.5803 | 3701.951 | 33026.6293 | 0 | 0 | 19.5487 | 312.5711 | 149.5544 | 35.201 | 360.1251 | 0 | 263.3674 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.6142 | 114.9649 | 1030.3744 | 0 | 0 | 3.4617 | 0.8148 | 8.3358 | 6.0962 | 0.0057056 | 0 | 7.2351 | 0.4525 | 0 | 0 | 0 | 23.8502 | 26.4019 | 26.4019
US_3B_SH_2019_EL | 3B | SH | EL | 0 | 0 | HotelSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 6236.1112 | 96908.3341 | 49255.5559 | 14497.2223 | 122138.8899 | 0 | 80322.2229 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 369430.5585 | 0 | 369430.5585 | 0 | 0 | 685.3486 | 10650.2259 | 5413.1856 | 1593.2447 | 13423.064 | 0 | 8827.4123 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 40600.4184 | 0 | 40600.4184 | 0 | 0 | 21.2837 | 330.7451 | 168.1077 | 49.4786 | 416.8562 | 0 | 274.1373 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.855 | 0 | 1260.8541 | 0 | 0 | 3.8912 | 1.1453 | 9.649 | 6.3455 | 0.0057056 | 0 | 7.6558 | 0.49265 | 0 | 0 | 0 | 29.1851 | 29.1851 | 29.1851
US_3B_SH_2022_NG | 3B | SH | NG | 0 | 0 | HotelSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 151.6507 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 733136.5423 | 0 | 0 | 1132783.631 | 0 | 1132783.631 | 0 | 0 | 1.4907 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 7206.7322 | 0 | 0 | 11135.2631 | 0 | 11135.2631 | 0 | 0 | 0.15165 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 733.1365 | 0 | 0 | 1132.7836 | 0 | 1132.7836 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.0035103 | 16.97 | 0 | 0 | 26.2206 | 26.2206 | 26.2206
US_3B_SH_2019_NG | 3B | SH | NG | 0 | 0 | HotelSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 12776.5748 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 865290.6834 | 0 | 0 | 1277562.696 | 0 | 1277562.696 | 0 | 0 | 125.5937 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 8505.8074 | 0 | 0 | 12558.4413 | 0 | 12558.4413 | 0 | 0 | 12.7766 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 865.2907 | 0 | 0 | 1277.5627 | 0 | 1277.5627 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.29574 | 20.0289 | 0 | 0 | 29.5718 | 29.5718 | 29.5718
US_4A_SH_2022_EL | 4A | SH | EL | 0 | 0 | HotelSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 32313.8891 | 64838.8894 | 45669.4448 | 10297.2223 | 105516.6675 | 0 | 62716.6672 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 321425.0026 | 24285.0002 | 297140.0024 | 0 | 0 | 3551.2964 | 7125.7939 | 5019.072 | 1131.6647 | 11596.2818 | 0 | 6892.5617 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 35324.6078 | 2668.9215 | 32655.6863 | 0 | 0 | 110.2863 | 221.2931 | 155.8684 | 35.1441 | 360.1251 | 0 | 214.05 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1097.0136 | 82.884 | 1017.8052 | 0 | 0 | 3.6079 | 0.81348 | 8.3358 | 4.9546 | 0.0057056 | 0 | 5.1223 | 2.5528 | 0 | 0 | 0 | 23.5592 | 25.3927 | 25.3927
US_4A_SH_2019_EL | 4A | SH | EL | 0 | 0 | HotelSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 35502.7781 | 73327.7784 | 48761.1115 | 14475.0001 | 122138.8899 | 0 | 67911.1117 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 362188.8918 | 0 | 362188.8918 | 0 | 0 | 3901.7553 | 8058.7228 | 5358.8462 | 1590.8025 | 13423.064 | 0 | 7463.4312 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 39804.5592 | 0 | 39804.5592 | 0 | 0 | 121.1699 | 250.2654 | 166.4202 | 49.4027 | 416.8562 | 0 | 231.7785 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.1395 | 0 | 1236.1309 | 0 | 0 | 3.8521 | 1.1435 | 9.649 | 5.365 | 0.0057056 | 0 | 5.7929 | 2.8047 | 0 | 0 | 0 | 28.6128 | 28.613 | 28.613
US_4A_SH_2022_NG | 4A | SH | NG | 0 | 0 | HotelSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 14236.2131 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 792545.7194 | 0 | 0 | 1206277.3705 | 0 | 1206277.3705 | 0 | 0 | 139.942 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.7244 | 0 | 0 | 11857.7066 | 0 | 11857.7066 | 0 | 0 | 14.2362 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 792.5457 | 0 | 0 | 1206.2774 | 0 | 1206.2774 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.32953 | 18.3451 | 0 | 0 | 27.9218 | 27.9218 | 27.9218
US_4A_SH_2019_NG | 4A | SH | NG | 0 | 0 | HotelSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 67835.2713 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 935504.9756 | 0 | 0 | 1402835.6848 | 0 | 1402835.6848 | 0 | 0 | 666.8207 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 9196.0139 | 0 | 0 | 13789.8748 | 0 | 13789.8748 | 0 | 0 | 67.8353 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 935.505 | 0 | 0 | 1402.8357 | 0 | 1402.8357 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5702 | 21.6542 | 0 | 0 | 32.4715 | 32.4715 | 32.4715
US_5A_SH_2022_EL | 5A | SH | EL | 0 | 0 | HotelSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 54716.6671 | 47647.2226 | 43947.2226 | 10300.0001 | 105516.6675 | 0 | 61594.4449 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 323794.447 | 23386.3891 | 300408.058 | 0 | 0 | 6013.3617 | 5236.4298 | 4829.7998 | 1131.97 | 11596.2818 | 0 | 6769.2295 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 35585.0097 | 2570.1642 | 33014.8456 | 0 | 0 | 186.7463 | 162.6185 | 149.9905 | 35.1536 | 360.1251 | 0 | 210.2199 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.1004 | 79.817 | 1028.8651 | 0 | 0 | 3.4718 | 0.8137 | 8.3358 | 4.866 | 0.0057056 | 0 | 3.7641 | 4.3226 | 0 | 0 | 0 | 23.8152 | 25.5798 | 25.5798
US_5A_SH_2019_EL | 5A | SH | EL | 0 | 0 | HotelSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 59441.6671 | 55194.4449 | 48708.3337 | 14480.5557 | 122138.8899 | 0 | 67088.8894 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 367125.0029 | 0 | 367125.0029 | 0 | 0 | 6532.6392 | 6065.8695 | 5353.0459 | 1591.4131 | 13423.064 | 0 | 7373.0689 | 7.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 40347.0378 | 0 | 40347.0378 | 0 | 0 | 202.8726 | 188.3769 | 166.24 | 49.4217 | 416.8562 | 0 | 228.9723 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.9863 | 0 | 1252.9701 | 0 | 0 | 3.848 | 1.144 | 9.649 | 5.3 | 0.0057056 | 0 | 4.3604 | 4.6959 | 0 | 0 | 0 | 29.0026 | 29.003 | 29.003
US_5A_SH_2022_NG | 5A | SH | NG | 0 | 0 | HotelSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 35600.011 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 830581.6204 | 0 | 0 | 1265677.0694 | 0 | 1265677.0694 | 0 | 0 | 349.9481 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 8164.6173 | 0 | 0 | 12441.6056 | 0 | 12441.6056 | 0 | 0 | 35.6 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 830.5816 | 0 | 0 | 1265.6771 | 0 | 1265.6771 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.82404 | 19.2255 | 0 | 0 | 29.2967 | 29.2967 | 29.2967
US_5A_SH_2019_NG | 5A | SH | NG | 0 | 0 | HotelSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 107217.0726 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 980403.0726 | 0 | 0 | 1487115.5831 | 0 | 1487115.5831 | 0 | 0 | 1053.9438 | 0 | 0 | 0 | 3927.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 9637.3622 | 0 | 0 | 14618.3462 | 0 | 14618.3462 | 0 | 0 | 107.2171 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 980.4031 | 0 | 0 | 1487.1156 | 0 | 1487.1156 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.4818 | 22.6935 | 0 | 0 | 34.4224 | 34.4224 | 34.4224
US_2A_MA_2022_EL | 2A | MA | EL | 0 | 0 | ApartmentMidRise | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 65427.7783 | 15900.0001 | 6336.1112 | 117269.4454 | 0 | 33194.4447 | 0 | 0 | 0 | 0 | 97408.3341 | 0 | 0 | 335536.1138 | 21642.5002 | 313893.6136 | 0 | 0 | 0 | 7190.5128 | 1747.41 | 696.3386 | 12887.912 | 0 | 3648.0695 | 0 | 0 | 0 | 0 | 10705.1759 | 0 | 0 | 36875.4189 | 2378.5108 | 34496.9081 | 0 | 0 | 0 | 223.303 | 54.2662 | 21.625 | 400.237 | 0 | 113.2916 | 0 | 0 | 0 | 0 | 332.4516 | 0 | 0 | 1145.1744 | 73.8652 | 1074.4216 | 0 | 0 | 1.6083 | 0.64091 | 11.862 | 3.3577 | 0 | 0 | 6.6181 | 0 | 9.853 | 0 | 0 | 31.8432 | 33.9401 | 33.9401
US_2A_MA_2019_EL | 2A | MA | EL | 0 | 0 | ApartmentMidRise | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 75686.1117 | 20277.7779 | 9172.2223 | 125580.5566 | 0 | 35080.5558 | 0 | 0 | 0 | 0 | 105561.112 | 0 | 0 | 371358.3363 | 0 | 371358.3363 | 0 | 0 | 0 | 8317.9037 | 2228.5278 | 1008.0272 | 13801.3032 | 0 | 3855.3531 | 0 | 0 | 0 | 0 | 11601.1662 | 0 | 0 | 40812.2812 | 0 | 40812.2812 | 0 | 0 | 0 | 258.3144 | 69.2074 | 31.3045 | 428.6025 | 0 | 119.7288 | 0 | 0 | 0 | 0 | 360.2768 | 0 | 0 | 1267.4345 | 0 | 1267.4335 | 0 | 0 | 2.0511 | 0.92779 | 12.7027 | 3.5485 | 0 | 0 | 7.6558 | 0 | 10.6777 | 0 | 0 | 37.5636 | 37.5636 | 37.5636
US_2A_MA_2022_NG | 2A | MA | NG | 0 | 0 | ApartmentMidRise | STD2022 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 4748.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4748.5638 | 0 | 4748.5638 | 0 | 0 | 46.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6784 | 0 | 46.6784 | 0 | 0 | 4.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7486 | 0 | 4.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14074 | 0 | 0 | 0 | 0.14074 | 0.14074 | 0.14074
US_2A_MA_2019_NG | 2A | MA | NG | 0 | 0 | ApartmentMidRise | STD2019 | Tampa | Zone2A | Zone2A(Tampa) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 4682.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4682.2166 | 0 | 4682.2166 | 0 | 0 | 46.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.0262 | 0 | 46.0262 | 0 | 0 | 4.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6822 | 0 | 4.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13877 | 0 | 0 | 0 | 0.13877 | 0.13877 | 0.13877
US_3A_MA_2022_EL | 3A | MA | EL | 0 | 0 | ApartmentMidRise | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 39969.4448 | 15900.0001 | 6341.6667 | 117269.4454 | 0 | 27047.2224 | 0 | 0 | 0 | 0 | 107886.112 | 0 | 0 | 314413.8914 | 20941.3891 | 293472.5023 | 0 | 0 | 0 | 4392.642 | 1747.41 | 696.9492 | 12887.912 | 0 | 2972.4897 | 0 | 0 | 0 | 0 | 11856.6837 | 0 | 0 | 34554.0867 | 2301.4587 | 32252.628 | 0 | 0 | 0 | 136.4145 | 54.2662 | 21.6439 | 400.237 | 0 | 92.3113 | 0 | 0 | 0 | 0 | 368.212 | 0 | 0 | 1073.0849 | 71.4723 | 1004.6463 | 0 | 0 | 1.6083 | 0.64147 | 11.862 | 2.7359 | 0 | 0 | 4.043 | 0 | 10.9129 | 0 | 0 | 29.7752 | 31.8036 | 31.8036
US_3A_MA_2019_EL | 3A | MA | EL | 0 | 0 | ApartmentMidRise | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 44241.667 | 20277.7779 | 9177.7779 | 125580.5566 | 0 | 28511.1113 | 0 | 0 | 0 | 0 | 117227.7787 | 0 | 0 | 345016.6694 | 0 | 345016.6694 | 0 | 0 | 0 | 4862.1592 | 2228.5278 | 1008.6378 | 13801.3032 | 0 | 3133.3711 | 0 | 0 | 0 | 0 | 12883.3329 | 0 | 0 | 37917.332 | 0 | 37917.332 | 0 | 0 | 0 | 150.9954 | 69.2074 | 31.3235 | 428.6025 | 0 | 97.3075 | 0 | 0 | 0 | 0 | 400.0948 | 0 | 0 | 1177.5312 | 0 | 1177.5274 | 0 | 0 | 2.0511 | 0.92835 | 12.7027 | 2.884 | 0 | 0 | 4.4751 | 0 | 11.8578 | 0 | 0 | 34.899 | 34.8991 | 34.8991
US_3A_MA_2022_NG | 3A | MA | NG | 0 | 0 | ApartmentMidRise | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 74327.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74327.8186 | 0 | 74327.8186 | 0 | 0 | 730.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730.6425 | 0 | 730.6425 | 0 | 0 | 74.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3278 | 0 | 74.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2029 | 0 | 0 | 0 | 2.2029 | 2.2029 | 2.2029
US_3A_MA_2019_NG | 3A | MA | NG | 0 | 0 | ApartmentMidRise | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 72176.2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72176.2737 | 0 | 72176.2737 | 0 | 0 | 709.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.4928 | 0 | 709.4928 | 0 | 0 | 72.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1763 | 0 | 72.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1391 | 0 | 0 | 0 | 2.1391 | 2.1391 | 2.1391
US_3B_MA_2022_EL | 3B | MA | EL | 0 | 0 | ApartmentMidRise | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 45877.7781 | 15900.0001 | 6341.6667 | 117269.4454 | 0 | 30013.8891 | 0 | 0 | 0 | 0 | 105172.2231 | 0 | 0 | 320575.0026 | 25187.2224 | 295387.7801 | 0 | 0 | 0 | 5041.9678 | 1747.41 | 696.9492 | 12887.912 | 0 | 3298.5264 | 0 | 0 | 0 | 0 | 11558.4273 | 0 | 0 | 35231.1928 | 2768.0757 | 32463.117 | 0 | 0 | 0 | 156.5794 | 54.2662 | 21.6439 | 400.237 | 0 | 102.4365 | 0 | 0 | 0 | 0 | 358.9495 | 0 | 0 | 1094.1125 | 85.9632 | 1011.678 | 0 | 0 | 1.6083 | 0.64147 | 11.862 | 3.036 | 0 | 0 | 4.6406 | 0 | 10.6384 | 0 | 0 | 29.9836 | 32.4268 | 32.4268
US_3B_MA_2019_EL | 3B | MA | EL | 0 | 0 | ApartmentMidRise | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 50672.2226 | 20277.7779 | 9177.7779 | 125580.5566 | 0 | 31447.2225 | 0 | 0 | 0 | 0 | 114222.2231 | 0 | 0 | 351377.7806 | 0 | 351377.7806 | 0 | 0 | 0 | 5568.8773 | 2228.5278 | 1008.6378 | 13801.3032 | 0 | 3456.0497 | 0 | 0 | 0 | 0 | 12553.0223 | 0 | 0 | 38616.4181 | 0 | 38616.4181 | 0 | 0 | 0 | 172.9427 | 69.2074 | 31.3235 | 428.6025 | 0 | 107.3284 | 0 | 0 | 0 | 0 | 389.8369 | 0 | 0 | 1199.2415 | 0 | 1199.2377 | 0 | 0 | 2.0511 | 0.92835 | 12.7027 | 3.1809 | 0 | 0 | 5.1256 | 0 | 11.5538 | 0 | 0 | 35.5424 | 35.5426 | 35.5426
US_3B_MA_2022_NG | 3B | MA | NG | 0 | 0 | ApartmentMidRise | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 23212.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23212.0413 | 0 | 23212.0413 | 0 | 0 | 228.1744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228.1744 | 0 | 228.1744 | 0 | 0 | 23.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.212 | 0 | 23.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68795 | 0 | 0 | 0 | 0.68795 | 0.68795 | 0.68795
US_3B_MA_2019_NG | 3B | MA | NG | 0 | 0 | ApartmentMidRise | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 22586.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22586.482 | 0 | 22586.482 | 0 | 0 | 222.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.0251 | 0 | 222.0251 | 0 | 0 | 22.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5865 | 0 | 22.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66941 | 0 | 0 | 0 | 0.66941 | 0.66941 | 0.66941
US_4A_MA_2022_EL | 4A | MA | EL | 0 | 0 | ApartmentMidRise | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 28708.3336 | 15900.0001 | 6330.5556 | 117269.4454 | 0 | 25008.3335 | 0 | 0 | 0 | 0 | 116119.4454 | 0 | 0 | 309336.1136 | 18158.889 | 291177.2246 | 0 | 0 | 0 | 3155.0459 | 1747.41 | 695.7281 | 12887.912 | 0 | 2748.4159 | 0 | 0 | 0 | 0 | 12761.527 | 0 | 0 | 33996.0389 | 1995.6619 | 32000.377 | 0 | 0 | 0 | 97.9807 | 54.2662 | 21.606 | 400.237 | 0 | 85.3527 | 0 | 0 | 0 | 0 | 396.3121 | 0 | 0 | 1055.7546 | 61.9757 | 996.5358 | 0 | 0 | 1.6083 | 0.64035 | 11.862 | 2.5296 | 0 | 0 | 2.9039 | 0 | 11.7457 | 0 | 0 | 29.5349 | 31.29 | 31.29
US_4A_MA_2019_EL | 4A | MA | EL | 0 | 0 | ApartmentMidRise | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 33241.6669 | 20277.7779 | 9163.889 | 125580.5566 | 0 | 26719.4447 | 0 | 0 | 0 | 0 | 126444.4455 | 0 | 0 | 341427.7805 | 0 | 341427.7805 | 0 | 0 | 0 | 3653.2592 | 2228.5278 | 1007.1114 | 13801.3032 | 0 | 2936.467 | 0 | 0 | 0 | 0 | 13896.2446 | 0 | 0 | 37522.9131 | 0 | 37522.9131 | 0 | 0 | 0 | 113.4528 | 69.2074 | 31.2761 | 428.6025 | 0 | 91.1926 | 0 | 0 | 0 | 0 | 431.551 | 0 | 0 | 1165.2824 | 0 | 1165.273 | 0 | 0 | 2.0511 | 0.92695 | 12.7027 | 2.7027 | 0 | 0 | 3.3625 | 0 | 12.7901 | 0 | 0 | 34.5358 | 34.5361 | 34.5361
US_4A_MA_2022_NG | 4A | MA | NG | 0 | 0 | ApartmentMidRise | STD2022 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 163356.2806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163356.2806 | 0 | 163356.2806 | 0 | 0 | 1605.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1605.7922 | 0 | 1605.7922 | 0 | 0 | 163.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.3563 | 0 | 163.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8415 | 0 | 0 | 0 | 4.8415 | 4.8415 | 4.8415
US_4A_MA_2019_NG | 4A | MA | NG | 0 | 0 | ApartmentMidRise | STD2019 | Newyork | Zone4A | Zone4A(Newyork) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 196065.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196065.4494 | 0 | 196065.4494 | 0 | 0 | 1927.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1927.3234 | 0 | 1927.3234 | 0 | 0 | 196.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.0654 | 0 | 196.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8109 | 0 | 0 | 0 | 5.8109 | 5.8109 | 5.8109
US_5A_MA_2022_EL | 5A | MA | EL | 0 | 0 | ApartmentMidRise | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 18452.7779 | 15900.0001 | 6333.3334 | 117269.4454 | 0 | 23527.778 | 0 | 0 | 0 | 0 | 123055.5565 | 0 | 0 | 304538.8913 | 17486.9446 | 287051.9467 | 0 | 0 | 0 | 2027.9603 | 1747.41 | 696.0333 | 12887.912 | 0 | 2585.7028 | 0 | 0 | 0 | 0 | 13523.8057 | 0 | 0 | 33468.8242 | 1921.8152 | 31547.0089 | 0 | 0 | 0 | 62.9788 | 54.2662 | 21.6155 | 400.237 | 0 | 80.2996 | 0 | 0 | 0 | 0 | 419.9848 | 0 | 0 | 1039.3818 | 59.6824 | 982.3748 | 0 | 0 | 1.6083 | 0.64063 | 11.862 | 2.3799 | 0 | 0 | 1.8665 | 0 | 12.4473 | 0 | 0 | 29.1152 | 30.8047 | 30.8047
US_5A_MA_2019_EL | 5A | MA | EL | 0 | 0 | ApartmentMidRise | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Electricity | 0 | 20866.6668 | 20277.7779 | 9166.6667 | 125580.5566 | 0 | 25136.1113 | 0 | 0 | 0 | 0 | 134177.7789 | 0 | 0 | 335205.5582 | 0 | 335205.5582 | 0 | 0 | 0 | 2293.2467 | 2228.5278 | 1007.4167 | 13801.3032 | 0 | 2762.4586 | 0 | 0 | 0 | 0 | 14746.1379 | 0 | 0 | 36839.0909 | 0 | 36839.0909 | 0 | 0 | 0 | 71.2173 | 69.2074 | 31.2855 | 428.6025 | 0 | 85.7888 | 0 | 0 | 0 | 0 | 457.9446 | 0 | 0 | 1144.0462 | 0 | 1144.0462 | 0 | 0 | 2.0511 | 0.92723 | 12.7027 | 2.5426 | 0 | 0 | 2.1107 | 0 | 13.5723 | 0 | 0 | 33.9067 | 33.9067 | 33.9067
US_5A_MA_2022_NG | 5A | MA | NG | 0 | 0 | ApartmentMidRise | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 273312.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273312.5447 | 0 | 273312.5447 | 0 | 0 | 2686.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2686.6623 | 0 | 2686.6623 | 0 | 0 | 273.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.3125 | 0 | 273.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1003 | 0 | 0 | 0 | 8.1003 | 8.1003 | 8.1003
US_5A_MA_2019_NG | 5A | MA | NG | 0 | 0 | ApartmentMidRise | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) | 0 | 0 | US | 0.1099 | 0.00983 | 0 | 0 | 0 | Natural Gas | 336768.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336768.9009 | 0 | 336768.9009 | 0 | 0 | 3310.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.4383 | 0 | 3310.4383 | 0 | 0 | 336.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336.7689 | 0 | 336.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.981 | 0 | 0 | 0 | 9.981 | 9.981 | 9.981
Lookup values |  |  |  | Energy Data for Current State 5: Energy Data from model runs; Energy Data for Current State 11: yellow indiv State cost files; Energy Data for Current State 14: Also in big EplusOUT file; B. Energy Usage, electricity in kWh, natural gas in kBtu 21: B. Energy Usage, electricity in kWh, natural gas in kBtu; C. Energy Cost 40: C. Energy Cost, $; D. Energy Usage mmBtu 59: D. Energy Usage mmBtu; E. EUI kBtu/ft2 78: E. EUI kBtu/ft2
|  |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
Lookup | CZ | Prototype | Fuel Type | Placeholder | A.case.name | A.building | A.std.year | A.climate.city | A.climate.zone | A.climates | A.standard | A.type.anal | A.state.abb | A.elec.price | A.gas.price/Therm | A.filename | A.bldg | A.loc | A.fuel | B.htg | B.clg | B.intLgt | B.extLgt | B.intEqp | B.extEqp | B.fans | B.pumps | B.heatRej | B.humid | B.heatRec | B.swh | B.refrg | B.gentor | B.total | B.renew | B.sum | B.transLoss | B.extEqp.rev | C.htg | C.clg | C.intLgt | C.extLgt | C.intEqp | C.extEqp | C.fans | C.pumps | C.heatRej | C.humid | C.heatRec | C.swh | C.refrg | C.gentor | C.total | C.renew | C.sum | C.transLoss | C.extEqp.rev | D.htg | D.clg | D.intLgt | D.extLgt | D.intEqp | D.extEqp | D.fans | D.pumps | D.heatRej | D.humid | D.heatRec | D.swh | D.refrg | D.gentor | D.total | D.renew | D.sum | D.transLoss | D.extEqp.rev | E.intLgt | E.extLgt | E.plug | E.fans | E.pumps | E.heatRec | E.clg | E.htg | E.swh | E.humid | E.refrg | E.sum | E.total | E.add
US_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 1278305.5658 | 682308.3388 | 97358.3341 | 4076777.8104 | 530358.3376 | 578358.338 | 186600.0015 | 441794.448 | 94158.3341 | 14030.5557 | 0 | 0 | 0 | 7980050.0638 | 0 | 7980050.0638 |  | 530358.3376 | 0 | 135883.8816 | 72529.3764 | 10349.1909 | 433361.4812 | 56377.0913 | 61479.4913 | 19835.5802 | 46962.7498 | 10009.0309 | 1491.4481 | 0 | 0 | 0 | 848279.3218 | 0 | 848279.2332 |  | 56377.0913 | 0 | 4362.8173 | 2328.6972 | 332.281 | 13913.9163 | 1810.0966 | 1973.9191 | 636.86 | 1507.8308 | 321.3595 | 47.8859 | 0 | 0 | 0 | 27235.6635 | 0 | 27235.6606 |  | 1810.0966 | 4.6706 | 0.66644 | 31.5371 | 3.959 | 1.2773 | 0.096043 | 11.7745 | 0 | 0 | 0.64454 | 0 | 54.6256 | 54.6256 | 54.6256
US_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 70925.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611218.8262 | 0 | 0 | 682143.9813 | 0 | 682143.9813 |  | 0 | 695.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5989.9445 | 0 | 0 | 6685.011 | 0 | 6685.011 |  | 0 | 70.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611.2188 | 0 | 0 | 682.144 | 0 | 682.144 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14225 | 1.2259 | 0 | 0 | 1.3682 | 1.3682 | 1.3682
US_2A_LO_2022_EL | 2A | LO | EL |  |  | OfficeLarge | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 1191736.1206 | 475586.1149 | 73427.7784 | 4076777.8104 | 334358.336 | 563352.7823 | 179419.4459 | 431069.4479 | 94055.5563 | 14058.3334 | 0 | 0 | 0 | 7433841.7261 | 157366.6679 | 7276475.0582 |  | 334358.336 | 0 | 126681.5496 | 50554.804 | 7805.3728 | 433361.4812 | 35542.2911 | 59884.4008 | 19072.2871 | 45822.6823 | 9998.1056 | 1494.4008 | 0 | 0 | 0 | 790217.3755 | 16728.0768 | 774192.3256 |  | 35542.2911 | 0 | 4067.3584 | 1623.1607 | 250.6067 | 13913.9163 | 1141.1546 | 1922.7056 | 612.353 | 1471.2267 | 321.0087 | 47.9807 | 0 | 0 | 0 | 25371.4714 | 537.0876 | 24856.9559 |  | 1141.1546 | 3.2555 | 0.50263 | 30.1954 | 3.8563 | 1.2282 | 0.096233 | 11.1085 | 0 | 0 | 0.64384 | 0 | 49.8547 | 50.8866 | 50.8866
US_2A_LO_2022_NG | 2A | LO | NG |  |  | OfficeLarge | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 63503.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611228.3043 | 0 | 0 | 674732.0514 | 0 | 674732.0514 |  | 0 | 622.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5990.0374 | 0 | 0 | 6612.3741 | 0 | 6612.3741 |  | 0 | 63.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611.2283 | 0 | 0 | 674.7321 | 0 | 674.7321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12737 | 1.2259 | 0 | 0 | 1.3533 | 1.3533 | 1.3533
US_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 75686.1117 | 20277.7779 | 9172.2223 | 125580.5566 | 0 | 35080.5558 | 0 | 0 | 0 | 0 | 105561.112 | 0 | 0 | 371358.3363 | 0 | 371358.3363 |  | 0 | 0 | 8045.4337 | 2155.5278 | 975.0072 | 13349.2132 | 0 | 3729.0631 | 0 | 0 | 0 | 0 | 11221.1462 | 0 | 0 | 39475.3911 | 0 | 39475.3616 |  | 0 | 0 | 258.3144 | 69.2074 | 31.3045 | 428.6025 | 0 | 119.7288 | 0 | 0 | 0 | 0 | 360.2768 | 0 | 0 | 1267.4345 | 0 | 1267.4335 |  | 0 | 2.0511 | 0.92779 | 12.7027 | 3.5485 | 0 | 0 | 7.6558 | 0 | 10.6777 | 0 | 0 | 37.5636 | 37.5636 | 37.5636
US_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 4682.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4682.2166 | 0 | 4682.2166 |  | 0 | 45.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.8857 | 0 | 45.8857 |  | 0 | 4.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6822 | 0 | 4.6822 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13877 | 0 | 0 | 0 | 0.13877 | 0.13877 | 0.13877
US_2A_MA_2022_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 65427.7783 | 15900.0001 | 6336.1112 | 117269.4454 | 0 | 33194.4447 | 0 | 0 | 0 | 0 | 97408.3341 | 0 | 0 | 335536.1138 | 21642.5002 | 313893.6136 |  | 0 | 0 | 6954.9728 | 1690.17 | 673.5286 | 12465.742 | 0 | 3528.5695 | 0 | 0 | 0 | 0 | 10354.5059 | 0 | 0 | 35667.4889 | 2300.5978 | 33463.8308 |  | 0 | 0 | 223.303 | 54.2662 | 21.625 | 400.237 | 0 | 113.2916 | 0 | 0 | 0 | 0 | 332.4516 | 0 | 0 | 1145.1744 | 73.8652 | 1074.4216 |  | 0 | 1.6083 | 0.64091 | 11.862 | 3.3577 | 0 | 0 | 6.6181 | 0 | 9.853 | 0 | 0 | 31.8432 | 33.9401 | 33.9401
US_2A_MA_2022_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 4748.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4748.5638 | 0 | 4748.5638 |  | 0 | 46.5359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.5359 | 0 | 46.5359 |  | 0 | 4.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7486 | 0 | 4.7486 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14074 | 0 | 0 | 0 | 0.14074 | 0.14074 | 0.14074
US_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 301227.7802 | 78172.2228 | 8308.3334 | 312394.4469 | 4741.6667 | 72483.3339 | 119.4444 | 0 | 0 | 15058.3335 | 7177.7778 | 12555.5557 | 0 | 812238.8954 | 0 | 812238.8954 |  | 4741.6667 | 0 | 32020.513 | 8309.7073 | 883.1758 | 33207.5297 | 504.0392 | 7704.9784 | 12.6969 | 0 | 0 | 1600.7008 | 762.9978 | 1334.6556 | 0 | 86340.9946 | 0 | 86341.0536 |  | 504.0392 | 0 | 1028.0811 | 266.7994 | 28.3561 | 1066.1926 | 16.1832 | 247.3834 | 0.40766 | 0 | 0 | 51.3936 | 24.4975 | 42.8517 | 0 | 2772.1462 | 0 | 2772.1481 |  | 16.1832 | 3.6074 | 0.3834 | 14.6348 | 3.3449 | 0.005512 | 0.69489 | 13.9007 | 0 | 0.33123 | 0 | 0.5794 | 37.4822 | 37.4822 | 37.4822
US_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 100914.0888 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117595.6701 | 0 | 0 | 560700.1737 | 0 | 560700.1737 |  | 0 | 988.9581 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.4376 | 0 | 0 | 5494.8617 | 0 | 5494.8617 |  | 0 | 100.9141 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5957 | 0 | 0 | 560.7002 | 0 | 560.7002 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.3645 | 1.59 | 0 | 0 | 7.5812 | 7.5812 | 7.5812
US_2A_PS_2022_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 274613.8911 | 68561.1117 | 5833.3334 | 312394.4469 | 4741.6667 | 72361.1117 | 122.2222 | 0 | 0 | 14944.4446 | 7177.7778 | 12555.5557 | 0 | 773305.5617 | 65034.7227 | 708270.839 |  | 4741.6667 | 0 | 29191.4566 | 7288.0462 | 620.0833 | 33207.5297 | 504.0392 | 7691.9862 | 12.9922 | 0 | 0 | 1588.5945 | 762.9978 | 1334.6556 | 0 | 82202.3812 | 6913.191 | 75579.9797 |  | 504.0392 | 0 | 937.2487 | 233.9969 | 19.909 | 1066.1926 | 16.1832 | 246.9662 | 0.41714 | 0 | 0 | 51.0049 | 24.4975 | 42.8517 | 0 | 2639.2679 | 221.9615 | 2426.6428 |  | 16.1832 | 3.1639 | 0.26919 | 14.6348 | 3.3392 | 0.0056402 | 0.68964 | 12.6725 | 0 | 0.33123 | 0 | 0.5794 | 32.8106 | 35.6856 | 35.6856
US_2A_PS_2022_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 104857.008 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117595.6701 | 0 | 0 | 564643.0929 | 0 | 564643.0929 |  | 0 | 1027.5987 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.4376 | 0 | 0 | 5533.5023 | 0 | 5533.5023 |  | 0 | 104.857 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5957 | 0 | 0 | 564.6431 | 0 | 564.6431 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.4178 | 1.59 | 0 | 0 | 7.6345 | 7.6345 | 7.6345
US_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 98269.4452 | 62308.3338 | 12102.7779 | 53972.2227 | 0 | 35091.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261744.4465 | 0 | 261744.4465 |  | 0 | 0 | 10446.042 | 6623.3759 | 1286.5253 | 5737.2473 | 0 | 3730.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27823.4347 | 0 | 27823.7595 |  | 0 | 0 | 335.3906 | 212.6564 | 41.3064 | 184.2055 | 0 | 119.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3257 | 0 | 893.3361 |  | 0 | 8.6124 | 1.6729 | 7.4601 | 4.8504 | 0 | 0 | 13.583 | 0 | 0 | 0 | 0 | 36.1792 | 36.1787 | 36.1787
US_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 16198.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83000.3452 | 0 | 0 | 99198.5398 | 0 | 99198.5398 |  | 0 | 158.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813.4034 | 0 | 0 | 972.1457 | 0 | 972.1457 |  | 0 | 16.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0003 | 0 | 0 | 99.1985 | 0 | 99.1985 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65601 | 3.3614 | 0 | 0 | 4.0174 | 4.0174 | 4.0174
US_2A_RS_2022_EL | 2A | RS | EL |  |  | RetailStandalone | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 84894.4451 | 46583.3337 | 8225.0001 | 53972.2227 | 0 | 32805.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226480.5574 | 21709.1668 | 204771.3905 |  | 0 | 0 | 9024.2795 | 4951.8084 | 874.3175 | 5737.2473 | 0 | 3487.2306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24074.8832 | 2307.6844 | 21864.3157 |  | 0 | 0 | 289.7421 | 158.9875 | 28.0717 | 184.2055 | 0 | 111.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772.9711 | 74.0927 | 701.9965 |  | 0 | 6.4388 | 1.1369 | 7.4601 | 4.5344 | 0 | 0 | 11.7343 | 0 | 0 | 0 | 0 | 28.4301 | 31.3045 | 31.3045
US_2A_RS_2022_NG | 2A | RS | NG |  |  | RetailStandalone | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 9222.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83000.3452 | 0 | 0 | 92222.6058 | 0 | 92222.6058 |  | 0 | 90.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813.4034 | 0 | 0 | 903.7815 | 0 | 903.7815 |  | 0 | 9.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0003 | 0 | 0 | 92.2226 | 0 | 92.2226 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37349 | 3.3614 | 0 | 0 | 3.7349 | 3.7349 | 3.7349
US_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 2116.6667 | 144080.5567 | 48975.0004 | 14488.889 | 122138.8899 | 0 | 71175.0006 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 403047.2254 | 0 | 403047.2254 |  | 0 | 225.0017 | 15315.7632 | 5206.0425 | 1540.1689 | 12983.364 | 0 | 7565.9026 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 42843.9201 | 0 | 42843.6838 |  | 0 | 7.2241 | 491.7425 | 167.1502 | 49.4501 | 416.8562 | 0 | 242.9181 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1375.5877 | 0 | 1375.5801 |  | 0 | 3.869 | 1.1446 | 9.649 | 5.6228 | 0.0057056 | 0 | 11.3824 | 0.16722 | 0 | 0 | 0 | 31.8407 | 31.8408 | 31.8408
US_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 3990.3101 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 815141.6795 | 0 | 0 | 1218627.4275 | 0 | 1218627.4275 |  | 0 | 39.105 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 7988.3885 | 0 | 0 | 11942.5488 | 0 | 11942.5488 |  | 0 | 3.9903 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 815.1417 | 0 | 0 | 1218.6274 | 0 | 1218.6274 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.092364 | 18.8681 | 0 | 0 | 28.2077 | 28.2077 | 28.2077
US_2A_SH_2022_EL | 2A | SH | EL |  |  | HotelSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 2000 | 127822.2232 | 43594.4448 | 10308.3334 | 105516.6675 | 0 | 68255.5561 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 357569.4473 | 28944.1669 | 328625.2804 |  | 0 | 212.6 | 13587.5023 | 4634.0895 | 1095.7758 | 11216.4218 | 0 | 7255.5656 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 38009.6322 | 3076.7649 | 35061.9923 |  | 0 | 6.8259 | 436.2533 | 148.7865 | 35.182 | 360.1251 | 0 | 232.9541 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.3734 | 98.7855 | 1125.7337 |  | 0 | 3.444 | 0.81436 | 8.3358 | 5.3922 | 0.0057056 | 0 | 10.098 | 0.158 | 0 | 0 | 0 | 26.0574 | 28.2481 | 28.2481
US_2A_SH_2022_NG | 2A | SH | NG |  |  | HotelSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 37.9127 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 690683.8135 | 0 | 0 | 1090217.1641 | 0 | 1090217.1641 |  | 0 | 0.37154 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 6768.7014 | 0 | 0 | 10684.1282 | 0 | 10684.1282 |  | 0 | 0.037913 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 690.6838 | 0 | 0 | 1090.2172 | 0 | 1090.2172 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.00087757 | 15.9873 | 0 | 0 | 25.2353 | 25.2353 | 25.2353
US_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 83.3333 | 10700.0001 | 7394.4445 | 2744.4445 | 13416.6668 | 0 | 5336.1112 | 0 | 0 | 0 | 0 | 6502.7778 | 0 | 0 | 46177.7781 | 0 | 46177.7781 |  | 0 | 8.8583 | 1137.41 | 786.0295 | 291.7344 | 1426.1917 | 0 | 567.2286 | 0 | 0 | 0 | 0 | 691.2453 | 0 | 0 | 4908.6978 | 0 | 4908.4616 |  | 0 | 0.28441 | 36.5188 | 25.237 | 9.3667 | 45.7907 | 0 | 18.212 | 0 | 0 | 0 | 0 | 22.1938 | 0 | 0 | 157.6033 | 0 | 157.5957 |  | 0 | 4.5869 | 1.7024 | 8.3225 | 3.3101 | 0 | 0 | 6.6374 | 0.051693 | 4.0338 | 0 | 0 | 28.6434 | 28.6447 | 28.6447
US_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_2A_SO_2022_EL | 2A | SO | EL |  |  | OfficeSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 77.7778 | 9777.7779 | 5391.6667 | 1927.7778 | 13416.6668 | 0 | 5150 | 0 | 0 | 0 | 0 | 6505.5556 | 0 | 0 | 42247.2226 | 805.8333 | 41441.3892 |  | 0 | 8.2678 | 1039.3778 | 573.1342 | 204.9228 | 1426.1917 | 0 | 547.445 | 0 | 0 | 0 | 0 | 691.5406 | 0 | 0 | 4490.8798 | 85.6601 | 4408.4973 |  | 0 | 0.26545 | 33.3713 | 18.4016 | 6.5794 | 45.7907 | 0 | 17.5768 | 0 | 0 | 0 | 0 | 22.2033 | 0 | 0 | 144.1885 | 2.7503 | 141.5434 |  | 0 | 3.3445 | 1.1958 | 8.3225 | 3.1946 | 0 | 0 | 6.0653 | 0.048247 | 4.0355 | 0 | 0 | 25.7258 | 26.2066 | 26.2066
US_2A_SO_2022_NG | 2A | SO | NG |  |  | OfficeSmall | STD2022 | Tampa | Zone2A | Zone2A(Tampa) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 807900.0065 | 683780.561 | 98152.7786 | 4076777.8104 | 530358.3376 | 646741.6718 | 134530.5566 | 287894.4467 | 266897.2244 | 10752.7779 | 0 | 0 | 0 | 7543786.1715 | 0 | 7543786.1715 |  | 530358.3376 | 0 | 85879.7707 | 72685.8736 | 10433.6404 | 433361.4812 | 56377.0913 | 68748.6397 | 14300.5982 | 30603.1797 | 28371.1749 | 1143.0203 | 0 | 0 | 0 | 801904.47 | 0 | 801904.47 |  | 56377.0913 | 0 | 2757.3377 | 2333.7219 | 334.9924 | 13913.9163 | 1810.0966 | 2207.3093 | 459.1486 | 982.5748 | 910.912 | 36.6989 | 0 | 0 | 0 | 25746.7083 | 0 | 25746.7083 |  | 1810.0966 | 4.6807 | 0.67188 | 31.5371 | 4.4271 | 0.9209 | 0.073606 | 7.501 | 0 | 0 | 1.827 | 0 | 51.6392 | 51.6392 | 51.6392
US_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 418224.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670353.1363 | 0 | 0 | 1088577.4405 | 0 | 1088577.4405 |  | 0 | 4098.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6569.4607 | 0 | 0 | 10668.0589 | 0 | 10668.0589 |  | 0 | 418.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670.3531 | 0 | 0 | 1088.5774 | 0 | 1088.5774 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83882 | 1.3445 | 0 | 0 | 2.1833 | 2.1833 | 2.1833
US_3A_LO_2022_EL | 3A | LO | EL |  |  | OfficeLarge | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 748405.5615 | 476594.4483 | 73952.7784 | 4076777.8104 | 334358.336 | 624638.8939 | 127863.8899 | 281800.0023 | 266638.891 | 10869.4445 | 0 | 0 | 0 | 7021900.0562 | 152267.779 | 6869632.2772 |  | 334358.336 | 0 | 79555.5112 | 50661.9898 | 7861.1803 | 433361.4812 | 35542.2911 | 66399.1144 | 13591.9315 | 29955.3402 | 28343.7141 | 1155.422 | 0 | 0 | 0 | 746427.976 | 16186.0649 | 730932.3296 |  | 35542.2911 | 0 | 2554.285 | 1626.6021 | 252.3985 | 13913.9163 | 1141.1546 | 2131.8732 | 436.3955 | 961.7747 | 910.0303 | 37.0971 | 0 | 0 | 0 | 23965.5272 | 519.6852 | 23468.0092 |  | 1141.1546 | 3.2624 | 0.50623 | 30.1954 | 4.2758 | 0.87526 | 0.074404 | 7.052 | 0 | 0 | 1.8252 | 0 | 47.0689 | 48.0668 | 48.0668
US_3A_LO_2022_NG | 3A | LO | NG |  |  | OfficeLarge | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 381600.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670372.0926 | 0 | 0 | 1051972.7433 | 0 | 1051972.7433 |  | 0 | 3739.6864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6569.6465 | 0 | 0 | 10309.3329 | 0 | 10309.3329 |  | 0 | 381.6007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670.3721 | 0 | 0 | 1051.9727 | 0 | 1051.9727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76536 | 1.3445 | 0 | 0 | 2.1099 | 2.1099 | 2.1099
US_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 44241.667 | 20277.7779 | 9177.7779 | 125580.5566 | 0 | 28511.1113 | 0 | 0 | 0 | 0 | 117227.7787 | 0 | 0 | 345016.6694 | 0 | 345016.6694 |  | 0 | 0 | 4702.8892 | 2155.5278 | 975.5978 | 13349.2132 | 0 | 3030.7311 | 0 | 0 | 0 | 0 | 12461.3129 | 0 | 0 | 36675.272 | 0 | 36675.1538 |  | 0 | 0 | 150.9954 | 69.2074 | 31.3235 | 428.6025 | 0 | 97.3075 | 0 | 0 | 0 | 0 | 400.0948 | 0 | 0 | 1177.5312 | 0 | 1177.5274 |  | 0 | 2.0511 | 0.92835 | 12.7027 | 2.884 | 0 | 0 | 4.4751 | 0 | 11.8578 | 0 | 0 | 34.899 | 34.8991 | 34.8991
US_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 72176.2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72176.2737 | 0 | 72176.2737 |  | 0 | 707.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.3275 | 0 | 707.3275 |  | 0 | 72.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1763 | 0 | 72.1763 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1391 | 0 | 0 | 0 | 2.1391 | 2.1391 | 2.1391
US_3A_MA_2022_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 39969.4448 | 15900.0001 | 6341.6667 | 117269.4454 | 0 | 27047.2224 | 0 | 0 | 0 | 0 | 107886.112 | 0 | 0 | 314413.8914 | 20941.3891 | 293472.5023 |  | 0 | 0 | 4248.752 | 1690.17 | 674.1192 | 12465.742 | 0 | 2875.1197 | 0 | 0 | 0 | 0 | 11468.2937 | 0 | 0 | 33422.1967 | 2226.0697 | 31290.6159 |  | 0 | 0 | 136.4145 | 54.2662 | 21.6439 | 400.237 | 0 | 92.3113 | 0 | 0 | 0 | 0 | 368.212 | 0 | 0 | 1073.0849 | 71.4723 | 1004.6463 |  | 0 | 1.6083 | 0.64147 | 11.862 | 2.7359 | 0 | 0 | 4.043 | 0 | 10.9129 | 0 | 0 | 29.7752 | 31.8036 | 31.8036
US_3A_MA_2022_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 74327.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74327.8186 | 0 | 74327.8186 |  | 0 | 728.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.4126 | 0 | 728.4126 |  | 0 | 74.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3278 | 0 | 74.3278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2029 | 0 | 0 | 0 | 2.2029 | 2.2029 | 2.2029
US_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 169541.668 | 79038.8895 | 8333.3334 | 312394.4469 | 4744.4445 | 66347.2228 | 386.1111 | 0 | 0 | 12025.0001 | 7177.7778 | 12505.5557 | 0 | 672494.4498 | 0 | 672494.4498 |  | 4744.4445 | 0 | 18022.2793 | 8401.834 | 885.8333 | 33207.5297 | 504.3344 | 7052.7098 | 41.0436 | 0 | 0 | 1278.2575 | 762.9978 | 1329.3406 | 0 | 71486.16 | 0 | 71485.658 |  | 504.3344 | 0 | 578.6405 | 269.7573 | 28.4414 | 1066.1926 | 16.1926 | 226.441 | 1.3178 | 0 | 0 | 41.041 | 24.4975 | 42.6811 | 0 | 2295.2027 | 0 | 2295.1866 |  | 16.1926 | 3.6474 | 0.38456 | 14.6349 | 3.0617 | 0.017818 | 0.55491 | 7.8238 | 0 | 0.33123 | 0 | 0.57709 | 31.0332 | 31.0334 | 31.0334
US_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 449369.5748 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130410.1575 | 0 | 0 | 921970.1471 | 0 | 921970.1471 |  | 0 | 4403.8218 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1278.0195 | 0 | 0 | 9035.3074 | 0 | 9035.3074 |  | 0 | 449.3696 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4102 | 0 | 0 | 921.9701 | 0 | 921.9701 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.0759 | 1.7633 | 0 | 0 | 12.466 | 12.466 | 12.466
US_3A_PS_2022_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 155088.8901 | 69272.2228 | 5850 | 312394.4469 | 4741.6667 | 66327.7783 | 794.4445 | 0 | 0 | 11227.7779 | 7177.7778 | 12505.5557 | 0 | 645380.5607 | 62927.5005 | 582453.0602 |  | 4741.6667 | 0 | 16485.949 | 7363.6373 | 621.855 | 33207.5297 | 504.0392 | 7050.6428 | 84.4494 | 0 | 0 | 1193.5128 | 762.9978 | 1329.3406 | 0 | 68603.9536 | 6689.1933 | 62200.3234 |  | 504.0392 | 0 | 529.3136 | 236.4239 | 19.9659 | 1066.1926 | 16.1832 | 226.3747 | 2.7114 | 0 | 0 | 38.3201 | 24.4975 | 42.6811 | 0 | 2202.6638 | 214.7696 | 1997.0628 |  | 16.1832 | 3.1967 | 0.26996 | 14.6348 | 3.0608 | 0.036661 | 0.51813 | 7.1569 | 0 | 0.33123 | 0 | 0.57709 | 27.0023 | 29.7822 | 29.7822
US_3A_PS_2022_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 405940.5943 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130419.6357 | 0 | 0 | 878550.6449 | 0 | 878550.6449 |  | 0 | 3978.2178 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1278.1124 | 0 | 0 | 8609.7963 | 0 | 8609.7963 |  | 0 | 405.9406 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4196 | 0 | 0 | 878.5506 | 0 | 878.5506 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.4887 | 1.7634 | 0 | 0 | 11.8789 | 11.8789 | 11.8789
US_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 54113.8893 | 62802.7783 | 12113.889 | 53972.2227 | 0 | 35272.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218275.0017 | 0 | 218275.0017 |  | 0 | 0 | 5752.3064 | 6675.9353 | 1287.7064 | 5737.2473 | 0 | 3749.4373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23202.6327 | 0 | 23202.6622 |  | 0 | 0 | 184.689 | 214.3439 | 41.3443 | 184.2055 | 0 | 120.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744.9658 | 0 | 744.9668 |  | 0 | 8.6807 | 1.6744 | 7.4601 | 4.8754 | 0 | 0 | 7.4797 | 0 | 0 | 0 | 0 | 30.1704 | 30.1703 | 30.1703
US_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 186511.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86564.1376 | 0 | 0 | 273075.5904 | 0 | 273075.5904 |  | 0 | 1827.8122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.3285 | 0 | 0 | 2676.1408 | 0 | 2676.1408 |  | 0 | 186.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5641 | 0 | 0 | 273.0756 | 0 | 273.0756 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5535 | 3.5058 | 0 | 0 | 11.0593 | 11.0593 | 11.0593
US_3A_RS_2022_EL | 3A | RS | EL |  |  | RetailStandalone | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 46230.5559 | 40625.0003 | 8230.5556 | 53972.2227 | 0 | 35716.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184775.0015 | 21005.8335 | 163769.168 |  | 0 | 0 | 4914.3081 | 4318.4375 | 874.9081 | 5737.2473 | 0 | 3796.6817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19641.5827 | 2232.9201 | 17503.8306 |  | 0 | 0 | 157.7835 | 138.6519 | 28.0906 | 184.2055 | 0 | 121.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630.6314 | 71.6923 | 561.9946 |  | 0 | 5.6153 | 1.1376 | 7.4601 | 4.9368 | 0 | 0 | 6.3901 | 0 | 0 | 0 | 0 | 22.7602 | 25.5399 | 25.5399
US_3A_RS_2022_NG | 3A | RS | NG |  |  | RetailStandalone | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 149271.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86564.1376 | 0 | 0 | 235835.8558 | 0 | 235835.8558 |  | 0 | 1462.8628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.3285 | 0 | 0 | 2311.1914 | 0 | 2311.1914 |  | 0 | 149.2717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5641 | 0 | 0 | 235.8359 | 0 | 235.8359 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0453 | 3.5058 | 0 | 0 | 9.5511 | 9.5511 | 9.5511
US_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 15588.889 | 95338.8897 | 49186.1115 | 14497.2223 | 122138.8899 | 0 | 69980.5561 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 366802.7807 | 0 | 366802.7807 |  | 0 | 1657.0989 | 10134.524 | 5228.4837 | 1541.0547 | 12983.364 | 0 | 7438.9331 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 38991.1356 | 0 | 38990.8108 |  | 0 | 53.2044 | 325.3887 | 167.8707 | 49.4786 | 416.8562 | 0 | 238.8415 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.8865 | 0 | 1251.8761 |  | 0 | 3.8857 | 1.1453 | 9.649 | 5.5285 | 0.0057056 | 0 | 7.5318 | 1.2315 | 0 | 0 | 0 | 28.9773 | 28.9775 | 28.9775
US_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 28718.8587 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 882597.824 | 0 | 0 | 1310812.1206 | 0 | 1310812.1206 |  | 0 | 281.4448 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 8649.4587 | 0 | 0 | 12845.9588 | 0 | 12845.9588 |  | 0 | 28.7189 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 882.5978 | 0 | 0 | 1310.8121 | 0 | 1310.8121 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.66476 | 20.4296 | 0 | 0 | 30.3415 | 30.3415 | 30.3415
US_3A_SH_2022_EL | 3A | SH | EL |  |  | HotelSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 14480.5557 | 88172.2229 | 45511.1115 | 10313.889 | 105516.6675 | 0 | 67102.7783 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 331169.4471 | 28006.3891 | 303163.058 |  | 0 | 1539.2831 | 9372.7073 | 4837.8311 | 1096.3664 | 11216.4218 | 0 | 7133.0253 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 35203.3122 | 2977.0792 | 32352.8186 |  | 0 | 49.4217 | 300.9291 | 155.328 | 35.201 | 360.1251 | 0 | 229.0197 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1130.2711 | 95.5849 | 1038.7504 |  | 0 | 3.5954 | 0.8148 | 8.3358 | 5.3011 | 0.0057056 | 0 | 6.9656 | 1.144 | 0 | 0 | 0 | 24.044 | 26.1625 | 26.1625
US_3A_SH_2022_NG | 3A | SH | NG |  |  | HotelSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 4141.9608 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 747770.8387 | 0 | 0 | 1151408.2374 | 0 | 1151408.2374 |  | 0 | 40.5912 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 7328.1542 | 0 | 0 | 11283.8007 | 0 | 11283.8007 |  | 0 | 4.142 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 747.7708 | 0 | 0 | 1151.4082 | 0 | 1151.4082 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.095874 | 17.3087 | 0 | 0 | 26.6517 | 26.6517 | 26.6517
US_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 1727.7778 | 5725 | 7427.7778 | 2766.6667 | 13416.6668 | 0 | 5163.8889 | 0 | 0 | 0 | 0 | 6694.4445 | 0 | 0 | 42922.2226 | 0 | 42922.2226 |  | 0 | 183.6628 | 608.5675 | 789.5728 | 294.0967 | 1426.1917 | 0 | 548.9214 | 0 | 0 | 0 | 0 | 711.6195 | 0 | 0 | 4562.6323 | 0 | 4562.8685 |  | 0 | 5.8969 | 19.5392 | 25.3508 | 9.4425 | 45.7907 | 0 | 17.6242 | 0 | 0 | 0 | 0 | 22.8479 | 0 | 0 | 146.4922 | 0 | 146.4998 |  | 0 | 4.6076 | 1.7162 | 8.3225 | 3.2032 | 0 | 0 | 3.5513 | 1.0718 | 4.1527 | 0 | 0 | 26.6266 | 26.6253 | 26.6253
US_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 1573.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3764 | 0 | 1573.3764 |  | 0 | 15.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4191 | 0 | 15.4191 |  | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5734 | 0 | 1.5734 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28596 | 0 | 0 | 0 | 0.28596 | 0.28596 | 0.28596
US_3A_SO_2022_EL | 3A | SO | EL |  |  | OfficeSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 1666.6667 | 5197.2223 | 5413.8889 | 1941.6667 | 13416.6668 | 0 | 4947.2223 | 0 | 0 | 0 | 0 | 6697.2223 | 0 | 0 | 39280.5559 | 779.7222 | 38500.8336 |  | 0 | 177.1667 | 552.4647 | 575.4964 | 206.3992 | 1426.1917 | 0 | 525.8897 | 0 | 0 | 0 | 0 | 711.9147 | 0 | 0 | 4175.5231 | 82.8845 | 4096.0638 |  | 0 | 5.6883 | 17.738 | 18.4774 | 6.6268 | 45.7907 | 0 | 16.8847 | 0 | 0 | 0 | 0 | 22.8574 | 0 | 0 | 134.0633 | 2.6612 | 131.5121 |  | 0 | 3.3583 | 1.2044 | 8.3225 | 3.0688 | 0 | 0 | 3.2239 | 1.0339 | 4.1544 | 0 | 0 | 23.9026 | 24.3663 | 24.3663
US_3A_SO_2022_NG | 3A | SO | NG |  |  | OfficeSmall | STD2022 | Atlanta | Zone3A | Zone3A(Atlanta) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 1516.5074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1516.5074 | 0 | 1516.5074 |  | 0 | 14.8618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8618 | 0 | 14.8618 |  | 0 | 1.5165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5165 | 0 | 1.5165 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27563 | 0 | 0 | 0 | 0.27563 | 0.27563 | 0.27563
US_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 879747.2293 | 682994.4499 | 96608.3341 | 4076777.8104 | 530358.3376 | 758438.895 | 139966.6678 | 267875.0021 | 496619.4484 | 0 | 0 | 0 | 0 | 7929386.1745 | 0 | 7929386.1745 |  | 530358.3376 | 0 | 93517.1305 | 72602.31 | 10269.4659 | 433361.4812 | 56377.0913 | 80622.0545 | 14878.4568 | 28475.1127 | 52790.6474 | 0 | 0 | 0 | 0 | 842893.7504 | 0 | 842893.3665 |  | 56377.0913 | 0 | 3002.55 | 2331.0389 | 329.7212 | 13913.9163 | 1810.0966 | 2588.5284 | 477.7019 | 914.2491 | 1694.9468 | 0 | 0 | 0 | 0 | 27062.7492 | 0 | 27062.7369 |  | 1810.0966 | 4.6753 | 0.66131 | 31.5371 | 5.1917 | 0.95811 | 0 | 7.8558 | 0 | 0 | 3.3995 | 0 | 54.2788 | 54.2788 | 54.2788
US_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 371563.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655216.4969 | 0 | 0 | 1026779.7643 | 0 | 1026779.7643 |  | 0 | 3641.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6421.1217 | 0 | 0 | 10062.4417 | 0 | 10062.4417 |  | 0 | 371.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.2165 | 0 | 0 | 1026.7798 | 0 | 1026.7798 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74523 | 1.3141 | 0 | 0 | 2.0594 | 2.0594 | 2.0594
US_3B_LO_2022_EL | 3B | LO | EL |  |  | OfficeLarge | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 815747.2287 | 490958.3373 | 72950.0006 | 4076777.8104 | 334363.8916 | 734255.5614 | 135425.0011 | 263938.891 | 496616.6706 | 0 | 0 | 0 | 0 | 7421033.3927 | 183140.557 | 7237892.8357 |  | 334363.8916 | 0 | 86713.9304 | 52188.8713 | 7754.5851 | 433361.4812 | 35542.8817 | 78051.3662 | 14395.6776 | 28056.7041 | 52790.3521 | 0 | 0 | 0 | 0 | 788855.8496 | 19467.8412 | 770189.1561 |  | 35542.8817 | 0 | 2784.12 | 1675.6256 | 248.9761 | 13913.9163 | 1141.1736 | 2505.9915 | 462.2013 | 900.8153 | 1694.9373 | 0 | 0 | 0 | 0 | 25327.7569 | 625.053 | 24728.4263 |  | 1141.1736 | 3.3607 | 0.49936 | 30.1955 | 5.0262 | 0.92702 | 0 | 7.3907 | 0 | 0 | 3.3995 | 0 | 49.5969 | 50.799 | 50.799
US_3B_LO_2022_NG | 3B | LO | NG |  |  | OfficeLarge | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 328191.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655225.9751 | 0 | 0 | 983417.131 | 0 | 983417.131 |  | 0 | 3216.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6421.2146 | 0 | 0 | 9637.4879 | 0 | 9637.4879 |  | 0 | 328.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.226 | 0 | 0 | 983.4171 | 0 | 983.4171 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65824 | 1.3142 | 0 | 0 | 1.9724 | 1.9724 | 1.9724
US_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 50672.2226 | 20277.7779 | 9177.7779 | 125580.5566 | 0 | 31447.2225 | 0 | 0 | 0 | 0 | 114222.2231 | 0 | 0 | 351377.7806 | 0 | 351377.7806 |  | 0 | 0 | 5386.4573 | 2155.5278 | 975.5978 | 13349.2132 | 0 | 3342.8397 | 0 | 0 | 0 | 0 | 12141.8223 | 0 | 0 | 37351.4581 | 0 | 37351.34 |  | 0 | 0 | 172.9427 | 69.2074 | 31.3235 | 428.6025 | 0 | 107.3284 | 0 | 0 | 0 | 0 | 389.8369 | 0 | 0 | 1199.2415 | 0 | 1199.2377 |  | 0 | 2.0511 | 0.92835 | 12.7027 | 3.1809 | 0 | 0 | 5.1256 | 0 | 11.5538 | 0 | 0 | 35.5424 | 35.5426 | 35.5426
US_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 22586.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22586.482 | 0 | 22586.482 |  | 0 | 221.3475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.3475 | 0 | 221.3475 |  | 0 | 22.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5865 | 0 | 22.5865 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66941 | 0 | 0 | 0 | 0.66941 | 0.66941 | 0.66941
US_3B_MA_2022_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 45877.7781 | 15900.0001 | 6341.6667 | 117269.4454 | 0 | 30013.8891 | 0 | 0 | 0 | 0 | 105172.2231 | 0 | 0 | 320575.0026 | 25187.2224 | 295387.7801 |  | 0 | 0 | 4876.8078 | 1690.17 | 674.1192 | 12465.742 | 0 | 3190.4764 | 0 | 0 | 0 | 0 | 11179.8073 | 0 | 0 | 34077.1228 | 2677.4017 | 31509.6234 |  | 0 | 0 | 156.5794 | 54.2662 | 21.6439 | 400.237 | 0 | 102.4365 | 0 | 0 | 0 | 0 | 358.9495 | 0 | 0 | 1094.1125 | 85.9632 | 1011.678 |  | 0 | 1.6083 | 0.64147 | 11.862 | 3.036 | 0 | 0 | 4.6406 | 0 | 10.6384 | 0 | 0 | 29.9836 | 32.4268 | 32.4268
US_3B_MA_2022_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 23212.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23212.0413 | 0 | 23212.0413 |  | 0 | 227.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.478 | 0 | 227.478 |  | 0 | 23.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.212 | 0 | 23.212 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68795 | 0 | 0 | 0 | 0.68795 | 0.68795 | 0.68795
US_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 155222.2235 | 80119.4451 | 8283.3334 | 312394.4469 | 4744.4445 | 74466.6673 | 163.8889 | 0 | 0 | 0 | 7177.7778 | 12411.1112 | 0 | 654983.3386 | 0 | 654983.3386 |  | 4744.4445 | 0 | 16500.1224 | 8516.697 | 880.5183 | 33207.5297 | 504.3344 | 7915.8067 | 17.4214 | 0 | 0 | 0 | 762.9978 | 1319.3011 | 0 | 69624.7289 | 0 | 69624.6994 |  | 504.3344 | 0 | 529.7686 | 273.4452 | 28.2708 | 1066.1926 | 16.1926 | 254.1524 | 0.55935 | 0 | 0 | 0 | 24.4975 | 42.3587 | 0 | 2235.4378 | 0 | 2235.4369 |  | 16.1926 | 3.6973 | 0.38225 | 14.6349 | 3.4364 | 0.0075629 | 0 | 7.163 | 0 | 0.33123 | 0 | 0.57273 | 30.2254 | 30.2254 | 30.2254
US_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 157053.2968 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127225.492 | 0 | 0 | 626469.2036 | 0 | 626469.2036 |  | 0 | 1539.1223 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.8098 | 0 | 0 | 6139.3982 | 0 | 6139.3982 |  | 0 | 157.0533 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2255 | 0 | 0 | 626.4692 | 0 | 626.4692 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.1235 | 1.7202 | 0 | 0 | 8.4705 | 8.4705 | 8.4705
US_3B_PS_2022_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 147066.6678 | 73866.6673 | 5819.4445 | 312394.4469 | 4741.6667 | 74288.8895 | 311.1111 | 0 | 0 | 0 | 7177.7778 | 12413.889 | 0 | 638080.5607 | 75686.3895 | 562394.1712 |  | 4741.6667 | 0 | 15633.1868 | 7852.0267 | 618.6069 | 33207.5297 | 504.0392 | 7896.909 | 33.0711 | 0 | 0 | 0 | 762.9978 | 1319.5964 | 0 | 67827.9636 | 8045.4632 | 60113.8611 |  | 504.0392 | 0 | 501.934 | 252.1046 | 19.8616 | 1066.1926 | 16.1832 | 253.5457 | 1.0618 | 0 | 0 | 0 | 24.4975 | 42.3682 | 0 | 2177.7492 | 258.3153 | 1930.0729 |  | 16.1832 | 3.4087 | 0.26855 | 14.6348 | 3.4282 | 0.014357 | 0 | 6.7867 | 0 | 0.33123 | 0 | 0.57286 | 26.0965 | 29.4454 | 29.4454
US_3B_PS_2022_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 137556.6986 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127225.492 | 0 | 0 | 606972.6055 | 0 | 606972.6055 |  | 0 | 1348.0556 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.8098 | 0 | 0 | 5948.3315 | 0 | 5948.3315 |  | 0 | 137.5567 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2255 | 0 | 0 | 606.9726 | 0 | 606.9726 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.8599 | 1.7202 | 0 | 0 | 8.2069 | 8.2069 | 8.2069
US_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 54041.6671 | 64861.1116 | 12111.1112 | 53972.2227 | 0 | 38888.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223875.0018 | 0 | 223875.0018 |  | 0 | 0 | 5744.6292 | 6894.7362 | 1287.4111 | 5737.2473 | 0 | 4133.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23797.9127 | 0 | 23798.0308 |  | 0 | 0 | 184.4425 | 221.369 | 41.3348 | 184.2055 | 0 | 132.7266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0784 | 0 | 764.0822 |  | 0 | 8.9652 | 1.674 | 7.4601 | 5.3753 | 0 | 0 | 7.4697 | 0 | 0 | 0 | 0 | 30.9445 | 30.9444 | 30.9444
US_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 71332.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85625.7986 | 0 | 0 | 156958.5151 | 0 | 156958.5151 |  | 0 | 699.0606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839.1328 | 0 | 0 | 1538.1934 | 0 | 1538.1934 |  | 0 | 71.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6258 | 0 | 0 | 156.9585 | 0 | 156.9585 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8889 | 3.4678 | 0 | 0 | 6.3567 | 6.3567 | 6.3567
US_3B_RS_2022_EL | 3B | RS | EL |  |  | RetailStandalone | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 47222.2226 | 48436.1115 | 8230.5556 | 53972.2227 | 0 | 39683.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197544.446 | 25264.7224 | 172279.7236 |  | 0 | 0 | 5019.7223 | 5148.7587 | 874.9081 | 5737.2473 | 0 | 4218.3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20998.9746 | 2685.64 | 18423.9161 |  | 0 | 0 | 161.168 | 165.3109 | 28.0906 | 184.2055 | 0 | 135.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.2131 | 86.2277 | 591.5358 |  | 0 | 6.6949 | 1.1376 | 7.4601 | 5.4851 | 0 | 0 | 6.5271 | 0 | 0 | 0 | 0 | 23.9566 | 27.3049 | 27.3049
US_3B_RS_2022_NG | 3B | RS | NG |  |  | RetailStandalone | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 48130.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85625.7986 | 0 | 0 | 133755.952 | 0 | 133755.952 |  | 0 | 471.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839.1328 | 0 | 0 | 1310.8083 | 0 | 1310.8083 |  | 0 | 48.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6258 | 0 | 0 | 133.756 | 0 | 133.756 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9492 | 3.4678 | 0 | 0 | 5.417 | 5.417 | 5.417
US_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 6236.1112 | 96908.3341 | 49255.5559 | 14497.2223 | 122138.8899 | 0 | 80322.2229 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 369430.5585 | 0 | 369430.5585 |  | 0 | 662.8986 | 10301.3559 | 5235.8656 | 1541.0547 | 12983.364 | 0 | 8538.2523 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 39270.4684 | 0 | 39270.4388 |  | 0 | 21.2837 | 330.7451 | 168.1077 | 49.4786 | 416.8562 | 0 | 274.1373 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.855 | 0 | 1260.8541 |  | 0 | 3.8912 | 1.1453 | 9.649 | 6.3455 | 0.0057056 | 0 | 7.6558 | 0.49265 | 0 | 0 | 0 | 29.1851 | 29.1851 | 29.1851
US_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 12776.5748 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 865290.6834 | 0 | 0 | 1277562.696 | 0 | 1277562.696 |  | 0 | 125.2104 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 8479.8487 | 0 | 0 | 12520.1144 | 0 | 12520.1144 |  | 0 | 12.7766 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 865.2907 | 0 | 0 | 1277.5627 | 0 | 1277.5627 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.29574 | 20.0289 | 0 | 0 | 29.5718 | 29.5718 | 29.5718
US_3B_SH_2022_EL | 3B | SH | EL |  |  | HotelSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 5727.7778 | 91583.3341 | 43819.4448 | 10313.889 | 105516.6675 | 0 | 77166.6673 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 334200.0027 | 33684.7225 | 300515.2802 |  | 0 | 608.8628 | 9735.3084 | 4658.007 | 1096.3664 | 11216.4218 | 0 | 8202.8167 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 35525.4603 | 3580.686 | 32091.9407 |  | 0 | 19.5487 | 312.5711 | 149.5544 | 35.201 | 360.1251 | 0 | 263.3674 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.6142 | 114.9649 | 1030.3744 |  | 0 | 3.4617 | 0.8148 | 8.3358 | 6.0962 | 0.0057056 | 0 | 7.2351 | 0.4525 | 0 | 0 | 0 | 23.8502 | 26.4019 | 26.4019
US_3B_SH_2022_NG | 3B | SH | NG |  |  | HotelSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 151.6507 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 733136.5423 | 0 | 0 | 1132783.631 | 0 | 1132783.631 |  | 0 | 1.4862 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 7184.7381 | 0 | 0 | 11101.2796 | 0 | 11101.2796 |  | 0 | 0.15165 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 733.1365 | 0 | 0 | 1132.7836 | 0 | 1132.7836 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.0035103 | 16.97 | 0 | 0 | 26.2206 | 26.2206 | 26.2206
US_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 702.7778 | 6463.8889 | 7444.4445 | 2722.2222 | 13416.6668 | 0 | 6102.7778 | 0 | 0 | 0 | 0 | 6644.4445 | 0 | 0 | 43497.2226 | 0 | 43497.2226 |  | 0 | 74.7053 | 687.1114 | 791.3445 | 289.3722 | 1426.1917 | 0 | 648.7253 | 0 | 0 | 0 | 0 | 706.3045 | 0 | 0 | 4623.7548 | 0 | 4623.8729 |  | 0 | 2.3986 | 22.0611 | 25.4077 | 9.2909 | 45.7907 | 0 | 20.8286 | 0 | 0 | 0 | 0 | 22.6773 | 0 | 0 | 148.4547 | 0 | 148.4585 |  | 0 | 4.6179 | 1.6886 | 8.3225 | 3.7856 | 0 | 0 | 4.0096 | 0.43594 | 4.1216 | 0 | 0 | 26.9826 | 26.9819 | 26.9819
US_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 208.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.5198 | 0 | 208.5198 |  | 0 | 2.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0435 | 0 | 2.0435 |  | 0 | 0.20852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20852 | 0 | 0.20852 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037899 | 0 | 0 | 0 | 0.037899 | 0.037899 | 0.037899
US_3B_SO_2022_EL | 3B | SO | EL |  |  | OfficeSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 702.7778 | 5880.5556 | 5458.3334 | 1911.1111 | 13416.6668 | 0 | 5855.5556 | 0 | 0 | 0 | 0 | 6644.4445 | 0 | 0 | 39869.4448 | 937.7778 | 38931.667 |  | 0 | 74.7053 | 625.1031 | 580.2208 | 203.1511 | 1426.1917 | 0 | 622.4456 | 0 | 0 | 0 | 0 | 706.3045 | 0 | 0 | 4238.122 | 99.6858 | 4142.6587 |  | 0 | 2.3986 | 20.0702 | 18.6291 | 6.5226 | 45.7907 | 0 | 19.9848 | 0 | 0 | 0 | 0 | 22.6773 | 0 | 0 | 136.0732 | 3.2006 | 133.0081 |  | 0 | 3.3859 | 1.1855 | 8.3225 | 3.6323 | 0 | 0 | 3.6478 | 0.43594 | 4.1216 | 0 | 0 | 24.1745 | 24.7316 | 24.7316
US_3B_SO_2022_NG | 3B | SO | NG |  |  | OfficeSmall | STD2022 | Elpaso | Zone3B | Zone3B(Elpaso) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 217.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217.9979 | 0 | 217.9979 |  | 0 | 2.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1364 | 0 | 2.1364 |  | 0 | 0.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.218 | 0 | 0.218 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039622 | 0 | 0 | 0 | 0.039622 | 0.039622 | 0.039622
US_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 601619.4493 | 684355.561 | 97658.3341 | 4076777.8104 | 530358.3376 | 617022.2272 | 113919.4454 | 203600.0016 | 350750.0028 | 12013.889 | 0 | 0 | 0 | 7288075.0583 | 0 | 7288075.0583 |  | 530358.3376 | 0 | 63952.1475 | 72746.9961 | 10381.0809 | 433361.4812 | 56377.0913 | 65589.4627 | 12109.637 | 21642.6802 | 37284.7253 | 1277.0764 | 0 | 0 | 0 | 774722.3787 | 0 | 774721.8767 |  | 56377.0913 | 0 | 2053.3085 | 2335.6843 | 333.3049 | 13913.9163 | 1810.0966 | 2105.8777 | 388.8035 | 694.8805 | 1197.0989 | 41.003 | 0 | 0 | 0 | 24873.9742 | 0 | 24873.9581 |  | 1810.0966 | 4.6846 | 0.6685 | 31.5371 | 4.2237 | 0.77981 | 0.082238 | 5.5119 | 0 | 0 | 2.401 | 0 | 49.8888 | 49.8888 | 49.8888
US_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 853575.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716957.3041 | 0 | 0 | 1570532.9678 | 0 | 1570532.9678 |  | 0 | 8365.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7026.1816 | 0 | 0 | 15391.2231 | 0 | 15391.2231 |  | 0 | 853.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.9573 | 0 | 0 | 1570.533 | 0 | 1570.533 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.712 | 1.438 | 0 | 0 | 3.15 | 3.15 | 3.15
US_4A_LO_2022_EL | 4A | LO | EL |  |  | OfficeLarge | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 557408.3378 | 476997.226 | 73786.1117 | 4076777.8104 | 334358.336 | 599333.3381 | 108847.2231 | 198902.7794 | 350380.5584 | 12130.5557 | 0 | 0 | 0 | 6788922.2765 | 132035.2788 | 6656886.9977 |  | 334358.336 | 0 | 59252.5063 | 50704.8051 | 7843.4637 | 433361.4812 | 35542.2911 | 63709.1338 | 11570.4598 | 21143.3654 | 37245.4534 | 1289.4781 | 0 | 0 | 0 | 721662.438 | 14035.3501 | 708251.6889 |  | 35542.2911 | 0 | 1902.4174 | 1627.9767 | 251.8297 | 13913.9163 | 1141.1546 | 2045.5061 | 371.4922 | 678.849 | 1195.838 | 41.4012 | 0 | 0 | 0 | 23170.3813 | 450.6323 | 22739.803 |  | 1141.1546 | 3.2652 | 0.50509 | 30.1954 | 4.1026 | 0.74509 | 0.083037 | 5.1772 | 0 | 0 | 2.3984 | 0 | 45.6084 | 46.472 | 46.472
US_4A_LO_2022_NG | 4A | LO | NG |  |  | OfficeLarge | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 690731.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716985.7386 | 0 | 0 | 1407716.943 | 0 | 1407716.943 |  | 0 | 6769.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7026.4602 | 0 | 0 | 13795.626 | 0 | 13795.626 |  | 0 | 690.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.9857 | 0 | 0 | 1407.7169 | 0 | 1407.7169 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3854 | 1.438 | 0 | 0 | 2.8234 | 2.8234 | 2.8234
US_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 33241.6669 | 20277.7779 | 9163.889 | 125580.5566 | 0 | 26719.4447 | 0 | 0 | 0 | 0 | 126444.4455 | 0 | 0 | 341427.7805 | 0 | 341427.7805 |  | 0 | 0 | 3533.5892 | 2155.5278 | 974.1214 | 13349.2132 | 0 | 2840.277 | 0 | 0 | 0 | 0 | 13441.0446 | 0 | 0 | 36293.7731 | 0 | 36293.4778 |  | 0 | 0 | 113.4528 | 69.2074 | 31.2761 | 428.6025 | 0 | 91.1926 | 0 | 0 | 0 | 0 | 431.551 | 0 | 0 | 1165.2824 | 0 | 1165.273 |  | 0 | 2.0511 | 0.92695 | 12.7027 | 2.7027 | 0 | 0 | 3.3625 | 0 | 12.7901 | 0 | 0 | 34.5358 | 34.5361 | 34.5361
US_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 196065.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196065.4494 | 0 | 196065.4494 |  | 0 | 1921.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1921.4414 | 0 | 1921.4414 |  | 0 | 196.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.0654 | 0 | 196.0654 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8109 | 0 | 0 | 0 | 5.8109 | 5.8109 | 5.8109
US_4A_MA_2022_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 28708.3336 | 15900.0001 | 6330.5556 | 117269.4454 | 0 | 25008.3335 | 0 | 0 | 0 | 0 | 116119.4454 | 0 | 0 | 309336.1136 | 18158.889 | 291177.2246 |  | 0 | 0 | 3051.6959 | 1690.17 | 672.9381 | 12465.742 | 0 | 2658.3859 | 0 | 0 | 0 | 0 | 12343.497 | 0 | 0 | 32882.4289 | 1930.2899 | 31038.0057 |  | 0 | 0 | 97.9807 | 54.2662 | 21.606 | 400.237 | 0 | 85.3527 | 0 | 0 | 0 | 0 | 396.3121 | 0 | 0 | 1055.7546 | 61.9757 | 996.5358 |  | 0 | 1.6083 | 0.64035 | 11.862 | 2.5296 | 0 | 0 | 2.9039 | 0 | 11.7457 | 0 | 0 | 29.5349 | 31.29 | 31.29
US_4A_MA_2022_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 163356.2806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163356.2806 | 0 | 163356.2806 |  | 0 | 1600.8916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600.8916 | 0 | 1600.8916 |  | 0 | 163.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.3563 | 0 | 163.3563 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8415 | 0 | 0 | 0 | 4.8415 | 4.8415 | 4.8415
US_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 108397.2231 | 79377.7784 | 8327.7778 | 312394.4469 | 4741.6667 | 70625.0006 | 441.6667 | 0 | 0 | 14147.2223 | 7177.7778 | 12502.7779 | 0 | 618133.3383 | 0 | 618133.3383 |  | 4741.6667 | 0 | 11522.6248 | 8437.8578 | 885.2428 | 33207.5297 | 504.0392 | 7507.4376 | 46.9492 | 0 | 0 | 1503.8497 | 762.9978 | 1329.0453 | 0 | 65707.5739 | 0 | 65707.9872 |  | 504.0392 | 0 | 369.9564 | 270.9139 | 28.4224 | 1066.1926 | 16.1832 | 241.0409 | 1.5074 | 0 | 0 | 48.284 | 24.4975 | 42.6716 | 0 | 2109.6699 | 0 | 2109.6832 |  | 16.1832 | 3.663 | 0.3843 | 14.6348 | 3.2591 | 0.020381 | 0.65285 | 5.0022 | 0 | 0.33123 | 0 | 0.57696 | 28.525 | 28.5249 | 28.5249
US_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 564235.5315 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 139679.809 | 0 | 0 | 1046105.7553 | 0 | 1046105.7553 |  | 0 | 5529.5082 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.8621 | 0 | 0 | 10251.8364 | 0 | 10251.8364 |  | 0 | 564.2355 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 139.6798 | 0 | 0 | 1046.1058 | 0 | 1046.1058 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.629 | 1.8886 | 0 | 0 | 14.1444 | 14.1444 | 14.1444
US_4A_PS_2022_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 97913.8897 | 69666.6672 | 5850 | 312394.4469 | 4741.6667 | 71430.5561 | 836.1111 | 0 | 0 | 13150.0001 | 7177.7778 | 12502.7779 | 0 | 595663.8937 | 54566.1115 | 541097.7821 |  | 4741.6667 | 0 | 10408.2465 | 7405.5667 | 621.855 | 33207.5297 | 504.0392 | 7593.0681 | 88.8786 | 0 | 0 | 1397.845 | 762.9978 | 1329.0453 | 0 | 63319.0719 | 5800.3777 | 57776.7965 |  | 504.0392 | 0 | 334.1771 | 237.7702 | 19.9659 | 1066.1926 | 16.1832 | 243.7903 | 2.8536 | 0 | 0 | 44.8805 | 24.4975 | 42.6716 | 0 | 2032.9824 | 186.2324 | 1855.0368 |  | 16.1832 | 3.2149 | 0.26996 | 14.6348 | 3.2963 | 0.038584 | 0.60683 | 4.5184 | 0 | 0.33123 | 0 | 0.57696 | 25.082 | 27.488 | 27.488
US_4A_PS_2022_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 459226.8728 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 139651.3745 | 0 | 0 | 941068.6621 | 0 | 941068.6621 |  | 0 | 4500.4234 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.5835 | 0 | 0 | 9222.4729 | 0 | 9222.4729 |  | 0 | 459.2269 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 139.6514 | 0 | 0 | 941.0687 | 0 | 941.0687 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.2092 | 1.8882 | 0 | 0 | 12.7242 | 12.7242 | 12.7242
US_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 36305.5558 | 64775.0005 | 12175.0001 | 53972.2227 | 0 | 36750.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203977.7794 | 0 | 203977.7794 |  | 0 | 0 | 3859.2806 | 6885.5826 | 1294.2025 | 5737.2473 | 0 | 3906.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21682.838 | 0 | 21682.7494 |  | 0 | 0 | 123.9097 | 221.0751 | 41.5529 | 184.2055 | 0 | 125.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.1698 | 0 | 696.167 |  | 0 | 8.9533 | 1.6828 | 7.4601 | 5.0796 | 0 | 0 | 5.0182 | 0 | 0 | 0 | 0 | 28.194 | 28.1941 | 28.1941
US_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 424792.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89360.1981 | 0 | 0 | 514152.8749 | 0 | 514152.8749 |  | 0 | 4162.9682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875.7299 | 0 | 0 | 5038.6982 | 0 | 5038.6982 |  | 0 | 424.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3602 | 0 | 0 | 514.1529 | 0 | 514.1529 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2037 | 3.619 | 0 | 0 | 20.8227 | 20.8227 | 20.8227
US_4A_RS_2022_EL | 4A | RS | EL |  |  | RetailStandalone | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 31652.778 | 41841.667 | 8275.0001 | 53972.2227 | 0 | 36508.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172250.0014 | 18214.7224 | 154035.279 |  | 0 | 0 | 3364.6903 | 4447.7692 | 879.6325 | 5737.2473 | 0 | 3880.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18310.1751 | 1936.225 | 16460.2008 |  | 0 | 0 | 108.03 | 142.8043 | 28.2423 | 184.2055 | 0 | 124.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.8839 | 62.1663 | 528.4869 |  | 0 | 5.7834 | 1.1438 | 7.4601 | 5.0462 | 0 | 0 | 4.3751 | 0 | 0 | 0 | 0 | 21.4032 | 23.8087 | 23.8087
US_4A_RS_2022_NG | 4A | RS | NG |  |  | RetailStandalone | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 321992.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89360.1981 | 0 | 0 | 411352.6301 | 0 | 411352.6301 |  | 0 | 3155.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875.7299 | 0 | 0 | 4031.2558 | 0 | 4031.2558 |  | 0 | 321.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3602 | 0 | 0 | 411.3526 | 0 | 411.3526 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0404 | 3.619 | 0 | 0 | 16.6593 | 16.6593 | 16.6593
US_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 35502.7781 | 73327.7784 | 48761.1115 | 14475.0001 | 122138.8899 | 0 | 67911.1117 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 362188.8918 | 0 | 362188.8918 |  | 0 | 3773.9453 | 7794.7428 | 5183.3062 | 1538.6925 | 12983.364 | 0 | 7218.9512 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 38500.6792 | 0 | 38500.4134 |  | 0 | 121.1699 | 250.2654 | 166.4202 | 49.4027 | 416.8562 | 0 | 231.7785 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.1395 | 0 | 1236.1309 |  | 0 | 3.8521 | 1.1435 | 9.649 | 5.365 | 0.0057056 | 0 | 5.7929 | 2.8047 | 0 | 0 | 0 | 28.6128 | 28.613 | 28.613
US_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 67835.2713 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 935504.9756 | 0 | 0 | 1402835.6848 | 0 | 1402835.6848 |  | 0 | 664.7857 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 9167.9488 | 0 | 0 | 13747.7897 | 0 | 13747.7897 |  | 0 | 67.8353 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 935.505 | 0 | 0 | 1402.8357 | 0 | 1402.8357 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5702 | 21.6542 | 0 | 0 | 32.4715 | 32.4715 | 32.4715
US_4A_SH_2022_EL | 4A | SH | EL |  |  | HotelSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 32313.8891 | 64838.8894 | 45669.4448 | 10297.2223 | 105516.6675 | 0 | 62716.6672 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 321425.0026 | 24285.0002 | 297140.0024 |  | 0 | 3434.9664 | 6892.3739 | 4854.662 | 1094.5947 | 11216.4218 | 0 | 6666.7817 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 34167.4778 | 2581.4955 | 31700.4614 |  | 0 | 110.2863 | 221.2931 | 155.8684 | 35.1441 | 360.1251 | 0 | 214.05 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1097.0136 | 82.884 | 1017.8052 |  | 0 | 3.6079 | 0.81348 | 8.3358 | 4.9546 | 0.0057056 | 0 | 5.1223 | 2.5528 | 0 | 0 | 0 | 23.5592 | 25.3927 | 25.3927
US_4A_SH_2022_NG | 4A | SH | NG |  |  | HotelSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 14236.2131 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 792545.7194 | 0 | 0 | 1206277.3705 | 0 | 1206277.3705 |  | 0 | 139.5149 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 7766.9481 | 0 | 0 | 11821.5182 | 0 | 11821.5182 |  | 0 | 14.2362 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 792.5457 | 0 | 0 | 1206.2774 | 0 | 1206.2774 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.32953 | 18.3451 | 0 | 0 | 27.9218 | 27.9218 | 27.9218
US_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 3341.6667 | 4291.6667 | 7344.4445 | 2744.4445 | 13416.6668 | 0 | 4922.2223 | 0 | 0 | 0 | 0 | 6844.4445 | 0 | 0 | 42905.5559 | 0 | 42905.5559 |  | 0 | 355.2192 | 456.2042 | 780.7145 | 291.7344 | 1426.1917 | 0 | 523.2322 | 0 | 0 | 0 | 0 | 727.5645 | 0 | 0 | 4560.8606 | 0 | 4560.713 |  | 0 | 11.405 | 14.6473 | 25.0664 | 9.3667 | 45.7907 | 0 | 16.7994 | 0 | 0 | 0 | 0 | 23.3599 | 0 | 0 | 146.4353 | 0 | 146.4306 |  | 0 | 4.5559 | 1.7024 | 8.3225 | 3.0533 | 0 | 0 | 2.6622 | 2.0729 | 4.2457 | 0 | 0 | 26.6141 | 26.6149 | 26.6149
US_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 3004.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3004.5803 | 0 | 3004.5803 |  | 0 | 29.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.4449 | 0 | 29.4449 |  | 0 | 3.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0046 | 0 | 3.0046 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54609 | 0 | 0 | 0 | 0.54609 | 0.54609 | 0.54609
US_4A_SO_2022_EL | 4A | SO | EL |  |  | OfficeSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 2916.6667 | 3908.3334 | 5352.7778 | 1927.7778 | 13416.6668 | 0 | 4636.1111 | 0 | 0 | 0 | 0 | 6844.4445 | 0 | 0 | 39002.7781 | 676.1111 | 38326.667 |  | 0 | 310.0417 | 415.4558 | 569.0003 | 204.9228 | 1426.1917 | 0 | 492.8186 | 0 | 0 | 0 | 0 | 727.5645 | 0 | 0 | 4145.9953 | 71.8706 | 4077.4318 |  | 0 | 9.9545 | 13.339 | 18.2689 | 6.5794 | 45.7907 | 0 | 15.8229 | 0 | 0 | 0 | 0 | 23.3599 | 0 | 0 | 133.1153 | 2.3075 | 130.9139 |  | 0 | 3.3204 | 1.1958 | 8.3225 | 2.8758 | 0 | 0 | 2.4244 | 1.8092 | 4.2457 | 0 | 0 | 23.7939 | 24.194 | 24.194
US_4A_SO_2022_NG | 4A | SO | NG |  |  | OfficeSmall | STD2022 | Newyork | Zone4A | Zone4A(Newyork) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 2549.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2549.6281 | 0 | 2549.6281 |  | 0 | 24.9864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9864 | 0 | 24.9864 |  | 0 | 2.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5496 | 0 | 2.5496 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4634 | 0 | 0 | 0 | 0.4634 | 0.4634 | 0.4634
US_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 440350.0035 | 683655.561 | 98133.3341 | 4076777.8104 | 530358.3376 | 620355.5605 | 90044.4452 | 147002.779 | 401683.3365 | 10333.3334 | 0 | 0 | 0 | 7098694.5012 | 0 | 7098694.5012 |  | 530358.3376 | 0 | 46809.2054 | 72672.5861 | 10431.5734 | 433361.4812 | 56377.0913 | 65943.7961 | 9571.7245 | 15626.3954 | 42698.9387 | 1098.4333 | 0 | 0 | 0 | 754591.2255 | 0 | 754591.6093 |  | 56377.0913 | 0 | 1502.9009 | 2333.2952 | 334.926 | 13913.9163 | 1810.0966 | 2117.2543 | 307.3189 | 501.7159 | 1370.9328 | 35.2673 | 0 | 0 | 0 | 24227.6243 | 0 | 24227.6366 |  | 1810.0966 | 4.6798 | 0.67175 | 31.5371 | 4.2465 | 0.61638 | 0.070734 | 4.0206 | 0 | 0 | 2.7496 | 0 | 48.5925 | 48.5925 | 48.5925
US_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 1472301.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756481.278 | 0 | 0 | 2228782.4795 | 0 | 2228782.4795 |  | 0 | 14428.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7413.5165 | 0 | 0 | 21842.0683 | 0 | 21842.0683 |  | 0 | 1472.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.4813 | 0 | 0 | 2228.7825 | 0 | 2228.7825 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9529 | 1.5172 | 0 | 0 | 4.4702 | 4.4702 | 4.4702
US_5A_LO_2022_EL | 5A | LO | EL |  |  | OfficeLarge | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 387850.0031 | 476502.7816 | 74002.7784 | 4076777.8104 | 334358.336 | 603352.7826 | 85550.0007 | 142841.6678 | 401177.781 | 10480.5556 | 0 | 0 | 0 | 6592894.4972 | 127149.7232 | 6465744.7739 |  | 334358.336 | 0 | 41228.4553 | 50652.2457 | 7866.4953 | 433361.4812 | 35542.2911 | 64136.4008 | 9093.9651 | 15184.0693 | 42645.1981 | 1114.0831 | 0 | 0 | 0 | 700824.6851 | 13516.0156 | 687916.6464 |  | 35542.2911 | 0 | 1323.72 | 1626.2892 | 252.5692 | 13913.9163 | 1141.1546 | 2059.2243 | 291.9795 | 487.5142 | 1369.2073 | 35.7698 | 0 | 0 | 0 | 22501.3445 | 433.9581 | 22086.9068 |  | 1141.1546 | 3.2618 | 0.50657 | 30.1954 | 4.1301 | 0.58561 | 0.071742 | 3.6327 | 0 | 0 | 2.7462 | 0 | 44.2989 | 45.1301 | 45.1301
US_5A_LO_2022_NG | 5A | LO | NG |  |  | OfficeLarge | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 1197235.1951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756519.1907 | 0 | 0 | 1953754.3858 | 0 | 1953754.3858 |  | 0 | 11732.9049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7413.8881 | 0 | 0 | 19146.793 | 0 | 19146.793 |  | 0 | 1197.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.5192 | 0 | 0 | 1953.7544 | 0 | 1953.7544 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4013 | 1.5173 | 0 | 0 | 3.9186 | 3.9186 | 3.9186
US_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 20866.6668 | 20277.7779 | 9166.6667 | 125580.5566 | 0 | 25136.1113 | 0 | 0 | 0 | 0 | 134177.7789 | 0 | 0 | 335205.5582 | 0 | 335205.5582 |  | 0 | 0 | 2218.1267 | 2155.5278 | 974.4167 | 13349.2132 | 0 | 2671.9686 | 0 | 0 | 0 | 0 | 14263.0979 | 0 | 0 | 35632.3508 | 0 | 35632.3508 |  | 0 | 0 | 71.2173 | 69.2074 | 31.2855 | 428.6025 | 0 | 85.7888 | 0 | 0 | 0 | 0 | 457.9446 | 0 | 0 | 1144.0462 | 0 | 1144.0462 |  | 0 | 2.0511 | 0.92723 | 12.7027 | 2.5426 | 0 | 0 | 2.1107 | 0 | 13.5723 | 0 | 0 | 33.9067 | 33.9067 | 33.9067
US_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 336768.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336768.9009 | 0 | 336768.9009 |  | 0 | 3300.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3300.3352 | 0 | 3300.3352 |  | 0 | 336.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336.7689 | 0 | 336.7689 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.981 | 0 | 0 | 0 | 9.981 | 9.981 | 9.981
US_5A_MA_2022_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 18452.7779 | 15900.0001 | 6333.3334 | 117269.4454 | 0 | 23527.778 | 0 | 0 | 0 | 0 | 123055.5565 | 0 | 0 | 304538.8913 | 17486.9446 | 287051.9467 |  | 0 | 0 | 1961.5303 | 1690.17 | 673.2333 | 12465.742 | 0 | 2501.0028 | 0 | 0 | 0 | 0 | 13080.8057 | 0 | 0 | 32372.4841 | 1858.8622 | 30596.9493 |  | 0 | 0 | 62.9788 | 54.2662 | 21.6155 | 400.237 | 0 | 80.2996 | 0 | 0 | 0 | 0 | 419.9848 | 0 | 0 | 1039.3818 | 59.6824 | 982.3748 |  | 0 | 1.6083 | 0.64063 | 11.862 | 2.3799 | 0 | 0 | 1.8665 | 0 | 12.4473 | 0 | 0 | 29.1152 | 30.8047 | 30.8047
US_5A_MA_2022_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 273312.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273312.5447 | 0 | 273312.5447 |  | 0 | 2678.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2678.4629 | 0 | 2678.4629 |  | 0 | 273.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.3125 | 0 | 273.3125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1003 | 0 | 0 | 0 | 8.1003 | 8.1003 | 8.1003
US_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 64183.3338 | 78475.0006 | 8327.7778 | 312394.4469 | 4741.6667 | 67794.445 | 719.4445 | 0 | 0 | 13305.5557 | 7180.5556 | 12477.7779 | 0 | 569600.0046 | 0 | 569600.0046 |  | 4741.6667 | 0 | 6822.6884 | 8341.8926 | 885.2428 | 33207.5297 | 504.0392 | 7206.5495 | 76.4769 | 0 | 0 | 1414.3806 | 763.2931 | 1326.3878 | 0 | 60548.4805 | 0 | 60548.6281 |  | 504.0392 | 0 | 219.0557 | 267.8327 | 28.4224 | 1066.1926 | 16.1832 | 231.3803 | 2.4554 | 0 | 0 | 45.4114 | 24.507 | 42.5863 | 0 | 1944.0272 | 0 | 1944.0319 |  | 16.1832 | 3.6214 | 0.3843 | 14.6348 | 3.1285 | 0.0332 | 0.61401 | 2.9619 | 0 | 0.33136 | 0 | 0.57581 | 26.2853 | 26.2852 | 26.2852
US_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 943182.2943 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 147338.1713 | 0 | 0 | 1432710.8804 | 0 | 1432710.8804 |  | 0 | 9243.1865 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.9141 | 0 | 0 | 14040.5666 | 0 | 14040.5666 |  | 0 | 943.1823 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 147.3382 | 0 | 0 | 1432.7109 | 0 | 1432.7109 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.7528 | 1.9922 | 0 | 0 | 19.3717 | 19.3717 | 19.3717
US_5A_PS_2022_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 59258.3338 | 65497.2227 | 5850 | 312394.4469 | 4738.8889 | 68033.3339 | 1427.7778 | 0 | 0 | 12419.4445 | 7180.5556 | 12480.5557 | 0 | 549280.5599 | 52546.9449 | 496733.6151 |  | 4738.8889 | 0 | 6299.1609 | 6962.3548 | 621.855 | 33207.5297 | 503.7439 | 7231.9434 | 151.7728 | 0 | 0 | 1320.187 | 763.2931 | 1326.6831 | 0 | 58388.5235 | 5585.7402 | 53054.1828 |  | 503.7439 | 0 | 202.2469 | 223.54 | 19.9659 | 1066.1926 | 16.1737 | 232.1957 | 4.873 | 0 | 0 | 42.3872 | 24.507 | 42.5957 | 0 | 1874.6775 | 179.3411 | 1703.4081 |  | 16.1737 | 3.0225 | 0.26996 | 14.6347 | 3.1395 | 0.065887 | 0.57312 | 2.7346 | 0 | 0.33136 | 0 | 0.57594 | 23.0318 | 25.3475 | 25.3475
US_5A_PS_2022_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 746841.9779 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 147319.215 | 0 | 0 | 1236351.6077 | 0 | 1236351.6077 |  | 0 | 7319.0514 | 0 | 0 | 0 | 3353.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.7283 | 0 | 0 | 12116.2458 | 0 | 12116.2458 |  | 0 | 746.842 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 147.3192 | 0 | 0 | 1236.3516 | 0 | 1236.3516 |  | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.0981 | 1.9919 | 0 | 0 | 16.7167 | 16.7167 | 16.7167
US_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 20330.5557 | 64719.445 | 12133.3334 | 53972.2227 | 0 | 40625.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191780.5571 | 0 | 191780.5571 |  | 0 | 0 | 2161.1381 | 6879.677 | 1289.7733 | 5737.2473 | 0 | 4318.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20386.2732 | 0 | 20386.3618 |  | 0 | 0 | 69.3876 | 220.8855 | 41.4107 | 184.2055 | 0 | 138.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.5411 | 0 | 654.5439 |  | 0 | 8.9456 | 1.6771 | 7.4601 | 5.6153 | 0 | 0 | 2.8101 | 0 | 0 | 0 | 0 | 26.5083 | 26.5082 | 26.5082
US_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 642231.4023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91710.7845 | 0 | 0 | 733942.1869 | 0 | 733942.1869 |  | 0 | 6293.8677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 898.7657 | 0 | 0 | 7192.6334 | 0 | 7192.6334 |  | 0 | 642.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7108 | 0 | 0 | 733.9422 | 0 | 733.9422 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0097 | 3.7142 | 0 | 0 | 29.7239 | 29.7239 | 29.7239
US_5A_RS_2022_EL | 5A | RS | EL |  |  | RetailStandalone | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 0 | 17355.5557 | 48336.1115 | 8247.2223 | 53972.2227 | 0 | 35841.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163752.7791 | 17540.8335 | 146211.9456 |  | 0 | 0 | 1844.8956 | 5138.1287 | 876.6797 | 5737.2473 | 0 | 3809.9692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17406.9204 | 1864.5906 | 15626.1297 |  | 0 | 0 | 59.234 | 164.9697 | 28.1475 | 184.2055 | 0 | 122.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.8832 | 59.8663 | 501.7074 |  | 0 | 6.6811 | 1.1399 | 7.4601 | 4.9541 | 0 | 0 | 2.3989 | 0 | 0 | 0 | 0 | 20.3186 | 22.6342 | 22.6342
US_5A_RS_2022_NG | 5A | RS | NG |  |  | RetailStandalone | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 485813.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91701.3064 | 0 | 0 | 577514.4494 | 0 | 577514.4494 |  | 0 | 4760.9688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 898.6728 | 0 | 0 | 5659.6416 | 0 | 5659.6416 |  | 0 | 485.8131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7013 | 0 | 0 | 577.5144 | 0 | 577.5144 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6749 | 3.7138 | 0 | 0 | 23.3887 | 23.3887 | 23.3887
US_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 59441.6671 | 55194.4449 | 48708.3337 | 14480.5557 | 122138.8899 | 0 | 67088.8894 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 367125.0029 | 0 | 367125.0029 |  | 0 | 6318.6492 | 5867.1695 | 5177.6959 | 1539.2831 | 12983.364 | 0 | 7131.5489 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 39025.3878 | 0 | 39024.8858 |  | 0 | 202.8726 | 188.3769 | 166.24 | 49.4217 | 416.8562 | 0 | 228.9723 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.9863 | 0 | 1252.9701 |  | 0 | 3.848 | 1.144 | 9.649 | 5.3 | 0.0057056 | 0 | 4.3604 | 4.6959 | 0 | 0 | 0 | 29.0026 | 29.003 | 29.003
US_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 107217.0726 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 980403.0726 | 0 | 0 | 1487115.5831 | 0 | 1487115.5831 |  | 0 | 1050.7273 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 9607.9501 | 0 | 0 | 14573.7327 | 0 | 14573.7327 |  | 0 | 107.2171 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 980.4031 | 0 | 0 | 1487.1156 | 0 | 1487.1156 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.4818 | 22.6935 | 0 | 0 | 34.4224 | 34.4224 | 34.4224
US_5A_SH_2022_EL | 5A | SH | EL |  |  | HotelSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 54716.6671 | 47647.2226 | 43947.2226 | 10300.0001 | 105516.6675 | 0 | 61594.4449 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 323794.447 | 23386.3891 | 300408.058 |  | 0 | 5816.3817 | 5064.8998 | 4671.5898 | 1094.89 | 11216.4218 | 0 | 6547.4895 | 7.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 34419.3497 | 2485.9732 | 32044.9325 |  | 0 | 186.7463 | 162.6185 | 149.9905 | 35.1536 | 360.1251 | 0 | 210.2199 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.1004 | 79.817 | 1028.8651 |  | 0 | 3.4718 | 0.8137 | 8.3358 | 4.866 | 0.0057056 | 0 | 3.7641 | 4.3226 | 0 | 0 | 0 | 23.8152 | 25.5798 | 25.5798
US_5A_SH_2022_NG | 5A | SH | NG |  |  | HotelSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 35600.011 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 830581.6204 | 0 | 0 | 1265677.0694 | 0 | 1265677.0694 |  | 0 | 348.8801 | 0 | 0 | 0 | 3915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 8139.6999 | 0 | 0 | 12403.6353 | 0 | 12403.6353 |  | 0 | 35.6 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 830.5816 | 0 | 0 | 1265.6771 | 0 | 1265.6771 |  | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.82404 | 19.2255 | 0 | 0 | 29.2967 | 29.2967 | 29.2967
US_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 5533.3334 | 2558.3334 | 7336.1112 | 2763.8889 | 13416.6668 | 0 | 4941.6667 | 0 | 0 | 0 | 0 | 6969.4445 | 0 | 0 | 43519.4448 | 0 | 43519.4448 |  | 0 | 588.1933 | 271.9508 | 779.8286 | 293.8014 | 1426.1917 | 0 | 525.2992 | 0 | 0 | 0 | 0 | 740.852 | 0 | 0 | 4626.117 | 0 | 4625.615 |  | 0 | 18.8851 | 8.7315 | 25.0379 | 9.4331 | 45.7907 | 0 | 16.8658 | 0 | 0 | 0 | 0 | 23.7865 | 0 | 0 | 148.5305 | 0 | 148.5144 |  | 0 | 4.5507 | 1.7145 | 8.3225 | 3.0654 | 0 | 0 | 1.587 | 3.4324 | 4.3232 | 0 | 0 | 26.9928 | 26.9957 | 26.9957
US_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 13155.7016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13155.7016 | 0 | 13155.7016 |  | 0 | 128.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.9259 | 0 | 128.9259 |  | 0 | 13.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1557 | 0 | 13.1557 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3911 | 0 | 0 | 0 | 2.3911 | 2.3911 | 2.3911
US_5A_SO_2022_EL | 5A | SO | EL |  |  | OfficeSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Electricity | 4813.8889 | 2219.4445 | 5347.2223 | 1938.8889 | 13416.6668 | 0 | 4625 | 0 | 0 | 0 | 0 | 6969.4445 | 0 | 0 | 39330.5559 | 651.1111 | 38679.4448 |  | 0 | 511.7164 | 235.9269 | 568.4097 | 206.1039 | 1426.1917 | 0 | 491.6375 | 0 | 0 | 0 | 0 | 740.852 | 0 | 0 | 4180.8381 | 69.2131 | 4115.0502 |  | 0 | 16.4297 | 7.5749 | 18.2499 | 6.6174 | 45.7907 | 0 | 15.785 | 0 | 0 | 0 | 0 | 23.7865 | 0 | 0 | 134.234 | 2.2222 | 132.1217 |  | 0 | 3.317 | 1.2027 | 8.3225 | 2.869 | 0 | 0 | 1.3768 | 2.9861 | 4.3232 | 0 | 0 | 24.0134 | 24.3973 | 24.3973
US_5A_SO_2022_NG | 5A | SO | NG |  |  | OfficeSmall | STD2022 | Buffalo | Zone5A | Zone5A(Buffalo) |  |  | US | 0.1063 | 0.98 |  |  |  | Natural Gas | 11440.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11440.1526 | 0 | 11440.1526 |  | 0 | 112.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1135 | 0 | 112.1135 |  | 0 | 11.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4402 | 0 | 11.4402 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0793 | 0 | 0 | 0 | 2.0793 | 2.0793 | 2.0793
AK_5C_LO_2016_EL | 5C | LO | EL |  |  | OfficeLarge | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 212932.6791 | 894537.3149 | 99845.0152 | 4077910.5986 | 543465.4145 | 564515.8357 | 42503.7345 | 63623.6199 | 403350.6324 | 0 | 0 | 0 | 0 | 6902684.8449 | 0 | 6902680.6771 | 4.1679 | 543469.5824 | 0 | 42331.0166 | 177834.0182 | 19849.189 | 810688.627 | 108040.9244 | 112225.7481 | 8449.7424 | 12648.3756 | 80186.1057 | 0 | 0 | 0 | 0 | 1372253.7472 | 0 | 1372252.9186 | 0.82857 | 108041.753 | 0 | 726.5263 | 3052.1613 | 340.6712 | 13913.831 | 1854.304 | 1926.128 | 145.0227 | 217.0838 | 1376.2324 | 0 | 0 | 0 | 0 | 23551.9607 | 0 | 23551.9465 | 0.014221 | 1854.3182 | 6.1216 | 0.68327 | 27.9065 | 3.8632 | 0.29087 | 0 | 1.4572 | 0 | 0 | 2.7603 | 0 | 47.2373 | 47.2373 | 2.8522e-05
AK_5C_LO_2016_NG | 5C | LO | NG |  |  | OfficeLarge | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 2939152.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617720.8516 | 0 | 0 | 3556873.3062 | 0 | 3556873.3062 | 0 | 0 | 29447.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6188.9452 | 0 | 0 | 35636.3137 | 0 | 35636.3137 | 0 | 0 | 2939.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.7209 | 0 | 0 | 3556.8733 | 0 | 3556.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.895 | 1.2389 | 0 | 0 | 7.1339 | 7.1339 | 0
AK_5C_LO_2019_EL | 5C | LO | EL |  |  | OfficeLarge | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 198122.9187 | 726506.2733 | 99845.0152 | 4077910.5986 | 543390.3932 | 531214.714 | 41986.9211 | 56549.3891 | 403061.6615 | 0 | 0 | 0 | 0 | 6678587.8849 | 0 | 6678584.2727 | 3.6121 | 543394.0054 | 0 | 39386.8362 | 144429.4471 | 19849.189 | 810688.627 | 108026.0102 | 105605.4852 | 8346.9999 | 11242.0186 | 80128.6583 | 0 | 0 | 0 | 0 | 1327703.2715 | 0 | 1327702.5534 | 0.71809 | 108026.7283 | 0 | 675.9954 | 2478.8394 | 340.6712 | 13913.831 | 1854.048 | 1812.5046 | 143.2594 | 192.9465 | 1375.2464 | 0 | 0 | 0 | 0 | 22787.3419 | 0 | 22787.3295 | 0.012325 | 1854.0603 | 4.9717 | 0.68327 | 27.9065 | 3.6353 | 0.28733 | 0 | 1.3558 | 0 | 0 | 2.7583 | 0 | 45.7037 | 45.7038 | 2.4719e-05
AK_5C_LO_2019_NG | 5C | LO | NG |  |  | OfficeLarge | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 4325041.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617692.4171 | 0 | 0 | 4942733.5864 | 0 | 4942733.5864 | 0 | 0 | 43332.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6188.6603 | 0 | 0 | 49521.2478 | 0 | 49521.2478 | 0 | 0 | 4325.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.6924 | 0 | 0 | 4942.7336 | 0 | 4942.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6746 | 1.2389 | 0 | 0 | 9.9135 | 9.9135 | 0
AK_5C_MA_2016_EL | 5C | MA | EL |  |  | ApartmentMidRise | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 5426.5407 | 28374.723 | 7182.5949 | 142004.2074 | 0 | 19283.2528 | 0 | 0 | 0 | 0 | 123949.0811 | 0 | 0 | 326220.3999 | 0 | 326222.3449 | -1.945 | -1.945 | 0 | 1078.7963 | 5640.8949 | 1427.8999 | 28230.4364 | 0 | 3833.5107 | 0 | 0 | 0 | 0 | 24641.0773 | 0 | 0 | 64852.6155 | 0 | 64853.0022 | -0.38667 | -0.38667 | 0 | 18.5154 | 96.8146 | 24.507 | 484.5184 | 0 | 65.7945 | 0 | 0 | 0 | 0 | 422.9143 | 0 | 0 | 1113.064 | 0 | 1113.0706 | -0.0066363 | -0.0066363 | 2.8693 | 0.72633 | 14.3599 | 1.95 | 0 | 0 | 0.54875 | 0 | 12.5341 | 0 | 0 | 32.9887 | 32.9885 | -0.00019668
AK_5C_MA_2016_NG | 5C | MA | NG |  |  | ApartmentMidRise | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 448383.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448383.845 | 0 | 448383.845 | 0 | 0 | 4492.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4492.3577 | 0 | 4492.3577 | 0 | 0 | 448.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448.3838 | 0 | 448.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.289 | 0 | 0 | 0 | 13.289 | 13.289 | 0
AK_5C_MA_2019_EL | 5C | MA | EL |  |  | ApartmentMidRise | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 9202.6129 | 23181.5818 | 7182.5949 | 142004.2074 | 0 | 17077.0708 | 0 | 0 | 0 | 0 | 123724.0172 | 0 | 0 | 322372.0851 | 0 | 322374.0301 | -1.945 | -1.945 | 0 | 1829.4794 | 4608.4985 | 1427.8999 | 28230.4364 | 0 | 3394.9217 | 0 | 0 | 0 | 0 | 24596.3346 | 0 | 0 | 64087.5705 | 0 | 64087.9572 | -0.38667 | -0.38667 | 0 | 31.3993 | 79.0956 | 24.507 | 484.5184 | 0 | 58.267 | 0 | 0 | 0 | 0 | 422.1463 | 0 | 0 | 1099.9336 | 0 | 1099.9402 | -0.0066363 | -0.0066363 | 2.3442 | 0.72633 | 14.3599 | 1.7269 | 0 | 0 | 0.9306 | 0 | 12.5114 | 0 | 0 | 32.5995 | 32.5993 | -0.00019668
AK_5C_MA_2019_NG | 5C | MA | NG |  |  | ApartmentMidRise | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 172606.9757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172606.9757 | 0 | 172606.9757 | 0 | 0 | 1729.3493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1729.3493 | 0 | 1729.3493 | 0 | 0 | 172.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.607 | 0 | 172.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1156 | 0 | 0 | 0 | 5.1156 | 5.1156 | 0
AK_5C_PS_2016_EL | 5C | PS | EL |  |  | SchoolPrimary | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 17752.2625 | 104107.3365 | 7290.959 | 317887.4784 | 4818.0346 | 91742.7147 | 1511.5403 | 0 | 0 | 15915.63 | 7179.8163 | 17638.3413 | 0 | 585844.1136 | 0 | 585845.5029 | -1.3893 | 4816.6453 | 0 | 3529.1498 | 20696.5385 | 1449.4426 | 63196.0307 | 957.8253 | 18238.4517 | 300.4942 | 0 | 0 | 3164.0272 | 1427.3475 | 3506.5023 | 0 | 116465.8098 | 0 | 116466.086 | -0.27619 | 957.5491 | 0 | 60.5707 | 355.2142 | 24.8768 | 1084.6321 | 16.4391 | 313.0261 | 5.1574 | 0 | 0 | 54.3041 | 24.4975 | 60.182 | 0 | 1998.9001 | 0 | 1998.9049 | -0.0047402 | 16.4344 | 4.8029 | 0.33636 | 14.6653 | 4.2324 | 0.069733 | 0.73425 | 0.81898 | 0 | 0.33123 | 0 | 0.81372 | 27.0272 | 27.0271 | -6.4093e-05
AK_5C_PS_2016_NG | 5C | PS | NG |  |  | SchoolPrimary | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 986838.7508 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127794.1823 | 0 | 0 | 1456823.348 | 0 | 1456823.348 | 0 | 0 | 9887.1374 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.3699 | 0 | 0 | 14595.9131 | 0 | 14595.9131 | 0 | 0 | 986.8388 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.7942 | 0 | 0 | 1456.8233 | 0 | 1456.8233 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.3431 | 1.7279 | 0 | 0 | 19.6977 | 19.6977 | 0
AK_5C_PS_2019_EL | 5C | PS | EL |  |  | SchoolPrimary | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 16543.586 | 84729.6124 | 7290.959 | 312483.1662 | 4745.7919 | 81914.9244 | 1303.1478 | 0 | 0 | 20439.1365 | 7179.8163 | 12495.2144 | 0 | 549125.3549 | 0 | 549124.2434 | 1.1114 | 4746.9033 | 0 | 3288.8649 | 16844.2469 | 1449.4426 | 62121.6534 | 943.4634 | 16284.687 | 259.0658 | 0 | 0 | 4063.3003 | 1427.3475 | 2484.0486 | 0 | 109166.1205 | 0 | 109165.8996 | 0.22095 | 943.6844 | 0 | 56.4467 | 289.0974 | 24.8768 | 1066.1926 | 16.1926 | 279.4937 | 4.4463 | 0 | 0 | 69.7383 | 24.4975 | 42.6337 | 0 | 1873.6157 | 0 | 1873.6119 | 0.0037922 | 16.1964 | 3.9089 | 0.33636 | 14.416 | 3.779 | 0.060119 | 0.94293 | 0.76322 | 0 | 0.33123 | 0 | 0.57645 | 25.3331 | 25.3332 | 5.1274e-05
AK_5C_PS_2019_NG | 5C | PS | NG |  |  | SchoolPrimary | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 920368.3362 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127405.5773 | 0 | 0 | 1389964.3283 | 0 | 1389964.3283 | 0 | 0 | 9221.1704 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1276.4765 | 0 | 0 | 13926.0526 | 0 | 13926.0526 | 0 | 0 | 920.3683 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.4056 | 0 | 0 | 1389.9643 | 0 | 1389.9643 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.4443 | 1.7227 | 0 | 0 | 18.7937 | 18.7937 | 0
AK_5C_RS_2016_EL | 5C | RS | EL |  |  | RetailStandalone | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 2978.6235 | 87391.4793 | 10944.7742 | 53987.5506 | 0 | 42056.3853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197358.8129 | 0 | 197357.1457 | 1.6671 | 1.6671 | 0 | 592.1503 | 17373.4261 | 2175.8211 | 10732.7251 | 0 | 8360.8094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39234.932 | 0 | 39234.6006 | 0.33143 | 0.33143 | 0 | 10.1631 | 298.1797 | 37.3436 | 184.2055 | 0 | 143.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 673.3883 | 0 | 673.3826 | 0.0056883 | 0.0056883 | 12.076 | 1.5124 | 7.4601 | 5.8115 | 0 | 0 | 0.41159 | 0 | 0 | 0 | 0 | 27.2713 | 27.2715 | 0.00023037
AK_5C_RS_2016_NG | 5C | RS | NG |  |  | RetailStandalone | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 634819.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93540.0716 | 0 | 0 | 728359.544 | 0 | 728359.544 | 0 | 0 | 6360.2563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937.178 | 0 | 0 | 7297.4343 | 0 | 7297.4343 | 0 | 0 | 634.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5401 | 0 | 0 | 728.3595 | 0 | 728.3595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.7095 | 3.7883 | 0 | 0 | 29.4978 | 29.4978 | 0
AK_5C_RS_2019_EL | 5C | RS | EL |  |  | RetailStandalone | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 2320.1032 | 69869.8378 | 10944.7742 | 53987.5506 | 0 | 43837.4465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180959.7123 | 0 | 180958.6009 | 1.1114 | 1.1114 | 0 | 461.2365 | 13890.1238 | 2175.8211 | 10732.7251 | 0 | 8714.8844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35974.7908 | 0 | 35974.5699 | 0.22095 | 0.22095 | 0 | 7.9162 | 238.3959 | 37.3436 | 184.2055 | 0 | 149.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.4345 | 0 | 617.4307 | 0.0037922 | 0.0037922 | 9.6548 | 1.5124 | 7.4601 | 6.0576 | 0 | 0 | 0.3206 | 0 | 0 | 0 | 0 | 25.0053 | 25.0054 | 0.00015358
AK_5C_RS_2019_NG | 5C | RS | NG |  |  | RetailStandalone | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 669888.7059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93559.0279 | 0 | 0 | 763447.7338 | 0 | 763447.7338 | 0 | 0 | 6711.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937.3679 | 0 | 0 | 7648.9828 | 0 | 7648.9828 | 0 | 0 | 669.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.559 | 0 | 0 | 763.4477 | 0 | 763.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1298 | 3.789 | 0 | 0 | 30.9188 | 30.9188 | 0
AK_5C_SH_2016_EL | 5C | SH | EL |  |  | HotelSmall | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 37585.6715 | 36860.4656 | 80408.9412 | 12267.3719 | 154949.5496 | 0 | 54218.1717 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 376362.4143 | 0 | 376359.6357 | 2.7786 | 2.7786 | 7472.0315 | 7327.8606 | 15985.2975 | 2438.7535 | 30803.9705 | 0 | 10778.5725 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 74820.848 | 0 | 74820.2956 | 0.55238 | 0.55238 | 128.2423 | 125.7679 | 274.3553 | 41.8563 | 528.6879 | 0 | 184.9924 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.1486 | 0 | 1284.1391 | 0.0094805 | 0.0094805 | 6.3505 | 0.96885 | 12.2376 | 4.282 | 0.0057056 | 0 | 2.9112 | 2.9684 | 0 | 0 | 0 | 29.7241 | 29.7243 | 0.00021945
AK_5C_SH_2016_NG | 5C | SH | NG |  |  | HotelSmall | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 87436.1293 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649804.4611 | 0 | 0 | 1136736.0284 | 0 | 1136736.0284 | 0 | 0 | 876.0226 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6510.3909 | 0 | 0 | 11388.9583 | 0 | 11388.9583 | 0 | 0 | 87.4361 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.8045 | 0 | 0 | 1136.736 | 0 | 1136.736 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.0239 | 15.0411 | 0 | 0 | 26.3121 | 26.3121 | 0
AK_5C_SH_2019_EL | 5C | SH | EL |  |  | HotelSmall | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 43456.7829 | 33426.1572 | 51609.0976 | 12267.3719 | 154949.5496 | 0 | 51506.2906 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 347287.4925 | 0 | 347289.4375 | -1.945 | -1.945 | 8639.2084 | 6645.12 | 10259.8886 | 2438.7535 | 30803.9705 | 0 | 10239.4506 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 69040.7535 | 0 | 69041.1402 | -0.38667 | -0.38667 | 148.2745 | 114.05 | 176.0902 | 41.8563 | 528.6879 | 0 | 175.7395 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.9449 | 0 | 1184.9516 | -0.0066363 | -0.0066363 | 4.076 | 0.96885 | 12.2376 | 4.0679 | 0.0057056 | 0 | 2.6399 | 3.4321 | 0 | 0 | 0 | 27.4282 | 27.428 | -0.00015361
AK_5C_SH_2019_NG | 5C | SH | NG |  |  | HotelSmall | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 86791.6137 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649851.852 | 0 | 0 | 1136138.9036 | 0 | 1136138.9036 | 0 | 0 | 869.5652 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6510.8657 | 0 | 0 | 11382.9757 | 0 | 11382.9757 | 0 | 0 | 86.7916 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.8519 | 0 | 0 | 1136.1389 | 0 | 1136.1389 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.009 | 15.0422 | 0 | 0 | 26.2983 | 26.2983 | 0
AK_5C_SO_2016_EL | 5C | SO | EL |  |  | OfficeSmall | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 5070.8842 | 730.763 | 9063.6845 | 1639.3543 | 13417.6985 | 0 | 4590.1922 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39516.7754 | 0 | 39515.1082 | 1.6671 | 1.6671 | 1008.0918 | 145.2757 | 1801.8605 | 325.9036 | 2667.4385 | 0 | 912.5302 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 7855.9349 | 0 | 7855.6035 | 0.33143 | 0.33143 | 17.3019 | 2.4934 | 30.9253 | 5.5935 | 45.7812 | 0 | 15.6617 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.8312 | 0 | 134.8255 | 0.0056883 | 0.0056883 | 5.6207 | 1.0166 | 8.3208 | 2.8466 | 0 | 0 | 0.45317 | 3.1446 | 3.1033 | 0 | 0 | 24.5048 | 24.5059 | 0.0010339
AK_5C_SO_2016_NG | 5C | SO | NG |  |  | OfficeSmall | STD2016 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 10463.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10463.901 | 0 | 10463.901 | 0 | 0 | 104.8378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8378 | 0 | 104.8378 | 0 | 0 | 10.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4639 | 0 | 10.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9018 | 0 | 0 | 0 | 1.9018 | 1.9018 | 0
AK_5C_SO_2019_EL | 5C | SO | EL |  |  | OfficeSmall | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 5112.5627 | 633.5132 | 7293.7375 | 1639.3543 | 13417.6985 | 0 | 4201.1928 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37302.2577 | 0 | 37301.4241 | 0.83357 | 0.83357 | 1016.3775 | 125.9424 | 1449.995 | 325.9036 | 2667.4385 | 0 | 835.1971 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 7415.6888 | 0 | 7415.5231 | 0.16571 | 0.16571 | 17.4441 | 2.1615 | 24.8862 | 5.5935 | 45.7812 | 0 | 14.3345 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 127.2753 | 0 | 127.2725 | 0.0028441 | 0.0028441 | 4.5231 | 1.0166 | 8.3208 | 2.6053 | 0 | 0 | 0.39287 | 3.1705 | 3.1033 | 0 | 0 | 23.132 | 23.1326 | 0.00051693
AK_5C_SO_2019_NG | 5C | SO | NG |  |  | OfficeSmall | STD2019 | AK-KETCHIKAN-AK | Zone5C | Zone5C(AK-KETCHIKAN-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 11525.4562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11525.4562 | 0 | 11525.4562 | 0 | 0 | 115.4735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4735 | 0 | 115.4735 | 0 | 0 | 11.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5255 | 0 | 11.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0948 | 0 | 0 | 0 | 2.0948 | 2.0948 | 0
AK_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 176466.77 | 896204.4549 | 100931.4347 | 4077910.5986 | 543465.4145 | 568728.1428 | 39416.747 | 46796.6201 | 402436.484 | 11775.5656 | 0 | 0 | 0 | 6864132.2322 | 0 | 6864126.3972 | 5.835 | 543471.2495 | 0 | 35081.5939 | 178165.4456 | 20065.1692 | 810688.627 | 108040.9244 | 113063.1548 | 7836.0493 | 9303.1681 | 80004.373 | 2340.9824 | 0 | 0 | 0 | 1364589.4878 | 0 | 1364588.3278 | 1.16 | 108042.0844 | 0 | 602.1046 | 3057.8496 | 344.3781 | 13913.831 | 1854.304 | 1940.5004 | 134.4899 | 159.6701 | 1373.1133 | 40.1782 | 0 | 0 | 0 | 23420.4192 | 0 | 23420.3993 | 0.019909 | 1854.3239 | 6.133 | 0.69071 | 27.9065 | 3.892 | 0.26974 | 0.080584 | 1.2076 | 0 | 0 | 2.754 | 0 | 46.9735 | 46.9735 | 3.9931e-05
AK_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1411953.6855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626545.029 | 0 | 0 | 2038498.7145 | 0 | 2038498.7145 | 0 | 0 | 14146.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6277.3546 | 0 | 0 | 20423.7186 | 0 | 20423.7186 | 0 | 0 | 1411.9537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626.545 | 0 | 0 | 2038.4987 | 0 | 2038.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8319 | 1.2566 | 0 | 0 | 4.0885 | 4.0885 | 0
AK_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 164177.1696 | 728062.2707 | 100931.4347 | 4077910.5986 | 543390.3932 | 542801.3371 | 38591.5127 | 41578.4718 | 402169.7416 | 11867.2583 | 0 | 0 | 0 | 6651480.1883 | 0 | 6651479.0769 | 1.1114 | 543391.5047 | 0 | 32638.4213 | 144738.7794 | 20065.1692 | 810688.627 | 108026.0102 | 107908.9058 | 7671.9927 | 8265.8002 | 79951.3446 | 2359.211 | 0 | 0 | 0 | 1322314.2614 | 0 | 1322314.0405 | 0.22095 | 108026.2311 | 0 | 560.1725 | 2484.1485 | 344.3781 | 13913.831 | 1854.048 | 1852.0382 | 131.6742 | 141.8657 | 1372.2032 | 40.4911 | 0 | 0 | 0 | 22694.8504 | 0 | 22694.8466 | 0.0037922 | 1854.0518 | 4.9824 | 0.69071 | 27.9065 | 3.7146 | 0.26409 | 0.081212 | 1.1235 | 0 | 0 | 2.7522 | 0 | 45.5182 | 45.5182 | 7.6059e-06
AK_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1253317.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626535.5508 | 0 | 0 | 1879853.085 | 0 | 1879853.085 | 0 | 0 | 12556.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6277.2597 | 0 | 0 | 18834.2481 | 0 | 18834.2481 | 0 | 0 | 1253.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626.5356 | 0 | 0 | 1879.8531 | 0 | 1879.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5137 | 1.2566 | 0 | 0 | 3.7704 | 3.7704 | 0
AK_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 12058.9794 | 28374.723 | 7177.0377 | 142004.2074 | 0 | 18505.2541 | 0 | 0 | 0 | 0 | 125393.9358 | 0 | 0 | 333514.1375 | 0 | 333513.8596 | 0.27786 | 0.27786 | 0 | 2397.3251 | 5640.8949 | 1426.7951 | 28230.4364 | 0 | 3678.8445 | 0 | 0 | 0 | 0 | 24928.3144 | 0 | 0 | 66302.6105 | 0 | 66302.5553 | 0.055238 | 0.055238 | 0 | 41.1452 | 96.8146 | 24.4881 | 484.5184 | 0 | 63.1399 | 0 | 0 | 0 | 0 | 427.8441 | 0 | 0 | 1137.9502 | 0 | 1137.9493 | 0.00094805 | 0.00094805 | 2.8693 | 0.72577 | 14.3599 | 1.8713 | 0 | 0 | 1.2194 | 0 | 12.6802 | 0 | 0 | 33.726 | 33.726 | 2.8098e-05
AK_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 165858.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165858.5178 | 0 | 165858.5178 | 0 | 0 | 1661.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1661.7365 | 0 | 1661.7365 | 0 | 0 | 165.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.8585 | 0 | 165.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9156 | 0 | 0 | 0 | 4.9156 | 4.9156 | 0
AK_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 10169.5541 | 23181.5818 | 7177.0377 | 142004.2074 | 0 | 17588.3271 | 0 | 0 | 0 | 0 | 125443.95 | 0 | 0 | 325564.6582 | 0 | 325566.3253 | -1.6671 | -1.6671 | 0 | 2021.7073 | 4608.4985 | 1426.7951 | 28230.4364 | 0 | 3496.5594 | 0 | 0 | 0 | 0 | 24938.2573 | 0 | 0 | 64722.254 | 0 | 64722.5855 | -0.33143 | -0.33143 | 0 | 34.6985 | 79.0956 | 24.4881 | 484.5184 | 0 | 60.0114 | 0 | 0 | 0 | 0 | 428.0148 | 0 | 0 | 1110.8266 | 0 | 1110.8323 | -0.0056883 | -0.0056883 | 2.3442 | 0.72577 | 14.3599 | 1.7786 | 0 | 0 | 1.0284 | 0 | 12.6853 | 0 | 0 | 32.9223 | 32.9222 | -0.00016859
AK_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 191117.8441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191117.8441 | 0 | 191117.8441 | 0 | 0 | 1914.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1914.8097 | 0 | 1914.8097 | 0 | 0 | 191.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.1178 | 0 | 191.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6643 | 0 | 0 | 0 | 5.6643 | 5.6643 | 0
AK_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 15032.0458 | 104454.6573 | 7318.7446 | 317887.4784 | 4820.8132 | 92456.8064 | 1364.2762 | 0 | 0 | 21200.4638 | 7179.8163 | 17652.2341 | 0 | 589367.3361 | 0 | 589367.3361 | 0 | 4820.8132 | 0 | 2988.3707 | 20765.5859 | 1454.9664 | 63196.0307 | 958.3777 | 18380.4131 | 271.2181 | 0 | 0 | 4214.6522 | 1427.3475 | 3509.2641 | 0 | 117166.2264 | 0 | 117166.2264 | 0 | 958.3777 | 0 | 51.2893 | 356.3993 | 24.9716 | 1084.6321 | 16.4486 | 315.4626 | 4.6549 | 0 | 0 | 72.336 | 24.4975 | 60.2294 | 0 | 2010.9214 | 0 | 2010.9214 | 0 | 16.4486 | 4.8189 | 0.33764 | 14.6653 | 4.2654 | 0.062939 | 0.97806 | 0.69348 | 0 | 0.33123 | 0 | 0.81436 | 27.1897 | 27.1897 | 0
AK_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 830411.0133 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 129500.2531 | 0 | 0 | 1302101.6813 | 0 | 1302101.6813 | 0 | 0 | 8319.8879 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.463 | 0 | 0 | 13045.7567 | 0 | 13045.7567 | 0 | 0 | 830.411 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 129.5003 | 0 | 0 | 1302.1017 | 0 | 1302.1017 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.228 | 1.751 | 0 | 0 | 17.6057 | 17.6057 | 0
AK_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 13778.9122 | 85327.0042 | 7318.7446 | 312483.1662 | 4745.7919 | 82078.8598 | 1097.5338 | 0 | 0 | 23056.5463 | 7182.5949 | 12492.4358 | 0 | 549561.5898 | 0 | 549560.7563 | 0.83357 | 4746.6255 | 0 | 2739.2477 | 16963.0084 | 1454.9664 | 62121.6534 | 943.4634 | 16317.2773 | 218.1897 | 0 | 0 | 4583.6414 | 1427.8999 | 2483.4962 | 0 | 109252.8441 | 0 | 109252.6783 | 0.16571 | 943.6291 | 0 | 47.0136 | 291.1357 | 24.9716 | 1066.1926 | 16.1926 | 280.0531 | 3.7448 | 0 | 0 | 78.6689 | 24.507 | 42.6242 | 0 | 1875.1041 | 0 | 1875.1013 | 0.0028441 | 16.1955 | 3.9364 | 0.33764 | 14.416 | 3.7866 | 0.050633 | 1.0637 | 0.63567 | 0 | 0.33136 | 0 | 0.57632 | 25.3533 | 25.3533 | 3.8456e-05
AK_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 816724.5341 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 129149.5608 | 0 | 0 | 1288064.5097 | 0 | 1288064.5097 | 0 | 0 | 8182.7631 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1293.9494 | 0 | 0 | 12905.1183 | 0 | 12905.1183 | 0 | 0 | 816.7245 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 129.1496 | 0 | 0 | 1288.0645 | 0 | 1288.0645 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.0429 | 1.7462 | 0 | 0 | 17.4159 | 17.4159 | 0
AK_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 2325.6603 | 91692.7005 | 10953.1099 | 53987.5506 | 0 | 47066.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206025.1624 | 0 | 206024.0509 | 1.1114 | 1.1114 | 0 | 462.3413 | 18228.5089 | 2177.4782 | 10732.7251 | 0 | 9356.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40957.8023 | 0 | 40957.5813 | 0.22095 | 0.22095 | 0 | 7.9352 | 312.8555 | 37.372 | 184.2055 | 0 | 160.5897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702.9579 | 0 | 702.9541 | 0.0037922 | 0.0037922 | 12.6703 | 1.5135 | 7.4601 | 6.5037 | 0 | 0 | 0.32137 | 0 | 0 | 0 | 0 | 28.4689 | 28.4691 | 0.00015358
AK_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 670438.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94042.4146 | 0 | 0 | 764480.8545 | 0 | 764480.8545 | 0 | 0 | 6717.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 942.211 | 0 | 0 | 7659.3337 | 0 | 7659.3337 | 0 | 0 | 670.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0424 | 0 | 0 | 764.4809 | 0 | 764.4809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1521 | 3.8086 | 0 | 0 | 30.9607 | 30.9607 | 0
AK_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 1806.0683 | 76110.4986 | 10953.1099 | 53987.5506 | 0 | 45179.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188036.7217 | 0 | 188035.8881 | 0.83357 | 0.83357 | 0 | 359.0464 | 15130.7671 | 2177.4782 | 10732.7251 | 0 | 8981.6835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37381.7003 | 0 | 37381.5346 | 0.16571 | 0.16571 | 0 | 6.1623 | 259.689 | 37.372 | 184.2055 | 0 | 154.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641.5813 | 0 | 641.5785 | 0.0028441 | 0.0028441 | 10.5171 | 1.5135 | 7.4601 | 6.243 | 0 | 0 | 0.24957 | 0 | 0 | 0 | 0 | 25.9833 | 25.9834 | 0.00011518
AK_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 707232.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94061.371 | 0 | 0 | 801294.0714 | 0 | 801294.0714 | 0 | 0 | 7085.7644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 942.4009 | 0 | 0 | 8028.1653 | 0 | 8028.1653 | 0 | 0 | 707.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0614 | 0 | 0 | 801.2941 | 0 | 801.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6422 | 3.8094 | 0 | 0 | 32.4516 | 32.4516 | 0
AK_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 42053.6067 | 35793.496 | 80567.3195 | 12259.0362 | 154949.5496 | 0 | 54301.5287 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 379996.7795 | 0 | 379996.7795 | 0 | 0 | 8360.257 | 7115.747 | 16016.7831 | 2437.0964 | 30803.9705 | 0 | 10795.1439 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 75543.3598 | 0 | 75543.3598 | 0 | 0 | 143.4869 | 122.1274 | 274.8957 | 41.8278 | 528.6879 | 0 | 185.2768 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1296.549 | 0 | 1296.549 | 0 | 0 | 6.363 | 0.96819 | 12.2376 | 4.2886 | 0.0057056 | 0 | 2.8269 | 3.3213 | 0 | 0 | 0 | 30.0113 | 30.0113 | 0
AK_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 95691.6164 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 659965.0607 | 0 | 0 | 1155152.115 | 0 | 1155152.115 | 0 | 0 | 958.7343 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6612.1899 | 0 | 0 | 11573.469 | 0 | 11573.469 | 0 | 0 | 95.6916 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 659.9651 | 0 | 0 | 1155.1521 | 0 | 1155.1521 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.215 | 15.2763 | 0 | 0 | 26.7384 | 26.7384 | 0
AK_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 48297.0461 | 32200.8093 | 51792.483 | 12259.0362 | 154949.5496 | 0 | 51525.7406 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 351096.9074 | 0 | 351093.851 | 3.0564 | 3.0564 | 9601.4528 | 6401.5209 | 10296.3456 | 2437.0964 | 30803.9705 | 0 | 10243.3172 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 69798.0652 | 0 | 69797.4576 | 0.60762 | 0.60762 | 164.7895 | 109.8692 | 176.716 | 41.8278 | 528.6879 | 0 | 175.8058 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1197.9426 | 0 | 1197.9322 | 0.010429 | 0.010429 | 4.0905 | 0.96819 | 12.2376 | 4.0694 | 0.0057056 | 0 | 2.5431 | 3.8144 | 0 | 0 | 0 | 27.7286 | 27.7289 | 0.00024139
AK_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 94516.3232 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 660040.886 | 0 | 0 | 1154052.6471 | 0 | 1154052.6471 | 0 | 0 | 946.959 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6612.9496 | 0 | 0 | 11562.4535 | 0 | 11562.4535 | 0 | 0 | 94.5163 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 660.0409 | 0 | 0 | 1154.0526 | 0 | 1154.0526 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.1878 | 15.278 | 0 | 0 | 26.7129 | 26.7129 | 0
AK_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 5871.1114 | 789.1129 | 9085.9131 | 1656.0257 | 13417.6985 | 0 | 4642.9849 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40467.0452 | 0 | 40468.9902 | -1.945 | -1.945 | 1167.1769 | 156.8757 | 1806.2795 | 329.2179 | 2667.4385 | 0 | 923.0254 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 8044.8486 | 0 | 8045.2352 | -0.38667 | -0.38667 | 20.0322 | 2.6925 | 31.0011 | 5.6504 | 45.7812 | 0 | 15.8419 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.0736 | 0 | 138.0802 | -0.0066363 | -0.0066363 | 5.6345 | 1.027 | 8.3208 | 2.8793 | 0 | 0 | 0.48936 | 3.6409 | 3.1033 | 0 | 0 | 25.0964 | 25.0952 | -0.0012062
AK_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 13553.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13553.7848 | 0 | 13553.7848 | 0 | 0 | 135.7954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.7954 | 0 | 135.7954 | 0 | 0 | 13.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5538 | 0 | 13.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4634 | 0 | 0 | 0 | 2.4634 | 2.4634 | 0
AK_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 5885.0042 | 633.5132 | 7332.6375 | 1656.0257 | 13417.6985 | 0 | 4162.2929 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38091.3706 | 0 | 38092.4821 | -1.1114 | -1.1114 | 1169.9388 | 125.9424 | 1457.7283 | 329.2179 | 2667.4385 | 0 | 827.4638 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 7572.5645 | 0 | 7572.7854 | -0.22095 | -0.22095 | 20.0796 | 2.1615 | 25.019 | 5.6504 | 45.7812 | 0 | 14.2017 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 129.9678 | 0 | 129.9715 | -0.0037922 | -0.0037922 | 4.5472 | 1.027 | 8.3208 | 2.5812 | 0 | 0 | 0.39287 | 3.6495 | 3.1033 | 0 | 0 | 23.6226 | 23.6219 | -0.00068924
AK_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | AK-JUNEAU-AK | Zone6A | Zone6A(AK-JUNEAU-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 15402.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15402.0282 | 0 | 15402.0282 | 0 | 0 | 154.3129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.3129 | 0 | 154.3129 | 0 | 0 | 15.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.402 | 0 | 15.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7994 | 0 | 0 | 0 | 2.7994 | 2.7994 | 0
AK_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 183660.4791 | 896510.0972 | 101776.119 | 4077910.5986 | 543465.4145 | 599064.5339 | 49122.2804 | 51584.0905 | 521853.7229 | 13828.9264 | 0 | 0 | 0 | 7038776.2625 | 0 | 7038778.4853 | -2.2229 | 543463.1917 | 0 | 36511.7033 | 178226.2073 | 20233.0925 | 810688.627 | 108040.9244 | 119094.0293 | 9765.5093 | 10254.9172 | 103744.5201 | 2749.1906 | 0 | 0 | 0 | 1399308.721 | 0 | 1399309.1629 | -0.4419 | 108040.4825 | 0 | 626.6496 | 3058.8925 | 347.2601 | 13913.831 | 1854.304 | 2044.0082 | 167.6052 | 176.0049 | 1780.5649 | 47.1843 | 0 | 0 | 0 | 24016.3046 | 0 | 24016.3122 | -0.0075844 | 1854.2964 | 6.1351 | 0.69649 | 27.9065 | 4.0996 | 0.33616 | 0.094636 | 1.2568 | 0 | 0 | 3.5712 | 0 | 48.1687 | 48.1686 | -1.5212e-05
AK_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1854290.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655339.7131 | 0 | 0 | 2509630.1703 | 0 | 2509630.1703 | 0 | 0 | 18578.1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6565.8486 | 0 | 0 | 25143.9847 | 0 | 25143.9847 | 0 | 0 | 1854.2905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.3397 | 0 | 0 | 2509.6302 | 0 | 2509.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7191 | 1.3144 | 0 | 0 | 5.0335 | 5.0335 | 0
AK_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 169953.8097 | 729315.4042 | 101776.119 | 4077910.5986 | 543393.1718 | 562073.4756 | 48019.1894 | 45490.6937 | 521586.9805 | 12873.0994 | 0 | 0 | 0 | 6812392.542 | 0 | 6812392.542 | 0 | 543393.1718 | 0 | 33786.8174 | 144987.9024 | 20233.0925 | 810688.627 | 108026.5626 | 111740.207 | 9546.2149 | 9043.5499 | 103691.4917 | 2559.1722 | 0 | 0 | 0 | 1354303.6374 | 0 | 1354303.6374 | 0 | 108026.5626 | 0 | 579.8824 | 2488.4242 | 347.2601 | 13913.831 | 1854.0575 | 1917.7947 | 163.8415 | 155.2142 | 1779.6548 | 43.923 | 0 | 0 | 0 | 23243.8834 | 0 | 23243.8834 | 0 | 1854.0575 | 4.9909 | 0.69649 | 27.9065 | 3.8465 | 0.32861 | 0.088095 | 1.163 | 0 | 0 | 3.5694 | 0 | 46.6194 | 46.6194 | 0
AK_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1687114.4736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655263.8877 | 0 | 0 | 2342378.3613 | 0 | 2342378.3613 | 0 | 0 | 16903.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6565.0889 | 0 | 0 | 23468.2888 | 0 | 23468.2888 | 0 | 0 | 1687.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.2639 | 0 | 0 | 2342.3784 | 0 | 2342.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3838 | 1.3142 | 0 | 0 | 4.698 | 4.698 | 0
AK_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 12673.0426 | 28374.723 | 7165.9235 | 142004.2074 | 0 | 20111.2656 | 0 | 0 | 0 | 0 | 130989.9691 | 0 | 0 | 341319.1313 | 0 | 341316.6306 | 2.5007 | 2.5007 | 0 | 2519.4009 | 5640.8949 | 1424.5856 | 28230.4364 | 0 | 3998.1196 | 0 | 0 | 0 | 0 | 26040.8059 | 0 | 0 | 67854.2433 | 0 | 67853.7462 | 0.49714 | 0.49714 | 0 | 43.2404 | 96.8146 | 24.4501 | 484.5184 | 0 | 68.6196 | 0 | 0 | 0 | 0 | 446.9378 | 0 | 0 | 1164.5809 | 0 | 1164.5723 | 0.0085324 | 0.0085324 | 2.8693 | 0.72464 | 14.3599 | 2.0337 | 0 | 0 | 1.2815 | 0 | 13.2461 | 0 | 0 | 34.5151 | 34.5153 | 0.00025288
AK_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 270213.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270213.1827 | 0 | 270213.1827 | 0 | 0 | 2707.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2707.2659 | 0 | 2707.2659 | 0 | 0 | 270.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.2132 | 0 | 270.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0085 | 0 | 0 | 0 | 8.0085 | 8.0085 | 0
AK_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 11672.7586 | 23181.5818 | 7165.9235 | 142004.2074 | 0 | 18560.8254 | 0 | 0 | 0 | 0 | 130973.2977 | 0 | 0 | 333558.5945 | 0 | 333560.2617 | -1.6671 | -1.6671 | 0 | 2320.5444 | 4608.4985 | 1424.5856 | 28230.4364 | 0 | 3689.8921 | 0 | 0 | 0 | 0 | 26037.4916 | 0 | 0 | 66311.4486 | 0 | 66311.78 | -0.33143 | -0.33143 | 0 | 39.8275 | 79.0956 | 24.4501 | 484.5184 | 0 | 63.3295 | 0 | 0 | 0 | 0 | 446.8809 | 0 | 0 | 1138.1019 | 0 | 1138.1076 | -0.0056883 | -0.0056883 | 2.3442 | 0.72464 | 14.3599 | 1.8769 | 0 | 0 | 1.1804 | 0 | 13.2444 | 0 | 0 | 33.7307 | 33.7305 | -0.00016859
AK_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 244802.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244802.2058 | 0 | 244802.2058 | 0 | 0 | 2452.6733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2452.6733 | 0 | 2452.6733 | 0 | 0 | 244.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244.8022 | 0 | 244.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2553 | 0 | 0 | 0 | 7.2553 | 7.2553 | 0
AK_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 14684.7249 | 101856.6974 | 7279.8447 | 317887.4784 | 4818.0346 | 102370.7323 | 155.5997 | 0 | 0 | 21814.527 | 7182.5949 | 17585.5485 | 0 | 595635.7826 | 0 | 595632.7261 | 3.0564 | 4821.0911 | 0 | 2919.3233 | 20249.1115 | 1447.2331 | 63196.0307 | 957.8253 | 20351.3016 | 30.9332 | 0 | 0 | 4336.728 | 1427.8999 | 3496.007 | 0 | 118412.3936 | 0 | 118411.786 | 0.60762 | 958.4329 | 0 | 50.1043 | 347.5351 | 24.8388 | 1084.6321 | 16.4391 | 349.2889 | 0.53091 | 0 | 0 | 74.4312 | 24.507 | 60.0019 | 0 | 2032.3093 | 0 | 2032.2989 | 0.010429 | 16.4496 | 4.699 | 0.33585 | 14.6653 | 4.7227 | 0.0071784 | 1.0064 | 0.67746 | 0 | 0.33136 | 0 | 0.81129 | 27.4787 | 27.4789 | 0.000141
AK_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1191851.5939 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 135319.8502 | 0 | 0 | 1669361.8589 | 0 | 1669361.8589 | 0 | 0 | 11941.1611 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.7696 | 0 | 0 | 16725.3365 | 0 | 16725.3365 | 0 | 0 | 1191.8516 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 135.3199 | 0 | 0 | 1669.3619 | 0 | 1669.3619 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 16.115 | 1.8297 | 0 | 0 | 22.5714 | 22.5714 | 0
AK_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 12956.4564 | 83609.85 | 7279.8447 | 312483.1662 | 4745.7919 | 87169.194 | 1469.8618 | 0 | 0 | 22825.9253 | 7182.5949 | 12445.2002 | 0 | 552167.8854 | 0 | 552166.2182 | 1.6671 | 4747.459 | 0 | 2575.7435 | 16621.6382 | 1447.2331 | 62121.6534 | 943.4634 | 17329.2358 | 292.2085 | 0 | 0 | 4537.7939 | 1427.8999 | 2474.1058 | 0 | 109770.9756 | 0 | 109770.6442 | 0.33143 | 943.7949 | 0 | 44.2074 | 285.2768 | 24.8388 | 1066.1926 | 16.1926 | 297.4213 | 5.0152 | 0 | 0 | 77.8821 | 24.507 | 42.463 | 0 | 1883.9968 | 0 | 1883.9911 | 0.0056883 | 16.1983 | 3.8572 | 0.33585 | 14.416 | 4.0214 | 0.06781 | 1.053 | 0.59773 | 0 | 0.33136 | 0 | 0.57414 | 25.4735 | 25.4735 | 7.6911e-05
AK_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 1130148.6994 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 135016.5487 | 0 | 0 | 1607355.663 | 0 | 1607355.663 | 0 | 0 | 11322.9598 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1352.7308 | 0 | 0 | 16104.0964 | 0 | 16104.0964 | 0 | 0 | 1130.1487 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 135.0165 | 0 | 0 | 1607.3557 | 0 | 1607.3557 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 15.2807 | 1.8256 | 0 | 0 | 21.7331 | 21.7331 | 0
AK_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 5445.9907 | 90900.809 | 10778.0602 | 53987.5506 | 0 | 43476.2329 | 0 | 0 | 0 | 5443.2121 | 0 | 0 | 0 | 210031.8555 | 0 | 210032.6891 | -0.83357 | -0.83357 | 0 | 1082.663 | 18071.0808 | 2142.6784 | 10732.7251 | 0 | 8643.0751 | 0 | 0 | 0 | 1082.1106 | 0 | 0 | 0 | 41754.3329 | 0 | 41754.4986 | -0.16571 | -0.16571 | 0 | 18.5817 | 310.1536 | 36.7747 | 184.2055 | 0 | 148.3409 | 0 | 0 | 0 | 18.5722 | 0 | 0 | 0 | 716.6287 | 0 | 716.6315 | -0.0028441 | -0.0028441 | 12.5609 | 1.4893 | 7.4601 | 6.0077 | 0 | 0.75216 | 0.75254 | 0 | 0 | 0 | 0 | 29.0228 | 29.0227 | -0.00011518
AK_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 467453.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95691.6164 | 0 | 0 | 563145.5418 | 0 | 563145.5418 | 0 | 0 | 4683.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958.7343 | 0 | 0 | 5642.1552 | 0 | 5642.1552 | 0 | 0 | 467.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6916 | 0 | 0 | 563.1455 | 0 | 563.1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9314 | 3.8754 | 0 | 0 | 22.8068 | 22.8068 | 0
AK_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 5040.32 | 75304.7142 | 10778.0602 | 53987.5506 | 0 | 44909.9733 | 0 | 0 | 0 | 5646.0475 | 0 | 0 | 0 | 195666.6658 | 0 | 195665.8322 | 0.83357 | 0.83357 | 0 | 1002.0156 | 14970.5772 | 2142.6784 | 10732.7251 | 0 | 8928.1027 | 0 | 0 | 0 | 1122.4342 | 0 | 0 | 0 | 38898.5332 | 0 | 38898.3674 | 0.16571 | 0.16571 | 0 | 17.1976 | 256.9397 | 36.7747 | 184.2055 | 0 | 153.2328 | 0 | 0 | 0 | 19.2643 | 0 | 0 | 0 | 667.6147 | 0 | 667.6118 | 0.0028441 | 0.0028441 | 10.4058 | 1.4893 | 7.4601 | 6.2058 | 0 | 0.78018 | 0.69648 | 0 | 0 | 0 | 0 | 27.0376 | 27.0377 | 0.00011518
AK_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 487803.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95701.0946 | 0 | 0 | 583504.6536 | 0 | 583504.6536 | 0 | 0 | 4887.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958.8293 | 0 | 0 | 5846.1331 | 0 | 5846.1331 | 0 | 0 | 487.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7011 | 0 | 0 | 583.5047 | 0 | 583.5047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7555 | 3.8758 | 0 | 0 | 23.6313 | 23.6313 | 0
AK_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 62545.536 | 34179.1488 | 80339.4771 | 12239.5862 | 154949.5496 | 0 | 54623.8424 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 398949.3828 | 0 | 398948.8271 | 0.55571 | 0.55571 | 12434.0526 | 6794.8148 | 15971.488 | 2433.2297 | 30803.9705 | 0 | 10859.2199 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 79311.1373 | 0 | 79311.0268 | 0.11048 | 0.11048 | 213.4054 | 116.6193 | 274.1183 | 41.7615 | 528.6879 | 0 | 186.3766 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.2153 | 0 | 1361.2134 | 0.0018961 | 0.0018961 | 6.345 | 0.96666 | 12.2376 | 4.3141 | 0.0057056 | 0 | 2.6994 | 4.9397 | 0 | 0 | 0 | 31.5081 | 31.5082 | 4.3889e-05
AK_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 148456.5955 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 692769.0112 | 0 | 0 | 1240721.0446 | 0 | 1240721.0446 | 0 | 0 | 1487.3866 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6940.8527 | 0 | 0 | 12430.7841 | 0 | 12430.7841 | 0 | 0 | 148.4566 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 692.769 | 0 | 0 | 1240.721 | 0 | 1240.721 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.4363 | 16.0356 | 0 | 0 | 28.7191 | 28.7191 | 0
AK_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 68719.5112 | 30775.4046 | 51773.033 | 12239.5862 | 154949.5496 | 0 | 51689.676 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 370219.0033 | 0 | 370217.8919 | 1.1114 | 1.1114 | 13661.4388 | 6118.1504 | 10292.479 | 2433.2297 | 30803.9705 | 0 | 10275.9076 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 73599.5379 | 0 | 73599.3169 | 0.22095 | 0.22095 | 234.471 | 105.0057 | 176.6496 | 41.7615 | 528.6879 | 0 | 176.3652 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.1872 | 0 | 1263.1834 | 0.0037922 | 0.0037922 | 4.0889 | 0.96666 | 12.2376 | 4.0823 | 0.0057056 | 0 | 2.4306 | 5.4273 | 0 | 0 | 0 | 29.239 | 29.2391 | 8.7778e-05
AK_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 141423.7925 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 692806.9239 | 0 | 0 | 1233726.1542 | 0 | 1233726.1542 | 0 | 0 | 1416.925 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 6941.2326 | 0 | 0 | 12360.7023 | 0 | 12360.7023 | 0 | 0 | 141.4238 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 692.8069 | 0 | 0 | 1233.7262 | 0 | 1233.7262 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.2735 | 16.0365 | 0 | 0 | 28.5572 | 28.5572 | 0
AK_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 7107.5736 | 994.7269 | 9019.2275 | 1681.0328 | 13417.6985 | 0 | 5051.4342 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42275.8921 | 0 | 42274.7806 | 1.1114 | 1.1114 | 1412.9856 | 197.7517 | 1793.0224 | 334.1893 | 2667.4385 | 0 | 1004.2251 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 8404.4473 | 0 | 8404.2264 | 0.22095 | 0.22095 | 24.251 | 3.394 | 30.7736 | 5.7357 | 45.7812 | 0 | 17.2355 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.2453 | 0 | 144.2416 | 0.0037922 | 0.0037922 | 5.5932 | 1.0425 | 8.3208 | 3.1326 | 0 | 0 | 0.61687 | 4.4077 | 3.1033 | 0 | 0 | 26.2162 | 26.2169 | 0.00068924
AK_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 33675.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33675.9423 | 0 | 33675.9423 | 0 | 0 | 337.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337.3993 | 0 | 337.3993 | 0 | 0 | 33.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6759 | 0 | 33.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1207 | 0 | 0 | 0 | 6.1207 | 6.1207 | 0
AK_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 6890.8454 | 775.2201 | 7310.4089 | 1681.0328 | 13417.6985 | 0 | 4401.2496 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39480.654 | 0 | 39479.8204 | 0.83357 | 0.83357 | 1369.9001 | 154.1138 | 1453.3093 | 334.1893 | 2667.4385 | 0 | 874.9684 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 7848.754 | 0 | 7848.5883 | 0.16571 | 0.16571 | 23.5116 | 2.6451 | 24.9431 | 5.7357 | 45.7812 | 0 | 15.0171 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.708 | 0 | 134.7051 | 0.0028441 | 0.0028441 | 4.5335 | 1.0425 | 8.3208 | 2.7294 | 0 | 0 | 0.48074 | 4.2733 | 3.1033 | 0 | 0 | 24.4829 | 24.4835 | 0.00051693
AK_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | AK-ANCHORAGE-AK | Zone7 | Zone7(AK-ANCHORAGE-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 36680.5225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36680.5225 | 0 | 36680.5225 | 0 | 0 | 367.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.5022 | 0 | 367.5022 | 0 | 0 | 36.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.6805 | 0 | 36.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6668 | 0 | 0 | 0 | 6.6668 | 6.6668 | 0
AK_8_LO_2016_EL | 8 | LO | EL |  |  | OfficeLarge | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 261207.4967 | 902131.1376 | 104726.9568 | 4077910.5986 | 543468.1931 | 622548.9795 | 61003.4315 | 74184.9519 | 576399.7654 | 15362.6952 | 0 | 0 | 0 | 7238944.2063 | 0 | 7238944.2063 | 0 | 543468.1931 | 0 | 51928.0503 | 179343.6702 | 20819.719 | 810688.627 | 108041.4768 | 123762.7371 | 12127.4822 | 14747.9684 | 114588.2734 | 3054.1038 | 0 | 0 | 0 | 1439102.1082 | 0 | 1439102.1082 | 0 | 108041.4768 | 0 | 891.24 | 3078.0714 | 357.3284 | 13913.831 | 1854.3135 | 2124.1371 | 208.1437 | 253.1191 | 1966.676 | 52.4175 | 0 | 0 | 0 | 24699.2776 | 0 | 24699.2776 | 0 | 1854.3135 | 6.1736 | 0.71668 | 27.9065 | 4.2603 | 0.41747 | 0.10513 | 1.7875 | 0 | 0 | 3.9445 | 0 | 49.5385 | 49.5385 | 0
AK_8_LO_2016_NG | 8 | LO | NG |  |  | OfficeLarge | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 3601923.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698446.4357 | 0 | 0 | 4300369.4897 | 0 | 4300369.4897 | 0 | 0 | 36087.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6997.7348 | 0 | 0 | 43085.4019 | 0 | 43085.4019 | 0 | 0 | 3601.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698.4464 | 0 | 0 | 4300.3695 | 0 | 4300.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2242 | 1.4008 | 0 | 0 | 8.6251 | 8.6251 | 0
AK_8_LO_2019_EL | 8 | LO | EL |  |  | OfficeLarge | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 240876.7243 | 734225.1316 | 104726.9568 | 4077910.5986 | 543395.9504 | 588833.8513 | 60447.7182 | 65813.1304 | 576119.1302 | 13589.9696 | 0 | 0 | 0 | 7005939.1614 | 0 | 7005935.8271 | 3.3343 | 543399.2847 | 0 | 47886.2928 | 145963.9562 | 20819.719 | 810688.627 | 108027.1149 | 117060.1696 | 12017.0064 | 13083.6503 | 114532.4831 | 2701.686 | 0 | 0 | 0 | 1392780.7053 | 0 | 1392780.0424 | 0.66285 | 108027.7778 | 0 | 821.8714 | 2505.1761 | 357.3284 | 13913.831 | 1854.067 | 2009.1011 | 206.2476 | 224.5544 | 1965.7185 | 46.369 | 0 | 0 | 0 | 23904.2644 | 0 | 23904.253 | 0.011377 | 1854.0784 | 5.0245 | 0.71668 | 27.9065 | 4.0296 | 0.41366 | 0.093001 | 1.6484 | 0 | 0 | 3.9426 | 0 | 47.9439 | 47.9439 | 2.2818e-05
AK_8_LO_2019_NG | 8 | LO | NG |  |  | OfficeLarge | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 3988348.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698351.654 | 0 | 0 | 4686699.7478 | 0 | 4686699.7478 | 0 | 0 | 39959.2596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6996.7852 | 0 | 0 | 46956.0448 | 0 | 46956.0448 | 0 | 0 | 3988.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698.3517 | 0 | 0 | 4686.6997 | 0 | 4686.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9993 | 1.4007 | 0 | 0 | 9.3999 | 9.3999 | 0
AK_8_MA_2016_EL | 8 | MA | EL |  |  | ApartmentMidRise | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 15559.9734 | 28374.723 | 7152.0306 | 142004.2074 | 0 | 23228.8175 | 0 | 0 | 0 | 0 | 139242.3122 | 0 | 0 | 355562.0641 | 0 | 355560.6748 | 1.3893 | 1.3893 | 0 | 3093.3227 | 5640.8949 | 1421.8237 | 28230.4364 | 0 | 4617.8889 | 0 | 0 | 0 | 0 | 27681.3717 | 0 | 0 | 70685.7383 | 0 | 70685.4621 | 0.27619 | 0.27619 | 0 | 53.0906 | 96.8146 | 24.4027 | 484.5184 | 0 | 79.2567 | 0 | 0 | 0 | 0 | 475.0948 | 0 | 0 | 1213.1778 | 0 | 1213.173 | 0.0047402 | 0.0047402 | 2.8693 | 0.72324 | 14.3599 | 2.349 | 0 | 0 | 1.5735 | 0 | 14.0806 | 0 | 0 | 35.9555 | 35.9556 | 0.00014049
AK_8_MA_2016_NG | 8 | MA | NG |  |  | ApartmentMidRise | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 483993.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483993.3342 | 0 | 483993.3342 | 0 | 0 | 4849.1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4849.1292 | 0 | 4849.1292 | 0 | 0 | 483.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.9933 | 0 | 483.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3444 | 0 | 0 | 0 | 14.3444 | 14.3444 | 0
AK_8_MA_2019_EL | 8 | MA | EL |  |  | ApartmentMidRise | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 14473.5538 | 23181.5818 | 7152.0306 | 142004.2074 | 0 | 21442.1991 | 0 | 0 | 0 | 0 | 139222.8622 | 0 | 0 | 347476.435 | 0 | 347477.2686 | -0.83357 | -0.83357 | 0 | 2877.3425 | 4608.4985 | 1421.8237 | 28230.4364 | 0 | 4262.7092 | 0 | 0 | 0 | 0 | 27677.505 | 0 | 0 | 69078.3153 | 0 | 69078.481 | -0.16571 | -0.16571 | 0 | 49.3838 | 79.0956 | 24.4027 | 484.5184 | 0 | 73.1608 | 0 | 0 | 0 | 0 | 475.0284 | 0 | 0 | 1185.5896 | 0 | 1185.5924 | -0.0028441 | -0.0028441 | 2.3442 | 0.72324 | 14.3599 | 2.1683 | 0 | 0 | 1.4636 | 0 | 14.0787 | 0 | 0 | 35.138 | 35.138 | -8.4293e-05
AK_8_MA_2019_NG | 8 | MA | NG |  |  | ApartmentMidRise | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 438896.1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438896.1956 | 0 | 438896.1956 | 0 | 0 | 4397.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4397.301 | 0 | 4397.301 | 0 | 0 | 438.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438.8962 | 0 | 438.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0078 | 0 | 0 | 0 | 13.0078 | 13.0078 | 0
AK_8_PS_2016_EL | 8 | PS | EL |  |  | SchoolPrimary | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 27944.0451 | 103551.6231 | 7396.5445 | 317887.4784 | 4820.8132 | 118886.5326 | 864.1342 | 0 | 0 | 22867.6038 | 7185.3734 | 17463.2916 | 0 | 628867.4401 | 0 | 628864.1058 | 3.3343 | 4824.1475 | 0 | 5555.2762 | 20586.0627 | 1470.433 | 63196.0307 | 958.3777 | 23634.6427 | 171.7899 | 0 | 0 | 4546.0796 | 1428.4522 | 3471.7024 | 0 | 125018.8471 | 0 | 125018.1842 | 0.66285 | 959.0405 | 0 | 95.3451 | 353.3181 | 25.237 | 1084.6321 | 16.4486 | 405.6408 | 2.9484 | 0 | 0 | 78.0243 | 24.5165 | 59.5848 | 0 | 2145.6957 | 0 | 2145.6843 | 0.011377 | 16.46 | 4.7772 | 0.34123 | 14.6653 | 5.4847 | 0.039866 | 1.055 | 1.2892 | 0 | 0.33149 | 0 | 0.80565 | 29.0118 | 29.012 | 0.00015382
AK_8_PS_2016_NG | 8 | PS | NG |  |  | SchoolPrimary | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 2405095.4202 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 143726.9881 | 0 | 0 | 2891012.8231 | 0 | 2891012.8231 | 0 | 0 | 24096.651 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.0007 | 0 | 0 | 28965.0575 | 0 | 28965.0575 | 0 | 0 | 2405.0954 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 143.727 | 0 | 0 | 2891.0128 | 0 | 2891.0128 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 32.5193 | 1.9433 | 0 | 0 | 39.0894 | 39.0894 | 0
AK_8_PS_2019_EL | 8 | PS | EL |  |  | SchoolPrimary | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 25059.8929 | 85438.1469 | 7396.5445 | 312483.1662 | 4745.7919 | 100642.4638 | 758.5487 | 0 | 0 | 22486.9402 | 7185.3734 | 12353.5075 | 0 | 578550.376 | 0 | 578550.376 | 0 | 4745.7919 | 0 | 4981.9067 | 16985.1036 | 1470.433 | 62121.6534 | 943.4634 | 20007.7218 | 150.7995 | 0 | 0 | 4470.4037 | 1428.4522 | 2455.8773 | 0 | 115015.8148 | 0 | 115015.8148 | 0 | 943.4634 | 0 | 85.5044 | 291.515 | 25.237 | 1066.1926 | 16.1926 | 343.3921 | 2.5882 | 0 | 0 | 76.7254 | 24.5165 | 42.1502 | 0 | 1974.0139 | 0 | 1974.0139 | 0 | 16.1926 | 3.9416 | 0.34123 | 14.416 | 4.643 | 0.034995 | 1.0374 | 1.1561 | 0 | 0.33149 | 0 | 0.56991 | 26.6907 | 26.6907 | 0
AK_8_PS_2019_NG | 8 | PS | NG |  |  | SchoolPrimary | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 2278704.0072 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 143508.9901 | 0 | 0 | 2764403.4122 | 0 | 2764403.4122 | 0 | 0 | 22830.3354 | 0 | 0 | 0 | 3428.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 1437.8166 | 0 | 0 | 27696.5578 | 0 | 27696.5578 | 0 | 0 | 2278.704 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 143.509 | 0 | 0 | 2764.4034 | 0 | 2764.4034 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 30.8104 | 1.9404 | 0 | 0 | 37.3775 | 37.3775 | 0
AK_8_RS_2016_EL | 8 | RS | EL |  |  | RetailStandalone | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 9449.9053 | 91156.4371 | 10930.8813 | 53987.5506 | 0 | 51611.8761 | 0 | 0 | 0 | 5262.6053 | 0 | 0 | 0 | 222399.2558 | 0 | 222395.6437 | 3.6121 | 3.6121 | 0 | 1878.6412 | 18121.8997 | 2173.0592 | 10732.7251 | 0 | 10260.441 | 0 | 0 | 0 | 1046.2059 | 0 | 0 | 0 | 44212.9721 | 0 | 44212.254 | 0.71809 | 0.71809 | 0 | 32.2431 | 311.0258 | 37.2962 | 184.2055 | 0 | 176.0997 | 0 | 0 | 0 | 17.956 | 0 | 0 | 0 | 758.8263 | 0 | 758.8139 | 0.012325 | 0.012325 | 12.5962 | 1.5105 | 7.4601 | 7.1319 | 0 | 0.7272 | 1.3058 | 0 | 0 | 0 | 0 | 30.7312 | 30.7317 | 0.00049913
AK_8_RS_2016_NG | 8 | RS | NG |  |  | RetailStandalone | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 809976.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98146.4628 | 0 | 0 | 908122.539 | 0 | 908122.539 | 0 | 0 | 8115.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 983.3294 | 0 | 0 | 9098.4797 | 0 | 9098.4797 | 0 | 0 | 809.9761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1465 | 0 | 0 | 908.1225 | 0 | 908.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.8032 | 3.9748 | 0 | 0 | 36.778 | 36.778 | 0
AK_8_RS_2019_EL | 8 | RS | EL |  |  | RetailStandalone | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 0 | 8316.2501 | 75674.2636 | 10930.8813 | 53987.5506 | 0 | 49161.1803 | 0 | 0 | 0 | 5412.6479 | 0 | 0 | 0 | 203482.7739 | 0 | 203480.551 | 2.2229 | 2.2229 | 0 | 1653.2705 | 15044.0436 | 2173.0592 | 10732.7251 | 0 | 9773.2426 | 0 | 0 | 0 | 1076.0344 | 0 | 0 | 0 | 40452.3754 | 0 | 40451.9335 | 0.4419 | 0.4419 | 0 | 28.375 | 258.2006 | 37.2962 | 184.2055 | 0 | 167.7379 | 0 | 0 | 0 | 18.468 | 0 | 0 | 0 | 694.2832 | 0 | 694.2756 | 0.0075844 | 0.0075844 | 10.4569 | 1.5105 | 7.4601 | 6.7932 | 0 | 0.74793 | 1.1492 | 0 | 0 | 0 | 0 | 28.1174 | 28.1177 | 0.00030716
AK_8_RS_2019_NG | 8 | RS | NG |  |  | RetailStandalone | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 840505.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98165.4191 | 0 | 0 | 938670.6848 | 0 | 938670.6848 | 0 | 0 | 8421.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 983.5193 | 0 | 0 | 9404.5416 | 0 | 9404.5416 | 0 | 0 | 840.5053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1654 | 0 | 0 | 938.6707 | 0 | 938.6707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0396 | 3.9756 | 0 | 0 | 38.0152 | 38.0152 | 0
AK_8_SH_2016_EL | 8 | SH | EL |  |  | HotelSmall | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 108744.7642 | 35521.1965 | 80489.5197 | 12214.5791 | 154949.5496 | 0 | 55935.3259 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 447927.1777 | 0 | 447924.9549 | 2.2229 | 2.2229 | 21618.4591 | 7061.6139 | 16001.3165 | 2428.2583 | 30803.9705 | 0 | 11119.9428 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 89047.9229 | 0 | 89047.481 | 0.4419 | 0.4419 | 371.0371 | 121.1983 | 274.6302 | 41.6761 | 528.6879 | 0 | 190.8513 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1528.3275 | 0 | 1528.3199 | 0.0075844 | 0.0075844 | 6.3569 | 0.96468 | 12.2376 | 4.4177 | 0.0057056 | 0 | 2.8054 | 8.5884 | 0 | 0 | 0 | 35.3761 | 35.3763 | 0.00017556
AK_8_SH_2016_NG | 8 | SH | NG |  |  | HotelSmall | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 239048.9558 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 741439.4203 | 0 | 0 | 1379983.814 | 0 | 1379983.814 | 0 | 0 | 2395.0315 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 7428.4816 | 0 | 0 | 13826.0578 | 0 | 13826.0578 | 0 | 0 | 239.049 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 741.4394 | 0 | 0 | 1379.9838 | 0 | 1379.9838 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 5.5333 | 17.1622 | 0 | 0 | 31.9426 | 31.9426 | 0
AK_8_SH_2019_EL | 8 | SH | EL |  |  | HotelSmall | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 115646.7239 | 32261.9377 | 51909.1828 | 12214.5791 | 154949.5496 | 0 | 52990.0452 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 420044.2611 | 0 | 420045.3725 | -1.1114 | -1.1114 | 22990.5687 | 6413.6732 | 10319.5455 | 2428.2583 | 30803.9705 | 0 | 10534.421 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 83504.7991 | 0 | 83505.0201 | -0.22095 | -0.22095 | 394.5866 | 110.0777 | 177.1141 | 41.6761 | 528.6879 | 0 | 180.802 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.191 | 0 | 1433.1948 | -0.0037922 | -0.0037922 | 4.0997 | 0.96468 | 12.2376 | 4.185 | 0.0057056 | 0 | 2.548 | 9.1335 | 0 | 0 | 0 | 33.1743 | 33.1742 | -8.7778e-05
AK_8_SH_2019_NG | 8 | SH | NG |  |  | HotelSmall | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 224537.8757 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 741505.7675 | 0 | 0 | 1365539.0811 | 0 | 1365539.0811 | 0 | 0 | 2249.645 | 0 | 0 | 0 | 4002.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 7429.1463 | 0 | 0 | 13681.3361 | 0 | 13681.3361 | 0 | 0 | 224.5379 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 741.5058 | 0 | 0 | 1365.5391 | 0 | 1365.5391 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 5.1974 | 17.1637 | 0 | 0 | 31.6082 | 31.6082 | 0
AK_8_SO_2016_EL | 8 | SO | EL |  |  | OfficeSmall | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 4220.6428 | 1650.4686 | 9008.1132 | 1719.9328 | 13417.6985 | 0 | 5807.2044 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40828.2588 | 0 | 40828.2588 | 0 | 0 | 839.0638 | 328.1132 | 1790.8129 | 341.9226 | 2667.4385 | 0 | 1154.4722 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 8116.6579 | 0 | 8116.6579 | 0 | 0 | 14.4008 | 5.6314 | 30.7357 | 5.8684 | 45.7812 | 0 | 19.8142 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.306 | 0 | 139.306 | 0 | 0 | 5.5863 | 1.0666 | 8.3208 | 3.6013 | 0 | 0 | 1.0235 | 2.6174 | 3.1033 | 0 | 0 | 25.3192 | 25.3192 | 0
AK_8_SO_2016_NG | 8 | SO | NG |  |  | OfficeSmall | STD2016 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 90810.3583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90810.3583 | 0 | 90810.3583 | 0 | 0 | 909.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909.829 | 0 | 909.829 | 0 | 0 | 90.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8104 | 0 | 90.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.505 | 0 | 0 | 0 | 16.505 | 16.505 | 0
AK_8_SO_2019_EL | 8 | SO | EL |  |  | OfficeSmall | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Electricity | 4192.8571 | 1369.8334 | 7321.5232 | 1719.9328 | 13417.6985 | 0 | 5134.7912 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38160.8348 | 0 | 38157.5005 | 3.3343 | 3.3343 | 833.54 | 272.3229 | 1455.5188 | 341.9226 | 2667.4385 | 0 | 1020.7965 | 0 | 0 | 0 | 0 | 994.8347 | 0 | 0 | 7586.374 | 0 | 7585.7111 | 0.66285 | 0.66285 | 14.306 | 4.6739 | 24.981 | 5.8684 | 45.7812 | 0 | 17.5199 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.2048 | 0 | 130.1934 | 0.011377 | 0.011377 | 4.5404 | 1.0666 | 8.3208 | 3.1843 | 0 | 0 | 0.84949 | 2.6002 | 3.1033 | 0 | 0 | 23.6629 | 23.665 | 0.0020677
AK_8_SO_2019_NG | 8 | SO | NG |  |  | OfficeSmall | STD2019 | AK-FAIRBANKS-AK | Zone8 | Zone8(AK-FAIRBANKS-AK) |  |  | AK | 0.1988 | 0.010019 |  |  |  | Natural Gas | 92004.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92004.6078 | 0 | 92004.6078 | 0 | 0 | 921.7942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 921.7942 | 0 | 921.7942 | 0 | 0 | 92.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0046 | 0 | 92.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.722 | 0 | 0 | 0 | 16.722 | 16.722 | 0
AL_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 1149304.094 | 882397.757 | 94232.3105 | 4077910.5986 | 543459.8574 | 568678.1286 | 140245.3747 | 431019.5995 | 144174.268 | 15201.5383 | 0 | 0 | 0 | 8046623.5266 | 0 | 8046626.3052 | -2.7786 | 543457.0788 | 0 | 133204.3445 | 102269.9 | 10921.5248 | 472629.8384 | 62986.9975 | 65909.7951 | 16254.4389 | 49955.1716 | 16709.7977 | 1761.8583 | 0 | 0 | 0 | 932603.6667 | 0 | 932603.9888 | -0.32204 | 62986.6754 | 0 | 3921.4256 | 3010.7411 | 321.5206 | 13913.831 | 1854.285 | 1940.3298 | 478.5172 | 1470.6389 | 491.9226 | 51.8676 | 0 | 0 | 0 | 27455.0795 | 0 | 27455.089 | -0.0094805 | 1854.2756 | 6.0385 | 0.64486 | 27.9065 | 3.8916 | 0.95974 | 0.10403 | 7.8651 | 0 | 0 | 0.98663 | 0 | 55.0657 | 55.0657 | -1.9015e-05
AL_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 447000.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472126.6638 | 0 | 0 | 919126.6958 | 0 | 919126.6958 | 0 | 0 | 5245.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5540.4064 | 0 | 0 | 10785.9518 | 0 | 10785.9518 | 0 | 0 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.1267 | 0 | 0 | 919.1267 | 0 | 919.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89653 | 0.94693 | 0 | 0 | 1.8435 | 1.8435 | 0
AL_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 1087303.157 | 717878.8238 | 94232.3105 | 4077910.5986 | 543387.6147 | 554638.0312 | 136560.9953 | 390138.5479 | 144121.4752 | 13459.377 | 0 | 0 | 0 | 7759630.9312 | 0 | 7759630.3754 | 0.55571 | 543388.1704 | 0 | 126018.4359 | 83202.1557 | 10921.5248 | 472629.8384 | 62978.6245 | 64282.5478 | 15827.4194 | 45217.0577 | 16703.679 | 1559.9418 | 0 | 0 | 0 | 899341.2249 | 0 | 899341.1605 | 0.064407 | 62978.6889 | 0 | 3709.8784 | 2449.4025 | 321.5206 | 13913.831 | 1854.0385 | 1892.425 | 465.9461 | 1331.1527 | 491.7425 | 45.9234 | 0 | 0 | 0 | 26475.8607 | 0 | 26475.8588 | 0.0018961 | 1854.0404 | 4.9127 | 0.64486 | 27.9065 | 3.7956 | 0.93453 | 0.092107 | 7.4408 | 0 | 0 | 0.98627 | 0 | 53.1017 | 53.1017 | 3.8029e-06
AL_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 309670.8094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472088.7511 | 0 | 0 | 781759.5606 | 0 | 781759.5606 | 0 | 0 | 3633.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5539.9615 | 0 | 0 | 9173.9484 | 0 | 9173.9484 | 0 | 0 | 309.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.0888 | 0 | 0 | 781.7596 | 0 | 781.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6211 | 0.94685 | 0 | 0 | 1.5679 | 1.5679 | 0
AL_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 52451.0033 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 23776.1951 | 0 | 0 | 0 | 0 | 94935.2878 | 0 | 0 | 348757.3543 | 0 | 348755.1314 | 2.2229 | 2.2229 | 0 | 6079.0713 | 3288.6304 | 836.3272 | 16458.2876 | 0 | 2755.661 | 0 | 0 | 0 | 0 | 11002.9999 | 0 | 0 | 40420.9774 | 0 | 40420.7197 | 0.25763 | 0.25763 | 0 | 178.9628 | 96.8146 | 24.6208 | 484.5184 | 0 | 81.1244 | 0 | 0 | 0 | 0 | 323.9192 | 0 | 0 | 1189.9601 | 0 | 1189.9525 | 0.0075844 | 0.0075844 | 2.8693 | 0.7297 | 14.3599 | 2.4043 | 0 | 0 | 5.304 | 0 | 9.6002 | 0 | 0 | 35.2673 | 35.2675 | 0.00022478
AL_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 49286.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49286.4902 | 0 | 49286.4902 | 0 | 0 | 578.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.377 | 0 | 578.377 | 0 | 0 | 49.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2865 | 0 | 49.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 1.4607 | 1.4607 | 0
AL_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 47908.0467 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 23126.0105 | 0 | 0 | 0 | 0 | 94832.4809 | 0 | 0 | 338268.265 | 0 | 338266.8758 | 1.3893 | 1.3893 | 0 | 5552.5426 | 2686.7453 | 836.3272 | 16458.2876 | 0 | 2680.3046 | 0 | 0 | 0 | 0 | 10991.0845 | 0 | 0 | 39205.2919 | 0 | 39205.1309 | 0.16102 | 0.16102 | 0 | 163.4623 | 79.0956 | 24.6208 | 484.5184 | 0 | 78.9059 | 0 | 0 | 0 | 0 | 323.5684 | 0 | 0 | 1154.1713 | 0 | 1154.1666 | 0.0047402 | 0.0047402 | 2.3442 | 0.7297 | 14.3599 | 2.3386 | 0 | 0 | 4.8446 | 0 | 9.5898 | 0 | 0 | 34.2067 | 34.2068 | 0.00014049
AL_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 13800.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13800.2173 | 0 | 13800.2173 | 0 | 0 | 161.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.9455 | 0 | 161.9455 | 0 | 0 | 13.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8002 | 0 | 13.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0.409 | 0.409 | 0
AL_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 219209.4613 | 101020.3489 | 7085.345 | 317887.4784 | 4818.0346 | 94779.6881 | 252.8496 | 0 | 0 | 22692.5541 | 7179.8163 | 17735.5911 | 0 | 792661.1674 | 0 | 792661.4453 | -0.27786 | 4817.7568 | 0 | 25406.3766 | 11708.2584 | 821.1915 | 36843.1588 | 558.4102 | 10984.9659 | 29.3053 | 0 | 0 | 2630.067 | 832.1407 | 2055.555 | 0 | 91869.4293 | 0 | 91869.4615 | -0.032204 | 558.378 | 0 | 747.9427 | 344.6814 | 24.1752 | 1084.6321 | 16.4391 | 323.3883 | 0.86272 | 0 | 0 | 77.427 | 24.4975 | 60.5138 | 0 | 2704.5599 | 0 | 2704.5609 | -0.00094805 | 16.4382 | 4.6604 | 0.32687 | 14.6653 | 4.3725 | 0.011665 | 1.0469 | 10.1129 | 0 | 0.33123 | 0 | 0.81821 | 36.5684 | 36.5684 | -1.2819e-05
AL_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 142712.8238 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99321.756 | 0 | 0 | 584224.9946 | 0 | 584224.9946 | 0 | 0 | 1674.735 | 0 | 0 | 0 | 4015.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.5408 | 0 | 0 | 6855.8803 | 0 | 6855.8803 | 0 | 0 | 142.7128 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3218 | 0 | 0 | 584.225 | 0 | 584.225 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.9296 | 1.3429 | 0 | 0 | 7.8993 | 7.8993 | 0
AL_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 203466.1025 | 81667.6319 | 7085.345 | 312483.1662 | 4745.7919 | 84929.6692 | 208.3925 | 0 | 0 | 22992.6393 | 7179.8163 | 12542.45 | 0 | 737301.0049 | 0 | 737299.8934 | 1.1114 | 4746.9033 | 0 | 23581.7213 | 9465.2785 | 821.1915 | 36216.799 | 550.0373 | 9843.3487 | 24.1527 | 0 | 0 | 2664.8469 | 832.1407 | 1453.67 | 0 | 85453.1865 | 0 | 85453.0577 | 0.12881 | 550.1661 | 0 | 694.2263 | 278.65 | 24.1752 | 1066.1926 | 16.1926 | 289.78 | 0.71104 | 0 | 0 | 78.4509 | 24.4975 | 42.7948 | 0 | 2515.671 | 0 | 2515.6672 | 0.0037922 | 16.1964 | 3.7676 | 0.32687 | 14.416 | 3.9181 | 0.0096139 | 1.0607 | 9.3866 | 0 | 0.33123 | 0 | 0.57863 | 34.0143 | 34.0144 | 5.1274e-05
AL_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 119917.822 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99075.3236 | 0 | 0 | 561183.5604 | 0 | 561183.5604 | 0 | 0 | 1407.2356 | 0 | 0 | 0 | 4015.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.6489 | 0 | 0 | 6585.4891 | 0 | 6585.4891 | 0 | 0 | 119.9178 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0753 | 0 | 0 | 561.1836 | 0 | 561.1836 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.6214 | 1.3396 | 0 | 0 | 7.5878 | 7.5878 | 0
AL_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 83245.8578 | 83145.8294 | 10708.596 | 53987.5506 | 0 | 36824.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267912.1781 | 0 | 267911.6224 | 0.55571 | 0.55571 | 0 | 9648.1949 | 9636.6016 | 1241.1263 | 6257.1571 | 0 | 4267.9415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31051.0214 | 0 | 31050.957 | 0.064407 | 0.064407 | 0 | 284.0349 | 283.6936 | 36.5377 | 184.2055 | 0 | 125.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.1164 | 0 | 914.1145 | 0.0018961 | 0.0018961 | 11.4893 | 1.4797 | 7.4601 | 5.0885 | 0 | 0 | 11.5031 | 0 | 0 | 0 | 0 | 37.0207 | 37.0207 | 7.679e-05
AL_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 66650.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84753.8069 | 0 | 0 | 151404.3067 | 0 | 151404.3067 | 0 | 0 | 782.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.5859 | 0 | 0 | 1776.7295 | 0 | 1776.7295 | 0 | 0 | 66.6505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7538 | 0 | 0 | 151.4043 | 0 | 151.4043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6993 | 3.4324 | 0 | 0 | 6.1317 | 6.1317 | 0
AL_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 78291.6734 | 65613.0736 | 10708.596 | 53987.5506 | 0 | 34987.7117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243588.6053 | 0 | 243587.7718 | 0.83357 | 0.83357 | 0 | 9074.0049 | 7604.5552 | 1241.1263 | 6257.1571 | 0 | 4055.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28231.9194 | 0 | 28231.8227 | 0.096611 | 0.096611 | 0 | 267.1312 | 223.8718 | 36.5377 | 184.2055 | 0 | 119.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831.1243 | 0 | 831.1215 | 0.0028441 | 0.0028441 | 9.0666 | 1.4797 | 7.4601 | 4.8347 | 0 | 0 | 10.8185 | 0 | 0 | 0 | 0 | 33.6595 | 33.6597 | 0.00011518
AL_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 74090.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84763.285 | 0 | 0 | 158854.1493 | 0 | 158854.1493 | 0 | 0 | 869.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.6971 | 0 | 0 | 1864.1534 | 0 | 1864.1534 | 0 | 0 | 74.0909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7633 | 0 | 0 | 158.8541 | 0 | 158.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0006 | 3.4328 | 0 | 0 | 6.4334 | 6.4334 | 0
AL_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 5637.7118 | 117286.0782 | 80144.9774 | 12322.9432 | 154949.5496 | 0 | 46460.4135 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 416873.9165 | 0 | 416874.1943 | -0.27786 | -0.27786 | 653.4108 | 13593.4565 | 9288.8029 | 1428.2291 | 17958.6528 | 0 | 5384.7619 | 8.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 48315.6869 | 0 | 48315.7191 | -0.032204 | -0.032204 | 19.2359 | 400.1801 | 273.4547 | 42.0459 | 528.6879 | 0 | 158.5229 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1422.3738 | 0 | 1422.3748 | -0.00094805 | -0.00094805 | 6.3297 | 0.97324 | 12.2376 | 3.6693 | 0.0057056 | 0 | 9.263 | 0.44525 | 0 | 0 | 0 | 32.9238 | 32.9238 | -2.1945e-05
AL_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 11961.4521 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 484163.9412 | 0 | 0 | 895620.8312 | 0 | 895620.8312 | 0 | 0 | 140.3676 | 0 | 0 | 0 | 4688.079 | 0 | 0 | 0 | 0 | 0 | 0 | 5681.6639 | 0 | 0 | 10510.1105 | 0 | 10510.1105 | 0 | 0 | 11.9615 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 484.1639 | 0 | 0 | 895.6208 | 0 | 895.6208 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.27687 | 11.207 | 0 | 0 | 20.731 | 20.731 | 0
AL_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 6437.939 | 110937.0534 | 51339.5766 | 12322.9432 | 154949.5496 | 0 | 44234.7816 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380294.0861 | 0 | 380294.0861 | 0 | 0 | 746.1571 | 12857.6045 | 5950.2569 | 1428.2291 | 17958.6528 | 0 | 5126.8112 | 8.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 44076.0846 | 0 | 44076.0846 | 0 | 0 | 21.9662 | 378.5172 | 175.1706 | 42.0459 | 528.6879 | 0 | 150.9291 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.5634 | 0 | 1297.5634 | 0 | 0 | 4.0547 | 0.97324 | 12.2376 | 3.4936 | 0.0057056 | 0 | 8.7616 | 0.50845 | 0 | 0 | 0 | 30.0348 | 30.0348 | 0
AL_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 12795.5311 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 484144.9849 | 0 | 0 | 896435.9539 | 0 | 896435.9539 | 0 | 0 | 150.1556 | 0 | 0 | 0 | 4688.079 | 0 | 0 | 0 | 0 | 0 | 0 | 5681.4414 | 0 | 0 | 10519.6759 | 0 | 10519.6759 | 0 | 0 | 12.7955 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 484.145 | 0 | 0 | 896.436 | 0 | 896.436 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.29618 | 11.2065 | 0 | 0 | 20.7499 | 20.7499 | 0
AL_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 647.406 | 8357.9286 | 9005.3346 | 1561.5545 | 13417.6985 | 0 | 5070.8842 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43065.005 | 0 | 43065.005 | 0 | 0 | 75.0344 | 968.6839 | 1043.7183 | 180.9842 | 1555.1113 | 0 | 587.7155 | 0 | 0 | 0 | 0 | 579.9866 | 0 | 0 | 4991.2341 | 0 | 4991.2341 | 0 | 0 | 2.2089 | 28.5173 | 30.7262 | 5.328 | 45.7812 | 0 | 17.3019 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.9378 | 0 | 146.9378 | 0 | 0 | 5.5846 | 0.96838 | 8.3208 | 3.1446 | 0 | 0 | 5.1831 | 0.40148 | 3.1033 | 0 | 0 | 26.7063 | 26.7063 | 0
AL_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 568.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.6903 | 0 | 568.6903 | 0 | 0 | 6.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6736 | 0 | 6.6736 | 0 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56869 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10336 | 0 | 0 | 0 | 0.10336 | 0.10336 | 0
AL_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 630.7346 | 8005.0506 | 7232.6091 | 1561.5545 | 13417.6985 | 0 | 4640.2064 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40492.0523 | 0 | 40489.2737 | 2.7786 | 2.7786 | 73.1021 | 927.7854 | 838.2594 | 180.9842 | 1555.1113 | 0 | 537.7999 | 0 | 0 | 0 | 0 | 579.9866 | 0 | 0 | 4693.0289 | 0 | 4692.7068 | 0.32204 | 0.32204 | 2.1521 | 27.3132 | 24.6777 | 5.328 | 45.7812 | 0 | 15.8324 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.1589 | 0 | 138.1494 | 0.0094805 | 0.0094805 | 4.4852 | 0.96838 | 8.3208 | 2.8776 | 0 | 0 | 4.9642 | 0.39114 | 3.1033 | 0 | 0 | 25.1089 | 25.1107 | 0.0017231
AL_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | AL-MOBILE-AL | Zone2A | Zone2A(AL-MOBILE-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 559.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559.2121 | 0 | 559.2121 | 0 | 0 | 6.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5624 | 0 | 6.5624 | 0 | 0 | 0.55921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55921 | 0 | 0.55921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10164 | 0 | 0 | 0 | 0.10164 | 0.10164 | 0
AL_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 946821.6041 | 882903.4562 | 94574.0742 | 4077910.5986 | 543459.8574 | 576922.136 | 124113.0166 | 349590.9243 | 238106.4933 | 12589.6856 | 0 | 0 | 0 | 7846991.8462 | 0 | 7846991.8462 | 0 | 543459.8574 | 0 | 109736.6239 | 102328.5106 | 10961.1352 | 472629.8384 | 62986.9975 | 66865.2756 | 14384.6986 | 40517.5881 | 27596.5426 | 1459.1446 | 0 | 0 | 0 | 909466.355 | 0 | 909466.355 | 0 | 62986.9975 | 0 | 3230.5553 | 3012.4666 | 322.6867 | 13913.831 | 1854.285 | 1968.4583 | 423.4736 | 1192.8042 | 812.4194 | 42.956 | 0 | 0 | 0 | 26773.9362 | 0 | 26773.9362 | 0 | 1854.285 | 6.042 | 0.6472 | 27.9065 | 3.9481 | 0.84935 | 0.086155 | 6.4794 | 0 | 0 | 1.6294 | 0 | 53.6995 | 53.6995 | 0
AL_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 457653.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497139.5576 | 0 | 0 | 954793.054 | 0 | 954793.054 | 0 | 0 | 5370.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5833.9327 | 0 | 0 | 11204.4965 | 0 | 11204.4965 | 0 | 0 | 457.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497.1396 | 0 | 0 | 954.7931 | 0 | 954.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9179 | 0.99709 | 0 | 0 | 1.915 | 1.915 | 0
AL_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 884059.3399 | 718281.7159 | 94574.0742 | 4077910.5986 | 543387.6147 | 563165.4523 | 116074.6232 | 314928.3049 | 238031.472 | 12517.4429 | 0 | 0 | 0 | 7562930.6386 | 0 | 7562927.3043 | 3.3343 | 543390.949 | 0 | 102462.4775 | 83248.8509 | 10961.1352 | 472629.8384 | 62978.6245 | 65270.8759 | 13453.0488 | 36500.1905 | 27587.8476 | 1450.7716 | 0 | 0 | 0 | 876543.661 | 0 | 876543.2746 | 0.38644 | 62979.011 | 0 | 3016.4105 | 2450.7772 | 322.6867 | 13913.831 | 1854.0385 | 1921.5205 | 396.0466 | 1074.5354 | 812.1634 | 42.7095 | 0 | 0 | 0 | 25804.7193 | 0 | 25804.708 | 0.011377 | 1854.0499 | 4.9154 | 0.6472 | 27.9065 | 3.8539 | 0.79434 | 0.085661 | 6.0499 | 0 | 0 | 1.6289 | 0 | 51.7556 | 51.7556 | 2.2818e-05
AL_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 230888.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497177.4703 | 0 | 0 | 728065.7207 | 0 | 728065.7207 | 0 | 0 | 2709.4736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5834.3776 | 0 | 0 | 8543.8512 | 0 | 8543.8512 | 0 | 0 | 230.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497.1775 | 0 | 0 | 728.0657 | 0 | 728.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46308 | 0.99717 | 0 | 0 | 1.4603 | 1.4603 | 0
AL_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 42487.0631 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 22514.7258 | 0 | 0 | 0 | 0 | 99967.2721 | 0 | 0 | 342561.1506 | 0 | 342561.1506 | 0 | 0 | 0 | 4924.2506 | 3288.6304 | 836.0051 | 16458.2876 | 0 | 2609.4567 | 0 | 0 | 0 | 0 | 11586.2068 | 0 | 0 | 39702.8374 | 0 | 39702.8374 | 0 | 0 | 0 | 144.9659 | 96.8146 | 24.6113 | 484.5184 | 0 | 76.8202 | 0 | 0 | 0 | 0 | 341.0883 | 0 | 0 | 1168.8186 | 0 | 1168.8186 | 0 | 0 | 2.8693 | 0.72942 | 14.3599 | 2.2768 | 0 | 0 | 4.2964 | 0 | 10.109 | 0 | 0 | 34.6409 | 34.6409 | 0
AL_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 75730.5879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75730.5879 | 0 | 75730.5879 | 0 | 0 | 888.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888.6984 | 0 | 888.6984 | 0 | 0 | 75.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7306 | 0 | 75.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2445 | 0 | 0 | 0 | 2.2445 | 2.2445 | 0
AL_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 40503.1665 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 22039.5909 | 0 | 0 | 0 | 0 | 99822.7866 | 0 | 0 | 334764.4925 | 0 | 334768.1046 | -3.6121 | -3.6121 | 0 | 4694.317 | 2686.7453 | 836.0051 | 16458.2876 | 0 | 2554.3886 | 0 | 0 | 0 | 0 | 11569.461 | 0 | 0 | 38799.2047 | 0 | 38799.6233 | -0.41865 | -0.41865 | 0 | 138.1968 | 79.0956 | 24.6113 | 484.5184 | 0 | 75.1991 | 0 | 0 | 0 | 0 | 340.5953 | 0 | 0 | 1142.2164 | 0 | 1142.2288 | -0.012325 | -0.012325 | 2.3442 | 0.72942 | 14.3599 | 2.2287 | 0 | 0 | 4.0958 | 0 | 10.0944 | 0 | 0 | 33.8528 | 33.8525 | -0.00036527
AL_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 20368.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20368.5899 | 0 | 20368.5899 | 0 | 0 | 239.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.0254 | 0 | 239.0254 | 0 | 0 | 20.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3686 | 0 | 20.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60367 | 0 | 0 | 0 | 0.60367 | 0.60367 | 0
AL_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 173907.7101 | 101364.8911 | 7099.2379 | 317887.4784 | 4818.0346 | 91731.6005 | 372.3279 | 0 | 0 | 24840.3861 | 7179.8163 | 17671.6841 | 0 | 746873.1671 | 0 | 746875.6678 | -2.5007 | 4815.5339 | 0 | 20155.9036 | 11748.1909 | 822.8017 | 36843.1588 | 558.4102 | 10631.6925 | 43.1528 | 0 | 0 | 2879.0008 | 832.1407 | 2048.1482 | 0 | 86562.6001 | 0 | 86562.8899 | -0.28983 | 558.1204 | 0 | 593.3731 | 345.857 | 24.2226 | 1084.6321 | 16.4391 | 312.9882 | 1.2704 | 0 | 0 | 84.7554 | 24.4975 | 60.2958 | 0 | 2548.3312 | 0 | 2548.3398 | -0.0085324 | 16.4306 | 4.6763 | 0.32751 | 14.6653 | 4.2319 | 0.017177 | 1.146 | 8.023 | 0 | 0.33123 | 0 | 0.81526 | 34.4561 | 34.456 | -0.00011537
AL_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 213002.9414 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104610.5755 | 0 | 0 | 659803.9317 | 0 | 659803.9317 | 0 | 0 | 2499.5895 | 0 | 0 | 0 | 4015.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.6051 | 0 | 0 | 7742.7991 | 0 | 7742.7991 | 0 | 0 | 213.0029 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6106 | 0 | 0 | 659.8039 | 0 | 659.8039 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.88 | 1.4144 | 0 | 0 | 8.9212 | 8.9212 | 0
AL_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 160317.7404 | 82034.4027 | 7099.2379 | 312483.1662 | 4745.7919 | 81031.3402 | 269.521 | 0 | 0 | 22767.5754 | 7179.8163 | 12514.6643 | 0 | 690443.2563 | 0 | 690445.2013 | -1.945 | 4743.8469 | 0 | 18580.8261 | 9507.7873 | 822.8017 | 36216.799 | 550.0373 | 9391.5323 | 31.2375 | 0 | 0 | 2638.762 | 832.1407 | 1450.4496 | 0 | 80022.3734 | 0 | 80022.5988 | -0.22543 | 549.8119 | 0 | 547.0041 | 279.9014 | 24.2226 | 1066.1926 | 16.1926 | 276.4789 | 0.91961 | 0 | 0 | 77.683 | 24.4975 | 42.7 | 0 | 2355.7924 | 0 | 2355.799 | -0.0066363 | 16.186 | 3.7845 | 0.32751 | 14.416 | 3.7383 | 0.012434 | 1.0504 | 7.396 | 0 | 0.33123 | 0 | 0.57735 | 31.8528 | 31.8527 | -8.973e-05
AL_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 176616.2421 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104354.6649 | 0 | 0 | 623161.3219 | 0 | 623161.3219 | 0 | 0 | 2072.5916 | 0 | 0 | 0 | 4015.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 1224.602 | 0 | 0 | 7312.7981 | 0 | 7312.7981 | 0 | 0 | 176.6162 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3547 | 0 | 0 | 623.1613 | 0 | 623.1613 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.388 | 1.411 | 0 | 0 | 8.4258 | 8.4258 | 0
AL_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 65654.7521 | 83409.7932 | 10733.6031 | 53987.5506 | 0 | 37277.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251062.9497 | 0 | 251062.394 | 0.55571 | 0.55571 | 0 | 7609.3858 | 9667.195 | 1244.0246 | 6257.1571 | 0 | 4320.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29098.1959 | 0 | 29098.1315 | 0.064407 | 0.064407 | 0 | 224.014 | 284.5942 | 36.6231 | 184.2055 | 0 | 127.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.6268 | 0 | 856.6249 | 0.0018961 | 0.0018961 | 11.5258 | 1.4832 | 7.4601 | 5.1511 | 0 | 0 | 9.0723 | 0 | 0 | 0 | 0 | 34.6924 | 34.6925 | 7.679e-05
AL_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 116429.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86279.7924 | 0 | 0 | 202709.6475 | 0 | 202709.6475 | 0 | 0 | 1366.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012.4934 | 0 | 0 | 2378.7977 | 0 | 2378.7977 | 0 | 0 | 116.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2798 | 0 | 0 | 202.7096 | 0 | 202.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7153 | 3.4942 | 0 | 0 | 8.2095 | 8.2095 | 0
AL_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 0 | 61211.824 | 65824.2447 | 10733.6031 | 53987.5506 | 0 | 38363.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230120.8926 | 0 | 230119.5034 | 1.3893 | 1.3893 | 0 | 7094.4504 | 7629.03 | 1244.0246 | 6257.1571 | 0 | 4446.3494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26671.0115 | 0 | 26670.8504 | 0.16102 | 0.16102 | 0 | 208.8547 | 224.5923 | 36.6231 | 184.2055 | 0 | 130.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785.1725 | 0 | 785.1677 | 0.0047402 | 0.0047402 | 9.0958 | 1.4832 | 7.4601 | 5.3012 | 0 | 0 | 8.4584 | 0 | 0 | 0 | 0 | 31.7985 | 31.7987 | 0.00019197
AL_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 128590.3487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86289.2706 | 0 | 0 | 214879.6193 | 0 | 214879.6193 | 0 | 0 | 1509.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012.6046 | 0 | 0 | 2521.6123 | 0 | 2521.6123 | 0 | 0 | 128.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2893 | 0 | 0 | 214.8796 | 0 | 214.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2078 | 3.4946 | 0 | 0 | 8.7024 | 8.7024 | 0
AL_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 7955.0364 | 100434.0713 | 80053.2847 | 12320.1647 | 154949.5496 | 0 | 46327.0423 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 402111.3917 | 0 | 402110.836 | 0.55571 | 0.55571 | 921.9887 | 11640.3089 | 9278.1757 | 1427.9071 | 17958.6528 | 0 | 5369.3042 | 8.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 46604.7103 | 0 | 46604.6459 | 0.064407 | 0.064407 | 27.1426 | 342.6811 | 273.1418 | 42.0364 | 528.6879 | 0 | 158.0679 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.0041 | 0 | 1372.0022 | 0.0018961 | 0.0018961 | 6.3224 | 0.97302 | 12.2376 | 3.6588 | 0.0057056 | 0 | 7.9321 | 0.62827 | 0 | 0 | 0 | 31.7578 | 31.7579 | 4.3889e-05
AL_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 20349.6336 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511148.2946 | 0 | 0 | 930993.3661 | 0 | 930993.3661 | 0 | 0 | 238.8029 | 0 | 0 | 0 | 4688.079 | 0 | 0 | 0 | 0 | 0 | 0 | 5998.3252 | 0 | 0 | 10925.2072 | 0 | 10925.2072 | 0 | 0 | 20.3496 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.1483 | 0 | 0 | 930.9934 | 0 | 930.9934 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.47103 | 11.8316 | 0 | 0 | 21.5498 | 21.5498 | 0
AL_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 9355.434 | 94535.1742 | 51281.2267 | 12320.1647 | 154949.5496 | 0 | 43987.4891 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 366501.2811 | 0 | 366499.614 | 1.6671 | 1.6671 | 1084.2948 | 10956.6267 | 5943.4942 | 1427.9071 | 17958.6528 | 0 | 5098.15 | 8.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 42477.4985 | 0 | 42477.3053 | 0.19322 | 0.19322 | 31.9207 | 322.554 | 174.9715 | 42.0364 | 528.6879 | 0 | 150.0853 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.5024 | 0 | 1250.4967 | 0.0056883 | 0.0056883 | 4.0501 | 0.97302 | 12.2376 | 3.474 | 0.0057056 | 0 | 7.4662 | 0.73887 | 0 | 0 | 0 | 28.9453 | 28.9455 | 0.00013167
AL_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 21904.0536 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511186.2073 | 0 | 0 | 932585.6989 | 0 | 932585.6989 | 0 | 0 | 257.0441 | 0 | 0 | 0 | 4688.079 | 0 | 0 | 0 | 0 | 0 | 0 | 5998.7701 | 0 | 0 | 10943.8932 | 0 | 10943.8932 | 0 | 0 | 21.9041 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.1862 | 0 | 0 | 932.5857 | 0 | 932.5857 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.50701 | 11.8325 | 0 | 0 | 21.5866 | 21.5866 | 0
AL_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 1105.8695 | 6621.3244 | 8999.7775 | 1564.333 | 13417.6985 | 0 | 5068.1056 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41781.3072 | 0 | 41782.6965 | -1.3893 | -1.3893 | 128.1703 | 767.4115 | 1043.0742 | 181.3062 | 1555.1113 | 0 | 587.3934 | 0 | 0 | 0 | 0 | 579.9866 | 0 | 0 | 4842.4535 | 0 | 4842.6145 | -0.16102 | -0.16102 | 3.7732 | 22.592 | 30.7072 | 5.3375 | 45.7812 | 0 | 17.2924 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.5578 | 0 | 142.5626 | -0.0047402 | -0.0047402 | 5.5811 | 0.9701 | 8.3208 | 3.1429 | 0 | 0 | 4.1061 | 0.68579 | 3.1033 | 0 | 0 | 25.911 | 25.9102 | -0.00086155
AL_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 919.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919.3826 | 0 | 919.3826 | 0 | 0 | 10.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.789 | 0 | 10.789 | 0 | 0 | 0.91938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91938 | 0 | 0.91938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1671 | 0 | 0 | 0 | 0.1671 | 0.1671 | 0
AL_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Electricity | 1139.2123 | 6301.7892 | 7229.8305 | 1564.333 | 13417.6985 | 0 | 4665.2135 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39322.2757 | 0 | 39325.0543 | -2.7786 | -2.7786 | 132.0347 | 730.3774 | 837.9374 | 181.3062 | 1555.1113 | 0 | 540.6982 | 0 | 0 | 0 | 0 | 579.9866 | 0 | 0 | 4557.4518 | 0 | 4557.7738 | -0.32204 | -0.32204 | 3.887 | 21.5017 | 24.6682 | 5.3375 | 45.7812 | 0 | 15.9177 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.1676 | 0 | 134.1771 | -0.0094805 | -0.0094805 | 4.4835 | 0.9701 | 8.3208 | 2.8931 | 0 | 0 | 3.908 | 0.70647 | 3.1033 | 0 | 0 | 24.387 | 24.3852 | -0.0017231
AL_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | AL-BIRMINGHAM-AL | Zone3A | Zone3A(AL-BIRMINGHAM-AL) |  |  | AL | 0.1159 | 0.011735 |  |  |  | Natural Gas | 985.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 985.7298 | 0 | 985.7298 | 0 | 0 | 11.5675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5675 | 0 | 11.5675 | 0 | 0 | 0.98573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98573 | 0 | 0.98573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17916 | 0 | 0 | 0 | 0.17916 | 0.17916 | 0
AR_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 936941.021 | 882361.6357 | 94851.9308 | 4077910.5986 | 543459.8574 | 573737.8985 | 126269.1843 | 342677.8504 | 250393.3151 | 13292.663 | 0 | 0 | 0 | 7841895.9549 | 0 | 7841892.8985 | 3.0564 | 543462.9138 | 0 | 80389.5396 | 75706.6283 | 8138.2957 | 349884.7294 | 46628.8558 | 49226.7117 | 10833.896 | 29401.7596 | 21483.7464 | 1140.5105 | 0 | 0 | 0 | 672834.6729 | 0 | 672834.4107 | 0.26224 | 46629.118 | 0 | 3196.8428 | 3010.6179 | 323.6348 | 13913.831 | 1854.285 | 1957.5937 | 430.8305 | 1169.2168 | 854.342 | 45.3546 | 0 | 0 | 0 | 26756.549 | 0 | 26756.5386 | 0.010429 | 1854.2955 | 6.0383 | 0.6491 | 27.9065 | 3.9263 | 0.8641 | 0.090966 | 6.4118 | 0 | 0 | 1.7135 | 0 | 53.6646 | 53.6646 | 2.0916e-05
AR_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 887422.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501878.6432 | 0 | 0 | 1389300.8563 | 0 | 1389300.8563 | 0 | 0 | 6520.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.8043 | 0 | 0 | 10208.5827 | 0 | 10208.5827 | 0 | 0 | 887.4222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.8786 | 0 | 0 | 1389.3009 | 0 | 1389.3009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7799 | 1.0066 | 0 | 0 | 2.7865 | 2.7865 | 0
AR_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 877190.7231 | 717573.1814 | 94851.9308 | 4077910.5986 | 543387.6147 | 557733.3545 | 118314.1479 | 309551.7784 | 250332.1867 | 13056.4848 | 0 | 0 | 0 | 7559902.0009 | 0 | 7559897.2773 | 4.7236 | 543392.3382 | 0 | 75262.964 | 61567.779 | 8138.2957 | 349884.7294 | 46622.6573 | 47853.5218 | 10151.3539 | 26559.5426 | 21478.5016 | 1120.2464 | 0 | 0 | 0 | 648639.5917 | 0 | 648639.1864 | 0.40528 | 46623.0626 | 0 | 2992.9747 | 2448.3597 | 323.6348 | 13913.831 | 1854.0385 | 1902.9862 | 403.6879 | 1056.1907 | 854.1334 | 44.5487 | 0 | 0 | 0 | 25794.3856 | 0 | 25794.3695 | 0.016117 | 1854.0547 | 4.9106 | 0.6491 | 27.9065 | 3.8168 | 0.80966 | 0.08935 | 6.0029 | 0 | 0 | 1.7131 | 0 | 51.7348 | 51.7349 | 3.2325e-05
AR_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 516588.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501916.5559 | 0 | 0 | 1018505.3208 | 0 | 1018505.3208 | 0 | 0 | 3795.8942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688.0829 | 0 | 0 | 7483.9771 | 0 | 7483.9771 | 0 | 0 | 516.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.9166 | 0 | 0 | 1018.5053 | 0 | 1018.5053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0361 | 1.0067 | 0 | 0 | 2.0428 | 2.0428 | 0
AR_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 46757.7201 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 24231.88 | 0 | 0 | 0 | 0 | 100950.8847 | 0 | 0 | 349529.7958 | 0 | 349530.9072 | -1.1114 | -1.1114 | 0 | 4011.8124 | 2434.5512 | 618.6507 | 12183.961 | 0 | 2079.0953 | 0 | 0 | 0 | 0 | 8661.5859 | 0 | 0 | 29989.6565 | 0 | 29989.7518 | -0.09536 | -0.09536 | 0 | 159.5373 | 96.8146 | 24.6018 | 484.5184 | 0 | 82.6792 | 0 | 0 | 0 | 0 | 344.4444 | 0 | 0 | 1192.5957 | 0 | 1192.5995 | -0.0037922 | -0.0037922 | 2.8693 | 0.72914 | 14.3599 | 2.4504 | 0 | 0 | 4.7283 | 0 | 10.2085 | 0 | 0 | 35.3457 | 35.3456 | -0.00011239
AR_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 147973.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147973.2088 | 0 | 147973.2088 | 0 | 0 | 1087.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.3071 | 0 | 1087.3071 | 0 | 0 | 147.9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.9732 | 0 | 147.9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3856 | 0 | 0 | 0 | 4.3856 | 4.3856 | 0
AR_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 42484.2846 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 22559.1829 | 0 | 0 | 0 | 0 | 100820.2921 | 0 | 0 | 338259.9293 | 0 | 338261.3186 | -1.3893 | -1.3893 | 0 | 3645.1516 | 1988.9797 | 618.6507 | 12183.961 | 0 | 1935.5779 | 0 | 0 | 0 | 0 | 8650.3811 | 0 | 0 | 29022.7019 | 0 | 29022.8211 | -0.1192 | -0.1192 | 0 | 144.9564 | 79.0956 | 24.6018 | 484.5184 | 0 | 76.9719 | 0 | 0 | 0 | 0 | 343.9988 | 0 | 0 | 1154.1429 | 0 | 1154.1476 | -0.0047402 | -0.0047402 | 2.3442 | 0.72914 | 14.3599 | 2.2813 | 0 | 0 | 4.2961 | 0 | 10.1953 | 0 | 0 | 34.2061 | 34.2059 | -0.00014049
AR_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 49229.6212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49229.6212 | 0 | 49229.6212 | 0 | 0 | 361.7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361.7393 | 0 | 361.7393 | 0 | 0 | 49.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2296 | 0 | 49.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.459 | 0 | 0 | 0 | 1.459 | 1.459 | 0
AR_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 177339.2399 | 100500.7569 | 7093.6807 | 317887.4784 | 4818.0346 | 96474.6138 | 577.9419 | 0 | 0 | 21906.2197 | 7179.8163 | 17705.0269 | 0 | 751482.8092 | 0 | 751485.5878 | -2.7786 | 4815.2561 | 0 | 15215.7068 | 8622.9649 | 608.6378 | 27274.7456 | 413.3874 | 8277.5219 | 49.5874 | 0 | 0 | 1879.5537 | 616.0282 | 1519.0913 | 0 | 64477.225 | 0 | 64477.4634 | -0.2384 | 413.149 | 0 | 605.0815 | 342.9086 | 24.2036 | 1084.6321 | 16.4391 | 329.1714 | 1.9719 | 0 | 0 | 74.744 | 24.4975 | 60.4096 | 0 | 2564.0593 | 0 | 2564.0688 | -0.0094805 | 16.4297 | 4.6365 | 0.32726 | 14.6653 | 4.4507 | 0.026663 | 1.0106 | 8.1813 | 0 | 0.33123 | 0 | 0.8168 | 34.6688 | 34.6687 | -0.00012819
AR_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 372065.6105 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 106070.2139 | 0 | 0 | 820326.2392 | 0 | 820326.2392 | 0 | 0 | 2733.9381 | 0 | 0 | 0 | 2514.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 779.4039 | 0 | 0 | 6027.7572 | 0 | 6027.7572 | 0 | 0 | 372.0656 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 106.0702 | 0 | 0 | 820.3262 | 0 | 820.3262 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.0307 | 1.4342 | 0 | 0 | 11.0916 | 11.0916 | 0
AR_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 162679.5221 | 81056.3473 | 7093.6807 | 312483.1662 | 4745.7919 | 84910.2192 | 447.3492 | 0 | 0 | 22937.068 | 7179.8163 | 12528.5572 | 0 | 696061.5182 | 0 | 696058.7396 | 2.7786 | 4748.5705 | 0 | 13957.903 | 6954.6346 | 608.6378 | 26811.0557 | 407.1889 | 7285.2968 | 38.3826 | 0 | 0 | 1968.0004 | 616.0282 | 1074.9502 | 0 | 59722.0783 | 0 | 59721.8399 | 0.2384 | 407.4273 | 0 | 555.0625 | 276.5643 | 24.2036 | 1066.1926 | 16.1926 | 289.7137 | 1.5264 | 0 | 0 | 78.2613 | 24.4975 | 42.7474 | 0 | 2374.9619 | 0 | 2374.9524 | 0.0094805 | 16.2021 | 3.7394 | 0.32726 | 14.416 | 3.9172 | 0.020638 | 1.0582 | 7.505 | 0 | 0.33123 | 0 | 0.57799 | 32.1117 | 32.1119 | 0.00012819
AR_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 318153.7727 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 105804.8251 | 0 | 0 | 766149.0126 | 0 | 766149.0126 | 0 | 0 | 2337.7939 | 0 | 0 | 0 | 2514.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 777.4539 | 0 | 0 | 5629.6629 | 0 | 5629.6629 | 0 | 0 | 318.1538 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8048 | 0 | 0 | 766.149 | 0 | 766.149 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.3018 | 1.4306 | 0 | 0 | 10.3591 | 10.3591 | 0
AR_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 69869.8378 | 82765.1658 | 10689.146 | 53987.5506 | 0 | 38955.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256267.2051 | 0 | 256263.8708 | 3.3343 | 3.3343 | 0 | 5994.8321 | 7101.2512 | 917.1287 | 4632.1318 | 0 | 3342.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21987.7262 | 0 | 21987.4401 | 0.28608 | 0.28608 | 0 | 238.3959 | 282.3947 | 36.4714 | 184.2055 | 0 | 132.9162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874.3837 | 0 | 874.3723 | 0.011377 | 0.011377 | 11.4367 | 1.4771 | 7.4601 | 5.383 | 0 | 0 | 9.6548 | 0 | 0 | 0 | 0 | 35.4112 | 35.4116 | 0.00046074
AR_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 207458.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86573.6157 | 0 | 0 | 294031.827 | 0 | 294031.827 | 0 | 0 | 1524.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.1429 | 0 | 0 | 2160.5459 | 0 | 2160.5459 | 0 | 0 | 207.4582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5736 | 0 | 0 | 294.0318 | 0 | 294.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4018 | 3.5061 | 0 | 0 | 11.908 | 11.908 | 0
AR_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 65626.9665 | 65493.5953 | 10689.146 | 53987.5506 | 0 | 37102.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232899.4593 | 0 | 232896.6808 | 2.7786 | 2.7786 | 0 | 5630.7937 | 5619.3505 | 917.1287 | 4632.1318 | 0 | 3183.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19982.7736 | 0 | 19982.5352 | 0.2384 | 0.2384 | 0 | 223.9192 | 223.4641 | 36.4714 | 184.2055 | 0 | 126.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794.653 | 0 | 794.6435 | 0.0094805 | 0.0094805 | 9.0501 | 1.4771 | 7.4601 | 5.1269 | 0 | 0 | 9.0685 | 0 | 0 | 0 | 0 | 32.1822 | 32.1826 | 0.00038395
AR_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 225400.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86583.0939 | 0 | 0 | 311983.4832 | 0 | 311983.4832 | 0 | 0 | 1656.2421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.2126 | 0 | 0 | 2292.4546 | 0 | 2292.4546 | 0 | 0 | 225.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5831 | 0 | 0 | 311.9835 | 0 | 311.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1285 | 3.5065 | 0 | 0 | 12.635 | 12.635 | 0
AR_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 14362.4112 | 102115.1041 | 80092.1846 | 12314.6075 | 154949.5496 | 0 | 46452.0778 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 410358.1776 | 0 | 410361.234 | -3.0564 | -3.0564 | 1232.2949 | 8761.4759 | 6871.9094 | 1056.5933 | 13294.6714 | 0 | 3985.5883 | 6.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 35208.7316 | 0 | 35208.9939 | -0.26224 | -0.26224 | 49.0045 | 348.4167 | 273.2745 | 42.0174 | 528.6879 | 0 | 158.4945 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1400.1421 | 0 | 1400.1525 | -0.010429 | -0.010429 | 6.3255 | 0.97258 | 12.2376 | 3.6687 | 0.0057056 | 0 | 8.0648 | 1.1343 | 0 | 0 | 0 | 32.4094 | 32.4092 | -0.00024139
AR_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 32595.4308 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 516835.1974 | 0 | 0 | 948926.066 | 0 | 948926.066 | 0 | 0 | 239.5112 | 0 | 0 | 0 | 2935.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.705 | 0 | 0 | 6972.7087 | 0 | 6972.7087 | 0 | 0 | 32.5954 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 516.8352 | 0 | 0 | 948.9261 | 0 | 948.9261 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.75449 | 11.9632 | 0 | 0 | 21.9649 | 21.9649 | 0
AR_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 16196.2652 | 96327.3497 | 51309.0124 | 12314.6075 | 154949.5496 | 0 | 44123.6389 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 375292.6661 | 0 | 375293.2218 | -0.55571 | -0.55571 | 1389.6396 | 8264.8866 | 4402.3133 | 1056.5933 | 13294.6714 | 0 | 3785.8082 | 6.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 32200.1108 | 0 | 32200.1584 | -0.04768 | -0.04768 | 55.2617 | 328.6689 | 175.0664 | 42.0174 | 528.6879 | 0 | 150.5499 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.4986 | 0 | 1280.5005 | -0.0018961 | -0.0018961 | 4.0523 | 0.97258 | 12.2376 | 3.4848 | 0.0057056 | 0 | 7.6077 | 1.2791 | 0 | 0 | 0 | 29.6398 | 29.6398 | -4.3889e-05
AR_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 33230.4682 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 516873.11 | 0 | 0 | 949599.0162 | 0 | 949599.0162 | 0 | 0 | 244.1775 | 0 | 0 | 0 | 2935.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.9836 | 0 | 0 | 6977.6536 | 0 | 6977.6536 | 0 | 0 | 33.2305 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 516.8731 | 0 | 0 | 949.599 | 0 | 949.599 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.76919 | 11.9641 | 0 | 0 | 21.9804 | 21.9804 | 0
AR_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 2003.3466 | 6829.7169 | 9008.1132 | 1572.6687 | 13417.6985 | 0 | 5218.1482 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43053.8907 | 0 | 43055.8357 | -1.945 | -1.945 | 171.8871 | 585.9897 | 772.8961 | 134.935 | 1151.2385 | 0 | 447.7171 | 0 | 0 | 0 | 0 | 429.3602 | 0 | 0 | 3694.0238 | 0 | 3694.1907 | -0.16688 | -0.16688 | 6.8354 | 23.303 | 30.7357 | 5.3659 | 45.7812 | 0 | 17.8043 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.8999 | 0 | 146.9065 | -0.0066363 | -0.0066363 | 5.5863 | 0.97527 | 8.3208 | 3.236 | 0 | 0 | 4.2354 | 1.2424 | 3.1033 | 0 | 0 | 26.7006 | 26.6994 | -0.0012062
AR_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 3326.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3326.8381 | 0 | 3326.8381 | 0 | 0 | 24.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.4456 | 0 | 24.4456 | 0 | 0 | 3.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3268 | 0 | 3.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60466 | 0 | 0 | 0 | 0.60466 | 0.60466 | 0
AR_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 2036.6894 | 6515.7389 | 7235.3876 | 1572.6687 | 13417.6985 | 0 | 4798.5847 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40580.9664 | 0 | 40580.6885 | 0.27786 | 0.27786 | 174.7479 | 559.0504 | 620.7963 | 134.935 | 1151.2385 | 0 | 411.7186 | 0 | 0 | 0 | 0 | 429.3602 | 0 | 0 | 3481.8469 | 0 | 3481.8231 | 0.02384 | 0.02384 | 6.9492 | 22.2317 | 24.6871 | 5.3659 | 45.7812 | 0 | 16.3728 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.4623 | 0 | 138.4613 | 0.00094805 | 0.00094805 | 4.4869 | 0.97527 | 8.3208 | 2.9758 | 0 | 0 | 4.0407 | 1.263 | 3.1033 | 0 | 0 | 25.1656 | 25.1658 | 0.00017231
AR_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | AR-LITTLEROCK-AR | Zone3A | Zone3A(AR-LITTLEROCK-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 3440.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3440.5761 | 0 | 3440.5761 | 0 | 0 | 25.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2814 | 0 | 25.2814 | 0 | 0 | 3.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4406 | 0 | 3.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62533 | 0 | 0 | 0 | 0.62533 | 0.62533 | 0
AR_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 883245.2199 | 880047.0896 | 95218.7016 | 4077910.5986 | 543457.0788 | 615066.2994 | 116680.3507 | 323669.6757 | 265592.0749 | 14340.1826 | 0 | 0 | 0 | 7815227.2719 | 0 | 7815225.3269 | 1.945 | 543459.0238 | 0 | 75782.4399 | 75508.0403 | 8169.7646 | 349884.7294 | 46628.6174 | 52772.6885 | 10011.1741 | 27770.8582 | 22787.8 | 1230.3877 | 0 | 0 | 0 | 670546.4999 | 0 | 670546.333 | 0.16688 | 46628.7842 | 0 | 3013.6327 | 3002.7207 | 324.8862 | 13913.831 | 1854.2756 | 2098.6062 | 398.1134 | 1104.3609 | 906.2002 | 48.9287 | 0 | 0 | 0 | 26665.5555 | 0 | 26665.5488 | 0.0066363 | 1854.2822 | 6.0224 | 0.65161 | 27.9065 | 4.2091 | 0.79848 | 0.098135 | 6.0443 | 0 | 0 | 1.8175 | 0 | 53.4821 | 53.4821 | 1.331e-05
AR_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 389486.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516048.5092 | 0 | 0 | 905534.9983 | 0 | 905534.9983 | 0 | 0 | 2861.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3791.9244 | 0 | 0 | 6653.8712 | 0 | 6653.8712 | 0 | 0 | 389.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516.0485 | 0 | 0 | 905.535 | 0 | 905.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78118 | 1.035 | 0 | 0 | 1.8162 | 1.8162 | 0
AR_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 832000.1145 | 716456.1976 | 95218.7016 | 4077910.5986 | 543384.8361 | 590442.6414 | 113087.664 | 291799.5159 | 265428.1395 | 12753.6211 | 0 | 0 | 0 | 7538482.0303 | 0 | 7538480.6411 | 1.3893 | 543386.2254 | 0 | 71385.6098 | 61471.9418 | 8169.7646 | 349884.7294 | 46622.4189 | 50659.9786 | 9702.9216 | 25036.3985 | 22773.7344 | 1094.2607 | 0 | 0 | 0 | 646801.7582 | 0 | 646801.639 | 0.1192 | 46622.5381 | 0 | 2838.7844 | 2444.5485 | 324.8862 | 13913.831 | 1854.0291 | 2014.5903 | 385.8551 | 995.6199 | 905.6408 | 43.5154 | 0 | 0 | 0 | 25721.3007 | 0 | 25721.2959 | 0.0047402 | 1854.0338 | 4.9029 | 0.65161 | 27.9065 | 4.0406 | 0.7739 | 0.087277 | 5.6936 | 0 | 0 | 1.8164 | 0 | 51.5883 | 51.5883 | 9.5073e-06
AR_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 355184.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516010.5965 | 0 | 0 | 871195.584 | 0 | 871195.584 | 0 | 0 | 2609.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3791.6459 | 0 | 0 | 6401.5452 | 0 | 6401.5452 | 0 | 0 | 355.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516.0106 | 0 | 0 | 871.1956 | 0 | 871.1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71238 | 1.0349 | 0 | 0 | 1.7473 | 1.7473 | 0
AR_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 41942.4641 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 23428.8743 | 0 | 0 | 0 | 0 | 103512.7232 | 0 | 0 | 346473.3725 | 0 | 346474.4839 | -1.1114 | -1.1114 | 0 | 3598.6634 | 2434.5512 | 618.6507 | 12183.961 | 0 | 2010.1974 | 0 | 0 | 0 | 0 | 8881.3916 | 0 | 0 | 29727.4154 | 0 | 29727.5107 | -0.09536 | -0.09536 | 0 | 143.1077 | 96.8146 | 24.6018 | 484.5184 | 0 | 79.9393 | 0 | 0 | 0 | 0 | 353.1854 | 0 | 0 | 1182.1671 | 0 | 1182.1709 | -0.0037922 | -0.0037922 | 2.8693 | 0.72914 | 14.3599 | 2.3692 | 0 | 0 | 4.2414 | 0 | 10.4675 | 0 | 0 | 35.0366 | 35.0365 | -0.00011239
AR_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 31789.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31789.7862 | 0 | 31789.7862 | 0 | 0 | 233.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.5913 | 0 | 233.5913 | 0 | 0 | 31.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.7898 | 0 | 31.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94217 | 0 | 0 | 0 | 0.94217 | 0.94217 | 0
AR_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 41264.4938 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 22923.1751 | 0 | 0 | 0 | 0 | 103540.5089 | 0 | 0 | 340124.3476 | 0 | 340126.5704 | -2.2229 | -2.2229 | 0 | 3540.4936 | 1988.9797 | 618.6507 | 12183.961 | 0 | 1966.8084 | 0 | 0 | 0 | 0 | 8883.7757 | 0 | 0 | 29182.669 | 0 | 29182.8597 | -0.19072 | -0.19072 | 0 | 140.7945 | 79.0956 | 24.6018 | 484.5184 | 0 | 78.2139 | 0 | 0 | 0 | 0 | 353.2802 | 0 | 0 | 1160.5043 | 0 | 1160.5119 | -0.0075844 | -0.0075844 | 2.3442 | 0.72914 | 14.3599 | 2.3181 | 0 | 0 | 4.1728 | 0 | 10.4704 | 0 | 0 | 34.3947 | 34.3945 | -0.00022478
AR_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 37874.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37874.7721 | 0 | 37874.7721 | 0 | 0 | 278.3038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.3038 | 0 | 278.3038 | 0 | 0 | 37.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8748 | 0 | 37.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1225 | 0 | 0 | 0 | 1.1225 | 1.1225 | 0
AR_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 172974.1117 | 97349.8623 | 7104.795 | 317887.4784 | 4818.0346 | 97694.4046 | 386.2208 | 0 | 0 | 18419.1185 | 7179.8163 | 17655.0127 | 0 | 741468.8549 | 0 | 741467.7435 | 1.1114 | 4819.1461 | 0 | 14841.1788 | 8352.6182 | 609.5914 | 27274.7456 | 413.3874 | 8382.1799 | 33.1377 | 0 | 0 | 1580.3604 | 616.0282 | 1514.8001 | 0 | 63618.0277 | 0 | 63617.9324 | 0.09536 | 413.4827 | 0 | 590.1877 | 332.1577 | 24.2416 | 1084.6321 | 16.4391 | 333.3333 | 1.3178 | 0 | 0 | 62.846 | 24.4975 | 60.2389 | 0 | 2529.8917 | 0 | 2529.8879 | 0.0037922 | 16.4429 | 4.4911 | 0.32777 | 14.6653 | 4.507 | 0.017818 | 0.84974 | 7.9799 | 0 | 0.33123 | 0 | 0.81449 | 34.2066 | 34.2067 | 5.1274e-05
AR_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 168948.4016 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 108562.9729 | 0 | 0 | 619701.7894 | 0 | 619701.7894 | 0 | 0 | 1241.4329 | 0 | 0 | 0 | 2514.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 797.7207 | 0 | 0 | 4553.5687 | 0 | 4553.5687 | 0 | 0 | 168.9484 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 108.563 | 0 | 0 | 619.7018 | 0 | 619.7018 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.2844 | 1.4679 | 0 | 0 | 8.379 | 8.379 | 0
AR_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 158364.4081 | 79036.3293 | 7104.795 | 312483.1662 | 4743.0133 | 83479.2574 | 222.2853 | 0 | 0 | 22942.6251 | 7179.8163 | 12506.3286 | 0 | 688062.0247 | 0 | 688062.0247 | 0 | 4743.0133 | 0 | 13587.6662 | 6781.3171 | 609.5914 | 26811.0557 | 406.9505 | 7162.5203 | 19.0721 | 0 | 0 | 1968.4772 | 616.0282 | 1073.043 | 0 | 59035.7217 | 0 | 59035.7217 | 0 | 406.9505 | 0 | 540.3394 | 269.672 | 24.2416 | 1066.1926 | 16.1832 | 284.8312 | 0.75844 | 0 | 0 | 78.2802 | 24.4975 | 42.6716 | 0 | 2347.6676 | 0 | 2347.6676 | 0 | 16.1832 | 3.6462 | 0.32777 | 14.416 | 3.8512 | 0.010255 | 1.0584 | 7.3059 | 0 | 0.33123 | 0 | 0.57696 | 31.7428 | 31.7428 | 0
AR_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 154361.4962 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 108363.9313 | 0 | 0 | 604915.8423 | 0 | 604915.8423 | 0 | 0 | 1134.2483 | 0 | 0 | 0 | 2514.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 796.2582 | 0 | 0 | 4444.9216 | 0 | 4444.9216 | 0 | 0 | 154.3615 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3639 | 0 | 0 | 604.9158 | 0 | 604.9158 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.0871 | 1.4652 | 0 | 0 | 8.1791 | 8.1791 | 0
AR_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 59489.1127 | 84043.3064 | 10686.3675 | 53987.5506 | 0 | 38488.7057 | 0 | 0 | 0 | 5579.3619 | 0 | 0 | 0 | 252274.4048 | 0 | 252273.2934 | 1.1114 | 1.1114 | 0 | 5104.1659 | 7210.9157 | 916.8903 | 4632.1318 | 0 | 3302.3309 | 0 | 0 | 0 | 478.7093 | 0 | 0 | 0 | 21645.1439 | 0 | 21645.0486 | 0.09536 | 0.09536 | 0 | 202.9769 | 286.7558 | 36.4619 | 184.2055 | 0 | 131.3235 | 0 | 0 | 0 | 19.0368 | 0 | 0 | 0 | 860.7603 | 0 | 860.7565 | 0.0037922 | 0.0037922 | 11.6133 | 1.4767 | 7.4601 | 5.3185 | 0 | 0.77097 | 8.2203 | 0 | 0 | 0 | 0 | 34.8597 | 34.8599 | 0.00015358
AR_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 73086.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87379.2603 | 0 | 0 | 160465.4384 | 0 | 160465.4384 | 0 | 0 | 537.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642.0628 | 0 | 0 | 1179.1 | 0 | 1179.1 | 0 | 0 | 73.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3793 | 0 | 0 | 160.4654 | 0 | 160.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9599 | 3.5388 | 0 | 0 | 6.4987 | 6.4987 | 0
AR_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 0 | 55638.0192 | 66402.1866 | 10686.3675 | 53987.5506 | 0 | 39419.5255 | 0 | 0 | 0 | 5693.2831 | 0 | 0 | 0 | 231826.9326 | 0 | 231824.9876 | 1.945 | 1.945 | 0 | 4773.7421 | 5697.3076 | 916.8903 | 4632.1318 | 0 | 3382.1953 | 0 | 0 | 0 | 488.4837 | 0 | 0 | 0 | 19890.7508 | 0 | 19890.5839 | 0.16688 | 0.16688 | 0 | 189.8369 | 226.5643 | 36.4619 | 184.2055 | 0 | 134.4994 | 0 | 0 | 0 | 19.4255 | 0 | 0 | 0 | 790.9935 | 0 | 790.9869 | 0.0066363 | 0.0066363 | 9.1756 | 1.4767 | 7.4601 | 5.4471 | 0 | 0.78671 | 7.6882 | 0 | 0 | 0 | 0 | 32.0341 | 32.0344 | 0.00026876
AR_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 78289.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87388.7385 | 0 | 0 | 165678.4326 | 0 | 165678.4326 | 0 | 0 | 575.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642.1325 | 0 | 0 | 1217.4051 | 0 | 1217.4051 | 0 | 0 | 78.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3887 | 0 | 0 | 165.6784 | 0 | 165.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1707 | 3.5392 | 0 | 0 | 6.7098 | 6.7098 | 0
AR_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 12920.3351 | 97511.0192 | 79272.5074 | 12314.6075 | 154949.5496 | 0 | 46791.0629 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 403831.3245 | 0 | 403828.2681 | 3.0564 | 3.0564 | 1108.5647 | 8366.4454 | 6801.5811 | 1056.5933 | 13294.6714 | 0 | 4014.6732 | 6.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 34648.7276 | 0 | 34648.4654 | 0.26224 | 0.26224 | 44.0842 | 332.7076 | 270.4778 | 42.0174 | 528.6879 | 0 | 159.6511 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.8725 | 0 | 1377.8621 | 0.010429 | 0.010429 | 6.2608 | 0.97258 | 12.2376 | 3.6955 | 0.0057056 | 0 | 7.7012 | 1.0204 | 0 | 0 | 0 | 31.8935 | 31.8937 | 0.00024139
AR_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 32642.8216 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 532313.0509 | 0 | 0 | 964451.3105 | 0 | 964451.3105 | 0 | 0 | 239.8595 | 0 | 0 | 0 | 2935.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 3911.4363 | 0 | 0 | 7086.7882 | 0 | 7086.7882 | 0 | 0 | 32.6428 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 532.3131 | 0 | 0 | 964.4513 | 0 | 964.4513 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.75559 | 12.3215 | 0 | 0 | 22.3242 | 22.3242 | 0
AR_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 15118.1813 | 91653.8006 | 50842.2132 | 12314.6075 | 154949.5496 | 0 | 44395.9385 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 369346.5334 | 0 | 369347.0891 | -0.55571 | -0.55571 | 1297.14 | 7863.8961 | 4362.2619 | 1056.5933 | 13294.6714 | 0 | 3809.1715 | 6.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 31689.9326 | 0 | 31689.9802 | -0.04768 | -0.04768 | 51.5832 | 312.7228 | 173.4736 | 42.0174 | 528.6879 | 0 | 151.4789 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.2104 | 0 | 1260.2123 | -0.0018961 | -0.0018961 | 4.0154 | 0.97258 | 12.2376 | 3.5063 | 0.0057056 | 0 | 7.2386 | 1.194 | 0 | 0 | 0 | 29.1702 | 29.1702 | -4.3889e-05
AR_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 33761.2458 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 532379.3981 | 0 | 0 | 965636.0819 | 0 | 965636.0819 | 0 | 0 | 248.0776 | 0 | 0 | 0 | 2935.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 3911.9238 | 0 | 0 | 7095.4939 | 0 | 7095.4939 | 0 | 0 | 33.7612 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 532.3794 | 0 | 0 | 965.6361 | 0 | 965.6361 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.78147 | 12.323 | 0 | 0 | 22.3517 | 22.3517 | 0
AR_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 1269.805 | 6446.2747 | 8852.5135 | 1578.2259 | 13417.6985 | 0 | 5204.2554 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41772.9715 | 0 | 41773.2494 | -0.27786 | -0.27786 | 108.9493 | 553.0904 | 759.5457 | 135.4118 | 1151.2385 | 0 | 446.5251 | 0 | 0 | 0 | 0 | 429.3602 | 0 | 0 | 3584.121 | 0 | 3584.1448 | -0.02384 | -0.02384 | 4.3326 | 21.9947 | 30.2048 | 5.3849 | 45.7812 | 0 | 17.7569 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.5294 | 0 | 142.5303 | -0.00094805 | -0.00094805 | 5.4898 | 0.97872 | 8.3208 | 3.2274 | 0 | 0 | 3.9976 | 0.78745 | 3.1033 | 0 | 0 | 25.9052 | 25.905 | -0.00017231
AR_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 1601.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1601.8109 | 0 | 1601.8109 | 0 | 0 | 11.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7701 | 0 | 11.7701 | 0 | 0 | 1.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6018 | 0 | 1.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29113 | 0 | 0 | 0 | 0.29113 | 0.29113 | 0
AR_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Electricity | 1308.7049 | 6123.961 | 7127.0235 | 1578.2259 | 13417.6985 | 0 | 4787.4704 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39347.2828 | 0 | 39347.0049 | 0.27786 | 0.27786 | 112.2869 | 525.4359 | 611.4986 | 135.4118 | 1151.2385 | 0 | 410.765 | 0 | 0 | 0 | 0 | 429.3602 | 0 | 0 | 3375.9969 | 0 | 3375.973 | 0.02384 | 0.02384 | 4.4653 | 20.895 | 24.3174 | 5.3849 | 45.7812 | 0 | 16.3348 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.2529 | 0 | 134.252 | 0.00094805 | 0.00094805 | 4.4197 | 0.97872 | 8.3208 | 2.9689 | 0 | 0 | 3.7977 | 0.81158 | 3.1033 | 0 | 0 | 24.4006 | 24.4008 | 0.00017231
AR_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | AR-FAYETTEVILLE-AR | Zone4A | Zone4A(AR-FAYETTEVILLE-AR) |  |  | AR | 0.0858 | 0.007348 |  |  |  | Natural Gas | 1706.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1706.0708 | 0 | 1706.0708 | 0 | 0 | 12.5362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5362 | 0 | 12.5362 | 0 | 0 | 1.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7061 | 0 | 1.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31008 | 0 | 0 | 0 | 0.31008 | 0.31008 | 0
AZ_2B_LO_2016_EL | 2B | LO | EL |  |  | OfficeLarge | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 1057728.0932 | 880552.7887 | 95388.1942 | 4077910.5986 | 543457.0788 | 646625.2598 | 127491.7537 | 352841.8473 | 458057.8319 | 0 | 0 | 0 | 0 | 8240053.4462 | 0 | 8240051.2234 | 2.2229 | 543459.3017 | 0 | 108628.6752 | 90432.7714 | 9796.3675 | 418801.4185 | 55813.042 | 66408.4142 | 13093.4031 | 36236.8577 | 47042.5393 | 0 | 0 | 0 | 0 | 846253.4889 | 0 | 846253.2606 | 0.22829 | 55813.2703 | 0 | 3608.9683 | 3004.4461 | 325.4645 | 13913.831 | 1854.2756 | 2206.2854 | 435.0019 | 1203.8964 | 1562.8933 | 0 | 0 | 0 | 0 | 28115.0624 | 0 | 28115.0548 | 0.0075844 | 1854.2831 | 6.0259 | 0.65277 | 27.9065 | 4.4251 | 0.87247 | 0 | 7.2384 | 0 | 0 | 3.1346 | 0 | 56.3894 | 56.3894 | 1.5212e-05
AZ_2B_LO_2016_NG | 2B | LO | NG |  |  | OfficeLarge | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 220348.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459094.1784 | 0 | 0 | 679442.7025 | 0 | 679442.7025 | 0 | 0 | 1480.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.6538 | 0 | 0 | 4565.1755 | 0 | 4565.1755 | 0 | 0 | 220.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0942 | 0 | 0 | 679.4427 | 0 | 679.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44195 | 0.92079 | 0 | 0 | 1.3627 | 1.3627 | 0
AZ_2B_LO_2019_EL | 2B | LO | EL |  |  | OfficeLarge | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 998783.5796 | 716345.055 | 95388.1942 | 4077910.5986 | 543384.8361 | 632590.7194 | 122851.5473 | 316075.853 | 457863.3322 | 0 | 0 | 0 | 0 | 7961193.7154 | 0 | 7961193.9933 | -0.27786 | 543384.5583 | 0 | 102575.0736 | 73568.6371 | 9796.3675 | 418801.4185 | 55805.6227 | 64967.0669 | 12616.8539 | 32460.9901 | 47022.5642 | 0 | 0 | 0 | 0 | 817614.5946 | 0 | 817614.6231 | -0.028536 | 55805.5941 | 0 | 3407.8496 | 2444.1693 | 325.4645 | 13913.831 | 1854.0291 | 2158.3995 | 419.1695 | 1078.4508 | 1562.2297 | 0 | 0 | 0 | 0 | 27163.593 | 0 | 27163.5939 | -0.00094805 | 1854.0281 | 4.9022 | 0.65277 | 27.9065 | 4.329 | 0.84071 | 0 | 6.835 | 0 | 0 | 3.1333 | 0 | 54.481 | 54.481 | -1.9015e-06
AZ_2B_LO_2019_NG | 2B | LO | NG |  |  | OfficeLarge | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 344171.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459141.5693 | 0 | 0 | 803312.9219 | 0 | 803312.9219 | 0 | 0 | 2312.4873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.9722 | 0 | 0 | 5397.4595 | 0 | 5397.4595 | 0 | 0 | 344.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.1416 | 0 | 0 | 803.3129 | 0 | 803.3129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69029 | 0.92088 | 0 | 0 | 1.6112 | 1.6112 | 0
AZ_2B_MA_2016_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 54987.8346 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 27674.5242 | 0 | 0 | 0 | 0 | 92345.6637 | 0 | 0 | 352602.8906 | 0 | 352602.3348 | 0.55571 | 0.55571 | 0 | 5647.2506 | 2914.084 | 741.0768 | 14583.8321 | 0 | 2842.1736 | 0 | 0 | 0 | 0 | 9483.8997 | 0 | 0 | 36212.3169 | 0 | 36212.2598 | 0.057072 | 0.057072 | 0 | 187.6185 | 96.8146 | 24.6208 | 484.5184 | 0 | 94.4255 | 0 | 0 | 0 | 0 | 315.0834 | 0 | 0 | 1203.0811 | 0 | 1203.0792 | 0.0018961 | 0.0018961 | 2.8693 | 0.7297 | 14.3599 | 2.7985 | 0 | 0 | 5.5605 | 0 | 9.3383 | 0 | 0 | 35.6563 | 35.6564 | 5.6196e-05
AZ_2B_MA_2016_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 19989.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19989.4631 | 0 | 19989.4631 | 0 | 0 | 134.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.3092 | 0 | 134.3092 | 0 | 0 | 19.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9895 | 0 | 19.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59244 | 0 | 0 | 0 | 0.59244 | 0.59244 | 0
AZ_2B_MA_2019_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 52734.4171 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 27824.5668 | 0 | 0 | 0 | 0 | 92259.5281 | 0 | 0 | 345220.2389 | 0 | 345220.2389 | 0 | 0 | 0 | 5415.8246 | 2380.7485 | 741.0768 | 14583.8321 | 0 | 2857.583 | 0 | 0 | 0 | 0 | 9475.0535 | 0 | 0 | 35454.1185 | 0 | 35454.1185 | 0 | 0 | 0 | 179.9298 | 79.0956 | 24.6208 | 484.5184 | 0 | 94.9374 | 0 | 0 | 0 | 0 | 314.7895 | 0 | 0 | 1177.8915 | 0 | 1177.8915 | 0 | 0 | 2.3442 | 0.7297 | 14.3599 | 2.8137 | 0 | 0 | 5.3327 | 0 | 9.3296 | 0 | 0 | 34.9098 | 34.9098 | 0
AZ_2B_MA_2019_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 7743.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7743.6659 | 0 | 7743.6659 | 0 | 0 | 52.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.0297 | 0 | 52.0297 | 0 | 0 | 7.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7437 | 0 | 7.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2295 | 0 | 0 | 0 | 0.2295 | 0.2295 | 0
AZ_2B_PS_2016_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 212966.0219 | 100420.1785 | 7115.9093 | 317887.4784 | 4818.0346 | 111926.2231 | 155.5997 | 0 | 0 | 16724.1929 | 7179.8163 | 17474.4059 | 0 | 796667.8606 | 0 | 796670.0835 | -2.2229 | 4815.8118 | 0 | 21871.6105 | 10313.1523 | 730.8039 | 32647.044 | 494.8122 | 11494.8231 | 15.9801 | 0 | 0 | 1717.5746 | 737.3671 | 1794.6215 | 0 | 81817.7893 | 0 | 81818.0176 | -0.22829 | 494.5839 | 0 | 726.6401 | 342.6336 | 24.2795 | 1084.6321 | 16.4391 | 381.8923 | 0.53091 | 0 | 0 | 57.0629 | 24.4975 | 59.6227 | 0 | 2718.2307 | 0 | 2718.2383 | -0.0075844 | 16.4315 | 4.6328 | 0.32828 | 14.6653 | 5.1636 | 0.0071784 | 0.77155 | 9.8249 | 0 | 0.33123 | 0 | 0.80616 | 36.7533 | 36.7532 | -0.00010255
AZ_2B_PS_2016_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 72365.8371 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96705.7808 | 0 | 0 | 511262.0327 | 0 | 511262.0327 | 0 | 0 | 486.2261 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 649.7661 | 0 | 0 | 3435.1696 | 0 | 3435.1696 | 0 | 0 | 72.3658 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7058 | 0 | 0 | 511.262 | 0 | 511.262 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.97846 | 1.3076 | 0 | 0 | 6.9128 | 6.9128 | 0
AZ_2B_PS_2019_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 193932.8402 | 80547.8696 | 7115.9093 | 312483.1662 | 4745.7919 | 93054.1982 | 158.3783 | 0 | 0 | 19738.9377 | 7179.8163 | 12417.4145 | 0 | 731374.3221 | 0 | 731373.4886 | 0.83357 | 4746.6255 | 0 | 19916.9027 | 8272.2662 | 730.8039 | 32092.0212 | 487.3928 | 9556.6662 | 16.2655 | 0 | 0 | 2027.1889 | 737.3671 | 1275.2685 | 0 | 75112.1429 | 0 | 75112.0573 | 0.085608 | 487.4784 | 0 | 661.6989 | 274.8293 | 24.2795 | 1066.1926 | 16.1926 | 317.5009 | 0.54039 | 0 | 0 | 67.3493 | 24.4975 | 42.3682 | 0 | 2495.4492 | 0 | 2495.4463 | 0.0028441 | 16.1955 | 3.716 | 0.32828 | 14.416 | 4.2929 | 0.0073066 | 0.91063 | 8.9468 | 0 | 0.33123 | 0 | 0.57286 | 33.7409 | 33.741 | 3.8456e-05
AZ_2B_PS_2019_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 55523.1269 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96658.3899 | 0 | 0 | 494371.9316 | 0 | 494371.9316 | 0 | 0 | 373.0599 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 649.4477 | 0 | 0 | 3321.685 | 0 | 3321.685 | 0 | 0 | 55.5231 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6584 | 0 | 0 | 494.3719 | 0 | 494.3719 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.75073 | 1.3069 | 0 | 0 | 6.6844 | 6.6844 | 0
AZ_2B_RS_2016_EL | 2B | RS | EL |  |  | RetailStandalone | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 76996.8613 | 84946.3406 | 10697.4817 | 53987.5506 | 0 | 40769.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267398.1432 | 0 | 267397.5875 | 0.55571 | 0.55571 | 0 | 7907.5777 | 8723.9892 | 1098.6314 | 5544.5215 | 0 | 4187.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27461.7893 | 0 | 27461.7322 | 0.057072 | 0.057072 | 0 | 262.7133 | 289.8369 | 36.4998 | 184.2055 | 0 | 139.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912.3625 | 0 | 912.3606 | 0.0018961 | 0.0018961 | 11.7381 | 1.4782 | 7.4601 | 5.6337 | 0 | 0 | 10.6396 | 0 | 0 | 0 | 0 | 36.9496 | 36.9497 | 7.679e-05
AZ_2B_RS_2016_NG | 2B | RS | NG |  |  | RetailStandalone | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 25998.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83919.7278 | 0 | 0 | 109918.3514 | 0 | 109918.3514 | 0 | 0 | 174.6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.8567 | 0 | 0 | 738.5414 | 0 | 738.5414 | 0 | 0 | 25.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9197 | 0 | 0 | 109.9184 | 0 | 109.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0529 | 3.3987 | 0 | 0 | 4.4516 | 4.4516 | 0
AZ_2B_RS_2019_EL | 2B | RS | EL |  |  | RetailStandalone | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 72259.4051 | 67171.8495 | 10697.4817 | 53987.5506 | 0 | 41861.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245978.1727 | 0 | 245978.1727 | 0 | 0 | 0 | 7421.0409 | 6898.5489 | 1098.6314 | 5544.5215 | 0 | 4299.2157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25261.9583 | 0 | 25261.9583 | 0 | 0 | 0 | 246.5491 | 229.1904 | 36.4998 | 184.2055 | 0 | 142.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839.2775 | 0 | 839.2775 | 0 | 0 | 9.282 | 1.4782 | 7.4601 | 5.7846 | 0 | 0 | 9.985 | 0 | 0 | 0 | 0 | 33.9899 | 33.9899 | 0
AZ_2B_RS_2019_NG | 2B | RS | NG |  |  | RetailStandalone | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 30823.0127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83929.206 | 0 | 0 | 114752.2187 | 0 | 114752.2187 | 0 | 0 | 207.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.9203 | 0 | 0 | 771.0202 | 0 | 771.0202 | 0 | 0 | 30.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9292 | 0 | 0 | 114.7522 | 0 | 114.7522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2483 | 3.399 | 0 | 0 | 4.6473 | 4.6473 | 0
AZ_2B_SH_2016_EL | 2B | SH | EL |  |  | HotelSmall | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 2764.6738 | 111067.646 | 80533.9767 | 12325.7218 | 154949.5496 | 0 | 48483.21 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 410197.0208 | 0 | 410193.6865 | 3.3343 | 3.3343 | 283.932 | 11406.6472 | 8270.8394 | 1265.8516 | 15913.3187 | 0 | 4979.2257 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 42127.234 | 0 | 42126.8916 | 0.34243 | 0.34243 | 9.4331 | 378.9628 | 274.7819 | 42.0554 | 528.6879 | 0 | 165.4247 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.5922 | 0 | 1399.5809 | 0.011377 | 0.011377 | 6.3604 | 0.97346 | 12.2376 | 3.8291 | 0.0057056 | 0 | 8.7719 | 0.21835 | 0 | 0 | 0 | 32.3962 | 32.3965 | 0.00026333
AZ_2B_SH_2016_NG | 2B | SH | NG |  |  | HotelSmall | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 5004.4744 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 472211.9674 | 0 | 0 | 876711.8797 | 0 | 876711.8797 | 0 | 0 | 33.6251 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3172.7922 | 0 | 0 | 5890.6271 | 0 | 5890.6271 | 0 | 0 | 5.0045 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 472.212 | 0 | 0 | 876.7119 | 0 | 876.7119 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.11584 | 10.9303 | 0 | 0 | 20.2933 | 20.2933 | 0
AZ_2B_SH_2019_EL | 2B | SH | EL |  |  | HotelSmall | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 3320.3872 | 104949.2422 | 51592.4262 | 12325.7218 | 154949.5496 | 0 | 46063.0785 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373272.6481 | 0 | 373269.8695 | 2.7786 | 2.7786 | 341.0038 | 10778.2872 | 5298.5422 | 1265.8516 | 15913.3187 | 0 | 4730.6782 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 38335.101 | 0 | 38334.8156 | 0.28536 | 0.28536 | 11.3292 | 358.0868 | 176.0334 | 42.0554 | 528.6879 | 0 | 157.1672 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.6063 | 0 | 1273.5968 | 0.0094805 | 0.0094805 | 4.0747 | 0.97346 | 12.2376 | 3.638 | 0.0057056 | 0 | 8.2887 | 0.26224 | 0 | 0 | 0 | 29.48 | 29.4803 | 0.00021945
AZ_2B_SH_2019_NG | 2B | SH | NG |  |  | HotelSmall | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 5961.7697 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 472230.9237 | 0 | 0 | 877688.1313 | 0 | 877688.1313 | 0 | 0 | 40.0571 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3172.9196 | 0 | 0 | 5897.1866 | 0 | 5897.1866 | 0 | 0 | 5.9618 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 472.2309 | 0 | 0 | 877.6881 | 0 | 877.6881 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.138 | 10.9308 | 0 | 0 | 20.3159 | 20.3159 | 0
AZ_2B_SO_2016_EL | 2B | SO | EL |  |  | OfficeSmall | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 263.9638 | 8702.4708 | 9041.456 | 1581.0044 | 13417.6985 | 0 | 6123.961 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 44134.7532 | 0 | 44132.5303 | 2.2229 | 2.2229 | 27.1091 | 893.7438 | 928.5575 | 162.3692 | 1377.9976 | 0 | 628.9308 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4532.6392 | 0 | 4532.4109 | 0.22829 | 0.22829 | 0.90064 | 29.6928 | 30.8494 | 5.3944 | 45.7812 | 0 | 20.895 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 150.5878 | 0 | 150.5802 | 0.0075844 | 0.0075844 | 5.607 | 0.98044 | 8.3208 | 3.7977 | 0 | 0 | 5.3967 | 0.16369 | 3.1033 | 0 | 0 | 27.3683 | 27.3696 | 0.0013785
AZ_2B_SO_2016_NG | 2B | SO | NG |  |  | OfficeSmall | STD2016 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 47.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3909 | 0 | 47.3909 | 0 | 0 | 0.31842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31842 | 0 | 0.31842 | 0 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047391 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086134 | 0 | 0 | 0 | 0.0086134 | 0.0086134 | 0
AZ_2B_SO_2019_EL | 2B | SO | EL |  |  | OfficeSmall | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 252.8496 | 8313.4715 | 7260.3947 | 1581.0044 | 13417.6985 | 0 | 5629.3761 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41458.9935 | 0 | 41463.4392 | -4.4457 | -4.4457 | 25.9677 | 853.7935 | 745.6425 | 162.3692 | 1377.9976 | 0 | 578.1369 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4257.8386 | 0 | 4258.2952 | -0.45657 | -0.45657 | 0.86272 | 28.3656 | 24.7725 | 5.3944 | 45.7812 | 0 | 19.2074 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.4581 | 0 | 141.4733 | -0.015169 | -0.015169 | 4.5024 | 0.98044 | 8.3208 | 3.491 | 0 | 0 | 5.1555 | 0.1568 | 3.1033 | 0 | 0 | 25.7131 | 25.7103 | -0.002757
AZ_2B_SO_2019_NG | 2B | SO | NG |  |  | OfficeSmall | STD2019 | AZ-TUCSON-AZ | Zone2B | Zone2B(AZ-TUCSON-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 47.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3909 | 0 | 47.3909 | 0 | 0 | 0.31842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31842 | 0 | 0.31842 | 0 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047391 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086134 | 0 | 0 | 0 | 0.0086134 | 0.0086134 | 0
AZ_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 892792.375 | 881666.994 | 95974.4718 | 4077910.5986 | 543459.8574 | 706728.4357 | 117099.9143 | 274197.2959 | 579406.1746 | 0 | 0 | 0 | 0 | 8169236.1172 | 0 | 8169229.7265 | 6.3907 | 543466.2481 | 0 | 91689.7769 | 90547.2003 | 9856.5783 | 418801.4185 | 55813.3274 | 72581.0103 | 12026.1612 | 28160.0623 | 59505.0141 | 0 | 0 | 0 | 0 | 838980.5492 | 0 | 838979.8929 | 0.65633 | 55813.9837 | 0 | 3046.2076 | 3008.2478 | 327.4649 | 13913.831 | 1854.285 | 2411.3574 | 399.5449 | 935.5612 | 1976.9339 | 0 | 0 | 0 | 0 | 27873.4336 | 0 | 27873.4118 | 0.021805 | 1854.3068 | 6.0335 | 0.65678 | 27.9065 | 4.8364 | 0.80135 | 0 | 6.1097 | 0 | 0 | 3.9651 | 0 | 55.9047 | 55.9047 | 4.3734e-05
AZ_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 474382.4686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490504.8378 | 0 | 0 | 964887.3063 | 0 | 964887.3063 | 0 | 0 | 3187.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3295.702 | 0 | 0 | 6483.0778 | 0 | 6483.0778 | 0 | 0 | 474.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.5048 | 0 | 0 | 964.8873 | 0 | 964.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95145 | 0.98379 | 0 | 0 | 1.9352 | 1.9352 | 0
AZ_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 844514.7789 | 717009.1324 | 95974.4718 | 4077910.5986 | 543387.6147 | 684950.03 | 114382.476 | 246503.3218 | 579639.5742 | 0 | 0 | 0 | 0 | 7904271.9984 | 0 | 7904268.9419 | 3.0564 | 543390.6711 | 0 | 86731.6678 | 73636.8379 | 9856.5783 | 418801.4185 | 55805.908 | 70344.3681 | 11747.0803 | 25315.8911 | 59528.9843 | 0 | 0 | 0 | 0 | 811768.7342 | 0 | 811768.4203 | 0.31389 | 55806.2219 | 0 | 2881.4844 | 2446.4352 | 327.4649 | 13913.831 | 1854.0385 | 2337.0495 | 390.273 | 841.0693 | 1977.7302 | 0 | 0 | 0 | 0 | 26969.3761 | 0 | 26969.3656 | 0.010429 | 1854.049 | 4.9067 | 0.65678 | 27.9065 | 4.6873 | 0.78276 | 0 | 5.7793 | 0 | 0 | 3.9667 | 0 | 54.0915 | 54.0915 | 2.0916e-05
AZ_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 840419.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490457.4469 | 0 | 0 | 1330877.409 | 0 | 1330877.409 | 0 | 0 | 5646.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3295.3836 | 0 | 0 | 8942.1653 | 0 | 8942.1653 | 0 | 0 | 840.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.4574 | 0 | 0 | 1330.8774 | 0 | 1330.8774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6856 | 0.98369 | 0 | 0 | 2.6693 | 2.6693 | 0
AZ_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 45985.2786 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 27405.0032 | 0 | 0 | 0 | 0 | 98691.91 | 0 | 0 | 349671.5027 | 0 | 349669.2799 | 2.2229 | 2.2229 | 0 | 4722.6881 | 2914.084 | 740.5061 | 14583.8321 | 0 | 2814.4938 | 0 | 0 | 0 | 0 | 10135.6592 | 0 | 0 | 35911.2633 | 0 | 35911.035 | 0.22829 | 0.22829 | 0 | 156.9018 | 96.8146 | 24.6018 | 484.5184 | 0 | 93.5059 | 0 | 0 | 0 | 0 | 336.7368 | 0 | 0 | 1193.0792 | 0 | 1193.0716 | 0.0075844 | 0.0075844 | 2.8693 | 0.72914 | 14.3599 | 2.7713 | 0 | 0 | 4.6502 | 0 | 9.98 | 0 | 0 | 35.3597 | 35.3599 | 0.00022478
AZ_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 67020.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67020.1486 | 0 | 67020.1486 | 0 | 0 | 450.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450.3084 | 0 | 450.3084 | 0 | 0 | 67.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.0201 | 0 | 67.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9863 | 0 | 0 | 0 | 1.9863 | 1.9863 | 0
AZ_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 45057.2373 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 27007.6682 | 0 | 0 | 0 | 0 | 98577.9888 | 0 | 0 | 343039.064 | 0 | 343039.6198 | -0.55571 | -0.55571 | 0 | 4627.3783 | 2380.7485 | 740.5061 | 14583.8321 | 0 | 2773.6875 | 0 | 0 | 0 | 0 | 10123.9594 | 0 | 0 | 35230.1119 | 0 | 35230.1689 | -0.057072 | -0.057072 | 0 | 153.7353 | 79.0956 | 24.6018 | 484.5184 | 0 | 92.1502 | 0 | 0 | 0 | 0 | 336.3481 | 0 | 0 | 1170.4493 | 0 | 1170.4512 | -0.0018961 | -0.0018961 | 2.3442 | 0.72914 | 14.3599 | 2.7311 | 0 | 0 | 4.5563 | 0 | 9.9685 | 0 | 0 | 34.6893 | 34.6892 | -5.6196e-05
AZ_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 26320.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26320.8814 | 0 | 26320.8814 | 0 | 0 | 176.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.85 | 0 | 176.85 | 0 | 0 | 26.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3209 | 0 | 26.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78009 | 0 | 0 | 0 | 0.78009 | 0.78009 | 0
AZ_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 168878.5044 | 100820.2921 | 7124.245 | 317887.4784 | 4818.0346 | 107194.324 | 333.428 | 0 | 0 | 0 | 7179.8163 | 17435.5059 | 0 | 731671.6288 | 0 | 731673.8516 | -2.2229 | 4815.8118 | 0 | 17343.8224 | 10354.244 | 731.66 | 32647.044 | 494.8122 | 11008.8571 | 34.2431 | 0 | 0 | 0 | 737.3671 | 1790.6265 | 0 | 75142.6763 | 0 | 75142.9046 | -0.22829 | 494.5839 | 0 | 576.2135 | 343.9988 | 24.3079 | 1084.6321 | 16.4391 | 365.747 | 1.1377 | 0 | 0 | 0 | 24.4975 | 59.4899 | 0 | 2496.4636 | 0 | 2496.4712 | -0.0075844 | 16.4315 | 4.6512 | 0.32867 | 14.6653 | 4.9453 | 0.015382 | 0 | 7.791 | 0 | 0.33123 | 0 | 0.80436 | 33.7548 | 33.7547 | -0.00010255
AZ_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 206500.9159 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 103567.9767 | 0 | 0 | 652259.3075 | 0 | 652259.3075 | 0 | 0 | 1387.4797 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 695.8732 | 0 | 0 | 4382.5303 | 0 | 4382.5303 | 0 | 0 | 206.5009 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 103.568 | 0 | 0 | 652.2593 | 0 | 652.2593 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.7921 | 1.4003 | 0 | 0 | 8.8192 | 8.8192 | 0
AZ_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 170114.9666 | 80706.2479 | 7124.245 | 312483.1662 | 4745.7919 | 90920.259 | 536.2634 | 0 | 0 | 0 | 7179.8163 | 12403.5217 | 0 | 686214.2778 | 0 | 686215.3893 | -1.1114 | 4744.6805 | 0 | 17470.8071 | 8288.5317 | 731.66 | 32092.0212 | 487.3928 | 9337.5106 | 55.0742 | 0 | 0 | 0 | 737.3671 | 1273.8417 | 0 | 70474.2063 | 0 | 70474.3205 | -0.11414 | 487.2787 | 0 | 580.4323 | 275.3697 | 24.3079 | 1066.1926 | 16.1926 | 310.2199 | 1.8297 | 0 | 0 | 0 | 24.4975 | 42.3208 | 0 | 2341.3631 | 0 | 2341.3669 | -0.0037922 | 16.1888 | 3.7233 | 0.32867 | 14.416 | 4.1945 | 0.02474 | 0 | 7.848 | 0 | 0.33123 | 0 | 0.57222 | 31.6576 | 31.6576 | -5.1274e-05
AZ_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 321708.0869 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 103501.6295 | 0 | 0 | 767400.1312 | 0 | 767400.1312 | 0 | 0 | 2161.5566 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 695.4274 | 0 | 0 | 5156.1615 | 0 | 5156.1615 | 0 | 0 | 321.7081 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5016 | 0 | 0 | 767.4001 | 0 | 767.4001 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.3498 | 1.3994 | 0 | 0 | 10.376 | 10.376 | 0
AZ_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 61008.9886 | 86174.4671 | 10683.5889 | 53987.5506 | 0 | 43759.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255614.2419 | 0 | 255612.0191 | 2.2229 | 2.2229 | 0 | 6265.6231 | 8850.1178 | 1097.2046 | 5544.5215 | 0 | 4494.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26251.5826 | 0 | 26251.3544 | 0.22829 | 0.22829 | 0 | 208.1627 | 294.0273 | 36.4524 | 184.2055 | 0 | 149.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 872.1558 | 0 | 872.1482 | 0.0075844 | 0.0075844 | 11.9078 | 1.4763 | 7.4601 | 6.0468 | 0 | 0 | 8.4304 | 0 | 0 | 0 | 0 | 35.3211 | 35.3214 | 0.00030716
AZ_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 89322.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85862.7529 | 0 | 0 | 175185.0383 | 0 | 175185.0383 | 0 | 0 | 600.1564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.9118 | 0 | 0 | 1177.0683 | 0 | 1177.0683 | 0 | 0 | 89.3223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8628 | 0 | 0 | 175.185 | 0 | 175.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6175 | 3.4774 | 0 | 0 | 7.0948 | 7.0948 | 0
AZ_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 57524.666 | 68308.2833 | 10683.5889 | 53987.5506 | 0 | 41520.1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232024.2108 | 0 | 232023.933 | 0.27786 | 0.27786 | 0 | 5907.7832 | 7015.2607 | 1097.2046 | 5544.5215 | 0 | 4264.1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23828.8865 | 0 | 23828.8579 | 0.028536 | 0.028536 | 0 | 196.2742 | 233.0679 | 36.4524 | 184.2055 | 0 | 141.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 791.6666 | 0 | 791.6657 | 0.00094805 | 0.00094805 | 9.439 | 1.4763 | 7.4601 | 5.7374 | 0 | 0 | 7.9489 | 0 | 0 | 0 | 0 | 32.0616 | 32.0617 | 3.8395e-05
AZ_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 106458.8189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85881.7092 | 0 | 0 | 192340.5282 | 0 | 192340.5282 | 0 | 0 | 715.2968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.0392 | 0 | 0 | 1292.336 | 0 | 1292.336 | 0 | 0 | 106.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8817 | 0 | 0 | 192.3405 | 0 | 192.3405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3115 | 3.4781 | 0 | 0 | 7.7896 | 7.7896 | 0
AZ_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 6810.2669 | 93373.7334 | 80836.8405 | 12314.6075 | 154949.5496 | 0 | 48344.2817 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 396701.5224 | 0 | 396700.1331 | 1.3893 | 1.3893 | 699.4144 | 9589.4824 | 8301.9435 | 1264.7102 | 15913.3187 | 0 | 4964.9577 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 40741.2463 | 0 | 40741.1037 | 0.14268 | 0.14268 | 23.2366 | 318.5912 | 275.8153 | 42.0174 | 528.6879 | 0 | 164.9507 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1353.5456 | 0 | 1353.5409 | 0.0047402 | 0.0047402 | 6.3843 | 0.97258 | 12.2376 | 3.8181 | 0.0057056 | 0 | 7.3745 | 0.53786 | 0 | 0 | 0 | 31.3305 | 31.3306 | 0.00010972
AZ_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 16018.1093 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 504864.2671 | 0 | 0 | 920377.8144 | 0 | 920377.8144 | 0 | 0 | 107.6257 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3392.183 | 0 | 0 | 6184.0185 | 0 | 6184.0185 | 0 | 0 | 16.0181 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 504.8643 | 0 | 0 | 920.3778 | 0 | 920.3778 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.37077 | 11.6861 | 0 | 0 | 21.3041 | 21.3041 | 0
AZ_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 8285.6858 | 87758.2501 | 51773.033 | 12314.6075 | 154949.5496 | 0 | 45849.1288 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 361002.4976 | 0 | 360998.8855 | 3.6121 | 3.6121 | 850.9399 | 9012.7723 | 5317.0905 | 1264.7102 | 15913.3187 | 0 | 4708.7055 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 37074.9565 | 0 | 37074.5855 | 0.37097 | 0.37097 | 28.2708 | 299.4311 | 176.6496 | 42.0174 | 528.6879 | 0 | 156.4372 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.7405 | 0 | 1231.7282 | 0.012325 | 0.012325 | 4.0889 | 0.97258 | 12.2376 | 3.6211 | 0.0057056 | 0 | 6.931 | 0.65439 | 0 | 0 | 0 | 28.5109 | 28.5112 | 0.00028528
AZ_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 18624.6064 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 504902.1798 | 0 | 0 | 923022.2241 | 0 | 923022.2241 | 0 | 0 | 125.1387 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3392.4377 | 0 | 0 | 6201.7863 | 0 | 6201.7863 | 0 | 0 | 18.6246 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 504.9022 | 0 | 0 | 923.0222 | 0 | 923.0222 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.43111 | 11.687 | 0 | 0 | 21.3653 | 21.3653 | 0
AZ_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 939.1555 | 6896.4025 | 9094.2488 | 1592.1187 | 13417.6985 | 0 | 5998.9255 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42942.7481 | 0 | 42943.5816 | -0.83357 | -0.83357 | 96.4513 | 708.2605 | 933.9793 | 163.5106 | 1377.9976 | 0 | 616.0896 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4410.2202 | 0 | 4410.3058 | -0.085608 | -0.085608 | 3.2044 | 23.5305 | 31.0296 | 5.4323 | 45.7812 | 0 | 20.4683 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.5207 | 0 | 146.5235 | -0.0028441 | -0.0028441 | 5.6397 | 0.98733 | 8.3208 | 3.7202 | 0 | 0 | 4.2767 | 0.58241 | 3.1033 | 0 | 0 | 26.631 | 26.6304 | -0.00051693
AZ_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 454.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454.9522 | 0 | 454.9522 | 0 | 0 | 3.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0568 | 0 | 3.0568 | 0 | 0 | 0.45495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45495 | 0 | 0.45495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082689 | 0 | 0 | 0 | 0.082689 | 0.082689 | 0
AZ_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 972.4983 | 6554.6388 | 7304.8518 | 1592.1187 | 13417.6985 | 0 | 5537.6834 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40383.6882 | 0 | 40384.7996 | -1.1114 | -1.1114 | 99.8756 | 673.1614 | 750.2083 | 163.5106 | 1377.9976 | 0 | 568.7201 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4147.4048 | 0 | 4147.5189 | -0.11414 | -0.11414 | 3.3182 | 22.3644 | 24.9242 | 5.4323 | 45.7812 | 0 | 18.8946 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.7891 | 0 | 137.7929 | -0.0037922 | -0.0037922 | 4.53 | 0.98733 | 8.3208 | 3.4341 | 0 | 0 | 4.0648 | 0.60308 | 3.1033 | 0 | 0 | 25.0442 | 25.0435 | -0.00068924
AZ_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | AZ-KINGMAN-AZ | Zone3B | Zone3B(AZ-KINGMAN-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 511.8212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511.8212 | 0 | 511.8212 | 0 | 0 | 3.4389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4389 | 0 | 3.4389 | 0 | 0 | 0.51182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51182 | 0 | 0.51182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093025 | 0 | 0 | 0 | 0.093025 | 0.093025 | 0
AZ_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 682482.6628 | 878007.6217 | 95749.4079 | 4077910.5986 | 543457.0788 | 705536.4306 | 91248.1298 | 212338.0659 | 631904.4135 | 0 | 0 | 0 | 0 | 7918634.4096 | 0 | 7918633.2981 | 1.1114 | 543458.1903 | 0 | 70090.9695 | 90171.3827 | 9833.4642 | 418801.4185 | 55813.042 | 72458.5914 | 9371.1829 | 21807.1194 | 64896.5833 | 0 | 0 | 0 | 0 | 813243.7539 | 0 | 813243.6397 | 0.11414 | 55813.1561 | 0 | 2328.6308 | 2995.762 | 326.697 | 13913.831 | 1854.2756 | 2407.2903 | 311.3386 | 724.4975 | 2156.0579 | 0 | 0 | 0 | 0 | 27018.3806 | 0 | 27018.3768 | 0.0037922 | 1854.2793 | 6.0085 | 0.65524 | 27.9065 | 4.8282 | 0.62444 | 0 | 4.6705 | 0 | 0 | 4.3243 | 0 | 54.1898 | 54.1898 | 7.6059e-06
AZ_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 556880.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535763.1053 | 0 | 0 | 1092643.5759 | 0 | 1092643.5759 | 0 | 0 | 3741.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3599.7923 | 0 | 0 | 7341.4722 | 0 | 7341.4722 | 0 | 0 | 556.8805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535.7631 | 0 | 0 | 1092.6436 | 0 | 1092.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1169 | 1.0746 | 0 | 0 | 2.1915 | 2.1915 | 0
AZ_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 637192.0259 | 715111.3713 | 95749.4079 | 4077910.5986 | 543384.8361 | 688173.1674 | 89878.2965 | 189506.5834 | 632204.4987 | 0 | 0 | 0 | 0 | 7669110.7858 | 0 | 7669108.2851 | 2.5007 | 543387.3368 | 0 | 65439.6211 | 73441.9378 | 9833.4642 | 418801.4185 | 55805.6227 | 70675.3843 | 9230.501 | 19462.3261 | 64927.402 | 0 | 0 | 0 | 0 | 787617.6777 | 0 | 787617.4209 | 0.25682 | 55805.8795 | 0 | 2174.0992 | 2439.96 | 326.697 | 13913.831 | 1854.0291 | 2348.0468 | 306.6647 | 646.5965 | 2157.0817 | 0 | 0 | 0 | 0 | 26167.006 | 0 | 26166.9975 | 0.0085324 | 1854.0376 | 4.8937 | 0.65524 | 27.9065 | 4.7094 | 0.61507 | 0 | 4.3605 | 0 | 0 | 4.3264 | 0 | 52.4822 | 52.4822 | 1.7113e-05
AZ_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 973607.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535753.6271 | 0 | 0 | 1509360.8509 | 0 | 1509360.8509 | 0 | 0 | 6541.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3599.7286 | 0 | 0 | 10141.3956 | 0 | 10141.3956 | 0 | 0 | 973.6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535.7536 | 0 | 0 | 1509.3609 | 0 | 1509.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9527 | 1.0745 | 0 | 0 | 3.0273 | 3.0273 | 0
AZ_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 30147.4485 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 23226.0389 | 0 | 0 | 0 | 0 | 107616.6662 | 0 | 0 | 338582.2431 | 0 | 338581.4095 | 0.83357 | 0.83357 | 0 | 3096.143 | 2914.084 | 740.7914 | 14583.8321 | 0 | 2385.3142 | 0 | 0 | 0 | 0 | 11052.2316 | 0 | 0 | 34772.3964 | 0 | 34772.3108 | 0.085608 | 0.085608 | 0 | 102.8631 | 96.8146 | 24.6113 | 484.5184 | 0 | 79.2472 | 0 | 0 | 0 | 0 | 367.1881 | 0 | 0 | 1155.2426 | 0 | 1155.2398 | 0.0028441 | 0.0028441 | 2.8693 | 0.72942 | 14.3599 | 2.3487 | 0 | 0 | 3.0486 | 0 | 10.8825 | 0 | 0 | 34.2385 | 34.2385 | 8.4293e-05
AZ_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 75142.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75142.9413 | 0 | 75142.9413 | 0 | 0 | 504.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504.8854 | 0 | 504.8854 | 0 | 0 | 75.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1429 | 0 | 75.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2271 | 0 | 0 | 0 | 2.2271 | 2.2271 | 0
AZ_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 32798.2011 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 23601.1454 | 0 | 0 | 0 | 0 | 107488.8521 | 0 | 0 | 336287.147 | 0 | 336286.3134 | 0.83357 | 0.83357 | 0 | 3368.3753 | 2380.7485 | 740.7914 | 14583.8321 | 0 | 2423.8376 | 0 | 0 | 0 | 0 | 11039.1051 | 0 | 0 | 34536.69 | 0 | 34536.6044 | 0.085608 | 0.085608 | 0 | 111.9075 | 79.0956 | 24.6113 | 484.5184 | 0 | 80.5271 | 0 | 0 | 0 | 0 | 366.752 | 0 | 0 | 1147.4117 | 0 | 1147.4089 | 0.0028441 | 0.0028441 | 2.3442 | 0.72942 | 14.3599 | 2.3866 | 0 | 0 | 3.3167 | 0 | 10.8696 | 0 | 0 | 34.0064 | 34.0065 | 8.4293e-05
AZ_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 28614.5989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28614.5989 | 0 | 28614.5989 | 0 | 0 | 192.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.2615 | 0 | 192.2615 | 0 | 0 | 28.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6146 | 0 | 28.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84807 | 0 | 0 | 0 | 0.84807 | 0.84807 | 0
AZ_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 114557.5257 | 96555.1922 | 7121.4664 | 317887.4784 | 4818.0346 | 107249.8954 | 386.2208 | 0 | 0 | 0 | 7179.8163 | 17432.7274 | 0 | 673188.3572 | 0 | 673187.8015 | 0.55571 | 4818.5903 | 0 | 11765.0579 | 9916.2182 | 731.3746 | 32647.044 | 494.8122 | 11014.5643 | 39.6649 | 0 | 0 | 0 | 737.3671 | 1790.3411 | 0 | 69136.4443 | 0 | 69136.3872 | 0.057072 | 494.8692 | 0 | 390.8703 | 329.4463 | 24.2984 | 1084.6321 | 16.4391 | 365.9366 | 1.3178 | 0 | 0 | 0 | 24.4975 | 59.4805 | 0 | 2296.9187 | 0 | 2296.9168 | 0.0018961 | 16.441 | 4.4544 | 0.32854 | 14.6653 | 4.9478 | 0.017818 | 0 | 5.285 | 0 | 0.33123 | 0 | 0.80424 | 31.0566 | 31.0566 | 2.5637e-05
AZ_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 234878.5605 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111956.1582 | 0 | 0 | 689025.1336 | 0 | 689025.1336 | 0 | 0 | 1578.149 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 752.2334 | 0 | 0 | 4629.5599 | 0 | 4629.5599 | 0 | 0 | 234.8786 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9562 | 0 | 0 | 689.0251 | 0 | 689.0251 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.1758 | 1.5138 | 0 | 0 | 9.3163 | 9.3163 | 0
AZ_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 112620.8648 | 78066.6095 | 7121.4664 | 312483.1662 | 4743.0133 | 88330.6348 | 644.6275 | 0 | 0 | 0 | 7179.8163 | 12403.5217 | 0 | 623593.7205 | 0 | 623598.1662 | -4.4457 | 4738.5676 | 0 | 11566.1628 | 8017.4408 | 731.3746 | 32092.0212 | 487.1075 | 9071.5562 | 66.2032 | 0 | 0 | 0 | 737.3671 | 1273.8417 | 0 | 64043.0751 | 0 | 64043.5317 | -0.45657 | 486.6509 | 0 | 384.2624 | 266.3633 | 24.2984 | 1066.1926 | 16.1832 | 301.3841 | 2.1995 | 0 | 0 | 0 | 24.4975 | 42.3208 | 0 | 2127.7018 | 0 | 2127.7169 | -0.015169 | 16.168 | 3.6015 | 0.32854 | 14.416 | 4.075 | 0.029739 | 0 | 5.1956 | 0 | 0.33123 | 0 | 0.57222 | 28.7689 | 28.7687 | -0.0002051
AZ_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 388244.8487 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111908.7674 | 0 | 0 | 842344.0309 | 0 | 842344.0309 | 0 | 0 | 2608.6171 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 751.915 | 0 | 0 | 5659.7095 | 0 | 5659.7095 | 0 | 0 | 388.2448 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9088 | 0 | 0 | 842.344 | 0 | 842.344 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.2495 | 1.5131 | 0 | 0 | 11.3893 | 11.3893 | 0
AZ_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 39494.5468 | 85301.9971 | 10689.146 | 53987.5506 | 0 | 45296.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234769.4347 | 0 | 234768.6011 | 0.83357 | 0.83357 | 0 | 4056.09 | 8760.5151 | 1097.7753 | 5544.5215 | 0 | 4651.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24110.8209 | 0 | 24110.7353 | 0.085608 | 0.085608 | 0 | 134.7554 | 291.0504 | 36.4714 | 184.2055 | 0 | 154.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.0333 | 0 | 801.0305 | 0.0028441 | 0.0028441 | 11.7872 | 1.4771 | 7.4601 | 6.2591 | 0 | 0 | 5.4575 | 0 | 0 | 0 | 0 | 32.4409 | 32.441 | 0.00011518
AZ_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 110193.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88601.9444 | 0 | 0 | 198795.1627 | 0 | 198795.1627 | 0 | 0 | 740.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.3165 | 0 | 0 | 1335.7047 | 0 | 1335.7047 | 0 | 0 | 110.1932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6019 | 0 | 0 | 198.7952 | 0 | 198.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4627 | 3.5883 | 0 | 0 | 8.051 | 8.051 | 0
AZ_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 37566.2215 | 67613.6416 | 10689.146 | 53987.5506 | 0 | 42948.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212804.8651 | 0 | 212801.5308 | 3.3343 | 3.3343 | 0 | 3858.051 | 6943.921 | 1097.7753 | 5544.5215 | 0 | 4410.7909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21855.0596 | 0 | 21854.7172 | 0.34243 | 0.34243 | 0 | 128.1759 | 230.6977 | 36.4714 | 184.2055 | 0 | 146.5396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.0902 | 0 | 726.0788 | 0.011377 | 0.011377 | 9.343 | 1.4771 | 7.4601 | 5.9347 | 0 | 0 | 5.191 | 0 | 0 | 0 | 0 | 29.4054 | 29.4059 | 0.00046074
AZ_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 128106.9619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88611.4225 | 0 | 0 | 216718.3845 | 0 | 216718.3845 | 0 | 0 | 860.7507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.3801 | 0 | 0 | 1456.1308 | 0 | 1456.1308 | 0 | 0 | 128.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6114 | 0 | 0 | 216.7184 | 0 | 216.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1882 | 3.5887 | 0 | 0 | 8.7769 | 8.7769 | 0
AZ_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 7802.2152 | 74660.0868 | 79500.3499 | 12317.3861 | 154949.5496 | 0 | 48174.7891 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 377476.6195 | 0 | 377474.3966 | 2.2229 | 2.2229 | 801.2875 | 7667.5909 | 8164.6859 | 1264.9956 | 15913.3187 | 0 | 4947.5508 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 38766.8488 | 0 | 38766.6205 | 0.22829 | 0.22829 | 26.6212 | 254.7402 | 271.2552 | 42.0269 | 528.6879 | 0 | 164.3724 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.9502 | 0 | 1287.9426 | 0.0075844 | 0.0075844 | 6.2788 | 0.9728 | 12.2376 | 3.8047 | 0.0057056 | 0 | 5.8965 | 0.6162 | 0 | 0 | 0 | 29.8121 | 29.8123 | 0.00017556
AZ_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 21430.1451 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 555430.3105 | 0 | 0 | 976355.8935 | 0 | 976355.8935 | 0 | 0 | 143.9891 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.9363 | 0 | 0 | 6560.1352 | 0 | 6560.1352 | 0 | 0 | 21.4301 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 555.4303 | 0 | 0 | 976.3559 | 0 | 976.3559 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.49605 | 12.8566 | 0 | 0 | 22.5998 | 22.5998 | 0
AZ_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 9869.4689 | 69252.996 | 50983.9201 | 12317.3861 | 154949.5496 | 0 | 51111.7341 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348557.2975 | 0 | 348556.186 | 1.1114 | 1.1114 | 1013.5945 | 7112.2827 | 5236.0486 | 1264.9956 | 15913.3187 | 0 | 5249.1751 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 35796.8345 | 0 | 35796.7203 | 0.11414 | 0.11414 | 33.6746 | 236.2912 | 173.9571 | 42.0269 | 528.6879 | 0 | 174.3932 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.2775 | 0 | 1189.2737 | 0.0037922 | 0.0037922 | 4.0266 | 0.9728 | 12.2376 | 4.0367 | 0.0057056 | 0 | 5.4695 | 0.77947 | 0 | 0 | 0 | 27.5282 | 27.5283 | 8.7778e-05
AZ_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 16529.9306 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 555477.7013 | 0 | 0 | 971503.0698 | 0 | 971503.0698 | 0 | 0 | 111.0646 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 3732.2547 | 0 | 0 | 6527.5291 | 0 | 6527.5291 | 0 | 0 | 16.5299 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 555.4777 | 0 | 0 | 971.5031 | 0 | 971.5031 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.38262 | 12.8577 | 0 | 0 | 22.4875 | 22.4875 | 0
AZ_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 1114.2052 | 4940.2916 | 8863.6277 | 1589.3401 | 13417.6985 | 0 | 5723.8474 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40653.2091 | 0 | 40652.6534 | 0.55571 | 0.55571 | 114.4289 | 507.3679 | 910.2946 | 163.2252 | 1377.9976 | 0 | 587.8391 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4175.0846 | 0 | 4175.0275 | 0.057072 | 0.057072 | 3.8017 | 16.8563 | 30.2427 | 5.4228 | 45.7812 | 0 | 19.5298 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.7087 | 0 | 138.7069 | 0.0018961 | 0.0018961 | 5.4967 | 0.98561 | 8.3208 | 3.5496 | 0 | 0 | 3.0637 | 0.69096 | 3.1033 | 0 | 0 | 25.2103 | 25.2106 | 0.00034462
AZ_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 597.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597.1248 | 0 | 597.1248 | 0 | 0 | 4.0121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0121 | 0 | 4.0121 | 0 | 0 | 0.59712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59712 | 0 | 0.59712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10853 | 0 | 0 | 0 | 0.10853 | 0.10853 | 0
AZ_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 1153.1052 | 4645.7635 | 7135.3592 | 1589.3401 | 13417.6985 | 0 | 5254.2696 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38199.7347 | 0 | 38198.3455 | 1.3893 | 1.3893 | 118.4239 | 477.1199 | 732.8014 | 163.2252 | 1377.9976 | 0 | 539.6135 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 3923.1128 | 0 | 3922.9701 | 0.14268 | 0.14268 | 3.9344 | 15.8513 | 24.3458 | 5.4228 | 45.7812 | 0 | 17.9276 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.3375 | 0 | 130.3328 | 0.0047402 | 0.0047402 | 4.4249 | 0.98561 | 8.3208 | 3.2584 | 0 | 0 | 2.881 | 0.71508 | 3.1033 | 0 | 0 | 23.6883 | 23.6891 | 0.00086155
AZ_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | AZ-PRESCOTT-AZ | Zone4B | Zone4B(AZ-PRESCOTT-AZ) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 663.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.472 | 0 | 663.472 | 0 | 0 | 4.4579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4579 | 0 | 4.4579 | 0 | 0 | 0.66347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66347 | 0 | 0.66347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12059 | 0 | 0 | 0 | 0.12059 | 0.12059 | 0
AZ_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 548703.0127 | 879624.7475 | 95093.6661 | 4077910.5986 | 543457.0788 | 749076.5705 | 80333.9199 | 161759.8165 | 679517.9321 | 0 | 0 | 0 | 0 | 7815477.3429 | 0 | 7815477.065 | 0.27786 | 543457.3567 | 0 | 56351.7994 | 90337.4616 | 9766.1195 | 418801.4185 | 55813.042 | 76930.1638 | 8250.2936 | 16612.7332 | 69786.4916 | 0 | 0 | 0 | 0 | 802649.5231 | 0 | 802649.4946 | 0.028536 | 55813.0705 | 0 | 1872.1747 | 3001.2796 | 324.4596 | 13913.831 | 1854.2756 | 2555.8493 | 274.0993 | 551.9245 | 2318.5152 | 0 | 0 | 0 | 0 | 26666.4087 | 0 | 26666.4077 | 0.00094805 | 1854.2765 | 6.0196 | 0.65076 | 27.9065 | 5.1262 | 0.54975 | 0 | 3.755 | 0 | 0 | 4.6502 | 0 | 53.4839 | 53.4839 | 1.9015e-06
AZ_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 994260.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577609.2311 | 0 | 0 | 1571869.39 | 0 | 1571869.39 | 0 | 0 | 6680.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3880.9564 | 0 | 0 | 10561.3904 | 0 | 10561.3904 | 0 | 0 | 994.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6092 | 0 | 0 | 1571.8694 | 0 | 1571.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9942 | 1.1585 | 0 | 0 | 3.1526 | 3.1526 | 0
AZ_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 512903.9596 | 716553.4475 | 95093.6661 | 4077910.5986 | 543384.8361 | 718634.5939 | 77919.3455 | 144227.0608 | 680115.324 | 0 | 0 | 0 | 0 | 7566742.8321 | 0 | 7566744.2213 | -1.3893 | 543383.4468 | 0 | 52675.2367 | 73590.0391 | 9766.1195 | 418801.4185 | 55805.6227 | 73803.7728 | 8002.3168 | 14812.1191 | 69847.8438 | 0 | 0 | 0 | 0 | 777104.4889 | 0 | 777104.6315 | -0.14268 | 55805.48 | 0 | 1750.0283 | 2444.8804 | 324.4596 | 13913.831 | 1854.0291 | 2451.9812 | 265.8608 | 492.1027 | 2320.5535 | 0 | 0 | 0 | 0 | 25817.7265 | 0 | 25817.7313 | -0.0047402 | 1854.0243 | 4.9036 | 0.65076 | 27.9065 | 4.9179 | 0.53323 | 0 | 3.51 | 0 | 0 | 4.6543 | 0 | 51.7817 | 51.7817 | -9.5073e-06
AZ_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 1500119.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577552.3621 | 0 | 0 | 2077671.9961 | 0 | 2077671.9961 | 0 | 0 | 10079.3038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3880.5743 | 0 | 0 | 13959.8781 | 0 | 13959.8781 | 0 | 0 | 1500.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5524 | 0 | 0 | 2077.672 | 0 | 2077.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0087 | 1.1584 | 0 | 0 | 4.1671 | 4.1671 | 0
AZ_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 22056.2623 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 21317.1636 | 0 | 0 | 0 | 0 | 115830.1093 | 0 | 0 | 336792.8461 | 0 | 336794.7911 | -1.945 | -1.945 | 0 | 2265.1781 | 2914.084 | 740.5061 | 14583.8321 | 0 | 2189.2727 | 0 | 0 | 0 | 0 | 11895.7522 | 0 | 0 | 34588.6253 | 0 | 34588.825 | -0.19975 | -0.19975 | 0 | 75.256 | 96.8146 | 24.6018 | 484.5184 | 0 | 72.7342 | 0 | 0 | 0 | 0 | 395.2123 | 0 | 0 | 1149.1372 | 0 | 1149.1438 | -0.0066363 | -0.0066363 | 2.8693 | 0.72914 | 14.3599 | 2.1557 | 0 | 0 | 2.2304 | 0 | 11.7131 | 0 | 0 | 34.0578 | 34.0576 | -0.00019668
AZ_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 129433.9059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129433.9059 | 0 | 129433.9059 | 0 | 0 | 869.6664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.6664 | 0 | 869.6664 | 0 | 0 | 129.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4339 | 0 | 129.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8361 | 0 | 0 | 0 | 3.8361 | 3.8361 | 0
AZ_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 26110.1911 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21742.2843 | 0 | 0 | 0 | 0 | 115680.0667 | 0 | 0 | 335928.7119 | 0 | 335931.4905 | -2.7786 | -2.7786 | 0 | 2681.5166 | 2380.7485 | 740.5061 | 14583.8321 | 0 | 2232.9326 | 0 | 0 | 0 | 0 | 11880.3428 | 0 | 0 | 34499.8787 | 0 | 34500.1641 | -0.28536 | -0.28536 | 0 | 89.088 | 79.0956 | 24.6018 | 484.5184 | 0 | 74.1847 | 0 | 0 | 0 | 0 | 394.7004 | 0 | 0 | 1146.1888 | 0 | 1146.1982 | -0.0094805 | -0.0094805 | 2.3442 | 0.72914 | 14.3599 | 2.1987 | 0 | 0 | 2.6403 | 0 | 11.6979 | 0 | 0 | 33.9705 | 33.9702 | -0.00028098
AZ_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 52319.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52319.505 | 0 | 52319.505 | 0 | 0 | 351.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351.5348 | 0 | 351.5348 | 0 | 0 | 52.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.3195 | 0 | 52.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5506 | 0 | 0 | 0 | 1.5506 | 1.5506 | 0
AZ_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 78619.5443 | 97049.7771 | 7102.0164 | 317887.4784 | 4818.0346 | 104126.7864 | 614.0632 | 0 | 0 | 0 | 7179.8163 | 17443.8416 | 0 | 634841.3585 | 0 | 634839.9692 | 1.3893 | 4819.4239 | 0 | 8074.2272 | 9967.0121 | 729.3771 | 32647.044 | 494.8122 | 10693.821 | 63.0643 | 0 | 0 | 0 | 737.3671 | 1791.4825 | 0 | 65198.2075 | 0 | 65198.0648 | 0.14268 | 494.9548 | 0 | 268.2499 | 331.1338 | 24.2321 | 1084.6321 | 16.4391 | 355.2806 | 2.0952 | 0 | 0 | 0 | 24.4975 | 59.5184 | 0 | 2166.0787 | 0 | 2166.074 | 0.0047402 | 16.4439 | 4.4773 | 0.32764 | 14.6653 | 4.8038 | 0.028329 | 0 | 3.627 | 0 | 0.33123 | 0 | 0.80475 | 29.2875 | 29.2876 | 6.4093e-05
AZ_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 391931.8573 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120012.6037 | 0 | 0 | 854134.8759 | 0 | 854134.8759 | 0 | 0 | 2633.3901 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 806.3647 | 0 | 0 | 5738.9322 | 0 | 5738.9322 | 0 | 0 | 391.9319 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0126 | 0 | 0 | 854.1349 | 0 | 854.1349 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.2993 | 1.6227 | 0 | 0 | 11.5488 | 11.5488 | 0
AZ_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 75535.3353 | 78847.3867 | 7102.0164 | 312483.1662 | 4743.0133 | 82976.3368 | 1005.8411 | 0 | 0 | 0 | 7179.8163 | 12411.8574 | 0 | 582284.7697 | 0 | 582285.3254 | -0.55571 | 4742.4576 | 0 | 7757.4789 | 8097.6266 | 729.3771 | 32092.0212 | 487.1075 | 8521.6698 | 103.2999 | 0 | 0 | 0 | 737.3671 | 1274.6978 | 0 | 59800.6458 | 0 | 59800.7029 | -0.057072 | 487.0504 | 0 | 257.7266 | 269.0273 | 24.2321 | 1066.1926 | 16.1832 | 283.1153 | 3.4319 | 0 | 0 | 0 | 24.4975 | 42.3493 | 0 | 1986.7556 | 0 | 1986.7575 | -0.0018961 | 16.1813 | 3.6375 | 0.32764 | 14.416 | 3.828 | 0.046403 | 0 | 3.4847 | 0 | 0.33123 | 0 | 0.5726 | 26.863 | 26.8629 | -2.5637e-05
AZ_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 632620.5367 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119927.3002 | 0 | 0 | 1094738.2518 | 0 | 1094738.2518 | 0 | 0 | 4250.5774 | 0 | 0 | 0 | 2299.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 805.7915 | 0 | 0 | 7355.5463 | 0 | 7355.5463 | 0 | 0 | 632.6205 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.9273 | 0 | 0 | 1094.7383 | 0 | 1094.7383 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.5537 | 1.6215 | 0 | 0 | 14.802 | 14.802 | 0
AZ_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 27894.0309 | 84726.8338 | 10686.3675 | 53987.5506 | 0 | 46713.2631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224008.0459 | 0 | 224003.6002 | 4.4457 | 4.4457 | 0 | 2864.717 | 8701.4458 | 1097.4899 | 5544.5215 | 0 | 4797.4521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23005.6263 | 0 | 23005.1697 | 0.45657 | 0.45657 | 0 | 95.1744 | 289.088 | 36.4619 | 184.2055 | 0 | 159.3857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.3155 | 0 | 764.3003 | 0.015169 | 0.015169 | 11.7078 | 1.4767 | 7.4601 | 6.455 | 0 | 0 | 3.8545 | 0 | 0 | 0 | 0 | 30.9534 | 30.954 | 0.00061432
AZ_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 189819.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91085.2252 | 0 | 0 | 280904.5599 | 0 | 280904.5599 | 0 | 0 | 1275.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612.0016 | 0 | 0 | 1887.3977 | 0 | 1887.3977 | 0 | 0 | 189.8193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0852 | 0 | 0 | 280.9046 | 0 | 280.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6875 | 3.6889 | 0 | 0 | 11.3763 | 11.3763 | 0
AZ_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 0 | 25287.7354 | 67269.0994 | 10686.3675 | 53987.5506 | 0 | 48247.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205477.7847 | 0 | 205474.4504 | 3.3343 | 3.3343 | 0 | 2597.0504 | 6908.5365 | 1097.4899 | 5544.5215 | 0 | 4954.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21102.5685 | 0 | 21102.2261 | 0.34243 | 0.34243 | 0 | 86.2818 | 229.5222 | 36.4619 | 184.2055 | 0 | 164.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 701.0902 | 0 | 701.0788 | 0.011377 | 0.011377 | 9.2954 | 1.4767 | 7.4601 | 6.6669 | 0 | 0 | 3.4943 | 0 | 0 | 0 | 0 | 28.393 | 28.3934 | 0.00046074
AZ_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 211107.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91094.7034 | 0 | 0 | 302202.0105 | 0 | 302202.0105 | 0 | 0 | 1418.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612.0653 | 0 | 0 | 2030.4953 | 0 | 2030.4953 | 0 | 0 | 211.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0947 | 0 | 0 | 302.202 | 0 | 302.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5496 | 3.6892 | 0 | 0 | 12.2389 | 12.2389 | 0
AZ_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 14856.9961 | 62356.5935 | 79450.3357 | 12314.6075 | 154949.5496 | 0 | 54282.0787 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378282.4038 | 0 | 378285.1824 | -2.7786 | -2.7786 | 1525.8135 | 6404.0222 | 8159.5495 | 1264.7102 | 15913.3187 | 0 | 5574.7695 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 38849.6029 | 0 | 38849.8882 | -0.28536 | -0.28536 | 50.6921 | 212.7607 | 271.0845 | 42.0174 | 528.6879 | 0 | 185.2105 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.6996 | 0 | 1290.709 | -0.0094805 | -0.0094805 | 6.2748 | 0.97258 | 12.2376 | 4.2871 | 0.0057056 | 0 | 4.9248 | 1.1734 | 0 | 0 | 0 | 29.8761 | 29.8759 | -0.00021945
AZ_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 28140.6903 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 603484.6385 | 0 | 0 | 1031120.7667 | 0 | 1031120.7667 | 0 | 0 | 189.0773 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.8133 | 0 | 0 | 6928.1004 | 0 | 6928.1004 | 0 | 0 | 28.1407 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 603.4846 | 0 | 0 | 1031.1208 | 0 | 1031.1208 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.65137 | 13.9689 | 0 | 0 | 23.8674 | 23.8674 | 0
AZ_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 18030.1192 | 57588.5731 | 50967.2487 | 12314.6075 | 154949.5496 | 0 | 51189.534 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 345111.8748 | 0 | 345110.7634 | 1.1114 | 1.1114 | 1851.6932 | 5914.3465 | 5234.3364 | 1264.7102 | 15913.3187 | 0 | 5257.1651 | 7.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 35442.9895 | 0 | 35442.8754 | 0.11414 | 0.11414 | 61.5188 | 196.4922 | 173.9003 | 42.0174 | 528.6879 | 0 | 174.6587 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.5217 | 0 | 1177.5179 | 0.0037922 | 0.0037922 | 4.0253 | 0.97258 | 12.2376 | 4.0428 | 0.0057056 | 0 | 4.5482 | 1.424 | 0 | 0 | 0 | 27.2561 | 27.2562 | 8.7778e-05
AZ_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 31628.6573 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 603550.9857 | 0 | 0 | 1034675.0809 | 0 | 1034675.0809 | 0 | 0 | 212.5129 | 0 | 0 | 0 | 2684.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 4055.2591 | 0 | 0 | 6951.9819 | 0 | 6951.9819 | 0 | 0 | 31.6287 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 603.551 | 0 | 0 | 1034.6751 | 0 | 1034.6751 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.73211 | 13.9704 | 0 | 0 | 23.9497 | 23.9497 | 0
AZ_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 1995.0109 | 3570.4582 | 8841.3992 | 1578.2259 | 13417.6985 | 0 | 5704.3974 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40111.3886 | 0 | 40107.4986 | 3.89 | 3.89 | 204.8876 | 366.6861 | 908.0117 | 162.0838 | 1377.9976 | 0 | 585.8416 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 4119.4396 | 0 | 4119.0401 | 0.3995 | 0.3995 | 6.807 | 12.1824 | 30.1669 | 5.3849 | 45.7812 | 0 | 19.4634 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.8601 | 0 | 136.8468 | 0.013273 | 0.013273 | 5.4829 | 0.97872 | 8.3208 | 3.5375 | 0 | 0 | 2.2142 | 1.2372 | 3.1033 | 0 | 0 | 24.8722 | 24.8746 | 0.0024123
AZ_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 2701.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2701.2788 | 0 | 2701.2788 | 0 | 0 | 18.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1499 | 0 | 18.1499 | 0 | 0 | 2.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7013 | 0 | 2.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49096 | 0 | 0 | 0 | 0.49096 | 0.49096 | 0
AZ_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Electricity | 2045.0251 | 3328.7229 | 7124.245 | 1578.2259 | 13417.6985 | 0 | 5201.4768 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37699.5927 | 0 | 37699.5927 | 0 | 0 | 210.0241 | 341.8598 | 731.66 | 162.0838 | 1377.9976 | 0 | 534.1917 | 0 | 0 | 0 | 0 | 513.9312 | 0 | 0 | 3871.7482 | 0 | 3871.7482 | 0 | 0 | 6.9776 | 11.3576 | 24.3079 | 5.3849 | 45.7812 | 0 | 17.7474 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.631 | 0 | 128.631 | 0 | 0 | 4.418 | 0.97872 | 8.3208 | 3.2256 | 0 | 0 | 2.0643 | 1.2682 | 3.1033 | 0 | 0 | 23.379 | 23.379 | 0
AZ_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | AZ-GALLUP-NM | Zone5B | Zone5B(AZ-GALLUP-NM) |  |  | AZ | 0.1027 | 0.006719 |  |  |  | Natural Gas | 2919.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.2767 | 0 | 2919.2767 | 0 | 0 | 19.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6146 | 0 | 19.6146 | 0 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9193 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53058 | 0 | 0 | 0 | 0.53058 | 0.53058 | 0
CA_2B_LO_2016_EL | 2B | LO | EL |  |  | OfficeLarge | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 1057728.0932 | 880552.7887 | 95388.1942 | 4077910.5986 | 543457.0788 | 646625.2598 | 127491.7537 | 352841.8473 | 458057.8319 | 0 | 0 | 0 | 0 | 8240053.4462 | 0 | 8240051.2234 | 2.2229 | 543459.3017 | 0 | 187429.4181 | 156033.9542 | 16902.788 | 722605.7581 | 96300.5944 | 114581.996 | 22591.5387 | 62523.5753 | 81167.8478 | 0 | 0 | 0 | 0 | 1460137.4707 | 0 | 1460137.0768 | 0.39389 | 96300.9883 | 0 | 3608.9683 | 3004.4461 | 325.4645 | 13913.831 | 1854.2756 | 2206.2854 | 435.0019 | 1203.8964 | 1562.8933 | 0 | 0 | 0 | 0 | 28115.0624 | 0 | 28115.0548 | 0.0075844 | 1854.2831 | 6.0259 | 0.65277 | 27.9065 | 4.4251 | 0.87247 | 0 | 7.2384 | 0 | 0 | 3.1346 | 0 | 56.3894 | 56.3894 | 1.5212e-05
CA_2B_LO_2016_NG | 2B | LO | NG |  |  | OfficeLarge | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 220348.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459094.1784 | 0 | 0 | 679442.7025 | 0 | 679442.7025 | 0 | 0 | 2097.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4370.5766 | 0 | 0 | 6468.2945 | 0 | 6468.2945 | 0 | 0 | 220.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0942 | 0 | 0 | 679.4427 | 0 | 679.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44195 | 0.92079 | 0 | 0 | 1.3627 | 1.3627 | 0
CA_2B_LO_2019_EL | 2B | LO | EL |  |  | OfficeLarge | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 998783.5796 | 716345.055 | 95388.1942 | 4077910.5986 | 543384.8361 | 632590.7194 | 122851.5473 | 316075.853 | 457863.3322 | 0 | 0 | 0 | 0 | 7961193.7154 | 0 | 7961193.9933 | -0.27786 | 543384.5583 | 0 | 176984.4503 | 126936.3437 | 16902.788 | 722605.7581 | 96287.793 | 112095.0755 | 21769.2942 | 56008.6411 | 81133.3825 | 0 | 0 | 0 | 0 | 1410723.5264 | 0 | 1410723.5756 | -0.049236 | 96287.7437 | 0 | 3407.8496 | 2444.1693 | 325.4645 | 13913.831 | 1854.0291 | 2158.3995 | 419.1695 | 1078.4508 | 1562.2297 | 0 | 0 | 0 | 0 | 27163.593 | 0 | 27163.5939 | -0.00094805 | 1854.0281 | 4.9022 | 0.65277 | 27.9065 | 4.329 | 0.84071 | 0 | 6.835 | 0 | 0 | 3.1333 | 0 | 54.481 | 54.481 | -1.9015e-06
CA_2B_LO_2019_NG | 2B | LO | NG |  |  | OfficeLarge | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 344171.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459141.5693 | 0 | 0 | 803312.9219 | 0 | 803312.9219 | 0 | 0 | 3276.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4371.0277 | 0 | 0 | 7647.539 | 0 | 7647.539 | 0 | 0 | 344.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.1416 | 0 | 0 | 803.3129 | 0 | 803.3129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69029 | 0.92088 | 0 | 0 | 1.6112 | 1.6112 | 0
CA_2B_MA_2016_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 54987.8346 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 27674.5242 | 0 | 0 | 0 | 0 | 92345.6637 | 0 | 0 | 352602.8906 | 0 | 352602.3348 | 0.55571 | 0.55571 | 0 | 9743.8443 | 5028.0009 | 1278.6642 | 25163.1456 | 0 | 4903.9257 | 0 | 0 | 0 | 0 | 16363.6516 | 0 | 0 | 62481.2322 | 0 | 62481.1337 | 0.098472 | 0.098472 | 0 | 187.6185 | 96.8146 | 24.6208 | 484.5184 | 0 | 94.4255 | 0 | 0 | 0 | 0 | 315.0834 | 0 | 0 | 1203.0811 | 0 | 1203.0792 | 0.0018961 | 0.0018961 | 2.8693 | 0.7297 | 14.3599 | 2.7985 | 0 | 0 | 5.5605 | 0 | 9.3383 | 0 | 0 | 35.6563 | 35.6564 | 5.6196e-05
CA_2B_MA_2016_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 19989.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19989.4631 | 0 | 19989.4631 | 0 | 0 | 190.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.2997 | 0 | 190.2997 | 0 | 0 | 19.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9895 | 0 | 19.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59244 | 0 | 0 | 0 | 0.59244 | 0.59244 | 0
CA_2B_MA_2019_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 52734.4171 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 27824.5668 | 0 | 0 | 0 | 0 | 92259.5281 | 0 | 0 | 345220.2389 | 0 | 345220.2389 | 0 | 0 | 0 | 9344.5387 | 4107.7763 | 1278.6642 | 25163.1456 | 0 | 4930.5132 | 0 | 0 | 0 | 0 | 16348.3884 | 0 | 0 | 61173.0263 | 0 | 61173.0263 | 0 | 0 | 0 | 179.9298 | 79.0956 | 24.6208 | 484.5184 | 0 | 94.9374 | 0 | 0 | 0 | 0 | 314.7895 | 0 | 0 | 1177.8915 | 0 | 1177.8915 | 0 | 0 | 2.3442 | 0.7297 | 14.3599 | 2.8137 | 0 | 0 | 5.3327 | 0 | 9.3296 | 0 | 0 | 34.9098 | 34.9098 | 0
CA_2B_MA_2019_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 7743.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7743.6659 | 0 | 7743.6659 | 0 | 0 | 73.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7197 | 0 | 73.7197 | 0 | 0 | 7.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7437 | 0 | 7.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2295 | 0 | 0 | 0 | 0.2295 | 0.2295 | 0
CA_2B_PS_2016_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 212966.0219 | 100420.1785 | 7115.9093 | 317887.4784 | 4818.0346 | 111926.2231 | 155.5997 | 0 | 0 | 16724.1929 | 7179.8163 | 17474.4059 | 0 | 796667.8606 | 0 | 796670.0835 | -2.2229 | 4815.8118 | 0 | 37737.5791 | 17794.4556 | 1260.9391 | 56329.6612 | 853.7557 | 19833.3267 | 27.5723 | 0 | 0 | 2963.527 | 1272.2634 | 3096.4647 | 0 | 141169.5449 | 0 | 141169.9388 | -0.39389 | 853.3618 | 0 | 726.6401 | 342.6336 | 24.2795 | 1084.6321 | 16.4391 | 381.8923 | 0.53091 | 0 | 0 | 57.0629 | 24.4975 | 59.6227 | 0 | 2718.2307 | 0 | 2718.2383 | -0.0075844 | 16.4315 | 4.6328 | 0.32828 | 14.6653 | 5.1636 | 0.0071784 | 0.77155 | 9.8249 | 0 | 0.33123 | 0 | 0.80616 | 36.7533 | 36.7532 | -0.00010255
CA_2B_PS_2016_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 72365.8371 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96705.7808 | 0 | 0 | 511262.0327 | 0 | 511262.0327 | 0 | 0 | 688.9228 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 920.639 | 0 | 0 | 4867.2146 | 0 | 4867.2146 | 0 | 0 | 72.3658 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7058 | 0 | 0 | 511.262 | 0 | 511.262 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.97846 | 1.3076 | 0 | 0 | 6.9128 | 6.9128 | 0
CA_2B_PS_2019_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 193932.8402 | 80547.8696 | 7115.9093 | 312483.1662 | 4745.7919 | 93054.1982 | 158.3783 | 0 | 0 | 19738.9377 | 7179.8163 | 12417.4145 | 0 | 731374.3221 | 0 | 731373.4886 | 0.83357 | 4746.6255 | 0 | 34364.8993 | 14273.0825 | 1260.9391 | 55372.0171 | 840.9543 | 16489.2039 | 28.0646 | 0 | 0 | 3497.7398 | 1272.2634 | 2200.3659 | 0 | 129599.5299 | 0 | 129599.3822 | 0.14771 | 841.102 | 0 | 661.6989 | 274.8293 | 24.2795 | 1066.1926 | 16.1926 | 317.5009 | 0.54039 | 0 | 0 | 67.3493 | 24.4975 | 42.3682 | 0 | 2495.4492 | 0 | 2495.4463 | 0.0028441 | 16.1955 | 3.716 | 0.32828 | 14.416 | 4.2929 | 0.0073066 | 0.91063 | 8.9468 | 0 | 0.33123 | 0 | 0.57286 | 33.7409 | 33.741 | 3.8456e-05
CA_2B_PS_2019_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 55523.1269 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96658.3899 | 0 | 0 | 494371.9316 | 0 | 494371.9316 | 0 | 0 | 528.5802 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 920.1879 | 0 | 0 | 4706.4208 | 0 | 4706.4208 | 0 | 0 | 55.5231 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6584 | 0 | 0 | 494.3719 | 0 | 494.3719 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.75073 | 1.3069 | 0 | 0 | 6.6844 | 6.6844 | 0
CA_2B_RS_2016_EL | 2B | RS | EL |  |  | RetailStandalone | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 76996.8613 | 84946.3406 | 10697.4817 | 53987.5506 | 0 | 40769.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267398.1432 | 0 | 267397.5875 | 0.55571 | 0.55571 | 0 | 13643.8438 | 15052.4916 | 1895.5938 | 9566.594 | 0 | 7224.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47382.951 | 0 | 47382.8525 | 0.098472 | 0.098472 | 0 | 262.7133 | 289.8369 | 36.4998 | 184.2055 | 0 | 139.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912.3625 | 0 | 912.3606 | 0.0018961 | 0.0018961 | 11.7381 | 1.4782 | 7.4601 | 5.6337 | 0 | 0 | 10.6396 | 0 | 0 | 0 | 0 | 36.9496 | 36.9497 | 7.679e-05
CA_2B_RS_2016_NG | 2B | RS | NG |  |  | RetailStandalone | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 25998.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83919.7278 | 0 | 0 | 109918.3514 | 0 | 109918.3514 | 0 | 0 | 247.5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798.9158 | 0 | 0 | 1046.4227 | 0 | 1046.4227 | 0 | 0 | 25.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9197 | 0 | 0 | 109.9184 | 0 | 109.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0529 | 3.3987 | 0 | 0 | 4.4516 | 4.4516 | 0
CA_2B_RS_2019_EL | 2B | RS | EL |  |  | RetailStandalone | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 72259.4051 | 67171.8495 | 10697.4817 | 53987.5506 | 0 | 41861.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245978.1727 | 0 | 245978.1727 | 0 | 0 | 0 | 12804.3666 | 11902.8517 | 1895.5938 | 9566.594 | 0 | 7417.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43587.3322 | 0 | 43587.3322 | 0 | 0 | 0 | 246.5491 | 229.1904 | 36.4998 | 184.2055 | 0 | 142.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839.2775 | 0 | 839.2775 | 0 | 0 | 9.282 | 1.4782 | 7.4601 | 5.7846 | 0 | 0 | 9.985 | 0 | 0 | 0 | 0 | 33.9899 | 33.9899 | 0
CA_2B_RS_2019_NG | 2B | RS | NG |  |  | RetailStandalone | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 30823.0127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83929.206 | 0 | 0 | 114752.2187 | 0 | 114752.2187 | 0 | 0 | 293.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.006 | 0 | 0 | 1092.4411 | 0 | 1092.4411 | 0 | 0 | 30.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9292 | 0 | 0 | 114.7522 | 0 | 114.7522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2483 | 3.399 | 0 | 0 | 4.6473 | 4.6473 | 0
CA_2B_SH_2016_EL | 2B | SH | EL |  |  | HotelSmall | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 2764.6738 | 111067.646 | 80533.9767 | 12325.7218 | 154949.5496 | 0 | 48483.21 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 410197.0208 | 0 | 410193.6865 | 3.3343 | 3.3343 | 489.9002 | 19681.1869 | 14270.6207 | 2184.1179 | 27457.0602 | 0 | 8591.2248 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 72686.9121 | 0 | 72686.3212 | 0.59083 | 0.59083 | 9.4331 | 378.9628 | 274.7819 | 42.0554 | 528.6879 | 0 | 165.4247 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.5922 | 0 | 1399.5809 | 0.011377 | 0.011377 | 6.3604 | 0.97346 | 12.2376 | 3.8291 | 0.0057056 | 0 | 8.7719 | 0.21835 | 0 | 0 | 0 | 32.3962 | 32.3965 | 0.00026333
CA_2B_SH_2016_NG | 2B | SH | NG |  |  | HotelSmall | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 5004.4744 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 472211.9674 | 0 | 0 | 876711.8797 | 0 | 876711.8797 | 0 | 0 | 47.6426 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 4495.4579 | 0 | 0 | 8346.2971 | 0 | 8346.2971 | 0 | 0 | 5.0045 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 472.212 | 0 | 0 | 876.7119 | 0 | 876.7119 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.11584 | 10.9303 | 0 | 0 | 20.2933 | 20.2933 | 0
CA_2B_SH_2019_EL | 2B | SH | EL |  |  | HotelSmall | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 3320.3872 | 104949.2422 | 51592.4262 | 12325.7218 | 154949.5496 | 0 | 46063.0785 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373272.6481 | 0 | 373269.8695 | 2.7786 | 2.7786 | 588.3726 | 18597.0057 | 9142.1779 | 2184.1179 | 27457.0602 | 0 | 8162.3775 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 66143.9132 | 0 | 66143.4209 | 0.49236 | 0.49236 | 11.3292 | 358.0868 | 176.0334 | 42.0554 | 528.6879 | 0 | 157.1672 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.6063 | 0 | 1273.5968 | 0.0094805 | 0.0094805 | 4.0747 | 0.97346 | 12.2376 | 3.638 | 0.0057056 | 0 | 8.2887 | 0.26224 | 0 | 0 | 0 | 29.48 | 29.4803 | 0.00021945
CA_2B_SH_2019_NG | 2B | SH | NG |  |  | HotelSmall | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 5961.7697 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 472230.9237 | 0 | 0 | 877688.1313 | 0 | 877688.1313 | 0 | 0 | 56.756 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 4495.6384 | 0 | 0 | 8355.591 | 0 | 8355.591 | 0 | 0 | 5.9618 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 472.2309 | 0 | 0 | 877.6881 | 0 | 877.6881 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.138 | 10.9308 | 0 | 0 | 20.3159 | 20.3159 | 0
CA_2B_SO_2016_EL | 2B | SO | EL |  |  | OfficeSmall | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 263.9638 | 8702.4708 | 9041.456 | 1581.0044 | 13417.6985 | 0 | 6123.961 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 44134.7532 | 0 | 44132.5303 | 2.2229 | 2.2229 | 46.7744 | 1542.0778 | 1602.146 | 280.154 | 2377.6162 | 0 | 1085.1659 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 7820.6783 | 0 | 7820.2844 | 0.39389 | 0.39389 | 0.90064 | 29.6928 | 30.8494 | 5.3944 | 45.7812 | 0 | 20.895 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 150.5878 | 0 | 150.5802 | 0.0075844 | 0.0075844 | 5.607 | 0.98044 | 8.3208 | 3.7977 | 0 | 0 | 5.3967 | 0.16369 | 3.1033 | 0 | 0 | 27.3683 | 27.3696 | 0.0013785
CA_2B_SO_2016_NG | 2B | SO | NG |  |  | OfficeSmall | STD2016 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 47.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3909 | 0 | 47.3909 | 0 | 0 | 0.45116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45116 | 0 | 0.45116 | 0 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047391 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086134 | 0 | 0 | 0 | 0.0086134 | 0.0086134 | 0
CA_2B_SO_2019_EL | 2B | SO | EL |  |  | OfficeSmall | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 252.8496 | 8313.4715 | 7260.3947 | 1581.0044 | 13417.6985 | 0 | 5629.3761 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41458.9935 | 0 | 41463.4392 | -4.4457 | -4.4457 | 44.8049 | 1473.1472 | 1286.5419 | 280.154 | 2377.6162 | 0 | 997.5254 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 7346.5336 | 0 | 7347.3214 | -0.78778 | -0.78778 | 0.86272 | 28.3656 | 24.7725 | 5.3944 | 45.7812 | 0 | 19.2074 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.4581 | 0 | 141.4733 | -0.015169 | -0.015169 | 4.5024 | 0.98044 | 8.3208 | 3.491 | 0 | 0 | 5.1555 | 0.1568 | 3.1033 | 0 | 0 | 25.7131 | 25.7103 | -0.002757
CA_2B_SO_2019_NG | 2B | SO | NG |  |  | OfficeSmall | STD2019 | CA-TUCSON-AZ | Zone2B | Zone2B(CA-TUCSON-AZ) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 47.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3909 | 0 | 47.3909 | 0 | 0 | 0.45116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45116 | 0 | 0.45116 | 0 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047391 | 0 | 0.047391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086134 | 0 | 0 | 0 | 0.0086134 | 0.0086134 | 0
CA_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 664244.1511 | 881792.0295 | 94529.6171 | 4077910.5986 | 543457.0788 | 568152.9795 | 102456.8678 | 297362.2063 | 109861.7481 | 0 | 0 | 0 | 0 | 7339767.2769 | 0 | 7339768.3883 | -1.1114 | 543455.9674 | 0 | 117704.0636 | 156253.5476 | 16750.6482 | 722605.7581 | 96300.5944 | 100676.708 | 18155.357 | 52692.583 | 19467.5018 | 0 | 0 | 0 | 0 | 1300606.7615 | 0 | 1300606.9584 | -0.19694 | 96300.3974 | 0 | 2266.401 | 3008.6744 | 322.5351 | 13913.831 | 1854.2756 | 1938.538 | 349.5828 | 1014.5998 | 374.8483 | 0 | 0 | 0 | 0 | 25043.2859 | 0 | 25043.2897 | -0.0037922 | 1854.2718 | 6.0344 | 0.6469 | 27.9065 | 3.8881 | 0.70115 | 0 | 4.5456 | 0 | 0 | 0.75182 | 0 | 50.2284 | 50.2284 | -7.6059e-06
CA_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 25098.1973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498475.9798 | 0 | 0 | 523574.1771 | 0 | 523574.1771 | 0 | 0 | 238.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4745.4913 | 0 | 0 | 4984.4262 | 0 | 4984.4262 | 0 | 0 | 25.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498.476 | 0 | 0 | 523.5742 | 0 | 523.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050339 | 0.99978 | 0 | 0 | 1.0501 | 1.0501 | 0
CA_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 612243.2756 | 717662.0956 | 94529.6171 | 4077910.5986 | 543387.6147 | 547616.5932 | 95863.3291 | 265383.6824 | 110067.362 | 0 | 0 | 0 | 0 | 7064664.1683 | 0 | 7064659.1668 | 5.0014 | 543392.6161 | 0 | 108489.5084 | 127169.7233 | 16750.6482 | 722605.7581 | 96288.2853 | 97037.6603 | 16986.9819 | 47025.9885 | 19503.9365 | 0 | 0 | 0 | 0 | 1251858.4906 | 0 | 1251857.6044 | 0.88625 | 96289.1716 | 0 | 2088.9741 | 2448.6631 | 322.5351 | 13913.831 | 1854.0385 | 1868.4678 | 327.0857 | 905.4891 | 375.5498 | 0 | 0 | 0 | 0 | 24104.6341 | 0 | 24104.6171 | 0.017065 | 1854.0556 | 4.9112 | 0.6469 | 27.9065 | 3.7475 | 0.65602 | 0 | 4.1898 | 0 | 0 | 0.75323 | 0 | 48.3458 | 48.3458 | 3.4226e-05
CA_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 72356.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498419.1107 | 0 | 0 | 570775.4697 | 0 | 570775.4697 | 0 | 0 | 688.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4744.9499 | 0 | 0 | 5433.7825 | 0 | 5433.7825 | 0 | 0 | 72.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498.4191 | 0 | 0 | 570.7755 | 0 | 570.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14512 | 0.99966 | 0 | 0 | 1.1448 | 1.1448 | 0
CA_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 19472.1953 | 28374.723 | 7207.602 | 142004.2074 | 0 | 17299.3562 | 0 | 0 | 0 | 0 | 100017.2863 | 0 | 0 | 314375.3701 | 0 | 314377.0373 | -1.6671 | -1.6671 | 0 | 3450.473 | 5028.0009 | 1277.1871 | 25163.1456 | 0 | 3065.4459 | 0 | 0 | 0 | 0 | 17723.0631 | 0 | 0 | 55707.3156 | 0 | 55707.611 | -0.29542 | -0.29542 | 0 | 66.4391 | 96.8146 | 24.5923 | 484.5184 | 0 | 59.0254 | 0 | 0 | 0 | 0 | 341.259 | 0 | 0 | 1072.6488 | 0 | 1072.6545 | -0.0056883 | -0.0056883 | 2.8693 | 0.72886 | 14.3599 | 1.7494 | 0 | 0 | 1.9691 | 0 | 10.1141 | 0 | 0 | 31.7908 | 31.7907 | -0.00016859
CA_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 2767.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2767.626 | 0 | 2767.626 | 0 | 0 | 26.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3478 | 0 | 26.3478 | 0 | 0 | 2.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7676 | 0 | 2.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082026 | 0 | 0 | 0 | 0.082026 | 0.082026 | 0
CA_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 25899.02 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 20141.8299 | 0 | 0 | 0 | 0 | 99892.2508 | 0 | 0 | 318326.492 | 0 | 318326.2141 | 0.27786 | 0.27786 | 0 | 4589.3064 | 4107.7763 | 1277.1871 | 25163.1456 | 0 | 3569.1323 | 0 | 0 | 0 | 0 | 17700.9068 | 0 | 0 | 56407.4544 | 0 | 56407.4051 | 0.049236 | 0.049236 | 0 | 88.3675 | 79.0956 | 24.5923 | 484.5184 | 0 | 68.7239 | 0 | 0 | 0 | 0 | 340.8324 | 0 | 0 | 1086.13 | 0 | 1086.129 | 0.00094805 | 0.00094805 | 2.3442 | 0.72886 | 14.3599 | 2.0368 | 0 | 0 | 2.619 | 0 | 10.1014 | 0 | 0 | 32.1902 | 32.1902 | 2.8098e-05
CA_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 208.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.5198 | 0 | 208.5198 | 0 | 0 | 1.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9851 | 0 | 1.9851 | 0 | 0 | 0.20852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20852 | 0 | 0.20852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00618 | 0 | 0 | 0 | 0.00618 | 0.00618 | 0
CA_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 118853.1898 | 99839.458 | 7090.9022 | 317887.4784 | 4818.0346 | 83826.5782 | 116.6998 | 0 | 0 | 0 | 7179.8163 | 17663.3484 | 0 | 657275.5059 | 0 | 657278.8401 | -3.3343 | 4814.7003 | 0 | 21060.7852 | 17691.552 | 1256.5079 | 56329.6612 | 853.7557 | 14854.0697 | 20.6792 | 0 | 0 | 0 | 1272.2634 | 3129.9453 | 0 | 116469.2196 | 0 | 116469.8105 | -0.59083 | 853.1649 | 0 | 405.5271 | 340.6522 | 24.1942 | 1084.6321 | 16.4391 | 286.0163 | 0.39818 | 0 | 0 | 0 | 24.4975 | 60.2673 | 0 | 2242.624 | 0 | 2242.6354 | -0.011377 | 16.4278 | 4.606 | 0.32713 | 14.6653 | 3.8672 | 0.0053838 | 0 | 5.4831 | 0 | 0.33123 | 0 | 0.81488 | 30.3227 | 30.3225 | -0.00015382
CA_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 45978.6085 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102705.4631 | 0 | 0 | 490874.4864 | 0 | 490874.4864 | 0 | 0 | 437.7164 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 977.756 | 0 | 0 | 4673.1251 | 0 | 4673.1251 | 0 | 0 | 45.9786 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7055 | 0 | 0 | 490.8745 | 0 | 490.8745 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.62168 | 1.3887 | 0 | 0 | 6.6371 | 6.6371 | 0
CA_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 110428.5757 | 80775.712 | 7090.9022 | 312483.1662 | 4745.7919 | 70147.6945 | 102.807 | 0 | 0 | 0 | 7179.8163 | 12503.5501 | 0 | 605458.0158 | 0 | 605460.5165 | -2.5007 | 4743.2912 | 0 | 19567.9436 | 14313.4562 | 1256.5079 | 55372.0171 | 840.9543 | 12430.1715 | 18.2174 | 0 | 0 | 0 | 1272.2634 | 2215.6291 | 0 | 107287.1604 | 0 | 107287.6035 | -0.44313 | 840.5112 | 0 | 376.7823 | 275.6067 | 24.1942 | 1066.1926 | 16.1926 | 239.3439 | 0.35078 | 0 | 0 | 0 | 24.4975 | 42.6621 | 0 | 2065.8227 | 0 | 2065.8313 | -0.0085324 | 16.1841 | 3.7265 | 0.32713 | 14.416 | 3.2362 | 0.0047429 | 0 | 5.0945 | 0 | 0.33123 | 0 | 0.57683 | 27.9321 | 27.932 | -0.00011537
CA_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 38585.635 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102459.0307 | 0 | 0 | 483235.0805 | 0 | 483235.0805 | 0 | 0 | 367.3352 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 975.41 | 0 | 0 | 4600.398 | 0 | 4600.398 | 0 | 0 | 38.5856 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.459 | 0 | 0 | 483.2351 | 0 | 483.2351 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.52172 | 1.3853 | 0 | 0 | 6.5338 | 6.5338 | 0
CA_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 28899.8721 | 83026.351 | 10711.3746 | 53987.5506 | 0 | 38908.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215533.4176 | 0 | 215534.8068 | -1.3893 | -1.3893 | 0 | 5121.0573 | 14712.2694 | 1898.0556 | 9566.594 | 0 | 6894.5453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38192.5216 | 0 | 38192.7678 | -0.24618 | -0.24618 | 0 | 98.6064 | 283.2859 | 36.5472 | 184.2055 | 0 | 132.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.4 | 0 | 735.4048 | -0.0047402 | -0.0047402 | 11.4728 | 1.4801 | 7.4601 | 5.3764 | 0 | 0 | 3.9935 | 0 | 0 | 0 | 0 | 29.7831 | 29.7829 | -0.00019197
CA_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 3184.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86270.3143 | 0 | 0 | 89454.9798 | 0 | 89454.9798 | 0 | 0 | 30.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821.2934 | 0 | 0 | 851.6114 | 0 | 851.6114 | 0 | 0 | 3.1847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2703 | 0 | 0 | 89.455 | 0 | 89.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12898 | 3.4939 | 0 | 0 | 3.6228 | 3.6228 | 0
CA_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 24876.5075 | 65521.3809 | 10711.3746 | 53987.5506 | 0 | 36729.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191826.6866 | 0 | 191828.0759 | -1.3893 | -1.3893 | 0 | 4408.1171 | 11610.3887 | 1898.0556 | 9566.594 | 0 | 6508.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33991.6889 | 0 | 33991.935 | -0.24618 | -0.24618 | 0 | 84.8786 | 223.559 | 36.5472 | 184.2055 | 0 | 125.3223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.5127 | 0 | 654.5174 | -0.0047402 | -0.0047402 | 9.0539 | 1.4801 | 7.4601 | 5.0754 | 0 | 0 | 3.4375 | 0 | 0 | 0 | 0 | 26.5073 | 26.5071 | -0.00019197
CA_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 5013.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86289.2706 | 0 | 0 | 91303.2232 | 0 | 91303.2232 | 0 | 0 | 47.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821.4739 | 0 | 0 | 869.2067 | 0 | 869.2067 | 0 | 0 | 5.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2893 | 0 | 0 | 91.3032 | 0 | 91.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20306 | 3.4946 | 0 | 0 | 3.6977 | 3.6977 | 0
CA_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 475.1349 | 83540.3859 | 79914.3564 | 12309.0504 | 154949.5496 | 0 | 55871.4188 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 387132.1387 | 0 | 387132.9723 | -0.83357 | -0.83357 | 84.1939 | 14803.3564 | 14160.8239 | 2181.1637 | 27457.0602 | 0 | 9900.4154 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 68599.815 | 0 | 68599.9627 | -0.14771 | -0.14771 | 1.6212 | 285.0398 | 272.6678 | 41.9985 | 528.6879 | 0 | 190.6333 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1320.8949 | 0 | 1320.8977 | -0.0028441 | -0.0028441 | 6.3115 | 0.97214 | 12.2376 | 4.4126 | 0.0057056 | 0 | 6.5978 | 0.037525 | 0 | 0 | 0 | 30.5749 | 30.5749 | -6.5834e-05
CA_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 132.6944 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 512370.9787 | 0 | 0 | 911999.111 | 0 | 911999.111 | 0 | 0 | 1.2633 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 4877.7717 | 0 | 0 | 8682.2315 | 0 | 8682.2315 | 0 | 0 | 0.13269 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 512.371 | 0 | 0 | 911.9991 | 0 | 911.9991 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.0030715 | 11.8599 | 0 | 0 | 21.1101 | 21.1101 | 0
CA_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 625.1775 | 77672.053 | 51200.6483 | 12309.0504 | 154949.5496 | 0 | 53256.7876 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 350085.5091 | 0 | 350088.2877 | -2.7786 | -2.7786 | 110.7815 | 13763.4878 | 9072.7549 | 2181.1637 | 27457.0602 | 0 | 9437.1028 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 62035.1522 | 0 | 62035.6446 | -0.49236 | -0.49236 | 2.1331 | 265.017 | 174.6966 | 41.9985 | 528.6879 | 0 | 181.7122 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.4918 | 0 | 1194.5012 | -0.0094805 | -0.0094805 | 4.0437 | 0.97214 | 12.2376 | 4.2061 | 0.0057056 | 0 | 6.1344 | 0.049375 | 0 | 0 | 0 | 27.6492 | 27.649 | -0.00021945
CA_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 284.3451 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 512418.3696 | 0 | 0 | 912198.1526 | 0 | 912198.1526 | 0 | 0 | 2.707 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 4878.2229 | 0 | 0 | 8684.1264 | 0 | 8684.1264 | 0 | 0 | 0.28435 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 512.4184 | 0 | 0 | 912.1982 | 0 | 912.1982 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.0065818 | 11.861 | 0 | 0 | 21.1147 | 21.1147 | 0
CA_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 36.1214 | 4495.7209 | 8963.6561 | 1564.333 | 13417.6985 | 0 | 4581.8565 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38063.585 | 0 | 38066.0857 | -2.5007 | -2.5007 | 6.4007 | 796.6417 | 1588.3599 | 277.1998 | 2377.6162 | 0 | 811.905 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 6744.8673 | 0 | 6745.3104 | -0.44313 | -0.44313 | 0.12325 | 15.3394 | 30.584 | 5.3375 | 45.7812 | 0 | 15.6333 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 129.873 | 0 | 129.8815 | -0.0085324 | -0.0085324 | 5.5587 | 0.9701 | 8.3208 | 2.8414 | 0 | 0 | 2.788 | 0.0224 | 3.1033 | 0 | 0 | 23.6062 | 23.6047 | -0.0015508
CA_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 41.6785 | 4167.85 | 7204.8234 | 1564.333 | 13417.6985 | 0 | 4178.9643 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 35579.5464 | 0 | 35578.9907 | 0.55571 | 0.55571 | 7.3854 | 738.543 | 1276.6947 | 277.1998 | 2377.6162 | 0 | 740.5125 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 6304.6956 | 0 | 6304.5971 | 0.098472 | 0.098472 | 0.14221 | 14.2207 | 24.5829 | 5.3375 | 45.7812 | 0 | 14.2586 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 121.3974 | 0 | 121.3955 | 0.0018961 | 0.0018961 | 4.468 | 0.9701 | 8.3208 | 2.5915 | 0 | 0 | 2.5846 | 0.025846 | 3.1033 | 0 | 0 | 22.0639 | 22.0642 | 0.00034462
CA_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | CA-LOSANGELES-CA | Zone3B | Zone3B(CA-LOSANGELES-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA_3C_LO_2016_EL | 3C | LO | EL |  |  | OfficeLarge | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 312635.9874 | 882878.4491 | 95199.2517 | 4077910.5986 | 543459.8574 | 544240.6346 | 66046.53 | 137241.7441 | 123718.4601 | 0 | 0 | 0 | 0 | 6783331.5131 | 0 | 6783330.6795 | 0.83357 | 543460.691 | 0 | 55399.097 | 156446.0612 | 16869.3074 | 722605.7581 | 96301.0867 | 96439.4405 | 11703.4451 | 24319.2371 | 21922.9111 | 0 | 0 | 0 | 0 | 1202006.3441 | 0 | 1202006.1964 | 0.14771 | 96301.2344 | 0 | 1066.714 | 3012.3813 | 324.8198 | 13913.831 | 1854.285 | 1856.949 | 225.3508 | 468.2688 | 422.1274 | 0 | 0 | 0 | 0 | 23144.7271 | 0 | 23144.7243 | 0.0028441 | 1854.2879 | 6.0418 | 0.65148 | 27.9065 | 3.7244 | 0.45198 | 0 | 2.1395 | 0 | 0 | 0.84665 | 0 | 46.4205 | 46.4205 | 5.7044e-06
CA_3C_LO_2016_NG | 3C | LO | NG |  |  | OfficeLarge | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 129471.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532284.6164 | 0 | 0 | 661756.435 | 0 | 661756.435 | 0 | 0 | 1232.5717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5067.3495 | 0 | 0 | 6299.9213 | 0 | 6299.9213 | 0 | 0 | 129.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.2846 | 0 | 0 | 661.7564 | 0 | 661.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25968 | 1.0676 | 0 | 0 | 1.3273 | 1.3273 | 0
CA_3C_LO_2019_EL | 3C | LO | EL |  |  | OfficeLarge | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 292619.193 | 718181.6875 | 95199.2517 | 4077910.5986 | 543387.6147 | 528919.618 | 63651.4056 | 122042.9844 | 123496.1748 | 0 | 0 | 0 | 0 | 6565408.5282 | 0 | 6565404.9161 | 3.6121 | 543391.2268 | 0 | 51852.121 | 127261.795 | 16869.3074 | 722605.7581 | 96288.2853 | 93724.5563 | 11279.0291 | 21626.0168 | 21883.5222 | 0 | 0 | 0 | 0 | 1163390.3912 | 0 | 1163389.7511 | 0.64007 | 96288.9254 | 0 | 998.4167 | 2450.4359 | 324.8198 | 13913.831 | 1854.0385 | 1804.6737 | 217.1786 | 416.4107 | 421.3689 | 0 | 0 | 0 | 0 | 22401.1739 | 0 | 22401.1616 | 0.012325 | 1854.0509 | 4.9148 | 0.65148 | 27.9065 | 3.6196 | 0.43559 | 0 | 2.0025 | 0 | 0 | 0.84512 | 0 | 44.9292 | 44.9292 | 2.4719e-05
CA_3C_LO_2019_NG | 3C | LO | NG |  |  | OfficeLarge | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 400234.7353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532322.5291 | 0 | 0 | 932557.2644 | 0 | 932557.2644 | 0 | 0 | 3810.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5067.7105 | 0 | 0 | 8877.9452 | 0 | 8877.9452 | 0 | 0 | 400.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.3225 | 0 | 0 | 932.5573 | 0 | 932.5573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80274 | 1.0677 | 0 | 0 | 1.8704 | 1.8704 | 0
CA_3C_MA_2016_EL | 3C | MA | EL |  |  | ApartmentMidRise | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 8780.2707 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 14373.5254 | 0 | 0 | 0 | 0 | 106999.8244 | 0 | 0 | 307742.9315 | 0 | 307741.5422 | 1.3893 | 1.3893 | 0 | 1555.864 | 5028.0009 | 1277.6794 | 25163.1456 | 0 | 2546.9887 | 0 | 0 | 0 | 0 | 18960.3689 | 0 | 0 | 54532.0475 | 0 | 54531.8013 | 0.24618 | 0.24618 | 0 | 29.9583 | 96.8146 | 24.6018 | 484.5184 | 0 | 49.0425 | 0 | 0 | 0 | 0 | 365.0834 | 0 | 0 | 1050.0189 | 0 | 1050.0141 | 0.0047402 | 0.0047402 | 2.8693 | 0.72914 | 14.3599 | 1.4535 | 0 | 0 | 0.88789 | 0 | 10.8202 | 0 | 0 | 31.1198 | 31.12 | 0.00014049
CA_3C_MA_2016_NG | 3C | MA | NG |  |  | ApartmentMidRise | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 24121.9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24121.9457 | 0 | 24121.9457 | 0 | 0 | 229.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.6409 | 0 | 229.6409 | 0 | 0 | 24.1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1219 | 0 | 24.1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71491 | 0 | 0 | 0 | 0.71491 | 0.71491 | 0
CA_3C_MA_2019_EL | 3C | MA | EL |  |  | ApartmentMidRise | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 8519.0854 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 13901.1691 | 0 | 0 | 0 | 0 | 107008.1601 | 0 | 0 | 301824.5844 | 0 | 301825.6959 | -1.1114 | -1.1114 | 0 | 1509.5819 | 4107.7763 | 1277.6794 | 25163.1456 | 0 | 2463.2872 | 0 | 0 | 0 | 0 | 18961.846 | 0 | 0 | 53483.3164 | 0 | 53483.5133 | -0.19694 | -0.19694 | 0 | 29.0671 | 79.0956 | 24.6018 | 484.5184 | 0 | 47.4308 | 0 | 0 | 0 | 0 | 365.1118 | 0 | 0 | 1029.8255 | 0 | 1029.8293 | -0.0037922 | -0.0037922 | 2.3442 | 0.72914 | 14.3599 | 1.4057 | 0 | 0 | 0.86148 | 0 | 10.821 | 0 | 0 | 30.5216 | 30.5215 | -0.00011239
CA_3C_MA_2019_NG | 3C | MA | NG |  |  | ApartmentMidRise | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 24358.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24358.9 | 0 | 24358.9 | 0 | 0 | 231.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.8967 | 0 | 231.8967 | 0 | 0 | 24.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.3589 | 0 | 24.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72194 | 0 | 0 | 0 | 0.72194 | 0.72194 | 0
CA_3C_PS_2016_EL | 3C | PS | EL |  |  | SchoolPrimary | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 52253.725 | 100409.0642 | 7104.795 | 317887.4784 | 4818.0346 | 79505.907 | 377.8851 | 0 | 0 | 0 | 7179.8163 | 17616.1128 | 0 | 587152.8185 | 0 | 587153.3742 | -0.55571 | 4817.4789 | 0 | 9259.3601 | 17792.4862 | 1258.9697 | 56329.6612 | 853.7557 | 14088.4467 | 66.9612 | 0 | 0 | 0 | 1272.2634 | 3121.5752 | 0 | 104043.4794 | 0 | 104043.5779 | -0.098472 | 853.6573 | 0 | 178.2897 | 342.5957 | 24.2416 | 1084.6321 | 16.4391 | 271.2742 | 1.2893 | 0 | 0 | 0 | 24.4975 | 60.1062 | 0 | 2003.3654 | 0 | 2003.3673 | -0.0018961 | 16.4372 | 4.6322 | 0.32777 | 14.6653 | 3.6679 | 0.017433 | 0 | 2.4107 | 0 | 0.33123 | 0 | 0.8127 | 27.0875 | 27.0875 | -2.5637e-05
CA_3C_PS_2016_NG | 3C | PS | NG |  |  | SchoolPrimary | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 215287.1806 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 109738.2662 | 0 | 0 | 667215.8616 | 0 | 667215.8616 | 0 | 0 | 2049.534 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1044.7083 | 0 | 0 | 6351.895 | 0 | 6351.895 | 0 | 0 | 215.2872 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7383 | 0 | 0 | 667.2159 | 0 | 667.2159 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.9109 | 1.4838 | 0 | 0 | 9.0214 | 9.0214 | 0
CA_3C_PS_2019_EL | 3C | PS | EL |  |  | SchoolPrimary | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 47721.8828 | 81009.1116 | 7104.795 | 312483.1662 | 4745.7919 | 65104.5959 | 377.8851 | 0 | 0 | 0 | 7179.8163 | 12486.8787 | 0 | 538213.9235 | 0 | 538216.1464 | -2.2229 | 4743.569 | 0 | 8456.3176 | 14354.8146 | 1258.9697 | 55372.0171 | 840.9543 | 11536.5344 | 66.9612 | 0 | 0 | 0 | 1272.2634 | 2212.6749 | 0 | 95371.5072 | 0 | 95371.9011 | -0.39389 | 840.5604 | 0 | 162.8271 | 276.4031 | 24.2416 | 1066.1926 | 16.1926 | 222.1369 | 1.2893 | 0 | 0 | 0 | 24.4975 | 42.6052 | 0 | 1836.3859 | 0 | 1836.3935 | -0.0075844 | 16.1851 | 3.7372 | 0.32777 | 14.416 | 3.0035 | 0.017433 | 0 | 2.2016 | 0 | 0.33123 | 0 | 0.57607 | 24.8299 | 24.8298 | -0.00010255
CA_3C_PS_2019_NG | 3C | PS | NG |  |  | SchoolPrimary | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 217230.2057 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 109340.183 | 0 | 0 | 668760.8035 | 0 | 668760.8035 | 0 | 0 | 2068.0316 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.9185 | 0 | 0 | 6366.6028 | 0 | 6366.6028 | 0 | 0 | 217.2302 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3402 | 0 | 0 | 668.7608 | 0 | 668.7608 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.9372 | 1.4784 | 0 | 0 | 9.0423 | 9.0423 | 0
CA_3C_RS_2016_EL | 3C | RS | EL |  |  | RetailStandalone | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 9719.4263 | 83740.4427 | 10697.4817 | 53987.5506 | 0 | 37699.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195844.494 | 0 | 195844.2162 | 0.27786 | 0.27786 | 0 | 1722.2823 | 14838.8064 | 1895.5938 | 9566.594 | 0 | 6680.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34703.6443 | 0 | 34703.5951 | 0.049236 | 0.049236 | 0 | 33.1627 | 285.7224 | 36.4998 | 184.2055 | 0 | 128.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668.2214 | 0 | 668.2205 | 0.00094805 | 0.00094805 | 11.5715 | 1.4782 | 7.4601 | 5.2094 | 0 | 0 | 1.3431 | 0 | 0 | 0 | 0 | 27.0622 | 27.0623 | 3.8395e-05
CA_3C_RS_2016_NG | 3C | RS | NG |  |  | RetailStandalone | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 43969.2362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88412.381 | 0 | 0 | 132381.6172 | 0 | 132381.6172 | 0 | 0 | 418.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.6859 | 0 | 0 | 1260.273 | 0 | 1260.273 | 0 | 0 | 43.9692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4124 | 0 | 0 | 132.3816 | 0 | 132.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7807 | 3.5806 | 0 | 0 | 5.3613 | 5.3613 | 0
CA_3C_RS_2019_EL | 3C | RS | EL |  |  | RetailStandalone | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 9319.3127 | 66299.3796 | 10697.4817 | 53987.5506 | 0 | 35571.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175874.9353 | 0 | 175875.2132 | -0.27786 | -0.27786 | 0 | 1651.3822 | 11748.2501 | 1895.5938 | 9566.594 | 0 | 6303.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31165.0385 | 0 | 31165.0878 | -0.049236 | -0.049236 | 0 | 31.7975 | 226.2135 | 36.4998 | 184.2055 | 0 | 121.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600.0853 | 0 | 600.0862 | -0.00094805 | -0.00094805 | 9.1614 | 1.4782 | 7.4601 | 4.9153 | 0 | 0 | 1.2878 | 0 | 0 | 0 | 0 | 24.3029 | 24.3028 | -3.8395e-05
CA_3C_RS_2019_NG | 3C | RS | NG |  |  | RetailStandalone | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 59655.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88440.8155 | 0 | 0 | 148096.425 | 0 | 148096.425 | 0 | 0 | 567.9214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.9566 | 0 | 0 | 1409.878 | 0 | 1409.878 | 0 | 0 | 59.6556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4408 | 0 | 0 | 148.0964 | 0 | 148.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.416 | 3.5818 | 0 | 0 | 5.9977 | 5.9977 | 0
CA_3C_SH_2016_EL | 3C | SH | EL |  |  | HotelSmall | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 1933.8824 | 60756.1391 | 80189.4345 | 12314.6075 | 154949.5496 | 0 | 55112.8701 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 365328.726 | 0 | 365328.726 | 0 | 0 | 342.684 | 10765.9878 | 14209.5678 | 2182.1485 | 27457.0602 | 0 | 9766.0006 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 64736.2502 | 0 | 64736.2502 | 0 | 0 | 6.5984 | 207.2999 | 273.6064 | 42.0174 | 528.6879 | 0 | 188.0451 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.5016 | 0 | 1246.5016 | 0 | 0 | 6.3332 | 0.97258 | 12.2376 | 4.3527 | 0.0057056 | 0 | 4.7984 | 0.15273 | 0 | 0 | 0 | 28.8529 | 28.8529 | 0
CA_3C_SH_2016_NG | 3C | SH | NG |  |  | HotelSmall | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 2739.1915 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 551932.8653 | 0 | 0 | 954167.4947 | 0 | 954167.4947 | 0 | 0 | 26.0771 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5254.4009 | 0 | 0 | 9083.6745 | 0 | 9083.6745 | 0 | 0 | 2.7392 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 551.9329 | 0 | 0 | 954.1675 | 0 | 954.1675 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.063404 | 12.7756 | 0 | 0 | 22.0862 | 22.0862 | 0
CA_3C_SH_2019_EL | 3C | SH | EL |  |  | HotelSmall | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 2739.6667 | 55596.3407 | 51378.4765 | 12314.6075 | 154949.5496 | 0 | 52303.7392 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 329354.6231 | 0 | 329355.7346 | -1.1114 | -1.1114 | 485.4689 | 9851.6716 | 9104.266 | 2182.1485 | 27457.0602 | 0 | 9268.2226 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 58361.6392 | 0 | 58361.8362 | -0.19694 | -0.19694 | 9.3477 | 189.6947 | 175.3034 | 42.0174 | 528.6879 | 0 | 178.4604 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.758 | 0 | 1123.7618 | -0.0037922 | -0.0037922 | 4.0578 | 0.97258 | 12.2376 | 4.1308 | 0.0057056 | 0 | 4.3909 | 0.21637 | 0 | 0 | 0 | 26.0118 | 26.0117 | -8.7778e-05
CA_3C_SH_2019_NG | 3C | SH | NG |  |  | HotelSmall | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 4331.5242 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 551961.2998 | 0 | 0 | 955788.262 | 0 | 955788.262 | 0 | 0 | 41.2361 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5254.6716 | 0 | 0 | 9099.1043 | 0 | 9099.1043 | 0 | 0 | 4.3315 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 551.9613 | 0 | 0 | 955.7883 | 0 | 955.7883 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.10026 | 12.7763 | 0 | 0 | 22.1237 | 22.1237 | 0
CA_3C_SO_2016_EL | 3C | SO | EL |  |  | OfficeSmall | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 358.4351 | 2000.568 | 9022.006 | 1578.2259 | 13417.6985 | 0 | 4473.4924 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 35854.6245 | 0 | 35854.0688 | 0.55571 | 0.55571 | 63.5147 | 354.5007 | 1598.6995 | 279.6616 | 2377.6162 | 0 | 792.7028 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 6353.4395 | 0 | 6353.341 | 0.098472 | 0.098472 | 1.223 | 6.8259 | 30.7831 | 5.3849 | 45.7812 | 0 | 15.2636 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 122.336 | 0 | 122.3341 | 0.0018961 | 0.0018961 | 5.5949 | 0.97872 | 8.3208 | 2.7742 | 0 | 0 | 1.2406 | 0.22228 | 3.1033 | 0 | 0 | 22.2345 | 22.2348 | 0.00034462
CA_3C_SO_2016_NG | 3C | SO | NG |  |  | OfficeSmall | STD2016 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 18.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9563 | 0 | 18.9563 | 0 | 0 | 0.18046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18046 | 0 | 0.18046 | 0 | 0 | 0.018956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018956 | 0 | 0.018956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034454 | 0 | 0 | 0 | 0.0034454 | 0.0034454 | 0
CA_3C_SO_2019_EL | 3C | SO | EL |  |  | OfficeSmall | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 391.7779 | 1775.5041 | 7252.059 | 1578.2259 | 13417.6985 | 0 | 4062.2645 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 33481.7285 | 0 | 33481.7285 | 0 | 0 | 69.423 | 314.6193 | 1285.0649 | 279.6616 | 2377.6162 | 0 | 719.8333 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 5932.9623 | 0 | 5932.9623 | 0 | 0 | 1.3367 | 6.058 | 24.744 | 5.3849 | 45.7812 | 0 | 13.8604 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 114.2397 | 0 | 114.2397 | 0 | 0 | 4.4973 | 0.97872 | 8.3208 | 2.5192 | 0 | 0 | 1.1011 | 0.24296 | 3.1033 | 0 | 0 | 20.7633 | 20.7633 | 0
CA_3C_SO_2019_NG | 3C | SO | NG |  |  | OfficeSmall | STD2019 | CA-SANFRANCISCO-CA | Zone3C | Zone3C(CA-SANFRANCISCO-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 28.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4345 | 0 | 28.4345 | 0 | 0 | 0.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2707 | 0 | 0.2707 | 0 | 0 | 0.028435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028435 | 0 | 0.028435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005168 | 0 | 0 | 0 | 0.005168 | 0.005168 | 0
CA_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 742088.4753 | 880147.118 | 95029.7591 | 4077910.5986 | 543457.0788 | 705164.1026 | 96282.8927 | 207878.4663 | 698281.5929 | 0 | 0 | 0 | 0 | 8046240.0844 | 0 | 8046238.973 | 1.1114 | 543458.1903 | 0 | 131498.0778 | 155962.0693 | 16839.2733 | 722605.7581 | 96300.5944 | 124955.079 | 17061.3286 | 36836.0642 | 123735.4983 | 0 | 0 | 0 | 0 | 1425793.743 | 0 | 1425793.546 | 0.19694 | 96300.7913 | 0 | 2532.0059 | 3003.062 | 324.2415 | 13913.831 | 1854.2756 | 2406.0199 | 328.5172 | 709.2813 | 2382.5368 | 0 | 0 | 0 | 0 | 27453.7712 | 0 | 27453.7674 | 0.0037922 | 1854.2793 | 6.0231 | 0.65032 | 27.9065 | 4.8257 | 0.6589 | 0 | 5.0784 | 0 | 0 | 4.7786 | 0 | 55.063 | 55.063 | 7.6059e-06
CA_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 492305.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526720.9299 | 0 | 0 | 1019026.6202 | 0 | 1019026.6202 | 0 | 0 | 4686.7502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5014.3833 | 0 | 0 | 9701.1334 | 0 | 9701.1334 | 0 | 0 | 492.3057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526.7209 | 0 | 0 | 1019.0266 | 0 | 1019.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9874 | 1.0564 | 0 | 0 | 2.0438 | 2.0438 | 0
CA_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 691421.3118 | 717184.1821 | 95029.7591 | 4077910.5986 | 543387.6147 | 709923.7873 | 98958.6524 | 187506.0154 | 699148.5058 | 0 | 0 | 0 | 0 | 7820470.4272 | 0 | 7820469.3158 | 1.1114 | 543388.7261 | 0 | 122519.8565 | 127085.0371 | 16839.2733 | 722605.7581 | 96288.2853 | 125798.4951 | 17535.4732 | 33226.0659 | 123889.1152 | 0 | 0 | 0 | 0 | 1385787.3597 | 0 | 1385787.1628 | 0.19694 | 96288.4823 | 0 | 2359.1295 | 2447.0324 | 324.2415 | 13913.831 | 1854.0385 | 2422.26 | 337.6469 | 639.7705 | 2385.4947 | 0 | 0 | 0 | 0 | 26683.4451 | 0 | 26683.4413 | 0.0037922 | 1854.0423 | 4.9079 | 0.65032 | 27.9065 | 4.8582 | 0.67721 | 0 | 4.7316 | 0 | 0 | 4.7845 | 0 | 53.518 | 53.518 | 7.6059e-06
CA_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 892805.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526796.7553 | 0 | 0 | 1419602.5697 | 0 | 1419602.5697 | 0 | 0 | 8499.5114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5015.1051 | 0 | 0 | 13514.6165 | 0 | 13514.6165 | 0 | 0 | 892.8058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526.7968 | 0 | 0 | 1419.6026 | 0 | 1419.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7907 | 1.0566 | 0 | 0 | 2.8472 | 2.8472 | 0
CA_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 35704.5819 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 24312.4585 | 0 | 0 | 0 | 0 | 105827.2692 | 0 | 0 | 343428.0634 | 0 | 343430.0084 | -1.945 | -1.945 | 0 | 6326.8519 | 5028.0009 | 1276.6947 | 25163.1456 | 0 | 4308.1676 | 0 | 0 | 0 | 0 | 18752.5921 | 0 | 0 | 60855.4528 | 0 | 60855.7975 | -0.34465 | -0.34465 | 0 | 121.824 | 96.8146 | 24.5829 | 484.5184 | 0 | 82.9541 | 0 | 0 | 0 | 0 | 361.0826 | 0 | 0 | 1171.7766 | 0 | 1171.7832 | -0.0066363 | -0.0066363 | 2.8693 | 0.72858 | 14.3599 | 2.4586 | 0 | 0 | 3.6106 | 0 | 10.7016 | 0 | 0 | 34.7288 | 34.7286 | -0.00019668
CA_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 67304.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67304.4937 | 0 | 67304.4937 | 0 | 0 | 640.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.7388 | 0 | 640.7388 | 0 | 0 | 67.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.3045 | 0 | 67.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9947 | 0 | 0 | 0 | 1.9947 | 1.9947 | 0
CA_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 37382.8361 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 24687.565 | 0 | 0 | 0 | 0 | 105705.0123 | 0 | 0 | 340166.0261 | 0 | 340170.1939 | -4.1679 | -4.1679 | 0 | 6624.2386 | 4107.7763 | 1276.6947 | 25163.1456 | 0 | 4374.6365 | 0 | 0 | 0 | 0 | 18730.9282 | 0 | 0 | 60277.4198 | 0 | 60278.1584 | -0.73854 | -0.73854 | 0 | 127.5502 | 79.0956 | 24.5829 | 484.5184 | 0 | 84.234 | 0 | 0 | 0 | 0 | 360.6655 | 0 | 0 | 1160.6465 | 0 | 1160.6607 | -0.014221 | -0.014221 | 2.3442 | 0.72858 | 14.3599 | 2.4965 | 0 | 0 | 3.7803 | 0 | 10.6892 | 0 | 0 | 34.3991 | 34.3987 | -0.00042147
CA_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 26055.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26055.4926 | 0 | 26055.4926 | 0 | 0 | 248.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.0483 | 0 | 248.0483 | 0 | 0 | 26.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0555 | 0 | 26.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77222 | 0 | 0 | 0 | 0.77222 | 0.77222 | 0
CA_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 136680.4737 | 98469.6247 | 7107.5736 | 317887.4784 | 4818.0346 | 107424.9451 | 311.1995 | 0 | 0 | 0 | 7179.8163 | 17388.2703 | 0 | 697267.4161 | 0 | 697268.8054 | -1.3893 | 4816.6453 | 0 | 24219.7799 | 17448.8175 | 1259.462 | 56329.6612 | 853.7557 | 19035.7003 | 55.1445 | 0 | 0 | 0 | 1272.2634 | 3081.2015 | 0 | 123555.7861 | 0 | 123556.0323 | -0.24618 | 853.5096 | 0 | 466.3538 | 335.9784 | 24.251 | 1084.6321 | 16.4391 | 366.5339 | 1.0618 | 0 | 0 | 0 | 24.4975 | 59.3288 | 0 | 2379.0764 | 0 | 2379.0812 | -0.0047402 | 16.4344 | 4.5428 | 0.3279 | 14.6653 | 4.9559 | 0.014357 | 0 | 6.3056 | 0 | 0.33123 | 0 | 0.80218 | 32.1676 | 32.1675 | -6.4093e-05
CA_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 189222.2098 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 110278.5219 | 0 | 0 | 641691.1466 | 0 | 641691.1466 | 0 | 0 | 1801.3954 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1049.8515 | 0 | 0 | 6108.8997 | 0 | 6108.8997 | 0 | 0 | 189.2222 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2785 | 0 | 0 | 641.6911 | 0 | 641.6911 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.5585 | 1.4911 | 0 | 0 | 8.6763 | 8.6763 | 0
CA_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 138544.8919 | 80078.2918 | 7107.5736 | 312483.1662 | 4745.7919 | 88689.0699 | 597.3918 | 0 | 0 | 0 | 7179.8163 | 12381.2931 | 0 | 651807.2866 | 0 | 651808.398 | -1.1114 | 4744.6805 | 0 | 24550.1548 | 14189.8733 | 1259.462 | 55372.0171 | 840.9543 | 15715.7032 | 105.8578 | 0 | 0 | 0 | 1272.2634 | 2193.9651 | 0 | 115500.2512 | 0 | 115500.4481 | -0.19694 | 840.7574 | 0 | 472.7152 | 273.2271 | 24.251 | 1066.1926 | 16.1926 | 302.6071 | 2.0383 | 0 | 0 | 0 | 24.4975 | 42.245 | 0 | 2223.9665 | 0 | 2223.9703 | -0.0037922 | 16.1888 | 3.6943 | 0.3279 | 14.416 | 4.0916 | 0.02756 | 0 | 6.3916 | 0 | 0.33123 | 0 | 0.57119 | 30.0703 | 30.0703 | -5.1274e-05
CA_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 350995.6359 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 110202.6965 | 0 | 0 | 803388.7473 | 0 | 803388.7473 | 0 | 0 | 3341.4785 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1049.1297 | 0 | 0 | 7648.2609 | 0 | 7648.2609 | 0 | 0 | 350.9956 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2027 | 0 | 0 | 803.3887 | 0 | 803.3887 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.7458 | 1.4901 | 0 | 0 | 10.8626 | 10.8626 | 0
CA_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 48544.3385 | 86224.4813 | 10728.046 | 53987.5506 | 0 | 43740.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243224.6131 | 0 | 243225.4467 | -0.83357 | -0.83357 | 0 | 8602.0568 | 15278.9781 | 1901.0097 | 9566.594 | 0 | 7750.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43099.4014 | 0 | 43099.5492 | -0.14771 | -0.14771 | 0 | 165.6333 | 294.1979 | 36.6041 | 184.2055 | 0 | 149.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 829.8824 | 0 | 829.8852 | -0.0028441 | -0.0028441 | 11.9147 | 1.4824 | 7.4601 | 6.0441 | 0 | 0 | 6.708 | 0 | 0 | 0 | 0 | 33.6095 | 33.6094 | -0.00011518
CA_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 91047.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88061.6886 | 0 | 0 | 179109.0012 | 0 | 179109.0012 | 0 | 0 | 866.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838.3473 | 0 | 0 | 1705.1177 | 0 | 1705.1177 | 0 | 0 | 91.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0617 | 0 | 0 | 179.109 | 0 | 179.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6873 | 3.5664 | 0 | 0 | 7.2537 | 7.2537 | 0
CA_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 45704.6434 | 68672.2756 | 10728.046 | 53987.5506 | 0 | 41642.3789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220734.8944 | 0 | 220734.6165 | 0.27786 | 0.27786 | 0 | 8098.8628 | 12168.7272 | 1901.0097 | 9566.594 | 0 | 7379.0295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39114.2233 | 0 | 39114.174 | 0.049236 | 0.049236 | 0 | 155.9442 | 234.3098 | 36.6041 | 184.2055 | 0 | 142.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.1475 | 0 | 753.1465 | 0.00094805 | 0.00094805 | 9.4893 | 1.4824 | 7.4601 | 5.7542 | 0 | 0 | 6.3156 | 0 | 0 | 0 | 0 | 30.5016 | 30.5017 | 3.8395e-05
CA_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 107624.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88080.645 | 0 | 0 | 195705.2789 | 0 | 195705.2789 | 0 | 0 | 1024.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838.5277 | 0 | 0 | 1863.1143 | 0 | 1863.1143 | 0 | 0 | 107.6246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0806 | 0 | 0 | 195.7053 | 0 | 195.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3587 | 3.5672 | 0 | 0 | 7.9259 | 7.9259 | 0
CA_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 8052.2862 | 77966.5811 | 79622.6069 | 12306.2718 | 154949.5496 | 0 | 47966.3966 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380935.935 | 0 | 380935.1015 | 0.83357 | 0.83357 | 1426.8651 | 13815.6782 | 14109.1259 | 2180.6714 | 27457.0602 | 0 | 8499.6455 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 67501.8477 | 0 | 67501.7 | 0.14771 | 0.14771 | 27.4744 | 266.022 | 271.6723 | 41.989 | 528.6879 | 0 | 163.6613 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.7534 | 0 | 1299.7506 | 0.0028441 | 0.0028441 | 6.2884 | 0.97192 | 12.2376 | 3.7883 | 0.0057056 | 0 | 6.1576 | 0.63595 | 0 | 0 | 0 | 30.0854 | 30.0855 | 6.5834e-05
CA_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 21856.6628 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 544881.1059 | 0 | 0 | 966233.2066 | 0 | 966233.2066 | 0 | 0 | 208.0754 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5187.2681 | 0 | 0 | 9198.5401 | 0 | 9198.5401 | 0 | 0 | 21.8567 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 544.8811 | 0 | 0 | 966.2332 | 0 | 966.2332 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.50592 | 12.6124 | 0 | 0 | 22.3655 | 22.3655 | 0
CA_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 10172.3326 | 72612.2831 | 51092.2842 | 12306.2718 | 154949.5496 | 0 | 45474.0223 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 346678.9864 | 0 | 346676.4857 | 2.5007 | 2.5007 | 1802.5373 | 12866.8966 | 9053.5528 | 2180.6714 | 27457.0602 | 0 | 8057.9968 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 61431.5164 | 0 | 61431.0733 | 0.44313 | 0.44313 | 34.708 | 247.7531 | 174.3269 | 41.989 | 528.6879 | 0 | 155.1574 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.8687 | 0 | 1182.8602 | 0.0085324 | 0.0085324 | 4.0352 | 0.97192 | 12.2376 | 3.5914 | 0.0057056 | 0 | 5.7348 | 0.80339 | 0 | 0 | 0 | 27.3798 | 27.38 | 0.0001975
CA_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 25031.8501 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 544966.4095 | 0 | 0 | 969493.6975 | 0 | 969493.6975 | 0 | 0 | 238.3032 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5188.0802 | 0 | 0 | 9229.58 | 0 | 9229.58 | 0 | 0 | 25.0319 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 544.9664 | 0 | 0 | 969.4937 | 0 | 969.4937 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.57941 | 12.6144 | 0 | 0 | 22.4409 | 22.4409 | 0
CA_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 914.1484 | 5687.726 | 8896.9705 | 1572.6687 | 13417.6985 | 0 | 5612.7047 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41106.1155 | 0 | 41106.1155 | 0 | 0 | 161.9871 | 1007.865 | 1576.5432 | 278.6769 | 2377.6162 | 0 | 994.5713 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 7284.0037 | 0 | 7284.0037 | 0 | 0 | 3.1191 | 19.4065 | 30.3565 | 5.3659 | 45.7812 | 0 | 19.1505 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.2541 | 0 | 140.2541 | 0 | 0 | 5.5174 | 0.97527 | 8.3208 | 3.4807 | 0 | 0 | 3.5272 | 0.5669 | 3.1033 | 0 | 0 | 25.4915 | 25.4915 | 0
CA_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 312.7796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.7796 | 0 | 312.7796 | 0 | 0 | 2.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9777 | 0 | 2.9777 | 0 | 0 | 0.31278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31278 | 0 | 0.31278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056848 | 0 | 0 | 0 | 0.056848 | 0.056848 | 0
CA_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 950.2698 | 5376.5265 | 7163.1449 | 1572.6687 | 13417.6985 | 0 | 5190.3626 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38674.8697 | 0 | 38672.3689 | 2.5007 | 2.5007 | 168.3878 | 952.7205 | 1269.3093 | 278.6769 | 2377.6162 | 0 | 919.7322 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 6853.1869 | 0 | 6852.7438 | 0.44313 | 0.44313 | 3.2423 | 18.3447 | 24.4407 | 5.3659 | 45.7812 | 0 | 17.7095 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.9587 | 0 | 131.9501 | 0.0085324 | 0.0085324 | 4.4421 | 0.97527 | 8.3208 | 3.2187 | 0 | 0 | 3.3342 | 0.5893 | 3.1033 | 0 | 0 | 23.9822 | 23.9838 | 0.0015508
CA_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | CA-BISHOP-CA | Zone4B | Zone4B(CA-BISHOP-CA) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 360.1705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360.1705 | 0 | 360.1705 | 0 | 0 | 3.4288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4288 | 0 | 3.4288 | 0 | 0 | 0.36017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36017 | 0 | 0.36017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065462 | 0 | 0 | 0 | 0.065462 | 0.065462 | 0
CA_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 567672.2875 | 880144.3394 | 95749.4079 | 4077910.5986 | 543457.0788 | 691990.918 | 81248.0684 | 156502.7684 | 701971.5295 | 0 | 0 | 0 | 0 | 7796646.9965 | 0 | 7796649.2194 | -2.2229 | 543454.856 | 0 | 100591.5293 | 155961.5769 | 16966.7951 | 722605.7581 | 96300.5944 | 122620.7907 | 14397.1577 | 27732.2906 | 124389.355 | 0 | 0 | 0 | 0 | 1381565.8478 | 0 | 1381566.2417 | -0.39389 | 96300.2005 | 0 | 1936.8978 | 3003.0525 | 326.697 | 13913.831 | 1854.2756 | 2361.073 | 277.2184 | 533.9874 | 2395.1269 | 0 | 0 | 0 | 0 | 26602.1596 | 0 | 26602.1671 | -0.0075844 | 1854.268 | 6.0231 | 0.65524 | 27.9065 | 4.7355 | 0.55601 | 0 | 3.8848 | 0 | 0 | 4.8038 | 0 | 53.355 | 53.355 | -1.5212e-05
CA_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 1329834.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572557.3658 | 0 | 0 | 1902392.1761 | 0 | 1902392.1761 | 0 | 0 | 12660.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5450.7461 | 0 | 0 | 18110.7735 | 0 | 18110.7735 | 0 | 0 | 1329.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5574 | 0 | 0 | 1902.3922 | 0 | 1902.3922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6672 | 1.1484 | 0 | 0 | 3.8156 | 3.8156 | 0
CA_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 530278.3371 | 716995.2396 | 95749.4079 | 4077910.5986 | 543387.6147 | 699042.9202 | 83290.3149 | 140703.8382 | 702585.5927 | 0 | 0 | 0 | 0 | 7589943.8639 | 0 | 7589943.586 | 0.27786 | 543387.8925 | 0 | 93965.3213 | 127051.5564 | 16966.7951 | 722605.7581 | 96288.2853 | 123870.4055 | 14759.0438 | 24932.7201 | 124498.167 | 0 | 0 | 0 | 0 | 1344938.0527 | 0 | 1344938.0034 | 0.049236 | 96288.3346 | 0 | 1809.3097 | 2446.3878 | 326.697 | 13913.831 | 1854.0385 | 2385.1344 | 284.1866 | 480.0815 | 2397.222 | 0 | 0 | 0 | 0 | 25896.8885 | 0 | 25896.8875 | 0.00094805 | 1854.0395 | 4.9066 | 0.65524 | 27.9065 | 4.7838 | 0.56998 | 0 | 3.6289 | 0 | 0 | 4.808 | 0 | 51.9405 | 51.9405 | 1.9015e-06
CA_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 2016139.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572557.3658 | 0 | 0 | 2588697.0745 | 0 | 2588697.0745 | 0 | 0 | 19193.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5450.7461 | 0 | 0 | 24644.3961 | 0 | 24644.3961 | 0 | 0 | 2016.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5574 | 0 | 0 | 2588.6971 | 0 | 2588.6971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0437 | 1.1484 | 0 | 0 | 5.1921 | 5.1921 | 0
CA_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 24173.5301 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22670.3256 | 0 | 0 | 0 | 0 | 114952.0822 | 0 | 0 | 339379.6917 | 0 | 339379.4139 | 0.27786 | 0.27786 | 0 | 4283.5495 | 5028.0009 | 1276.6947 | 25163.1456 | 0 | 4017.1817 | 0 | 0 | 0 | 0 | 20369.509 | 0 | 0 | 60138.0814 | 0 | 60138.0321 | 0.049236 | 0.049236 | 0 | 82.4801 | 96.8146 | 24.5829 | 484.5184 | 0 | 77.3512 | 0 | 0 | 0 | 0 | 392.2165 | 0 | 0 | 1157.9635 | 0 | 1157.9626 | 0.00094805 | 0.00094805 | 2.8693 | 0.72858 | 14.3599 | 2.2925 | 0 | 0 | 2.4445 | 0 | 11.6243 | 0 | 0 | 34.3192 | 34.3192 | 2.8098e-05
CA_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 181905.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181905.0617 | 0 | 181905.0617 | 0 | 0 | 1731.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1731.7362 | 0 | 1731.7362 | 0 | 0 | 181.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181.9051 | 0 | 181.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3912 | 0 | 0 | 0 | 5.3912 | 5.3912 | 0
CA_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 26746.4829 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 22259.0977 | 0 | 0 | 0 | 0 | 114802.0396 | 0 | 0 | 336198.2329 | 0 | 336201.5671 | -3.3343 | -3.3343 | 0 | 4739.4768 | 4107.7763 | 1276.6947 | 25163.1456 | 0 | 3944.3121 | 0 | 0 | 0 | 0 | 20342.9214 | 0 | 0 | 59574.3269 | 0 | 59574.9177 | -0.59083 | -0.59083 | 0 | 91.259 | 79.0956 | 24.5829 | 484.5184 | 0 | 75.948 | 0 | 0 | 0 | 0 | 391.7046 | 0 | 0 | 1147.1084 | 0 | 1147.1197 | -0.011377 | -0.011377 | 2.3442 | 0.72858 | 14.3599 | 2.2509 | 0 | 0 | 2.7047 | 0 | 11.6092 | 0 | 0 | 33.9978 | 33.9975 | -0.00033717
CA_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 78858.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78858.3844 | 0 | 78858.3844 | 0 | 0 | 750.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.7318 | 0 | 750.7318 | 0 | 0 | 78.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8584 | 0 | 78.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3372 | 0 | 0 | 0 | 2.3372 | 2.3372 | 0
CA_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 90297.86 | 97933.3613 | 7138.1378 | 317887.4784 | 4818.0346 | 104090.6651 | 808.5629 | 0 | 0 | 0 | 7179.8163 | 17441.0631 | 0 | 647594.9795 | 0 | 647595.8131 | -0.83357 | 4817.2011 | 0 | 16000.7808 | 17353.7916 | 1264.878 | 56329.6612 | 853.7557 | 18444.8658 | 143.2773 | 0 | 0 | 0 | 1272.2634 | 3090.5564 | 0 | 114753.8304 | 0 | 114753.9781 | -0.14771 | 853.608 | 0 | 308.0963 | 334.1486 | 24.3553 | 1084.6321 | 16.4391 | 355.1573 | 2.7588 | 0 | 0 | 0 | 24.4975 | 59.5089 | 0 | 2209.5941 | 0 | 2209.5969 | -0.0028441 | 16.4363 | 4.518 | 0.32931 | 14.6653 | 4.8021 | 0.037302 | 0 | 4.1658 | 0 | 0.33123 | 0 | 0.80462 | 29.876 | 29.8759 | -3.8456e-05
CA_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 529005.1692 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119443.9135 | 0 | 0 | 990639.4975 | 0 | 990639.4975 | 0 | 0 | 5036.1292 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.1061 | 0 | 0 | 9430.888 | 0 | 9430.888 | 0 | 0 | 529.0052 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4439 | 0 | 0 | 990.6395 | 0 | 990.6395 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.1527 | 1.615 | 0 | 0 | 13.3944 | 13.3944 | 0
CA_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 89878.2965 | 79744.8638 | 7138.1378 | 312483.1662 | 4743.0133 | 81136.9257 | 1255.9121 | 0 | 0 | 0 | 7179.8163 | 12411.8574 | 0 | 595971.9891 | 0 | 595974.212 | -2.2229 | 4740.7905 | 0 | 15926.4341 | 14130.7899 | 1264.878 | 55372.0171 | 840.462 | 14377.4632 | 222.5476 | 0 | 0 | 0 | 1272.2634 | 2199.3811 | 0 | 105606.2365 | 0 | 105606.6304 | -0.39389 | 840.0681 | 0 | 306.6647 | 272.0895 | 24.3553 | 1066.1926 | 16.1832 | 276.8392 | 4.2852 | 0 | 0 | 0 | 24.4975 | 42.3493 | 0 | 2033.4564 | 0 | 2033.464 | -0.0075844 | 16.1756 | 3.6789 | 0.32931 | 14.416 | 3.7431 | 0.05794 | 0 | 4.1464 | 0 | 0.33123 | 0 | 0.5726 | 27.4945 | 27.4944 | -0.00010255
CA_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 794232.8339 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119387.0444 | 0 | 0 | 1255810.2931 | 0 | 1255810.2931 | 0 | 0 | 7561.0966 | 0 | 0 | 0 | 3257.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 1136.5647 | 0 | 0 | 11955.314 | 0 | 11955.314 | 0 | 0 | 794.2328 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.387 | 0 | 0 | 1255.8103 | 0 | 1255.8103 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.7388 | 1.6142 | 0 | 0 | 16.9798 | 16.9798 | 0
CA_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 31850.7099 | 85782.6892 | 10766.9459 | 53987.5506 | 0 | 45832.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228220.353 | 0 | 228220.0752 | 0.27786 | 0.27786 | 0 | 5643.9458 | 15200.6925 | 1907.9028 | 9566.594 | 0 | 8121.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40440.6466 | 0 | 40440.5973 | 0.049236 | 0.049236 | 0 | 108.6746 | 292.6905 | 36.7368 | 184.2055 | 0 | 156.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778.6878 | 0 | 778.6869 | 0.00094805 | 0.00094805 | 11.8537 | 1.4878 | 7.4601 | 6.3332 | 0 | 0 | 4.4012 | 0 | 0 | 0 | 0 | 31.536 | 31.536 | 3.8395e-05
CA_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 267066.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90810.3583 | 0 | 0 | 357876.7882 | 0 | 357876.7882 | 0 | 0 | 2542.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864.5146 | 0 | 0 | 3406.987 | 0 | 3406.987 | 0 | 0 | 267.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8104 | 0 | 0 | 357.8768 | 0 | 357.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8159 | 3.6777 | 0 | 0 | 14.4936 | 14.4936 | 0
CA_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 0 | 29688.985 | 68116.5622 | 10766.9459 | 53987.5506 | 0 | 43651.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206211.3263 | 0 | 206209.3813 | 1.945 | 1.945 | 0 | 5260.8881 | 12070.2548 | 1907.9028 | 9566.594 | 0 | 7735.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36540.647 | 0 | 36540.3024 | 0.34465 | 0.34465 | 0 | 101.2988 | 232.4137 | 36.7368 | 184.2055 | 0 | 148.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703.593 | 0 | 703.5864 | 0.0066363 | 0.0066363 | 9.4125 | 1.4878 | 7.4601 | 6.0318 | 0 | 0 | 4.1025 | 0 | 0 | 0 | 0 | 28.4945 | 28.4948 | 0.00026876
CA_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 293747.4818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90829.3146 | 0 | 0 | 384576.7964 | 0 | 384576.7964 | 0 | 0 | 2796.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864.6951 | 0 | 0 | 3661.1711 | 0 | 3661.1711 | 0 | 0 | 293.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8293 | 0 | 0 | 384.5768 | 0 | 384.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8965 | 3.6785 | 0 | 0 | 15.575 | 15.575 | 0
CA_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 19469.4167 | 61364.6452 | 79297.5145 | 12306.2718 | 154949.5496 | 0 | 47488.4832 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 374948.1238 | 0 | 374947.0124 | 1.1114 | 1.1114 | 3449.9806 | 10873.8151 | 14051.5196 | 2180.6714 | 27457.0602 | 0 | 8414.9592 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 66440.8075 | 0 | 66440.6106 | 0.19694 | 0.19694 | 66.4296 | 209.3762 | 270.5631 | 41.989 | 528.6879 | 0 | 162.0307 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1279.323 | 0 | 1279.3192 | 0.0037922 | 0.0037922 | 6.2627 | 0.97192 | 12.2376 | 3.7505 | 0.0057056 | 0 | 4.8464 | 1.5377 | 0 | 0 | 0 | 29.6125 | 29.6126 | 8.7778e-05
CA_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 49684.5734 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 597949.3865 | 0 | 0 | 1047129.3978 | 0 | 1047129.3978 | 0 | 0 | 472.9971 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5692.4782 | 0 | 0 | 9968.6719 | 0 | 9968.6719 | 0 | 0 | 49.6846 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 597.9494 | 0 | 0 | 1047.1294 | 0 | 1047.1294 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.1501 | 13.8408 | 0 | 0 | 24.238 | 24.238 | 0
CA_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 23226.0389 | 56793.903 | 50867.2203 | 12306.2718 | 154949.5496 | 0 | 50183.6929 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348398.9192 | 0 | 348401.9756 | -3.0564 | -3.0564 | 4115.6541 | 10063.8796 | 9013.6714 | 2180.6714 | 27457.0602 | 0 | 8892.5504 | 12.8014 | 0 | 0 | 0 | 0 | 0 | 0 | 61736.2885 | 0 | 61736.8301 | -0.5416 | -0.5416 | 79.2472 | 193.7808 | 173.559 | 41.989 | 528.6879 | 0 | 171.2268 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.7371 | 0 | 1188.7475 | -0.010429 | -0.010429 | 4.0174 | 0.97192 | 12.2376 | 3.9634 | 0.0057056 | 0 | 4.4855 | 1.8343 | 0 | 0 | 0 | 27.516 | 27.5158 | -0.00024139
CA_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 41201.6102 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598015.7337 | 0 | 0 | 1038712.7818 | 0 | 1038712.7818 | 0 | 0 | 392.2393 | 0 | 0 | 0 | 3803.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 5693.1098 | 0 | 0 | 9888.5457 | 0 | 9888.5457 | 0 | 0 | 41.2016 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.0157 | 0 | 0 | 1038.7128 | 0 | 1038.7128 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.9537 | 13.8423 | 0 | 0 | 24.0432 | 24.0432 | 0
CA_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 2559.0599 | 3778.8507 | 8830.2849 | 1581.0044 | 13417.6985 | 0 | 5532.1263 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40703.2233 | 0 | 40705.724 | -2.5007 | -2.5007 | 453.4654 | 669.6123 | 1564.7265 | 280.154 | 2377.6162 | 0 | 980.2928 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 7212.6112 | 0 | 7213.0543 | -0.44313 | -0.44313 | 8.7315 | 12.8934 | 30.1289 | 5.3944 | 45.7812 | 0 | 18.8756 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8794 | 0 | 138.8879 | -0.0085324 | -0.0085324 | 5.476 | 0.98044 | 8.3208 | 3.4307 | 0 | 0 | 2.3434 | 1.587 | 3.1033 | 0 | 0 | 25.2432 | 25.2416 | -0.0015508
CA_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 2919.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.2767 | 0 | 2919.2767 | 0 | 0 | 27.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7915 | 0 | 27.7915 | 0 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9193 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53058 | 0 | 0 | 0 | 0.53058 | 0.53058 | 0
CA_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Electricity | 2617.4098 | 3553.7868 | 7118.6878 | 1581.0044 | 13417.6985 | 0 | 5084.777 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38377.563 | 0 | 38380.6194 | -3.0564 | -3.0564 | 463.805 | 629.731 | 1261.4315 | 280.154 | 2377.6162 | 0 | 901.0225 | 0 | 0 | 0 | 0 | 886.744 | 0 | 0 | 6800.5042 | 0 | 6801.0458 | -0.5416 | -0.5416 | 8.9306 | 12.1255 | 24.289 | 5.3944 | 45.7812 | 0 | 17.3493 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.9442 | 0 | 130.9547 | -0.010429 | -0.010429 | 4.4146 | 0.98044 | 8.3208 | 3.1533 | 0 | 0 | 2.2038 | 1.6232 | 3.1033 | 0 | 0 | 23.8013 | 23.7994 | -0.0018954
CA_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | CA-WINNERMUCCA-NV | Zone5B | Zone5B(CA-WINNERMUCCA-NV) |  |  | CA | 0.1772 | 0.00952 |  |  |  | Natural Gas | 3213.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213.1 | 0 | 3213.1 | 0 | 0 | 30.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5887 | 0 | 30.5887 | 0 | 0 | 3.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2131 | 0 | 3.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58399 | 0 | 0 | 0 | 0.58399 | 0.58399 | 0
CO_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 597514.0936 | 880261.0392 | 95076.9947 | 4077910.5986 | 543457.0788 | 703019.0491 | 84596.2412 | 185599.9187 | 637330.9542 | 0 | 0 | 0 | 0 | 7804765.9683 | 0 | 7804762.9119 | 3.0564 | 543460.1353 | 0 | 62081.7143 | 91459.122 | 9878.4998 | 423694.9112 | 56465.1905 | 73043.6792 | 8789.5495 | 19283.8316 | 66218.6861 | 0 | 0 | 0 | 0 | 810915.1841 | 0 | 810914.8665 | 0.31756 | 56465.5081 | 0 | 2038.7181 | 3003.4507 | 324.4027 | 13913.831 | 1854.2756 | 2398.701 | 288.6424 | 633.2669 | 2174.5732 | 0 | 0 | 0 | 0 | 26629.8615 | 0 | 26629.8511 | 0.010429 | 1854.286 | 6.0239 | 0.65064 | 27.9065 | 4.811 | 0.57892 | 0 | 4.089 | 0 | 0 | 4.3615 | 0 | 53.4105 | 53.4106 | 2.0916e-05
CO_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 1238692.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561989.205 | 0 | 0 | 1800681.9209 | 0 | 1800681.9209 | 0 | 0 | 7238.9202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.2649 | 0 | 0 | 10523.1851 | 0 | 10523.1851 | 0 | 0 | 1238.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.9892 | 0 | 0 | 1800.6819 | 0 | 1800.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4844 | 1.1272 | 0 | 0 | 3.6116 | 3.6116 | 0
CO_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 554896.4379 | 716981.3467 | 95076.9947 | 4077910.5986 | 543384.8361 | 684402.6524 | 83034.6867 | 165396.9603 | 637475.4397 | 0 | 0 | 0 | 0 | 7558559.9532 | 0 | 7558560.5089 | -0.55571 | 543384.2804 | 0 | 57653.7399 | 74494.3619 | 9878.4998 | 423694.9112 | 56457.6845 | 71109.4356 | 8627.304 | 17184.7442 | 66233.6982 | 0 | 0 | 0 | 0 | 785334.3791 | 0 | 785334.4369 | -0.057739 | 56457.6267 | 0 | 1893.3066 | 2446.3404 | 324.4027 | 13913.831 | 1854.0291 | 2335.1818 | 283.3144 | 564.3344 | 2175.0662 | 0 | 0 | 0 | 0 | 25789.8066 | 0 | 25789.8085 | -0.0018961 | 1854.0272 | 4.9065 | 0.65064 | 27.9065 | 4.6836 | 0.56823 | 0 | 3.7973 | 0 | 0 | 4.3625 | 0 | 51.7257 | 51.7257 | -3.8029e-06
CO_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 1777716.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561970.2486 | 0 | 0 | 2339686.5607 | 0 | 2339686.5607 | 0 | 0 | 10388.9741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.1541 | 0 | 0 | 13673.1283 | 0 | 13673.1283 | 0 | 0 | 1777.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.9702 | 0 | 0 | 2339.6866 | 0 | 2339.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5655 | 1.1271 | 0 | 0 | 4.6926 | 4.6926 | 0
CO_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 23106.5605 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 21970.1268 | 0 | 0 | 0 | 0 | 112779.2431 | 0 | 0 | 335445.2413 | 0 | 335444.6856 | 0.55571 | 0.55571 | 0 | 2400.7716 | 2948.1337 | 749.1585 | 14754.2372 | 0 | 2282.6962 | 0 | 0 | 0 | 0 | 11717.7634 | 0 | 0 | 34852.7606 | 0 | 34852.7028 | 0.057739 | 0.057739 | 0 | 78.8396 | 96.8146 | 24.6018 | 484.5184 | 0 | 74.9621 | 0 | 0 | 0 | 0 | 384.8028 | 0 | 0 | 1144.5392 | 0 | 1144.5373 | 0.0018961 | 0.0018961 | 2.8693 | 0.72914 | 14.3599 | 2.2217 | 0 | 0 | 2.3366 | 0 | 11.4046 | 0 | 0 | 33.9213 | 33.9213 | 5.6196e-05
CO_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 162844.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162844.4594 | 0 | 162844.4594 | 0 | 0 | 951.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.663 | 0 | 951.663 | 0 | 0 | 162.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.8445 | 0 | 162.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8263 | 0 | 0 | 0 | 4.8263 | 4.8263 | 0
CO_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 25665.6204 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21886.7698 | 0 | 0 | 0 | 0 | 112651.429 | 0 | 0 | 332599.989 | 0 | 332599.989 | 0 | 0 | 0 | 2666.658 | 2408.5664 | 749.1585 | 14754.2372 | 0 | 2274.0354 | 0 | 0 | 0 | 0 | 11704.4835 | 0 | 0 | 34557.1389 | 0 | 34557.1389 | 0 | 0 | 0 | 87.5711 | 79.0956 | 24.6018 | 484.5184 | 0 | 74.6777 | 0 | 0 | 0 | 0 | 384.3667 | 0 | 0 | 1134.8312 | 0 | 1134.8312 | 0 | 0 | 2.3442 | 0.72914 | 14.3599 | 2.2133 | 0 | 0 | 2.5954 | 0 | 11.3917 | 0 | 0 | 33.6336 | 33.6336 | 0
CO_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 75522.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75522.0681 | 0 | 75522.0681 | 0 | 0 | 441.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441.351 | 0 | 441.351 | 0 | 0 | 75.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5221 | 0 | 75.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2383 | 0 | 0 | 0 | 2.2383 | 2.2383 | 0
CO_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 92737.4416 | 98636.3387 | 7110.3521 | 317887.4784 | 4818.0346 | 105916.1834 | 677.9703 | 0 | 0 | 0 | 7179.8163 | 17449.3988 | 0 | 652413.0142 | 0 | 652412.7363 | 0.27786 | 4818.3125 | 0 | 9635.4202 | 10248.3156 | 738.7656 | 33028.509 | 500.5938 | 11004.6915 | 70.4411 | 0 | 0 | 0 | 745.9829 | 1812.9925 | 0 | 67785.7122 | 0 | 67785.6833 | 0.028869 | 500.6227 | 0 | 316.4202 | 336.5472 | 24.2605 | 1084.6321 | 16.4391 | 361.386 | 2.3132 | 0 | 0 | 0 | 24.4975 | 59.5373 | 0 | 2226.0332 | 0 | 2226.0323 | 0.00094805 | 16.4401 | 4.5505 | 0.32803 | 14.6653 | 4.8863 | 0.031277 | 0 | 4.2783 | 0 | 0.33123 | 0 | 0.805 | 30.0982 | 30.0982 | 1.2819e-05
CO_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 444080.7552 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117064.8925 | 0 | 0 | 903336.0626 | 0 | 903336.0626 | 0 | 0 | 2595.2079 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 684.1272 | 0 | 0 | 5279.0959 | 0 | 5279.0959 | 0 | 0 | 444.0808 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0649 | 0 | 0 | 903.3361 | 0 | 903.3361 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.0044 | 1.5828 | 0 | 0 | 12.214 | 12.214 | 0
CO_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 87277.5581 | 80100.5203 | 7110.3521 | 312483.1662 | 4745.7919 | 84576.7912 | 1100.3124 | 0 | 0 | 0 | 7179.8163 | 12409.0788 | 0 | 596983.3874 | 0 | 596982.8317 | 0.55571 | 4746.3476 | 0 | 9068.1383 | 8322.4441 | 738.7656 | 32467.001 | 493.0878 | 8787.5286 | 114.3225 | 0 | 0 | 0 | 745.9829 | 1289.3033 | 0 | 62026.574 | 0 | 62026.5162 | 0.057739 | 493.1455 | 0 | 297.791 | 273.303 | 24.2605 | 1066.1926 | 16.1926 | 288.576 | 3.7543 | 0 | 0 | 0 | 24.4975 | 42.3398 | 0 | 2036.9073 | 0 | 2036.9054 | 0.0018961 | 16.1945 | 3.6953 | 0.32803 | 14.416 | 3.9018 | 0.050761 | 0 | 4.0264 | 0 | 0.33123 | 0 | 0.57248 | 27.541 | 27.541 | 2.5637e-05
CO_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 687868.7967 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117017.5016 | 0 | 0 | 1147076.7131 | 0 | 1147076.7131 | 0 | 0 | 4019.9052 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 683.8503 | 0 | 0 | 6703.5163 | 0 | 6703.5163 | 0 | 0 | 687.8688 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0175 | 0 | 0 | 1147.0767 | 0 | 1147.0767 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3007 | 1.5822 | 0 | 0 | 15.5096 | 15.5096 | 0
CO_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 32228.5949 | 85407.5827 | 10725.2674 | 53987.5506 | 0 | 47432.9118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229781.9075 | 0 | 229780.5182 | 1.3893 | 1.3893 | 0 | 3348.551 | 8873.8478 | 1114.3553 | 5609.3065 | 0 | 4928.2795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23874.3402 | 0 | 23874.1958 | 0.14435 | 0.14435 | 0 | 109.964 | 291.4107 | 36.5946 | 184.2055 | 0 | 161.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784.0159 | 0 | 784.0111 | 0.0047402 | 0.0047402 | 11.8018 | 1.482 | 7.4601 | 6.5544 | 0 | 0 | 4.4534 | 0 | 0 | 0 | 0 | 31.7516 | 31.7518 | 0.00019197
CO_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 219874.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90175.3208 | 0 | 0 | 310049.9363 | 0 | 310049.9363 | 0 | 0 | 1284.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526.9846 | 0 | 0 | 1811.9318 | 0 | 1811.9318 | 0 | 0 | 219.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1753 | 0 | 0 | 310.0499 | 0 | 310.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9047 | 3.652 | 0 | 0 | 12.5567 | 12.5567 | 0
CO_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 29805.6848 | 67824.8127 | 10725.2674 | 53987.5506 | 0 | 45160.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207503.3598 | 0 | 207502.8041 | 0.55571 | 0.55571 | 0 | 3096.8107 | 7046.998 | 1114.3553 | 5609.3065 | 0 | 4692.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21559.5991 | 0 | 21559.5413 | 0.057739 | 0.057739 | 0 | 101.697 | 231.4183 | 36.5946 | 184.2055 | 0 | 154.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708.0015 | 0 | 707.9996 | 0.0018961 | 0.0018961 | 9.3722 | 1.482 | 7.4601 | 6.2403 | 0 | 0 | 4.1186 | 0 | 0 | 0 | 0 | 28.6732 | 28.6733 | 7.679e-05
CO_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 242489.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90184.799 | 0 | 0 | 332674.3309 | 0 | 332674.3309 | 0 | 0 | 1417.1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527.04 | 0 | 0 | 1944.1488 | 0 | 1944.1488 | 0 | 0 | 242.4895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1848 | 0 | 0 | 332.6743 | 0 | 332.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8206 | 3.6524 | 0 | 0 | 13.473 | 13.473 | 0
CO_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 17485.5201 | 65140.7173 | 79519.7999 | 12314.6075 | 154949.5496 | 0 | 54032.0077 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 383514.4449 | 0 | 383516.9456 | -2.5007 | -2.5007 | 1816.7455 | 6768.1205 | 8262.1072 | 1279.4877 | 16099.2582 | 0 | 5613.9256 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 39847.1508 | 0 | 39847.4106 | -0.25982 | -0.25982 | 59.6606 | 222.2601 | 271.3216 | 42.0174 | 528.6879 | 0 | 184.3572 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1308.5513 | 0 | 1308.5598 | -0.0085324 | -0.0085324 | 6.2803 | 0.97258 | 12.2376 | 4.2673 | 0.0057056 | 0 | 5.1447 | 1.381 | 0 | 0 | 0 | 30.2893 | 30.2891 | -0.0001975
CO_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 30623.9711 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 585523.5041 | 0 | 0 | 1015642.9131 | 0 | 1015642.9131 | 0 | 0 | 178.9665 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3421.7994 | 0 | 0 | 5935.4172 | 0 | 5935.4172 | 0 | 0 | 30.624 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 585.5235 | 0 | 0 | 1015.6429 | 0 | 1015.6429 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.70886 | 13.5532 | 0 | 0 | 23.5092 | 23.5092 | 0
CO_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 20772.5645 | 60358.804 | 51000.5915 | 12314.6075 | 154949.5496 | 0 | 51003.37 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 350471.7299 | 0 | 350474.5085 | -2.7786 | -2.7786 | 2158.2695 | 6271.2797 | 5298.9615 | 1279.4877 | 16099.2582 | 0 | 5299.2501 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 36414.0127 | 0 | 36414.3014 | -0.28869 | -0.28869 | 70.876 | 205.9442 | 174.014 | 42.0174 | 528.6879 | 0 | 174.0235 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.8095 | 0 | 1195.819 | -0.0094805 | -0.0094805 | 4.0279 | 0.97258 | 12.2376 | 4.0281 | 0.0057056 | 0 | 4.767 | 1.6406 | 0 | 0 | 0 | 27.6797 | 27.6795 | -0.00021945
CO_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 32879.7759 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 585580.3731 | 0 | 0 | 1017955.5869 | 0 | 1017955.5869 | 0 | 0 | 192.1494 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3422.1317 | 0 | 0 | 5948.9324 | 0 | 5948.9324 | 0 | 0 | 32.8798 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 585.5804 | 0 | 0 | 1017.9556 | 0 | 1017.9556 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.76107 | 13.5545 | 0 | 0 | 23.5627 | 23.5627 | 0
CO_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 2153.3892 | 3934.4504 | 8883.0777 | 1572.6687 | 13417.6985 | 0 | 5701.6188 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40667.102 | 0 | 40666.2684 | 0.83357 | 0.83357 | 223.7371 | 408.7894 | 922.9518 | 163.4003 | 1394.0989 | 0 | 592.3982 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 4225.3119 | 0 | 4225.2253 | 0.086608 | 0.086608 | 7.3474 | 13.4243 | 30.3091 | 5.3659 | 45.7812 | 0 | 19.4539 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.7562 | 0 | 138.7533 | 0.0028441 | 0.0028441 | 5.5087 | 0.97527 | 8.3208 | 3.5358 | 0 | 0 | 2.4399 | 1.3354 | 3.1033 | 0 | 0 | 25.2187 | 25.2192 | 0.00051693
CO_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 3298.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3298.4036 | 0 | 3298.4036 | 0 | 0 | 19.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2759 | 0 | 19.2759 | 0 | 0 | 3.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2984 | 0 | 3.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59949 | 0 | 0 | 0 | 0.59949 | 0.59949 | 0
CO_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 2200.6248 | 3681.6009 | 7152.0306 | 1572.6687 | 13417.6985 | 0 | 5215.3697 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38244.1918 | 0 | 38243.914 | 0.27786 | 0.27786 | 228.6449 | 382.5183 | 743.096 | 163.4003 | 1394.0989 | 0 | 541.8769 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 3973.5715 | 0 | 3973.5427 | 0.028869 | 0.028869 | 7.5085 | 12.5616 | 24.4027 | 5.3659 | 45.7812 | 0 | 17.7948 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.4892 | 0 | 130.4882 | 0.00094805 | 0.00094805 | 4.4352 | 0.97527 | 8.3208 | 3.2342 | 0 | 0 | 2.2831 | 1.3647 | 3.1033 | 0 | 0 | 23.7165 | 23.7167 | 0.00017231
CO_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | CO-TRINIDAD-CO | Zone4B | Zone4B(CO-TRINIDAD-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 3582.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3582.7487 | 0 | 3582.7487 | 0 | 0 | 20.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9376 | 0 | 20.9376 | 0 | 0 | 3.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5827 | 0 | 3.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65117 | 0 | 0 | 0 | 0.65117 | 0.65117 | 0
CO_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 511967.5826 | 879469.1477 | 95229.8159 | 4077910.5986 | 543457.0788 | 725511.5464 | 78472.2802 | 158539.4578 | 635388.7361 | 0 | 0 | 0 | 0 | 7705946.2443 | 0 | 7705945.9664 | 0.27786 | 543457.3567 | 0 | 53193.4318 | 91376.8445 | 9894.3779 | 423694.9112 | 56465.1905 | 75380.6497 | 8153.2699 | 16472.2497 | 66016.8897 | 0 | 0 | 0 | 0 | 800647.8148 | 0 | 800647.7859 | 0.028869 | 56465.2194 | 0 | 1746.8334 | 3000.7487 | 324.9241 | 13913.831 | 1854.2756 | 2475.4454 | 267.7474 | 540.9366 | 2167.9464 | 0 | 0 | 0 | 0 | 26292.6886 | 0 | 26292.6876 | 0.00094805 | 1854.2765 | 6.0185 | 0.65169 | 27.9065 | 4.9649 | 0.53701 | 0 | 3.5036 | 0 | 0 | 4.3482 | 0 | 52.7343 | 52.7343 | 1.9015e-06
CO_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 1372477.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579182.6075 | 0 | 0 | 1951659.71 | 0 | 1951659.71 | 0 | 0 | 8020.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.7432 | 0 | 0 | 11405.4993 | 0 | 11405.4993 | 0 | 0 | 1372.4771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1826 | 0 | 0 | 1951.6597 | 0 | 1951.6597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7527 | 1.1616 | 0 | 0 | 3.9144 | 3.9144 | 0
CO_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 479211.06 | 716381.1763 | 95229.8159 | 4077910.5986 | 543384.8361 | 695300.1909 | 76085.4915 | 141448.4941 | 635174.7865 | 0 | 0 | 0 | 0 | 7460126.4499 | 0 | 7460125.3385 | 1.1114 | 543385.9475 | 0 | 49790.0291 | 74432.0042 | 9894.3779 | 423694.9112 | 56457.6845 | 72241.6898 | 7905.2826 | 14696.4985 | 65994.6603 | 0 | 0 | 0 | 0 | 775107.1381 | 0 | 775107.0227 | 0.11548 | 56457.7999 | 0 | 1635.0681 | 2444.2926 | 324.9241 | 13913.831 | 1854.0291 | 2372.3643 | 259.6037 | 482.6223 | 2167.2164 | 0 | 0 | 0 | 0 | 25453.9514 | 0 | 25453.9477 | 0.0037922 | 1854.0329 | 4.9024 | 0.65169 | 27.9065 | 4.7582 | 0.52068 | 0 | 3.2794 | 0 | 0 | 4.3467 | 0 | 51.0521 | 51.0521 | 7.6059e-06
CO_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 2016831.6151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579154.173 | 0 | 0 | 2595985.7881 | 0 | 2595985.7881 | 0 | 0 | 11786.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.577 | 0 | 0 | 15170.9409 | 0 | 15170.9409 | 0 | 0 | 2016.8316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1542 | 0 | 0 | 2595.9858 | 0 | 2595.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0451 | 1.1616 | 0 | 0 | 5.2067 | 5.2067 | 0
CO_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 19997.3444 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 21547.7846 | 0 | 0 | 0 | 0 | 116174.6516 | 0 | 0 | 335300.7558 | 0 | 335302.9787 | -2.2229 | -2.2229 | 0 | 2077.7241 | 2948.1337 | 748.2925 | 14754.2372 | 0 | 2238.8148 | 0 | 0 | 0 | 0 | 12070.5463 | 0 | 0 | 34837.7485 | 0 | 34837.9795 | -0.23095 | -0.23095 | 0 | 68.2309 | 96.8146 | 24.5734 | 484.5184 | 0 | 73.521 | 0 | 0 | 0 | 0 | 396.3879 | 0 | 0 | 1144.0462 | 0 | 1144.0538 | -0.0075844 | -0.0075844 | 2.8693 | 0.72829 | 14.3599 | 2.179 | 0 | 0 | 2.0222 | 0 | 11.748 | 0 | 0 | 33.9069 | 33.9067 | -0.00022478
CO_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 185317.2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185317.2033 | 0 | 185317.2033 | 0 | 0 | 1082.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.9937 | 0 | 1082.9937 | 0 | 0 | 185.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185.3172 | 0 | 185.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4923 | 0 | 0 | 0 | 5.4923 | 5.4923 | 0
CO_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 23134.3462 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 21381.0706 | 0 | 0 | 0 | 0 | 116032.9447 | 0 | 0 | 332936.1956 | 0 | 332939.5299 | -3.3343 | -3.3343 | 0 | 2403.6586 | 2408.5664 | 748.2925 | 14754.2372 | 0 | 2221.4932 | 0 | 0 | 0 | 0 | 12055.8229 | 0 | 0 | 34592.0707 | 0 | 34592.4172 | -0.34643 | -0.34643 | 0 | 78.9344 | 79.0956 | 24.5734 | 484.5184 | 0 | 72.9522 | 0 | 0 | 0 | 0 | 395.9044 | 0 | 0 | 1135.9783 | 0 | 1135.9897 | -0.011377 | -0.011377 | 2.3442 | 0.72829 | 14.3599 | 2.1621 | 0 | 0 | 2.3394 | 0 | 11.7336 | 0 | 0 | 33.6679 | 33.6676 | -0.00033717
CO_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 85891.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85891.1874 | 0 | 85891.1874 | 0 | 0 | 501.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.9481 | 0 | 501.9481 | 0 | 0 | 85.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8912 | 0 | 85.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5456 | 0 | 0 | 0 | 2.5456 | 2.5456 | 0
CO_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 70964.5931 | 97827.7758 | 7110.3521 | 317887.4784 | 4818.0346 | 106205.1543 | 816.8986 | 0 | 0 | 0 | 7179.8163 | 17460.513 | 0 | 630270.6163 | 0 | 630270.8941 | -0.27786 | 4817.7568 | 0 | 7373.2212 | 10164.3059 | 738.7656 | 33028.509 | 500.5938 | 11034.7155 | 84.8758 | 0 | 0 | 0 | 745.9829 | 1814.1473 | 0 | 65485.117 | 0 | 65485.1459 | -0.028869 | 500.5649 | 0 | 242.1312 | 333.7884 | 24.2605 | 1084.6321 | 16.4391 | 362.372 | 2.7873 | 0 | 0 | 0 | 24.4975 | 59.5753 | 0 | 2150.4833 | 0 | 2150.4843 | -0.00094805 | 16.4382 | 4.5132 | 0.32803 | 14.6653 | 4.8996 | 0.037687 | 0 | 3.2739 | 0 | 0.33123 | 0 | 0.80552 | 29.0767 | 29.0767 | -1.2819e-05
CO_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 537772.4775 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120505.4686 | 0 | 0 | 1000468.361 | 0 | 1000468.361 | 0 | 0 | 3142.7424 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 704.234 | 0 | 0 | 5846.7371 | 0 | 5846.7371 | 0 | 0 | 537.7725 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5055 | 0 | 0 | 1000.4684 | 0 | 1000.4684 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.2712 | 1.6294 | 0 | 0 | 13.5273 | 13.5273 | 0
CO_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 67813.6985 | 79547.5855 | 7110.3521 | 312483.1662 | 4743.0133 | 83131.9366 | 1297.5906 | 0 | 0 | 0 | 7179.8163 | 12420.1931 | 0 | 575727.3523 | 0 | 575730.4087 | -3.0564 | 4739.9569 | 0 | 7045.8433 | 8264.9941 | 738.7656 | 32467.001 | 492.7991 | 8637.4082 | 134.8197 | 0 | 0 | 0 | 745.9829 | 1290.4581 | 0 | 59818.0719 | 0 | 59818.3895 | -0.31756 | 492.4815 | 0 | 231.3803 | 271.4164 | 24.2605 | 1066.1926 | 16.1832 | 283.6462 | 4.4274 | 0 | 0 | 0 | 24.4975 | 42.3777 | 0 | 1964.3817 | 0 | 1964.3922 | -0.010429 | 16.1727 | 3.6698 | 0.32803 | 14.416 | 3.8352 | 0.059863 | 0 | 3.1285 | 0 | 0.33123 | 0 | 0.57299 | 26.5606 | 26.5604 | -0.000141
CO_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 829463.1962 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120448.5996 | 0 | 0 | 1292102.2107 | 0 | 1292102.2107 | 0 | 0 | 4847.3829 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 703.9016 | 0 | 0 | 7551.0453 | 0 | 7551.0453 | 0 | 0 | 829.4632 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4486 | 0 | 0 | 1292.1022 | 0 | 1292.1022 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.2152 | 1.6286 | 0 | 0 | 17.4705 | 17.4705 | 0
CO_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 24968.2002 | 85446.4826 | 10719.7103 | 53987.5506 | 0 | 48458.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223580.1467 | 0 | 223580.1467 | 0 | 0 | 0 | 2594.196 | 8877.8895 | 1113.7779 | 5609.3065 | 0 | 5034.8073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23229.9772 | 0 | 23229.9772 | 0 | 0 | 0 | 85.1915 | 291.5434 | 36.5757 | 184.2055 | 0 | 165.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762.8555 | 0 | 762.8555 | 0 | 0 | 11.8072 | 1.4813 | 7.4601 | 6.6961 | 0 | 0 | 3.4502 | 0 | 0 | 0 | 0 | 30.8948 | 30.8948 | 0
CO_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 269815.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91189.4851 | 0 | 0 | 361004.5847 | 0 | 361004.5847 | 0 | 0 | 1576.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.9114 | 0 | 0 | 2109.7108 | 0 | 2109.7108 | 0 | 0 | 269.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1895 | 0 | 0 | 361.0046 | 0 | 361.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9272 | 3.6931 | 0 | 0 | 14.6203 | 14.6203 | 0
CO_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 22806.4753 | 67833.1484 | 10719.7103 | 53987.5506 | 0 | 46121.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201468.313 | 0 | 201467.4794 | 0.83357 | 0.83357 | 0 | 2369.5928 | 7047.8641 | 1113.7779 | 5609.3065 | 0 | 4792.0164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20932.5577 | 0 | 20932.4711 | 0.086608 | 0.086608 | 0 | 77.8157 | 231.4467 | 36.5757 | 184.2055 | 0 | 157.3663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.4099 | 0 | 687.407 | 0.0028441 | 0.0028441 | 9.3733 | 1.4813 | 7.4601 | 6.3732 | 0 | 0 | 3.1515 | 0 | 0 | 0 | 0 | 27.8393 | 27.8394 | 0.00011518
CO_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 295396.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91198.9633 | 0 | 0 | 386595.6469 | 0 | 386595.6469 | 0 | 0 | 1726.2982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.9667 | 0 | 0 | 2259.265 | 0 | 2259.265 | 0 | 0 | 295.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.199 | 0 | 0 | 386.5956 | 0 | 386.5956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9633 | 3.6935 | 0 | 0 | 15.6567 | 15.6567 | 0
CO_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 19549.9952 | 60161.5258 | 79286.4003 | 12303.4933 | 154949.5496 | 0 | 54059.7934 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380383.0003 | 0 | 380382.7224 | 0.27786 | 0.27786 | 2031.2445 | 6250.7825 | 8237.857 | 1278.333 | 16099.2582 | 0 | 5616.8125 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 39521.7937 | 0 | 39521.7649 | 0.028869 | 0.028869 | 66.7046 | 205.2711 | 270.5252 | 41.9795 | 528.6879 | 0 | 184.452 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.8668 | 0 | 1297.8658 | 0.00094805 | 0.00094805 | 6.2619 | 0.9717 | 12.2376 | 4.2695 | 0.0057056 | 0 | 4.7514 | 1.544 | 0 | 0 | 0 | 30.0418 | 30.0418 | 2.1945e-05
CO_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 35979.1379 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605418.1854 | 0 | 0 | 1040892.7612 | 0 | 1040892.7612 | 0 | 0 | 210.2621 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3538.0639 | 0 | 0 | 6082.9773 | 0 | 6082.9773 | 0 | 0 | 35.9791 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4182 | 0 | 0 | 1040.8928 | 0 | 1040.8928 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.83281 | 14.0137 | 0 | 0 | 24.0936 | 24.0936 | 0
CO_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 23173.2461 | 55629.6835 | 50850.5489 | 12303.4933 | 154949.5496 | 0 | 51014.4843 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 347993.2484 | 0 | 347992.137 | 1.1114 | 1.1114 | 2407.7003 | 5779.9241 | 5283.372 | 1278.333 | 16099.2582 | 0 | 5300.4049 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 36156.4985 | 0 | 36156.383 | 0.11548 | 0.11548 | 79.0671 | 189.8085 | 173.5021 | 41.9795 | 528.6879 | 0 | 174.0614 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.353 | 0 | 1187.3492 | 0.0037922 | 0.0037922 | 4.0161 | 0.9717 | 12.2376 | 4.029 | 0.0057056 | 0 | 4.3935 | 1.8302 | 0 | 0 | 0 | 27.4837 | 27.4837 | 8.7778e-05
CO_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 37656.7742 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605475.0544 | 0 | 0 | 1042627.2665 | 0 | 1042627.2665 | 0 | 0 | 220.0662 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3538.3962 | 0 | 0 | 6093.1137 | 0 | 6093.1137 | 0 | 0 | 37.6568 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4751 | 0 | 0 | 1042.6273 | 0 | 1042.6273 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.87164 | 14.015 | 0 | 0 | 24.1338 | 24.1338 | 0
CO_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 2564.617 | 3295.3801 | 8833.0635 | 1575.4473 | 13417.6985 | 0 | 5712.7331 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40403.1381 | 0 | 40405.361 | -2.2229 | -2.2229 | 266.4637 | 342.39 | 917.7553 | 163.689 | 1394.0989 | 0 | 593.553 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 4197.8861 | 0 | 4198.117 | -0.23095 | -0.23095 | 8.7505 | 11.2438 | 30.1384 | 5.3754 | 45.7812 | 0 | 19.4918 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.8555 | 0 | 137.8631 | -0.0075844 | -0.0075844 | 5.4777 | 0.97699 | 8.3208 | 3.5427 | 0 | 0 | 2.0436 | 1.5904 | 3.1033 | 0 | 0 | 25.0569 | 25.0555 | -0.0013785
CO_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 3705.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705.9649 | 0 | 3705.9649 | 0 | 0 | 21.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6577 | 0 | 21.6577 | 0 | 0 | 3.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.706 | 0 | 3.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67357 | 0 | 0 | 0 | 0.67357 | 0.67357 | 0
CO_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 2617.4098 | 3067.5376 | 7118.6878 | 1575.4473 | 13417.6985 | 0 | 5220.9268 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38021.9065 | 0 | 38024.1293 | -2.2229 | -2.2229 | 271.9489 | 318.7172 | 739.6317 | 163.689 | 1394.0989 | 0 | 542.4543 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 3950.4761 | 0 | 3950.707 | -0.23095 | -0.23095 | 8.9306 | 10.4664 | 24.289 | 5.3754 | 45.7812 | 0 | 17.8138 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 129.7307 | 0 | 129.7383 | -0.0075844 | -0.0075844 | 4.4146 | 0.97699 | 8.3208 | 3.2377 | 0 | 0 | 1.9023 | 1.6232 | 3.1033 | 0 | 0 | 23.5802 | 23.5788 | -0.0013785
CO_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | CO-COLORADOSPRINGS-CO | Zone5B | Zone5B(CO-COLORADOSPRINGS-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 4047.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4047.1791 | 0 | 4047.1791 | 0 | 0 | 23.6517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6517 | 0 | 23.6517 | 0 | 0 | 4.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0472 | 0 | 4.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73558 | 0 | 0 | 0 | 0.73558 | 0.73558 | 0
CO_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 423300.7412 | 878982.8986 | 95474.3298 | 4077910.5986 | 543457.0788 | 745750.6262 | 68127.6765 | 116719.2506 | 721201.9895 | 0 | 0 | 0 | 0 | 7670925.1898 | 0 | 7670922.1334 | 3.0564 | 543460.1353 | 0 | 43980.947 | 91326.3232 | 9919.7829 | 423694.9112 | 56465.1905 | 77483.4901 | 7078.4656 | 12127.1301 | 74932.8867 | 0 | 0 | 0 | 0 | 797009.1272 | 0 | 797008.8097 | 0.31756 | 56465.5081 | 0 | 1444.3021 | 2999.0896 | 325.7584 | 13913.831 | 1854.2756 | 2544.5011 | 232.4516 | 398.2461 | 2460.7412 | 0 | 0 | 0 | 0 | 26173.1967 | 0 | 26173.1863 | 0.010429 | 1854.286 | 6.0152 | 0.65336 | 27.9065 | 5.1034 | 0.46622 | 0 | 2.8968 | 0 | 0 | 4.9354 | 0 | 52.4946 | 52.4946 | 2.0916e-05
CO_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 1849115.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618109.4566 | 0 | 0 | 2467224.8324 | 0 | 2467224.8324 | 0 | 0 | 10806.2303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612.2317 | 0 | 0 | 14418.4619 | 0 | 14418.4619 | 0 | 0 | 1849.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.1095 | 0 | 0 | 2467.2248 | 0 | 2467.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7087 | 1.2397 | 0 | 0 | 4.9484 | 4.9484 | 0
CO_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 392939.3431 | 716214.4623 | 95474.3298 | 4077910.5986 | 543384.8361 | 717320.3319 | 65510.2667 | 103840.5941 | 721224.218 | 0 | 0 | 0 | 0 | 7433818.9805 | 0 | 7433820.3698 | -1.3893 | 543383.4468 | 0 | 40826.3977 | 74414.6826 | 9919.7829 | 423694.9112 | 56457.6845 | 74529.5825 | 6806.5167 | 10789.0377 | 74935.1963 | 0 | 0 | 0 | 0 | 772373.7921 | 0 | 772373.9364 | -0.14435 | 56457.5401 | 0 | 1340.709 | 2443.7237 | 325.7584 | 13913.831 | 1854.0291 | 2447.497 | 223.521 | 354.3041 | 2460.817 | 0 | 0 | 0 | 0 | 25364.1904 | 0 | 25364.1951 | -0.0047402 | 1854.0243 | 4.9013 | 0.65336 | 27.9065 | 4.9089 | 0.44831 | 0 | 2.689 | 0 | 0 | 4.9356 | 0 | 50.8721 | 50.872 | -9.5073e-06
CO_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 2656683.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618128.413 | 0 | 0 | 3274812.4095 | 0 | 3274812.4095 | 0 | 0 | 15525.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612.3424 | 0 | 0 | 19138.0037 | 0 | 19138.0037 | 0 | 0 | 2656.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.1284 | 0 | 0 | 3274.8124 | 0 | 3274.8124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3284 | 1.2398 | 0 | 0 | 6.5682 | 6.5682 | 0
CO_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 21417.192 | 28374.723 | 7207.602 | 142004.2074 | 0 | 21519.999 | 0 | 0 | 0 | 0 | 123582.3103 | 0 | 0 | 344106.0336 | 0 | 344103.5329 | 2.5007 | 2.5007 | 0 | 2225.2462 | 2948.1337 | 748.8698 | 14754.2372 | 0 | 2235.9279 | 0 | 0 | 0 | 0 | 12840.202 | 0 | 0 | 35752.6169 | 0 | 35752.3571 | 0.25982 | 0.25982 | 0 | 73.0755 | 96.8146 | 24.5923 | 484.5184 | 0 | 73.4262 | 0 | 0 | 0 | 0 | 421.6628 | 0 | 0 | 1174.0898 | 0 | 1174.0813 | 0.0085324 | 0.0085324 | 2.8693 | 0.72886 | 14.3599 | 2.1762 | 0 | 0 | 2.1658 | 0 | 12.497 | 0 | 0 | 34.7969 | 34.7971 | 0.00025288
CO_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 107055.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107055.9437 | 0 | 107055.9437 | 0 | 0 | 625.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.6349 | 0 | 625.6349 | 0 | 0 | 107.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0559 | 0 | 107.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1729 | 0 | 0 | 0 | 3.1729 | 3.1729 | 0
CO_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 20411.3508 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 20369.6723 | 0 | 0 | 0 | 0 | 123568.4175 | 0 | 0 | 336742.8319 | 0 | 336741.7205 | 1.1114 | 1.1114 | 0 | 2120.7394 | 2408.5664 | 748.8698 | 14754.2372 | 0 | 2116.409 | 0 | 0 | 0 | 0 | 12838.7586 | 0 | 0 | 34987.5802 | 0 | 34987.4648 | 0.11548 | 0.11548 | 0 | 69.6435 | 79.0956 | 24.5923 | 484.5184 | 0 | 69.5013 | 0 | 0 | 0 | 0 | 421.6154 | 0 | 0 | 1148.9665 | 0 | 1148.9628 | 0.0037922 | 0.0037922 | 2.3442 | 0.72886 | 14.3599 | 2.0598 | 0 | 0 | 2.0641 | 0 | 12.4956 | 0 | 0 | 34.0524 | 34.0525 | 0.00011239
CO_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 95056.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95056.579 | 0 | 95056.579 | 0 | 0 | 555.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.5106 | 0 | 555.5106 | 0 | 0 | 95.0566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0566 | 0 | 95.0566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8172 | 0 | 0 | 0 | 2.8172 | 2.8172 | 0
CO_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 50594.9207 | 96752.4704 | 7115.9093 | 317887.4784 | 4818.0346 | 102718.0531 | 944.7127 | 0 | 0 | 14715.2891 | 7179.8163 | 17471.6273 | 0 | 620198.312 | 0 | 620196.367 | 1.945 | 4819.9796 | 0 | 5256.8123 | 10052.5817 | 739.343 | 33028.509 | 500.5938 | 10672.4057 | 98.1556 | 0 | 0 | 1528.9185 | 745.9829 | 1815.3021 | 0 | 64438.6046 | 0 | 64438.4025 | 0.20209 | 500.7959 | 0 | 172.6299 | 330.1194 | 24.2795 | 1084.6321 | 16.4391 | 350.474 | 3.2234 | 0 | 0 | 50.2086 | 24.4975 | 59.6132 | 0 | 2116.1166 | 0 | 2116.11 | 0.0066363 | 16.4458 | 4.4635 | 0.32828 | 14.6653 | 4.7388 | 0.043583 | 0.67887 | 2.3341 | 0 | 0.33123 | 0 | 0.80603 | 28.6119 | 28.612 | 8.973e-05
CO_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 482145.0908 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 128258.6127 | 0 | 0 | 952594.1183 | 0 | 952594.1183 | 0 | 0 | 2817.6559 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 749.5433 | 0 | 0 | 5566.96 | 0 | 5566.96 | 0 | 0 | 482.1451 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 128.2586 | 0 | 0 | 952.5941 | 0 | 952.5941 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.5191 | 1.7342 | 0 | 0 | 12.88 | 12.88 | 0
CO_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 44384.8242 | 79047.4435 | 7115.9093 | 312483.1662 | 4743.0133 | 80197.7702 | 764.1058 | 0 | 0 | 20405.7937 | 7179.8163 | 12420.1931 | 0 | 568742.0357 | 0 | 568745.6478 | -3.6121 | 4739.4012 | 0 | 4611.5832 | 8213.0294 | 739.343 | 32467.001 | 492.7991 | 8332.5483 | 79.3906 | 0 | 0 | 2120.162 | 745.9829 | 1290.4581 | 0 | 59092.2975 | 0 | 59092.6728 | -0.3753 | 492.4238 | 0 | 151.441 | 269.7099 | 24.2795 | 1066.1926 | 16.1832 | 273.6348 | 2.6071 | 0 | 0 | 69.6246 | 24.4975 | 42.3777 | 0 | 1940.5478 | 0 | 1940.5602 | -0.012325 | 16.1708 | 3.6467 | 0.32828 | 14.416 | 3.6998 | 0.035251 | 0.94139 | 2.0476 | 0 | 0.33123 | 0 | 0.57299 | 26.2383 | 26.2382 | -0.00016664
CO_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 522778.0107 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 128182.7873 | 0 | 0 | 993151.2128 | 0 | 993151.2128 | 0 | 0 | 3055.1147 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 749.1002 | 0 | 0 | 5803.9757 | 0 | 5803.9757 | 0 | 0 | 522.778 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 128.1828 | 0 | 0 | 993.1512 | 0 | 993.1512 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.0685 | 1.7332 | 0 | 0 | 13.4284 | 13.4284 | 0
CO_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 18063.462 | 90945.2661 | 10708.596 | 53987.5506 | 0 | 48577.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222282.556 | 0 | 222282.2782 | 0.27786 | 0.27786 | 0 | 1876.7937 | 9449.2131 | 1112.6231 | 5609.3065 | 0 | 5047.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23095.1576 | 0 | 23095.1287 | 0.028869 | 0.028869 | 0 | 61.6325 | 310.3052 | 36.5377 | 184.2055 | 0 | 165.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.4281 | 0 | 758.4271 | 0.00094805 | 0.00094805 | 12.567 | 1.4797 | 7.4601 | 6.7126 | 0 | 0 | 2.4961 | 0 | 0 | 0 | 0 | 30.7155 | 30.7155 | 3.8395e-05
CO_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 382368.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93464.2462 | 0 | 0 | 475832.6288 | 0 | 475832.6288 | 0 | 0 | 2234.5608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.2051 | 0 | 0 | 2780.7659 | 0 | 2780.7659 | 0 | 0 | 382.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4642 | 0 | 0 | 475.8326 | 0 | 475.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4855 | 3.7852 | 0 | 0 | 19.2707 | 19.2707 | 0
CO_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 16040.6655 | 75271.3714 | 10708.596 | 53987.5506 | 0 | 50050.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206058.5052 | 0 | 206058.2273 | 0.27786 | 0.27786 | 0 | 1666.6251 | 7820.6955 | 1112.6231 | 5609.3065 | 0 | 5200.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21409.4787 | 0 | 21409.4498 | 0.028869 | 0.028869 | 0 | 54.7308 | 256.8259 | 36.5377 | 184.2055 | 0 | 170.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703.0716 | 0 | 703.0707 | 0.00094805 | 0.00094805 | 10.4012 | 1.4797 | 7.4601 | 6.9161 | 0 | 0 | 2.2165 | 0 | 0 | 0 | 0 | 28.4736 | 28.4737 | 3.8395e-05
CO_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 406964.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93473.7244 | 0 | 0 | 500437.9612 | 0 | 500437.9612 | 0 | 0 | 2378.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.2604 | 0 | 0 | 2924.5594 | 0 | 2924.5594 | 0 | 0 | 406.9642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4737 | 0 | 0 | 500.438 | 0 | 500.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4816 | 3.7856 | 0 | 0 | 20.2672 | 20.2672 | 0
CO_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 26299.1336 | 51792.483 | 79114.1291 | 12309.0504 | 154949.5496 | 0 | 53745.8153 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378282.4038 | 0 | 378281.2924 | 1.1114 | 1.1114 | 2732.48 | 5381.239 | 8219.958 | 1278.9103 | 16099.2582 | 0 | 5584.1902 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 39303.5418 | 0 | 39303.4263 | 0.11548 | 0.11548 | 89.7326 | 176.716 | 269.9374 | 41.9985 | 528.6879 | 0 | 183.3807 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.6996 | 0 | 1290.6958 | 0.0037922 | 0.0037922 | 6.2483 | 0.97214 | 12.2376 | 4.2447 | 0.0057056 | 0 | 4.0905 | 2.077 | 0 | 0 | 0 | 29.8758 | 29.8759 | 8.7778e-05
CO_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 55466.2579 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649757.0703 | 0 | 0 | 1104718.766 | 0 | 1104718.766 | 0 | 0 | 324.1448 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.1803 | 0 | 0 | 6455.9765 | 0 | 6455.9765 | 0 | 0 | 55.4663 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.7571 | 0 | 0 | 1104.7188 | 0 | 1104.7188 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2839 | 15.04 | 0 | 0 | 25.571 | 25.571 | 0
CO_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 30958.79 | 47255.0836 | 50839.4346 | 12309.0504 | 154949.5496 | 0 | 50581.0279 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 346965.1788 | 0 | 346966.0123 | -0.83357 | -0.83357 | 3216.6183 | 4909.8032 | 5282.2173 | 1278.9103 | 16099.2582 | 0 | 5255.3688 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 36049.6821 | 0 | 36049.7687 | -0.086608 | -0.086608 | 105.6314 | 161.2343 | 173.4642 | 41.9985 | 528.6879 | 0 | 172.5825 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.8452 | 0 | 1183.848 | -0.0028441 | -0.0028441 | 4.0152 | 0.97214 | 12.2376 | 3.9948 | 0.0057056 | 0 | 3.7321 | 2.4451 | 0 | 0 | 0 | 27.4026 | 27.4026 | -6.5834e-05
CO_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 56992.2434 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649832.8956 | 0 | 0 | 1106320.577 | 0 | 1106320.577 | 0 | 0 | 333.0627 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.6234 | 0 | 0 | 6465.3375 | 0 | 6465.3375 | 0 | 0 | 56.9922 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.8329 | 0 | 0 | 1106.3206 | 0 | 1106.3206 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3192 | 15.0417 | 0 | 0 | 25.6081 | 25.6081 | 0
CO_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 3664.9295 | 2456.2529 | 8796.9421 | 1581.0044 | 13417.6985 | 0 | 5634.9332 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40555.9593 | 0 | 40556.2372 | -0.27786 | -0.27786 | 380.7862 | 255.2047 | 914.0023 | 164.2664 | 1394.0989 | 0 | 585.4696 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 4213.7642 | 0 | 4213.793 | -0.028869 | -0.028869 | 12.5047 | 8.3807 | 30.0152 | 5.3944 | 45.7812 | 0 | 19.2264 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.3769 | 0 | 138.3779 | -0.00094805 | -0.00094805 | 5.4553 | 0.98044 | 8.3208 | 3.4944 | 0 | 0 | 1.5232 | 2.2728 | 3.1033 | 0 | 0 | 25.1505 | 25.1503 | -0.00017231
CO_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 11620.2379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11620.2379 | 0 | 11620.2379 | 0 | 0 | 67.9087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9087 | 0 | 67.9087 | 0 | 0 | 11.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6202 | 0 | 11.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.112 | 0 | 0 | 0 | 2.112 | 2.112 | 0
CO_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 3801.0792 | 2186.732 | 7115.9093 | 1581.0044 | 13417.6985 | 0 | 5059.7699 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38166.3919 | 0 | 38166.6698 | -0.27786 | -0.27786 | 394.9321 | 227.2015 | 739.343 | 164.2664 | 1394.0989 | 0 | 525.7101 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 3965.4881 | 0 | 3965.517 | -0.028869 | -0.028869 | 12.9693 | 7.4611 | 24.2795 | 5.3944 | 45.7812 | 0 | 17.2639 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.2237 | 0 | 130.2247 | -0.00094805 | -0.00094805 | 4.4128 | 0.98044 | 8.3208 | 3.1378 | 0 | 0 | 1.3561 | 2.3572 | 3.1033 | 0 | 0 | 23.6686 | 23.6684 | -0.00017231
CO_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | CO-EAGLECOUNTY-CO | Zone6B | Zone6B(CO-EAGLECOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 12549.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12549.0987 | 0 | 12549.0987 | 0 | 0 | 73.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3369 | 0 | 73.3369 | 0 | 0 | 12.5491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5491 | 0 | 12.5491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2808 | 0 | 0 | 0 | 2.2808 | 2.2808 | 0
CO_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 348932.404 | 878724.4919 | 95232.5945 | 4077910.5986 | 543457.0788 | 817273.7111 | 59225.1488 | 97811.1044 | 797126.3241 | 9063.6845 | 0 | 0 | 0 | 7724757.1407 | 0 | 7724757.6964 | -0.55571 | 543456.5231 | 0 | 36254.0768 | 91299.4747 | 9894.6666 | 423694.9112 | 56465.1905 | 84914.7386 | 6153.493 | 10162.5737 | 82821.4251 | 941.7168 | 0 | 0 | 0 | 802602.2669 | 0 | 802602.3247 | -0.057739 | 56465.1328 | 0 | 1190.5574 | 2998.208 | 324.9336 | 13913.831 | 1854.2756 | 2788.5379 | 202.0762 | 333.7315 | 2719.795 | 30.9253 | 0 | 0 | 0 | 26356.8714 | 0 | 26356.8733 | -0.0018961 | 1854.2737 | 6.0134 | 0.65171 | 27.9065 | 5.5929 | 0.4053 | 0.062026 | 2.3879 | 0 | 0 | 5.455 | 0 | 52.863 | 52.863 | -3.8029e-06
CO_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 631179.8547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641387.8451 | 0 | 0 | 1272567.6998 | 0 | 1272567.6998 | 0 | 0 | 3688.6151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3748.2706 | 0 | 0 | 7436.8856 | 0 | 7436.8856 | 0 | 0 | 631.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641.3878 | 0 | 0 | 1272.5677 | 0 | 1272.5677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2659 | 1.2864 | 0 | 0 | 2.5523 | 2.5523 | 0
CO_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 320577.131 | 716358.9478 | 95232.5945 | 4077910.5986 | 543384.8361 | 788373.8391 | 57027.3026 | 86741.2947 | 796998.51 | 8327.3643 | 0 | 0 | 0 | 7490932.4187 | 0 | 7490935.4751 | -3.0564 | 543381.7797 | 0 | 33307.9639 | 74429.6947 | 9894.6666 | 423694.9112 | 56457.6845 | 81912.0419 | 5925.1367 | 9012.4205 | 82808.1452 | 865.2132 | 0 | 0 | 0 | 778307.8783 | 0 | 778308.1959 | -0.31756 | 56457.3669 | 0 | 1093.8092 | 2444.2167 | 324.9336 | 13913.831 | 1854.0291 | 2689.9315 | 194.5772 | 295.9613 | 2719.3589 | 28.413 | 0 | 0 | 0 | 25559.0614 | 0 | 25559.0718 | -0.010429 | 1854.0186 | 4.9023 | 0.65171 | 27.9065 | 5.3951 | 0.39026 | 0.056987 | 2.1938 | 0 | 0 | 5.4541 | 0 | 51.2629 | 51.2629 | -2.0916e-05
CO_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 630032.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641435.236 | 0 | 0 | 1271468.232 | 0 | 1271468.232 | 0 | 0 | 3681.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3748.5475 | 0 | 0 | 7430.4603 | 0 | 7430.4603 | 0 | 0 | 630.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641.4352 | 0 | 0 | 1271.4682 | 0 | 1271.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2636 | 1.2865 | 0 | 0 | 2.5501 | 2.5501 | 0
CO_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 22161.8479 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21675.5987 | 0 | 0 | 0 | 0 | 128028.017 | 0 | 0 | 349449.2174 | 0 | 349450.6067 | -1.3893 | -1.3893 | 0 | 2302.616 | 2948.1337 | 748.5812 | 14754.2372 | 0 | 2252.0947 | 0 | 0 | 0 | 0 | 13302.111 | 0 | 0 | 36307.7737 | 0 | 36307.918 | -0.14435 | -0.14435 | 0 | 75.6162 | 96.8146 | 24.5829 | 484.5184 | 0 | 73.9571 | 0 | 0 | 0 | 0 | 436.8316 | 0 | 0 | 1192.3207 | 0 | 1192.3255 | -0.0047402 | -0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.1919 | 0 | 0 | 2.2411 | 0 | 12.9466 | 0 | 0 | 35.3376 | 35.3374 | -0.00014049
CO_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 98828.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98828.8911 | 0 | 98828.8911 | 0 | 0 | 577.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.556 | 0 | 577.556 | 0 | 0 | 98.8289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8289 | 0 | 98.8289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.929 | 0 | 0 | 0 | 2.929 | 2.929 | 0
CO_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 20486.3721 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20058.4729 | 0 | 0 | 0 | 0 | 128003.0099 | 0 | 0 | 340938.4676 | 0 | 340938.1898 | 0.27786 | 0.27786 | 0 | 2128.5341 | 2408.5664 | 748.5812 | 14754.2372 | 0 | 2084.0753 | 0 | 0 | 0 | 0 | 13299.5127 | 0 | 0 | 35423.5068 | 0 | 35423.4779 | 0.028869 | 0.028869 | 0 | 69.8995 | 79.0956 | 24.5829 | 484.5184 | 0 | 68.4395 | 0 | 0 | 0 | 0 | 436.7463 | 0 | 0 | 1163.2821 | 0 | 1163.2811 | 0.00094805 | 0.00094805 | 2.3442 | 0.72858 | 14.3599 | 2.0284 | 0 | 0 | 2.0716 | 0 | 12.9441 | 0 | 0 | 34.4768 | 34.4768 | 2.8098e-05
CO_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 78564.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78564.5611 | 0 | 78564.5611 | 0 | 0 | 459.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.1313 | 0 | 459.1313 | 0 | 0 | 78.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5646 | 0 | 78.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3285 | 0 | 0 | 0 | 2.3285 | 2.3285 | 0
CO_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 39308.3829 | 95832.7649 | 7104.795 | 317887.4784 | 4818.0346 | 105077.0562 | 883.5842 | 0 | 0 | 16821.4427 | 7179.8163 | 17429.9488 | 0 | 612343.304 | 0 | 612345.249 | -1.945 | 4816.0896 | 0 | 4084.141 | 9957.0243 | 738.1882 | 33028.509 | 500.5938 | 10917.5061 | 91.8044 | 0 | 0 | 1747.7479 | 745.9829 | 1810.9717 | 0 | 63622.4693 | 0 | 63622.6714 | -0.20209 | 500.3917 | 0 | 134.1202 | 326.9814 | 24.2416 | 1084.6321 | 16.4391 | 358.5229 | 3.0148 | 0 | 0 | 57.3948 | 24.4975 | 59.471 | 0 | 2089.3154 | 0 | 2089.322 | -0.0066363 | 16.4325 | 4.4211 | 0.32777 | 14.6653 | 4.8476 | 0.040763 | 0.77603 | 1.8134 | 0 | 0.33123 | 0 | 0.80411 | 28.2497 | 28.2496 | -8.973e-05
CO_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 410575.42 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 132552.2242 | 0 | 0 | 885318.0591 | 0 | 885318.0591 | 0 | 0 | 2399.4028 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 774.6352 | 0 | 0 | 5173.7987 | 0 | 5173.7987 | 0 | 0 | 410.5754 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 132.5522 | 0 | 0 | 885.3181 | 0 | 885.3181 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.5514 | 1.7922 | 0 | 0 | 11.9704 | 11.9704 | 0
CO_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 33590.0926 | 78652.8871 | 7104.795 | 312483.1662 | 4743.0133 | 82028.8456 | 558.4919 | 0 | 0 | 22295.2191 | 7179.8163 | 12400.7431 | 0 | 561037.0702 | 0 | 561041.7938 | -4.7236 | 4738.2898 | 0 | 3490.0106 | 8172.035 | 738.1882 | 32467.001 | 492.7991 | 8522.7971 | 58.0273 | 0 | 0 | 2316.4733 | 745.9829 | 1288.4372 | 0 | 58291.7516 | 0 | 58292.2424 | -0.49078 | 492.3083 | 0 | 114.6094 | 268.3637 | 24.2416 | 1066.1926 | 16.1832 | 279.8824 | 1.9056 | 0 | 0 | 76.0713 | 24.4975 | 42.3113 | 0 | 1914.2585 | 0 | 1914.2746 | -0.016117 | 16.167 | 3.6285 | 0.32777 | 14.416 | 3.7843 | 0.025765 | 1.0286 | 1.5496 | 0 | 0.33123 | 0 | 0.57209 | 25.8829 | 25.8827 | -0.00021792
CO_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 416764.6658 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 132495.3552 | 0 | 0 | 891450.4359 | 0 | 891450.4359 | 0 | 0 | 2435.5727 | 0 | 0 | 0 | 1999.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 774.3029 | 0 | 0 | 5209.6363 | 0 | 5209.6363 | 0 | 0 | 416.7647 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 132.4954 | 0 | 0 | 891.4504 | 0 | 891.4504 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.6351 | 1.7915 | 0 | 0 | 12.0533 | 12.0533 | 0
CO_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 15923.9657 | 90075.5747 | 10697.4817 | 53987.5506 | 0 | 47791.3469 | 0 | 0 | 0 | 4409.5853 | 0 | 0 | 0 | 222885.505 | 0 | 222884.9493 | 0.55571 | 0.55571 | 0 | 1654.5 | 9358.8522 | 1111.4684 | 5609.3065 | 0 | 4965.5209 | 0 | 0 | 0 | 458.1559 | 0 | 0 | 0 | 23157.804 | 0 | 23157.7462 | 0.057739 | 0.057739 | 0 | 54.3326 | 307.3379 | 36.4998 | 184.2055 | 0 | 163.0641 | 0 | 0 | 0 | 15.0455 | 0 | 0 | 0 | 760.4853 | 0 | 760.4834 | 0.0018961 | 0.0018961 | 12.4469 | 1.4782 | 7.4601 | 6.6039 | 0 | 0.60933 | 2.2004 | 0 | 0 | 0 | 0 | 30.7988 | 30.7989 | 7.679e-05
CO_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 184350.4298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94791.1902 | 0 | 0 | 279141.62 | 0 | 279141.62 | 0 | 0 | 1077.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.9597 | 0 | 0 | 1631.3036 | 0 | 1631.3036 | 0 | 0 | 184.3504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7912 | 0 | 0 | 279.1416 | 0 | 279.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.466 | 3.8389 | 0 | 0 | 11.3049 | 11.3049 | 0
CO_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 0 | 13698.3337 | 74535.0513 | 10697.4817 | 53987.5506 | 0 | 49252.873 | 0 | 0 | 0 | 4587.4136 | 0 | 0 | 0 | 206758.704 | 0 | 206755.9254 | 2.7786 | 2.7786 | 0 | 1423.2569 | 7744.1918 | 1111.4684 | 5609.3065 | 0 | 5117.3735 | 0 | 0 | 0 | 476.6323 | 0 | 0 | 0 | 21482.2293 | 0 | 21481.9406 | 0.28869 | 0.28869 | 0 | 46.7387 | 254.3136 | 36.4998 | 184.2055 | 0 | 168.0508 | 0 | 0 | 0 | 15.6523 | 0 | 0 | 0 | 705.4607 | 0 | 705.4512 | 0.0094805 | 0.0094805 | 10.2994 | 1.4782 | 7.4601 | 6.8059 | 0 | 0.6339 | 1.8929 | 0 | 0 | 0 | 0 | 28.57 | 28.5704 | 0.00038395
CO_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 199155.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94810.1465 | 0 | 0 | 293965.4798 | 0 | 293965.4798 | 0 | 0 | 1163.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554.0705 | 0 | 0 | 1717.9343 | 0 | 1717.9343 | 0 | 0 | 199.1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8101 | 0 | 0 | 293.9655 | 0 | 293.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0656 | 3.8397 | 0 | 0 | 11.9053 | 11.9053 | 0
CO_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 26554.7618 | 48294.2675 | 79005.765 | 12303.4933 | 154949.5496 | 0 | 54112.5861 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 375292.6661 | 0 | 375294.6111 | -1.945 | -1.945 | 2759.0397 | 5017.7744 | 8208.699 | 1278.333 | 16099.2582 | 0 | 5622.2977 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 38992.908 | 0 | 38993.1101 | -0.20209 | -0.20209 | 90.6048 | 164.78 | 269.5677 | 41.9795 | 528.6879 | 0 | 184.6321 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.4986 | 0 | 1280.5052 | -0.0066363 | -0.0066363 | 6.2397 | 0.9717 | 12.2376 | 4.2737 | 0.0057056 | 0 | 3.8142 | 2.0972 | 0 | 0 | 0 | 29.64 | 29.6398 | -0.00015361
CO_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 61465.9402 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 676333.8623 | 0 | 0 | 1137295.2405 | 0 | 1137295.2405 | 0 | 0 | 359.207 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3952.4951 | 0 | 0 | 6646.3534 | 0 | 6646.3534 | 0 | 0 | 61.4659 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 676.3339 | 0 | 0 | 1137.2952 | 0 | 1137.2952 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4228 | 15.6552 | 0 | 0 | 26.3251 | 26.3251 | 0
CO_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 30897.6615 | 43467.8972 | 50883.8917 | 12303.4933 | 154949.5496 | 0 | 50828.3203 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 343403.0563 | 0 | 343403.3341 | -0.27786 | -0.27786 | 3210.267 | 4516.3145 | 5286.8363 | 1278.333 | 16099.2582 | 0 | 5281.0625 | 7.506 | 0 | 0 | 0 | 0 | 0 | 0 | 35679.5775 | 0 | 35679.6064 | -0.028869 | -0.028869 | 105.4228 | 148.3125 | 173.6158 | 41.9795 | 528.6879 | 0 | 173.4262 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1171.6912 | 0 | 1171.6922 | -0.00094805 | -0.00094805 | 4.0187 | 0.9717 | 12.2376 | 4.0143 | 0.0057056 | 0 | 3.433 | 2.4402 | 0 | 0 | 0 | 27.1212 | 27.1212 | -2.1945e-05
CO_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 62119.934 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 676400.2095 | 0 | 0 | 1138015.5815 | 0 | 1138015.5815 | 0 | 0 | 363.0289 | 0 | 0 | 0 | 2334.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 3952.8828 | 0 | 0 | 6650.5631 | 0 | 6650.5631 | 0 | 0 | 62.1199 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 676.4002 | 0 | 0 | 1138.0156 | 0 | 1138.0156 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4379 | 15.6567 | 0 | 0 | 26.3417 | 26.3417 | 0
CO_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 3512.1083 | 2220.0748 | 8763.5993 | 1578.2259 | 13417.6985 | 0 | 5709.9545 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40205.8599 | 0 | 40208.9163 | -3.0564 | -3.0564 | 364.9081 | 230.6658 | 910.538 | 163.9777 | 1394.0989 | 0 | 593.2643 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 4177.3888 | 0 | 4177.7064 | -0.31756 | -0.31756 | 11.9833 | 7.5749 | 29.9014 | 5.3849 | 45.7812 | 0 | 19.4824 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.1824 | 0 | 137.1928 | -0.010429 | -0.010429 | 5.4346 | 0.97872 | 8.3208 | 3.541 | 0 | 0 | 1.3768 | 2.178 | 3.1033 | 0 | 0 | 24.9351 | 24.9332 | -0.0018954
CO_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 14785.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14785.9471 | 0 | 14785.9471 | 0 | 0 | 86.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4091 | 0 | 86.4091 | 0 | 0 | 14.7859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7859 | 0 | 14.7859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6874 | 0 | 0 | 0 | 2.6874 | 2.6874 | 0
CO_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Electricity | 3653.8152 | 1833.854 | 7118.6878 | 1578.2259 | 13417.6985 | 0 | 4979.1915 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37585.6715 | 0 | 37585.6715 | 0 | 0 | 379.6314 | 190.5374 | 739.6317 | 163.9777 | 1394.0989 | 0 | 517.338 | 0 | 0 | 0 | 0 | 519.9362 | 0 | 0 | 3905.1513 | 0 | 3905.1513 | 0 | 0 | 12.4668 | 6.2571 | 24.289 | 5.3849 | 45.7812 | 0 | 16.989 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.2423 | 0 | 128.2423 | 0 | 0 | 4.4146 | 0.97872 | 8.3208 | 3.0878 | 0 | 0 | 1.1372 | 2.2659 | 3.1033 | 0 | 0 | 23.3083 | 23.3083 | 0
CO_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | CO-GUNNISONCOUNTY-CO | Zone7 | Zone7(CO-GUNNISONCOUNTY-CO) |  |  | CO | 0.1039 | 0.005844 |  |  |  | Natural Gas | 15942.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15942.284 | 0 | 15942.284 | 0 | 0 | 93.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1667 | 0 | 93.1667 | 0 | 0 | 15.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9423 | 0 | 15.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8975 | 0 | 0 | 0 | 2.8975 | 2.8975 | 0
CT_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 574790.9753 | 881622.5369 | 95935.5718 | 4077910.5986 | 543457.0788 | 578514.2547 | 86813.5374 | 195049.824 | 417335.1586 | 11622.7444 | 0 | 0 | 0 | 7463052.2806 | 0 | 7463054.5035 | -2.2229 | 543454.856 | 0 | 97484.5494 | 149523.1823 | 16270.673 | 691613.6375 | 92170.3206 | 98116.0176 | 14723.5759 | 33080.4501 | 70780.0429 | 1971.2175 | 0 | 0 | 0 | 1265733.6668 | 0 | 1265734.0438 | -0.377 | 92169.9436 | 0 | 1961.1868 | 3008.0961 | 327.3322 | 13913.831 | 1854.2756 | 1973.8906 | 296.2078 | 665.51 | 1423.9476 | 39.6568 | 0 | 0 | 0 | 25463.9344 | 0 | 25463.942 | -0.0075844 | 1854.268 | 6.0332 | 0.65652 | 27.9065 | 3.959 | 0.59409 | 0.079538 | 3.9335 | 0 | 0 | 2.856 | 0 | 51.0721 | 51.0721 | -1.5212e-05
CT_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 864703.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571135.6402 | 0 | 0 | 1435838.6769 | 0 | 1435838.6769 | 0 | 0 | 7785.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5142.5053 | 0 | 0 | 12928.2914 | 0 | 12928.2914 | 0 | 0 | 864.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.1356 | 0 | 0 | 1435.8387 | 0 | 1435.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7343 | 1.1455 | 0 | 0 | 2.8798 | 2.8798 | 0
CT_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 538600.1443 | 717887.1595 | 95935.5718 | 4077910.5986 | 543387.6147 | 561503.8694 | 82712.373 | 175199.7436 | 417126.7661 | 10650.2461 | 0 | 0 | 0 | 7220914.0871 | 0 | 7220909.0857 | 5.0014 | 543392.6161 | 0 | 91346.5845 | 121753.6622 | 16270.673 | 691613.6375 | 92158.5394 | 95231.0563 | 14028.0185 | 29713.8765 | 70744.6995 | 1806.2817 | 0 | 0 | 0 | 1224667.0292 | 0 | 1224666.1809 | 0.84824 | 92159.3877 | 0 | 1837.7037 | 2449.431 | 327.3322 | 13913.831 | 1854.0385 | 1915.8512 | 282.2146 | 597.7815 | 1423.2365 | 36.3386 | 0 | 0 | 0 | 24637.7589 | 0 | 24637.7418 | 0.017065 | 1854.0556 | 4.9127 | 0.65652 | 27.9065 | 3.8426 | 0.56603 | 0.072883 | 3.6858 | 0 | 0 | 2.8545 | 0 | 49.415 | 49.4151 | 3.4226e-05
CT_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 771096.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571183.031 | 0 | 0 | 1342279.649 | 0 | 1342279.649 | 0 | 0 | 6942.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5142.932 | 0 | 0 | 12085.886 | 0 | 12085.886 | 0 | 0 | 771.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.183 | 0 | 0 | 1342.2796 | 0 | 1342.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5466 | 1.1456 | 0 | 0 | 2.6922 | 2.6922 | 0
CT_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 25512.7993 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20461.365 | 0 | 0 | 0 | 0 | 114507.5115 | 0 | 0 | 338065.4297 | 0 | 338064.874 | 0.55571 | 0.55571 | 0 | 4326.9708 | 4812.353 | 1221.938 | 24083.9136 | 0 | 3470.2475 | 0 | 0 | 0 | 0 | 19420.474 | 0 | 0 | 57335.8969 | 0 | 57335.8026 | 0.094249 | 0.094249 | 0 | 87.0497 | 96.8146 | 24.5829 | 484.5184 | 0 | 69.8142 | 0 | 0 | 0 | 0 | 390.6996 | 0 | 0 | 1153.4792 | 0 | 1153.4773 | 0.0018961 | 0.0018961 | 2.8693 | 0.72858 | 14.3599 | 2.0691 | 0 | 0 | 2.5799 | 0 | 11.5794 | 0 | 0 | 34.1862 | 34.1863 | 5.6196e-05
CT_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 100696.0908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100696.0908 | 0 | 100696.0908 | 0 | 0 | 906.6676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906.6676 | 0 | 906.6676 | 0 | 0 | 100.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6961 | 0 | 100.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9844 | 0 | 0 | 0 | 2.9844 | 2.9844 | 0
CT_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 24348.5798 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19891.7589 | 0 | 0 | 0 | 0 | 114540.8543 | 0 | 0 | 331171.8057 | 0 | 331173.7507 | -1.945 | -1.945 | 0 | 4129.5191 | 3931.5963 | 1221.938 | 24083.9136 | 0 | 3373.6423 | 0 | 0 | 0 | 0 | 19426.1289 | 0 | 0 | 56166.7383 | 0 | 56167.0681 | -0.32987 | -0.32987 | 0 | 83.0774 | 79.0956 | 24.5829 | 484.5184 | 0 | 67.8707 | 0 | 0 | 0 | 0 | 390.8134 | 0 | 0 | 1129.9582 | 0 | 1129.9648 | -0.0066363 | -0.0066363 | 2.3442 | 0.72858 | 14.3599 | 2.0115 | 0 | 0 | 2.4622 | 0 | 11.5827 | 0 | 0 | 33.4894 | 33.4892 | -0.00019668
CT_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 116808.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116808.9819 | 0 | 116808.9819 | 0 | 0 | 1051.7481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.7481 | 0 | 1051.7481 | 0 | 0 | 116.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.809 | 0 | 116.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4619 | 0 | 0 | 0 | 3.4619 | 3.4619 | 0
CT_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 87035.8228 | 98052.8397 | 7143.6949 | 317887.4784 | 4818.0346 | 91278.6941 | 841.9057 | 0 | 0 | 19399.9526 | 7179.8163 | 17613.3342 | 0 | 651251.5733 | 0 | 651252.9626 | -1.3893 | 4816.6453 | 0 | 14761.2755 | 16629.7616 | 1211.5707 | 53913.7163 | 817.1387 | 15480.8665 | 142.7872 | 0 | 0 | 3290.232 | 1217.6968 | 2987.2215 | 0 | 110452.2668 | 0 | 110452.5025 | -0.23562 | 816.9031 | 0 | 296.9662 | 334.5563 | 24.3743 | 1084.6321 | 16.4391 | 311.4429 | 2.8726 | 0 | 0 | 66.1926 | 24.4975 | 60.0967 | 0 | 2222.0704 | 0 | 2222.0751 | -0.0047402 | 16.4344 | 4.5235 | 0.32956 | 14.6653 | 4.211 | 0.03884 | 0.89499 | 4.0153 | 0 | 0.33123 | 0 | 0.81257 | 30.0447 | 30.0446 | -6.4093e-05
CT_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 426839.9618 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119443.9135 | 0 | 0 | 888474.2901 | 0 | 888474.2901 | 0 | 0 | 3843.267 | 0 | 0 | 0 | 3081.0825 | 0 | 0 | 0 | 0 | 0 | 0 | 1075.473 | 0 | 0 | 7999.8225 | 0 | 7999.8225 | 0 | 0 | 426.84 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4439 | 0 | 0 | 888.4743 | 0 | 888.4743 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.7713 | 1.615 | 0 | 0 | 12.0131 | 12.0131 | 0
CT_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 82726.2658 | 79989.3777 | 7143.6949 | 312483.1662 | 4745.7919 | 78972.4222 | 525.1491 | 0 | 0 | 22709.2255 | 7179.8163 | 12486.8787 | 0 | 608961.7884 | 0 | 608964.5669 | -2.7786 | 4743.0133 | 0 | 14030.3747 | 13566.1984 | 1211.5707 | 52997.145 | 804.8863 | 13393.7228 | 89.0653 | 0 | 0 | 3851.4846 | 1217.6968 | 2117.7746 | 0 | 103279.9193 | 0 | 103280.3906 | -0.47124 | 804.4151 | 0 | 282.262 | 272.9238 | 24.3743 | 1066.1926 | 16.1926 | 269.4539 | 1.7918 | 0 | 0 | 77.4839 | 24.4975 | 42.6052 | 0 | 2077.7776 | 0 | 2077.7871 | -0.0094805 | 16.1832 | 3.6902 | 0.32956 | 14.416 | 3.6433 | 0.024227 | 1.0477 | 3.8165 | 0 | 0.33123 | 0 | 0.57607 | 28.0938 | 28.0936 | -0.00012819
CT_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 410442.7256 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119150.0902 | 0 | 0 | 871783.2306 | 0 | 871783.2306 | 0 | 0 | 3695.6263 | 0 | 0 | 0 | 3081.0825 | 0 | 0 | 0 | 0 | 0 | 0 | 1072.8274 | 0 | 0 | 7849.5362 | 0 | 7849.5362 | 0 | 0 | 410.4427 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1501 | 0 | 0 | 871.7832 | 0 | 871.7832 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.5496 | 1.611 | 0 | 0 | 11.7874 | 11.7874 | 0
CT_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 31725.6744 | 84346.1702 | 10775.2816 | 53987.5506 | 0 | 42737.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223571.811 | 0 | 223569.0324 | 2.7786 | 2.7786 | 0 | 5380.6744 | 14305.1105 | 1827.4878 | 9156.2886 | 0 | 7248.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37917.7791 | 0 | 37917.3079 | 0.47124 | 0.47124 | 0 | 108.248 | 287.7891 | 36.7653 | 184.2055 | 0 | 145.8191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762.827 | 0 | 762.8175 | 0.0094805 | 0.0094805 | 11.6552 | 1.489 | 7.4601 | 5.9055 | 0 | 0 | 4.3839 | 0 | 0 | 0 | 0 | 30.8933 | 30.8937 | 0.00038395
CT_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 436877.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90725.0547 | 0 | 0 | 527602.3998 | 0 | 527602.3998 | 0 | 0 | 3933.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.8884 | 0 | 0 | 4750.532 | 0 | 4750.532 | 0 | 0 | 436.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7251 | 0 | 0 | 527.6024 | 0 | 527.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6931 | 3.6743 | 0 | 0 | 21.3673 | 21.3673 | 0
CT_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 0 | 29522.271 | 66738.3931 | 10775.2816 | 53987.5506 | 0 | 40922.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201946.2265 | 0 | 201945.6708 | 0.55571 | 0.55571 | 0 | 5006.9772 | 11318.8315 | 1827.4878 | 9156.2886 | 0 | 6940.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34250.08 | 0 | 34249.9858 | 0.094249 | 0.094249 | 0 | 100.73 | 227.7114 | 36.7653 | 184.2055 | 0 | 139.6284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689.0405 | 0 | 689.0386 | 0.0018961 | 0.0018961 | 9.2221 | 1.489 | 7.4601 | 5.6548 | 0 | 0 | 4.0795 | 0 | 0 | 0 | 0 | 27.9053 | 27.9054 | 7.679e-05
CT_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 465122.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90734.5329 | 0 | 0 | 555856.8282 | 0 | 555856.8282 | 0 | 0 | 4187.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.9737 | 0 | 0 | 5004.9349 | 0 | 5004.9349 | 0 | 0 | 465.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7345 | 0 | 0 | 555.8568 | 0 | 555.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.837 | 3.6747 | 0 | 0 | 22.5116 | 22.5116 | 0
CT_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 29538.9424 | 64393.2829 | 79111.3506 | 12306.2718 | 154949.5496 | 0 | 45312.8655 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 385684.5055 | 0 | 385685.0612 | -0.55571 | -0.55571 | 5009.8046 | 10921.1008 | 13417.2851 | 2087.1437 | 26279.4436 | 0 | 7685.062 | 12.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 65412.0921 | 0 | 65412.1864 | -0.094249 | -0.094249 | 100.7869 | 219.7099 | 269.9279 | 41.989 | 528.6879 | 0 | 154.6075 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1315.9555 | 0 | 1315.9574 | -0.0018961 | -0.0018961 | 6.248 | 0.97192 | 12.2376 | 3.5787 | 0.0057056 | 0 | 5.0856 | 2.3329 | 0 | 0 | 0 | 30.4606 | 30.4605 | -4.3889e-05
CT_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 75323.0265 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 596328.6192 | 0 | 0 | 1071147.0837 | 0 | 1071147.0837 | 0 | 0 | 678.2085 | 0 | 0 | 0 | 3597.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 5369.3429 | 0 | 0 | 9644.6083 | 0 | 9644.6083 | 0 | 0 | 75.323 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 596.3286 | 0 | 0 | 1071.1471 | 0 | 1071.1471 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.7435 | 13.8033 | 0 | 0 | 24.7939 | 24.7939 | 0
CT_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 33806.8208 | 59950.3547 | 50758.8562 | 12306.2718 | 154949.5496 | 0 | 42931.6338 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 354775.7297 | 0 | 354774.0626 | 1.6671 | 1.6671 | 5733.6368 | 10167.5802 | 8608.702 | 2087.1437 | 26279.4436 | 0 | 7281.2051 | 12.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 60169.9638 | 0 | 60169.681 | 0.28275 | 0.28275 | 115.3489 | 204.5506 | 173.1892 | 41.989 | 528.6879 | 0 | 146.4827 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.4948 | 0 | 1210.4891 | 0.0056883 | 0.0056883 | 4.0088 | 0.97192 | 12.2376 | 3.3906 | 0.0057056 | 0 | 4.7347 | 2.67 | 0 | 0 | 0 | 28.0193 | 28.0194 | 0.00013167
CT_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 74081.3861 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 596413.9228 | 0 | 0 | 1069990.7468 | 0 | 1069990.7468 | 0 | 0 | 667.0288 | 0 | 0 | 0 | 3597.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 5370.111 | 0 | 0 | 9634.1967 | 0 | 9634.1967 | 0 | 0 | 74.0814 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 596.4139 | 0 | 0 | 1069.9907 | 0 | 1069.9907 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.7148 | 13.8052 | 0 | 0 | 24.7672 | 24.7672 | 0
CT_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 3723.2794 | 3573.2368 | 8810.8349 | 1583.783 | 13417.6985 | 0 | 4712.4491 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40825.4803 | 0 | 40825.4803 | 0 | 0 | 631.4682 | 606.021 | 1494.3176 | 268.6096 | 2275.6417 | 0 | 799.2314 | 0 | 0 | 0 | 0 | 848.7121 | 0 | 0 | 6924.0015 | 0 | 6924.0015 | 0 | 0 | 12.7038 | 12.1919 | 30.0626 | 5.4039 | 45.7812 | 0 | 16.0789 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.2965 | 0 | 139.2965 | 0 | 0 | 5.4639 | 0.98216 | 8.3208 | 2.9224 | 0 | 0 | 2.2159 | 2.3089 | 3.1033 | 0 | 0 | 25.3174 | 25.3174 | 0
CT_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 4160.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4160.9172 | 0 | 4160.9172 | 0 | 0 | 37.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.4649 | 0 | 37.4649 | 0 | 0 | 4.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1609 | 0 | 4.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75626 | 0 | 0 | 0 | 0.75626 | 0.75626 | 0
CT_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Electricity | 3770.515 | 3364.8443 | 7107.5736 | 1583.783 | 13417.6985 | 0 | 4323.4498 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38572.0627 | 0 | 38572.6184 | -0.55571 | -0.55571 | 639.4793 | 570.6776 | 1205.4445 | 268.6096 | 2275.6417 | 0 | 733.2571 | 0 | 0 | 0 | 0 | 848.7121 | 0 | 0 | 6541.8218 | 0 | 6541.9161 | -0.094249 | -0.094249 | 12.865 | 11.4808 | 24.251 | 5.4039 | 45.7812 | 0 | 14.7516 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.6079 | 0 | 131.6098 | -0.0018961 | -0.0018961 | 4.4077 | 0.98216 | 8.3208 | 2.6811 | 0 | 0 | 2.0867 | 2.3382 | 3.1033 | 0 | 0 | 23.9204 | 23.92 | -0.00034462
CT_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | CT-HARTFORDBRADLEY-CT | Zone5A | Zone5A(CT-HARTFORDBRADLEY-CT) |  |  | CT | 0.1696 | 0.009004 |  |  |  | Natural Gas | 4530.5658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4530.5658 | 0 | 4530.5658 | 0 | 0 | 40.7932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7932 | 0 | 40.7932 | 0 | 0 | 4.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5306 | 0 | 4.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82344 | 0 | 0 | 0 | 0.82344 | 0.82344 | 0
DC_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 710154.4084 | 880419.4175 | 95365.9657 | 4077910.5986 | 543457.0788 | 583668.4959 | 100150.6575 | 256992.411 | 364589.6272 | 13592.7482 | 0 | 0 | 0 | 7626301.4089 | 0 | 7626301.6868 | -0.27786 | 543456.801 | 0 | 84863.4518 | 105210.1204 | 11396.2329 | 487310.3165 | 64943.1209 | 69748.3853 | 11968.0036 | 30710.5931 | 43568.4605 | 1624.3334 | 0 | 0 | 0 | 911343.0184 | 0 | 911343.0516 | -0.033204 | 64943.0877 | 0 | 2423.0468 | 3003.9911 | 325.3887 | 13913.831 | 1854.2756 | 1991.4769 | 341.714 | 876.8581 | 1243.9798 | 46.3785 | 0 | 0 | 0 | 26020.9404 | 0 | 26020.9414 | -0.00094805 | 1854.2746 | 6.025 | 0.65262 | 27.9065 | 3.9942 | 0.68536 | 0.09302 | 4.8598 | 0 | 0 | 2.495 | 0 | 52.1893 | 52.1893 | -1.9015e-06
DC_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 662220.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539383.7666 | 0 | 0 | 1201604.6321 | 0 | 1201604.6321 | 0 | 0 | 7104.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5786.509 | 0 | 0 | 12890.8145 | 0 | 12890.8145 | 0 | 0 | 662.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.3838 | 0 | 0 | 1201.6046 | 0 | 1201.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3282 | 1.0818 | 0 | 0 | 2.41 | 2.41 | 0
DC_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 667511.7455 | 716778.5114 | 95365.9657 | 4077910.5986 | 543384.8361 | 558608.603 | 96733.0205 | 231668.5543 | 364422.9132 | 12347.9503 | 0 | 0 | 0 | 7364732.6986 | 0 | 7364734.0878 | -1.3893 | 543383.4468 | 0 | 79767.6536 | 85655.0321 | 11396.2329 | 487310.3165 | 64934.4879 | 66753.7281 | 11559.5959 | 27684.3922 | 43548.5381 | 1475.5801 | 0 | 0 | 0 | 880085.5575 | 0 | 880085.7235 | -0.16602 | 64934.3219 | 0 | 2277.5501 | 2445.6483 | 325.3887 | 13913.831 | 1854.0291 | 1905.9726 | 330.0531 | 790.4531 | 1243.411 | 42.1312 | 0 | 0 | 0 | 25128.468 | 0 | 25128.4727 | -0.0047402 | 1854.0243 | 4.9051 | 0.65262 | 27.9065 | 3.8227 | 0.66198 | 0.084501 | 4.568 | 0 | 0 | 2.4939 | 0 | 50.3993 | 50.3993 | -9.5073e-06
DC_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 600499.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539488.0265 | 0 | 0 | 1139987.0411 | 0 | 1139987.0411 | 0 | 0 | 6442.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5787.6275 | 0 | 0 | 12229.781 | 0 | 12229.781 | 0 | 0 | 600.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.488 | 0 | 0 | 1139.987 | 0 | 1139.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2044 | 1.082 | 0 | 0 | 2.2864 | 2.2864 | 0
DC_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 32548.1301 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21508.8847 | 0 | 0 | 0 | 0 | 108272.4079 | 0 | 0 | 339913.1765 | 0 | 339914.5658 | -1.3893 | -1.3893 | 0 | 3889.5015 | 3390.7794 | 860.9764 | 16969.5028 | 0 | 2570.3117 | 0 | 0 | 0 | 0 | 12938.5527 | 0 | 0 | 40619.6246 | 0 | 40619.7906 | -0.16602 | -0.16602 | 0 | 111.0542 | 96.8146 | 24.5829 | 484.5184 | 0 | 73.3883 | 0 | 0 | 0 | 0 | 369.4255 | 0 | 0 | 1159.7838 | 0 | 1159.7885 | -0.0047402 | -0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.175 | 0 | 0 | 3.2914 | 0 | 10.9489 | 0 | 0 | 34.3733 | 34.3731 | -0.00014049
DC_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 69057.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69057.9554 | 0 | 69057.9554 | 0 | 0 | 740.8537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740.8537 | 0 | 740.8537 | 0 | 0 | 69.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.058 | 0 | 69.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0467 | 0 | 0 | 0 | 2.0467 | 2.0467 | 0
DC_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 31633.9817 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21072.6497 | 0 | 0 | 0 | 0 | 108302.9721 | 0 | 0 | 333400.2162 | 0 | 333403.8284 | -3.6121 | -3.6121 | 0 | 3780.2608 | 2770.199 | 860.9764 | 16969.5028 | 0 | 2518.1816 | 0 | 0 | 0 | 0 | 12942.2052 | 0 | 0 | 39841.3258 | 0 | 39841.7575 | -0.43165 | -0.43165 | 0 | 107.9351 | 79.0956 | 24.5829 | 484.5184 | 0 | 71.8999 | 0 | 0 | 0 | 0 | 369.5297 | 0 | 0 | 1137.5615 | 0 | 1137.5739 | -0.012325 | -0.012325 | 2.3442 | 0.72858 | 14.3599 | 2.1309 | 0 | 0 | 3.1989 | 0 | 10.9519 | 0 | 0 | 33.7149 | 33.7145 | -0.00036527
DC_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 80536.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80536.0207 | 0 | 80536.0207 | 0 | 0 | 863.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 863.9904 | 0 | 863.9904 | 0 | 0 | 80.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.536 | 0 | 80.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3869 | 0 | 0 | 0 | 2.3869 | 2.3869 | 0
DC_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 122229.1484 | 97783.3187 | 7110.3521 | 317887.4784 | 4818.0346 | 93551.5616 | 502.9206 | 0 | 0 | 21136.5568 | 7179.8163 | 17613.3342 | 0 | 689812.5217 | 0 | 689810.8546 | 1.6671 | 4819.7018 | 0 | 14606.3832 | 11685.1066 | 849.6871 | 37987.5537 | 575.7551 | 11179.4116 | 60.099 | 0 | 0 | 2525.8185 | 857.988 | 2104.7934 | 0 | 82432.5963 | 0 | 82432.3971 | 0.19922 | 575.9544 | 0 | 417.0459 | 333.6367 | 24.2605 | 1084.6321 | 16.4391 | 319.1979 | 1.716 | 0 | 0 | 72.1179 | 24.4975 | 60.0967 | 0 | 2353.6403 | 0 | 2353.6346 | 0.0056883 | 16.4448 | 4.5111 | 0.32803 | 14.6653 | 4.3159 | 0.023202 | 0.97511 | 5.6389 | 0 | 0.33123 | 0 | 0.81257 | 31.8235 | 31.8236 | 7.6911e-05
DC_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 291472.7207 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113339.9712 | 0 | 0 | 747003.1068 | 0 | 747003.1068 | 0 | 0 | 3126.9193 | 0 | 0 | 0 | 3671.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.9112 | 0 | 0 | 8013.8493 | 0 | 8013.8493 | 0 | 0 | 291.4727 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.34 | 0 | 0 | 747.0031 | 0 | 747.0031 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.941 | 1.5325 | 0 | 0 | 10.1002 | 10.1002 | 0
DC_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 117555.5992 | 79453.1143 | 7110.3521 | 312483.1662 | 4743.0133 | 81003.5545 | 366.7708 | 0 | 0 | 22698.1112 | 7179.8163 | 12489.6572 | 0 | 645083.1552 | 0 | 645088.7124 | -5.5571 | 4737.4562 | 0 | 14047.8941 | 9494.6472 | 849.6871 | 37341.7384 | 566.7901 | 9679.9248 | 43.8291 | 0 | 0 | 2712.4243 | 857.988 | 1492.514 | 0 | 77087.4371 | 0 | 77088.1011 | -0.66408 | 566.126 | 0 | 401.0997 | 271.094 | 24.2605 | 1066.1926 | 16.1832 | 276.3841 | 1.2514 | 0 | 0 | 77.446 | 24.4975 | 42.6147 | 0 | 2201.0237 | 0 | 2201.0427 | -0.018961 | 16.1642 | 3.6655 | 0.32803 | 14.416 | 3.737 | 0.01692 | 1.0471 | 5.4233 | 0 | 0.33123 | 0 | 0.57619 | 29.7603 | 29.7601 | -0.00025637
DC_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 276516.1666 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113103.0169 | 0 | 0 | 731809.5984 | 0 | 731809.5984 | 0 | 0 | 2966.4654 | 0 | 0 | 0 | 3671.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.3692 | 0 | 0 | 7850.8534 | 0 | 7850.8534 | 0 | 0 | 276.5162 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.103 | 0 | 0 | 731.8096 | 0 | 731.8096 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7388 | 1.5293 | 0 | 0 | 9.8948 | 9.8948 | 0
DC_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 46782.7272 | 84032.1922 | 10708.596 | 53987.5506 | 0 | 38791.5695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234302.6355 | 0 | 234300.4126 | 2.2229 | 2.2229 | 0 | 5590.5359 | 10041.847 | 1279.6772 | 6451.5123 | 0 | 4635.5925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27999.1649 | 0 | 27998.8993 | 0.26563 | 0.26563 | 0 | 159.6227 | 286.7178 | 36.5377 | 184.2055 | 0 | 132.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.4406 | 0 | 799.433 | 0.0075844 | 0.0075844 | 11.6118 | 1.4797 | 7.4601 | 5.3603 | 0 | 0 | 6.4645 | 0 | 0 | 0 | 0 | 32.3762 | 32.3765 | 0.00030716
DC_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 299614.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88838.8987 | 0 | 0 | 388453.3685 | 0 | 388453.3685 | 0 | 0 | 3214.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953.0637 | 0 | 0 | 4167.3277 | 0 | 4167.3277 | 0 | 0 | 299.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8389 | 0 | 0 | 388.4534 | 0 | 388.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1341 | 3.5979 | 0 | 0 | 15.732 | 15.732 | 0
DC_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 0 | 43851.3394 | 66585.572 | 10708.596 | 53987.5506 | 0 | 39961.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215094.404 | 0 | 215092.1812 | 2.2229 | 2.2229 | 0 | 5240.2351 | 7956.9759 | 1279.6772 | 6451.5123 | 0 | 4775.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25703.7813 | 0 | 25703.5156 | 0.26563 | 0.26563 | 0 | 149.6208 | 227.19 | 36.5377 | 184.2055 | 0 | 136.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733.9021 | 0 | 733.8945 | 0.0075844 | 0.0075844 | 9.201 | 1.4797 | 7.4601 | 5.522 | 0 | 0 | 6.0595 | 0 | 0 | 0 | 0 | 29.722 | 29.7223 | 0.00030716
DC_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 318731.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88857.855 | 0 | 0 | 407589.7961 | 0 | 407589.7961 | 0 | 0 | 3419.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953.2671 | 0 | 0 | 4372.6233 | 0 | 4372.6233 | 0 | 0 | 318.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8579 | 0 | 0 | 407.5898 | 0 | 407.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9083 | 3.5986 | 0 | 0 | 16.507 | 16.507 | 0
DC_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 20842.0287 | 79086.3435 | 79269.7289 | 12306.2718 | 154949.5496 | 0 | 45785.2218 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392311.387 | 0 | 392312.2206 | -0.83357 | -0.83357 | 2490.6224 | 9450.818 | 9472.7326 | 1470.5995 | 18516.4712 | 0 | 5471.334 | 8.633 | 0 | 0 | 0 | 0 | 0 | 0 | 46881.2107 | 0 | 46881.3104 | -0.099612 | -0.099612 | 71.113 | 269.8426 | 270.4683 | 41.989 | 528.6879 | 0 | 156.2192 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.5665 | 0 | 1338.5693 | -0.0028441 | -0.0028441 | 6.2606 | 0.97192 | 12.2376 | 3.616 | 0.0057056 | 0 | 6.2461 | 1.6461 | 0 | 0 | 0 | 30.984 | 30.9839 | -6.5834e-05
DC_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 51722.3802 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 559875.5728 | 0 | 0 | 1011093.3909 | 0 | 1011093.3909 | 0 | 0 | 554.8777 | 0 | 0 | 0 | 4285.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 6006.3451 | 0 | 0 | 10847.0099 | 0 | 10847.0099 | 0 | 0 | 51.7224 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 559.8756 | 0 | 0 | 1011.0934 | 0 | 1011.0934 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.1972 | 12.9595 | 0 | 0 | 23.4039 | 23.4039 | 0
DC_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 24179.0873 | 74079.3663 | 50831.0989 | 12306.2718 | 154949.5496 | 0 | 43440.1115 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 359857.7282 | 0 | 359859.3953 | -1.6671 | -1.6671 | 2889.4009 | 8852.4843 | 6074.3163 | 1470.5995 | 18516.4712 | 0 | 5191.0933 | 8.633 | 0 | 0 | 0 | 0 | 0 | 0 | 43002.9985 | 0 | 43003.1977 | -0.19922 | -0.19922 | 82.499 | 252.7588 | 173.4357 | 41.989 | 528.6879 | 0 | 148.2177 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.8346 | 0 | 1227.8403 | -0.0056883 | -0.0056883 | 4.0145 | 0.97192 | 12.2376 | 3.4308 | 0.0057056 | 0 | 5.8506 | 1.9096 | 0 | 0 | 0 | 28.4209 | 28.4208 | -0.00013167
DC_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 51940.3782 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 559979.8327 | 0 | 0 | 1011415.6488 | 0 | 1011415.6488 | 0 | 0 | 557.2164 | 0 | 0 | 0 | 4285.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 6007.4636 | 0 | 0 | 10850.4671 | 0 | 10850.4671 | 0 | 0 | 51.9404 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 559.9798 | 0 | 0 | 1011.4156 | 0 | 1011.4156 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2023 | 12.9619 | 0 | 0 | 23.4113 | 23.4113 | 0
DC_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 2428.4673 | 4959.7415 | 8844.1778 | 1578.2259 | 13417.6985 | 0 | 4856.9346 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41089.4441 | 0 | 41091.667 | -2.2229 | -2.2229 | 290.2018 | 592.6891 | 1056.8792 | 188.598 | 1603.415 | 0 | 580.4037 | 0 | 0 | 0 | 0 | 598.0017 | 0 | 0 | 4910.1886 | 0 | 4910.4542 | -0.26563 | -0.26563 | 8.2859 | 16.9226 | 30.1763 | 5.3849 | 45.7812 | 0 | 16.5719 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.1972 | 0 | 140.2048 | -0.0075844 | -0.0075844 | 5.4846 | 0.97872 | 8.3208 | 3.012 | 0 | 0 | 3.0757 | 1.506 | 3.1033 | 0 | 0 | 25.4825 | 25.4811 | -0.0013785
DC_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 2663.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2663.3661 | 0 | 2663.3661 | 0 | 0 | 28.5726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.5726 | 0 | 28.5726 | 0 | 0 | 2.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6634 | 0 | 2.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48407 | 0 | 0 | 0 | 0.48407 | 0.48407 | 0
DC_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Electricity | 2475.7029 | 4706.892 | 7124.245 | 1578.2259 | 13417.6985 | 0 | 4473.4924 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38780.4552 | 0 | 38782.9559 | -2.5007 | -2.5007 | 295.8465 | 562.4736 | 851.3473 | 188.598 | 1603.415 | 0 | 534.5823 | 0 | 0 | 0 | 0 | 598.0017 | 0 | 0 | 4634.2644 | 0 | 4634.5632 | -0.29883 | -0.29883 | 8.4471 | 16.0599 | 24.3079 | 5.3849 | 45.7812 | 0 | 15.2636 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.3189 | 0 | 132.3274 | -0.0085324 | -0.0085324 | 4.418 | 0.97872 | 8.3208 | 2.7742 | 0 | 0 | 2.9189 | 1.5353 | 3.1033 | 0 | 0 | 24.0508 | 24.0492 | -0.0015508
DC_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | DC-BALTIMORE-MD | Zone4A | Zone4A(DC-BALTIMORE-MD) |  |  | DC | 0.1195 | 0.010728 |  |  |  | Natural Gas | 2852.9295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2852.9295 | 0 | 2852.9295 | 0 | 0 | 30.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6062 | 0 | 30.6062 | 0 | 0 | 2.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8529 | 0 | 2.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51853 | 0 | 0 | 0 | 0.51853 | 0.51853 | 0
DE_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 658775.9319 | 880686.1599 | 95404.8656 | 4077910.5986 | 543457.0788 | 578483.6904 | 95827.2077 | 239637.4835 | 353222.5109 | 13781.6907 | 0 | 0 | 0 | 7537187.2183 | 0 | 7537183.6061 | 3.6121 | 543460.691 | 0 | 61529.672 | 82256.0873 | 8910.8144 | 380876.8499 | 50758.8912 | 54030.3767 | 8950.2612 | 22382.141 | 32990.9825 | 1287.2099 | 0 | 0 | 0 | 703973.2862 | 0 | 703972.9488 | 0.33737 | 50759.2285 | 0 | 2247.7435 | 3004.9012 | 325.5214 | 13913.831 | 1854.2756 | 1973.7864 | 326.9624 | 817.6431 | 1205.1952 | 47.0231 | 0 | 0 | 0 | 25716.8828 | 0 | 25716.8705 | 0.012325 | 1854.2879 | 6.0268 | 0.65289 | 27.9065 | 3.9588 | 0.65578 | 0.094313 | 4.5082 | 0 | 0 | 2.4172 | 0 | 51.5794 | 51.5794 | 2.4719e-05
DE_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 787550.7232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550018.2747 | 0 | 0 | 1337568.9979 | 0 | 1337568.9979 | 0 | 0 | 8765.4395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6121.7034 | 0 | 0 | 14887.1429 | 0 | 14887.1429 | 0 | 0 | 787.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550.0183 | 0 | 0 | 1337.569 | 0 | 1337.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5796 | 1.1032 | 0 | 0 | 2.6827 | 2.6827 | 0
DE_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 619084.1068 | 717092.4894 | 95404.8656 | 4077910.5986 | 543387.6147 | 553537.7188 | 92579.0633 | 215772.3743 | 353022.4541 | 12686.9355 | 0 | 0 | 0 | 7280478.221 | 0 | 7280476.5539 | 1.6671 | 543389.2818 | 0 | 57822.4556 | 66976.4385 | 8910.8144 | 380876.8499 | 50752.4032 | 51700.4229 | 8646.8845 | 20153.1398 | 32972.2972 | 1184.9598 | 0 | 0 | 0 | 679996.6658 | 0 | 679996.5101 | 0.15571 | 50752.5589 | 0 | 2112.315 | 2446.7196 | 325.5214 | 13913.831 | 1854.0385 | 1888.6707 | 315.8798 | 736.2153 | 1204.5126 | 43.2878 | 0 | 0 | 0 | 24840.9917 | 0 | 24840.986 | 0.0056883 | 1854.0442 | 4.9073 | 0.65289 | 27.9065 | 3.788 | 0.63355 | 0.086821 | 4.2366 | 0 | 0 | 2.4158 | 0 | 49.8227 | 49.8227 | 1.1409e-05
DE_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 731288.2989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549980.3621 | 0 | 0 | 1281268.661 | 0 | 1281268.661 | 0 | 0 | 8139.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6121.2814 | 0 | 0 | 14260.5202 | 0 | 14260.5202 | 0 | 0 | 731.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549.9804 | 0 | 0 | 1281.2687 | 0 | 1281.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4667 | 1.1031 | 0 | 0 | 2.5698 | 2.5698 | 0
DE_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 30008.5202 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21067.0926 | 0 | 0 | 0 | 0 | 110317.433 | 0 | 0 | 338976.7996 | 0 | 338974.2988 | 2.5007 | 2.5007 | 0 | 2802.7958 | 2650.1991 | 672.9305 | 13263.193 | 0 | 1967.6664 | 0 | 0 | 0 | 0 | 10303.6482 | 0 | 0 | 31660.4331 | 0 | 31660.1995 | 0.23357 | 0.23357 | 0 | 102.3891 | 96.8146 | 24.5829 | 484.5184 | 0 | 71.8809 | 0 | 0 | 0 | 0 | 376.4031 | 0 | 0 | 1156.5888 | 0 | 1156.5803 | 0.0085324 | 0.0085324 | 2.8693 | 0.72858 | 14.3599 | 2.1304 | 0 | 0 | 3.0346 | 0 | 11.1557 | 0 | 0 | 34.2782 | 34.2784 | 0.00025288
DE_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 92753.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92753.3834 | 0 | 92753.3834 | 0 | 0 | 1032.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.3452 | 0 | 1032.3452 | 0 | 0 | 92.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7534 | 0 | 92.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.749 | 0 | 0 | 0 | 2.749 | 2.749 | 0
DE_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 29124.936 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20644.7505 | 0 | 0 | 0 | 0 | 110350.7758 | 0 | 0 | 332511.0749 | 0 | 332510.797 | 0.27786 | 0.27786 | 0 | 2720.269 | 2165.1597 | 672.9305 | 13263.193 | 0 | 1928.2197 | 0 | 0 | 0 | 0 | 10306.7625 | 0 | 0 | 31056.5344 | 0 | 31056.5084 | 0.025952 | 0.025952 | 0 | 99.3743 | 79.0956 | 24.5829 | 484.5184 | 0 | 70.4399 | 0 | 0 | 0 | 0 | 376.5168 | 0 | 0 | 1134.5278 | 0 | 1134.5268 | 0.00094805 | 0.00094805 | 2.3442 | 0.72858 | 14.3599 | 2.0877 | 0 | 0 | 2.9452 | 0 | 11.159 | 0 | 0 | 33.6246 | 33.6246 | 2.8098e-05
DE_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 106373.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106373.5154 | 0 | 106373.5154 | 0 | 0 | 1183.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.9372 | 0 | 1183.9372 | 0 | 0 | 106.3735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3735 | 0 | 106.3735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1526 | 0 | 0 | 0 | 3.1526 | 3.1526 | 0
DE_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 111676.1521 | 97644.3904 | 7115.9093 | 317887.4784 | 4818.0346 | 92479.0349 | 711.3131 | 0 | 0 | 18738.6537 | 7179.8163 | 17630.0056 | 0 | 675880.7884 | 0 | 675879.9548 | 0.83357 | 4818.8682 | 0 | 10430.5526 | 9119.9861 | 664.6259 | 29690.6905 | 450.0044 | 8637.5419 | 66.4366 | 0 | 0 | 1750.1903 | 670.5948 | 1646.6425 | 0 | 63127.2656 | 0 | 63127.1878 | 0.077855 | 450.0823 | 0 | 381.039 | 333.1627 | 24.2795 | 1084.6321 | 16.4391 | 315.5385 | 2.427 | 0 | 0 | 63.9363 | 24.4975 | 60.1536 | 0 | 2306.1052 | 0 | 2306.1024 | 0.0028441 | 16.442 | 4.5047 | 0.32828 | 14.6653 | 4.2664 | 0.032815 | 0.86448 | 5.152 | 0 | 0.33123 | 0 | 0.81334 | 31.1808 | 31.1809 | 3.8456e-05
DE_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 329906.705 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 115444.1252 | 0 | 0 | 787541.245 | 0 | 787541.245 | 0 | 0 | 3671.8616 | 0 | 0 | 0 | 3808.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.8931 | 0 | 0 | 8765.3341 | 0 | 8765.3341 | 0 | 0 | 329.9067 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4441 | 0 | 0 | 787.5412 | 0 | 787.5412 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.4607 | 1.5609 | 0 | 0 | 10.6483 | 10.6483 | 0
DE_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 106485.7895 | 79453.1143 | 7115.9093 | 312483.1662 | 4743.0133 | 81286.9683 | 427.8993 | 0 | 0 | 22750.904 | 7179.8163 | 12495.2144 | 0 | 634421.7949 | 0 | 634424.0177 | -2.2229 | 4740.7905 | 0 | 9945.7727 | 7420.9209 | 664.6259 | 29185.9277 | 442.9974 | 7592.2028 | 39.9658 | 0 | 0 | 2124.9344 | 670.5948 | 1167.053 | 0 | 59254.9956 | 0 | 59255.2033 | -0.20761 | 442.7898 | 0 | 363.3295 | 271.094 | 24.2795 | 1066.1926 | 16.1832 | 277.3511 | 1.46 | 0 | 0 | 77.6261 | 24.4975 | 42.6337 | 0 | 2164.6472 | 0 | 2164.6547 | -0.0075844 | 16.1756 | 3.6655 | 0.32828 | 14.416 | 3.7501 | 0.019741 | 1.0496 | 4.9126 | 0 | 0.33123 | 0 | 0.57645 | 29.2683 | 29.2682 | -0.00010255
DE_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 326816.8211 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 115150.3019 | 0 | 0 | 784157.5379 | 0 | 784157.5379 | 0 | 0 | 3637.4712 | 0 | 0 | 0 | 3808.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 1281.6229 | 0 | 0 | 8727.6734 | 0 | 8727.6734 | 0 | 0 | 326.8168 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 115.1503 | 0 | 0 | 784.1575 | 0 | 784.1575 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.4189 | 1.5569 | 0 | 0 | 10.6026 | 10.6026 | 0
DE_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 42953.8623 | 83787.6783 | 10719.7103 | 53987.5506 | 0 | 41814.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233263.4516 | 0 | 233264.0073 | -0.55571 | -0.55571 | 0 | 4011.8907 | 7825.7692 | 1001.2209 | 5042.4372 | 0 | 3905.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21786.8064 | 0 | 21786.8583 | -0.051904 | -0.051904 | 0 | 146.5586 | 285.8836 | 36.5757 | 184.2055 | 0 | 142.6716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795.8949 | 0 | 795.8968 | -0.0018961 | -0.0018961 | 11.578 | 1.4813 | 7.4601 | 5.778 | 0 | 0 | 5.9355 | 0 | 0 | 0 | 0 | 32.233 | 32.2329 | -7.679e-05
DE_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 351687.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89464.458 | 0 | 0 | 441152.0003 | 0 | 441152.0003 | 0 | 0 | 3914.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.7394 | 0 | 0 | 4910.0218 | 0 | 4910.0218 | 0 | 0 | 351.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4645 | 0 | 0 | 441.152 | 0 | 441.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.243 | 3.6232 | 0 | 0 | 17.8662 | 17.8662 | 0
DE_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 0 | 40464.2666 | 66338.2795 | 10719.7103 | 53987.5506 | 0 | 40041.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211551.7315 | 0 | 211552.5651 | -0.83357 | -0.83357 | 0 | 3779.3625 | 6195.9953 | 1001.2209 | 5042.4372 | 0 | 3739.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19758.9317 | 0 | 19759.0096 | -0.077855 | -0.077855 | 0 | 138.0641 | 226.3462 | 36.5757 | 184.2055 | 0 | 136.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721.8145 | 0 | 721.8174 | -0.0028441 | -0.0028441 | 9.1668 | 1.4813 | 7.4601 | 5.5331 | 0 | 0 | 5.5914 | 0 | 0 | 0 | 0 | 29.2328 | 29.2327 | -0.00011518
DE_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 376842.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89473.9361 | 0 | 0 | 466316.5449 | 0 | 466316.5449 | 0 | 0 | 4194.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.8449 | 0 | 0 | 5190.1031 | 0 | 5190.1031 | 0 | 0 | 376.8426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4739 | 0 | 0 | 466.3165 | 0 | 466.3165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2617 | 3.6236 | 0 | 0 | 18.8853 | 18.8853 | 0
DE_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 25965.7056 | 74465.5871 | 79200.2647 | 12306.2718 | 154949.5496 | 0 | 45560.1579 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392519.7795 | 0 | 392522.5581 | -2.7786 | -2.7786 | 2425.1969 | 6955.0858 | 7397.3047 | 1149.4058 | 14472.2879 | 0 | 4255.3187 | 6.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 36661.3474 | 0 | 36661.6069 | -0.25952 | -0.25952 | 88.595 | 254.0766 | 270.2313 | 41.989 | 528.6879 | 0 | 155.4513 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.2775 | 0 | 1339.287 | -0.0094805 | -0.0094805 | 6.2551 | 0.97192 | 12.2376 | 3.5982 | 0.0057056 | 0 | 5.8811 | 2.0507 | 0 | 0 | 0 | 31.0006 | 31.0004 | -0.00021945
DE_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 61617.591 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 571837.0248 | 0 | 0 | 1032950.0537 | 0 | 1032950.0537 | 0 | 0 | 685.8038 | 0 | 0 | 0 | 4446.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 6364.5461 | 0 | 0 | 11496.7341 | 0 | 11496.7341 | 0 | 0 | 61.6176 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 571.837 | 0 | 0 | 1032.9501 | 0 | 1032.9501 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4263 | 13.2364 | 0 | 0 | 23.9098 | 23.9098 | 0
DE_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 29713.9921 | 69639.2168 | 50794.9775 | 12306.2718 | 154949.5496 | 0 | 43217.8262 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360694.0767 | 0 | 360694.0767 | 0 | 0 | 2775.2869 | 6504.3028 | 4744.2509 | 1149.4058 | 14472.2879 | 0 | 4036.545 | 6.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 33688.8268 | 0 | 33688.8268 | 0 | 0 | 101.3841 | 237.609 | 173.3125 | 41.989 | 528.6879 | 0 | 147.4592 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6882 | 0 | 1230.6882 | 0 | 0 | 4.0117 | 0.97192 | 12.2376 | 3.4132 | 0.0057056 | 0 | 5.5 | 2.3467 | 0 | 0 | 0 | 28.4868 | 28.4868 | 0
DE_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 61437.5057 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 571884.4157 | 0 | 0 | 1032817.3593 | 0 | 1032817.3593 | 0 | 0 | 683.7994 | 0 | 0 | 0 | 4446.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 6365.0735 | 0 | 0 | 11495.2572 | 0 | 11495.2572 | 0 | 0 | 61.4375 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 571.8844 | 0 | 0 | 1032.8174 | 0 | 1032.8174 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4221 | 13.2375 | 0 | 0 | 23.9067 | 23.9067 | 0
DE_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 2934.1664 | 4506.8352 | 8830.2849 | 1578.2259 | 13417.6985 | 0 | 4787.4704 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41058.8799 | 0 | 41059.1577 | -0.27786 | -0.27786 | 274.0511 | 420.9384 | 824.7486 | 147.4063 | 1253.213 | 0 | 447.1497 | 0 | 0 | 0 | 0 | 467.3921 | 0 | 0 | 3834.8994 | 0 | 3834.9253 | -0.025952 | -0.025952 | 10.0114 | 15.3773 | 30.1289 | 5.3849 | 45.7812 | 0 | 16.3348 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.0929 | 0 | 140.0938 | -0.00094805 | -0.00094805 | 5.476 | 0.97872 | 8.3208 | 2.9689 | 0 | 0 | 2.7949 | 1.8196 | 3.1033 | 0 | 0 | 25.4623 | 25.4622 | -0.00017231
DE_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 4009.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4009.2664 | 0 | 4009.2664 | 0 | 0 | 44.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.6231 | 0 | 44.6231 | 0 | 0 | 4.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0093 | 0 | 4.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72869 | 0 | 0 | 0 | 0.72869 | 0.72869 | 0
DE_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Electricity | 2989.7378 | 4278.9927 | 7115.9093 | 1578.2259 | 13417.6985 | 0 | 4406.8068 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38791.5695 | 0 | 38793.5144 | -1.945 | -1.945 | 279.2415 | 399.6579 | 664.6259 | 147.4063 | 1253.213 | 0 | 411.5958 | 0 | 0 | 0 | 0 | 467.3921 | 0 | 0 | 3623.1326 | 0 | 3623.3142 | -0.18166 | -0.18166 | 10.201 | 14.5999 | 24.2795 | 5.3849 | 45.7812 | 0 | 15.036 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.3568 | 0 | 132.3635 | -0.0066363 | -0.0066363 | 4.4128 | 0.97872 | 8.3208 | 2.7328 | 0 | 0 | 2.6536 | 1.8541 | 3.1033 | 0 | 0 | 24.0573 | 24.0561 | -0.0012062
DE_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | DE-WILMINGTON-DE | Zone4A | Zone4A(DE-WILMINGTON-DE) |  |  | DE | 0.0934 | 0.01113 |  |  |  | Natural Gas | 4246.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4246.2207 | 0 | 4246.2207 | 0 | 0 | 47.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.2604 | 0 | 47.2604 | 0 | 0 | 4.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2462 | 0 | 4.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77176 | 0 | 0 | 0 | 0.77176 | 0.77176 | 0
FL_1A_LO_2016_EL | 1A | LO | EL |  |  | OfficeLarge | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 1780013.7238 | 879285.7623 | 94985.302 | 4077910.5986 | 543457.0788 | 617669.8164 | 190134.5395 | 642560.2167 | 586.2776 | 32978.808 | 0 | 0 | 0 | 8859582.1237 | 0 | 8859579.0673 | 3.0564 | 543460.1353 | 0 | 162871.2557 | 80454.6473 | 8691.1551 | 373128.8198 | 49726.3227 | 56516.7882 | 17397.3104 | 58794.2598 | 53.6444 | 3017.5609 | 0 | 0 | 0 | 810651.7643 | 0 | 810651.4847 | 0.27966 | 49726.6024 | 0 | 6073.4068 | 3000.123 | 324.0899 | 13913.831 | 1854.2756 | 2107.4894 | 648.739 | 2192.4155 | 2.0004 | 112.5237 | 0 | 0 | 0 | 30228.8942 | 0 | 30228.8838 | 0.010429 | 1854.286 | 6.0172 | 0.65002 | 27.9065 | 4.2269 | 1.3012 | 0.22568 | 12.1812 | 0 | 0 | 0.0040121 | 0 | 60.629 | 60.629 | 2.0916e-05
FL_1A_LO_2016_NG | 1A | LO | NG |  |  | OfficeLarge | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 35050.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414328.7758 | 0 | 0 | 449379.0529 | 0 | 449379.0529 | 0 | 0 | 388.4272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4591.5915 | 0 | 0 | 4980.0187 | 0 | 4980.0187 | 0 | 0 | 35.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.3288 | 0 | 0 | 449.3791 | 0 | 449.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070299 | 0.831 | 0 | 0 | 0.9013 | 0.9013 | 0
FL_1A_LO_2019_EL | 1A | LO | EL |  |  | OfficeLarge | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 1687957.031 | 716178.341 | 94985.302 | 4077910.5986 | 543384.8361 | 602270.9998 | 184168.9568 | 581654.035 | 589.0561 | 27218.8392 | 0 | 0 | 0 | 8516317.9958 | 0 | 8516316.8843 | 1.1114 | 543385.9475 | 0 | 154448.0683 | 65530.3182 | 8691.1551 | 373128.8198 | 49719.7125 | 55107.7965 | 16851.4596 | 53221.3442 | 53.8986 | 2490.5238 | 0 | 0 | 0 | 779243.0966 | 0 | 779242.9949 | 0.1017 | 49719.8142 | 0 | 5759.3094 | 2443.6005 | 324.0899 | 13913.831 | 1854.0291 | 2054.9487 | 628.3845 | 1984.6036 | 2.0099 | 92.8707 | 0 | 0 | 0 | 29057.677 | 0 | 29057.6732 | 0.0037922 | 1854.0329 | 4.901 | 0.65002 | 27.9065 | 4.1215 | 1.2603 | 0.18627 | 11.5512 | 0 | 0 | 0.0040311 | 0 | 58.2799 | 58.2799 | 7.6059e-06
FL_1A_LO_2019_NG | 1A | LO | NG |  |  | OfficeLarge | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 25401.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414395.123 | 0 | 0 | 439796.6219 | 0 | 439796.6219 | 0 | 0 | 281.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4592.3268 | 0 | 0 | 4873.8262 | 0 | 4873.8262 | 0 | 0 | 25.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.3951 | 0 | 0 | 439.7966 | 0 | 439.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050947 | 0.83114 | 0 | 0 | 0.88208 | 0.88208 | 0
FL_1A_MA_2016_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 93340.3906 | 28374.723 | 7218.7162 | 142004.2074 | 0 | 32003.531 | 0 | 0 | 0 | 0 | 83170.8365 | 0 | 0 | 386112.4048 | 0 | 386109.6262 | 2.7786 | 2.7786 | 0 | 8540.6457 | 2596.2872 | 660.5125 | 12993.385 | 0 | 2928.3231 | 0 | 0 | 0 | 0 | 7610.1315 | 0 | 0 | 35329.285 | 0 | 35329.0308 | 0.25424 | 0.25424 | 0 | 318.4774 | 96.8146 | 24.6303 | 484.5184 | 0 | 109.196 | 0 | 0 | 0 | 0 | 283.7789 | 0 | 0 | 1317.4155 | 0 | 1317.406 | 0.0094805 | 0.0094805 | 2.8693 | 0.72998 | 14.3599 | 3.2363 | 0 | 0 | 9.4389 | 0 | 8.4105 | 0 | 0 | 39.0447 | 39.0449 | 0.00028098
FL_1A_MA_2016_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 435.9959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.9959 | 0 | 435.9959 | 0 | 0 | 4.8317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8317 | 0 | 4.8317 | 0 | 0 | 0.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.436 | 0 | 0.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012922 | 0 | 0 | 0 | 0.012922 | 0.012922 | 0
FL_1A_MA_2019_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 79072.4506 | 23181.5818 | 7218.7162 | 142004.2074 | 0 | 29866.8133 | 0 | 0 | 0 | 0 | 83162.5008 | 0 | 0 | 364506.2702 | 0 | 364506.8259 | -0.55571 | -0.55571 | 0 | 7235.1292 | 2121.1147 | 660.5125 | 12993.385 | 0 | 2732.8134 | 0 | 0 | 0 | 0 | 7609.3688 | 0 | 0 | 33352.3237 | 0 | 33352.3746 | -0.050848 | -0.050848 | 0 | 269.7952 | 79.0956 | 24.6303 | 484.5184 | 0 | 101.9056 | 0 | 0 | 0 | 0 | 283.7505 | 0 | 0 | 1243.6954 | 0 | 1243.6973 | -0.0018961 | -0.0018961 | 2.3442 | 0.72998 | 14.3599 | 3.0202 | 0 | 0 | 7.9961 | 0 | 8.4097 | 0 | 0 | 36.8601 | 36.8601 | -5.6196e-05
FL_1A_MA_2019_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 56.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.869 | 0 | 56.869 | 0 | 0 | 0.63022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63022 | 0 | 0.63022 | 0 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056869 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016855 | 0 | 0 | 0 | 0.0016855 | 0.0016855 | 0
FL_1A_PS_2016_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 342222.1654 | 97674.9546 | 7107.5736 | 317887.4784 | 4818.0346 | 114368.5832 | 50.0142 | 0 | 0 | 31320.0036 | 7177.0377 | 17846.7338 | 0 | 940472.5793 | 0 | 940473.135 | -0.55571 | 4817.4789 | 0 | 31313.3281 | 8937.2583 | 650.343 | 29086.7043 | 440.8502 | 10464.7254 | 4.5763 | 0 | 0 | 2865.7803 | 656.699 | 1632.9761 | 0 | 86053.241 | 0 | 86053.2918 | -0.050848 | 440.7993 | 0 | 1167.662 | 333.2669 | 24.251 | 1084.6321 | 16.4391 | 390.2256 | 0.17065 | 0 | 0 | 106.8639 | 24.4881 | 60.8931 | 0 | 3208.8924 | 0 | 3208.8943 | -0.0018961 | 16.4372 | 4.5061 | 0.3279 | 14.6653 | 5.2762 | 0.0023073 | 1.4449 | 15.788 | 0 | 0.3311 | 0 | 0.82334 | 43.3875 | 43.3875 | -2.5637e-05
FL_1A_PS_2016_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 5819.5971 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 85967.0128 | 0 | 0 | 433977.0247 | 0 | 433977.0247 | 0 | 0 | 64.4928 | 0 | 0 | 0 | 3792.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 952.6864 | 0 | 0 | 4809.3334 | 0 | 4809.3334 | 0 | 0 | 5.8196 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 85.967 | 0 | 0 | 433.977 | 0 | 433.977 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.078687 | 1.1624 | 0 | 0 | 5.8678 | 5.8678 | 0
FL_1A_PS_2019_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 327790.2901 | 79411.4358 | 7107.5736 | 312483.1662 | 4743.0133 | 105813.3764 | 47.2356 | 0 | 0 | 32339.7376 | 7177.0377 | 12595.2428 | 0 | 889508.1092 | 0 | 889512.8327 | -4.7236 | 4738.2898 | 0 | 29992.8115 | 7266.1464 | 650.343 | 28592.2097 | 433.9857 | 9681.9239 | 4.3221 | 0 | 0 | 2959.086 | 656.699 | 1152.4647 | 0 | 81389.992 | 0 | 81390.4242 | -0.43221 | 433.5535 | 0 | 1118.4205 | 270.9518 | 24.251 | 1066.1926 | 16.1832 | 361.0352 | 0.16117 | 0 | 0 | 110.3432 | 24.4881 | 42.975 | 0 | 3035.0017 | 0 | 3035.0178 | -0.016117 | 16.167 | 3.6635 | 0.3279 | 14.416 | 4.8816 | 0.0021792 | 1.492 | 15.1222 | 0 | 0.3311 | 0 | 0.58106 | 41.0365 | 41.0363 | -0.00021792
FL_1A_PS_2019_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 4559.0003 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 85862.7529 | 0 | 0 | 432612.1681 | 0 | 432612.1681 | 0 | 0 | 50.5228 | 0 | 0 | 0 | 3792.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 951.531 | 0 | 0 | 4794.208 | 0 | 4794.208 | 0 | 0 | 4.559 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8628 | 0 | 0 | 432.6122 | 0 | 432.6122 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.061642 | 1.161 | 0 | 0 | 5.8494 | 5.8494 | 0
FL_1A_RS_2016_EL | 1A | RS | EL |  |  | RetailStandalone | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 140278.7175 | 80106.0775 | 10700.2603 | 53987.5506 | 0 | 40342.0097 | 0 | 0 | 0 | 7424.3302 | 0 | 0 | 0 | 332838.9457 | 0 | 332835.6115 | 3.3343 | 3.3343 | 0 | 12835.5027 | 7329.7061 | 979.0738 | 4939.8609 | 0 | 3691.2939 | 0 | 0 | 0 | 679.3262 | 0 | 0 | 0 | 30454.7635 | 0 | 30454.4584 | 0.30509 | 0.30509 | 0 | 478.631 | 273.3219 | 36.5093 | 184.2055 | 0 | 137.6469 | 0 | 0 | 0 | 25.3318 | 0 | 0 | 0 | 1135.6465 | 0 | 1135.6351 | 0.011377 | 0.011377 | 11.0693 | 1.4786 | 7.4601 | 5.5746 | 0 | 1.0259 | 19.3841 | 0 | 0 | 0 | 0 | 45.992 | 45.9925 | 0.00046074
FL_1A_RS_2016_NG | 1A | RS | NG |  |  | RetailStandalone | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 492.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81208.9708 | 0 | 0 | 81701.8357 | 0 | 81701.8357 | 0 | 0 | 5.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899.9578 | 0 | 0 | 905.4197 | 0 | 905.4197 | 0 | 0 | 0.49286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.209 | 0 | 0 | 81.7018 | 0 | 81.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019961 | 3.2889 | 0 | 0 | 3.3088 | 3.3088 | 0
FL_1A_RS_2019_EL | 1A | RS | EL |  |  | RetailStandalone | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 148806.1387 | 63006.7781 | 10700.2603 | 53987.5506 | 0 | 39933.5604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316434.2881 | 0 | 316431.7873 | 2.5007 | 2.5007 | 0 | 13615.7617 | 5765.1202 | 979.0738 | 4939.8609 | 0 | 3653.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28953.7374 | 0 | 28953.5085 | 0.22881 | 0.22881 | 0 | 507.7265 | 214.9791 | 36.5093 | 184.2055 | 0 | 136.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.6738 | 0 | 1079.6653 | 0.0085324 | 0.0085324 | 8.7064 | 1.4786 | 7.4601 | 5.5181 | 0 | 0 | 20.5624 | 0 | 0 | 0 | 0 | 43.7253 | 43.7257 | 0.00034555
FL_1A_RS_2019_NG | 1A | RS | NG |  |  | RetailStandalone | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 862.5136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81208.9708 | 0 | 0 | 82071.4844 | 0 | 82071.4844 | 0 | 0 | 9.5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899.9578 | 0 | 0 | 909.5162 | 0 | 909.5162 | 0 | 0 | 0.86251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.209 | 0 | 0 | 82.0715 | 0 | 82.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034931 | 3.2889 | 0 | 0 | 3.3238 | 3.3238 | 0
FL_1A_SH_2016_EL | 1A | SH | EL |  |  | HotelSmall | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 108.3641 | 168653.4405 | 79580.9284 | 12328.5004 | 154949.5496 | 0 | 47927.4967 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 463620.5224 | 0 | 463618.2995 | 2.2229 | 2.2229 | 9.9153 | 15431.7898 | 7281.6549 | 1128.0578 | 14177.8838 | 0 | 4385.3659 | 6.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 42421.2778 | 0 | 42421.0744 | 0.20339 | 0.20339 | 0.36974 | 575.4455 | 271.5301 | 42.0648 | 528.6879 | 0 | 163.5286 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1581.8732 | 0 | 1581.8656 | 0.0075844 | 0.0075844 | 6.2851 | 0.97368 | 12.2376 | 3.7852 | 0.0057056 | 0 | 13.3199 | 0.0085584 | 0 | 0 | 0 | 36.6156 | 36.6157 | 0.00017556
FL_1A_SH_2016_NG | 1A | SH | NG |  |  | HotelSmall | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 18.9563 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 425200.2382 | 0 | 0 | 824714.6325 | 0 | 824714.6325 | 0 | 0 | 0.21007 | 0 | 0 | 0 | 4427.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 4712.069 | 0 | 0 | 9139.4876 | 0 | 9139.4876 | 0 | 0 | 0.018956 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 425.2002 | 0 | 0 | 824.7146 | 0 | 824.7146 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.00043878 | 9.8421 | 0 | 0 | 19.0897 | 19.0897 | 0
FL_1A_SH_2019_EL | 1A | SH | EL |  |  | HotelSmall | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 125.0355 | 160423.326 | 51178.4197 | 12328.5004 | 154949.5496 | 0 | 45854.686 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 424931.7599 | 0 | 424933.7049 | -1.945 | -1.945 | 11.4407 | 14678.7343 | 4682.8254 | 1128.0578 | 14177.8838 | 0 | 4195.7038 | 6.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 38881.256 | 0 | 38881.434 | -0.17797 | -0.17797 | 0.42662 | 547.3644 | 174.6208 | 42.0648 | 528.6879 | 0 | 156.4562 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.8672 | 0 | 1449.8738 | -0.0066363 | -0.0066363 | 4.042 | 0.97368 | 12.2376 | 3.6215 | 0.0057056 | 0 | 12.6699 | 0.009875 | 0 | 0 | 0 | 33.5603 | 33.5602 | -0.00015361
FL_1A_SH_2019_NG | 1A | SH | NG |  |  | HotelSmall | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 37.9127 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 425219.1945 | 0 | 0 | 824752.5451 | 0 | 824752.5451 | 0 | 0 | 0.42015 | 0 | 0 | 0 | 4427.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 4712.2791 | 0 | 0 | 9139.9077 | 0 | 9139.9077 | 0 | 0 | 0.037913 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 425.2192 | 0 | 0 | 824.7525 | 0 | 824.7525 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.00087757 | 9.8426 | 0 | 0 | 19.0906 | 19.0906 | 0
FL_1A_SO_2016_EL | 1A | SO | EL |  |  | OfficeSmall | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 13570.5197 | 8908.0848 | 1575.4473 | 13417.6985 | 0 | 5223.7054 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 47699.6542 | 0 | 47698.5428 | 1.1114 | 1.1114 | 0 | 1241.7026 | 815.0898 | 144.1534 | 1227.7194 | 0 | 477.969 | 0 | 0 | 0 | 0 | 457.8842 | 0 | 0 | 4364.5184 | 0 | 4364.4167 | 0.1017 | 0.1017 | 0 | 46.3026 | 30.3944 | 5.3754 | 45.7812 | 0 | 17.8233 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 162.7512 | 0 | 162.7474 | 0.0037922 | 0.0037922 | 5.5242 | 0.97699 | 8.3208 | 3.2394 | 0 | 0 | 8.4156 | 0 | 3.1033 | 0 | 0 | 29.5797 | 29.5804 | 0.00068924
FL_1A_SO_2016_NG | 1A | SO | NG |  |  | OfficeSmall | STD2016 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FL_1A_SO_2019_EL | 1A | SO | EL |  |  | OfficeSmall | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 12945.3422 | 7196.4877 | 1575.4473 | 13417.6985 | 0 | 4779.1347 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 44918.309 | 0 | 44916.9197 | 1.3893 | 1.3893 | 0 | 1184.4988 | 658.4786 | 144.1534 | 1227.7194 | 0 | 437.2908 | 0 | 0 | 0 | 0 | 457.8842 | 0 | 0 | 4110.0253 | 0 | 4109.8982 | 0.12712 | 0.12712 | 0 | 44.1695 | 24.5544 | 5.3754 | 45.7812 | 0 | 16.3064 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 153.2613 | 0 | 153.2565 | 0.0047402 | 0.0047402 | 4.4628 | 0.97699 | 8.3208 | 2.9637 | 0 | 0 | 8.0279 | 0 | 3.1033 | 0 | 0 | 27.8547 | 27.8556 | 0.00086155
FL_1A_SO_2019_NG | 1A | SO | NG |  |  | OfficeSmall | STD2019 | FL-MIAMI-FL | Zone1A | Zone1A(FL-MIAMI-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FL_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 1397857.998 | 879808.1329 | 95293.7229 | 4077910.5986 | 543457.0788 | 592721.0661 | 161834.8378 | 524968.4961 | 51128.4055 | 18082.912 | 0 | 0 | 0 | 8343063.2489 | 0 | 8343064.3603 | -1.1114 | 543455.9674 | 0 | 127904.0068 | 80502.4442 | 8719.3756 | 373128.8198 | 49726.3227 | 54233.9775 | 14807.8877 | 48034.6174 | 4678.2491 | 1654.5864 | 0 | 0 | 0 | 763390.2873 | 0 | 763390.389 | -0.1017 | 49726.221 | 0 | 4769.4915 | 3001.9053 | 325.1422 | 13913.831 | 1854.2756 | 2022.3643 | 552.1805 | 1791.1925 | 174.4501 | 61.6989 | 0 | 0 | 0 | 28466.5318 | 0 | 28466.5356 | -0.0037922 | 1854.2718 | 6.0208 | 0.65213 | 27.9065 | 4.0562 | 1.1075 | 0.12375 | 9.566 | 0 | 0 | 0.34989 | 0 | 57.0943 | 57.0943 | -7.6059e-06
FL_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 91464.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438564.4596 | 0 | 0 | 530028.8117 | 0 | 530028.8117 | 0 | 0 | 1013.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4860.1713 | 0 | 0 | 5873.7793 | 0 | 5873.7793 | 0 | 0 | 91.4644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438.5645 | 0 | 0 | 530.0288 | 0 | 530.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18345 | 0.87961 | 0 | 0 | 1.0631 | 1.0631 | 0
FL_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 1327724.1963 | 715922.7128 | 95293.7229 | 4077910.5986 | 543384.8361 | 580109.1519 | 158731.1789 | 474101.2759 | 51075.6128 | 15009.8172 | 0 | 0 | 0 | 8039263.1035 | 0 | 8039266.7156 | -3.6121 | 543381.224 | 0 | 121486.764 | 65506.9282 | 8719.3756 | 373128.8198 | 49719.7125 | 53079.9874 | 14523.9029 | 43380.2667 | 4673.4186 | 1373.3983 | 0 | 0 | 0 | 735592.574 | 0 | 735592.9045 | -0.33051 | 49719.382 | 0 | 4530.195 | 2442.7283 | 325.1422 | 13913.831 | 1854.0291 | 1979.3324 | 541.5908 | 1617.6336 | 174.27 | 51.2135 | 0 | 0 | 0 | 27429.9657 | 0 | 27429.978 | -0.012325 | 1854.0167 | 4.8993 | 0.65213 | 27.9065 | 3.9699 | 1.0862 | 0.10272 | 9.086 | 0 | 0 | 0.34953 | 0 | 55.0153 | 55.0153 | -2.4719e-05
FL_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 58243.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438573.9378 | 0 | 0 | 496817.2998 | 0 | 496817.2998 | 0 | 0 | 645.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4860.2764 | 0 | 0 | 5505.7293 | 0 | 5505.7293 | 0 | 0 | 58.2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438.5739 | 0 | 0 | 496.8173 | 0 | 496.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11682 | 0.87963 | 0 | 0 | 0.99645 | 0.99645 | 0
FL_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 74329.4373 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 27596.7243 | 0 | 0 | 0 | 0 | 88097.2352 | 0 | 0 | 367612.7078 | 0 | 367610.7628 | 1.945 | 1.945 | 0 | 6801.1435 | 2596.2872 | 659.7498 | 12993.385 | 0 | 2525.1003 | 0 | 0 | 0 | 0 | 8060.897 | 0 | 0 | 33636.5628 | 0 | 33636.3848 | 0.17797 | 0.17797 | 0 | 253.612 | 96.8146 | 24.6018 | 484.5184 | 0 | 94.16 | 0 | 0 | 0 | 0 | 300.5878 | 0 | 0 | 1254.2946 | 0 | 1254.2879 | 0.0066363 | 0.0066363 | 2.8693 | 0.72914 | 14.3599 | 2.7907 | 0 | 0 | 7.5164 | 0 | 8.9087 | 0 | 0 | 37.174 | 37.1742 | 0.00019668
FL_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 5810.1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5810.1189 | 0 | 5810.1189 | 0 | 0 | 64.3877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3877 | 0 | 64.3877 | 0 | 0 | 5.8101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8101 | 0 | 5.8101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1722 | 0 | 0 | 0 | 0.1722 | 0.1722 | 0
FL_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 64862.8606 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 26582.5475 | 0 | 0 | 0 | 0 | 88055.5567 | 0 | 0 | 351897.1346 | 0 | 351894.6339 | 2.5007 | 2.5007 | 0 | 5934.9517 | 2121.1147 | 659.7498 | 12993.385 | 0 | 2432.3031 | 0 | 0 | 0 | 0 | 8057.0834 | 0 | 0 | 32198.5878 | 0 | 32198.359 | 0.22881 | 0.22881 | 0 | 221.3121 | 79.0956 | 24.6018 | 484.5184 | 0 | 90.6997 | 0 | 0 | 0 | 0 | 300.4456 | 0 | 0 | 1200.673 | 0 | 1200.6645 | 0.0085324 | 0.0085324 | 2.3442 | 0.72914 | 14.3599 | 2.6881 | 0 | 0 | 6.5591 | 0 | 8.9045 | 0 | 0 | 35.5847 | 35.585 | 0.00025288
FL_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 1156.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.3369 | 0 | 1156.3369 | 0 | 0 | 12.8145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8145 | 0 | 12.8145 | 0 | 0 | 1.1563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1563 | 0 | 1.1563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034271 | 0 | 0 | 0 | 0.034271 | 0.034271 | 0
FL_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 287634.4444 | 98316.8035 | 7110.3521 | 317887.4784 | 4818.0346 | 105860.612 | 91.6927 | 0 | 0 | 26902.0826 | 7177.0377 | 17805.0553 | 0 | 873603.5935 | 0 | 873606.372 | -2.7786 | 4815.2561 | 0 | 26318.5517 | 8995.9875 | 650.5972 | 29086.7043 | 440.8502 | 9686.246 | 8.3899 | 0 | 0 | 2461.5406 | 656.699 | 1629.1626 | 0 | 79934.7288 | 0 | 79934.983 | -0.25424 | 440.5959 | 0 | 981.4087 | 335.4569 | 24.2605 | 1084.6321 | 16.4391 | 361.1964 | 0.31286 | 0 | 0 | 91.7899 | 24.4881 | 60.7508 | 0 | 2980.7355 | 0 | 2980.7449 | -0.0094805 | 16.4297 | 4.5357 | 0.32803 | 14.6653 | 4.8837 | 0.0042301 | 1.2411 | 13.2696 | 0 | 0.3311 | 0 | 0.82141 | 40.3027 | 40.3025 | -0.00012819
FL_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 26538.8794 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 91568.612 | 0 | 0 | 460297.9062 | 0 | 460297.9062 | 0 | 0 | 294.1039 | 0 | 0 | 0 | 3792.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 1014.7634 | 0 | 0 | 5101.0214 | 0 | 5101.0214 | 0 | 0 | 26.5389 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5686 | 0 | 0 | 460.2979 | 0 | 460.2979 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.35883 | 1.2381 | 0 | 0 | 6.2237 | 6.2237 | 0
FL_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 264202.7916 | 79047.4435 | 7110.3521 | 312483.1662 | 4743.0133 | 96307.8998 | 75.0213 | 0 | 0 | 23139.9033 | 7177.0377 | 12575.7928 | 0 | 806862.4218 | 0 | 806866.3118 | -3.89 | 4739.1233 | 0 | 24174.5554 | 7232.8411 | 650.5972 | 28592.2097 | 433.9857 | 8812.1728 | 6.8644 | 0 | 0 | 2117.3012 | 656.699 | 1150.685 | 0 | 73827.9116 | 0 | 73828.2675 | -0.35593 | 433.6298 | 0 | 901.4599 | 269.7099 | 24.2605 | 1066.1926 | 16.1832 | 328.6026 | 0.25597 | 0 | 0 | 78.9534 | 24.4881 | 42.9086 | 0 | 2753.0146 | 0 | 2753.0279 | -0.013273 | 16.1699 | 3.6467 | 0.32803 | 14.416 | 4.443 | 0.003461 | 1.0675 | 12.1886 | 0 | 0.3311 | 0 | 0.58017 | 37.2237 | 37.2235 | -0.00017946
FL_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 22074.6607 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 91398.0049 | 0 | 0 | 455663.0804 | 0 | 455663.0804 | 0 | 0 | 244.6314 | 0 | 0 | 0 | 3792.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 1012.8727 | 0 | 0 | 5049.6583 | 0 | 5049.6583 | 0 | 0 | 22.0747 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 91.398 | 0 | 0 | 455.6631 | 0 | 455.6631 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.29847 | 1.2358 | 0 | 0 | 6.161 | 6.161 | 0
FL_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 113618.3702 | 82659.5802 | 10683.5889 | 53987.5506 | 0 | 37202.2293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298151.3193 | 0 | 298152.4307 | -1.1114 | -1.1114 | 0 | 10396.0809 | 7563.3516 | 977.5484 | 4939.8609 | 0 | 3404.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27280.8457 | 0 | 27280.9474 | -0.1017 | -0.1017 | 0 | 387.6659 | 282.0345 | 36.4524 | 184.2055 | 0 | 126.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017.2923 | 0 | 1017.2961 | -0.0037922 | -0.0037922 | 11.4221 | 1.4763 | 7.4601 | 5.1407 | 0 | 0 | 15.7001 | 0 | 0 | 0 | 0 | 41.1994 | 41.1993 | -0.00015358
FL_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 6122.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82678.0874 | 0 | 0 | 88800.986 | 0 | 88800.986 | 0 | 0 | 67.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.2386 | 0 | 0 | 984.0925 | 0 | 984.0925 | 0 | 0 | 6.1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6781 | 0 | 0 | 88.801 | 0 | 88.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24797 | 3.3484 | 0 | 0 | 3.5963 | 3.5963 | 0
FL_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 0 | 107238.7811 | 64996.2318 | 10683.5889 | 53987.5506 | 0 | 35271.1255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272177.2779 | 0 | 272175.0551 | 2.2229 | 2.2229 | 0 | 9812.3485 | 5947.1552 | 977.5484 | 4939.8609 | 0 | 3227.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24904.2209 | 0 | 24904.0175 | 0.20339 | 0.20339 | 0 | 365.8987 | 221.7671 | 36.4524 | 184.2055 | 0 | 120.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928.6689 | 0 | 928.6613 | 0.0075844 | 0.0075844 | 8.9813 | 1.4763 | 7.4601 | 4.8738 | 0 | 0 | 14.8185 | 0 | 0 | 0 | 0 | 37.6098 | 37.6101 | 0.00030716
FL_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 7648.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82687.5655 | 0 | 0 | 90336.4497 | 0 | 90336.4497 | 0 | 0 | 84.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.3436 | 0 | 0 | 1001.1085 | 0 | 1001.1085 | 0 | 0 | 7.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6876 | 0 | 0 | 90.3364 | 0 | 90.3364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30977 | 3.3488 | 0 | 0 | 3.6585 | 3.6585 | 0
FL_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 880.8056 | 145269.0233 | 79911.5778 | 12314.6075 | 154949.5496 | 0 | 47285.6478 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 440683.4544 | 0 | 440682.6208 | 0.83357 | 0.83357 | 80.5937 | 13292.1156 | 7311.9094 | 1126.7866 | 14177.8838 | 0 | 4326.6368 | 6.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 40322.5361 | 0 | 40322.4598 | 0.076272 | 0.076272 | 3.0053 | 495.6579 | 272.6583 | 42.0174 | 528.6879 | 0 | 161.3386 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1503.6119 | 0 | 1503.6091 | 0.0028441 | 0.0028441 | 6.3112 | 0.97258 | 12.2376 | 3.7345 | 0.0057056 | 0 | 11.473 | 0.069564 | 0 | 0 | 0 | 34.8042 | 34.8042 | 6.5834e-05
FL_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 1507.0292 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 448677.6683 | 0 | 0 | 849680.1354 | 0 | 849680.1354 | 0 | 0 | 16.7009 | 0 | 0 | 0 | 4427.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 4972.2459 | 0 | 0 | 9416.1553 | 0 | 9416.1553 | 0 | 0 | 1.507 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 448.6777 | 0 | 0 | 849.6801 | 0 | 849.6801 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.034883 | 10.3856 | 0 | 0 | 19.6676 | 19.6676 | 0
FL_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 1055.8553 | 137969.7286 | 51220.0982 | 12314.6075 | 154949.5496 | 0 | 45171.1586 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 402753.2406 | 0 | 402754.6299 | -1.3893 | -1.3893 | 96.6108 | 12624.2302 | 4686.639 | 1126.7866 | 14177.8838 | 0 | 4133.161 | 6.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 36851.9215 | 0 | 36852.0486 | -0.12712 | -0.12712 | 3.6026 | 470.7527 | 174.763 | 42.0174 | 528.6879 | 0 | 154.124 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1374.1941 | 0 | 1374.1988 | -0.0047402 | -0.0047402 | 4.0453 | 0.97258 | 12.2376 | 3.5675 | 0.0057056 | 0 | 10.8965 | 0.083389 | 0 | 0 | 0 | 31.8087 | 31.8086 | -0.00010972
FL_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 1800.8525 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 448658.7119 | 0 | 0 | 849955.0024 | 0 | 849955.0024 | 0 | 0 | 19.957 | 0 | 0 | 0 | 4427.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 4972.0358 | 0 | 0 | 9419.2013 | 0 | 9419.2013 | 0 | 0 | 1.8009 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 448.6587 | 0 | 0 | 849.955 | 0 | 849.955 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.041684 | 10.3851 | 0 | 0 | 19.674 | 19.674 | 0
FL_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 50.0142 | 11536.6089 | 8958.099 | 1581.0044 | 13417.6985 | 0 | 5279.2767 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 45826.9003 | 0 | 45828.2896 | -1.3893 | -1.3893 | 4.5763 | 1055.5997 | 819.6661 | 144.6619 | 1227.7194 | 0 | 483.0538 | 0 | 0 | 0 | 0 | 457.8842 | 0 | 0 | 4193.1614 | 0 | 4193.2885 | -0.12712 | -0.12712 | 0.17065 | 39.3629 | 30.565 | 5.3944 | 45.7812 | 0 | 18.0129 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 156.3614 | 0 | 156.3661 | -0.0047402 | -0.0047402 | 5.5553 | 0.98044 | 8.3208 | 3.2739 | 0 | 0 | 7.1543 | 0.031016 | 3.1033 | 0 | 0 | 28.4199 | 28.419 | -0.00086155
FL_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 9.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4782 | 0 | 9.4782 | 0 | 0 | 0.10504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10504 | 0 | 0.10504 | 0 | 0 | 0.0094782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094782 | 0 | 0.0094782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017227 | 0 | 0 | 0 | 0.0017227 | 0.0017227 | 0
FL_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Electricity | 47.2356 | 11108.7096 | 7193.7091 | 1581.0044 | 13417.6985 | 0 | 4862.4917 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43215.0476 | 0 | 43214.7698 | 0.27786 | 0.27786 | 4.3221 | 1016.4469 | 658.2244 | 144.6619 | 1227.7194 | 0 | 444.918 | 0 | 0 | 0 | 0 | 457.8842 | 0 | 0 | 3954.1769 | 0 | 3954.1514 | 0.025424 | 0.025424 | 0.16117 | 37.9029 | 24.5449 | 5.3944 | 45.7812 | 0 | 16.5908 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 147.4497 | 0 | 147.4488 | 0.00094805 | 0.00094805 | 4.4611 | 0.98044 | 8.3208 | 3.0154 | 0 | 0 | 6.8889 | 0.029293 | 3.1033 | 0 | 0 | 26.7991 | 26.7993 | 0.00017231
FL_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | FL-TAMPA-FL | Zone2A | Zone2A(FL-TAMPA-FL) |  |  | FL | 0.0915 | 0.011082 |  |  |  | Natural Gas | 9.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4782 | 0 | 9.4782 | 0 | 0 | 0.10504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10504 | 0 | 0.10504 | 0 | 0 | 0.0094782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094782 | 0 | 0.0094782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017227 | 0 | 0 | 0 | 0.0017227 | 0.0017227 | 0
GA_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 1095572.1715 | 882150.4646 | 95443.7655 | 4077910.5986 | 543459.8574 | 569733.984 | 140103.6678 | 408427.0738 | 141617.9867 | 14056.7688 | 0 | 0 | 0 | 7968476.3387 | 0 | 7968475.2273 | 1.1114 | 543460.9688 | 0 | 107913.8589 | 86891.8208 | 9401.2109 | 401674.194 | 53530.796 | 56118.7974 | 13800.2113 | 40230.0668 | 13949.3717 | 1384.5917 | 0 | 0 | 0 | 784894.9194 | 0 | 784894.8099 | 0.10948 | 53530.9054 | 0 | 3738.0922 | 3009.8974 | 325.6541 | 13913.831 | 1854.285 | 1943.9324 | 478.0337 | 1393.5532 | 483.2006 | 47.9617 | 0 | 0 | 0 | 27188.4413 | 0 | 27188.4375 | 0.0037922 | 1854.2888 | 6.0368 | 0.65315 | 27.9065 | 3.8989 | 0.95878 | 0.096195 | 7.4974 | 0 | 0 | 0.96914 | 0 | 54.5309 | 54.5309 | 7.6059e-06
GA_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 397135.3733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473434.6514 | 0 | 0 | 870570.0247 | 0 | 870570.0247 | 0 | 0 | 2920.9307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3482.1119 | 0 | 0 | 6403.0425 | 0 | 6403.0425 | 0 | 0 | 397.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473.4347 | 0 | 0 | 870.57 | 0 | 870.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79652 | 0.94955 | 0 | 0 | 1.7461 | 1.7461 | 0
GA_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 1036674.8935 | 717342.5604 | 95443.7655 | 4077910.5986 | 543387.6147 | 555877.2719 | 135960.8249 | 369457.6761 | 141509.6226 | 12617.4713 | 0 | 0 | 0 | 7686182.2995 | 0 | 7686177.5759 | 4.7236 | 543392.3382 | 0 | 102112.477 | 70658.2422 | 9401.2109 | 401674.194 | 53523.68 | 54753.9113 | 13392.1413 | 36391.5811 | 13938.6978 | 1242.8209 | 0 | 0 | 0 | 757088.9565 | 0 | 757088.4912 | 0.46527 | 53524.1453 | 0 | 3537.1347 | 2447.5728 | 325.6541 | 13913.831 | 1854.0385 | 1896.6533 | 463.8983 | 1260.5896 | 482.8308 | 43.0508 | 0 | 0 | 0 | 26225.254 | 0 | 26225.2379 | 0.016117 | 1854.0547 | 4.909 | 0.65315 | 27.9065 | 3.804 | 0.93042 | 0.086345 | 7.0943 | 0 | 0 | 0.9684 | 0 | 52.599 | 52.599 | 3.2325e-05
GA_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 264914.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473453.6078 | 0 | 0 | 738368.4928 | 0 | 738368.4928 | 0 | 0 | 1948.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3482.2513 | 0 | 0 | 5430.7003 | 0 | 5430.7003 | 0 | 0 | 264.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473.4536 | 0 | 0 | 738.3685 | 0 | 738.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53133 | 0.94959 | 0 | 0 | 1.4809 | 1.4809 | 0
GA_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 53381.8231 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 24087.3946 | 0 | 0 | 0 | 0 | 95210.3659 | 0 | 0 | 350274.4517 | 0 | 350272.5067 | 1.945 | 1.945 | 0 | 5258.1096 | 2794.9102 | 710.7699 | 13987.4144 | 0 | 2372.6084 | 0 | 0 | 0 | 0 | 9378.221 | 0 | 0 | 34502.0335 | 0 | 34501.8419 | 0.19158 | 0.19158 | 0 | 182.1388 | 96.8146 | 24.6208 | 484.5184 | 0 | 82.1862 | 0 | 0 | 0 | 0 | 324.8578 | 0 | 0 | 1195.1364 | 0 | 1195.1298 | 0.0066363 | 0.0066363 | 2.8693 | 0.7297 | 14.3599 | 2.4358 | 0 | 0 | 5.3981 | 0 | 9.628 | 0 | 0 | 35.4207 | 35.4209 | 0.00019668
GA_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 49428.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49428.6628 | 0 | 49428.6628 | 0 | 0 | 363.5478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363.5478 | 0 | 363.5478 | 0 | 0 | 49.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4287 | 0 | 49.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4649 | 0 | 0 | 0 | 1.4649 | 1.4649 | 0
GA_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 49155.6232 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 23431.6528 | 0 | 0 | 0 | 0 | 95104.7804 | 0 | 0 | 340093.7834 | 0 | 340095.1726 | -1.3893 | -1.3893 | 0 | 4841.8289 | 2283.3858 | 710.7699 | 13987.4144 | 0 | 2308.0178 | 0 | 0 | 0 | 0 | 9367.8209 | 0 | 0 | 33499.2377 | 0 | 33499.3745 | -0.13684 | -0.13684 | 0 | 167.719 | 79.0956 | 24.6208 | 484.5184 | 0 | 79.9488 | 0 | 0 | 0 | 0 | 324.4975 | 0 | 0 | 1160.4 | 0 | 1160.4047 | -0.0047402 | -0.0047402 | 2.3442 | 0.7297 | 14.3599 | 2.3695 | 0 | 0 | 4.9708 | 0 | 9.6173 | 0 | 0 | 34.3915 | 34.3914 | -0.00014049
GA_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 13117.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13117.7889 | 0 | 13117.7889 | 0 | 0 | 96.4813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4813 | 0 | 96.4813 | 0 | 0 | 13.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1178 | 0 | 13.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38878 | 0 | 0 | 0 | 0.38878 | 0.38878 | 0
GA_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 215805.7171 | 99883.9151 | 7115.9093 | 317887.4784 | 4818.0346 | 95818.872 | 258.4067 | 0 | 0 | 23253.8246 | 7179.8163 | 17730.034 | 0 | 789752.0081 | 0 | 789753.3974 | -1.3893 | 4816.6453 | 0 | 21256.8631 | 9838.5656 | 700.9171 | 31311.9166 | 474.5764 | 9438.1589 | 25.4531 | 0 | 0 | 2290.5017 | 707.2119 | 1746.4083 | 0 | 77790.5728 | 0 | 77790.7096 | -0.13684 | 474.4396 | 0 | 736.3291 | 340.8039 | 24.2795 | 1084.6321 | 16.4391 | 326.934 | 0.88168 | 0 | 0 | 79.342 | 24.4975 | 60.4949 | 0 | 2694.6339 | 0 | 2694.6386 | -0.0047402 | 16.4344 | 4.608 | 0.32828 | 14.6653 | 4.4205 | 0.011921 | 1.0728 | 9.9559 | 0 | 0.33123 | 0 | 0.81795 | 36.4342 | 36.4342 | -6.4093e-05
GA_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 140551.8007 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99530.2758 | 0 | 0 | 582272.4913 | 0 | 582272.4913 | 0 | 0 | 1033.7585 | 0 | 0 | 0 | 2516.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 732.0452 | 0 | 0 | 4282.6142 | 0 | 4282.6142 | 0 | 0 | 140.5518 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5303 | 0 | 0 | 582.2725 | 0 | 582.2725 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.9004 | 1.3457 | 0 | 0 | 7.8729 | 7.8729 | 0
GA_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 199831.7372 | 80386.7127 | 7115.9093 | 312483.1662 | 4745.7919 | 85388.1327 | 208.3925 | 0 | 0 | 22709.2255 | 7179.8163 | 12539.6714 | 0 | 732588.5558 | 0 | 732589.6672 | -1.1114 | 4744.6805 | 0 | 19683.4261 | 7918.0912 | 700.9171 | 30779.5919 | 467.4605 | 8410.7311 | 20.5267 | 0 | 0 | 2236.8587 | 707.2119 | 1235.1576 | 0 | 72159.9727 | 0 | 72160.0822 | -0.10948 | 467.351 | 0 | 681.8259 | 274.2795 | 24.2795 | 1066.1926 | 16.1926 | 291.3443 | 0.71104 | 0 | 0 | 77.4839 | 24.4975 | 42.7854 | 0 | 2499.5922 | 0 | 2499.5959 | -0.0037922 | 16.1888 | 3.7085 | 0.32828 | 14.416 | 3.9393 | 0.0096139 | 1.0477 | 9.219 | 0 | 0.33123 | 0 | 0.5785 | 33.797 | 33.797 | -5.1274e-05
GA_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 116391.9423 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99283.8433 | 0 | 0 | 557866.2005 | 0 | 557866.2005 | 0 | 0 | 856.0627 | 0 | 0 | 0 | 2516.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 730.2327 | 0 | 0 | 4103.1059 | 0 | 4103.1059 | 0 | 0 | 116.3919 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2838 | 0 | 0 | 557.8662 | 0 | 557.8662 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.5737 | 1.3424 | 0 | 0 | 7.5429 | 7.5429 | 0
GA_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 82331.7094 | 82531.7662 | 10694.7032 | 53987.5506 | 0 | 36896.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266442.3163 | 0 | 266444.817 | -2.5007 | -2.5007 | 0 | 8109.6734 | 8129.379 | 1053.4283 | 5317.7737 | 0 | 3634.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26244.5682 | 0 | 26244.8145 | -0.24632 | -0.24632 | 0 | 280.9158 | 281.5984 | 36.4903 | 184.2055 | 0 | 125.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909.1012 | 0 | 909.1097 | -0.0085324 | -0.0085324 | 11.4044 | 1.4778 | 7.4601 | 5.0985 | 0 | 0 | 11.3768 | 0 | 0 | 0 | 0 | 36.818 | 36.8176 | -0.00034555
GA_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 71711.8433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84839.1104 | 0 | 0 | 156550.9537 | 0 | 156550.9537 | 0 | 0 | 527.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.9917 | 0 | 0 | 1151.4323 | 0 | 1151.4323 | 0 | 0 | 71.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8391 | 0 | 0 | 156.551 | 0 | 156.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9043 | 3.4359 | 0 | 0 | 6.3401 | 6.3401 | 0
GA_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 77549.7961 | 65051.8032 | 10694.7032 | 53987.5506 | 0 | 35062.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242346.586 | 0 | 242347.4196 | -0.83357 | -0.83357 | 0 | 7638.6549 | 6407.6026 | 1053.4283 | 5317.7737 | 0 | 3453.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23871.1387 | 0 | 23871.2208 | -0.082107 | -0.082107 | 0 | 264.5999 | 221.9568 | 36.4903 | 184.2055 | 0 | 119.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826.8866 | 0 | 826.8894 | -0.0028441 | -0.0028441 | 8.989 | 1.4778 | 7.4601 | 4.8451 | 0 | 0 | 10.716 | 0 | 0 | 0 | 0 | 33.4881 | 33.488 | -0.00011518
GA_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 79844.1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84848.5886 | 0 | 0 | 164692.7028 | 0 | 164692.7028 | 0 | 0 | 587.2535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624.0614 | 0 | 0 | 1211.3148 | 0 | 1211.3148 | 0 | 0 | 79.8441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8486 | 0 | 0 | 164.6927 | 0 | 164.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2336 | 3.4363 | 0 | 0 | 6.6699 | 6.6699 | 0
GA_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 5487.6692 | 116071.8446 | 80047.7276 | 12322.9432 | 154949.5496 | 0 | 46457.6349 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 415409.6118 | 0 | 415412.6683 | -3.0564 | -3.0564 | 540.5354 | 11433.0767 | 7884.7012 | 1213.8099 | 15262.5306 | 0 | 4576.077 | 7.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 40917.8468 | 0 | 40918.1478 | -0.30106 | -0.30106 | 18.7239 | 396.0371 | 273.1228 | 42.0459 | 528.6879 | 0 | 158.5135 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1417.3776 | 0 | 1417.388 | -0.010429 | -0.010429 | 6.322 | 0.97324 | 12.2376 | 3.6691 | 0.0057056 | 0 | 9.1671 | 0.4334 | 0 | 0 | 0 | 32.8084 | 32.8081 | -0.00024139
GA_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 11933.0175 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 485348.7126 | 0 | 0 | 896777.1681 | 0 | 896777.1681 | 0 | 0 | 87.7673 | 0 | 0 | 0 | 2938.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 3569.7398 | 0 | 0 | 6595.7961 | 0 | 6595.7961 | 0 | 0 | 11.933 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 485.3487 | 0 | 0 | 896.7772 | 0 | 896.7772 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.27621 | 11.2344 | 0 | 0 | 20.7578 | 20.7578 | 0
GA_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 6282.3393 | 109822.8481 | 51295.1195 | 12322.9432 | 154949.5496 | 0 | 44220.8888 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378965.9312 | 0 | 378967.5984 | -1.6671 | -1.6671 | 618.8104 | 10817.5505 | 5052.5693 | 1213.8099 | 15262.5306 | 0 | 4355.7575 | 7.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 37328.1442 | 0 | 37328.3084 | -0.16421 | -0.16421 | 21.4353 | 374.7156 | 175.0189 | 42.0459 | 528.6879 | 0 | 150.8817 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1293.0318 | 0 | 1293.0374 | -0.0056883 | -0.0056883 | 4.0512 | 0.97324 | 12.2376 | 3.4925 | 0.0057056 | 0 | 8.6736 | 0.49617 | 0 | 0 | 0 | 29.93 | 29.9299 | -0.00013167
GA_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 12643.8804 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 485348.7126 | 0 | 0 | 897488.0309 | 0 | 897488.0309 | 0 | 0 | 92.9957 | 0 | 0 | 0 | 2938.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 3569.7398 | 0 | 0 | 6601.0245 | 0 | 6601.0245 | 0 | 0 | 12.6439 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 485.3487 | 0 | 0 | 897.488 | 0 | 897.488 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.29267 | 11.2344 | 0 | 0 | 20.7742 | 20.7742 | 0
GA_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 569.6062 | 8355.15 | 8994.2204 | 1583.783 | 13417.6985 | 0 | 5120.8984 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43045.555 | 0 | 43041.9429 | 3.6121 | 3.6121 | 56.1062 | 822.9823 | 885.9307 | 156.0026 | 1321.6433 | 0 | 504.4085 | 0 | 0 | 0 | 0 | 492.9136 | 0 | 0 | 4239.9872 | 0 | 4239.6314 | 0.3558 | 0.3558 | 1.9435 | 28.5078 | 30.6883 | 5.4039 | 45.7812 | 0 | 17.4725 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.8714 | 0 | 146.8591 | 0.012325 | 0.012325 | 5.5777 | 0.98216 | 8.3208 | 3.1757 | 0 | 0 | 5.1813 | 0.35323 | 3.1033 | 0 | 0 | 26.692 | 26.6942 | 0.00224
GA_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 246.4325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.4325 | 0 | 246.4325 | 0 | 0 | 1.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8125 | 0 | 1.8125 | 0 | 0 | 0.24643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24643 | 0 | 0.24643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04479 | 0 | 0 | 0 | 0.04479 | 0.04479 | 0
GA_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 555.7133 | 8016.1649 | 7224.2734 | 1583.783 | 13417.6985 | 0 | 4692.9991 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40494.8308 | 0 | 40495.6644 | -0.83357 | -0.83357 | 54.7378 | 789.5922 | 711.5909 | 156.0026 | 1321.6433 | 0 | 462.2604 | 0 | 0 | 0 | 0 | 492.9136 | 0 | 0 | 3988.7408 | 0 | 3988.8229 | -0.082107 | -0.082107 | 1.8961 | 27.3512 | 24.6492 | 5.4039 | 45.7812 | 0 | 16.0125 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.1684 | 0 | 138.1712 | -0.0028441 | -0.0028441 | 4.48 | 0.98216 | 8.3208 | 2.9103 | 0 | 0 | 4.9711 | 0.34462 | 3.1033 | 0 | 0 | 25.1129 | 25.1124 | -0.00051693
GA_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | GA-SAVANNAH-GA | Zone2A | Zone2A(GA-SAVANNAH-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 236.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9543 | 0 | 236.9543 | 0 | 0 | 1.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7428 | 0 | 1.7428 | 0 | 0 | 0.23695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23695 | 0 | 0.23695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043067 | 0 | 0 | 0 | 0.043067 | 0.043067 | 0
GA_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 889927.6727 | 882581.1424 | 96063.3859 | 4077910.5986 | 543459.8574 | 583696.2815 | 119789.5668 | 332444.3893 | 267325.9005 | 11745.0014 | 0 | 0 | 0 | 7804943.7966 | 0 | 7804942.1295 | 1.6671 | 543461.5245 | 0 | 87657.8758 | 86934.2425 | 9462.2435 | 401674.194 | 53530.796 | 57494.0837 | 11799.2723 | 32745.7723 | 26331.6012 | 1156.8826 | 0 | 0 | 0 | 768786.964 | 0 | 768786.7998 | 0.16421 | 53530.9602 | 0 | 3036.4332 | 3011.3669 | 327.7683 | 13913.831 | 1854.285 | 1991.5717 | 408.722 | 1134.3003 | 912.116 | 40.0739 | 0 | 0 | 0 | 26630.4682 | 0 | 26630.4625 | 0.0056883 | 1854.2907 | 6.0398 | 0.65739 | 27.9065 | 3.9944 | 0.81976 | 0.080375 | 6.0901 | 0 | 0 | 1.8294 | 0 | 53.4118 | 53.4118 | 1.1409e-05
GA_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 653444.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501110.9113 | 0 | 0 | 1154554.9902 | 0 | 1154554.9902 | 0 | 0 | 4806.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3685.6708 | 0 | 0 | 8491.752 | 0 | 8491.752 | 0 | 0 | 653.4441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.1109 | 0 | 0 | 1154.555 | 0 | 1154.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3106 | 1.0051 | 0 | 0 | 2.3156 | 2.3156 | 0
GA_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 828638.0489 | 717520.3887 | 96063.3859 | 4077910.5986 | 543387.6147 | 570056.2977 | 110973.1747 | 299435.0171 | 267278.6649 | 11828.3584 | 0 | 0 | 0 | 7523091.5495 | 0 | 7523092.3831 | -0.83357 | 543386.7811 | 0 | 81620.8478 | 70675.7583 | 9462.2435 | 401674.194 | 53523.68 | 56150.5453 | 10930.8577 | 29494.3492 | 26326.9485 | 1165.0933 | 0 | 0 | 0 | 741024.5176 | 0 | 741024.5997 | -0.082107 | 53523.5979 | 0 | 2827.313 | 2448.1796 | 327.7683 | 13913.831 | 1854.0385 | 1945.0321 | 378.6405 | 1021.6723 | 911.9548 | 40.3584 | 0 | 0 | 0 | 25668.7884 | 0 | 25668.7912 | -0.0028441 | 1854.0357 | 4.9102 | 0.65739 | 27.9065 | 3.9011 | 0.75943 | 0.080945 | 5.6706 | 0 | 0 | 1.8291 | 0 | 51.483 | 51.483 | -5.7044e-06
GA_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 371316.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501044.5641 | 0 | 0 | 872361.3991 | 0 | 872361.3991 | 0 | 0 | 2731.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3685.1828 | 0 | 0 | 6416.2181 | 0 | 6416.2181 | 0 | 0 | 371.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.0446 | 0 | 0 | 872.3614 | 0 | 872.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74474 | 1.0049 | 0 | 0 | 1.7497 | 1.7497 | 0
GA_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 39547.3396 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 22803.6968 | 0 | 0 | 0 | 0 | 100775.835 | 0 | 0 | 340718.9609 | 0 | 340718.9609 | 0 | 0 | 0 | 3895.4129 | 2794.9102 | 710.4962 | 13987.4144 | 0 | 2246.1641 | 0 | 0 | 0 | 0 | 9926.4197 | 0 | 0 | 33560.8176 | 0 | 33560.8176 | 0 | 0 | 0 | 134.9355 | 96.8146 | 24.6113 | 484.5184 | 0 | 77.8062 | 0 | 0 | 0 | 0 | 343.8471 | 0 | 0 | 1162.5331 | 0 | 1162.5331 | 0 | 0 | 2.8693 | 0.72942 | 14.3599 | 2.306 | 0 | 0 | 3.9992 | 0 | 10.1908 | 0 | 0 | 34.4546 | 34.4546 | 0
GA_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 110505.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110505.998 | 0 | 110505.998 | 0 | 0 | 812.7716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812.7716 | 0 | 812.7716 | 0 | 0 | 110.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.506 | 0 | 110.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2751 | 0 | 0 | 0 | 3.2751 | 3.2751 | 0
GA_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 38019.1279 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 22092.3837 | 0 | 0 | 0 | 0 | 100639.6852 | 0 | 0 | 333150.1452 | 0 | 333151.8124 | -1.6671 | -1.6671 | 0 | 3744.8841 | 2283.3858 | 710.4962 | 13987.4144 | 0 | 2176.0998 | 0 | 0 | 0 | 0 | 9913.009 | 0 | 0 | 32815.2893 | 0 | 32815.4535 | -0.16421 | -0.16421 | 0 | 129.7213 | 79.0956 | 24.6113 | 484.5184 | 0 | 75.3792 | 0 | 0 | 0 | 0 | 343.3826 | 0 | 0 | 1136.7083 | 0 | 1136.714 | -0.0056883 | -0.0056883 | 2.3442 | 0.72942 | 14.3599 | 2.2341 | 0 | 0 | 3.8446 | 0 | 10.177 | 0 | 0 | 33.6894 | 33.6892 | -0.00016859
GA_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 36841.6515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36841.6515 | 0 | 36841.6515 | 0 | 0 | 270.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9703 | 0 | 270.9703 | 0 | 0 | 36.8417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8417 | 0 | 36.8417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0919 | 0 | 0 | 0 | 1.0919 | 1.0919 | 0
GA_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 160626.1613 | 99164.2663 | 7132.5807 | 317887.4784 | 4818.0346 | 92048.3571 | 408.4493 | 0 | 0 | 22514.7258 | 7179.8163 | 17652.2341 | 0 | 729432.104 | 0 | 729429.8812 | 2.2229 | 4820.2575 | 0 | 15821.6769 | 9767.6802 | 702.5592 | 31311.9166 | 474.5764 | 9066.7632 | 40.2323 | 0 | 0 | 2217.7005 | 707.2119 | 1738.7451 | 0 | 71849.0622 | 0 | 71848.8433 | 0.21895 | 474.7954 | 0 | 548.0565 | 338.3485 | 24.3364 | 1084.6321 | 16.4391 | 314.069 | 1.3936 | 0 | 0 | 76.8202 | 24.4975 | 60.2294 | 0 | 2488.8223 | 0 | 2488.8148 | 0.0075844 | 16.4467 | 4.5748 | 0.32905 | 14.6653 | 4.2465 | 0.018843 | 1.0387 | 7.4103 | 0 | 0.33123 | 0 | 0.81436 | 33.6513 | 33.6514 | 0.00010255
GA_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 251835.0088 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 105558.3927 | 0 | 0 | 699583.8163 | 0 | 699583.8163 | 0 | 0 | 1852.2465 | 0 | 0 | 0 | 2516.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 776.382 | 0 | 0 | 5145.439 | 0 | 5145.439 | 0 | 0 | 251.835 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5584 | 0 | 0 | 699.5838 | 0 | 699.5838 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.4051 | 1.4273 | 0 | 0 | 9.4591 | 9.4591 | 0
GA_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 148597.7462 | 79733.7495 | 7132.5807 | 312483.1662 | 4745.7919 | 81336.9825 | 316.7566 | 0 | 0 | 22712.0041 | 7179.8163 | 12503.5501 | 0 | 676742.144 | 0 | 676740.7547 | 1.3893 | 4747.1812 | 0 | 14636.878 | 7853.7743 | 702.5592 | 30779.5919 | 467.4605 | 8011.6928 | 31.2005 | 0 | 0 | 2237.1324 | 707.2119 | 1231.5997 | 0 | 66659.1012 | 0 | 66658.9643 | 0.13684 | 467.5973 | 0 | 507.0155 | 272.0516 | 24.3364 | 1066.1926 | 16.1926 | 277.5218 | 1.0808 | 0 | 0 | 77.4934 | 24.4975 | 42.6621 | 0 | 2309.0442 | 0 | 2309.0395 | 0.0047402 | 16.1974 | 3.6784 | 0.32905 | 14.416 | 3.7524 | 0.014613 | 1.0478 | 6.8554 | 0 | 0.33123 | 0 | 0.57683 | 31.2205 | 31.2206 | 6.4093e-05
GA_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 214310.929 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 105293.0039 | 0 | 0 | 661794.3477 | 0 | 661794.3477 | 0 | 0 | 1576.2569 | 0 | 0 | 0 | 2516.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 774.43 | 0 | 0 | 4867.4974 | 0 | 4867.4974 | 0 | 0 | 214.3109 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 105.293 | 0 | 0 | 661.7943 | 0 | 661.7943 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.8977 | 1.4237 | 0 | 0 | 8.9481 | 8.9481 | 0
GA_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 60269.8899 | 82192.781 | 10691.9246 | 53987.5506 | 0 | 40467.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247609.1913 | 0 | 247605.8571 | 3.3343 | 3.3343 | 0 | 5936.5842 | 8095.9889 | 1053.1546 | 5317.7737 | 0 | 3986.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24389.5053 | 0 | 24389.1769 | 0.32843 | 0.32843 | 0 | 205.6409 | 280.4418 | 36.4808 | 184.2055 | 0 | 138.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 844.8426 | 0 | 844.8312 | 0.011377 | 0.011377 | 11.3576 | 1.4774 | 7.4601 | 5.5918 | 0 | 0 | 8.3282 | 0 | 0 | 0 | 0 | 34.2148 | 34.2152 | 0.00046074
GA_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 146409.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86516.7467 | 0 | 0 | 232926.0572 | 0 | 232926.0572 | 0 | 0 | 1076.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.3307 | 0 | 0 | 1713.1712 | 0 | 1713.1712 | 0 | 0 | 146.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5167 | 0 | 0 | 232.9261 | 0 | 232.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9294 | 3.5038 | 0 | 0 | 9.4333 | 9.4333 | 0
GA_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 0 | 56507.7106 | 64765.6108 | 10691.9246 | 53987.5506 | 0 | 38422.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224374.8167 | 0 | 224372.8717 | 1.945 | 1.945 | 0 | 5566.0095 | 6379.4127 | 1053.1546 | 5317.7737 | 0 | 3784.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22100.9194 | 0 | 22100.7279 | 0.19158 | 0.19158 | 0 | 192.8043 | 220.9803 | 36.4808 | 184.2055 | 0 | 131.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765.5669 | 0 | 765.5602 | 0.0066363 | 0.0066363 | 8.9495 | 1.4774 | 7.4601 | 5.3092 | 0 | 0 | 7.8084 | 0 | 0 | 0 | 0 | 31.0044 | 31.0047 | 0.00026876
GA_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 162133.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86526.2249 | 0 | 0 | 248659.8214 | 0 | 248659.8214 | 0 | 0 | 1192.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.4004 | 0 | 0 | 1828.893 | 0 | 1828.893 | 0 | 0 | 162.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5262 | 0 | 0 | 248.6598 | 0 | 248.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5662 | 3.5042 | 0 | 0 | 10.0705 | 10.0705 | 0
GA_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 10377.9466 | 96018.9288 | 80111.6346 | 12320.1647 | 154949.5496 | 0 | 46374.2779 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 400224.7449 | 0 | 400224.4671 | 0.27786 | 0.27786 | 1022.2277 | 9457.8645 | 7890.996 | 1213.5362 | 15262.5306 | 0 | 4567.8664 | 7.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 39422.1374 | 0 | 39422.11 | 0.027369 | 0.027369 | 35.4096 | 327.6166 | 273.3409 | 42.0364 | 528.6879 | 0 | 158.229 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1365.5668 | 0 | 1365.5659 | 0.00094805 | 0.00094805 | 6.327 | 0.97302 | 12.2376 | 3.6625 | 0.0057056 | 0 | 7.5834 | 0.81963 | 0 | 0 | 0 | 31.6089 | 31.6089 | 2.1945e-05
GA_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 22889.7834 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 515754.6858 | 0 | 0 | 938139.9072 | 0 | 938139.9072 | 0 | 0 | 168.3544 | 0 | 0 | 0 | 2938.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 3793.3757 | 0 | 0 | 6900.019 | 0 | 6900.019 | 0 | 0 | 22.8898 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 515.7547 | 0 | 0 | 938.1399 | 0 | 938.1399 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.52983 | 11.9382 | 0 | 0 | 21.7152 | 21.7152 | 0
GA_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 11920.0511 | 90275.6315 | 51322.9052 | 12320.1647 | 154949.5496 | 0 | 43984.7106 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 364845.2554 | 0 | 364844.6997 | 0.55571 | 0.55571 | 1174.125 | 8892.1497 | 5055.3062 | 1213.5362 | 15262.5306 | 0 | 4332.494 | 7.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 35937.2577 | 0 | 35937.2029 | 0.054738 | 0.054738 | 40.6712 | 308.0205 | 175.1138 | 42.0364 | 528.6879 | 0 | 150.0758 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.852 | 0 | 1244.8501 | 0.0018961 | 0.0018961 | 4.0534 | 0.97302 | 12.2376 | 3.4738 | 0.0057056 | 0 | 7.1298 | 0.94142 | 0 | 0 | 0 | 28.8146 | 28.8147 | 4.3889e-05
GA_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 23960.8168 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 515773.6422 | 0 | 0 | 939229.8969 | 0 | 939229.8969 | 0 | 0 | 176.2318 | 0 | 0 | 0 | 2938.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 3793.5151 | 0 | 0 | 6908.0359 | 0 | 6908.0359 | 0 | 0 | 23.9608 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 515.7736 | 0 | 0 | 939.2299 | 0 | 939.2299 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.55462 | 11.9387 | 0 | 0 | 21.7404 | 21.7404 | 0
GA_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 1428.1833 | 6090.6182 | 8985.8847 | 1592.1187 | 13417.6985 | 0 | 5126.4555 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41645.1574 | 0 | 41644.3239 | 0.83357 | 0.83357 | 140.6761 | 599.9259 | 885.1096 | 156.8237 | 1321.6433 | 0 | 504.9559 | 0 | 0 | 0 | 0 | 492.9136 | 0 | 0 | 4102.048 | 0 | 4101.9659 | 0.082107 | 0.082107 | 4.873 | 20.7812 | 30.6598 | 5.4323 | 45.7812 | 0 | 17.4915 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.0933 | 0 | 142.0904 | 0.0028441 | 0.0028441 | 5.5725 | 0.98733 | 8.3208 | 3.1791 | 0 | 0 | 3.777 | 0.88567 | 3.1033 | 0 | 0 | 25.8252 | 25.8258 | 0.00051693
GA_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 1317.4658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1317.4658 | 0 | 1317.4658 | 0 | 0 | 9.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.69 | 0 | 9.69 | 0 | 0 | 1.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3175 | 0 | 1.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23945 | 0 | 0 | 0 | 0.23945 | 0.23945 | 0
GA_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Electricity | 1455.9689 | 5790.533 | 7218.7162 | 1592.1187 | 13417.6985 | 0 | 4718.0062 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39197.2402 | 0 | 39194.4616 | 2.7786 | 2.7786 | 143.4129 | 570.3675 | 711.0435 | 156.8237 | 1321.6433 | 0 | 464.7236 | 0 | 0 | 0 | 0 | 492.9136 | 0 | 0 | 3860.9282 | 0 | 3860.6545 | 0.27369 | 0.27369 | 4.9678 | 19.7573 | 24.6303 | 5.4323 | 45.7812 | 0 | 16.0978 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.741 | 0 | 133.7315 | 0.0094805 | 0.0094805 | 4.4766 | 0.98733 | 8.3208 | 2.9258 | 0 | 0 | 3.5909 | 0.9029 | 3.1033 | 0 | 0 | 24.306 | 24.3077 | 0.0017231
GA_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | GA-ATLANTA-GA | Zone3A | Zone3A(GA-ATLANTA-GA) |  |  | GA | 0.0985 | 0.007355 |  |  |  | Natural Gas | 1402.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.7693 | 0 | 1402.7693 | 0 | 0 | 10.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3174 | 0 | 10.3174 | 0 | 0 | 1.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4028 | 0 | 1.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25496 | 0 | 0 | 0 | 0.25496 | 0.25496 | 0
HI_1A_LO_2016_EL | 1A | LO | EL |  |  | OfficeLarge | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 1752753.206 | 879816.4686 | 95304.8372 | 4077910.5986 | 543457.0788 | 633429.8466 | 181718.261 | 642162.8817 | 0 | 32745.4084 | 0 | 0 | 0 | 8839298.5869 | 0 | 8839295.5305 | 3.0564 | 543460.1353 | 0 | 504442.3727 | 253211.1797 | 27428.7321 | 1173622.6703 | 156406.9473 | 182301.1098 | 52298.5155 | 184814.4773 | 0 | 9424.1285 | 0 | 0 | 0 | 2543950.1333 | 0 | 2543949.2537 | 0.87964 | 156407.8269 | 0 | 5980.3939 | 3001.9338 | 325.1801 | 13913.831 | 1854.2756 | 2161.2626 | 620.0227 | 2191.0598 | 0 | 111.7273 | 0 | 0 | 0 | 30159.6868 | 0 | 30159.6764 | 0.010429 | 1854.286 | 6.0209 | 0.6522 | 27.9065 | 4.3348 | 1.2436 | 0.22409 | 11.9947 | 0 | 0 | 0 | 0 | 60.4902 | 60.4902 | 2.0916e-05
HI_1A_LO_2016_NG | 1A | LO | NG |  |  | OfficeLarge | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 14416.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409968.8171 | 0 | 0 | 424385.1155 | 0 | 424385.1155 | 0 | 0 | 415.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11808.3318 | 0 | 0 | 12223.5645 | 0 | 12223.5645 | 0 | 0 | 14.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.9688 | 0 | 0 | 424.3851 | 0 | 424.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028914 | 0.82226 | 0 | 0 | 0.85117 | 0.85117 | 0
HI_1A_LO_2019_EL | 1A | LO | EL |  |  | OfficeLarge | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 1661335.5836 | 716700.7115 | 95304.8372 | 4077910.5986 | 543384.8361 | 616577.8397 | 176602.9198 | 580025.7949 | 0 | 27029.8967 | 0 | 0 | 0 | 8494873.0181 | 0 | 8494872.4624 | 0.55571 | 543385.3918 | 0 | 478132.381 | 206266.4648 | 27428.7321 | 1173622.6703 | 156386.1558 | 177451.1023 | 50826.3203 | 166931.4238 | 0 | 7779.2043 | 0 | 0 | 0 | 2444824.4546 | 0 | 2444824.2947 | 0.15993 | 156386.3158 | 0 | 5668.477 | 2445.3828 | 325.1801 | 13913.831 | 1854.0291 | 2103.7636 | 602.5692 | 1979.048 | 0 | 92.226 | 0 | 0 | 0 | 28984.5067 | 0 | 28984.5048 | 0.0018961 | 1854.031 | 4.9046 | 0.6522 | 27.9065 | 4.2194 | 1.2086 | 0.18497 | 11.3691 | 0 | 0 | 0 | 0 | 58.1332 | 58.1332 | 3.8029e-06
HI_1A_LO_2019_NG | 1A | LO | NG |  |  | OfficeLarge | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 19278.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409949.8607 | 0 | 0 | 429228.461 | 0 | 429228.461 | 0 | 0 | 555.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11807.7858 | 0 | 0 | 12363.0674 | 0 | 12363.0674 | 0 | 0 | 19.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.9499 | 0 | 0 | 429.2285 | 0 | 429.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038666 | 0.82222 | 0 | 0 | 0.86089 | 0.86089 | 0
HI_1A_MA_2016_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 89003.048 | 28374.723 | 7221.4948 | 142004.2074 | 0 | 32445.3232 | 0 | 0 | 0 | 0 | 82203.8953 | 0 | 0 | 381252.6916 | 0 | 381250.4688 | 2.2229 | 2.2229 | 0 | 25615.0772 | 8166.2453 | 2078.3462 | 40868.8109 | 0 | 9337.764 | 0 | 0 | 0 | 0 | 23658.2811 | 0 | 0 | 109724.5246 | 0 | 109723.8849 | 0.63974 | 0.63974 | 0 | 303.6784 | 96.8146 | 24.6397 | 484.5184 | 0 | 110.7034 | 0 | 0 | 0 | 0 | 280.4797 | 0 | 0 | 1300.8342 | 0 | 1300.8266 | 0.0075844 | 0.0075844 | 2.8693 | 0.73026 | 14.3599 | 3.281 | 0 | 0 | 9.0003 | 0 | 8.3127 | 0 | 0 | 38.5533 | 38.5535 | 0.00022478
HI_1A_MA_2016_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HI_1A_MA_2019_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 78486.1731 | 23181.5818 | 7221.4948 | 142004.2074 | 0 | 30897.6615 | 0 | 0 | 0 | 0 | 82209.4524 | 0 | 0 | 364000.5711 | 0 | 364003.3497 | -2.7786 | -2.7786 | 0 | 22588.3206 | 6671.6593 | 2078.3462 | 40868.8109 | 0 | 8892.347 | 0 | 0 | 0 | 0 | 23659.8804 | 0 | 0 | 104759.3644 | 0 | 104760.164 | -0.79967 | -0.79967 | 0 | 267.7948 | 79.0956 | 24.6397 | 484.5184 | 0 | 105.4228 | 0 | 0 | 0 | 0 | 280.4987 | 0 | 0 | 1241.9699 | 0 | 1241.9794 | -0.0094805 | -0.0094805 | 2.3442 | 0.73026 | 14.3599 | 3.1245 | 0 | 0 | 7.9368 | 0 | 8.3133 | 0 | 0 | 36.8092 | 36.8089 | -0.00028098
HI_1A_MA_2019_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HI_1A_PS_2016_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 343680.9129 | 98678.0172 | 7124.245 | 317887.4784 | 4818.0346 | 113376.6349 | 41.6785 | 0 | 0 | 30564.2335 | 7177.0377 | 17816.1696 | 0 | 941164.4424 | 0 | 941166.9431 | -2.5007 | 4815.5339 | 0 | 98911.3667 | 28399.5333 | 2050.3577 | 91488.0163 | 1386.6304 | 32629.7955 | 11.9951 | 0 | 0 | 8796.3864 | 2065.5515 | 5127.4936 | 0 | 270867.1265 | 0 | 270867.8462 | -0.7197 | 1385.9107 | 0 | 1172.6393 | 336.6894 | 24.3079 | 1084.6321 | 16.4391 | 386.8411 | 0.14221 | 0 | 0 | 104.2852 | 24.4881 | 60.7888 | 0 | 3211.2531 | 0 | 3211.2616 | -0.0085324 | 16.4306 | 4.5524 | 0.32867 | 14.6653 | 5.2305 | 0.0019228 | 1.41 | 15.8553 | 0 | 0.3311 | 0 | 0.82193 | 43.4195 | 43.4194 | -0.00011537
HI_1A_PS_2016_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 350.6923 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 84298.8547 | 0 | 0 | 426839.9618 | 0 | 426839.9618 | 0 | 0 | 10.101 | 0 | 0 | 0 | 9856.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 2428.0599 | 0 | 0 | 12294.2714 | 0 | 12294.2714 | 0 | 0 | 0.35069 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2989 | 0 | 0 | 426.84 | 0 | 426.84 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.0047417 | 1.1398 | 0 | 0 | 5.7713 | 5.7713 | 0
HI_1A_PS_2019_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 327951.447 | 80181.0988 | 7124.245 | 312483.1662 | 4743.0133 | 104579.6928 | 41.6785 | 0 | 0 | 31756.2386 | 7177.0377 | 12578.5714 | 0 | 888616.1893 | 0 | 888618.4121 | -2.2229 | 4740.7905 | 0 | 94384.4264 | 23076.1202 | 2050.3577 | 89932.6552 | 1365.0392 | 30098.0356 | 11.9951 | 0 | 0 | 9139.4455 | 2065.5515 | 3620.1128 | 0 | 255743.7393 | 0 | 255744.379 | -0.63974 | 1364.3995 | 0 | 1118.9703 | 273.5779 | 24.3079 | 1066.1926 | 16.1832 | 356.8259 | 0.14221 | 0 | 0 | 108.3523 | 24.4881 | 42.9181 | 0 | 3031.9584 | 0 | 3031.966 | -0.0075844 | 16.1756 | 3.699 | 0.32867 | 14.416 | 4.8246 | 0.0019228 | 1.465 | 15.1296 | 0 | 0.3311 | 0 | 0.5803 | 40.9952 | 40.9951 | -0.00010255
HI_1A_PS_2019_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 246.4325 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 84213.5511 | 0 | 0 | 426650.3984 | 0 | 426650.3984 | 0 | 0 | 7.098 | 0 | 0 | 0 | 9856.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 2425.6029 | 0 | 0 | 12288.8114 | 0 | 12288.8114 | 0 | 0 | 0.24643 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2136 | 0 | 0 | 426.6504 | 0 | 426.6504 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.003332 | 1.1387 | 0 | 0 | 5.7687 | 5.7687 | 0
HI_1A_RS_2016_EL | 1A | RS | EL |  |  | RetailStandalone | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 153443.5665 | 81384.2181 | 10705.8174 | 53987.5506 | 0 | 40786.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340307.733 | 0 | 340306.6216 | 1.1114 | 1.1114 | 0 | 44161.0584 | 23422.378 | 3081.1343 | 15537.6171 | 0 | 11738.3778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97940.5656 | 0 | 97940.2457 | 0.31987 | 0.31987 | 0 | 523.5494 | 277.683 | 36.5282 | 184.2055 | 0 | 139.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.13 | 0 | 1161.1262 | 0.0037922 | 0.0037922 | 11.2459 | 1.4794 | 7.4601 | 5.636 | 0 | 0 | 21.2032 | 0 | 0 | 0 | 0 | 47.0244 | 47.0245 | 0.00015358
HI_1A_RS_2016_NG | 1A | RS | NG |  |  | RetailStandalone | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80915.1475 | 0 | 0 | 80915.1475 | 0 | 80915.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2330.599 | 0 | 0 | 2330.599 | 0 | 2330.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9151 | 0 | 0 | 80.9151 | 0 | 80.9151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.277 | 0 | 0 | 3.277 | 3.277 | 0
HI_1A_RS_2019_EL | 1A | RS | EL |  |  | RetailStandalone | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 147419.6339 | 64218.2332 | 10705.8174 | 53987.5506 | 0 | 38691.5411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315022.7762 | 0 | 315023.054 | -0.27786 | -0.27786 | 0 | 42427.3706 | 18482.0075 | 3081.1343 | 15537.6171 | 0 | 11135.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90663.555 | 0 | 90663.635 | -0.079967 | -0.079967 | 0 | 502.9958 | 219.1126 | 36.5282 | 184.2055 | 0 | 132.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.8577 | 0 | 1074.8587 | -0.00094805 | -0.00094805 | 8.8738 | 1.4794 | 7.4601 | 5.3465 | 0 | 0 | 20.3708 | 0 | 0 | 0 | 0 | 43.5306 | 43.5306 | -3.8395e-05
HI_1A_RS_2019_NG | 1A | RS | NG |  |  | RetailStandalone | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80915.1475 | 0 | 0 | 80915.1475 | 0 | 80915.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2330.599 | 0 | 0 | 2330.599 | 0 | 2330.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9151 | 0 | 0 | 80.9151 | 0 | 80.9151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.277 | 0 | 0 | 3.277 | 3.277 | 0
HI_1A_SH_2016_EL | 1A | SH | EL |  |  | HotelSmall | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 19.45 | 163196.3355 | 79839.3351 | 12334.0575 | 154949.5496 | 0 | 47916.3824 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 458327.3528 | 0 | 458327.6307 | -0.27786 | -0.27786 | 5.5977 | 46967.9054 | 22977.7606 | 3549.7417 | 44594.4804 | 0 | 13790.3349 | 20.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 131906.6121 | 0 | 131906.6921 | -0.079967 | -0.079967 | 0.066363 | 556.8259 | 272.4118 | 42.0838 | 528.6879 | 0 | 163.4907 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1563.8129 | 0 | 1563.8139 | -0.00094805 | -0.00094805 | 6.3055 | 0.97412 | 12.2376 | 3.7843 | 0.0057056 | 0 | 12.8889 | 0.0015361 | 0 | 0 | 0 | 36.1977 | 36.1977 | -2.1945e-05
HI_1A_SH_2016_NG | 1A | SH | NG |  |  | HotelSmall | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 419769.2461 | 0 | 0 | 819264.684 | 0 | 819264.684 | 0 | 0 | 0 | 0 | 0 | 0 | 11506.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 12090.6136 | 0 | 0 | 23597.2807 | 0 | 23597.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 419.7692 | 0 | 0 | 819.2647 | 0 | 819.2647 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0 | 9.7164 | 0 | 0 | 18.9636 | 18.9636 | 0
HI_1A_SH_2019_EL | 1A | SH | EL |  |  | HotelSmall | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 22.2285 | 155021.7923 | 51378.4765 | 12334.0575 | 154949.5496 | 0 | 45776.8861 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 419555.2333 | 0 | 419552.1769 | 3.0564 | 3.0564 | 6.3974 | 44615.2718 | 14786.7255 | 3549.7417 | 44594.4804 | 0 | 13174.5878 | 20.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 120747.9962 | 0 | 120747.1165 | 0.87964 | 0.87964 | 0.075844 | 528.9344 | 175.3034 | 42.0838 | 528.6879 | 0 | 156.1907 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1431.5225 | 0 | 1431.512 | 0.010429 | 0.010429 | 4.0578 | 0.97412 | 12.2376 | 3.6154 | 0.0057056 | 0 | 12.2433 | 0.0017556 | 0 | 0 | 0 | 33.1353 | 33.1356 | 0.00024139
HI_1A_SH_2019_NG | 1A | SH | NG |  |  | HotelSmall | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 419788.2024 | 0 | 0 | 819283.6404 | 0 | 819283.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 11506.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 12091.1596 | 0 | 0 | 23597.8267 | 0 | 23597.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 419.7882 | 0 | 0 | 819.2836 | 0 | 819.2836 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0 | 9.7169 | 0 | 0 | 18.964 | 18.964 | 0
HI_1A_SO_2016_EL | 1A | SO | EL |  |  | OfficeSmall | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 13651.0981 | 8952.5419 | 1581.0044 | 13417.6985 | 0 | 5220.9268 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 47827.4683 | 0 | 47826.6347 | 0.83357 | 0.83357 | 0 | 3928.786 | 2576.5415 | 455.0131 | 3861.6136 | 0 | 1502.5827 | 0 | 0 | 0 | 0 | 1440.2084 | 0 | 0 | 13764.7454 | 0 | 13764.5055 | 0.2399 | 0.2399 | 0 | 46.5775 | 30.5461 | 5.3944 | 45.7812 | 0 | 17.8138 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 163.1873 | 0 | 163.1845 | 0.0028441 | 0.0028441 | 5.5518 | 0.98044 | 8.3208 | 3.2377 | 0 | 0 | 8.4656 | 0 | 3.1033 | 0 | 0 | 29.6591 | 29.6596 | 0.00051693
HI_1A_SO_2016_NG | 1A | SO | NG |  |  | OfficeSmall | STD2016 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HI_1A_SO_2019_EL | 1A | SO | EL |  |  | OfficeSmall | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Electricity | 0 | 13006.4706 | 7227.0519 | 1581.0044 | 13417.6985 | 0 | 4787.4704 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 45023.8945 | 0 | 45022.2274 | 1.6671 | 1.6671 | 0 | 3743.2623 | 2079.9455 | 455.0131 | 3861.6136 | 0 | 1377.834 | 0 | 0 | 0 | 0 | 1440.2084 | 0 | 0 | 12957.8768 | 0 | 12957.397 | 0.4798 | 0.4798 | 0 | 44.3781 | 24.6587 | 5.3944 | 45.7812 | 0 | 16.3348 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 153.6215 | 0 | 153.6158 | 0.0056883 | 0.0056883 | 4.4818 | 0.98044 | 8.3208 | 2.9689 | 0 | 0 | 8.0658 | 0 | 3.1033 | 0 | 0 | 27.92 | 27.921 | 0.0010339
HI_1A_SO_2019_NG | 1A | SO | NG |  |  | OfficeSmall | STD2019 | HI-HONOLULU-HI | Zone1A | Zone1A(HI-HONOLULU-HI) |  |  | HI | 0.2878 | 0.028803 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IA_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 714827.9575 | 879816.4686 | 95782.7507 | 4077910.5986 | 543457.0788 | 603549.1405 | 101542.7194 | 234991.72 | 436801.7967 | 13300.9987 | 0 | 0 | 0 | 7701981.2296 | 0 | 7701978.7289 | 2.5007 | 543459.5796 | 0 | 73198.3829 | 90093.2064 | 9808.1537 | 417578.0453 | 55650.0049 | 61803.432 | 10397.9745 | 24063.1521 | 44728.504 | 1362.0223 | 0 | 0 | 0 | 788682.8779 | 0 | 788682.6218 | 0.25607 | 55650.2609 | 0 | 2438.993 | 3001.9338 | 326.8107 | 13913.831 | 1854.2756 | 2059.3097 | 346.4638 | 801.7917 | 1490.3677 | 45.383 | 0 | 0 | 0 | 26279.16 | 0 | 26279.1514 | 0.0085324 | 1854.2841 | 6.0209 | 0.65547 | 27.9065 | 4.1303 | 0.69489 | 0.091023 | 4.8918 | 0 | 0 | 2.9892 | 0 | 52.7071 | 52.7072 | 1.7113e-05
IA_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 1336441.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572756.4074 | 0 | 0 | 1909197.503 | 0 | 1909197.503 | 0 | 0 | 7374.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3160.4699 | 0 | 0 | 10534.9518 | 0 | 10534.9518 | 0 | 0 | 1336.4411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.7564 | 0 | 0 | 1909.1975 | 0 | 1909.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6805 | 1.1488 | 0 | 0 | 3.8292 | 3.8292 | 0
IA_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 669317.8139 | 716483.9833 | 95782.7507 | 4077910.5986 | 543384.8361 | 584582.6443 | 96949.7487 | 211715.6669 | 436532.2758 | 11658.8658 | 0 | 0 | 0 | 7444319.184 | 0 | 7444318.9062 | 0.27786 | 543385.114 | 0 | 68538.1441 | 73367.9599 | 9808.1537 | 417578.0453 | 55642.6072 | 59861.2628 | 9927.6543 | 21679.6843 | 44700.905 | 1193.8679 | 0 | 0 | 0 | 762298.2844 | 0 | 762298.256 | 0.028453 | 55642.6357 | 0 | 2283.7124 | 2444.6434 | 326.8107 | 13913.831 | 1854.0291 | 1994.596 | 330.7925 | 722.3739 | 1489.4481 | 39.7801 | 0 | 0 | 0 | 25400.0171 | 0 | 25400.0161 | 0.00094805 | 1854.03 | 4.9031 | 0.65547 | 27.9065 | 4.0005 | 0.66346 | 0.079785 | 4.5804 | 0 | 0 | 2.9873 | 0 | 50.9439 | 50.9439 | 1.9015e-06
IA_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 1275183.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572832.2328 | 0 | 0 | 1848015.9079 | 0 | 1848015.9079 | 0 | 0 | 7036.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3160.8883 | 0 | 0 | 10197.3518 | 0 | 10197.3518 | 0 | 0 | 1275.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.8322 | 0 | 0 | 1848.0159 | 0 | 1848.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5576 | 1.1489 | 0 | 0 | 3.7065 | 3.7065 | 0
IA_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 30550.3407 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 21906.2197 | 0 | 0 | 0 | 0 | 114863.1681 | 0 | 0 | 344900.7037 | 0 | 344901.5373 | -0.83357 | -0.83357 | 0 | 3128.3549 | 2905.5716 | 737.4894 | 14541.2308 | 0 | 2243.1969 | 0 | 0 | 0 | 0 | 11761.9884 | 0 | 0 | 35317.8321 | 0 | 35317.9174 | -0.085358 | -0.085358 | 0 | 104.2378 | 96.8146 | 24.5734 | 484.5184 | 0 | 74.744 | 0 | 0 | 0 | 0 | 391.9131 | 0 | 0 | 1176.8012 | 0 | 1176.804 | -0.0028441 | -0.0028441 | 2.8693 | 0.72829 | 14.3599 | 2.2152 | 0 | 0 | 3.0894 | 0 | 11.6153 | 0 | 0 | 34.8776 | 34.8775 | -8.4293e-05
IA_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 165242.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165242.4367 | 0 | 165242.4367 | 0 | 0 | 911.8078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 911.8078 | 0 | 911.8078 | 0 | 0 | 165.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.2424 | 0 | 165.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8974 | 0 | 0 | 0 | 4.8974 | 4.8974 | 0
IA_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 29822.3562 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 21450.5348 | 0 | 0 | 0 | 0 | 114893.7323 | 0 | 0 | 338554.4574 | 0 | 338556.9581 | -2.5007 | -2.5007 | 0 | 3053.8093 | 2373.794 | 737.4894 | 14541.2308 | 0 | 2196.5348 | 0 | 0 | 0 | 0 | 11765.1182 | 0 | 0 | 34667.9764 | 0 | 34668.2325 | -0.25607 | -0.25607 | 0 | 101.7539 | 79.0956 | 24.5734 | 484.5184 | 0 | 73.1892 | 0 | 0 | 0 | 0 | 392.0174 | 0 | 0 | 1155.1478 | 0 | 1155.1563 | -0.0085324 | -0.0085324 | 2.3442 | 0.72829 | 14.3599 | 2.1691 | 0 | 0 | 3.0157 | 0 | 11.6184 | 0 | 0 | 34.236 | 34.2357 | -0.00025288
IA_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 184359.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184359.908 | 0 | 184359.908 | 0 | 0 | 1017.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017.298 | 0 | 1017.298 | 0 | 0 | 184.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184.3599 | 0 | 184.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.464 | 0 | 0 | 0 | 5.464 | 5.464 | 0
IA_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 114354.6904 | 96582.9779 | 7118.6878 | 317887.4784 | 4818.0346 | 99775.551 | 944.7127 | 0 | 0 | 21117.1068 | 7179.8163 | 17610.5556 | 0 | 687389.6116 | 0 | 687390.4451 | -0.83357 | 4817.2011 | 0 | 11709.9203 | 9890.0969 | 728.9536 | 32551.6778 | 493.3667 | 10217.0164 | 96.7386 | 0 | 0 | 2162.3917 | 735.2132 | 1803.3209 | 0 | 70388.6962 | 0 | 70388.7816 | -0.085358 | 493.2814 | 0 | 390.1782 | 329.5411 | 24.289 | 1084.6321 | 16.4391 | 340.4342 | 3.2234 | 0 | 0 | 72.0516 | 24.4975 | 60.0872 | 0 | 2345.3734 | 0 | 2345.3762 | -0.0028441 | 16.4363 | 4.4557 | 0.32841 | 14.6653 | 4.603 | 0.043583 | 0.97421 | 5.2756 | 0 | 0.33123 | 0 | 0.81244 | 31.7118 | 31.7118 | -3.8456e-05
IA_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 596679.3116 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120353.8179 | 0 | 0 | 1059223.5443 | 0 | 1059223.5443 | 0 | 0 | 3292.4764 | 0 | 0 | 0 | 1888.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 664.1124 | 0 | 0 | 5844.7955 | 0 | 5844.7955 | 0 | 0 | 596.6793 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.3538 | 0 | 0 | 1059.2235 | 0 | 1059.2235 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.0677 | 1.6273 | 0 | 0 | 14.3218 | 14.3218 | 0
IA_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 108544.7074 | 78566.7515 | 7118.6878 | 312483.1662 | 4743.0133 | 83365.3362 | 719.6488 | 0 | 0 | 22856.4895 | 7179.8163 | 12472.9858 | 0 | 638050.603 | 0 | 638051.7144 | -1.1114 | 4741.9019 | 0 | 11114.978 | 8045.2354 | 728.9536 | 31998.2762 | 485.6846 | 8536.6104 | 73.692 | 0 | 0 | 2340.5045 | 735.2132 | 1277.2337 | 0 | 65336.3817 | 0 | 65336.4956 | -0.11381 | 485.5708 | 0 | 370.3545 | 268.0698 | 24.289 | 1066.1926 | 16.1832 | 284.4425 | 2.4554 | 0 | 0 | 77.9863 | 24.4975 | 42.5578 | 0 | 2177.0287 | 0 | 2177.0324 | -0.0037922 | 16.1794 | 3.6246 | 0.32841 | 14.416 | 3.8459 | 0.0332 | 1.0545 | 5.0076 | 0 | 0.33123 | 0 | 0.57542 | 29.4357 | 29.4356 | -5.1274e-05
IA_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 570405.821 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120088.4291 | 0 | 0 | 1032684.6649 | 0 | 1032684.6649 | 0 | 0 | 3147.4993 | 0 | 0 | 0 | 1888.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 662.648 | 0 | 0 | 5698.354 | 0 | 5698.354 | 0 | 0 | 570.4058 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0884 | 0 | 0 | 1032.6847 | 0 | 1032.6847 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.7125 | 1.6237 | 0 | 0 | 13.9629 | 13.9629 | 0
IA_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 44648.788 | 84421.1915 | 10700.2603 | 53987.5506 | 0 | 43562.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237320.1589 | 0 | 237319.3253 | 0.83357 | 0.83357 | 0 | 4572.0359 | 8644.73 | 1095.7067 | 5528.3252 | 0 | 4460.7865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24301.5843 | 0 | 24301.4989 | 0.085358 | 0.085358 | 0 | 152.3417 | 288.0451 | 36.5093 | 184.2055 | 0 | 148.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809.7364 | 0 | 809.7335 | 0.0028441 | 0.0028441 | 11.6655 | 1.4786 | 7.4601 | 6.0196 | 0 | 0 | 6.1697 | 0 | 0 | 0 | 0 | 32.7934 | 32.7935 | 0.00011518
IA_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 539791.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90829.3146 | 0 | 0 | 630620.6426 | 0 | 630620.6426 | 0 | 0 | 2978.5685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.1962 | 0 | 0 | 3479.7647 | 0 | 3479.7647 | 0 | 0 | 539.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8293 | 0 | 0 | 630.6206 | 0 | 630.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.861 | 3.6785 | 0 | 0 | 25.5395 | 25.5395 | 0
IA_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 41995.2568 | 66907.8857 | 10700.2603 | 53987.5506 | 0 | 41670.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215261.118 | 0 | 215259.7287 | 1.3893 | 1.3893 | 0 | 4300.3143 | 6851.3675 | 1095.7067 | 5528.3252 | 0 | 4267.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22042.7385 | 0 | 22042.5962 | 0.14226 | 0.14226 | 0 | 143.2878 | 228.2897 | 36.5093 | 184.2055 | 0 | 142.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4709 | 0 | 734.4662 | 0.0047402 | 0.0047402 | 9.2455 | 1.4786 | 7.4601 | 5.7581 | 0 | 0 | 5.803 | 0 | 0 | 0 | 0 | 29.7451 | 29.7453 | 0.00019197
IA_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 567922.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90838.7928 | 0 | 0 | 658761.3329 | 0 | 658761.3329 | 0 | 0 | 3133.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.2485 | 0 | 0 | 3635.045 | 0 | 3635.045 | 0 | 0 | 567.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8388 | 0 | 0 | 658.7613 | 0 | 658.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.0003 | 3.6789 | 0 | 0 | 26.6791 | 26.6791 | 0
IA_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 43309.5189 | 71700.9132 | 79111.3506 | 12303.4933 | 154949.5496 | 0 | 46196.4497 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 407643.518 | 0 | 407641.0173 | 2.5007 | 2.5007 | 4434.8947 | 7342.1735 | 8101.0023 | 1259.8777 | 15866.8339 | 0 | 4730.5164 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 41742.6962 | 0 | 41742.4402 | 0.25607 | 0.25607 | 147.7721 | 244.6435 | 269.9279 | 41.9795 | 528.6879 | 0 | 157.6223 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1390.8797 | 0 | 1390.8712 | 0.0085324 | 0.0085324 | 6.248 | 0.9717 | 12.2376 | 3.6485 | 0.0057056 | 0 | 5.6628 | 3.4205 | 0 | 0 | 0 | 32.1946 | 32.1948 | 0.0001975
IA_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 96080.2215 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598281.1225 | 0 | 0 | 1093856.7818 | 0 | 1093856.7818 | 0 | 0 | 530.1707 | 0 | 0 | 0 | 2204.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 3301.3152 | 0 | 0 | 6035.9017 | 0 | 6035.9017 | 0 | 0 | 96.0802 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.2811 | 0 | 0 | 1093.8568 | 0 | 1093.8568 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.224 | 13.8485 | 0 | 0 | 25.3196 | 25.3196 | 0
IA_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 48013.6323 | 67210.7495 | 50750.5205 | 12303.4933 | 154949.5496 | 0 | 43748.5324 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 377048.7202 | 0 | 377046.2195 | 2.5007 | 2.5007 | 4916.5959 | 6882.3807 | 5196.8533 | 1259.8777 | 15866.8339 | 0 | 4479.8497 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 38609.789 | 0 | 38609.5329 | 0.25607 | 0.25607 | 163.8225 | 229.3231 | 173.1608 | 41.9795 | 528.6879 | 0 | 149.27 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.4902 | 0 | 1286.4817 | 0.0085324 | 0.0085324 | 4.0082 | 0.9717 | 12.2376 | 3.4552 | 0.0057056 | 0 | 5.3082 | 3.792 | 0 | 0 | 0 | 29.7783 | 29.7785 | 0.0001975
IA_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 93037.7285 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598347.4697 | 0 | 0 | 1090880.6361 | 0 | 1090880.6361 | 0 | 0 | 513.3822 | 0 | 0 | 0 | 2204.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 3301.6813 | 0 | 0 | 6019.4793 | 0 | 6019.4793 | 0 | 0 | 93.0377 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.3475 | 0 | 0 | 1090.8806 | 0 | 1090.8806 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.1536 | 13.85 | 0 | 0 | 25.2507 | 25.2507 | 0
IA_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 4006.6932 | 4456.821 | 8802.4992 | 1586.5616 | 13417.6985 | 0 | 5173.6912 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42448.1632 | 0 | 42449.5525 | -1.3893 | -1.3893 | 410.2854 | 456.3785 | 901.3759 | 162.4639 | 1373.9723 | 0 | 529.786 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4346.6919 | 0 | 4346.8342 | -0.14226 | -0.14226 | 13.6708 | 15.2067 | 30.0341 | 5.4133 | 45.7812 | 0 | 17.6526 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.8331 | 0 | 144.8379 | -0.0047402 | -0.0047402 | 5.4588 | 0.98389 | 8.3208 | 3.2084 | 0 | 0 | 2.7638 | 2.4847 | 3.1033 | 0 | 0 | 26.3246 | 26.3237 | -0.00086155
IA_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 14577.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14577.4273 | 0 | 14577.4273 | 0 | 0 | 80.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4382 | 0 | 80.4382 | 0 | 0 | 14.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5774 | 0 | 14.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6495 | 0 | 0 | 0 | 2.6495 | 2.6495 | 0
IA_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 4056.7074 | 4240.0928 | 7096.4593 | 1586.5616 | 13417.6985 | 0 | 4754.1276 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40155.8457 | 0 | 40156.4014 | -0.55571 | -0.55571 | 415.4068 | 434.1855 | 726.6774 | 162.4639 | 1373.9723 | 0 | 486.8227 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4111.9586 | 0 | 4112.0155 | -0.056905 | -0.056905 | 13.8415 | 14.4672 | 24.2131 | 5.4133 | 45.7812 | 0 | 16.2211 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.0117 | 0 | 137.0136 | -0.0018961 | -0.0018961 | 4.4008 | 0.98389 | 8.3208 | 2.9482 | 0 | 0 | 2.6294 | 2.5157 | 3.1033 | 0 | 0 | 24.9025 | 24.9022 | -0.00034462
IA_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | IA-DESMOINES-IA | Zone5A | Zone5A(IA-DESMOINES-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 14823.8598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14823.8598 | 0 | 14823.8598 | 0 | 0 | 81.7981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7981 | 0 | 81.7981 | 0 | 0 | 14.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8239 | 0 | 14.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6943 | 0 | 0 | 0 | 2.6943 | 2.6943 | 0
IA_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 593757.4715 | 880236.0321 | 96013.3717 | 4077910.5986 | 543457.0788 | 608286.5967 | 90470.1312 | 188183.9857 | 399555.1104 | 12748.0639 | 0 | 0 | 0 | 7490618.4407 | 0 | 7490617.885 | 0.55571 | 543457.6346 | 0 | 60800.7651 | 90136.1697 | 9831.7693 | 417578.0453 | 55650.0049 | 62288.5475 | 9264.1414 | 19270.0401 | 40914.4433 | 1305.4017 | 0 | 0 | 0 | 767039.3283 | 0 | 767039.2714 | 0.056905 | 55650.0618 | 0 | 2025.9005 | 3003.3653 | 327.5976 | 13913.831 | 1854.2756 | 2075.4739 | 308.6841 | 642.0838 | 1363.282 | 43.4964 | 0 | 0 | 0 | 25557.9901 | 0 | 25557.9882 | 0.0018961 | 1854.2774 | 6.0237 | 0.65705 | 27.9065 | 4.1627 | 0.61912 | 0.087239 | 4.0633 | 0 | 0 | 2.7343 | 0 | 51.2607 | 51.2607 | 3.8029e-06
IA_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 1944731.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605550.8798 | 0 | 0 | 2550282.0466 | 0 | 2550282.0466 | 0 | 0 | 10731.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3341.4298 | 0 | 0 | 14072.4563 | 0 | 14072.4563 | 0 | 0 | 1944.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5509 | 0 | 0 | 2550.282 | 0 | 2550.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9005 | 1.2145 | 0 | 0 | 5.115 | 5.115 | 0
IA_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 549453.2257 | 717034.1395 | 96013.3717 | 4077910.5986 | 543387.6147 | 583443.432 | 85085.2689 | 168517.2907 | 399310.5965 | 11367.1163 | 0 | 0 | 0 | 7231522.6547 | 0 | 7231518.7647 | 3.89 | 543391.5047 | 0 | 56264.0103 | 73424.2959 | 9831.7693 | 417578.0453 | 55642.8917 | 59744.6074 | 8712.7315 | 17256.1706 | 40889.4051 | 1163.9927 | 0 | 0 | 0 | 740507.9198 | 0 | 740507.5215 | 0.39834 | 55643.2901 | 0 | 1874.7344 | 2446.5205 | 327.5976 | 13913.831 | 1854.0385 | 1990.709 | 290.3109 | 574.981 | 1362.4478 | 38.7846 | 0 | 0 | 0 | 24673.9553 | 0 | 24673.942 | 0.013273 | 1854.0518 | 4.9069 | 0.65705 | 27.9065 | 3.9927 | 0.58227 | 0.077789 | 3.7601 | 0 | 0 | 2.7326 | 0 | 49.4876 | 49.4877 | 2.662e-05
IA_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 1982321.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605579.3143 | 0 | 0 | 2587900.9081 | 0 | 2587900.9081 | 0 | 0 | 10938.4506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3341.5867 | 0 | 0 | 14280.0372 | 0 | 14280.0372 | 0 | 0 | 1982.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5793 | 0 | 0 | 2587.9009 | 0 | 2587.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9759 | 1.2146 | 0 | 0 | 5.1905 | 5.1905 | 0
IA_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 25104.35 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 21959.0125 | 0 | 0 | 0 | 0 | 121212.193 | 0 | 0 | 345853.7521 | 0 | 345854.5857 | -0.83357 | -0.83357 | 0 | 2570.6854 | 2905.5716 | 737.2049 | 14541.2308 | 0 | 2248.6029 | 0 | 0 | 0 | 0 | 12412.1286 | 0 | 0 | 35415.4242 | 0 | 35415.5096 | -0.085358 | -0.085358 | 0 | 85.656 | 96.8146 | 24.5639 | 484.5184 | 0 | 74.9242 | 0 | 0 | 0 | 0 | 413.576 | 0 | 0 | 1180.053 | 0 | 1180.0558 | -0.0028441 | -0.0028441 | 2.8693 | 0.72801 | 14.3599 | 2.2206 | 0 | 0 | 2.5386 | 0 | 12.2574 | 0 | 0 | 34.9739 | 34.9739 | -8.4293e-05
IA_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 267066.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267066.4299 | 0 | 267066.4299 | 0 | 0 | 1473.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1473.6726 | 0 | 1473.6726 | 0 | 0 | 267.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.0664 | 0 | 267.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9152 | 0 | 0 | 0 | 7.9152 | 7.9152 | 0
IA_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 23534.4598 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 21208.7995 | 0 | 0 | 0 | 0 | 121245.5358 | 0 | 0 | 338373.8506 | 0 | 338376.0734 | -2.2229 | -2.2229 | 0 | 2409.9287 | 2373.794 | 737.2049 | 14541.2308 | 0 | 2171.7811 | 0 | 0 | 0 | 0 | 12415.5429 | 0 | 0 | 34649.4823 | 0 | 34649.7099 | -0.22762 | -0.22762 | 0 | 80.2996 | 79.0956 | 24.5639 | 484.5184 | 0 | 72.3644 | 0 | 0 | 0 | 0 | 413.6898 | 0 | 0 | 1154.5316 | 0 | 1154.5392 | -0.0075844 | -0.0075844 | 2.3442 | 0.72801 | 14.3599 | 2.1447 | 0 | 0 | 2.3799 | 0 | 12.2607 | 0 | 0 | 34.2177 | 34.2175 | -0.00022478
IA_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 294543.6482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294543.6482 | 0 | 294543.6482 | 0 | 0 | 1625.2919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1625.2919 | 0 | 1625.2919 | 0 | 0 | 294.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.5436 | 0 | 294.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7295 | 0 | 0 | 0 | 8.7295 | 8.7295 | 0
IA_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 89986.6606 | 96627.4349 | 7127.0235 | 317887.4784 | 4818.0346 | 102348.5037 | 1283.6978 | 0 | 0 | 22053.4838 | 7182.5949 | 17624.4485 | 0 | 666939.3608 | 0 | 666938.2493 | 1.1114 | 4819.1461 | 0 | 9214.634 | 9894.6493 | 729.8072 | 32551.6778 | 493.3667 | 10480.4868 | 131.4507 | 0 | 0 | 2258.2767 | 735.4977 | 1804.7435 | 0 | 68294.5905 | 0 | 68294.4767 | 0.11381 | 493.4806 | 0 | 307.0345 | 329.6928 | 24.3174 | 1084.6321 | 16.4391 | 349.2131 | 4.38 | 0 | 0 | 75.2465 | 24.507 | 60.1346 | 0 | 2275.5971 | 0 | 2275.5933 | 0.0037922 | 16.4429 | 4.4578 | 0.3288 | 14.6653 | 4.7217 | 0.059222 | 1.0174 | 4.1514 | 0 | 0.33136 | 0 | 0.81308 | 30.7683 | 30.7684 | 5.1274e-05
IA_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 897345.8584 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126704.1926 | 0 | 0 | 1366240.4658 | 0 | 1366240.4658 | 0 | 0 | 4951.5544 | 0 | 0 | 0 | 1888.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 699.1537 | 0 | 0 | 7538.9149 | 0 | 7538.9149 | 0 | 0 | 897.3459 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.7042 | 0 | 0 | 1366.2405 | 0 | 1366.2405 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.133 | 1.7132 | 0 | 0 | 18.4729 | 18.4729 | 0
IA_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 83726.5498 | 79033.5507 | 7127.0235 | 312483.1662 | 4743.0133 | 86099.4458 | 1114.2052 | 0 | 0 | 22809.2539 | 7182.5949 | 12461.8716 | 0 | 616780.675 | 0 | 616780.675 | 0 | 4743.0133 | 0 | 8573.5987 | 8093.0356 | 729.8072 | 31998.2762 | 485.6846 | 8816.5832 | 114.0946 | 0 | 0 | 2335.6676 | 735.4977 | 1276.0956 | 0 | 63158.3411 | 0 | 63158.3411 | 0 | 485.6846 | 0 | 285.675 | 269.6625 | 24.3174 | 1066.1926 | 16.1832 | 293.7713 | 3.8017 | 0 | 0 | 77.8252 | 24.507 | 42.5199 | 0 | 2104.4557 | 0 | 2104.4557 | 0 | 16.1832 | 3.6461 | 0.3288 | 14.416 | 3.9721 | 0.051402 | 1.0523 | 3.8626 | 0 | 0.33136 | 0 | 0.57491 | 28.4544 | 28.4544 | 0
IA_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 872977.4802 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126467.2383 | 0 | 0 | 1341635.1334 | 0 | 1341635.1334 | 0 | 0 | 4817.0897 | 0 | 0 | 0 | 1888.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 697.8462 | 0 | 0 | 7403.1427 | 0 | 7403.1427 | 0 | 0 | 872.9775 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.4672 | 0 | 0 | 1341.6351 | 0 | 1341.6351 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.8035 | 1.71 | 0 | 0 | 18.1403 | 18.1403 | 0
IA_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 32361.9661 | 90603.5024 | 10708.596 | 53987.5506 | 0 | 46988.3412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234649.9563 | 0 | 234648.0113 | 1.945 | 1.945 | 0 | 3313.8653 | 9277.7986 | 1096.5602 | 5528.3252 | 0 | 4811.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24028.1555 | 0 | 24027.9564 | 0.19917 | 0.19917 | 0 | 110.419 | 309.1392 | 36.5377 | 184.2055 | 0 | 160.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800.6257 | 0 | 800.619 | 0.0066363 | 0.0066363 | 12.5198 | 1.4797 | 7.4601 | 6.493 | 0 | 0 | 4.4719 | 0 | 0 | 0 | 0 | 32.4242 | 32.4245 | 0.00026876
IA_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 700408.4172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92753.3834 | 0 | 0 | 793161.8005 | 0 | 793161.8005 | 0 | 0 | 3864.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511.8132 | 0 | 0 | 4376.6668 | 0 | 4376.6668 | 0 | 0 | 700.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7534 | 0 | 0 | 793.1618 | 0 | 793.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3658 | 3.7564 | 0 | 0 | 32.1222 | 32.1222 | 0
IA_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 0 | 30250.2555 | 74990.7362 | 10708.596 | 53987.5506 | 0 | 45065.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215002.7113 | 0 | 214999.377 | 3.3343 | 3.3343 | 0 | 3097.6262 | 7679.0514 | 1096.5602 | 5528.3252 | 0 | 4614.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22016.2776 | 0 | 22015.9362 | 0.34143 | 0.34143 | 0 | 103.2139 | 255.8684 | 36.5377 | 184.2055 | 0 | 153.7637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733.5893 | 0 | 733.5779 | 0.011377 | 0.011377 | 10.3624 | 1.4797 | 7.4601 | 6.2273 | 0 | 0 | 4.1801 | 0 | 0 | 0 | 0 | 29.7091 | 29.7096 | 0.00046074
IA_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 728994.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92762.8615 | 0 | 0 | 821757.443 | 0 | 821757.443 | 0 | 0 | 4022.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511.8655 | 0 | 0 | 4534.4576 | 0 | 4534.4576 | 0 | 0 | 728.9946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7629 | 0 | 0 | 821.7574 | 0 | 821.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5235 | 3.7568 | 0 | 0 | 33.2803 | 33.2803 | 0
IA_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 64079.3048 | 61231.274 | 79041.8864 | 12295.1576 | 154949.5496 | 0 | 46060.2999 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 417729.715 | 0 | 417734.4386 | -4.7236 | -4.7236 | 6561.7208 | 6270.0825 | 8093.8892 | 1259.0241 | 15866.8339 | 0 | 4716.5747 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 42775.5228 | 0 | 42776.0065 | -0.48369 | -0.48369 | 218.6386 | 208.9211 | 269.6909 | 41.9511 | 528.6879 | 0 | 157.1577 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1425.2938 | 0 | 1425.3099 | -0.016117 | -0.016117 | 6.2426 | 0.97104 | 12.2376 | 3.6377 | 0.0057056 | 0 | 4.8359 | 5.0608 | 0 | 0 | 0 | 32.9918 | 32.9914 | -0.00037306
IA_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 131831.8832 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 635644.0734 | 0 | 0 | 1166971.3945 | 0 | 1166971.3945 | 0 | 0 | 727.4483 | 0 | 0 | 0 | 2204.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 3507.484 | 0 | 0 | 6439.3482 | 0 | 6439.3482 | 0 | 0 | 131.8319 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 635.6441 | 0 | 0 | 1166.9714 | 0 | 1166.9714 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.0515 | 14.7133 | 0 | 0 | 27.012 | 27.012 | 0
IA_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 69911.5163 | 56724.4388 | 50786.6418 | 12295.1576 | 154949.5496 | 0 | 43551.2542 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 388290.801 | 0 | 388291.9125 | -1.1114 | -1.1114 | 7158.9393 | 5808.5825 | 5200.5521 | 1259.0241 | 15866.8339 | 0 | 4459.6484 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 39760.978 | 0 | 39761.0918 | -0.11381 | -0.11381 | 238.5381 | 193.5438 | 173.284 | 41.9511 | 528.6879 | 0 | 148.5969 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.8482 | 0 | 1324.852 | -0.0037922 | -0.0037922 | 4.011 | 0.97104 | 12.2376 | 3.4396 | 0.0057056 | 0 | 4.48 | 5.5215 | 0 | 0 | 0 | 30.6665 | 30.6664 | -8.7778e-05
IA_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 126457.7602 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 635719.8987 | 0 | 0 | 1161673.0968 | 0 | 1161673.0968 | 0 | 0 | 697.7939 | 0 | 0 | 0 | 2204.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 3507.9024 | 0 | 0 | 6410.1121 | 0 | 6410.1121 | 0 | 0 | 126.4578 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 635.7199 | 0 | 0 | 1161.6731 | 0 | 1161.6731 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.9271 | 14.7151 | 0 | 0 | 26.8893 | 26.8893 | 0
IA_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 5068.1056 | 3503.7726 | 8788.6064 | 1589.3401 | 13417.6985 | 0 | 5304.2838 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42676.0057 | 0 | 42674.6164 | 1.3893 | 1.3893 | 518.974 | 358.7863 | 899.9533 | 162.7484 | 1373.9723 | 0 | 543.1587 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4370.023 | 0 | 4369.8807 | 0.14226 | 0.14226 | 17.2924 | 11.9549 | 29.9867 | 5.4228 | 45.7812 | 0 | 18.0982 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.6105 | 0 | 145.6058 | 0.0047402 | 0.0047402 | 5.4501 | 0.98561 | 8.3208 | 3.2894 | 0 | 0 | 2.1728 | 3.1429 | 3.1033 | 0 | 0 | 26.4642 | 26.465 | 0.00086155
IA_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 29297.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29297.0272 | 0 | 29297.0272 | 0 | 0 | 161.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.661 | 0 | 161.661 | 0 | 0 | 29.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.297 | 0 | 29.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3248 | 0 | 0 | 0 | 5.3248 | 5.3248 | 0
IA_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Electricity | 5140.3484 | 3225.9159 | 7110.3521 | 1589.3401 | 13417.6985 | 0 | 4818.0346 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40305.8883 | 0 | 40305.3326 | 0.55571 | 0.55571 | 526.3717 | 330.3338 | 728.1001 | 162.7484 | 1373.9723 | 0 | 493.3667 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4127.323 | 0 | 4127.2661 | 0.056905 | 0.056905 | 17.5389 | 11.0068 | 24.2605 | 5.4228 | 45.7812 | 0 | 16.4391 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.5237 | 0 | 137.5218 | 0.0018961 | 0.0018961 | 4.4094 | 0.98561 | 8.3208 | 2.9878 | 0 | 0 | 2.0005 | 3.1877 | 3.1033 | 0 | 0 | 24.9949 | 24.9952 | 0.00034462
IA_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | IA-MASONCITY-IA | Zone6A | Zone6A(IA-MASONCITY-IA) |  |  | IA | 0.1024 | 0.005518 |  |  |  | Natural Gas | 30415.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30415.4514 | 0 | 30415.4514 | 0 | 0 | 167.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.8325 | 0 | 167.8325 | 0 | 0 | 30.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.4155 | 0 | 30.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5281 | 0 | 0 | 0 | 5.5281 | 5.5281 | 0
ID_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 519630.8695 | 882117.1218 | 96816.3775 | 4077910.5986 | 543459.8574 | 667233.8888 | 83384.7861 | 158533.9006 | 631773.8208 | 0 | 0 | 0 | 0 | 7660861.2213 | 0 | 7660858.9984 | 2.2229 | 543462.0803 | 0 | 40271.3924 | 68364.0769 | 7503.2693 | 316038.0714 | 42118.1389 | 51710.6264 | 6462.3209 | 12286.3773 | 48962.4711 | 0 | 0 | 0 | 0 | 593716.7447 | 0 | 593716.5724 | 0.17227 | 42118.3112 | 0 | 1772.9805 | 3009.7836 | 330.3375 | 13913.831 | 1854.285 | 2276.602 | 284.5089 | 540.9177 | 2155.6123 | 0 | 0 | 0 | 0 | 26138.8585 | 0 | 26138.8509 | 0.0075844 | 1854.2926 | 6.0366 | 0.66255 | 27.9065 | 4.5661 | 0.57063 | 0 | 3.556 | 0 | 0 | 4.3234 | 0 | 52.4258 | 52.4258 | 1.5212e-05
ID_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 1375974.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562065.0303 | 0 | 0 | 1938039.5779 | 0 | 1938039.5779 | 0 | 0 | 7544.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.8026 | 0 | 0 | 10626.271 | 0 | 10626.271 | 0 | 0 | 1375.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.065 | 0 | 0 | 1938.0396 | 0 | 1938.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7597 | 1.1273 | 0 | 0 | 3.8871 | 3.8871 | 0
ID_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 488797.1151 | 717820.4739 | 96816.3775 | 4077910.5986 | 543387.6147 | 646655.824 | 79486.4571 | 141562.4153 | 631687.6853 | 0 | 0 | 0 | 0 | 7424124.5614 | 0 | 7424123.7278 | 0.83357 | 543388.4482 | 0 | 37881.7764 | 55631.0867 | 7503.2693 | 316038.0714 | 42112.5401 | 50115.8264 | 6160.2004 | 10971.0872 | 48955.7956 | 0 | 0 | 0 | 0 | 575369.6535 | 0 | 575369.5889 | 0.064602 | 42112.6047 | 0 | 1667.7758 | 2449.2035 | 330.3375 | 13913.831 | 1854.0385 | 2206.3897 | 271.2078 | 483.011 | 2155.3184 | 0 | 0 | 0 | 0 | 25331.113 | 0 | 25331.1102 | 0.0028441 | 1854.0414 | 4.9123 | 0.66255 | 27.9065 | 4.4253 | 0.54395 | 0 | 3.345 | 0 | 0 | 4.3228 | 0 | 50.8057 | 50.8057 | 5.7044e-06
ID_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 2171031.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561989.205 | 0 | 0 | 2733021.1873 | 0 | 2733021.1873 | 0 | 0 | 11903.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.3868 | 0 | 0 | 14985.1552 | 0 | 14985.1552 | 0 | 0 | 2171.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.9892 | 0 | 0 | 2733.0212 | 0 | 2733.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3544 | 1.1272 | 0 | 0 | 5.4815 | 5.4815 | 0
ID_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 23353.853 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 22128.5051 | 0 | 0 | 0 | 0 | 112859.8215 | 0 | 0 | 335920.3762 | 0 | 335919.5426 | 0.83357 | 0.83357 | 0 | 1809.9236 | 2199.041 | 557.9431 | 11005.3261 | 0 | 1714.9591 | 0 | 0 | 0 | 0 | 8746.6362 | 0 | 0 | 26033.8292 | 0 | 26033.7646 | 0.064602 | 0.064602 | 0 | 79.6833 | 96.8146 | 24.5639 | 484.5184 | 0 | 75.5025 | 0 | 0 | 0 | 0 | 385.0777 | 0 | 0 | 1146.1603 | 0 | 1146.1575 | 0.0028441 | 0.0028441 | 2.8693 | 0.72801 | 14.3599 | 2.2377 | 0 | 0 | 2.3616 | 0 | 11.4128 | 0 | 0 | 33.9693 | 33.9694 | 8.4293e-05
ID_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 175270.3418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175270.3418 | 0 | 175270.3418 | 0 | 0 | 961.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.0073 | 0 | 961.0073 | 0 | 0 | 175.2703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.2703 | 0 | 175.2703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1946 | 0 | 0 | 0 | 5.1946 | 5.1946 | 0
ID_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 26060.1769 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 21895.1055 | 0 | 0 | 0 | 0 | 112715.336 | 0 | 0 | 333055.674 | 0 | 333060.3975 | -4.7236 | -4.7236 | 0 | 2019.6637 | 1796.5726 | 557.9431 | 11005.3261 | 0 | 1696.8707 | 0 | 0 | 0 | 0 | 8735.4385 | 0 | 0 | 25811.8147 | 0 | 25812.1808 | -0.36608 | -0.36608 | 0 | 88.9173 | 79.0956 | 24.5639 | 484.5184 | 0 | 74.7061 | 0 | 0 | 0 | 0 | 384.5847 | 0 | 0 | 1136.386 | 0 | 1136.4021 | -0.016117 | -0.016117 | 2.3442 | 0.72801 | 14.3599 | 2.2141 | 0 | 0 | 2.6353 | 0 | 11.3981 | 0 | 0 | 33.6802 | 33.6797 | -0.00047766
ID_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 75360.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75360.9392 | 0 | 75360.9392 | 0 | 0 | 413.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.204 | 0 | 413.204 | 0 | 0 | 75.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3609 | 0 | 75.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2335 | 0 | 0 | 0 | 2.2335 | 2.2335 | 0
ID_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 82053.8527 | 96933.0773 | 7135.3592 | 317887.4784 | 4818.0346 | 99075.3522 | 911.3699 | 0 | 0 | 0 | 7179.8163 | 17485.5201 | 0 | 633479.8608 | 0 | 633477.9158 | 1.945 | 4819.9796 | 0 | 6359.1736 | 7512.3135 | 552.9903 | 24636.2796 | 373.3977 | 7678.3398 | 70.6312 | 0 | 0 | 0 | 556.4358 | 1355.1278 | 0 | 49094.6892 | 0 | 49094.5385 | 0.15074 | 373.5484 | 0 | 279.9677 | 330.7357 | 24.3458 | 1084.6321 | 16.4391 | 338.0451 | 3.1096 | 0 | 0 | 0 | 24.4975 | 59.6606 | 0 | 2161.4333 | 0 | 2161.4266 | 0.0066363 | 16.4458 | 4.4719 | 0.32918 | 14.6653 | 4.5707 | 0.042045 | 0 | 3.7854 | 0 | 0.33123 | 0 | 0.80667 | 29.2247 | 29.2247 | 8.973e-05
ID_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 599247.8959 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117519.8447 | 0 | 0 | 1058958.1555 | 0 | 1058958.1555 | 0 | 0 | 3285.6762 | 0 | 0 | 0 | 1876.23 | 0 | 0 | 0 | 0 | 0 | 0 | 644.3613 | 0 | 0 | 5806.2676 | 0 | 5806.2676 | 0 | 0 | 599.2479 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5198 | 0 | 0 | 1058.9582 | 0 | 1058.9582 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.1024 | 1.589 | 0 | 0 | 14.3182 | 14.3182 | 0
ID_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 81195.2756 | 78500.0659 | 7135.3592 | 312483.1662 | 4743.0133 | 79622.6069 | 1317.0406 | 0 | 0 | 0 | 7179.8163 | 12431.3073 | 0 | 584607.6514 | 0 | 584608.485 | -0.83357 | 4742.1798 | 0 | 6292.6339 | 6083.7551 | 552.9903 | 24217.4454 | 367.5835 | 6170.752 | 102.0706 | 0 | 0 | 0 | 556.4358 | 963.4263 | 0 | 45307.093 | 0 | 45307.1576 | -0.064602 | 367.5189 | 0 | 277.0383 | 267.8422 | 24.3458 | 1066.1926 | 16.1832 | 271.6723 | 4.4937 | 0 | 0 | 0 | 24.4975 | 42.4156 | 0 | 1994.6813 | 0 | 1994.6842 | -0.0028441 | 16.1803 | 3.6215 | 0.32918 | 14.416 | 3.6733 | 0.06076 | 0 | 3.7458 | 0 | 0.33123 | 0 | 0.5735 | 26.9701 | 26.9701 | -3.8456e-05
ID_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 844817.8336 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117453.4975 | 0 | 0 | 1304461.7459 | 0 | 1304461.7459 | 0 | 0 | 4632.1362 | 0 | 0 | 0 | 1876.23 | 0 | 0 | 0 | 0 | 0 | 0 | 643.9975 | 0 | 0 | 7152.3638 | 0 | 7152.3638 | 0 | 0 | 844.8178 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.4535 | 0 | 0 | 1304.4617 | 0 | 1304.4617 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.4228 | 1.5881 | 0 | 0 | 17.6376 | 17.6376 | 0
ID_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 27452.2388 | 85710.4465 | 10664.1389 | 53987.5506 | 0 | 44470.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222285.3346 | 0 | 222284.2232 | 1.1114 | 1.1114 | 0 | 2127.5485 | 6642.5596 | 826.4708 | 4184.0352 | 0 | 3446.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17227.1134 | 0 | 17227.0273 | 0.086136 | 0.086136 | 0 | 93.667 | 292.444 | 36.386 | 184.2055 | 0 | 151.7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.4376 | 0 | 758.4338 | 0.0037922 | 0.0037922 | 11.8437 | 1.4736 | 7.4601 | 6.1451 | 0 | 0 | 3.7934 | 0 | 0 | 0 | 0 | 30.7158 | 30.7159 | 0.00015358
ID_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 293652.7001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90175.3208 | 0 | 0 | 383828.0209 | 0 | 383828.0209 | 0 | 0 | 1610.0978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494.4313 | 0 | 0 | 2104.529 | 0 | 2104.529 | 0 | 0 | 293.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1753 | 0 | 0 | 383.828 | 0 | 383.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8926 | 3.652 | 0 | 0 | 15.5446 | 15.5446 | 0
ID_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 25415.5494 | 67980.4125 | 10664.1389 | 53987.5506 | 0 | 42281.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200329.1007 | 0 | 200329.1007 | 0 | 0 | 0 | 1969.7051 | 5268.482 | 826.4708 | 4184.0352 | 0 | 3276.8123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15525.5053 | 0 | 15525.5053 | 0 | 0 | 0 | 86.7179 | 231.9492 | 36.386 | 184.2055 | 0 | 144.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683.5229 | 0 | 683.5229 | 0 | 0 | 9.3937 | 1.4736 | 7.4601 | 5.8426 | 0 | 0 | 3.512 | 0 | 0 | 0 | 0 | 27.682 | 27.682 | 0
ID_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 320333.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90184.799 | 0 | 0 | 410518.551 | 0 | 410518.551 | 0 | 0 | 1756.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494.4833 | 0 | 0 | 2250.8732 | 0 | 2250.8732 | 0 | 0 | 320.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1848 | 0 | 0 | 410.5186 | 0 | 410.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9732 | 3.6524 | 0 | 0 | 16.6256 | 16.6256 | 0
ID_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 16943.6996 | 61912.0228 | 79561.4784 | 12297.9361 | 154949.5496 | 0 | 46632.6846 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 372369.6139 | 0 | 372370.7254 | -1.1114 | -1.1114 | 1313.1367 | 4798.1818 | 6166.0146 | 953.0901 | 12008.5901 | 0 | 3614.0331 | 5.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 28858.6451 | 0 | 28858.7312 | -0.086136 | -0.086136 | 57.8119 | 211.2438 | 271.4638 | 41.9606 | 528.6879 | 0 | 159.1107 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.5251 | 0 | 1270.5289 | -0.0037922 | -0.0037922 | 6.2836 | 0.97126 | 12.2376 | 3.6829 | 0.0057056 | 0 | 4.8897 | 1.3382 | 0 | 0 | 0 | 29.409 | 29.4089 | -8.7778e-05
ID_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 47646.7666 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 585675.1548 | 0 | 0 | 1032817.3593 | 0 | 1032817.3593 | 0 | 0 | 261.2472 | 0 | 0 | 0 | 2190.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 3211.2569 | 0 | 0 | 5662.9376 | 0 | 5662.9376 | 0 | 0 | 47.6468 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 585.6752 | 0 | 0 | 1032.8174 | 0 | 1032.8174 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.1029 | 13.5567 | 0 | 0 | 23.9067 | 23.9067 | 0
ID_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 20422.4651 | 57349.6163 | 51039.4914 | 12297.9361 | 154949.5496 | 0 | 49077.8233 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 345209.1246 | 0 | 345207.1796 | 1.945 | 1.945 | 1582.741 | 4444.5953 | 3955.5606 | 953.0901 | 12008.5901 | 0 | 3803.5313 | 5.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 26753.7072 | 0 | 26753.5564 | 0.15074 | 0.15074 | 69.6815 | 195.6769 | 174.1467 | 41.9606 | 528.6879 | 0 | 167.4535 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.8535 | 0 | 1177.8469 | 0.0066363 | 0.0066363 | 4.031 | 0.97126 | 12.2376 | 3.8761 | 0.0057056 | 0 | 4.5293 | 1.6129 | 0 | 0 | 0 | 27.2637 | 27.2639 | 0.00015361
ID_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 39372.3232 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 585732.0238 | 0 | 0 | 1024599.7849 | 0 | 1024599.7849 | 0 | 0 | 215.8784 | 0 | 0 | 0 | 2190.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 3211.5687 | 0 | 0 | 5617.8806 | 0 | 5617.8806 | 0 | 0 | 39.3723 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 585.732 | 0 | 0 | 1024.5998 | 0 | 1024.5998 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.91135 | 13.558 | 0 | 0 | 23.7165 | 23.7165 | 0
ID_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 2611.8527 | 3559.3439 | 8885.8563 | 1606.0115 | 13417.6985 | 0 | 5423.7622 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40508.7237 | 0 | 40509.0015 | -0.27786 | -0.27786 | 202.4186 | 275.8492 | 688.6539 | 124.4659 | 1039.8716 | 0 | 420.3416 | 0 | 0 | 0 | 0 | 387.8254 | 0 | 0 | 3139.4261 | 0 | 3139.4476 | -0.021534 | -0.021534 | 8.9116 | 12.1445 | 30.3185 | 5.4797 | 45.7812 | 0 | 18.5059 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.2158 | 0 | 138.2167 | -0.00094805 | -0.00094805 | 5.5105 | 0.99595 | 8.3208 | 3.3635 | 0 | 0 | 2.2073 | 1.6197 | 3.1033 | 0 | 0 | 25.1212 | 25.121 | -0.00017231
ID_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 2104.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2104.154 | 0 | 2104.154 | 0 | 0 | 11.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5371 | 0 | 11.5371 | 0 | 0 | 2.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1042 | 0 | 2.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38243 | 0 | 0 | 0 | 0.38243 | 0.38243 | 0
ID_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 2678.5383 | 3339.8372 | 7157.5878 | 1606.0115 | 13417.6985 | 0 | 4976.4129 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38180.2848 | 0 | 38181.9519 | -1.6671 | -1.6671 | 207.5867 | 258.8374 | 554.7131 | 124.4659 | 1039.8716 | 0 | 385.672 | 0 | 0 | 0 | 0 | 387.8254 | 0 | 0 | 2958.9721 | 0 | 2959.1013 | -0.1292 | -0.1292 | 9.1392 | 11.3955 | 24.4217 | 5.4797 | 45.7812 | 0 | 16.9795 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.2711 | 0 | 130.2768 | -0.0056883 | -0.0056883 | 4.4387 | 0.99595 | 8.3208 | 3.0861 | 0 | 0 | 2.0712 | 1.6611 | 3.1033 | 0 | 0 | 23.6781 | 23.6771 | -0.0010339
ID_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | ID-BOISE-ID | Zone5B | Zone5B(ID-BOISE-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 2360.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2360.0646 | 0 | 2360.0646 | 0 | 0 | 12.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9402 | 0 | 12.9402 | 0 | 0 | 2.3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3601 | 0 | 2.3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42895 | 0 | 0 | 0 | 0.42895 | 0.42895 | 0
ID_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 444139.9913 | 881755.9081 | 96346.7997 | 4077910.5986 | 543459.8574 | 717242.532 | 72153.8196 | 122145.7914 | 638064.4958 | 0 | 0 | 0 | 0 | 7593219.794 | 0 | 7593220.0718 | -0.27786 | 543459.5796 | 0 | 34420.8493 | 68336.0829 | 7466.877 | 316038.0714 | 42118.1389 | 55586.2962 | 5591.921 | 9466.2988 | 49449.9984 | 0 | 0 | 0 | 0 | 588474.534 | 0 | 588474.5556 | -0.021534 | 42118.1174 | 0 | 1515.4057 | 3008.5512 | 328.7353 | 13913.831 | 1854.285 | 2447.2315 | 246.1888 | 416.7614 | 2177.0761 | 0 | 0 | 0 | 0 | 25908.0659 | 0 | 25908.0669 | -0.00094805 | 1854.2841 | 6.0341 | 0.65933 | 27.9065 | 4.9083 | 0.49377 | 0 | 3.0394 | 0 | 0 | 4.3665 | 0 | 51.9629 | 51.9629 | -1.9015e-06
ID_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 2475688.8393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610498.4852 | 0 | 0 | 3086187.3244 | 0 | 3086187.3244 | 0 | 0 | 13574.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3347.3632 | 0 | 0 | 16921.5651 | 0 | 16921.5651 | 0 | 0 | 2475.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.4985 | 0 | 0 | 3086.1873 | 0 | 3086.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9654 | 1.2245 | 0 | 0 | 6.1899 | 6.1899 | 0
ID_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 410933.3409 | 718039.9806 | 96346.7997 | 4077910.5986 | 543387.6147 | 691565.7973 | 70264.3943 | 108711.4214 | 637875.5533 | 0 | 0 | 0 | 0 | 7355035.5008 | 0 | 7355035.223 | 0.27786 | 543387.8925 | 0 | 31847.3339 | 55648.0985 | 7466.877 | 316038.0714 | 42112.5401 | 53596.3493 | 5445.4906 | 8425.1352 | 49435.3554 | 0 | 0 | 0 | 0 | 570015.2513 | 0 | 570015.2298 | 0.021534 | 42112.5617 | 0 | 1402.1046 | 2449.9524 | 328.7353 | 13913.831 | 1854.0385 | 2359.6225 | 239.7421 | 370.9234 | 2176.4314 | 0 | 0 | 0 | 0 | 25095.3811 | 0 | 25095.3802 | 0.00094805 | 1854.0395 | 4.9138 | 0.65933 | 27.9065 | 4.7326 | 0.48084 | 0 | 2.8122 | 0 | 0 | 4.3652 | 0 | 50.3329 | 50.3329 | 1.9015e-06
ID_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 3469437.1769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610507.9633 | 0 | 0 | 4079945.1402 | 0 | 4079945.1402 | 0 | 0 | 19022.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3347.4152 | 0 | 0 | 22370.3392 | 0 | 22370.3392 | 0 | 0 | 3469.4372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.508 | 0 | 0 | 4079.9451 | 0 | 4079.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9585 | 1.2245 | 0 | 0 | 8.183 | 8.183 | 0
ID_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 21311.6065 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22111.8337 | 0 | 0 | 0 | 0 | 122176.3556 | 0 | 0 | 343183.5495 | 0 | 343184.6609 | -1.1114 | -1.1114 | 0 | 1651.6495 | 2199.041 | 558.3738 | 11005.3261 | 0 | 1713.6671 | 0 | 0 | 0 | 0 | 9468.6676 | 0 | 0 | 26596.7251 | 0 | 26596.8112 | -0.086136 | -0.086136 | 0 | 72.7152 | 96.8146 | 24.5829 | 484.5184 | 0 | 75.4456 | 0 | 0 | 0 | 0 | 416.8657 | 0 | 0 | 1170.9423 | 0 | 1170.9461 | -0.0037922 | -0.0037922 | 2.8693 | 0.72858 | 14.3599 | 2.236 | 0 | 0 | 2.1551 | 0 | 12.3549 | 0 | 0 | 34.704 | 34.7038 | -0.00011239
ID_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 161612.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161612.2971 | 0 | 161612.2971 | 0 | 0 | 886.1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.1202 | 0 | 886.1202 | 0 | 0 | 161.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.6123 | 0 | 161.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7898 | 0 | 0 | 0 | 4.7898 | 4.7898 | 0
ID_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 20161.2798 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20989.2927 | 0 | 0 | 0 | 0 | 122170.7985 | 0 | 0 | 335711.9837 | 0 | 335715.0401 | -3.0564 | -3.0564 | 0 | 1562.4992 | 1796.5726 | 558.3738 | 11005.3261 | 0 | 1626.6702 | 0 | 0 | 0 | 0 | 9468.2369 | 0 | 0 | 26017.6787 | 0 | 26017.9156 | -0.23687 | -0.23687 | 0 | 68.7903 | 79.0956 | 24.5829 | 484.5184 | 0 | 71.6155 | 0 | 0 | 0 | 0 | 416.8468 | 0 | 0 | 1145.4493 | 0 | 1145.4597 | -0.010429 | -0.010429 | 2.3442 | 0.72858 | 14.3599 | 2.1225 | 0 | 0 | 2.0388 | 0 | 12.3543 | 0 | 0 | 33.9486 | 33.9483 | -0.00030908
ID_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 155896.9599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155896.9599 | 0 | 155896.9599 | 0 | 0 | 854.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854.783 | 0 | 854.783 | 0 | 0 | 155.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.897 | 0 | 155.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6204 | 0 | 0 | 0 | 4.6204 | 4.6204 | 0
ID_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 57960.901 | 96894.1773 | 7129.8021 | 317887.4784 | 4818.0346 | 105574.4197 | 1055.8553 | 0 | 0 | 18360.7686 | 7179.8163 | 17527.1986 | 0 | 634388.4521 | 0 | 634389.2857 | -0.83357 | 4817.2011 | 0 | 4491.9698 | 7509.2987 | 552.5597 | 24636.2796 | 373.3977 | 8182.0175 | 81.8288 | 0 | 0 | 1422.9596 | 556.4358 | 1358.3579 | 0 | 49165.105 | 0 | 49165.1696 | -0.064602 | 373.3331 | 0 | 197.7626 | 330.6029 | 24.3269 | 1084.6321 | 16.4391 | 360.2199 | 3.6026 | 0 | 0 | 62.6469 | 24.4975 | 59.8028 | 0 | 2164.5334 | 0 | 2164.5362 | -0.0028441 | 16.4363 | 4.4701 | 0.32892 | 14.6653 | 4.8705 | 0.04871 | 0.84705 | 2.6739 | 0 | 0.33123 | 0 | 0.80859 | 29.2667 | 29.2667 | -3.8456e-05
ID_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 527251.7075 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126846.3652 | 0 | 0 | 996288.4875 | 0 | 996288.4875 | 0 | 0 | 2890.9211 | 0 | 0 | 0 | 1876.23 | 0 | 0 | 0 | 0 | 0 | 0 | 695.4986 | 0 | 0 | 5462.6498 | 0 | 5462.6498 | 0 | 0 | 527.2517 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.8464 | 0 | 0 | 996.2885 | 0 | 996.2885 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.129 | 1.7151 | 0 | 0 | 13.4708 | 13.4708 | 0
ID_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 51784.1473 | 79089.122 | 7129.8021 | 312483.1662 | 4745.7919 | 81923.2601 | 989.1697 | 0 | 0 | 20339.1081 | 7179.8163 | 12439.643 | 0 | 578103.0268 | 0 | 578104.6939 | -1.6671 | 4744.1248 | 0 | 4013.2714 | 6129.407 | 552.5597 | 24217.4454 | 367.7989 | 6349.0527 | 76.6607 | 0 | 0 | 1576.2809 | 556.4358 | 964.0723 | 0 | 44802.9846 | 0 | 44803.1138 | -0.1292 | 367.6697 | 0 | 176.6875 | 269.8521 | 24.3269 | 1066.1926 | 16.1926 | 279.5222 | 3.375 | 0 | 0 | 69.397 | 24.4975 | 42.4441 | 0 | 1972.4875 | 0 | 1972.4932 | -0.0056883 | 16.187 | 3.6487 | 0.32892 | 14.416 | 3.7794 | 0.045634 | 0.93832 | 2.389 | 0 | 0.33123 | 0 | 0.57389 | 26.6701 | 26.67 | -7.6911e-05
ID_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 646894.6626 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126808.4525 | 0 | 0 | 1115893.5299 | 0 | 1115893.5299 | 0 | 0 | 3546.9234 | 0 | 0 | 0 | 1876.23 | 0 | 0 | 0 | 0 | 0 | 0 | 695.2907 | 0 | 0 | 6118.4442 | 0 | 6118.4442 | 0 | 0 | 646.8947 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.8085 | 0 | 0 | 1115.8935 | 0 | 1115.8935 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.7467 | 1.7146 | 0 | 0 | 15.088 | 15.088 | 0
ID_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 20780.9002 | 90953.6018 | 10686.3675 | 53987.5506 | 0 | 48183.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224591.5449 | 0 | 224589.5999 | 1.945 | 1.945 | 0 | 1610.5198 | 7048.9041 | 828.1935 | 4184.0352 | 0 | 3734.1922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17405.8447 | 0 | 17405.694 | 0.15074 | 0.15074 | 0 | 70.9044 | 310.3337 | 36.4619 | 184.2055 | 0 | 164.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766.3064 | 0 | 766.2997 | 0.0066363 | 0.0066363 | 12.5682 | 1.4767 | 7.4601 | 6.6581 | 0 | 0 | 2.8716 | 0 | 0 | 0 | 0 | 31.0343 | 31.0346 | 0.00026876
ID_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 468610.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93028.2503 | 0 | 0 | 561638.5126 | 0 | 561638.5126 | 0 | 0 | 2569.3901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510.0739 | 0 | 0 | 3079.464 | 0 | 3079.464 | 0 | 0 | 468.6103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0283 | 0 | 0 | 561.6385 | 0 | 561.6385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9782 | 3.7675 | 0 | 0 | 22.7458 | 22.7458 | 0
ID_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 0 | 18833.125 | 75279.7071 | 10686.3675 | 53987.5506 | 0 | 49825.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208612.0079 | 0 | 208611.1744 | 0.83357 | 0.83357 | 0 | 1459.5672 | 5834.1773 | 828.1935 | 4184.0352 | 0 | 3861.4575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16167.4306 | 0 | 16167.366 | 0.064602 | 0.064602 | 0 | 64.2586 | 256.8544 | 36.4619 | 184.2055 | 0 | 170.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.7842 | 0 | 711.7813 | 0.0028441 | 0.0028441 | 10.4023 | 1.4767 | 7.4601 | 6.885 | 0 | 0 | 2.6024 | 0 | 0 | 0 | 0 | 28.8264 | 28.8265 | 0.00011518
ID_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 493386.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93047.2067 | 0 | 0 | 586433.4085 | 0 | 586433.4085 | 0 | 0 | 2705.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510.1778 | 0 | 0 | 3215.4144 | 0 | 3215.4144 | 0 | 0 | 493.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0472 | 0 | 0 | 586.4334 | 0 | 586.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9816 | 3.7683 | 0 | 0 | 23.7499 | 23.7499 | 0
ID_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 32845.4368 | 51945.3041 | 79414.2143 | 12306.2718 | 154949.5496 | 0 | 52739.9742 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 384272.9936 | 0 | 384271.8822 | 1.1114 | 1.1114 | 2545.5213 | 4025.7611 | 6154.6016 | 953.7361 | 12008.5901 | 0 | 4087.348 | 5.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 29781.157 | 0 | 29781.0709 | 0.086136 | 0.086136 | 112.0686 | 177.2374 | 270.9613 | 41.989 | 528.6879 | 0 | 179.9488 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.1395 | 0 | 1311.1357 | 0.0037922 | 0.0037922 | 6.272 | 0.97192 | 12.2376 | 4.1653 | 0.0057056 | 0 | 4.1025 | 2.5941 | 0 | 0 | 0 | 30.349 | 30.349 | 8.7778e-05
ID_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 65721.6391 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 641112.9781 | 0 | 0 | 1106330.0551 | 0 | 1106330.0551 | 0 | 0 | 360.3517 | 0 | 0 | 0 | 2190.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 3515.2225 | 0 | 0 | 6066.0077 | 0 | 6066.0077 | 0 | 0 | 65.7216 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 641.113 | 0 | 0 | 1106.3301 | 0 | 1106.3301 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5213 | 14.8399 | 0 | 0 | 25.6083 | 25.6083 | 0
ID_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 37946.8852 | 47530.1617 | 51028.3771 | 12306.2718 | 154949.5496 | 0 | 49716.8936 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 353550.3818 | 0 | 353550.3818 | 0 | 0 | 2940.8836 | 3683.5875 | 3954.6992 | 953.7361 | 12008.5901 | 0 | 3853.0593 | 5.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 27400.1546 | 0 | 27400.1546 | 0 | 0 | 129.4748 | 162.1729 | 174.1088 | 41.989 | 528.6879 | 0 | 169.634 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.3139 | 0 | 1206.3139 | 0 | 0 | 4.0301 | 0.97192 | 12.2376 | 3.9265 | 0.0057056 | 0 | 3.7538 | 2.997 | 0 | 0 | 0 | 27.9226 | 27.9226 | 0
ID_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 66072.3314 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 641169.8472 | 0 | 0 | 1106737.6165 | 0 | 1106737.6165 | 0 | 0 | 362.2746 | 0 | 0 | 0 | 2190.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 3515.5343 | 0 | 0 | 6068.2424 | 0 | 6068.2424 | 0 | 0 | 66.0723 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 641.1698 | 0 | 0 | 1106.7376 | 0 | 1106.7376 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5294 | 14.8412 | 0 | 0 | 25.6177 | 25.6177 | 0
ID_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 4729.1205 | 2656.3097 | 8858.0706 | 1597.6758 | 13417.6985 | 0 | 5646.0475 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41909.1213 | 0 | 41910.2327 | -1.1114 | -1.1114 | 366.5068 | 205.864 | 686.5005 | 123.8199 | 1039.8716 | 0 | 437.5687 | 0 | 0 | 0 | 0 | 387.8254 | 0 | 0 | 3247.9569 | 0 | 3248.043 | -0.086136 | -0.086136 | 16.1358 | 9.0633 | 30.2237 | 5.4513 | 45.7812 | 0 | 19.2643 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.9939 | 0 | 142.9977 | -0.0037922 | -0.0037922 | 5.4932 | 0.99078 | 8.3208 | 3.5013 | 0 | 0 | 1.6473 | 2.9327 | 3.1033 | 0 | 0 | 25.9901 | 25.9894 | -0.00068924
ID_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 12302.6662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12302.6662 | 0 | 12302.6662 | 0 | 0 | 67.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4555 | 0 | 67.4555 | 0 | 0 | 12.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3027 | 0 | 12.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.236 | 0 | 0 | 0 | 2.236 | 2.236 | 0
ID_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Electricity | 4806.9204 | 2384.0102 | 7160.3663 | 1597.6758 | 13417.6985 | 0 | 5095.8913 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39466.7612 | 0 | 39466.4833 | 0.27786 | 0.27786 | 372.5363 | 184.7608 | 554.9284 | 123.8199 | 1039.8716 | 0 | 394.9316 | 0 | 0 | 0 | 0 | 387.8254 | 0 | 0 | 3058.674 | 0 | 3058.6525 | 0.021534 | 0.021534 | 16.4012 | 8.1342 | 24.4312 | 5.4513 | 45.7812 | 0 | 17.3872 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.6606 | 0 | 134.6596 | 0.00094805 | 0.00094805 | 4.4404 | 0.99078 | 8.3208 | 3.1602 | 0 | 0 | 1.4784 | 2.981 | 3.1033 | 0 | 0 | 24.4747 | 24.4748 | 0.00017231
ID_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | ID-IDAHOFALLS-ID | Zone6B | Zone6B(ID-IDAHOFALLS-ID) |  |  | ID | 0.0775 | 0.005483 |  |  |  | Natural Gas | 13449.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13449.5249 | 0 | 13449.5249 | 0 | 0 | 73.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7437 | 0 | 73.7437 | 0 | 0 | 13.4495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4495 | 0 | 13.4495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4445 | 0 | 0 | 0 | 2.4445 | 2.4445 | 0
IL_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 783350.1905 | 880463.8746 | 95310.3943 | 4077910.5986 | 543457.0788 | 594188.1493 | 107513.8592 | 273021.9622 | 336581.6751 | 14570.8037 | 0 | 0 | 0 | 7706368.5864 | 0 | 7706371.9207 | -3.3343 | 543453.7446 | 0 | 70109.842 | 78801.5168 | 8530.2803 | 364972.9986 | 48639.4086 | 53179.8394 | 9622.4904 | 24435.4656 | 30124.0599 | 1304.0869 | 0 | 0 | 0 | 689719.9885 | 0 | 689720.2869 | -0.29842 | 48639.1101 | 0 | 2672.7908 | 3004.1427 | 325.1991 | 13913.831 | 1854.2756 | 2027.37 | 366.8373 | 931.5509 | 1148.4167 | 49.7156 | 0 | 0 | 0 | 26294.1296 | 0 | 26294.141 | -0.011377 | 1854.2642 | 6.0253 | 0.65224 | 27.9065 | 4.0662 | 0.73575 | 0.099713 | 5.3607 | 0 | 0 | 2.3033 | 0 | 52.7372 | 52.7372 | -2.2818e-05
IL_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 847016.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537526.0451 | 0 | 0 | 1384542.8144 | 0 | 1384542.8144 | 0 | 0 | 5913.8711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3753.0068 | 0 | 0 | 9666.8779 | 0 | 9666.8779 | 0 | 0 | 847.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.526 | 0 | 0 | 1384.5428 | 0 | 1384.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6988 | 1.0781 | 0 | 0 | 2.7769 | 2.7769 | 0
IL_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 734427.9669 | 716934.1111 | 95310.3943 | 4077910.5986 | 543387.6147 | 569922.9265 | 103576.6302 | 246383.8434 | 336462.1967 | 12917.5565 | 0 | 0 | 0 | 7437233.839 | 0 | 7437232.1719 | 1.6671 | 543389.2818 | 0 | 65731.303 | 64165.6029 | 8530.2803 | 364972.9986 | 48633.1915 | 51008.1019 | 9270.1084 | 22051.354 | 30113.3666 | 1156.1213 | 0 | 0 | 0 | 665632.4286 | 0 | 665632.2794 | 0.14921 | 48633.3407 | 0 | 2505.8682 | 2446.1792 | 325.1991 | 13913.831 | 1854.0385 | 1944.577 | 353.4035 | 840.6617 | 1148.009 | 44.0747 | 0 | 0 | 0 | 25375.8419 | 0 | 25375.8362 | 0.0056883 | 1854.0442 | 4.9062 | 0.65224 | 27.9065 | 3.9002 | 0.70881 | 0.088399 | 5.0259 | 0 | 0 | 2.3025 | 0 | 50.8954 | 50.8954 | 1.1409e-05
IL_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 787143.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537488.1324 | 0 | 0 | 1324631.2942 | 0 | 1324631.2942 | 0 | 0 | 5495.8336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3752.7421 | 0 | 0 | 9248.5757 | 0 | 9248.5757 | 0 | 0 | 787.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.4881 | 0 | 0 | 1324.6313 | 0 | 1324.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5787 | 1.078 | 0 | 0 | 2.6568 | 2.6568 | 0
IL_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 36046.3456 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 22439.7045 | 0 | 0 | 0 | 0 | 107883.4086 | 0 | 0 | 343958.7696 | 0 | 343959.0475 | -0.27786 | -0.27786 | 0 | 3226.1479 | 2539.5377 | 645.3291 | 12709.3766 | 0 | 2008.3536 | 0 | 0 | 0 | 0 | 9655.5651 | 0 | 0 | 30784.3099 | 0 | 30784.3347 | -0.024868 | -0.024868 | 0 | 122.9901 | 96.8146 | 24.6018 | 484.5184 | 0 | 76.5643 | 0 | 0 | 0 | 0 | 368.0982 | 0 | 0 | 1173.5873 | 0 | 1173.5883 | -0.00094805 | -0.00094805 | 2.8693 | 0.72914 | 14.3599 | 2.2692 | 0 | 0 | 3.6451 | 0 | 10.9095 | 0 | 0 | 34.7823 | 34.7822 | -2.8098e-05
IL_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 93615.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93615.8969 | 0 | 93615.8969 | 0 | 0 | 653.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.6262 | 0 | 653.6262 | 0 | 0 | 93.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6159 | 0 | 93.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7745 | 0 | 0 | 0 | 2.7745 | 2.7745 | 0
IL_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 35265.5683 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21981.241 | 0 | 0 | 0 | 0 | 107911.1942 | 0 | 0 | 337554.1734 | 0 | 337553.6177 | 0.55571 | 0.55571 | 0 | 3156.2684 | 2074.7516 | 645.3291 | 12709.3766 | 0 | 1967.3211 | 0 | 0 | 0 | 0 | 9658.0519 | 0 | 0 | 30211.0985 | 0 | 30211.0488 | 0.049736 | 0.049736 | 0 | 120.3261 | 79.0956 | 24.6018 | 484.5184 | 0 | 75 | 0 | 0 | 0 | 0 | 368.193 | 0 | 0 | 1151.7348 | 0 | 1151.7329 | 0.0018961 | 0.0018961 | 2.3442 | 0.72914 | 14.3599 | 2.2228 | 0 | 0 | 3.5662 | 0 | 10.9123 | 0 | 0 | 34.1345 | 34.1346 | 5.6196e-05
IL_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 106724.2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106724.2077 | 0 | 106724.2077 | 0 | 0 | 745.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745.1484 | 0 | 745.1484 | 0 | 0 | 106.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7242 | 0 | 106.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.163 | 0 | 0 | 0 | 3.163 | 3.163 | 0
IL_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 133332.3008 | 97780.5401 | 7115.9093 | 317887.4784 | 4818.0346 | 97747.1973 | 683.5274 | 0 | 0 | 18913.7034 | 7179.8163 | 17624.4485 | 0 | 703082.9562 | 0 | 703084.3455 | -1.3893 | 4816.6453 | 0 | 11933.2409 | 8751.3583 | 636.8739 | 28450.9293 | 431.2141 | 8748.3742 | 61.1757 | 0 | 0 | 1692.7765 | 642.5936 | 1577.3881 | 0 | 62925.9246 | 0 | 62926.0489 | -0.12434 | 431.0898 | 0 | 454.9298 | 333.6272 | 24.2795 | 1084.6321 | 16.4391 | 333.5134 | 2.3322 | 0 | 0 | 64.5336 | 24.4975 | 60.1346 | 0 | 2398.919 | 0 | 2398.9238 | -0.0047402 | 16.4344 | 4.511 | 0.32828 | 14.6653 | 4.5094 | 0.031534 | 0.87256 | 6.1511 | 0 | 0.33123 | 0 | 0.81308 | 32.4359 | 32.4358 | -6.4093e-05
IL_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 357592.443 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113321.0149 | 0 | 0 | 813103.8727 | 0 | 813103.8727 | 0 | 0 | 2496.7104 | 0 | 0 | 0 | 2389.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 791.2073 | 0 | 0 | 5677.0912 | 0 | 5677.0912 | 0 | 0 | 357.5924 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.321 | 0 | 0 | 813.1039 | 0 | 813.1039 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.835 | 1.5322 | 0 | 0 | 10.994 | 10.994 | 0
IL_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 126722.0907 | 79517.0213 | 7115.9093 | 312483.1662 | 4743.0133 | 82526.209 | 439.0135 | 0 | 0 | 22989.8607 | 7179.8163 | 12489.6572 | 0 | 656205.7577 | 0 | 656210.4812 | -4.7236 | 4738.2898 | 0 | 11341.6271 | 7116.7734 | 636.8739 | 27967.2434 | 424.4997 | 7386.0957 | 39.2917 | 0 | 0 | 2057.5925 | 642.5936 | 1117.8243 | 0 | 58730.4153 | 0 | 58730.8381 | -0.42276 | 424.0769 | 0 | 432.3758 | 271.3121 | 24.2795 | 1066.1926 | 16.1832 | 281.5794 | 1.4979 | 0 | 0 | 78.4414 | 24.4975 | 42.6147 | 0 | 2238.974 | 0 | 2238.9902 | -0.016117 | 16.167 | 3.6684 | 0.32828 | 14.416 | 3.8072 | 0.020253 | 1.0606 | 5.8462 | 0 | 0.33123 | 0 | 0.57619 | 30.2734 | 30.2732 | -0.00021792
IL_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 337536.6328 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113093.5388 | 0 | 0 | 792820.5864 | 0 | 792820.5864 | 0 | 0 | 2356.6808 | 0 | 0 | 0 | 2389.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 789.6191 | 0 | 0 | 5535.4733 | 0 | 5535.4733 | 0 | 0 | 337.5366 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0935 | 0 | 0 | 792.8206 | 0 | 792.8206 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.5638 | 1.5291 | 0 | 0 | 10.7197 | 10.7197 | 0
IL_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 50978.3629 | 84223.9133 | 10722.4888 | 53987.5506 | 0 | 39950.2318 | 0 | 0 | 0 | 5709.9545 | 0 | 0 | 0 | 245572.502 | 0 | 245570.0012 | 2.5007 | 2.5007 | 0 | 4562.5635 | 7538.0402 | 959.6628 | 4831.8858 | 0 | 3575.5457 | 0 | 0 | 0 | 511.0409 | 0 | 0 | 0 | 21978.7389 | 0 | 21978.5151 | 0.22381 | 0.22381 | 0 | 173.9382 | 287.372 | 36.5851 | 184.2055 | 0 | 136.3102 | 0 | 0 | 0 | 19.4824 | 0 | 0 | 0 | 837.8934 | 0 | 837.8848 | 0.0085324 | 0.0085324 | 11.6383 | 1.4817 | 7.4601 | 5.5204 | 0 | 0.78902 | 7.0443 | 0 | 0 | 0 | 0 | 33.9335 | 33.9338 | 0.00034555
IL_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 165687.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88706.2043 | 0 | 0 | 254394.115 | 0 | 254394.115 | 0 | 0 | 1156.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619.3467 | 0 | 0 | 1776.1797 | 0 | 1776.1797 | 0 | 0 | 165.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7062 | 0 | 0 | 254.3941 | 0 | 254.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7102 | 3.5925 | 0 | 0 | 10.3027 | 10.3027 | 0
IL_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 47644.0829 | 66632.8076 | 10722.4888 | 53987.5506 | 0 | 38088.5921 | 0 | 0 | 0 | 5801.6472 | 0 | 0 | 0 | 222877.1693 | 0 | 222875.5022 | 1.6671 | 1.6671 | 0 | 4264.1454 | 5963.6363 | 959.6628 | 4831.8858 | 0 | 3408.929 | 0 | 0 | 0 | 519.2474 | 0 | 0 | 0 | 19947.5067 | 0 | 19947.3574 | 0.14921 | 0.14921 | 0 | 162.5616 | 227.3511 | 36.5851 | 184.2055 | 0 | 129.9583 | 0 | 0 | 0 | 19.7952 | 0 | 0 | 0 | 760.4569 | 0 | 760.4512 | 0.0056883 | 0.0056883 | 9.2075 | 1.4817 | 7.4601 | 5.2632 | 0 | 0.80169 | 6.5836 | 0 | 0 | 0 | 0 | 30.7975 | 30.7977 | 0.00023037
IL_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 179383.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88715.6824 | 0 | 0 | 268099.5506 | 0 | 268099.5506 | 0 | 0 | 1252.4582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619.4129 | 0 | 0 | 1871.8711 | 0 | 1871.8711 | 0 | 0 | 179.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7157 | 0 | 0 | 268.0996 | 0 | 268.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2649 | 3.5929 | 0 | 0 | 10.8577 | 10.8577 | 0
IL_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 26432.5048 | 84098.8778 | 79216.9361 | 12314.6075 | 154949.5496 | 0 | 46288.1424 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 403372.861 | 0 | 403371.7496 | 1.1114 | 1.1114 | 2365.7092 | 7526.8496 | 7089.9158 | 1102.1574 | 13867.9847 | 0 | 4142.7887 | 6.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 36101.8711 | 0 | 36101.7716 | 0.099473 | 0.099473 | 90.1877 | 286.9454 | 270.2882 | 42.0174 | 528.6879 | 0 | 157.9351 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.3082 | 0 | 1376.3044 | 0.0037922 | 0.0037922 | 6.2564 | 0.97258 | 12.2376 | 3.6557 | 0.0057056 | 0 | 6.6419 | 2.0876 | 0 | 0 | 0 | 31.8574 | 31.8575 | 8.7778e-05
IL_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 60603.4267 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 557553.4208 | 0 | 0 | 1017652.2854 | 0 | 1017652.2854 | 0 | 0 | 423.1331 | 0 | 0 | 0 | 2789.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 3892.838 | 0 | 0 | 7105.2483 | 0 | 7105.2483 | 0 | 0 | 60.6034 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 557.5534 | 0 | 0 | 1017.6523 | 0 | 1017.6523 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4028 | 12.9057 | 0 | 0 | 23.5557 | 23.5557 | 0
IL_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 29914.0489 | 79008.5436 | 50811.6489 | 12314.6075 | 154949.5496 | 0 | 43904.1321 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 370974.7735 | 0 | 370972.5506 | 2.2229 | 2.2229 | 2677.3074 | 7071.2647 | 4547.6426 | 1102.1574 | 13867.9847 | 0 | 3929.4198 | 6.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 33202.2422 | 0 | 33202.0433 | 0.19895 | 0.19895 | 102.0667 | 269.5772 | 173.3693 | 42.0174 | 528.6879 | 0 | 149.8009 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.7659 | 0 | 1265.7583 | 0.0075844 | 0.0075844 | 4.013 | 0.97258 | 12.2376 | 3.4675 | 0.0057056 | 0 | 6.2399 | 2.3625 | 0 | 0 | 0 | 29.2986 | 29.2988 | 0.00017556
IL_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 59845.173 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 557629.2462 | 0 | 0 | 1016969.8571 | 0 | 1016969.8571 | 0 | 0 | 417.839 | 0 | 0 | 0 | 2789.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 3893.3674 | 0 | 0 | 7100.4835 | 0 | 7100.4835 | 0 | 0 | 59.8452 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6292 | 0 | 0 | 1016.9699 | 0 | 1016.9699 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3852 | 12.9075 | 0 | 0 | 23.5399 | 23.5399 | 0
IL_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 2792.4595 | 5498.7835 | 8838.6206 | 1578.2259 | 13417.6985 | 0 | 5182.0269 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42312.0134 | 0 | 42310.0684 | 1.945 | 1.945 | 249.9251 | 492.1411 | 791.0565 | 141.2512 | 1200.884 | 0 | 463.7914 | 0 | 0 | 0 | 0 | 447.8758 | 0 | 0 | 3786.9252 | 0 | 3786.7511 | 0.17408 | 0.17408 | 9.5279 | 18.7618 | 30.1574 | 5.3849 | 45.7812 | 0 | 17.6811 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.3686 | 0 | 144.362 | 0.0066363 | 0.0066363 | 5.4812 | 0.97872 | 8.3208 | 3.2136 | 0 | 0 | 3.41 | 1.7317 | 3.1033 | 0 | 0 | 26.2381 | 26.2393 | 0.0012062
IL_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 5592.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5592.121 | 0 | 5592.121 | 0 | 0 | 39.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.0442 | 0 | 39.0442 | 0 | 0 | 5.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5921 | 0 | 5.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0164 | 0 | 0 | 0 | 1.0164 | 1.0164 | 0
IL_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 2845.2523 | 5240.3768 | 7118.6878 | 1578.2259 | 13417.6985 | 0 | 4768.0204 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39972.4603 | 0 | 39975.2389 | -2.7786 | -2.7786 | 254.6501 | 469.0137 | 637.1226 | 141.2512 | 1200.884 | 0 | 426.7378 | 0 | 0 | 0 | 0 | 447.8758 | 0 | 0 | 3577.5352 | 0 | 3577.7839 | -0.24868 | -0.24868 | 9.708 | 17.8802 | 24.289 | 5.3849 | 45.7812 | 0 | 16.2685 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.386 | 0 | 136.3955 | -0.0094805 | -0.0094805 | 4.4146 | 0.97872 | 8.3208 | 2.9568 | 0 | 0 | 3.2498 | 1.7644 | 3.1033 | 0 | 0 | 24.7902 | 24.7884 | -0.0017231
IL_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | IL-STLOUIS-MO | Zone4A | Zone4A(IL-STLOUIS-MO) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 5762.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5762.7281 | 0 | 5762.7281 | 0 | 0 | 40.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.2354 | 0 | 40.2354 | 0 | 0 | 5.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7627 | 0 | 5.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 0 | 0 | 0 | 1.0474 | 1.0474 | 0
IL_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 660809.8427 | 880480.546 | 95593.8081 | 4077910.5986 | 543457.0788 | 593279.558 | 97008.0986 | 218142.4917 | 365789.968 | 12347.9503 | 0 | 0 | 0 | 7544819.9409 | 0 | 7544820.7745 | -0.83357 | 543456.2453 | 0 | 59142.4809 | 78803.0089 | 8555.6458 | 364972.9986 | 48639.4086 | 53098.5204 | 8682.2248 | 19523.753 | 32738.2021 | 1105.1416 | 0 | 0 | 0 | 675261.3847 | 0 | 675261.4593 | -0.074605 | 48639.334 | 0 | 2254.6832 | 3004.1996 | 326.1661 | 13913.831 | 1854.2756 | 2024.2699 | 330.9916 | 744.3022 | 1248.0754 | 42.1312 | 0 | 0 | 0 | 25742.9256 | 0 | 25742.9285 | -0.0028441 | 1854.2727 | 6.0254 | 0.65418 | 27.9065 | 4.06 | 0.66386 | 0.084501 | 4.5221 | 0 | 0 | 2.5032 | 0 | 51.6317 | 51.6317 | -5.7044e-06
IL_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 1244171.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572832.2328 | 0 | 0 | 1817003.3317 | 0 | 1817003.3317 | 0 | 0 | 8686.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3999.5146 | 0 | 0 | 12686.3173 | 0 | 12686.3173 | 0 | 0 | 1244.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.8322 | 0 | 0 | 1817.0033 | 0 | 1817.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4954 | 1.1489 | 0 | 0 | 3.6443 | 3.6443 | 0
IL_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 618300.551 | 717036.9181 | 95593.8081 | 4077910.5986 | 543387.6147 | 576847.1147 | 93001.4054 | 196375.2003 | 365701.0539 | 11197.6237 | 0 | 0 | 0 | 7295351.8885 | 0 | 7295352.1664 | -0.27786 | 543387.3368 | 0 | 55337.8993 | 64174.8042 | 8555.6458 | 364972.9986 | 48633.1915 | 51627.8168 | 8323.6258 | 17575.5804 | 32730.2443 | 1002.1873 | 0 | 0 | 0 | 652933.994 | 0 | 652934.0189 | -0.024868 | 48633.1666 | 0 | 2109.6415 | 2446.53 | 326.1661 | 13913.831 | 1854.0385 | 1968.2024 | 317.3208 | 670.0322 | 1247.772 | 38.2063 | 0 | 0 | 0 | 24891.7406 | 0 | 24891.7416 | -0.00094805 | 1854.0376 | 4.9069 | 0.65418 | 27.9065 | 3.9476 | 0.63644 | 0.076629 | 4.2312 | 0 | 0 | 2.5026 | 0 | 49.9245 | 49.9245 | -1.9015e-06
IL_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 1190202.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572851.1892 | 0 | 0 | 1763053.5813 | 0 | 1763053.5813 | 0 | 0 | 8309.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3999.647 | 0 | 0 | 12309.6401 | 0 | 12309.6401 | 0 | 0 | 1190.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.8512 | 0 | 0 | 1763.0536 | 0 | 1763.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3871 | 1.1489 | 0 | 0 | 3.5361 | 3.5361 | 0
IL_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 28533.1013 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21264.3708 | 0 | 0 | 0 | 0 | 114843.7181 | 0 | 0 | 342224.944 | 0 | 342224.6661 | 0.27786 | 0.27786 | 0 | 2553.7126 | 2539.5377 | 644.8317 | 12709.3766 | 0 | 1903.1612 | 0 | 0 | 0 | 0 | 10278.5128 | 0 | 0 | 30629.1325 | 0 | 30629.1076 | 0.024868 | 0.024868 | 0 | 97.3549 | 96.8146 | 24.5829 | 484.5184 | 0 | 72.554 | 0 | 0 | 0 | 0 | 391.8468 | 0 | 0 | 1167.6715 | 0 | 1167.6706 | 0.00094805 | 0.00094805 | 2.8693 | 0.72858 | 14.3599 | 2.1503 | 0 | 0 | 2.8854 | 0 | 11.6134 | 0 | 0 | 34.6069 | 34.6069 | 2.8098e-05
IL_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 154607.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154607.9286 | 0 | 154607.9286 | 0 | 0 | 1079.4726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.4726 | 0 | 1079.4726 | 0 | 0 | 154.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.6079 | 0 | 154.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5822 | 0 | 0 | 0 | 4.5822 | 4.5822 | 0
IL_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 27638.4028 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20775.3431 | 0 | 0 | 0 | 0 | 114874.2823 | 0 | 0 | 335678.6409 | 0 | 335679.4745 | -0.83357 | -0.83357 | 0 | 2473.637 | 2074.7516 | 644.8317 | 12709.3766 | 0 | 1859.3932 | 0 | 0 | 0 | 0 | 10281.2483 | 0 | 0 | 30043.2384 | 0 | 30043.313 | -0.074605 | -0.074605 | 0 | 94.3022 | 79.0956 | 24.5829 | 484.5184 | 0 | 70.8855 | 0 | 0 | 0 | 0 | 391.9511 | 0 | 0 | 1145.3355 | 0 | 1145.3384 | -0.0028441 | -0.0028441 | 2.3442 | 0.72858 | 14.3599 | 2.1009 | 0 | 0 | 2.7949 | 0 | 11.6165 | 0 | 0 | 33.945 | 33.9449 | -8.4293e-05
IL_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 172720.7138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172720.7138 | 0 | 172720.7138 | 0 | 0 | 1205.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.936 | 0 | 1205.936 | 0 | 0 | 172.7207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.7207 | 0 | 172.7207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.119 | 0 | 0 | 0 | 5.119 | 5.119 | 0
IL_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 106035.6617 | 97463.7835 | 7127.0235 | 317887.4784 | 4818.0346 | 96738.5776 | 1036.4054 | 0 | 0 | 21214.3566 | 7179.8163 | 17627.227 | 0 | 677128.3648 | 0 | 677131.1434 | -2.7786 | 4815.2561 | 0 | 9490.1917 | 8723.0086 | 637.8686 | 28450.9293 | 431.2141 | 8658.1027 | 92.7583 | 0 | 0 | 1898.6849 | 642.5936 | 1577.6368 | 0 | 60602.9886 | 0 | 60603.2373 | -0.24868 | 430.9654 | 0 | 361.7937 | 332.5464 | 24.3174 | 1084.6321 | 16.4391 | 330.072 | 3.5362 | 0 | 0 | 72.3834 | 24.4975 | 60.1441 | 0 | 2310.362 | 0 | 2310.3715 | -0.0094805 | 16.4297 | 4.4964 | 0.3288 | 14.6653 | 4.4629 | 0.047813 | 0.9787 | 4.8918 | 0 | 0.33123 | 0 | 0.81321 | 31.2385 | 31.2384 | -0.00012819
IL_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 555127.009 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120116.8636 | 0 | 0 | 1017434.2875 | 0 | 1017434.2875 | 0 | 0 | 3875.8968 | 0 | 0 | 0 | 2389.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 838.6559 | 0 | 0 | 7103.7262 | 0 | 7103.7262 | 0 | 0 | 555.127 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1169 | 0 | 0 | 1017.4343 | 0 | 1017.4343 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.5059 | 1.6241 | 0 | 0 | 13.7567 | 13.7567 | 0
IL_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 101109.263 | 79397.5429 | 7127.0235 | 312483.1662 | 4743.0133 | 83376.4504 | 680.7488 | 0 | 0 | 22739.7897 | 7179.8163 | 12484.1001 | 0 | 631320.9145 | 0 | 631322.5816 | -1.6671 | 4741.3462 | 0 | 9049.279 | 7106.0801 | 637.8686 | 27967.2434 | 424.4997 | 7462.1923 | 60.927 | 0 | 0 | 2035.2112 | 642.5936 | 1117.327 | 0 | 56503.2218 | 0 | 56503.3711 | -0.14921 | 424.3505 | 0 | 344.9848 | 270.9044 | 24.3174 | 1066.1926 | 16.1832 | 284.4804 | 2.3227 | 0 | 0 | 77.5882 | 24.4975 | 42.5957 | 0 | 2154.067 | 0 | 2154.0726 | -0.0056883 | 16.1775 | 3.6629 | 0.3288 | 14.416 | 3.8465 | 0.031405 | 1.0491 | 4.6645 | 0 | 0.33123 | 0 | 0.57594 | 29.1252 | 29.1251 | -7.6911e-05
IL_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 532824.8722 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119851.4748 | 0 | 0 | 994866.7618 | 0 | 994866.7618 | 0 | 0 | 3720.1833 | 0 | 0 | 0 | 2389.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 836.803 | 0 | 0 | 6946.1597 | 0 | 6946.1597 | 0 | 0 | 532.8249 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8515 | 0 | 0 | 994.8668 | 0 | 994.8668 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.2043 | 1.6205 | 0 | 0 | 13.4516 | 13.4516 | 0
IL_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 40494.8308 | 83932.1638 | 10739.1602 | 53987.5506 | 0 | 42186.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231340.6834 | 0 | 231338.1827 | 2.5007 | 2.5007 | 0 | 3624.2874 | 7511.9287 | 961.1548 | 4831.8858 | 0 | 3775.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20704.9912 | 0 | 20704.7674 | 0.22381 | 0.22381 | 0 | 138.1684 | 286.3765 | 36.642 | 184.2055 | 0 | 143.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789.3344 | 0 | 789.3259 | 0.0085324 | 0.0085324 | 11.5979 | 1.484 | 7.4601 | 5.8295 | 0 | 0 | 5.5957 | 0 | 0 | 0 | 0 | 31.9669 | 31.9672 | 0.00034555
IL_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 507195.8973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90829.3146 | 0 | 0 | 598025.2119 | 0 | 598025.2119 | 0 | 0 | 3541.2418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634.1703 | 0 | 0 | 4175.412 | 0 | 4175.412 | 0 | 0 | 507.1959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8293 | 0 | 0 | 598.0252 | 0 | 598.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5409 | 3.6785 | 0 | 0 | 24.2194 | 24.2194 | 0
IL_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 0 | 37866.3067 | 66477.2079 | 10739.1602 | 53987.5506 | 0 | 40447.5952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209517.8207 | 0 | 209518.0985 | -0.27786 | -0.27786 | 0 | 3389.0345 | 5949.7101 | 961.1548 | 4831.8858 | 0 | 3620.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18751.845 | 0 | 18751.8698 | -0.024868 | -0.024868 | 0 | 129.1998 | 226.8202 | 36.642 | 184.2055 | 0 | 138.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.8748 | 0 | 714.8758 | -0.00094805 | -0.00094805 | 9.186 | 1.484 | 7.4601 | 5.5891 | 0 | 0 | 5.2325 | 0 | 0 | 0 | 0 | 28.9517 | 28.9517 | -3.8395e-05
IL_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 534786.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90838.7928 | 0 | 0 | 625625.6464 | 0 | 625625.6464 | 0 | 0 | 3733.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634.2365 | 0 | 0 | 4368.1183 | 0 | 4368.1183 | 0 | 0 | 534.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8388 | 0 | 0 | 625.6256 | 0 | 625.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6583 | 3.6789 | 0 | 0 | 25.3372 | 25.3372 | 0
IL_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 40625.4235 | 69269.6674 | 79091.9006 | 12306.2718 | 154949.5496 | 0 | 45868.5788 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 402183.6344 | 0 | 402183.9123 | -0.27786 | -0.27786 | 3635.9754 | 6199.6352 | 7078.7251 | 1101.4113 | 13867.9847 | 0 | 4105.2378 | 6.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 35995.4353 | 0 | 35995.4602 | -0.024868 | -0.024868 | 138.6139 | 236.3481 | 269.8616 | 41.989 | 528.6879 | 0 | 156.5036 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.2506 | 0 | 1372.2515 | -0.00094805 | -0.00094805 | 6.2465 | 0.97192 | 12.2376 | 3.6226 | 0.0057056 | 0 | 5.4708 | 3.2085 | 0 | 0 | 0 | 31.7636 | 31.7636 | -2.1945e-05
IL_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 90260.6243 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598262.1661 | 0 | 0 | 1088018.2284 | 0 | 1088018.2284 | 0 | 0 | 630.1997 | 0 | 0 | 0 | 2789.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 4177.0664 | 0 | 0 | 7596.5433 | 0 | 7596.5433 | 0 | 0 | 90.2606 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.2622 | 0 | 0 | 1088.0182 | 0 | 1088.0182 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.0893 | 13.848 | 0 | 0 | 25.1844 | 25.1844 | 0
IL_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 45157.2657 | 64726.7109 | 50736.6276 | 12306.2718 | 154949.5496 | 0 | 43454.0043 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371402.6727 | 0 | 371402.9506 | -0.27786 | -0.27786 | 4041.5753 | 5793.0406 | 4540.9282 | 1101.4113 | 13867.9847 | 0 | 3889.1334 | 6.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 33240.5392 | 0 | 33240.5641 | -0.024868 | -0.024868 | 154.0766 | 220.8475 | 173.1134 | 41.989 | 528.6879 | 0 | 148.2651 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.2259 | 0 | 1267.2269 | -0.00094805 | -0.00094805 | 4.0071 | 0.97192 | 12.2376 | 3.4319 | 0.0057056 | 0 | 5.112 | 3.5664 | 0 | 0 | 0 | 29.3326 | 29.3326 | -2.1945e-05
IL_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 87853.1689 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598347.4697 | 0 | 0 | 1085696.0764 | 0 | 1085696.0764 | 0 | 0 | 613.3908 | 0 | 0 | 0 | 2789.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 4177.662 | 0 | 0 | 7580.33 | 0 | 7580.33 | 0 | 0 | 87.8532 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.3475 | 0 | 0 | 1085.6961 | 0 | 1085.6961 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.0335 | 13.85 | 0 | 0 | 25.1307 | 25.1307 | 0
IL_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 3789.965 | 4217.8642 | 8805.2778 | 1581.0044 | 13417.6985 | 0 | 5048.6557 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41864.6642 | 0 | 41862.9971 | 1.6671 | 1.6671 | 339.2019 | 377.4988 | 788.0724 | 141.4999 | 1200.884 | 0 | 451.8547 | 0 | 0 | 0 | 0 | 447.8758 | 0 | 0 | 3746.8874 | 0 | 3746.7382 | 0.14921 | 0.14921 | 12.9314 | 14.3914 | 30.0436 | 5.3944 | 45.7812 | 0 | 17.226 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.8422 | 0 | 142.8365 | 0.0056883 | 0.0056883 | 5.4605 | 0.98044 | 8.3208 | 3.1309 | 0 | 0 | 2.6157 | 2.3503 | 3.1033 | 0 | 0 | 25.9608 | 25.9619 | 0.0010339
IL_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 13591.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13591.6975 | 0 | 13591.6975 | 0 | 0 | 94.8972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8972 | 0 | 94.8972 | 0 | 0 | 13.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5917 | 0 | 13.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4703 | 0 | 0 | 0 | 2.4703 | 2.4703 | 0
IL_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Electricity | 3842.7577 | 4001.136 | 7102.0164 | 1581.0044 | 13417.6985 | 0 | 4640.2064 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39589.0181 | 0 | 39589.2959 | -0.27786 | -0.27786 | 343.9268 | 358.1017 | 635.6305 | 141.4999 | 1200.884 | 0 | 415.2985 | 0 | 0 | 0 | 0 | 447.8758 | 0 | 0 | 3543.2171 | 0 | 3543.242 | -0.024868 | -0.024868 | 13.1115 | 13.6519 | 24.2321 | 5.3944 | 45.7812 | 0 | 15.8324 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.0777 | 0 | 135.0787 | -0.00094805 | -0.00094805 | 4.4042 | 0.98044 | 8.3208 | 2.8776 | 0 | 0 | 2.4813 | 2.383 | 3.1033 | 0 | 0 | 24.5508 | 24.5507 | -0.00017231
IL_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | IL-PEORIA-IL | Zone5A | Zone5A(IL-PEORIA-IL) |  |  | IL | 0.0895 | 0.006982 |  |  |  | Natural Gas | 13838.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13838.13 | 0 | 13838.13 | 0 | 0 | 96.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6178 | 0 | 96.6178 | 0 | 0 | 13.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8381 | 0 | 13.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5151 | 0 | 0 | 0 | 2.5151 | 2.5151 | 0
IN_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 781674.7148 | 881633.6512 | 95263.1587 | 4077910.5986 | 543457.0788 | 592398.7524 | 109633.9056 | 277548.2473 | 311730.1747 | 14462.4396 | 0 | 0 | 0 | 7685712.7217 | 0 | 7685714.6667 | -1.945 | 543455.1338 | 0 | 85358.8789 | 96274.3947 | 10402.7369 | 445307.8374 | 59345.513 | 64689.9438 | 11972.0225 | 30308.2686 | 34040.9351 | 1579.2984 | 0 | 0 | 0 | 839279.8292 | 0 | 839280.0416 | -0.21239 | 59345.3006 | 0 | 2667.0741 | 3008.134 | 325.0379 | 13913.831 | 1854.2756 | 2021.2645 | 374.0709 | 946.9946 | 1063.6234 | 49.3458 | 0 | 0 | 0 | 26223.6518 | 0 | 26223.6584 | -0.0066363 | 1854.2689 | 6.0333 | 0.65192 | 27.9065 | 4.054 | 0.75026 | 0.098971 | 5.3493 | 0 | 0 | 2.1333 | 0 | 52.5958 | 52.5958 | -1.331e-05
IN_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 658704.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534521.4648 | 0 | 0 | 1193225.9287 | 0 | 1193225.9287 | 0 | 0 | 4372.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3548.1535 | 0 | 0 | 7920.6337 | 0 | 7920.6337 | 0 | 0 | 658.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534.5215 | 0 | 0 | 1193.2259 | 0 | 1193.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3211 | 1.0721 | 0 | 0 | 2.3932 | 2.3932 | 0
IN_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 735664.4291 | 717853.8167 | 95263.1587 | 4077910.5986 | 543387.6147 | 567133.2455 | 105454.9413 | 250379.4223 | 311535.675 | 12756.3996 | 0 | 0 | 0 | 7417339.3016 | 0 | 7417336.523 | 2.7786 | 543390.3932 | 0 | 80334.5557 | 78389.6368 | 10402.7369 | 445307.8374 | 59337.9275 | 61930.9504 | 11515.6796 | 27341.4329 | 34019.6957 | 1392.9988 | 0 | 0 | 0 | 809973.4517 | 0 | 809973.1483 | 0.30342 | 59338.2309 | 0 | 2510.087 | 2449.3172 | 325.0379 | 13913.831 | 1854.0385 | 1935.0586 | 359.8123 | 854.2946 | 1062.9597 | 43.5248 | 0 | 0 | 0 | 25307.9617 | 0 | 25307.9522 | 0.0094805 | 1854.048 | 4.9125 | 0.65192 | 27.9065 | 3.8811 | 0.72166 | 0.087296 | 5.0344 | 0 | 0 | 2.1319 | 0 | 50.7592 | 50.7593 | 1.9015e-05
IN_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 601257.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534530.943 | 0 | 0 | 1135788.2112 | 0 | 1135788.2112 | 0 | 0 | 3991.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3548.2164 | 0 | 0 | 7539.3621 | 0 | 7539.3621 | 0 | 0 | 601.2573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534.5309 | 0 | 0 | 1135.7882 | 0 | 1135.7882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2059 | 1.0721 | 0 | 0 | 2.278 | 2.278 | 0
IN_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 36582.6089 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 22250.762 | 0 | 0 | 0 | 0 | 107261.0096 | 0 | 0 | 343683.6915 | 0 | 343686.1922 | -2.5007 | -2.5007 | 0 | 3994.8209 | 3098.5197 | 787.3736 | 15506.8595 | 0 | 2429.7832 | 0 | 0 | 0 | 0 | 11712.9023 | 0 | 0 | 37530.2591 | 0 | 37530.5322 | -0.27308 | -0.27308 | 0 | 124.8199 | 96.8146 | 24.6018 | 484.5184 | 0 | 75.9196 | 0 | 0 | 0 | 0 | 365.9746 | 0 | 0 | 1172.6488 | 0 | 1172.6573 | -0.0085324 | -0.0085324 | 2.8693 | 0.72914 | 14.3599 | 2.2501 | 0 | 0 | 3.6994 | 0 | 10.8466 | 0 | 0 | 34.7547 | 34.7544 | -0.00025288
IN_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 71418.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71418.02 | 0 | 71418.02 | 0 | 0 | 474.0728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474.0728 | 0 | 474.0728 | 0 | 0 | 71.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.418 | 0 | 71.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1167 | 0 | 0 | 0 | 2.1167 | 2.1167 | 0
IN_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 35807.3888 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21736.7272 | 0 | 0 | 0 | 0 | 107291.5739 | 0 | 0 | 337231.8597 | 0 | 337234.3604 | -2.5007 | -2.5007 | 0 | 3910.1669 | 2531.4287 | 787.3736 | 15506.8595 | 0 | 2373.6506 | 0 | 0 | 0 | 0 | 11716.2399 | 0 | 0 | 36825.7191 | 0 | 36825.9922 | -0.27308 | -0.27308 | 0 | 122.1748 | 79.0956 | 24.6018 | 484.5184 | 0 | 74.1657 | 0 | 0 | 0 | 0 | 366.0789 | 0 | 0 | 1150.6351 | 0 | 1150.6436 | -0.0085324 | -0.0085324 | 2.3442 | 0.72914 | 14.3599 | 2.1981 | 0 | 0 | 3.621 | 0 | 10.8497 | 0 | 0 | 34.1022 | 34.102 | -0.00025288
IN_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 82355.8296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82355.8296 | 0 | 82355.8296 | 0 | 0 | 546.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.678 | 0 | 546.678 | 0 | 0 | 82.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3558 | 0 | 82.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4408 | 0 | 0 | 0 | 2.4408 | 2.4408 | 0
IN_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 142048.6645 | 98494.6318 | 7121.4664 | 317887.4784 | 4818.0346 | 95443.7655 | 633.5132 | 0 | 0 | 19411.0668 | 7179.8163 | 17649.4556 | 0 | 710687.8932 | 0 | 710686.226 | 1.6671 | 4819.7018 | 0 | 15511.7142 | 10755.6138 | 777.6641 | 34713.3126 | 526.1294 | 10422.4592 | 69.1796 | 0 | 0 | 2119.6885 | 784.0359 | 1927.3205 | 0 | 77607.1179 | 0 | 77606.9359 | 0.18205 | 526.3114 | 0 | 484.67 | 336.0637 | 24.2984 | 1084.6321 | 16.4391 | 325.6541 | 2.1615 | 0 | 0 | 66.2306 | 24.4975 | 60.2199 | 0 | 2424.8671 | 0 | 2424.8614 | 0.0056883 | 16.4448 | 4.5439 | 0.32854 | 14.6653 | 4.4032 | 0.029226 | 0.8955 | 6.5532 | 0 | 0.33123 | 0 | 0.81423 | 32.7866 | 32.7866 | 7.6911e-05
IN_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 287994.2319 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 112325.8069 | 0 | 0 | 742510.4536 | 0 | 742510.4536 | 0 | 0 | 1911.7057 | 0 | 0 | 0 | 2271.46 | 0 | 0 | 0 | 0 | 0 | 0 | 745.6187 | 0 | 0 | 4928.7844 | 0 | 4928.7844 | 0 | 0 | 287.9942 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 112.3258 | 0 | 0 | 742.5105 | 0 | 742.5105 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.894 | 1.5188 | 0 | 0 | 10.0395 | 10.0395 | 0
IN_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 135766.3252 | 80194.9916 | 7121.4664 | 312483.1662 | 4745.7919 | 84034.9707 | 369.5494 | 0 | 0 | 22953.7394 | 7179.8163 | 12500.7715 | 0 | 667350.5886 | 0 | 667351.1444 | -0.55571 | 4745.2362 | 0 | 14825.6827 | 8757.2931 | 777.6641 | 34123.1618 | 518.2405 | 9176.6188 | 40.3548 | 0 | 0 | 2506.5483 | 784.0359 | 1365.0842 | 0 | 72874.6843 | 0 | 72874.745 | -0.060684 | 518.1798 | 0 | 463.2347 | 273.6253 | 24.2984 | 1066.1926 | 16.1926 | 286.7273 | 1.2609 | 0 | 0 | 78.3182 | 24.4975 | 42.6526 | 0 | 2277.0002 | 0 | 2277.0021 | -0.0018961 | 16.1907 | 3.6997 | 0.32854 | 14.416 | 3.8768 | 0.017049 | 1.0589 | 6.2634 | 0 | 0.33123 | 0 | 0.57671 | 30.7874 | 30.7873 | -2.5637e-05
IN_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 274658.445 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 112079.3744 | 0 | 0 | 728928.2343 | 0 | 728928.2343 | 0 | 0 | 1823.1828 | 0 | 0 | 0 | 2271.46 | 0 | 0 | 0 | 0 | 0 | 0 | 743.9829 | 0 | 0 | 4838.6256 | 0 | 4838.6256 | 0 | 0 | 274.6584 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0794 | 0 | 0 | 728.9282 | 0 | 728.9282 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7137 | 1.5154 | 0 | 0 | 9.8558 | 9.8558 | 0
IN_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 55062.8559 | 84176.6776 | 10753.0531 | 53987.5506 | 0 | 39936.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243916.4762 | 0 | 243914.5312 | 1.945 | 1.945 | 0 | 6012.8639 | 9192.0932 | 1174.2334 | 5895.4405 | 0 | 4361.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26635.6792 | 0 | 26635.4668 | 0.21239 | 0.21239 | 0 | 187.8745 | 287.2108 | 36.6894 | 184.2055 | 0 | 136.2628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832.243 | 0 | 832.2364 | 0.0066363 | 0.0066363 | 11.6317 | 1.4859 | 7.4601 | 5.5185 | 0 | 0 | 7.6087 | 0 | 0 | 0 | 0 | 33.7047 | 33.705 | 0.00026876
IN_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 300751.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88526.119 | 0 | 0 | 389277.9694 | 0 | 389277.9694 | 0 | 0 | 1996.3908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.6364 | 0 | 0 | 2584.0272 | 0 | 2584.0272 | 0 | 0 | 300.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5261 | 0 | 0 | 389.278 | 0 | 389.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1801 | 3.5852 | 0 | 0 | 15.7653 | 15.7653 | 0
IN_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 51817.4901 | 66613.3576 | 10753.0531 | 53987.5506 | 0 | 38252.5275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221423.9789 | 0 | 221420.6446 | 3.3343 | 3.3343 | 0 | 5658.4699 | 7274.1787 | 1174.2334 | 5895.4405 | 0 | 4177.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24179.4985 | 0 | 24179.1344 | 0.3641 | 0.3641 | 0 | 176.8013 | 227.2848 | 36.6894 | 184.2055 | 0 | 130.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.4986 | 0 | 755.4872 | 0.011377 | 0.011377 | 9.2048 | 1.4859 | 7.4601 | 5.2858 | 0 | 0 | 7.1603 | 0 | 0 | 0 | 0 | 30.5964 | 30.5969 | 0.00046074
IN_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 321916.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88535.5972 | 0 | 0 | 410452.2038 | 0 | 410452.2038 | 0 | 0 | 2136.8824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.6993 | 0 | 0 | 2724.5817 | 0 | 2724.5817 | 0 | 0 | 321.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5356 | 0 | 0 | 410.4522 | 0 | 410.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0373 | 3.5856 | 0 | 0 | 16.6229 | 16.6229 | 0
IN_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 21517.2204 | 85654.8751 | 79261.3932 | 12314.6075 | 154949.5496 | 0 | 46032.5142 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 399802.4028 | 0 | 399803.2364 | -0.83357 | -0.83357 | 2349.6805 | 9353.5124 | 8655.3441 | 1344.7551 | 16920.4908 | 0 | 5026.7506 | 7.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 43658.4224 | 0 | 43658.5134 | -0.091026 | -0.091026 | 73.4168 | 292.2544 | 270.4399 | 42.0174 | 528.6879 | 0 | 157.0629 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.1258 | 0 | 1364.1286 | -0.0028441 | -0.0028441 | 6.2599 | 0.97258 | 12.2376 | 3.6355 | 0.0057056 | 0 | 6.7648 | 1.6994 | 0 | 0 | 0 | 31.5756 | 31.5755 | -6.5834e-05
IN_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 51968.8127 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 554018.063 | 0 | 0 | 1005482.3136 | 0 | 1005482.3136 | 0 | 0 | 344.969 | 0 | 0 | 0 | 2651.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 3677.5719 | 0 | 0 | 6674.3916 | 0 | 6674.3916 | 0 | 0 | 51.9688 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 554.0181 | 0 | 0 | 1005.4823 | 0 | 1005.4823 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2029 | 12.8239 | 0 | 0 | 23.274 | 23.274 | 0
IN_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 24618.1008 | 80345.0342 | 50847.7703 | 12314.6075 | 154949.5496 | 0 | 43701.2968 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 366848.6019 | 0 | 366851.1027 | -2.5007 | -2.5007 | 2688.2966 | 8773.6777 | 5552.5765 | 1344.7551 | 16920.4908 | 0 | 4772.1816 | 7.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 40059.8673 | 0 | 40060.1404 | -0.27308 | -0.27308 | 83.997 | 274.1373 | 173.4926 | 42.0174 | 528.6879 | 0 | 149.1088 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.6874 | 0 | 1251.696 | -0.0085324 | -0.0085324 | 4.0158 | 0.97258 | 12.2376 | 3.4514 | 0.0057056 | 0 | 6.3455 | 1.9443 | 0 | 0 | 0 | 28.9731 | 28.9729 | -0.0001975
IN_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 51959.3345 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 554065.4538 | 0 | 0 | 1005520.2263 | 0 | 1005520.2263 | 0 | 0 | 344.9061 | 0 | 0 | 0 | 2651.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 3677.8865 | 0 | 0 | 6674.6433 | 0 | 6674.6433 | 0 | 0 | 51.9593 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 554.0655 | 0 | 0 | 1005.5202 | 0 | 1005.5202 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2027 | 12.825 | 0 | 0 | 23.2749 | 23.2749 | 0
IN_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 2509.0457 | 5651.6046 | 8846.9563 | 1575.4473 | 13417.6985 | 0 | 4998.6415 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42003.5925 | 0 | 42007.2047 | -3.6121 | -3.6121 | 273.9878 | 617.1552 | 966.0876 | 172.0388 | 1465.2127 | 0 | 545.8516 | 0 | 0 | 0 | 0 | 546.4585 | 0 | 0 | 4586.7923 | 0 | 4587.1868 | -0.39445 | -0.39445 | 8.5609 | 19.2833 | 30.1858 | 5.3754 | 45.7812 | 0 | 17.0554 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.3163 | 0 | 143.3286 | -0.012325 | -0.012325 | 5.4863 | 0.97699 | 8.3208 | 3.0998 | 0 | 0 | 3.5048 | 1.556 | 3.1033 | 0 | 0 | 26.0503 | 26.048 | -0.00224
IN_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 2777.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2777.1042 | 0 | 2777.1042 | 0 | 0 | 18.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4344 | 0 | 18.4344 | 0 | 0 | 2.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7771 | 0 | 2.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50474 | 0 | 0 | 0 | 0.50474 | 0.50474 | 0
IN_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 2561.8385 | 5382.0837 | 7129.8021 | 1575.4473 | 13417.6985 | 0 | 4609.6421 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39680.7108 | 0 | 39679.3215 | 1.3893 | 1.3893 | 279.7528 | 587.7235 | 778.5744 | 172.0388 | 1465.2127 | 0 | 503.3729 | 0 | 0 | 0 | 0 | 546.4585 | 0 | 0 | 4333.1336 | 0 | 4332.9819 | 0.15171 | 0.15171 | 8.741 | 18.3637 | 24.3269 | 5.3754 | 45.7812 | 0 | 15.7281 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.3906 | 0 | 135.3858 | 0.0047402 | 0.0047402 | 4.4215 | 0.97699 | 8.3208 | 2.8586 | 0 | 0 | 3.3376 | 1.5887 | 3.1033 | 0 | 0 | 24.6067 | 24.6075 | 0.00086155
IN_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | IN-EVANSVILLE-IN | Zone4A | Zone4A(IN-EVANSVILLE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 2938.2331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2938.2331 | 0 | 2938.2331 | 0 | 0 | 19.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.504 | 0 | 19.504 | 0 | 0 | 2.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9382 | 0 | 2.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53403 | 0 | 0 | 0 | 0.53403 | 0.53403 | 0
IN_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 602193.1999 | 880430.5318 | 96532.9637 | 4077910.5986 | 543457.0788 | 592829.4302 | 90722.9807 | 208912.0931 | 380310.7575 | 12817.5281 | 0 | 0 | 0 | 7486117.1626 | 0 | 7486119.3855 | -2.2229 | 543454.856 | 0 | 65759.4974 | 96143.0141 | 10541.3996 | 445307.8374 | 59345.513 | 64736.9738 | 9906.9495 | 22813.2006 | 41529.9347 | 1399.6741 | 0 | 0 | 0 | 817483.9942 | 0 | 817484.2369 | -0.24274 | 59345.2703 | 0 | 2054.6832 | 3004.029 | 329.3705 | 13913.831 | 1854.2756 | 2022.734 | 309.5468 | 712.8081 | 1297.6203 | 43.7334 | 0 | 0 | 0 | 25542.6318 | 0 | 25542.6393 | -0.0075844 | 1854.268 | 6.0251 | 0.66061 | 27.9065 | 4.0569 | 0.62085 | 0.087715 | 4.121 | 0 | 0 | 2.6026 | 0 | 51.23 | 51.2299 | -1.5212e-05
IN_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 1443127.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579182.6075 | 0 | 0 | 2022309.9981 | 0 | 2022309.9981 | 0 | 0 | 9579.4796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3844.6141 | 0 | 0 | 13424.0938 | 0 | 13424.0938 | 0 | 0 | 1443.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.1826 | 0 | 0 | 2022.31 | 0 | 2022.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8944 | 1.1616 | 0 | 0 | 4.0561 | 4.0561 | 0
IN_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 563707.2728 | 716603.4617 | 96532.9637 | 4077910.5986 | 543387.6147 | 574240.8191 | 86171.6885 | 187600.4867 | 380099.5864 | 11167.0595 | 0 | 0 | 0 | 7237421.5517 | 0 | 7237420.4403 | 1.1114 | 543388.7261 | 0 | 61556.8342 | 78253.098 | 10541.3996 | 445307.8374 | 59337.9275 | 62707.0974 | 9409.9484 | 20485.9731 | 41506.8748 | 1219.4429 | 0 | 0 | 0 | 790326.4334 | 0 | 790326.3121 | 0.12137 | 59338.0489 | 0 | 1923.3692 | 2445.051 | 329.3705 | 13913.831 | 1854.0385 | 1959.3097 | 294.0178 | 640.0929 | 1296.8998 | 38.102 | 0 | 0 | 0 | 24694.0823 | 0 | 24694.0785 | 0.0037922 | 1854.0423 | 4.904 | 0.66061 | 27.9065 | 3.9297 | 0.5897 | 0.07642 | 3.8576 | 0 | 0 | 2.6011 | 0 | 49.528 | 49.528 | 7.6059e-06
IN_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 1380325.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579296.3456 | 0 | 0 | 1959621.3738 | 0 | 1959621.3738 | 0 | 0 | 9162.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3845.3691 | 0 | 0 | 13007.9667 | 0 | 13007.9667 | 0 | 0 | 1380.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2963 | 0 | 0 | 1959.6214 | 0 | 1959.6214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7685 | 1.1619 | 0 | 0 | 3.9303 | 3.9303 | 0
IN_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 25501.685 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21369.9564 | 0 | 0 | 0 | 0 | 116116.3017 | 0 | 0 | 340571.6968 | 0 | 340568.9183 | 2.7786 | 2.7786 | 0 | 2784.784 | 3098.5197 | 786.7667 | 15506.8595 | 0 | 2333.5992 | 0 | 0 | 0 | 0 | 12679.9001 | 0 | 0 | 37190.4293 | 0 | 37190.1259 | 0.30342 | 0.30342 | 0 | 87.0117 | 96.8146 | 24.5829 | 484.5184 | 0 | 72.9143 | 0 | 0 | 0 | 0 | 396.1888 | 0 | 0 | 1162.0306 | 0 | 1162.0211 | 0.0094805 | 0.0094805 | 2.8693 | 0.72858 | 14.3599 | 2.161 | 0 | 0 | 2.5788 | 0 | 11.7421 | 0 | 0 | 34.4394 | 34.4397 | 0.00028098
IN_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 189421.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189421.2514 | 0 | 189421.2514 | 0 | 0 | 1257.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.3783 | 0 | 1257.3783 | 0 | 0 | 189.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.4213 | 0 | 189.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.614 | 0 | 0 | 0 | 5.614 | 5.614 | 0
IN_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 24543.0795 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20858.7001 | 0 | 0 | 0 | 0 | 116141.3088 | 0 | 0 | 333933.701 | 0 | 333934.5346 | -0.83357 | -0.83357 | 0 | 2680.1043 | 2531.4287 | 786.7667 | 15506.8595 | 0 | 2277.77 | 0 | 0 | 0 | 0 | 12682.6309 | 0 | 0 | 36465.5602 | 0 | 36465.6512 | -0.091026 | -0.091026 | 0 | 83.741 | 79.0956 | 24.5829 | 484.5184 | 0 | 71.1699 | 0 | 0 | 0 | 0 | 396.2741 | 0 | 0 | 1139.3818 | 0 | 1139.3846 | -0.0028441 | -0.0028441 | 2.3442 | 0.72858 | 14.3599 | 2.1093 | 0 | 0 | 2.4819 | 0 | 11.7446 | 0 | 0 | 33.7685 | 33.7685 | -8.4293e-05
IN_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 209154.8039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209154.8039 | 0 | 209154.8039 | 0 | 0 | 1388.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.3696 | 0 | 1388.3696 | 0 | 0 | 209.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.1548 | 0 | 209.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1988 | 0 | 0 | 0 | 6.1988 | 6.1988 | 0
IN_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 95496.5583 | 95968.9146 | 7132.5807 | 317887.4784 | 4818.0346 | 95296.5015 | 1205.8979 | 0 | 0 | 19022.0675 | 7179.8163 | 17638.3413 | 0 | 661646.1912 | 0 | 661648.1362 | -1.945 | 4816.0896 | 0 | 10428.2242 | 10479.8055 | 778.8778 | 34713.3126 | 526.1294 | 10406.378 | 131.6841 | 0 | 0 | 2077.2098 | 784.0359 | 1926.1069 | 0 | 72251.7641 | 0 | 72251.9765 | -0.21239 | 525.917 | 0 | 325.8343 | 327.4459 | 24.3364 | 1084.6321 | 16.4391 | 325.1517 | 4.1145 | 0 | 0 | 64.9033 | 24.4975 | 60.182 | 0 | 2257.5368 | 0 | 2257.5434 | -0.0066363 | 16.4325 | 4.4274 | 0.32905 | 14.6653 | 4.3964 | 0.055632 | 0.87756 | 4.4056 | 0 | 0.33123 | 0 | 0.81372 | 30.5243 | 30.5242 | -8.973e-05
IN_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 631814.8922 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 121273.2005 | 0 | 0 | 1095278.5075 | 0 | 1095278.5075 | 0 | 0 | 4193.9873 | 0 | 0 | 0 | 2271.46 | 0 | 0 | 0 | 0 | 0 | 0 | 805.0115 | 0 | 0 | 7270.4587 | 0 | 7270.4587 | 0 | 0 | 631.8149 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 121.2732 | 0 | 0 | 1095.2785 | 0 | 1095.2785 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.5428 | 1.6397 | 0 | 0 | 14.8093 | 14.8093 | 0
IN_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 90645.1809 | 77841.5456 | 7132.5807 | 312483.1662 | 4743.0133 | 81914.9244 | 772.4415 | 0 | 0 | 22650.8756 | 7179.8163 | 12489.6572 | 0 | 617853.2018 | 0 | 617852.646 | 0.55571 | 4743.569 | 0 | 9898.4538 | 8500.2968 | 778.8778 | 34123.1618 | 517.9371 | 8945.1097 | 84.3506 | 0 | 0 | 2473.4756 | 784.0359 | 1363.8706 | 0 | 67469.5696 | 0 | 67469.5089 | 0.060684 | 517.9977 | 0 | 309.2814 | 265.5954 | 24.3364 | 1066.1926 | 16.1832 | 279.4937 | 2.6356 | 0 | 0 | 77.2848 | 24.4975 | 42.6147 | 0 | 2108.1151 | 0 | 2108.1132 | 0.0018961 | 16.1851 | 3.5911 | 0.32905 | 14.416 | 3.779 | 0.035636 | 1.045 | 4.1818 | 0 | 0.33123 | 0 | 0.57619 | 28.5038 | 28.5038 | 2.5637e-05
IN_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 611455.7805 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 121007.8117 | 0 | 0 | 1074654.007 | 0 | 1074654.007 | 0 | 0 | 4058.8435 | 0 | 0 | 0 | 2271.46 | 0 | 0 | 0 | 0 | 0 | 0 | 803.2499 | 0 | 0 | 7133.5533 | 0 | 7133.5533 | 0 | 0 | 611.4558 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0078 | 0 | 0 | 1074.654 | 0 | 1074.654 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.2675 | 1.6361 | 0 | 0 | 14.5304 | 14.5304 | 0
IN_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 34601.4909 | 83915.4924 | 10672.4746 | 53987.5506 | 0 | 44593.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227770.2252 | 0 | 227771.0588 | -0.83357 | -0.83357 | 0 | 3778.4828 | 9163.5718 | 1165.4342 | 5895.4405 | 0 | 4869.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24872.5086 | 0 | 24872.5996 | -0.091026 | -0.091026 | 0 | 118.0603 | 286.3197 | 36.4145 | 184.2055 | 0 | 152.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777.152 | 0 | 777.1549 | -0.0028441 | -0.0028441 | 11.5956 | 1.4747 | 7.4601 | 6.162 | 0 | 0 | 4.7813 | 0 | 0 | 0 | 0 | 31.474 | 31.4738 | -0.00011518
IN_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 568386.9705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91208.4415 | 0 | 0 | 659595.412 | 0 | 659595.412 | 0 | 0 | 3772.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4416 | 0 | 0 | 4378.3943 | 0 | 4378.3943 | 0 | 0 | 568.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2084 | 0 | 0 | 659.5954 | 0 | 659.5954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.0191 | 3.6938 | 0 | 0 | 26.7129 | 26.7129 | 0
IN_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 0 | 32103.5594 | 66163.2298 | 10672.4746 | 53987.5506 | 0 | 42492.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205419.4348 | 0 | 205419.9905 | -0.55571 | -0.55571 | 0 | 3505.7087 | 7225.0247 | 1165.4342 | 5895.4405 | 0 | 4640.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22431.8023 | 0 | 22431.863 | -0.060684 | -0.060684 | 0 | 109.5373 | 225.7489 | 36.4145 | 184.2055 | 0 | 144.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.8911 | 0 | 700.893 | -0.0018961 | -0.0018961 | 9.1426 | 1.4747 | 7.4601 | 5.8717 | 0 | 0 | 4.4361 | 0 | 0 | 0 | 0 | 28.3854 | 28.3854 | -7.679e-05
IN_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 597740.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91217.9196 | 0 | 0 | 688958.7864 | 0 | 688958.7864 | 0 | 0 | 3967.8039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5046 | 0 | 0 | 4573.3084 | 0 | 4573.3084 | 0 | 0 | 597.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2179 | 0 | 0 | 688.9588 | 0 | 688.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2079 | 3.6942 | 0 | 0 | 27.9021 | 27.9021 | 0
IN_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 44871.0734 | 65140.7173 | 79122.4648 | 12306.2718 | 154949.5496 | 0 | 45707.4219 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 402169.7416 | 0 | 402169.7416 | 0 | 0 | 4899.9212 | 7113.3663 | 8640.1732 | 1343.8449 | 16920.4908 | 0 | 4991.2505 | 7.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 43916.9358 | 0 | 43916.9358 | 0 | 0 | 153.1001 | 222.2601 | 269.9659 | 41.989 | 528.6879 | 0 | 155.9537 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.2032 | 0 | 1372.2032 | 0 | 0 | 6.2489 | 0.97192 | 12.2376 | 3.6099 | 0.0057056 | 0 | 5.1447 | 3.5438 | 0 | 0 | 0 | 31.7625 | 31.7625 | 0
IN_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 97378.7309 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605693.0524 | 0 | 0 | 1102567.2212 | 0 | 1102567.2212 | 0 | 0 | 646.4 | 0 | 0 | 0 | 2651.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.5905 | 0 | 0 | 7318.8412 | 0 | 7318.8412 | 0 | 0 | 97.3787 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.6931 | 0 | 0 | 1102.5672 | 0 | 1102.5672 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.254 | 14.02 | 0 | 0 | 25.5212 | 25.5212 | 0
IN_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 49697.4437 | 60761.6962 | 50756.0776 | 12306.2718 | 154949.5496 | 0 | 43290.0689 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371833.3506 | 0 | 371833.6284 | -0.27786 | -0.27786 | 5426.9608 | 6635.1772 | 5542.5637 | 1343.8449 | 16920.4908 | 0 | 4727.2755 | 7.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 40604.2019 | 0 | 40604.2322 | -0.030342 | -0.030342 | 169.5677 | 207.3189 | 173.1797 | 41.989 | 528.6879 | 0 | 147.7057 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.6954 | 0 | 1268.6963 | -0.00094805 | -0.00094805 | 4.0086 | 0.97192 | 12.2376 | 3.419 | 0.0057056 | 0 | 4.7988 | 3.925 | 0 | 0 | 0 | 29.3666 | 29.3666 | -2.1945e-05
IN_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 93957.1111 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605740.4432 | 0 | 0 | 1099192.9922 | 0 | 1099192.9922 | 0 | 0 | 623.6873 | 0 | 0 | 0 | 2651.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.9051 | 0 | 0 | 7296.4431 | 0 | 7296.4431 | 0 | 0 | 93.9571 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.7404 | 0 | 0 | 1099.193 | 0 | 1099.193 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.1748 | 14.0211 | 0 | 0 | 25.4431 | 25.4431 | 0
IN_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 4590.1922 | 3689.9366 | 8821.9492 | 1600.4544 | 13417.6985 | 0 | 4956.963 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42081.3924 | 0 | 42084.171 | -2.7786 | -2.7786 | 501.249 | 402.9411 | 963.3569 | 174.7696 | 1465.2127 | 0 | 541.3004 | 0 | 0 | 0 | 0 | 546.4585 | 0 | 0 | 4595.2881 | 0 | 4595.5915 | -0.30342 | -0.30342 | 15.6617 | 12.5901 | 30.1005 | 5.4608 | 45.7812 | 0 | 16.9132 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.5817 | 0 | 143.5912 | -0.0094805 | -0.0094805 | 5.4708 | 0.9925 | 8.3208 | 3.074 | 0 | 0 | 2.2883 | 2.8466 | 3.1033 | 0 | 0 | 26.098 | 26.0963 | -0.0017231
IN_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 15184.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15184.0303 | 0 | 15184.0303 | 0 | 0 | 100.7916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7916 | 0 | 100.7916 | 0 | 0 | 15.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.184 | 0 | 15.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7597 | 0 | 0 | 0 | 2.7597 | 2.7597 | 0
IN_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Electricity | 4629.0921 | 3484.3226 | 7110.3521 | 1600.4544 | 13417.6985 | 0 | 4554.0708 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39800.1892 | 0 | 39797.6884 | 2.5007 | 2.5007 | 505.4969 | 380.488 | 776.4505 | 174.7696 | 1465.2127 | 0 | 497.3045 | 0 | 0 | 0 | 0 | 546.4585 | 0 | 0 | 4346.1807 | 0 | 4345.9076 | 0.27308 | 0.27308 | 15.7945 | 11.8885 | 24.2605 | 5.4608 | 45.7812 | 0 | 15.5385 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.7982 | 0 | 135.7897 | 0.0085324 | 0.0085324 | 4.4094 | 0.9925 | 8.3208 | 2.8242 | 0 | 0 | 2.1608 | 2.8707 | 3.1033 | 0 | 0 | 24.6801 | 24.6816 | 0.0015508
IN_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | IN-FORTWAYNE-IN | Zone5A | Zone5A(IN-FORTWAYNE-IN) |  |  | IN | 0.1092 | 0.006638 |  |  |  | Natural Gas | 15591.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15591.5916 | 0 | 15591.5916 | 0 | 0 | 103.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.497 | 0 | 103.497 | 0 | 0 | 15.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5916 | 0 | 15.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8338 | 0 | 0 | 0 | 2.8338 | 2.8338 | 0
KS_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 755470.0524 | 879894.2684 | 95666.0509 | 4077910.5986 | 543457.0788 | 601912.5647 | 105535.5197 | 262774.6083 | 331619.155 | 14034.5403 | 0 | 0 | 0 | 7668274.4372 | 0 | 7668273.0479 | 1.3893 | 543458.4681 | 0 | 77964.5094 | 90805.0885 | 9872.7365 | 420840.3738 | 56084.7705 | 62117.3767 | 10891.2656 | 27118.3396 | 34223.0968 | 1448.3646 | 0 | 0 | 0 | 791365.9219 | 0 | 791365.7785 | 0.14337 | 56084.9139 | 0 | 2577.6638 | 3002.1992 | 326.4126 | 13913.831 | 1854.2756 | 2053.7257 | 360.0872 | 896.587 | 1131.4846 | 47.8859 | 0 | 0 | 0 | 26164.1524 | 0 | 26164.1476 | 0.0047402 | 1854.2803 | 6.0214 | 0.65467 | 27.9065 | 4.1191 | 0.72221 | 0.096043 | 5.1699 | 0 | 0 | 2.2694 | 0 | 52.4765 | 52.4765 | 9.5073e-06
KS_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 829226.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544018.5924 | 0 | 0 | 1373244.8343 | 0 | 1373244.8343 | 0 | 0 | 6579.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4316.7875 | 0 | 0 | 10896.6978 | 0 | 10896.6978 | 0 | 0 | 829.2262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.0186 | 0 | 0 | 1373.2448 | 0 | 1373.2448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6631 | 1.0911 | 0 | 0 | 2.7543 | 2.7543 | 0
KS_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 710999.0927 | 716322.8264 | 95666.0509 | 4077910.5986 | 543384.8361 | 575680.1167 | 102398.5179 | 237231.2448 | 331483.0052 | 12428.5288 | 0 | 0 | 0 | 7403504.818 | 0 | 7403505.0959 | -0.27786 | 543384.5583 | 0 | 73375.1064 | 73924.5157 | 9872.7365 | 420840.3738 | 56077.3151 | 59410.188 | 10567.5271 | 24482.2645 | 34209.0461 | 1282.6242 | 0 | 0 | 0 | 764041.6972 | 0 | 764041.7259 | -0.028675 | 56077.2864 | 0 | 2425.9289 | 2444.0935 | 326.4126 | 13913.831 | 1854.0291 | 1964.2206 | 349.3837 | 809.433 | 1131.02 | 42.4061 | 0 | 0 | 0 | 25260.7584 | 0 | 25260.7594 | -0.00094805 | 1854.0281 | 4.902 | 0.65467 | 27.9065 | 3.9396 | 0.70075 | 0.085052 | 4.8656 | 0 | 0 | 2.2684 | 0 | 50.6646 | 50.6646 | -1.9015e-06
KS_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 764082.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544009.1142 | 0 | 0 | 1308091.8855 | 0 | 1308091.8855 | 0 | 0 | 6062.9968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4316.7123 | 0 | 0 | 10379.7091 | 0 | 10379.7091 | 0 | 0 | 764.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.0091 | 0 | 0 | 1308.0919 | 0 | 1308.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5325 | 1.0911 | 0 | 0 | 2.6236 | 2.6236 | 0
KS_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 36074.1312 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 22814.811 | 0 | 0 | 0 | 0 | 109180.9992 | 0 | 0 | 345659.2524 | 0 | 345658.9746 | 0.27786 | 0.27786 | 0 | 3722.8503 | 2928.2714 | 744.1113 | 14654.8342 | 0 | 2354.4885 | 0 | 0 | 0 | 0 | 11267.4791 | 0 | 0 | 35672.0348 | 0 | 35672.0062 | 0.028675 | 0.028675 | 0 | 123.0849 | 96.8146 | 24.6018 | 484.5184 | 0 | 77.8441 | 0 | 0 | 0 | 0 | 372.5256 | 0 | 0 | 1179.3894 | 0 | 1179.3884 | 0.00094805 | 0.00094805 | 2.8693 | 0.72914 | 14.3599 | 2.3071 | 0 | 0 | 3.6479 | 0 | 11.0407 | 0 | 0 | 34.9542 | 34.9542 | 2.8098e-05
KS_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 104961.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104961.2679 | 0 | 104961.2679 | 0 | 0 | 832.8677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832.8677 | 0 | 832.8677 | 0 | 0 | 104.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9613 | 0 | 104.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1108 | 0 | 0 | 0 | 3.1108 | 3.1108 | 0
KS_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 35273.904 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 22247.9834 | 0 | 0 | 0 | 0 | 109203.2278 | 0 | 0 | 339121.285 | 0 | 339123.7857 | -2.5007 | -2.5007 | 0 | 3640.2669 | 2392.3392 | 744.1113 | 14654.8342 | 0 | 2295.9919 | 0 | 0 | 0 | 0 | 11269.7731 | 0 | 0 | 34997.3166 | 0 | 34997.5747 | -0.25807 | -0.25807 | 0 | 120.3546 | 79.0956 | 24.6018 | 484.5184 | 0 | 75.9101 | 0 | 0 | 0 | 0 | 372.6014 | 0 | 0 | 1157.0818 | 0 | 1157.0904 | -0.0085324 | -0.0085324 | 2.3442 | 0.72914 | 14.3599 | 2.2498 | 0 | 0 | 3.567 | 0 | 11.043 | 0 | 0 | 34.2933 | 34.2931 | -0.00025288
KS_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 109586.6154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109586.6154 | 0 | 109586.6154 | 0 | 0 | 869.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.5698 | 0 | 869.5698 | 0 | 0 | 109.5866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5866 | 0 | 109.5866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2479 | 0 | 0 | 0 | 3.2479 | 3.2479 | 0
KS_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 138475.4277 | 97083.1199 | 7113.1307 | 317887.4784 | 4818.0346 | 98766.9313 | 675.1917 | 0 | 0 | 18302.4187 | 7179.8163 | 17641.1199 | 0 | 707942.6693 | 0 | 707943.225 | -0.55571 | 4817.4789 | 0 | 14290.6641 | 10018.978 | 734.0751 | 32805.9878 | 497.2212 | 10192.7473 | 69.6798 | 0 | 0 | 1888.8096 | 740.957 | 1820.5636 | 0 | 73059.6835 | 0 | 73059.7408 | -0.05735 | 497.1638 | 0 | 472.4782 | 331.2476 | 24.27 | 1084.6321 | 16.4391 | 336.9928 | 2.3038 | 0 | 0 | 62.4479 | 24.4975 | 60.1915 | 0 | 2415.5004 | 0 | 2415.5023 | -0.0018961 | 16.4372 | 4.4788 | 0.32815 | 14.6653 | 4.5565 | 0.031149 | 0.84436 | 6.3884 | 0 | 0.33123 | 0 | 0.81385 | 32.66 | 32.66 | -2.5637e-05
KS_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 355943.2412 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114439.4391 | 0 | 0 | 812573.0951 | 0 | 812573.0951 | 0 | 0 | 2824.4096 | 0 | 0 | 0 | 2715.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 908.0769 | 0 | 0 | 6447.7675 | 0 | 6447.7675 | 0 | 0 | 355.9432 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4394 | 0 | 0 | 812.5731 | 0 | 812.5731 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.8127 | 1.5473 | 0 | 0 | 10.9868 | 10.9868 | 0
KS_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 126683.1907 | 78777.9226 | 7113.1307 | 312483.1662 | 4743.0133 | 82417.8449 | 439.0135 | 0 | 0 | 22903.7252 | 7179.8163 | 12495.2144 | 0 | 655236.0379 | 0 | 655237.4272 | -1.3893 | 4741.624 | 0 | 13073.7053 | 8129.8816 | 734.0751 | 32248.2628 | 489.479 | 8505.5216 | 45.3062 | 0 | 0 | 2363.6644 | 740.957 | 1289.5061 | 0 | 67620.3591 | 0 | 67620.5025 | -0.14337 | 489.3356 | 0 | 432.243 | 268.7903 | 24.27 | 1066.1926 | 16.1832 | 281.2097 | 1.4979 | 0 | 0 | 78.1475 | 24.4975 | 42.6337 | 0 | 2235.6654 | 0 | 2235.6701 | -0.0047402 | 16.1784 | 3.6343 | 0.32815 | 14.416 | 3.8022 | 0.020253 | 1.0566 | 5.8444 | 0 | 0.33123 | 0 | 0.57645 | 30.2285 | 30.2284 | -6.4093e-05
KS_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 334854.3103 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114211.963 | 0 | 0 | 791256.6881 | 0 | 791256.6881 | 0 | 0 | 2657.069 | 0 | 0 | 0 | 2715.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 906.2719 | 0 | 0 | 6278.6218 | 0 | 6278.6218 | 0 | 0 | 334.8543 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.212 | 0 | 0 | 791.2567 | 0 | 791.2567 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.5276 | 1.5443 | 0 | 0 | 10.6986 | 10.6986 | 0
KS_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 50039.2074 | 84721.2767 | 10683.5889 | 53987.5506 | 0 | 40072.4887 | 0 | 0 | 0 | 5557.1334 | 0 | 0 | 0 | 245061.2457 | 0 | 245063.1907 | -1.945 | -1.945 | 0 | 5164.0462 | 8743.2358 | 1102.5464 | 5571.5152 | 0 | 4135.4808 | 0 | 0 | 0 | 573.4962 | 0 | 0 | 0 | 25290.3206 | 0 | 25290.5213 | -0.20072 | -0.20072 | 0 | 170.7338 | 289.069 | 36.4524 | 184.2055 | 0 | 136.7273 | 0 | 0 | 0 | 18.9609 | 0 | 0 | 0 | 836.149 | 0 | 836.1556 | -0.0066363 | -0.0066363 | 11.707 | 1.4763 | 7.4601 | 5.5373 | 0 | 0.7679 | 6.9145 | 0 | 0 | 0 | 0 | 33.8634 | 33.8632 | -0.00026876
KS_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 159271.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89094.8093 | 0 | 0 | 248365.9981 | 0 | 248365.9981 | 0 | 0 | 1263.8169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706.9673 | 0 | 0 | 1970.7842 | 0 | 1970.7842 | 0 | 0 | 159.2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0948 | 0 | 0 | 248.366 | 0 | 248.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4503 | 3.6082 | 0 | 0 | 10.0586 | 10.0586 | 0
KS_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 46741.0487 | 67030.1426 | 10683.5889 | 53987.5506 | 0 | 38060.8064 | 0 | 0 | 0 | 5643.2689 | 0 | 0 | 0 | 222146.4063 | 0 | 222145.5727 | 0.83357 | 0.83357 | 0 | 4823.6762 | 6917.5107 | 1102.5464 | 5571.5152 | 0 | 3927.8752 | 0 | 0 | 0 | 582.3854 | 0 | 0 | 0 | 22925.5091 | 0 | 22925.4231 | 0.086024 | 0.086024 | 0 | 159.4805 | 228.7068 | 36.4524 | 184.2055 | 0 | 129.8635 | 0 | 0 | 0 | 19.2548 | 0 | 0 | 0 | 757.9635 | 0 | 757.9607 | 0.0028441 | 0.0028441 | 9.2624 | 1.4763 | 7.4601 | 5.2593 | 0 | 0.7798 | 6.4588 | 0 | 0 | 0 | 0 | 30.6966 | 30.6967 | 0.00011518
KS_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 173175.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89104.2875 | 0 | 0 | 262279.9534 | 0 | 262279.9534 | 0 | 0 | 1374.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.0425 | 0 | 0 | 2081.1914 | 0 | 2081.1914 | 0 | 0 | 173.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1043 | 0 | 0 | 262.28 | 0 | 262.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0134 | 3.6086 | 0 | 0 | 10.6221 | 10.6221 | 0
KS_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 26843.7327 | 83648.75 | 79328.0788 | 12314.6075 | 154949.5496 | 0 | 46571.5562 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 403728.5175 | 0 | 403729.0732 | -0.55571 | -0.55571 | 2770.2732 | 8632.551 | 8186.6577 | 1270.8675 | 15990.7935 | 0 | 4806.1846 | 7.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 41664.783 | 0 | 41664.8404 | -0.05735 | -0.05735 | 91.5908 | 285.4095 | 270.6674 | 42.0174 | 528.6879 | 0 | 158.9021 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.5217 | 0 | 1377.5236 | -0.0018961 | -0.0018961 | 6.2652 | 0.97258 | 12.2376 | 3.6781 | 0.0057056 | 0 | 6.6064 | 2.1201 | 0 | 0 | 0 | 31.8856 | 31.8856 | -4.3889e-05
KS_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 61503.8529 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 565135.9578 | 0 | 0 | 1026135.2486 | 0 | 1026135.2486 | 0 | 0 | 488.0331 | 0 | 0 | 0 | 3169.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 4484.3538 | 0 | 0 | 8142.3832 | 0 | 8142.3832 | 0 | 0 | 61.5039 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 565.136 | 0 | 0 | 1026.1352 | 0 | 1026.1352 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4236 | 13.0812 | 0 | 0 | 23.752 | 23.752 | 0
KS_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 30397.5195 | 78502.8445 | 50869.9988 | 12314.6075 | 154949.5496 | 0 | 44115.3032 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371222.0659 | 0 | 371222.0659 | 0 | 0 | 3137.024 | 8101.4936 | 5249.7839 | 1270.8675 | 15990.7935 | 0 | 4552.6993 | 7.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 38310.1172 | 0 | 38310.1172 | 0 | 0 | 103.7163 | 267.8517 | 173.5684 | 42.0174 | 528.6879 | 0 | 150.5214 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.6097 | 0 | 1266.6097 | 0 | 0 | 4.0176 | 0.97258 | 12.2376 | 3.4841 | 0.0057056 | 0 | 6.2 | 2.4007 | 0 | 0 | 0 | 29.3183 | 29.3183 | 0
KS_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 61172.1169 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 565202.305 | 0 | 0 | 1025869.8598 | 0 | 1025869.8598 | 0 | 0 | 485.4007 | 0 | 0 | 0 | 3169.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 4484.8803 | 0 | 0 | 8140.2773 | 0 | 8140.2773 | 0 | 0 | 61.1721 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 565.2023 | 0 | 0 | 1025.8699 | 0 | 1025.8699 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.416 | 13.0828 | 0 | 0 | 23.7459 | 23.7459 | 0
KS_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 2961.9521 | 5368.1908 | 8846.9563 | 1586.5616 | 13417.6985 | 0 | 5282.0553 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42467.6132 | 0 | 42468.1689 | -0.55571 | -0.55571 | 305.6735 | 553.9973 | 913.0059 | 163.7332 | 1384.7065 | 0 | 545.1081 | 0 | 0 | 0 | 0 | 516.4333 | 0 | 0 | 4382.6577 | 0 | 4382.715 | -0.05735 | -0.05735 | 10.1062 | 18.3163 | 30.1858 | 5.4133 | 45.7812 | 0 | 18.0224 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.8995 | 0 | 144.9014 | -0.0018961 | -0.0018961 | 5.4863 | 0.98389 | 8.3208 | 3.2756 | 0 | 0 | 3.329 | 1.8368 | 3.1033 | 0 | 0 | 26.3361 | 26.3358 | -0.00034462
KS_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 4634.8257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4634.8257 | 0 | 4634.8257 | 0 | 0 | 36.7773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7773 | 0 | 36.7773 | 0 | 0 | 4.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6348 | 0 | 4.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84239 | 0 | 0 | 0 | 0.84239 | 0.84239 | 0
KS_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 3014.7449 | 5104.227 | 7129.8021 | 1586.5616 | 13417.6985 | 0 | 4854.156 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40111.3886 | 0 | 40111.1108 | 0.27786 | 0.27786 | 311.1217 | 526.7562 | 735.7956 | 163.7332 | 1384.7065 | 0 | 500.9489 | 0 | 0 | 0 | 0 | 516.4333 | 0 | 0 | 4139.4953 | 0 | 4139.4666 | 0.028675 | 0.028675 | 10.2863 | 17.4156 | 24.3269 | 5.4133 | 45.7812 | 0 | 16.5624 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.8601 | 0 | 136.8591 | 0.00094805 | 0.00094805 | 4.4215 | 0.98389 | 8.3208 | 3.0102 | 0 | 0 | 3.1653 | 1.8696 | 3.1033 | 0 | 0 | 24.8744 | 24.8746 | 0.00017231
KS_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | KS-TOPEKA-KS | Zone4A | Zone4A(KS-TOPEKA-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 4852.8237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4852.8237 | 0 | 4852.8237 | 0 | 0 | 38.5072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.5072 | 0 | 38.5072 | 0 | 0 | 4.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8528 | 0 | 4.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88201 | 0 | 0 | 0 | 0.88201 | 0.88201 | 0
KS_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 623263.0711 | 880269.3749 | 95502.1154 | 4077910.5986 | 543457.0788 | 665839.0484 | 86085.553 | 201296.0419 | 481853.4769 | 11236.5237 | 0 | 0 | 0 | 7666712.8827 | 0 | 7666711.4934 | 1.3893 | 543458.4681 | 0 | 64320.7489 | 90843.7995 | 9855.8183 | 420840.3738 | 56084.7705 | 68714.5898 | 8884.0291 | 20773.7515 | 49727.2788 | 1159.6092 | 0 | 0 | 0 | 791204.7695 | 0 | 791204.6261 | 0.14337 | 56084.9139 | 0 | 2126.5736 | 3003.4791 | 325.8532 | 13913.831 | 1854.2756 | 2271.8428 | 293.7239 | 686.8221 | 1644.0841 | 38.339 | 0 | 0 | 0 | 26158.8244 | 0 | 26158.8196 | 0.0047402 | 1854.2803 | 6.024 | 0.65355 | 27.9065 | 4.5566 | 0.58911 | 0.076895 | 4.2652 | 0 | 0 | 3.2975 | 0 | 52.4658 | 52.4658 | 9.5073e-06
KS_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 1004695.6254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569723.3927 | 0 | 0 | 1574419.018 | 0 | 1574419.018 | 0 | 0 | 7972.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4520.7551 | 0 | 0 | 12493.0149 | 0 | 12493.0149 | 0 | 0 | 1004.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.7234 | 0 | 0 | 1574.419 | 0 | 1574.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0151 | 1.1427 | 0 | 0 | 3.1578 | 3.1578 | 0
KS_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 586138.6416 | 717103.6037 | 95502.1154 | 4077910.5986 | 543387.6147 | 647028.1519 | 83395.9004 | 180515.1417 | 481631.1916 | 3637.1438 | 0 | 0 | 0 | 7416250.1034 | 0 | 7416247.8806 | 2.2229 | 543389.8375 | 0 | 60489.5078 | 74005.0919 | 9855.8183 | 420840.3738 | 56077.6018 | 66773.3053 | 8606.4569 | 18629.1626 | 49704.339 | 375.3532 | 0 | 0 | 0 | 765357.0107 | 0 | 765356.7813 | 0.2294 | 56077.8312 | 0 | 1999.905 | 2446.7575 | 325.8532 | 13913.831 | 1854.0385 | 2207.6601 | 284.5468 | 615.9177 | 1643.3256 | 12.4099 | 0 | 0 | 0 | 25304.2454 | 0 | 25304.2378 | 0.0075844 | 1854.0461 | 4.9074 | 0.65355 | 27.9065 | 4.4278 | 0.57071 | 0.02489 | 4.0111 | 0 | 0 | 3.296 | 0 | 50.7518 | 50.7518 | 1.5212e-05
KS_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 1175890.3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569723.3927 | 0 | 0 | 1745613.7462 | 0 | 1745613.7462 | 0 | 0 | 9330.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4520.7551 | 0 | 0 | 13851.4451 | 0 | 13851.4451 | 0 | 0 | 1175.8904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.7234 | 0 | 0 | 1745.6137 | 0 | 1745.6137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3584 | 1.1427 | 0 | 0 | 3.5011 | 3.5011 | 0
KS_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 28410.8443 | 28374.723 | 7207.602 | 142004.2074 | 0 | 23867.8878 | 0 | 0 | 0 | 0 | 114218.5406 | 0 | 0 | 344083.8051 | 0 | 344080.7487 | 3.0564 | 3.0564 | 0 | 2931.9991 | 2928.2714 | 743.8245 | 14654.8342 | 0 | 2463.166 | 0 | 0 | 0 | 0 | 11787.3534 | 0 | 0 | 35509.4487 | 0 | 35509.1333 | 0.31542 | 0.31542 | 0 | 96.9378 | 96.8146 | 24.5923 | 484.5184 | 0 | 81.4372 | 0 | 0 | 0 | 0 | 389.7137 | 0 | 0 | 1174.0139 | 0 | 1174.0035 | 0.010429 | 0.010429 | 2.8693 | 0.72886 | 14.3599 | 2.4136 | 0 | 0 | 2.873 | 0 | 11.5502 | 0 | 0 | 34.7946 | 34.7949 | 0.00030908
KS_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 129860.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129860.4236 | 0 | 129860.4236 | 0 | 0 | 1030.4425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030.4425 | 0 | 1030.4425 | 0 | 0 | 129.8604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.8604 | 0 | 129.8604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8487 | 0 | 0 | 0 | 3.8487 | 3.8487 | 0
KS_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 26979.8825 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 23095.4463 | 0 | 0 | 0 | 0 | 114249.1048 | 0 | 0 | 336717.8248 | 0 | 336718.1027 | -0.27786 | -0.27786 | 0 | 2784.3239 | 2392.3392 | 743.8245 | 14654.8342 | 0 | 2383.4501 | 0 | 0 | 0 | 0 | 11790.5076 | 0 | 0 | 34749.2795 | 0 | 34749.3082 | -0.028675 | -0.028675 | 0 | 92.0554 | 79.0956 | 24.5923 | 484.5184 | 0 | 78.8017 | 0 | 0 | 0 | 0 | 389.8179 | 0 | 0 | 1148.8812 | 0 | 1148.8822 | -0.00094805 | -0.00094805 | 2.3442 | 0.72886 | 14.3599 | 2.3355 | 0 | 0 | 2.7283 | 0 | 11.5532 | 0 | 0 | 34.05 | 34.05 | -2.8098e-05
KS_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 143395.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143395.2521 | 0 | 143395.2521 | 0 | 0 | 1137.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.8413 | 0 | 1137.8413 | 0 | 0 | 143.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.3953 | 0 | 143.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2499 | 0 | 0 | 0 | 4.2499 | 4.2499 | 0
KS_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 107230.4454 | 98347.3677 | 7132.5807 | 317887.4784 | 4818.0346 | 107766.7088 | 714.0916 | 0 | 0 | 17705.0269 | 7179.8163 | 17557.7629 | 0 | 686339.3133 | 0 | 686339.5912 | -0.27786 | 4817.7568 | 0 | 11066.182 | 10149.4483 | 736.0823 | 32805.9878 | 497.2212 | 11121.5243 | 73.6943 | 0 | 0 | 1827.1588 | 740.957 | 1811.9611 | 0 | 70830.2171 | 0 | 70830.2458 | -0.028675 | 497.1925 | 0 | 365.8703 | 335.5612 | 24.3364 | 1084.6321 | 16.4391 | 367.7 | 2.4365 | 0 | 0 | 60.4096 | 24.4975 | 59.9071 | 0 | 2341.7897 | 0 | 2341.7907 | -0.00094805 | 16.4382 | 4.5371 | 0.32905 | 14.6653 | 4.9717 | 0.032944 | 0.8168 | 4.9469 | 0 | 0.33123 | 0 | 0.81 | 31.6634 | 31.6634 | -1.2819e-05
KS_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 385989.0439 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119150.0902 | 0 | 0 | 847329.5489 | 0 | 847329.5489 | 0 | 0 | 3062.8231 | 0 | 0 | 0 | 2715.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 945.456 | 0 | 0 | 6723.56 | 0 | 6723.56 | 0 | 0 | 385.989 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1501 | 0 | 0 | 847.3295 | 0 | 847.3295 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.219 | 1.611 | 0 | 0 | 11.4567 | 11.4567 | 0
KS_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 97613.8261 | 80122.7489 | 7132.5807 | 312483.1662 | 4745.7919 | 83804.3497 | 711.3131 | 0 | 0 | 22256.3191 | 7179.8163 | 12456.3144 | 0 | 628506.2264 | 0 | 628507.6157 | -1.3893 | 4744.4026 | 0 | 10073.7469 | 8268.6677 | 736.0823 | 32248.2628 | 489.7657 | 8648.6089 | 73.4075 | 0 | 0 | 2296.8521 | 740.957 | 1285.4916 | 0 | 64861.8426 | 0 | 64861.9859 | -0.14337 | 489.6223 | 0 | 333.0584 | 273.3788 | 24.3364 | 1066.1926 | 16.1926 | 285.9404 | 2.427 | 0 | 0 | 75.9386 | 24.4975 | 42.5009 | 0 | 2144.4632 | 0 | 2144.468 | -0.0047402 | 16.1879 | 3.6964 | 0.32905 | 14.416 | 3.8662 | 0.032815 | 1.0268 | 4.5033 | 0 | 0.33123 | 0 | 0.57466 | 28.9954 | 28.9953 | -6.4093e-05
KS_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 365592.0195 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119083.743 | 0 | 0 | 826866.1773 | 0 | 826866.1773 | 0 | 0 | 2900.9727 | 0 | 0 | 0 | 2715.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 944.9295 | 0 | 0 | 6561.1831 | 0 | 6561.1831 | 0 | 0 | 365.592 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.0837 | 0 | 0 | 826.8662 | 0 | 826.8662 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.9432 | 1.6101 | 0 | 0 | 11.1801 | 11.1801 | 0
KS_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 36827.1228 | 85932.7318 | 10769.7245 | 53987.5506 | 0 | 46265.9138 | 0 | 0 | 0 | 4984.7486 | 0 | 0 | 0 | 238767.7922 | 0 | 238764.7357 | 3.0564 | 3.0564 | 0 | 3800.5591 | 8868.2579 | 1111.4356 | 5571.5152 | 0 | 4774.6423 | 0 | 0 | 0 | 514.4261 | 0 | 0 | 0 | 24640.8361 | 0 | 24640.5207 | 0.31542 | 0.31542 | 0 | 125.6541 | 293.2025 | 36.7463 | 184.2055 | 0 | 157.8593 | 0 | 0 | 0 | 17.008 | 0 | 0 | 0 | 814.6757 | 0 | 814.6653 | 0.010429 | 0.010429 | 11.8744 | 1.4882 | 7.4601 | 6.3931 | 0 | 0.6888 | 5.0889 | 0 | 0 | 0 | 0 | 32.9931 | 32.9935 | 0.00042234
KS_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 163716.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90630.273 | 0 | 0 | 254346.7242 | 0 | 254346.7242 | 0 | 0 | 1299.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719.1512 | 0 | 0 | 2018.2413 | 0 | 2018.2413 | 0 | 0 | 163.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6303 | 0 | 0 | 254.3467 | 0 | 254.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6303 | 3.6704 | 0 | 0 | 10.3008 | 10.3008 | 0
KS_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 0 | 34118.0203 | 68311.0619 | 10769.7245 | 53987.5506 | 0 | 44126.4175 | 0 | 0 | 0 | 5129.2341 | 0 | 0 | 0 | 216442.0089 | 0 | 216440.6196 | 1.3893 | 1.3893 | 0 | 3520.9797 | 7049.7016 | 1111.4356 | 5571.5152 | 0 | 4553.8463 | 0 | 0 | 0 | 529.337 | 0 | 0 | 0 | 22336.8153 | 0 | 22336.6719 | 0.14337 | 0.14337 | 0 | 116.4107 | 233.0773 | 36.7463 | 184.2055 | 0 | 150.5593 | 0 | 0 | 0 | 17.5009 | 0 | 0 | 0 | 738.5001 | 0 | 738.4954 | 0.0047402 | 0.0047402 | 9.4394 | 1.4882 | 7.4601 | 6.0975 | 0 | 0.70877 | 4.7145 | 0 | 0 | 0 | 0 | 29.9083 | 29.9085 | 0.00019197
KS_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 178056.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90639.7512 | 0 | 0 | 268696.6753 | 0 | 268696.6753 | 0 | 0 | 1412.8817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719.2264 | 0 | 0 | 2132.1081 | 0 | 2132.1081 | 0 | 0 | 178.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6398 | 0 | 0 | 268.6967 | 0 | 268.6967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2111 | 3.6708 | 0 | 0 | 10.8819 | 10.8819 | 0
KS_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 30561.4549 | 67894.2769 | 79291.9574 | 12309.0504 | 154949.5496 | 0 | 47602.4044 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392680.9364 | 0 | 392677.0464 | 3.89 | 3.89 | 3153.9421 | 7006.6894 | 8182.93 | 1270.294 | 15990.7935 | 0 | 4912.5681 | 7.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 40524.6726 | 0 | 40524.2712 | 0.40145 | 0.40145 | 104.2757 | 231.6553 | 270.5442 | 41.9985 | 528.6879 | 0 | 162.4194 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.8274 | 0 | 1339.8141 | 0.013273 | 0.013273 | 6.2623 | 0.97214 | 12.2376 | 3.7595 | 0.0057056 | 0 | 5.3621 | 2.4137 | 0 | 0 | 0 | 31.0128 | 31.0131 | 0.00030722
KS_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 63541.6597 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594622.5484 | 0 | 0 | 1057659.646 | 0 | 1057659.646 | 0 | 0 | 504.2031 | 0 | 0 | 0 | 3169.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 4718.3299 | 0 | 0 | 8392.5293 | 0 | 8392.5293 | 0 | 0 | 63.5417 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.6225 | 0 | 0 | 1057.6596 | 0 | 1057.6596 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4708 | 13.7638 | 0 | 0 | 24.4817 | 24.4817 | 0
KS_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 34632.0551 | 63151.2636 | 50872.7774 | 12309.0504 | 154949.5496 | 0 | 45007.2231 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360994.1619 | 0 | 360992.2169 | 1.945 | 1.945 | 3574.0281 | 6517.2104 | 5250.0706 | 1270.294 | 15990.7935 | 0 | 4644.7454 | 7.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 37254.5975 | 0 | 37254.3968 | 0.20072 | 0.20072 | 118.1646 | 215.4721 | 173.5779 | 41.9985 | 528.6879 | 0 | 153.5646 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.7121 | 0 | 1231.7054 | 0.0066363 | 0.0066363 | 4.0178 | 0.97214 | 12.2376 | 3.5546 | 0.0057056 | 0 | 4.9875 | 2.7352 | 0 | 0 | 0 | 28.5104 | 28.5105 | 0.00015361
KS_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 63911.3084 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594707.8519 | 0 | 0 | 1058114.5983 | 0 | 1058114.5983 | 0 | 0 | 507.1362 | 0 | 0 | 0 | 3169.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 4719.0068 | 0 | 0 | 8396.1393 | 0 | 8396.1393 | 0 | 0 | 63.9113 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.7079 | 0 | 0 | 1058.1146 | 0 | 1058.1146 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4794 | 13.7657 | 0 | 0 | 24.4923 | 24.4923 | 0
KS_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 2734.1096 | 4234.5356 | 8844.1778 | 1578.2259 | 13417.6985 | 0 | 5723.8474 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41536.7933 | 0 | 41539.8498 | -3.0564 | -3.0564 | 282.1601 | 437.0041 | 912.7191 | 162.8729 | 1384.7065 | 0 | 590.701 | 0 | 0 | 0 | 0 | 516.4333 | 0 | 0 | 4286.5971 | 0 | 4286.9125 | -0.31542 | -0.31542 | 9.3288 | 14.4482 | 30.1763 | 5.3849 | 45.7812 | 0 | 19.5298 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.7235 | 0 | 141.734 | -0.010429 | -0.010429 | 5.4846 | 0.97872 | 8.3208 | 3.5496 | 0 | 0 | 2.626 | 1.6955 | 3.1033 | 0 | 0 | 25.7604 | 25.7585 | -0.0018954
KS_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 8871.5682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8871.5682 | 0 | 8871.5682 | 0 | 0 | 70.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3959 | 0 | 70.3959 | 0 | 0 | 8.8716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8716 | 0 | 8.8716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6124 | 0 | 0 | 0 | 1.6124 | 1.6124 | 0
KS_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Electricity | 2786.9024 | 3984.4646 | 7129.8021 | 1578.2259 | 13417.6985 | 0 | 5265.3839 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39166.676 | 0 | 39164.4531 | 2.2229 | 2.2229 | 287.6083 | 411.1967 | 735.7956 | 162.8729 | 1384.7065 | 0 | 543.3876 | 0 | 0 | 0 | 0 | 516.4333 | 0 | 0 | 4042.001 | 0 | 4041.7716 | 0.2294 | 0.2294 | 9.5089 | 13.595 | 24.3269 | 5.3849 | 45.7812 | 0 | 17.9655 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.6367 | 0 | 133.6291 | 0.0075844 | 0.0075844 | 4.4215 | 0.97872 | 8.3208 | 3.2653 | 0 | 0 | 2.4709 | 1.7283 | 3.1033 | 0 | 0 | 24.2874 | 24.2887 | 0.0013785
KS_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | KS-GOODLAND-KS | Zone5A | Zone5A(KS-GOODLAND-KS) |  |  | KS | 0.1032 | 0.007935 |  |  |  | Natural Gas | 9174.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9174.8697 | 0 | 9174.8697 | 0 | 0 | 72.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8026 | 0 | 72.8026 | 0 | 0 | 9.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1749 | 0 | 9.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6676 | 0 | 0 | 0 | 1.6676 | 1.6676 | 0
KY_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 729023.6547 | 879816.4686 | 96263.4427 | 4077910.5986 | 543457.0788 | 595913.6392 | 100789.7278 | 266181.131 | 321457.9366 | 14593.0322 | 0 | 0 | 0 | 7625406.7104 | 0 | 7625406.1547 | 0.55571 | 543457.6346 | 0 | 74360.4128 | 89741.2798 | 9818.8712 | 415946.8811 | 55432.622 | 60783.1912 | 10280.5522 | 27150.4754 | 32788.7095 | 1488.4893 | 0 | 0 | 0 | 777791.4845 | 0 | 777791.4278 | 0.056683 | 55432.6787 | 0 | 2487.4287 | 3001.9338 | 328.4509 | 13913.831 | 1854.2756 | 2033.2573 | 343.8946 | 908.21 | 1096.8145 | 49.7914 | 0 | 0 | 0 | 26017.8877 | 0 | 26017.8858 | 0.0018961 | 1854.2774 | 6.0209 | 0.65876 | 27.9065 | 4.078 | 0.68974 | 0.099865 | 4.9889 | 0 | 0 | 2.1998 | 0 | 52.1831 | 52.1831 | 3.8029e-06
KY_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 789266.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545885.7921 | 0 | 0 | 1335152.0643 | 0 | 1335152.0643 | 0 | 0 | 6565.9061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4541.2239 | 0 | 0 | 11107.13 | 0 | 11107.13 | 0 | 0 | 789.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.8858 | 0 | 0 | 1335.1521 | 0 | 1335.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.583 | 1.0949 | 0 | 0 | 2.6779 | 2.6779 | 0
KY_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 688153.7174 | 716117.2125 | 96263.4427 | 4077910.5986 | 543384.8361 | 571192.7315 | 97183.1483 | 239234.5914 | 321285.6655 | 12717.4997 | 0 | 0 | 0 | 7363443.4436 | 0 | 7363437.8865 | 5.5571 | 543390.3932 | 0 | 70191.6792 | 73043.9557 | 9818.8712 | 415946.8811 | 55425.2533 | 58261.6586 | 9912.6811 | 24401.9283 | 32771.1379 | 1297.185 | 0 | 0 | 0 | 751071.2312 | 0 | 751070.6644 | 0.56683 | 55425.8201 | 0 | 2347.9805 | 2443.3919 | 328.4509 | 13913.831 | 1854.0291 | 1948.9096 | 331.5889 | 816.2684 | 1096.2267 | 43.3921 | 0 | 0 | 0 | 25124.069 | 0 | 25124.0501 | 0.018961 | 1854.048 | 4.9006 | 0.65876 | 27.9065 | 3.9089 | 0.66506 | 0.08703 | 4.7093 | 0 | 0 | 2.1987 | 0 | 50.3904 | 50.3904 | 3.8029e-05
KY_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 744823.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545819.4449 | 0 | 0 | 1290642.5723 | 0 | 1290642.5723 | 0 | 0 | 6196.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4540.672 | 0 | 0 | 10736.8556 | 0 | 10736.8556 | 0 | 0 | 744.8231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.8194 | 0 | 0 | 1290.6426 | 0 | 1290.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4939 | 1.0947 | 0 | 0 | 2.5886 | 2.5886 | 0
KY_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 30892.1044 | 28374.723 | 7207.602 | 142004.2074 | 0 | 21870.0984 | 0 | 0 | 0 | 0 | 109531.0986 | 0 | 0 | 339879.8337 | 0 | 339880.1116 | -0.27786 | -0.27786 | 0 | 3150.9946 | 2894.2217 | 735.1754 | 14484.4292 | 0 | 2230.75 | 0 | 0 | 0 | 0 | 11172.1721 | 0 | 0 | 34667.743 | 0 | 34667.7714 | -0.028341 | -0.028341 | 0 | 105.4039 | 96.8146 | 24.5923 | 484.5184 | 0 | 74.6208 | 0 | 0 | 0 | 0 | 373.7201 | 0 | 0 | 1159.67 | 0 | 1159.6709 | -0.00094805 | -0.00094805 | 2.8693 | 0.72886 | 14.3599 | 2.2116 | 0 | 0 | 3.1239 | 0 | 11.0761 | 0 | 0 | 34.3698 | 34.3698 | -2.8098e-05
KY_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 87682.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87682.5618 | 0 | 87682.5618 | 0 | 0 | 729.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729.4312 | 0 | 729.4312 | 0 | 0 | 87.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6826 | 0 | 87.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5987 | 0 | 0 | 0 | 2.5987 | 2.5987 | 0
KY_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 30047.4201 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 21228.2495 | 0 | 0 | 0 | 0 | 109561.6629 | 0 | 0 | 333230.7237 | 0 | 333231.0015 | -0.27786 | -0.27786 | 0 | 3064.8369 | 2364.5213 | 735.1754 | 14484.4292 | 0 | 2165.2814 | 0 | 0 | 0 | 0 | 11175.2896 | 0 | 0 | 33989.5338 | 0 | 33989.5622 | -0.028341 | -0.028341 | 0 | 102.5218 | 79.0956 | 24.5923 | 484.5184 | 0 | 72.4308 | 0 | 0 | 0 | 0 | 373.8244 | 0 | 0 | 1136.9832 | 0 | 1136.9842 | -0.00094805 | -0.00094805 | 2.3442 | 0.72886 | 14.3599 | 2.1467 | 0 | 0 | 3.0385 | 0 | 11.0792 | 0 | 0 | 33.6974 | 33.6974 | -2.8098e-05
KY_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 101113.1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101113.1304 | 0 | 101113.1304 | 0 | 0 | 841.1601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.1601 | 0 | 841.1601 | 0 | 0 | 101.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1131 | 0 | 101.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9967 | 0 | 0 | 0 | 2.9967 | 2.9967 | 0
KY_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 126558.1552 | 95999.4789 | 7129.8021 | 317887.4784 | 4818.0346 | 92745.7773 | 677.9703 | 0 | 0 | 18396.89 | 7179.8163 | 17652.2341 | 0 | 689045.6373 | 0 | 689046.7487 | -1.1114 | 4816.9232 | 0 | 12908.9318 | 9791.9468 | 727.2398 | 32424.5228 | 491.4395 | 9460.0693 | 69.153 | 0 | 0 | 1876.4828 | 732.3413 | 1800.5279 | 0 | 70282.655 | 0 | 70282.7684 | -0.11337 | 491.3262 | 0 | 431.8164 | 327.5502 | 24.3269 | 1084.6321 | 16.4391 | 316.4486 | 2.3132 | 0 | 0 | 62.7702 | 24.4975 | 60.2294 | 0 | 2351.0237 | 0 | 2351.0275 | -0.0037922 | 16.4353 | 4.4288 | 0.32892 | 14.6653 | 4.2787 | 0.031277 | 0.84872 | 5.8386 | 0 | 0.33123 | 0 | 0.81436 | 31.7883 | 31.7882 | -5.1274e-05
KY_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 344048.1364 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114581.6116 | 0 | 0 | 800820.1629 | 0 | 800820.1629 | 0 | 0 | 2862.1364 | 0 | 0 | 0 | 2846.6821 | 0 | 0 | 0 | 0 | 0 | 0 | 953.2044 | 0 | 0 | 6662.0229 | 0 | 6662.0229 | 0 | 0 | 344.0481 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.5816 | 0 | 0 | 800.8202 | 0 | 800.8202 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.6519 | 1.5493 | 0 | 0 | 10.8279 | 10.8279 | 0
KY_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 120145.2233 | 77816.5385 | 7129.8021 | 312483.1662 | 4743.0133 | 80959.0974 | 433.4564 | 0 | 0 | 22898.168 | 7179.8163 | 12506.3286 | 0 | 646294.6103 | 0 | 646299.8896 | -5.2793 | 4737.7341 | 0 | 12254.8128 | 7937.2869 | 727.2398 | 31873.283 | 483.7874 | 8257.8279 | 44.2126 | 0 | 0 | 2335.6131 | 732.3413 | 1275.6455 | 0 | 65922.0503 | 0 | 65922.5887 | -0.53849 | 483.2489 | 0 | 409.9355 | 265.51 | 24.3269 | 1066.1926 | 16.1832 | 276.2324 | 1.479 | 0 | 0 | 78.1285 | 24.4975 | 42.6716 | 0 | 2205.1572 | 0 | 2205.1752 | -0.018013 | 16.1651 | 3.59 | 0.32892 | 14.416 | 3.7349 | 0.019997 | 1.0564 | 5.5427 | 0 | 0.33123 | 0 | 0.57696 | 29.8162 | 29.8159 | -0.00024355
KY_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 327982.6362 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114363.6137 | 0 | 0 | 784536.6647 | 0 | 784536.6647 | 0 | 0 | 2728.4876 | 0 | 0 | 0 | 2846.6821 | 0 | 0 | 0 | 0 | 0 | 0 | 951.3909 | 0 | 0 | 6526.5605 | 0 | 6526.5605 | 0 | 0 | 327.9826 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.3636 | 0 | 0 | 784.5367 | 0 | 784.5367 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.4347 | 1.5463 | 0 | 0 | 10.6077 | 10.6077 | 0
KY_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 45749.1004 | 83451.4717 | 10680.8103 | 53987.5506 | 0 | 42909.4053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236778.3384 | 0 | 236779.4498 | -1.1114 | -1.1114 | 0 | 4666.4082 | 8512.0501 | 1089.4427 | 5506.7302 | 0 | 4376.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24151.3905 | 0 | 24151.5039 | -0.11337 | -0.11337 | 0 | 156.0959 | 284.7364 | 36.4429 | 184.2055 | 0 | 146.4069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807.8877 | 0 | 807.8915 | -0.0037922 | -0.0037922 | 11.5315 | 1.4759 | 7.4601 | 5.9293 | 0 | 0 | 6.3217 | 0 | 0 | 0 | 0 | 32.7188 | 32.7186 | -0.00015358
KY_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 350881.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89208.5473 | 0 | 0 | 440090.4452 | 0 | 440090.4452 | 0 | 0 | 2918.9865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742.1259 | 0 | 0 | 3661.1124 | 0 | 3661.1124 | 0 | 0 | 350.8819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2085 | 0 | 0 | 440.0904 | 0 | 440.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2103 | 3.6129 | 0 | 0 | 17.8232 | 17.8232 | 0
KY_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 0 | 42828.8268 | 65771.4519 | 10680.8103 | 53987.5506 | 0 | 40900.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214169.1413 | 0 | 214169.4192 | -0.27786 | -0.27786 | 0 | 4368.5403 | 6708.6881 | 1089.4427 | 5506.7302 | 0 | 4171.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21845.2524 | 0 | 21845.2808 | -0.028341 | -0.028341 | 0 | 146.132 | 224.4122 | 36.4429 | 184.2055 | 0 | 139.5525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730.7451 | 0 | 730.7461 | -0.00094805 | -0.00094805 | 9.0885 | 1.4759 | 7.4601 | 5.6517 | 0 | 0 | 5.9182 | 0 | 0 | 0 | 0 | 29.5944 | 29.5944 | -3.8395e-05
KY_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 374179.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89218.0255 | 0 | 0 | 463397.2681 | 0 | 463397.2681 | 0 | 0 | 3112.7971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742.2048 | 0 | 0 | 3855.0019 | 0 | 3855.0019 | 0 | 0 | 374.1792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.218 | 0 | 0 | 463.3973 | 0 | 463.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1539 | 3.6132 | 0 | 0 | 18.7671 | 18.7671 | 0
KY_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 24401.3726 | 79005.765 | 79166.9219 | 12311.829 | 154949.5496 | 0 | 45999.1714 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 395906.8523 | 0 | 395906.5744 | 0.27786 | 0.27786 | 2488.94 | 8058.588 | 8075.026 | 1255.8066 | 15804.8541 | 0 | 4691.9155 | 7.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 40382.4989 | 0 | 40382.4706 | 0.028341 | 0.028341 | 83.2575 | 269.5677 | 270.1175 | 42.008 | 528.6879 | 0 | 156.9492 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.8342 | 0 | 1350.8332 | 0.00094805 | 0.00094805 | 6.2524 | 0.97236 | 12.2376 | 3.6329 | 0.0057056 | 0 | 6.2397 | 1.9272 | 0 | 0 | 0 | 31.2678 | 31.2679 | 2.1945e-05
KY_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 58309.7092 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 567192.721 | 0 | 0 | 1024997.8681 | 0 | 1024997.8681 | 0 | 0 | 485.0785 | 0 | 0 | 0 | 3323.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 4718.4762 | 0 | 0 | 8526.9573 | 0 | 8526.9573 | 0 | 0 | 58.3097 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 567.1927 | 0 | 0 | 1024.9979 | 0 | 1024.9979 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3497 | 13.1289 | 0 | 0 | 23.7257 | 23.7257 | 0
KY_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 27919.038 | 73934.8809 | 50778.3061 | 12311.829 | 154949.5496 | 0 | 43612.3826 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 363578.229 | 0 | 363577.1175 | 1.1114 | 1.1114 | 2847.7419 | 7541.3578 | 5179.3872 | 1255.8066 | 15804.8541 | 0 | 4448.463 | 7.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 37084.9794 | 0 | 37084.866 | 0.11337 | 0.11337 | 95.2598 | 252.2658 | 173.2556 | 42.008 | 528.6879 | 0 | 148.8054 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.5289 | 0 | 1240.5251 | 0.0037922 | 0.0037922 | 4.0104 | 0.97236 | 12.2376 | 3.4444 | 0.0057056 | 0 | 5.8392 | 2.205 | 0 | 0 | 0 | 28.7145 | 28.7146 | 8.7778e-05
KY_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 57466.152 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 567259.0681 | 0 | 0 | 1024220.658 | 0 | 1024220.658 | 0 | 0 | 478.0609 | 0 | 0 | 0 | 3323.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 4719.0282 | 0 | 0 | 8520.4917 | 0 | 8520.4917 | 0 | 0 | 57.4662 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 567.2591 | 0 | 0 | 1024.2207 | 0 | 1024.2207 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3302 | 13.1304 | 0 | 0 | 23.7077 | 23.7077 | 0
KY_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 2967.5092 | 4818.0346 | 8821.9492 | 1597.6758 | 13417.6985 | 0 | 4956.963 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41584.029 | 0 | 41585.974 | -1.945 | -1.945 | 302.6859 | 491.4395 | 899.8388 | 162.9629 | 1368.6052 | 0 | 505.6102 | 0 | 0 | 0 | 0 | 510.4283 | 0 | 0 | 4241.571 | 0 | 4241.7693 | -0.19839 | -0.19839 | 10.1251 | 16.4391 | 30.1005 | 5.4513 | 45.7812 | 0 | 16.9132 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.8847 | 0 | 141.8913 | -0.0066363 | -0.0066363 | 5.4708 | 0.99078 | 8.3208 | 3.074 | 0 | 0 | 2.9878 | 1.8403 | 3.1033 | 0 | 0 | 25.789 | 25.7878 | -0.0012062
KY_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 5051.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5051.8652 | 0 | 5051.8652 | 0 | 0 | 42.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0265 | 0 | 42.0265 | 0 | 0 | 5.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0519 | 0 | 5.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91819 | 0 | 0 | 0 | 0.91819 | 0.91819 | 0
KY_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Electricity | 3017.5234 | 4567.9636 | 7110.3521 | 1597.6758 | 13417.6985 | 0 | 4559.6279 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39275.0401 | 0 | 39275.5958 | -0.55571 | -0.55571 | 307.7874 | 465.9323 | 725.2559 | 162.9629 | 1368.6052 | 0 | 465.082 | 0 | 0 | 0 | 0 | 510.4283 | 0 | 0 | 4006.0541 | 0 | 4006.1108 | -0.056683 | -0.056683 | 10.2958 | 15.5859 | 24.2605 | 5.4513 | 45.7812 | 0 | 15.5575 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.0064 | 0 | 134.0083 | -0.0018961 | -0.0018961 | 4.4094 | 0.99078 | 8.3208 | 2.8276 | 0 | 0 | 2.8328 | 1.8713 | 3.1033 | 0 | 0 | 24.3563 | 24.3559 | -0.00034462
KY_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | KY-LEXINGTON-KY | Zone4A | Zone4A(KY-LEXINGTON-KY) |  |  | KY | 0.102 | 0.008319 |  |  |  | Natural Gas | 5326.7322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5326.7322 | 0 | 5326.7322 | 0 | 0 | 44.3131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.3131 | 0 | 44.3131 | 0 | 0 | 5.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3267 | 0 | 5.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96814 | 0 | 0 | 0 | 0.96814 | 0.96814 | 0
LA_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 1139695.8104 | 882092.1147 | 94371.2388 | 4077910.5986 | 543457.0788 | 568430.8362 | 141501.2869 | 428318.8327 | 128828.2442 | 15626.659 | 0 | 0 | 0 | 8020232.7003 | 0 | 8020233.256 | -0.55571 | 543456.5231 | 0 | 99837.353 | 77271.2692 | 8266.9205 | 357224.9684 | 47606.8401 | 49794.5412 | 12395.5127 | 37520.7297 | 11285.3542 | 1368.8953 | 0 | 0 | 0 | 702572.3845 | 0 | 702572.4332 | -0.04868 | 47606.7914 | 0 | 3888.6421 | 3009.6983 | 321.9947 | 13913.831 | 1854.2756 | 1939.486 | 482.8024 | 1461.4239 | 439.562 | 53.3182 | 0 | 0 | 0 | 27365.034 | 0 | 27365.0359 | -0.0018961 | 1854.2737 | 6.0364 | 0.64581 | 27.9065 | 3.89 | 0.96834 | 0.10694 | 7.7993 | 0 | 0 | 0.88161 | 0 | 54.8851 | 54.8851 | -3.8029e-06
LA_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 415124.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471330.4974 | 0 | 0 | 886455.4397 | 0 | 886455.4397 | 0 | 0 | 3380.7775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3838.5156 | 0 | 0 | 7219.2931 | 0 | 7219.2931 | 0 | 0 | 415.1249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.3305 | 0 | 0 | 886.4554 | 0 | 886.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8326 | 0.94533 | 0 | 0 | 1.7779 | 1.7779 | 0
LA_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 1080253.9333 | 717356.4532 | 94371.2388 | 4077910.5986 | 543387.6147 | 554123.9963 | 138242.0281 | 387568.3737 | 128733.773 | 13765.0193 | 0 | 0 | 0 | 7735713.0292 | 0 | 7735708.0277 | 5.0014 | 543392.6161 | 0 | 94630.2446 | 62840.4253 | 8266.9205 | 357224.9684 | 47600.755 | 48541.2621 | 12110.0017 | 33950.9895 | 11277.0785 | 1205.8157 | 0 | 0 | 0 | 677648.4614 | 0 | 677648.0232 | 0.43812 | 47601.1932 | 0 | 3685.8264 | 2447.6202 | 321.9947 | 13913.831 | 1854.0385 | 1890.6711 | 471.6818 | 1322.3833 | 439.2396 | 46.9662 | 0 | 0 | 0 | 26394.2529 | 0 | 26394.2358 | 0.017065 | 1854.0556 | 4.9091 | 0.64581 | 27.9065 | 3.7921 | 0.94604 | 0.094199 | 7.3925 | 0 | 0 | 0.88097 | 0 | 52.938 | 52.938 | 3.4226e-05
LA_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 275625.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471311.5411 | 0 | 0 | 746936.7596 | 0 | 746936.7596 | 0 | 0 | 2244.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3838.3612 | 0 | 0 | 6083.053 | 0 | 6083.053 | 0 | 0 | 275.6252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.3115 | 0 | 0 | 746.9368 | 0 | 746.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55281 | 0.94529 | 0 | 0 | 1.4981 | 1.4981 | 0
LA_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 55654.6906 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 24356.9155 | 0 | 0 | 0 | 0 | 94738.0096 | 0 | 0 | 352338.9267 | 0 | 352340.5939 | -1.6671 | -1.6671 | 0 | 4875.3509 | 2485.6257 | 631.6293 | 12439.5686 | 0 | 2133.6658 | 0 | 0 | 0 | 0 | 8299.0496 | 0 | 0 | 30864.89 | 0 | 30865.036 | -0.14604 | -0.14604 | 0 | 189.8938 | 96.8146 | 24.6018 | 484.5184 | 0 | 83.1058 | 0 | 0 | 0 | 0 | 323.2461 | 0 | 0 | 1202.1804 | 0 | 1202.1861 | -0.0056883 | -0.0056883 | 2.8693 | 0.72914 | 14.3599 | 2.4631 | 0 | 0 | 5.628 | 0 | 9.5802 | 0 | 0 | 35.6298 | 35.6297 | -0.00016859
LA_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 49495.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49495.01 | 0 | 49495.01 | 0 | 0 | 403.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403.0874 | 0 | 403.0874 | 0 | 0 | 49.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.495 | 0 | 49.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4669 | 0 | 0 | 0 | 1.4669 | 1.4669 | 0
LA_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 50022.536 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 23431.6528 | 0 | 0 | 0 | 0 | 94637.9812 | 0 | 0 | 340488.3398 | 0 | 340491.3962 | -3.0564 | -3.0564 | 0 | 4381.9742 | 2030.7066 | 631.6293 | 12439.5686 | 0 | 2052.6128 | 0 | 0 | 0 | 0 | 8290.2872 | 0 | 0 | 29826.7786 | 0 | 29827.0463 | -0.26774 | -0.26774 | 0 | 170.6769 | 79.0956 | 24.6018 | 484.5184 | 0 | 79.9488 | 0 | 0 | 0 | 0 | 322.9048 | 0 | 0 | 1161.7462 | 0 | 1161.7566 | -0.010429 | -0.010429 | 2.3442 | 0.72914 | 14.3599 | 2.3695 | 0 | 0 | 5.0584 | 0 | 9.5701 | 0 | 0 | 34.4316 | 34.4313 | -0.00030908
LA_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 12985.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12985.0945 | 0 | 12985.0945 | 0 | 0 | 105.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7506 | 0 | 105.7506 | 0 | 0 | 12.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9851 | 0 | 12.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38485 | 0 | 0 | 0 | 0.38485 | 0.38485 | 0
LA_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 227478.4757 | 100678.5852 | 7082.5665 | 317887.4784 | 4818.0346 | 96113.4001 | 266.7424 | 0 | 0 | 24298.5656 | 7179.8163 | 17749.484 | 0 | 803553.1488 | 0 | 803552.3153 | 0.83357 | 4818.8682 | 0 | 19927.1145 | 8819.4441 | 620.4328 | 27846.9431 | 422.0598 | 8419.5338 | 23.3666 | 0 | 0 | 2128.5543 | 628.9519 | 1554.8548 | 0 | 70391.2558 | 0 | 70391.1828 | 0.073021 | 422.1329 | 0 | 776.1566 | 343.5153 | 24.1657 | 1084.6321 | 16.4391 | 327.9389 | 0.91013 | 0 | 0 | 82.9067 | 24.4975 | 60.5612 | 0 | 2741.7233 | 0 | 2741.7205 | 0.0028441 | 16.442 | 4.6447 | 0.32674 | 14.6653 | 4.4341 | 0.012306 | 1.121 | 10.4944 | 0 | 0.33123 | 0 | 0.81885 | 37.0708 | 37.0709 | 3.8456e-05
LA_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 133225.1744 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 98895.2383 | 0 | 0 | 574310.8275 | 0 | 574310.8275 | 0 | 0 | 1084.9858 | 0 | 0 | 0 | 2786.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 805.4028 | 0 | 0 | 4677.1874 | 0 | 4677.1874 | 0 | 0 | 133.2252 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8952 | 0 | 0 | 574.3108 | 0 | 574.3108 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.8013 | 1.3372 | 0 | 0 | 7.7653 | 7.7653 | 0
LA_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 210351.3907 | 81148.04 | 7082.5665 | 312483.1662 | 4745.7919 | 85996.6388 | 197.2782 | 0 | 0 | 23023.2035 | 7179.8163 | 12550.7857 | 0 | 744758.6778 | 0 | 744757.8443 | 0.83357 | 4746.6255 | 0 | 18426.7818 | 7108.5683 | 620.4328 | 27373.5254 | 415.7314 | 7533.3056 | 17.2816 | 0 | 0 | 2016.8326 | 628.9519 | 1099.4488 | 0 | 65240.8602 | 0 | 65240.7872 | 0.073021 | 415.8044 | 0 | 717.7189 | 276.8771 | 24.1657 | 1066.1926 | 16.1926 | 293.4205 | 0.67311 | 0 | 0 | 78.5552 | 24.4975 | 42.8233 | 0 | 2541.1166 | 0 | 2541.1138 | 0.0028441 | 16.1955 | 3.7437 | 0.32674 | 14.416 | 3.9673 | 0.0091012 | 1.0621 | 9.7043 | 0 | 0.33123 | 0 | 0.57901 | 34.3584 | 34.3585 | 3.8456e-05
LA_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 111548.5969 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 98658.284 | 0 | 0 | 552397.2957 | 0 | 552397.2957 | 0 | 0 | 908.4518 | 0 | 0 | 0 | 2786.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 803.4731 | 0 | 0 | 4498.7236 | 0 | 4498.7236 | 0 | 0 | 111.5486 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6583 | 0 | 0 | 552.3973 | 0 | 552.3973 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.5082 | 1.334 | 0 | 0 | 7.469 | 7.469 | 0
LA_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 87113.6226 | 83081.9224 | 10686.3675 | 53987.5506 | 0 | 37338.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272207.8422 | 0 | 272208.12 | -0.27786 | -0.27786 | 0 | 7631.1533 | 7277.9764 | 936.1258 | 4729.3094 | 0 | 3270.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23845.407 | 0 | 23845.4313 | -0.02434 | -0.02434 | 0 | 297.2317 | 283.4755 | 36.4619 | 184.2055 | 0 | 127.3985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928.7732 | 0 | 928.7741 | -0.00094805 | -0.00094805 | 11.4805 | 1.4767 | 7.4601 | 5.1595 | 0 | 0 | 12.0376 | 0 | 0 | 0 | 0 | 37.6144 | 37.6143 | -3.8395e-05
LA_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 77085.9664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84696.9378 | 0 | 0 | 161782.9042 | 0 | 161782.9042 | 0 | 0 | 627.7881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689.7719 | 0 | 0 | 1317.56 | 0 | 1317.56 | 0 | 0 | 77.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6969 | 0 | 0 | 161.7829 | 0 | 161.7829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1219 | 3.4301 | 0 | 0 | 6.552 | 6.552 | 0
LA_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 81889.9173 | 65507.4881 | 10686.3675 | 53987.5506 | 0 | 35521.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247592.5199 | 0 | 247591.1307 | 1.3893 | 1.3893 | 0 | 7173.5568 | 5738.456 | 936.1258 | 4729.3094 | 0 | 3111.6568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21689.1047 | 0 | 21688.983 | 0.1217 | 0.1217 | 0 | 279.4084 | 223.5115 | 36.4619 | 184.2055 | 0 | 121.1983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 844.7857 | 0 | 844.7809 | 0.0047402 | 0.0047402 | 9.052 | 1.4767 | 7.4601 | 4.9084 | 0 | 0 | 11.3157 | 0 | 0 | 0 | 0 | 34.2127 | 34.2129 | 0.00019197
LA_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 85038.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84706.416 | 0 | 0 | 169744.568 | 0 | 169744.568 | 0 | 0 | 692.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689.8491 | 0 | 0 | 1382.3998 | 0 | 1382.3998 | 0 | 0 | 85.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7064 | 0 | 0 | 169.7446 | 0 | 169.7446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.444 | 3.4305 | 0 | 0 | 6.8745 | 6.8745 | 0
LA_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 5565.4691 | 119928.4951 | 80150.5345 | 12317.3861 | 154949.5496 | 0 | 46477.0849 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 419460.7621 | 0 | 419461.0399 | -0.27786 | -0.27786 | 487.5351 | 10505.7362 | 7021.1868 | 1079.003 | 13573.5805 | 0 | 4071.3926 | 6.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 36744.7628 | 0 | 36744.7871 | -0.02434 | -0.02434 | 18.9894 | 409.196 | 273.4736 | 42.0269 | 528.6879 | 0 | 158.5798 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1431.2001 | 0 | 1431.2011 | -0.00094805 | -0.00094805 | 6.3301 | 0.9728 | 12.2376 | 3.6707 | 0.0057056 | 0 | 9.4717 | 0.43955 | 0 | 0 | 0 | 33.1281 | 33.1281 | -2.1945e-05
LA_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 12463.7951 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 482533.6958 | 0 | 0 | 894492.9288 | 0 | 894492.9288 | 0 | 0 | 101.5051 | 0 | 0 | 0 | 3253.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 3929.7544 | 0 | 0 | 7284.7504 | 0 | 7284.7504 | 0 | 0 | 12.4638 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 482.5337 | 0 | 0 | 894.4929 | 0 | 894.4929 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.2885 | 11.1692 | 0 | 0 | 20.7049 | 20.7049 | 0
LA_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 6374.032 | 113471.1062 | 51356.248 | 12317.3861 | 154949.5496 | 0 | 44265.3458 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 382805.9104 | 0 | 382806.1883 | -0.27786 | -0.27786 | 558.3652 | 9940.0689 | 4498.8073 | 1079.003 | 13573.5805 | 0 | 3877.6443 | 6.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 33533.7978 | 0 | 33533.8221 | -0.02434 | -0.02434 | 21.7482 | 387.1634 | 175.2275 | 42.0269 | 528.6879 | 0 | 151.0334 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.1338 | 0 | 1306.1347 | -0.00094805 | -0.00094805 | 4.056 | 0.9728 | 12.2376 | 3.496 | 0.0057056 | 0 | 8.9617 | 0.50341 | 0 | 0 | 0 | 30.2332 | 30.2332 | -2.1945e-05
LA_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 13136.7453 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 482552.6521 | 0 | 0 | 895184.8353 | 0 | 895184.8353 | 0 | 0 | 106.9857 | 0 | 0 | 0 | 3253.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 3929.9088 | 0 | 0 | 7290.3853 | 0 | 7290.3853 | 0 | 0 | 13.1367 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 482.5527 | 0 | 0 | 895.1848 | 0 | 895.1848 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.30408 | 11.1697 | 0 | 0 | 20.7209 | 20.7209 | 0
LA_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 627.9561 | 8674.6852 | 9019.2275 | 1564.333 | 13417.6985 | 0 | 5101.4484 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43409.5473 | 0 | 43412.048 | -2.5007 | -2.5007 | 55.009 | 759.9024 | 790.0843 | 137.0356 | 1175.3904 | 0 | 446.8869 | 0 | 0 | 0 | 0 | 438.3678 | 0 | 0 | 3802.6763 | 0 | 3802.8954 | -0.21906 | -0.21906 | 2.1426 | 29.598 | 30.7736 | 5.3375 | 45.7812 | 0 | 17.4061 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 148.1134 | 0 | 148.1219 | -0.0085324 | -0.0085324 | 5.5932 | 0.9701 | 8.3208 | 3.1636 | 0 | 0 | 5.3795 | 0.38942 | 3.1033 | 0 | 0 | 26.9215 | 26.9199 | -0.0015508
LA_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 369.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6487 | 0 | 369.6487 | 0 | 0 | 3.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0104 | 0 | 3.0104 | 0 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36965 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067184 | 0 | 0 | 0 | 0.067184 | 0.067184 | 0
LA_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 608.5061 | 8307.9144 | 7238.1662 | 1564.333 | 13417.6985 | 0 | 4667.992 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40808.8089 | 0 | 40809.6424 | -0.83357 | -0.83357 | 53.3051 | 727.7733 | 634.0634 | 137.0356 | 1175.3904 | 0 | 408.9161 | 0 | 0 | 0 | 0 | 438.3678 | 0 | 0 | 3574.8517 | 0 | 3574.9247 | -0.073021 | -0.073021 | 2.0762 | 28.3466 | 24.6966 | 5.3375 | 45.7812 | 0 | 15.9272 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.2397 | 0 | 139.2425 | -0.0028441 | -0.0028441 | 4.4887 | 0.9701 | 8.3208 | 2.8948 | 0 | 0 | 5.1521 | 0.37736 | 3.1033 | 0 | 0 | 25.3076 | 25.3071 | -0.00051693
LA_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | LA-BATONROUGE-LA | Zone2A | Zone2A(LA-BATONROUGE-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 369.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6487 | 0 | 369.6487 | 0 | 0 | 3.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0104 | 0 | 3.0104 | 0 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36965 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067184 | 0 | 0 | 0 | 0.067184 | 0.067184 | 0
LA_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 1067122.4272 | 881536.4014 | 95018.6448 | 4077910.5986 | 543457.0788 | 579270.0248 | 133426.7721 | 391450.0313 | 196097.3436 | 14356.854 | 0 | 0 | 0 | 7979646.1768 | 0 | 7979646.1768 | 0 | 543457.0788 | 0 | 93479.9246 | 77222.5888 | 8323.6333 | 357224.9684 | 47606.8401 | 50744.0542 | 11688.1852 | 34291.0227 | 17178.1273 | 1257.6604 | 0 | 0 | 0 | 699017.0051 | 0 | 699017.0051 | 0 | 47606.8401 | 0 | 3641.0217 | 3007.8022 | 324.2036 | 13913.831 | 1854.2756 | 1976.4693 | 455.2521 | 1335.6275 | 669.0841 | 48.9856 | 0 | 0 | 0 | 27226.5528 | 0 | 27226.5528 | 0 | 1854.2756 | 6.0326 | 0.65024 | 27.9065 | 3.9641 | 0.91308 | 0.098249 | 7.3027 | 0 | 0 | 1.342 | 0 | 54.6073 | 54.6073 | 0
LA_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 516323.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483680.5545 | 0 | 0 | 1000003.9306 | 0 | 1000003.9306 | 0 | 0 | 4204.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3939.0944 | 0 | 0 | 8144.032 | 0 | 8144.032 | 0 | 0 | 516.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.6806 | 0 | 0 | 1000.0039 | 0 | 1000.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0356 | 0.9701 | 0 | 0 | 2.0057 | 2.0057 | 0
LA_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 1001501.0179 | 717036.9181 | 95018.6448 | 4077910.5986 | 543384.8361 | 564068.4865 | 126435.8983 | 353889.3669 | 196055.6651 | 13667.7695 | 0 | 0 | 0 | 7688969.2019 | 0 | 7688967.5347 | 1.6671 | 543386.5032 | 0 | 87731.4892 | 62812.434 | 8323.6333 | 357224.9684 | 47600.5116 | 49412.3994 | 11075.7847 | 31000.7085 | 17174.4763 | 1197.2966 | 0 | 0 | 0 | 673553.7021 | 0 | 673553.556 | 0.14604 | 47600.6577 | 0 | 3417.1215 | 2446.53 | 324.2036 | 13913.831 | 1854.0291 | 1924.6017 | 431.3993 | 1207.4705 | 668.9419 | 46.6344 | 0 | 0 | 0 | 26234.7629 | 0 | 26234.7572 | 0.0056883 | 1854.0347 | 4.9069 | 0.65024 | 27.9065 | 3.8601 | 0.86524 | 0.093533 | 6.8536 | 0 | 0 | 1.3417 | 0 | 52.6181 | 52.6181 | 1.1409e-05
LA_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 288676.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483623.6855 | 0 | 0 | 772300.3457 | 0 | 772300.3457 | 0 | 0 | 2350.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3938.6313 | 0 | 0 | 6289.614 | 0 | 6289.614 | 0 | 0 | 288.6767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.6237 | 0 | 0 | 772.3003 | 0 | 772.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57899 | 0.96999 | 0 | 0 | 1.549 | 1.549 | 0
LA_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 52456.5604 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 24748.6934 | 0 | 0 | 0 | 0 | 97283.1767 | 0 | 0 | 352083.2986 | 0 | 352081.6315 | 1.6671 | 1.6671 | 0 | 4595.1947 | 2485.6257 | 632.1161 | 12439.5686 | 0 | 2167.9855 | 0 | 0 | 0 | 0 | 8522.0063 | 0 | 0 | 30842.497 | 0 | 30842.3509 | 0.14604 | 0.14604 | 0 | 178.9818 | 96.8146 | 24.6208 | 484.5184 | 0 | 84.4425 | 0 | 0 | 0 | 0 | 331.9302 | 0 | 0 | 1201.3082 | 0 | 1201.3025 | 0.0056883 | 0.0056883 | 2.8693 | 0.7297 | 14.3599 | 2.5027 | 0 | 0 | 5.3046 | 0 | 9.8376 | 0 | 0 | 35.6036 | 35.6038 | 0.00016859
LA_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 74384.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74384.6876 | 0 | 74384.6876 | 0 | 0 | 605.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.7889 | 0 | 605.7889 | 0 | 0 | 74.3847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3847 | 0 | 74.3847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2046 | 0 | 0 | 0 | 2.2046 | 2.2046 | 0
LA_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 47682.9828 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 23617.8168 | 0 | 0 | 0 | 0 | 97160.9197 | 0 | 0 | 340863.4463 | 0 | 340861.2235 | 2.2229 | 2.2229 | 0 | 4177.0293 | 2030.7066 | 632.1161 | 12439.5686 | 0 | 2068.9208 | 0 | 0 | 0 | 0 | 8511.2966 | 0 | 0 | 29859.6379 | 0 | 29859.4432 | 0.19472 | 0.19472 | 0 | 162.6943 | 79.0956 | 24.6208 | 484.5184 | 0 | 80.584 | 0 | 0 | 0 | 0 | 331.5131 | 0 | 0 | 1163.0261 | 0 | 1163.0185 | 0.0075844 | 0.0075844 | 2.3442 | 0.7297 | 14.3599 | 2.3883 | 0 | 0 | 4.8219 | 0 | 9.8252 | 0 | 0 | 34.469 | 34.4692 | 0.00022478
LA_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 20870.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20870.933 | 0 | 20870.933 | 0 | 0 | 169.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9729 | 0 | 169.9729 | 0 | 0 | 20.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8709 | 0 | 20.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61856 | 0 | 0 | 0 | 0.61856 | 0.61856 | 0
LA_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 206186.3192 | 99903.3651 | 7102.0164 | 317887.4784 | 4818.0346 | 97319.2981 | 363.9922 | 0 | 0 | 21608.9131 | 7179.8163 | 17710.584 | 0 | 780079.8175 | 0 | 780084.2632 | -4.4457 | 4813.5889 | 0 | 18061.9216 | 8751.5348 | 622.1366 | 27846.9431 | 422.0598 | 8525.1705 | 31.8857 | 0 | 0 | 1892.9408 | 628.9519 | 1551.4472 | 0 | 68334.992 | 0 | 68335.3815 | -0.38944 | 421.6704 | 0 | 703.5077 | 340.8703 | 24.2321 | 1084.6321 | 16.4391 | 332.0534 | 1.2419 | 0 | 0 | 73.7296 | 24.4975 | 60.4285 | 0 | 2661.6323 | 0 | 2661.6475 | -0.015169 | 16.424 | 4.6089 | 0.32764 | 14.6653 | 4.4897 | 0.016792 | 0.9969 | 9.5121 | 0 | 0.33123 | 0 | 0.81705 | 35.9881 | 35.9879 | -0.0002051
LA_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 206917.9555 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102089.382 | 0 | 0 | 651197.7523 | 0 | 651197.7523 | 0 | 0 | 1685.1398 | 0 | 0 | 0 | 2786.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 831.4159 | 0 | 0 | 5303.3545 | 0 | 5303.3545 | 0 | 0 | 206.918 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0894 | 0 | 0 | 651.1978 | 0 | 651.1978 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.7977 | 1.3804 | 0 | 0 | 8.8048 | 8.8048 | 0
LA_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 189448.2335 | 80486.7411 | 7102.0164 | 312483.1662 | 4745.7919 | 86071.6601 | 266.7424 | 0 | 0 | 23078.7749 | 7179.8163 | 12534.1143 | 0 | 723397.0572 | 0 | 723397.0572 | 0 | 4745.7919 | 0 | 16595.6653 | 7050.6385 | 622.1366 | 27373.5254 | 415.7314 | 7539.8774 | 23.3666 | 0 | 0 | 2021.7007 | 628.9519 | 1097.9884 | 0 | 63369.5822 | 0 | 63369.5822 | 0 | 415.7314 | 0 | 646.3974 | 274.6208 | 24.2321 | 1066.1926 | 16.1926 | 293.6765 | 0.91013 | 0 | 0 | 78.7448 | 24.4975 | 42.7664 | 0 | 2468.2308 | 0 | 2468.2308 | 0 | 16.1926 | 3.7131 | 0.32764 | 14.416 | 3.9708 | 0.012306 | 1.0647 | 8.7399 | 0 | 0.33123 | 0 | 0.57824 | 33.373 | 33.373 | 0
LA_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 172019.3291 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 101833.4714 | 0 | 0 | 616043.2153 | 0 | 616043.2153 | 0 | 0 | 1400.9254 | 0 | 0 | 0 | 2786.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 829.3318 | 0 | 0 | 5017.0559 | 0 | 5017.0559 | 0 | 0 | 172.0193 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8335 | 0 | 0 | 616.0432 | 0 | 616.0432 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.3259 | 1.3769 | 0 | 0 | 8.3295 | 8.3295 | 0
LA_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 78994.6508 | 82440.0735 | 10691.9246 | 53987.5506 | 0 | 37899.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264013.849 | 0 | 264015.794 | -1.945 | -1.945 | 0 | 6919.9314 | 7221.7504 | 936.6126 | 4729.3094 | 0 | 3320.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127.6132 | 0 | 23127.7836 | -0.17038 | -0.17038 | 0 | 269.5297 | 281.2855 | 36.4808 | 184.2055 | 0 | 129.3136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900.8153 | 0 | 900.8219 | -0.0066363 | -0.0066363 | 11.3918 | 1.4774 | 7.4601 | 5.2371 | 0 | 0 | 10.9157 | 0 | 0 | 0 | 0 | 36.4823 | 36.4821 | -0.00026876
LA_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 106970.6402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85464.6697 | 0 | 0 | 192435.3099 | 0 | 192435.3099 | 0 | 0 | 871.1689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.0243 | 0 | 0 | 1567.1932 | 0 | 1567.1932 | 0 | 0 | 106.9706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4647 | 0 | 0 | 192.4353 | 0 | 192.4353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3322 | 3.4612 | 0 | 0 | 7.7934 | 7.7934 | 0
LA_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 0 | 74290.5374 | 65068.4746 | 10691.9246 | 53987.5506 | 0 | 35976.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240015.3686 | 0 | 240013.7015 | 1.6671 | 1.6671 | 0 | 6507.8511 | 5699.9984 | 936.6126 | 4729.3094 | 0 | 3151.5748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21025.3463 | 0 | 21025.2002 | 0.14604 | 0.14604 | 0 | 253.4793 | 222.0136 | 36.4808 | 184.2055 | 0 | 122.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 818.9324 | 0 | 818.9267 | 0.0056883 | 0.0056883 | 8.9913 | 1.4774 | 7.4601 | 4.9714 | 0 | 0 | 10.2656 | 0 | 0 | 0 | 0 | 33.1657 | 33.1659 | 0.00023037
LA_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 120003.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85474.1479 | 0 | 0 | 205477.2734 | 0 | 205477.2734 | 0 | 0 | 977.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.1015 | 0 | 0 | 1673.4069 | 0 | 1673.4069 | 0 | 0 | 120.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4741 | 0 | 0 | 205.4773 | 0 | 205.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.86 | 3.4616 | 0 | 0 | 8.3216 | 8.3216 | 0
LA_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 7441.0016 | 113043.2069 | 80036.6133 | 12322.9432 | 154949.5496 | 0 | 46624.3489 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 414489.9063 | 0 | 414486.0163 | 3.89 | 3.89 | 651.8317 | 9902.5849 | 7011.2073 | 1079.4898 | 13573.5805 | 0 | 4084.293 | 6.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 36309.3158 | 0 | 36308.975 | 0.34076 | 0.34076 | 25.3887 | 385.7034 | 273.0849 | 42.0459 | 528.6879 | 0 | 159.0823 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.2396 | 0 | 1414.2263 | 0.013273 | 0.013273 | 6.3211 | 0.97324 | 12.2376 | 3.6823 | 0.0057056 | 0 | 8.9279 | 0.58767 | 0 | 0 | 0 | 32.7352 | 32.7355 | 0.00030722
LA_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 18131.7415 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 497035.2977 | 0 | 0 | 914662.4771 | 0 | 914662.4771 | 0 | 0 | 147.6649 | 0 | 0 | 0 | 3253.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 4047.8555 | 0 | 0 | 7449.0112 | 0 | 7449.0112 | 0 | 0 | 18.1317 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 497.0353 | 0 | 0 | 914.6625 | 0 | 914.6625 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.4197 | 11.5049 | 0 | 0 | 21.1718 | 21.1718 | 0
LA_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 8719.1422 | 106746.9748 | 51275.6696 | 12322.9432 | 154949.5496 | 0 | 44329.2529 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378415.775 | 0 | 378414.3858 | 1.3893 | 1.3893 | 763.7969 | 9351.035 | 4491.7487 | 1079.4898 | 13573.5805 | 0 | 3883.2425 | 6.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 33149.2219 | 0 | 33149.1002 | 0.1217 | 0.1217 | 29.7497 | 364.2207 | 174.9526 | 42.0459 | 528.6879 | 0 | 151.2514 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1291.1546 | 0 | 1291.1499 | 0.0047402 | 0.0047402 | 4.0496 | 0.97324 | 12.2376 | 3.501 | 0.0057056 | 0 | 8.4306 | 0.68862 | 0 | 0 | 0 | 29.8863 | 29.8865 | 0.00010972
LA_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 19449.2073 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 497092.1668 | 0 | 0 | 916036.812 | 0 | 916036.812 | 0 | 0 | 158.3943 | 0 | 0 | 0 | 3253.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 4048.3186 | 0 | 0 | 7460.2038 | 0 | 7460.2038 | 0 | 0 | 19.4492 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 497.0922 | 0 | 0 | 916.0368 | 0 | 916.0368 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.45019 | 11.5062 | 0 | 0 | 21.2036 | 21.2036 | 0
LA_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 1005.8411 | 7932.8079 | 8996.9989 | 1575.4473 | 13417.6985 | 0 | 5265.3839 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43198.3762 | 0 | 43199.7655 | -1.3893 | -1.3893 | 88.1117 | 694.914 | 788.1371 | 138.0092 | 1175.3904 | 0 | 461.2476 | 0 | 0 | 0 | 0 | 438.3678 | 0 | 0 | 3784.1778 | 0 | 3784.2995 | -0.1217 | -0.1217 | 3.4319 | 27.0667 | 30.6978 | 5.3754 | 45.7812 | 0 | 17.9655 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 147.3929 | 0 | 147.3976 | -0.0047402 | -0.0047402 | 5.5794 | 0.97699 | 8.3208 | 3.2653 | 0 | 0 | 4.9194 | 0.62376 | 3.1033 | 0 | 0 | 26.7898 | 26.789 | -0.00086155
LA_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 729.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729.8192 | 0 | 729.8192 | 0 | 0 | 5.9436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9436 | 0 | 5.9436 | 0 | 0 | 0.72982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72982 | 0 | 0.72982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13265 | 0 | 0 | 0 | 0.13265 | 0.13265 | 0
LA_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Electricity | 1028.0697 | 7563.2585 | 7224.2734 | 1575.4473 | 13417.6985 | 0 | 4845.8203 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40658.7663 | 0 | 40658.2105 | 0.55571 | 0.55571 | 90.0589 | 662.5414 | 632.8463 | 138.0092 | 1175.3904 | 0 | 424.4939 | 0 | 0 | 0 | 0 | 438.3678 | 0 | 0 | 3561.7079 | 0 | 3561.6592 | 0.04868 | 0.04868 | 3.5078 | 25.8058 | 24.6492 | 5.3754 | 45.7812 | 0 | 16.5339 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.7277 | 0 | 138.7258 | 0.0018961 | 0.0018961 | 4.48 | 0.97699 | 8.3208 | 3.0051 | 0 | 0 | 4.6903 | 0.63755 | 3.1033 | 0 | 0 | 25.2137 | 25.2141 | 0.00034462
LA_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | LA-SHREVEPORT-LA | Zone3A | Zone3A(LA-SHREVEPORT-LA) |  |  | LA | 0.0876 | 0.008144 |  |  |  | Natural Gas | 777.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777.21 | 0 | 777.21 | 0 | 0 | 6.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3296 | 0 | 6.3296 | 0 | 0 | 0.77721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77721 | 0 | 0.77721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14126 | 0 | 0 | 0 | 0.14126 | 0.14126 | 0
MA_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 552982.0054 | 882036.5434 | 96157.8572 | 4077910.5986 | 543459.8574 | 574071.3265 | 84440.6415 | 189701.0831 | 397251.6786 | 10869.7529 | 0 | 0 | 0 | 7408881.3446 | 0 | 7408879.6774 | 1.6671 | 543461.5245 | 0 | 88421.8227 | 141037.6433 | 15375.6414 | 652057.9047 | 86899.2312 | 91794.0051 | 13502.0586 | 30333.2032 | 63520.5434 | 1738.0735 | 0 | 0 | 0 | 1184680.127 | 0 | 1184679.8604 | 0.26658 | 86899.4978 | 0 | 1886.7746 | 3009.5087 | 328.0906 | 13913.831 | 1854.285 | 1958.7314 | 288.1115 | 647.2601 | 1355.4227 | 37.0876 | 0 | 0 | 0 | 25279.1031 | 0 | 25279.0975 | 0.0056883 | 1854.2907 | 6.0361 | 0.65804 | 27.9065 | 3.9286 | 0.57785 | 0.074385 | 3.7842 | 0 | 0 | 2.7185 | 0 | 50.7014 | 50.7014 | 1.1409e-05
MA_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 1058815.9829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568661.8375 | 0 | 0 | 1627477.8204 | 0 | 1627477.8204 | 0 | 0 | 11115.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5969.812 | 0 | 0 | 17085.2622 | 0 | 17085.2622 | 0 | 0 | 1058.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.6618 | 0 | 0 | 1627.4778 | 0 | 1627.4778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1236 | 1.1405 | 0 | 0 | 3.2642 | 3.2642 | 0
MA_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 516643.9104 | 718237.2589 | 96157.8572 | 4077910.5986 | 543387.6147 | 555691.1079 | 80411.7198 | 170365.0376 | 396982.1576 | 10294.5896 | 0 | 0 | 0 | 7166081.8522 | 0 | 7166080.4629 | 1.3893 | 543389.004 | 0 | 82611.3613 | 114846.1377 | 15375.6414 | 652057.9047 | 86887.6796 | 88855.0082 | 12857.834 | 27241.3695 | 63477.447 | 1646.1049 | 0 | 0 | 0 | 1145856.4882 | 0 | 1145856.266 | 0.22215 | 86887.9017 | 0 | 1762.789 | 2450.6255 | 328.0906 | 13913.831 | 1854.0385 | 1896.0181 | 274.3648 | 581.2855 | 1354.5031 | 35.1251 | 0 | 0 | 0 | 24450.6713 | 0 | 24450.6665 | 0.0047402 | 1854.0433 | 4.9151 | 0.65804 | 27.9065 | 3.8028 | 0.55028 | 0.070449 | 3.5356 | 0 | 0 | 2.7167 | 0 | 49.0398 | 49.0398 | 9.5073e-06
MA_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 945002.1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568671.3157 | 0 | 0 | 1513673.4188 | 0 | 1513673.4188 | 0 | 0 | 9920.6321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5969.9115 | 0 | 0 | 15890.5436 | 0 | 15890.5436 | 0 | 0 | 945.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.6713 | 0 | 0 | 1513.6734 | 0 | 1513.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8954 | 1.1406 | 0 | 0 | 3.0359 | 3.0359 | 0
MA_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 22664.7684 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 19813.959 | 0 | 0 | 0 | 0 | 114079.6123 | 0 | 0 | 334142.0935 | 0 | 334141.5378 | 0.55571 | 0.55571 | 0 | 3624.0965 | 4537.1182 | 1152.0513 | 22706.4728 | 0 | 3168.252 | 0 | 0 | 0 | 0 | 18241.33 | 0 | 0 | 53429.3208 | 0 | 53429.2319 | 0.088859 | 0.088859 | 0 | 77.3322 | 96.8146 | 24.5829 | 484.5184 | 0 | 67.6052 | 0 | 0 | 0 | 0 | 389.2396 | 0 | 0 | 1140.0928 | 0 | 1140.0909 | 0.0018961 | 0.0018961 | 2.8693 | 0.72858 | 14.3599 | 2.0037 | 0 | 0 | 2.2919 | 0 | 11.5361 | 0 | 0 | 33.7895 | 33.7895 | 5.6196e-05
MA_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 130618.6773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130618.6773 | 0 | 130618.6773 | 0 | 0 | 1371.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.2349 | 0 | 1371.2349 | 0 | 0 | 130.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.6187 | 0 | 130.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8712 | 0 | 0 | 0 | 3.8712 | 3.8712 | 0
MA_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 21531.1132 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19263.8028 | 0 | 0 | 0 | 0 | 114112.9551 | 0 | 0 | 327298.4838 | 0 | 327301.8181 | -3.3343 | -3.3343 | 0 | 3442.825 | 3706.7349 | 1152.0513 | 22706.4728 | 0 | 3080.2821 | 0 | 0 | 0 | 0 | 18246.6615 | 0 | 0 | 52335.0276 | 0 | 52335.5607 | -0.53315 | -0.53315 | 0 | 73.4642 | 79.0956 | 24.5829 | 484.5184 | 0 | 65.7281 | 0 | 0 | 0 | 0 | 389.3534 | 0 | 0 | 1116.7424 | 0 | 1116.7538 | -0.011377 | -0.011377 | 2.3442 | 0.72858 | 14.3599 | 1.948 | 0 | 0 | 2.1773 | 0 | 11.5395 | 0 | 0 | 33.0978 | 33.0975 | -0.00033717
MA_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 147887.9052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147887.9052 | 0 | 147887.9052 | 0 | 0 | 1552.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1552.5272 | 0 | 1552.5272 | 0 | 0 | 147.8879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.8879 | 0 | 147.8879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.383 | 0 | 0 | 0 | 4.383 | 4.383 | 0
MA_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 80383.9341 | 98653.0101 | 7160.3663 | 317887.4784 | 4818.0346 | 90659.0737 | 600.1704 | 0 | 0 | 20322.4367 | 7179.8163 | 17607.7771 | 0 | 645272.0978 | 0 | 645269.8749 | 2.2229 | 4820.2575 | 0 | 12853.3911 | 15774.6163 | 1144.9426 | 50830.2078 | 770.4037 | 14496.3859 | 95.9672 | 0 | 0 | 3249.5576 | 1148.0526 | 2815.4836 | 0 | 103179.0084 | 0 | 103178.653 | 0.35543 | 770.7592 | 0 | 274.27 | 336.6041 | 24.4312 | 1084.6321 | 16.4391 | 309.3288 | 2.0478 | 0 | 0 | 69.3402 | 24.4975 | 60.0777 | 0 | 2201.6684 | 0 | 2201.6608 | 0.0075844 | 16.4467 | 4.5512 | 0.33033 | 14.6653 | 4.1824 | 0.027688 | 0.93755 | 3.7084 | 0 | 0.33123 | 0 | 0.81231 | 29.7687 | 29.7688 | 0.00010255
MA_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 443180.329 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119045.8303 | 0 | 0 | 904416.5741 | 0 | 904416.5741 | 0 | 0 | 4652.5071 | 0 | 0 | 0 | 3592.315 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7431 | 0 | 0 | 9494.5652 | 0 | 9494.5652 | 0 | 0 | 443.1803 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.0458 | 0 | 0 | 904.4166 | 0 | 904.4166 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.9922 | 1.6096 | 0 | 0 | 12.2286 | 12.2286 | 0
MA_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 76374.4624 | 80475.6268 | 7160.3663 | 312483.1662 | 4745.7919 | 78488.9516 | 530.7062 | 0 | 0 | 22586.9686 | 7179.8163 | 12486.8787 | 0 | 602512.7351 | 0 | 602512.4573 | 0.27786 | 4746.0698 | 0 | 12212.2765 | 12868.0527 | 1144.9426 | 49966.0583 | 758.8521 | 12550.3834 | 84.8599 | 0 | 0 | 3611.6563 | 1148.0526 | 1996.6519 | 0 | 96341.7863 | 0 | 96341.7419 | 0.044429 | 758.8966 | 0 | 260.5897 | 274.5828 | 24.4312 | 1066.1926 | 16.1926 | 267.8043 | 1.8108 | 0 | 0 | 77.0667 | 24.4975 | 42.6052 | 0 | 2055.7735 | 0 | 2055.7725 | 0.00094805 | 16.1936 | 3.7126 | 0.33033 | 14.416 | 3.621 | 0.024483 | 1.042 | 3.5234 | 0 | 0.33123 | 0 | 0.57607 | 27.7961 | 27.7961 | 1.2819e-05
MA_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 420754.9759 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118780.4415 | 0 | 0 | 881725.8322 | 0 | 881725.8322 | 0 | 0 | 4417.0857 | 0 | 0 | 0 | 3592.315 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.9571 | 0 | 0 | 9256.3578 | 0 | 9256.3578 | 0 | 0 | 420.755 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.7804 | 0 | 0 | 881.7258 | 0 | 881.7258 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.689 | 1.606 | 0 | 0 | 11.9218 | 11.9218 | 0
MA_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 28244.1303 | 84793.5194 | 10805.8458 | 53987.5506 | 0 | 43037.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220868.2656 | 0 | 220865.7649 | 2.5007 | 2.5007 | 0 | 4516.2364 | 13558.4838 | 1727.8547 | 8632.6093 | 0 | 6881.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35316.8357 | 0 | 35316.4358 | 0.39986 | 0.39986 | 0 | 96.369 | 289.3155 | 36.8695 | 184.2055 | 0 | 146.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.6025 | 0 | 753.594 | 0.0085324 | 0.0085324 | 11.717 | 1.4932 | 7.4601 | 5.947 | 0 | 0 | 3.9028 | 0 | 0 | 0 | 0 | 30.5198 | 30.5201 | 0.00034555
MA_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 438905.6738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90611.3167 | 0 | 0 | 529516.9904 | 0 | 529516.9904 | 0 | 0 | 4607.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.2376 | 0 | 0 | 5558.8694 | 0 | 5558.8694 | 0 | 0 | 438.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6113 | 0 | 0 | 529.517 | 0 | 529.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7752 | 3.6697 | 0 | 0 | 21.4449 | 21.4449 | 0
MA_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 0 | 26146.3125 | 67188.5209 | 10805.8458 | 53987.5506 | 0 | 41239.4867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199367.7166 | 0 | 199366.883 | 0.83357 | 0.83357 | 0 | 4180.7954 | 10743.4445 | 1727.8547 | 8632.6093 | 0 | 6594.1939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31878.8979 | 0 | 31878.7646 | 0.13329 | 0.13329 | 0 | 89.2112 | 229.2472 | 36.8695 | 184.2055 | 0 | 140.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680.2426 | 0 | 680.2398 | 0.0028441 | 0.0028441 | 9.2843 | 1.4932 | 7.4601 | 5.6986 | 0 | 0 | 3.613 | 0 | 0 | 0 | 0 | 27.549 | 27.5491 | 0.00011518
MA_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 468638.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90620.7948 | 0 | 0 | 559259.4917 | 0 | 559259.4917 | 0 | 0 | 4919.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.3371 | 0 | 0 | 5871.1061 | 0 | 5871.1061 | 0 | 0 | 468.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6208 | 0 | 0 | 559.2595 | 0 | 559.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9794 | 3.67 | 0 | 0 | 22.6494 | 22.6494 | 0
MA_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 31675.6602 | 61809.2158 | 79175.2576 | 12306.2718 | 154949.5496 | 0 | 45268.4084 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 385256.6062 | 0 | 385257.9955 | -1.3893 | -1.3893 | 5064.9381 | 9883.2936 | 12660.1237 | 1967.7729 | 24776.433 | 0 | 7238.4185 | 11.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 61602.5313 | 0 | 61602.7535 | -0.22215 | -0.22215 | 108.0774 | 210.893 | 270.146 | 41.989 | 528.6879 | 0 | 154.4558 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1314.4955 | 0 | 1314.5003 | -0.0047402 | -0.0047402 | 6.2531 | 0.97192 | 12.2376 | 3.5752 | 0.0057056 | 0 | 4.8816 | 2.5017 | 0 | 0 | 0 | 30.4268 | 30.4267 | -0.00010972
MA_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 75341.9829 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 593731.6003 | 0 | 0 | 1068569.0211 | 0 | 1068569.0211 | 0 | 0 | 790.9401 | 0 | 0 | 0 | 4193.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 6232.9943 | 0 | 0 | 11217.8376 | 0 | 11217.8376 | 0 | 0 | 75.342 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 593.7316 | 0 | 0 | 1068.569 | 0 | 1068.569 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.7439 | 13.7432 | 0 | 0 | 24.7342 | 24.7342 | 0
MA_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 36146.374 | 57485.7661 | 50803.3132 | 12306.2718 | 154949.5496 | 0 | 42873.2839 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 354636.8014 | 0 | 354637.6349 | -0.83357 | -0.83357 | 5779.8052 | 9191.974 | 8123.4498 | 1967.7729 | 24776.433 | 0 | 6855.4381 | 11.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 56706.4245 | 0 | 56706.5578 | -0.13329 | -0.13329 | 123.3314 | 196.1414 | 173.3409 | 41.989 | 528.6879 | 0 | 146.2836 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.0208 | 0 | 1210.0236 | -0.0028441 | -0.0028441 | 4.0123 | 0.97192 | 12.2376 | 3.386 | 0.0057056 | 0 | 4.5401 | 2.8548 | 0 | 0 | 0 | 28.0085 | 28.0084 | -6.5834e-05
MA_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 73996.0826 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 593778.9912 | 0 | 0 | 1067270.5116 | 0 | 1067270.5116 | 0 | 0 | 776.8109 | 0 | 0 | 0 | 4193.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 6233.4918 | 0 | 0 | 11204.2058 | 0 | 11204.2058 | 0 | 0 | 73.9961 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 593.779 | 0 | 0 | 1067.2705 | 0 | 1067.2705 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.7128 | 13.7442 | 0 | 0 | 24.7042 | 24.7042 | 0
MA_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 3717.7222 | 3350.9514 | 8827.5063 | 1586.5616 | 13417.6985 | 0 | 4695.7777 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40600.4164 | 0 | 40599.0271 | 1.3893 | 1.3893 | 594.4638 | 535.8171 | 1411.5183 | 253.6912 | 2145.49 | 0 | 750.8549 | 0 | 0 | 0 | 0 | 800.1714 | 0 | 0 | 6492.0066 | 0 | 6491.7844 | 0.22215 | 0.22215 | 12.6849 | 11.4334 | 30.1195 | 5.4133 | 45.7812 | 0 | 16.022 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.5286 | 0 | 138.5239 | 0.0047402 | 0.0047402 | 5.4743 | 0.98389 | 8.3208 | 2.912 | 0 | 0 | 2.0781 | 2.3055 | 3.1033 | 0 | 0 | 25.177 | 25.1779 | 0.00086155
MA_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 5506.8175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5506.8175 | 0 | 5506.8175 | 0 | 0 | 57.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.8106 | 0 | 57.8106 | 0 | 0 | 5.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5068 | 0 | 5.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 0 | 0 | 0 | 1.0009 | 1.0009 | 0
MA_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Electricity | 3770.515 | 3156.4518 | 7121.4664 | 1586.5616 | 13417.6985 | 0 | 4303.9998 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38360.8916 | 0 | 38359.7802 | 1.1114 | 1.1114 | 602.9053 | 504.7166 | 1138.7225 | 253.6912 | 2145.49 | 0 | 688.2096 | 0 | 0 | 0 | 0 | 800.1714 | 0 | 0 | 6133.9066 | 0 | 6133.7289 | 0.17772 | 0.17772 | 12.865 | 10.7698 | 24.2984 | 5.4133 | 45.7812 | 0 | 14.6852 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.8874 | 0 | 130.8836 | 0.0037922 | 0.0037922 | 4.4163 | 0.98389 | 8.3208 | 2.6691 | 0 | 0 | 1.9574 | 2.3382 | 3.1033 | 0 | 0 | 23.7884 | 23.7891 | 0.00068924
MA_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | MA-BOSTONLOGAN-MA | Zone5A | Zone5A(MA-BOSTONLOGAN-MA) |  |  | MA | 0.1599 | 0.010498 |  |  |  | Natural Gas | 5866.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5866.988 | 0 | 5866.988 | 0 | 0 | 61.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.5916 | 0 | 61.5916 | 0 | 0 | 5.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.867 | 0 | 5.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0663 | 0 | 0 | 0 | 1.0663 | 1.0663 | 0
MD_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 710154.4084 | 880419.4175 | 95365.9657 | 4077910.5986 | 543457.0788 | 583668.4959 | 100150.6575 | 256992.411 | 364589.6272 | 13592.7482 | 0 | 0 | 0 | 7626301.4089 | 0 | 7626301.6868 | -0.27786 | 543456.801 | 0 | 69098.0239 | 85664.8093 | 9279.1085 | 396780.7012 | 52878.3738 | 56790.9446 | 9744.659 | 25005.3616 | 35474.5707 | 1322.5744 | 0 | 0 | 0 | 742039.1271 | 0 | 742039.1541 | -0.027035 | 52878.3467 | 0 | 2423.0468 | 3003.9911 | 325.3887 | 13913.831 | 1854.2756 | 1991.4769 | 341.714 | 876.8581 | 1243.9798 | 46.3785 | 0 | 0 | 0 | 26020.9404 | 0 | 26020.9414 | -0.00094805 | 1854.2746 | 6.025 | 0.65262 | 27.9065 | 3.9942 | 0.68536 | 0.09302 | 4.8598 | 0 | 0 | 2.495 | 0 | 52.1893 | 52.1893 | -1.9015e-06
MD_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 662220.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539383.7666 | 0 | 0 | 1201604.6321 | 0 | 1201604.6321 | 0 | 0 | 7036.0967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.9525 | 0 | 0 | 12767.0492 | 0 | 12767.0492 | 0 | 0 | 662.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.3838 | 0 | 0 | 1201.6046 | 0 | 1201.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3282 | 1.0818 | 0 | 0 | 2.41 | 2.41 | 0
MD_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 667511.7455 | 716778.5114 | 95365.9657 | 4077910.5986 | 543384.8361 | 558608.603 | 96733.0205 | 231668.5543 | 364422.9132 | 12347.9503 | 0 | 0 | 0 | 7364732.6986 | 0 | 7364734.0878 | -1.3893 | 543383.4468 | 0 | 64948.8928 | 69742.5492 | 9279.1085 | 396780.7012 | 52871.3446 | 54352.6171 | 9412.1229 | 22541.3503 | 35458.3495 | 1201.4556 | 0 | 0 | 0 | 716588.4916 | 0 | 716588.6267 | -0.13518 | 52871.2094 | 0 | 2277.5501 | 2445.6483 | 325.3887 | 13913.831 | 1854.0291 | 1905.9726 | 330.0531 | 790.4531 | 1243.411 | 42.1312 | 0 | 0 | 0 | 25128.468 | 0 | 25128.4727 | -0.0047402 | 1854.0243 | 4.9051 | 0.65262 | 27.9065 | 3.8227 | 0.66198 | 0.084501 | 4.568 | 0 | 0 | 2.4939 | 0 | 50.3993 | 50.3993 | -9.5073e-06
MD_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 600499.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539488.0265 | 0 | 0 | 1139987.0411 | 0 | 1139987.0411 | 0 | 0 | 6380.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5732.0603 | 0 | 0 | 12112.3623 | 0 | 12112.3623 | 0 | 0 | 600.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.488 | 0 | 0 | 1139.987 | 0 | 1139.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2044 | 1.082 | 0 | 0 | 2.2864 | 2.2864 | 0
MD_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 32548.1301 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21508.8847 | 0 | 0 | 0 | 0 | 108272.4079 | 0 | 0 | 339913.1765 | 0 | 339914.5658 | -1.3893 | -1.3893 | 0 | 3166.9331 | 2760.8605 | 701.0293 | 13817.0094 | 0 | 2092.8145 | 0 | 0 | 0 | 0 | 10534.9053 | 0 | 0 | 33073.5521 | 0 | 33073.6873 | -0.13518 | -0.13518 | 0 | 111.0542 | 96.8146 | 24.5829 | 484.5184 | 0 | 73.3883 | 0 | 0 | 0 | 0 | 369.4255 | 0 | 0 | 1159.7838 | 0 | 1159.7885 | -0.0047402 | -0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.175 | 0 | 0 | 3.2914 | 0 | 10.9489 | 0 | 0 | 34.3733 | 34.3731 | -0.00014049
MD_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 69057.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69057.9554 | 0 | 69057.9554 | 0 | 0 | 733.7408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733.7408 | 0 | 733.7408 | 0 | 0 | 69.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.058 | 0 | 69.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0467 | 0 | 0 | 0 | 2.0467 | 2.0467 | 0
MD_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 31633.9817 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21072.6497 | 0 | 0 | 0 | 0 | 108302.9721 | 0 | 0 | 333400.2162 | 0 | 333403.8284 | -3.6121 | -3.6121 | 0 | 3077.9864 | 2255.5679 | 701.0293 | 13817.0094 | 0 | 2050.3688 | 0 | 0 | 0 | 0 | 10537.8792 | 0 | 0 | 32439.841 | 0 | 32440.1925 | -0.35146 | -0.35146 | 0 | 107.9351 | 79.0956 | 24.5829 | 484.5184 | 0 | 71.8999 | 0 | 0 | 0 | 0 | 369.5297 | 0 | 0 | 1137.5615 | 0 | 1137.5739 | -0.012325 | -0.012325 | 2.3442 | 0.72858 | 14.3599 | 2.1309 | 0 | 0 | 3.1989 | 0 | 10.9519 | 0 | 0 | 33.7149 | 33.7145 | -0.00036527
MD_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 80536.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80536.0207 | 0 | 80536.0207 | 0 | 0 | 855.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.6952 | 0 | 855.6952 | 0 | 0 | 80.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.536 | 0 | 80.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3869 | 0 | 0 | 0 | 2.3869 | 2.3869 | 0
MD_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 122229.1484 | 97783.3187 | 7110.3521 | 317887.4784 | 4818.0346 | 93551.5616 | 502.9206 | 0 | 0 | 21136.5568 | 7179.8163 | 17613.3342 | 0 | 689812.5217 | 0 | 689810.8546 | 1.6671 | 4819.7018 | 0 | 11892.8961 | 9514.3169 | 691.8373 | 30930.4517 | 468.7948 | 9102.5669 | 48.9342 | 0 | 0 | 2056.587 | 698.5961 | 1713.7774 | 0 | 67118.7584 | 0 | 67118.5961 | 0.16221 | 468.957 | 0 | 417.0459 | 333.6367 | 24.2605 | 1084.6321 | 16.4391 | 319.1979 | 1.716 | 0 | 0 | 72.1179 | 24.4975 | 60.0967 | 0 | 2353.6403 | 0 | 2353.6346 | 0.0056883 | 16.4448 | 4.5111 | 0.32803 | 14.6653 | 4.3159 | 0.023202 | 0.97511 | 5.6389 | 0 | 0.33123 | 0 | 0.81257 | 31.8235 | 31.8236 | 7.6911e-05
MD_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 291472.7207 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113339.9712 | 0 | 0 | 747003.1068 | 0 | 747003.1068 | 0 | 0 | 3096.8977 | 0 | 0 | 0 | 3635.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.2372 | 0 | 0 | 7936.908 | 0 | 7936.908 | 0 | 0 | 291.4727 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.34 | 0 | 0 | 747.0031 | 0 | 747.0031 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.941 | 1.5325 | 0 | 0 | 10.1002 | 10.1002 | 0
MD_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 117555.5992 | 79453.1143 | 7110.3521 | 312483.1662 | 4743.0133 | 81003.5545 | 366.7708 | 0 | 0 | 22698.1112 | 7179.8163 | 12489.6572 | 0 | 645083.1552 | 0 | 645088.7124 | -5.5571 | 4737.4562 | 0 | 11438.1598 | 7730.788 | 691.8373 | 30404.6121 | 461.4952 | 7881.6459 | 35.6868 | 0 | 0 | 2208.5262 | 698.5961 | 1215.2436 | 0 | 62766.591 | 0 | 62767.1317 | -0.54071 | 460.9545 | 0 | 401.0997 | 271.094 | 24.2605 | 1066.1926 | 16.1832 | 276.3841 | 1.2514 | 0 | 0 | 77.446 | 24.4975 | 42.6147 | 0 | 2201.0237 | 0 | 2201.0427 | -0.018961 | 16.1642 | 3.6655 | 0.32803 | 14.416 | 3.737 | 0.01692 | 1.0471 | 5.4233 | 0 | 0.33123 | 0 | 0.57619 | 29.7603 | 29.7601 | -0.00025637
MD_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 276516.1666 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113103.0169 | 0 | 0 | 731809.5984 | 0 | 731809.5984 | 0 | 0 | 2937.9843 | 0 | 0 | 0 | 3635.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.7196 | 0 | 0 | 7775.477 | 0 | 7775.477 | 0 | 0 | 276.5162 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.103 | 0 | 0 | 731.8096 | 0 | 731.8096 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7388 | 1.5293 | 0 | 0 | 9.8948 | 9.8948 | 0
MD_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 46782.7272 | 84032.1922 | 10708.596 | 53987.5506 | 0 | 38791.5695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234302.6355 | 0 | 234300.4126 | 2.2229 | 2.2229 | 0 | 4551.9594 | 8176.3323 | 1041.9464 | 5252.9887 | 0 | 3774.4197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22797.6464 | 0 | 22797.4301 | 0.21628 | 0.21628 | 0 | 159.6227 | 286.7178 | 36.5377 | 184.2055 | 0 | 132.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.4406 | 0 | 799.433 | 0.0075844 | 0.0075844 | 11.6118 | 1.4797 | 7.4601 | 5.3603 | 0 | 0 | 6.4645 | 0 | 0 | 0 | 0 | 32.3762 | 32.3765 | 0.00030716
MD_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 299614.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88838.8987 | 0 | 0 | 388453.3685 | 0 | 388453.3685 | 0 | 0 | 3183.4037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 943.9133 | 0 | 0 | 4127.317 | 0 | 4127.317 | 0 | 0 | 299.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8389 | 0 | 0 | 388.4534 | 0 | 388.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1341 | 3.5979 | 0 | 0 | 15.732 | 15.732 | 0
MD_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 43851.3394 | 66585.572 | 10708.596 | 53987.5506 | 0 | 39961.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215094.404 | 0 | 215092.1812 | 2.2229 | 2.2229 | 0 | 4266.7353 | 6478.7762 | 1041.9464 | 5252.9887 | 0 | 3888.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20928.6855 | 0 | 20928.4692 | 0.21628 | 0.21628 | 0 | 149.6208 | 227.19 | 36.5377 | 184.2055 | 0 | 136.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733.9021 | 0 | 733.8945 | 0.0075844 | 0.0075844 | 9.201 | 1.4797 | 7.4601 | 5.522 | 0 | 0 | 6.0595 | 0 | 0 | 0 | 0 | 29.722 | 29.7223 | 0.00030716
MD_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 318731.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88857.855 | 0 | 0 | 407589.7961 | 0 | 407589.7961 | 0 | 0 | 3386.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 944.1147 | 0 | 0 | 4330.6416 | 0 | 4330.6416 | 0 | 0 | 318.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8579 | 0 | 0 | 407.5898 | 0 | 407.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9083 | 3.5986 | 0 | 0 | 16.507 | 16.507 | 0
MD_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 20842.0287 | 79086.3435 | 79269.7289 | 12306.2718 | 154949.5496 | 0 | 45785.2218 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392311.387 | 0 | 392312.2206 | -0.83357 | -0.83357 | 2027.9294 | 7695.1012 | 7712.9446 | 1197.4002 | 15076.5912 | 0 | 4454.9021 | 7.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 38171.898 | 0 | 38171.9791 | -0.081106 | -0.081106 | 71.113 | 269.8426 | 270.4683 | 41.989 | 528.6879 | 0 | 156.2192 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.5665 | 0 | 1338.5693 | -0.0028441 | -0.0028441 | 6.2606 | 0.97192 | 12.2376 | 3.616 | 0.0057056 | 0 | 6.2461 | 1.6461 | 0 | 0 | 0 | 30.984 | 30.9839 | -6.5834e-05
MD_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 51722.3802 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 559875.5728 | 0 | 0 | 1011093.3909 | 0 | 1011093.3909 | 0 | 0 | 549.5503 | 0 | 0 | 0 | 4244.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5948.678 | 0 | 0 | 10742.8673 | 0 | 10742.8673 | 0 | 0 | 51.7224 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 559.8756 | 0 | 0 | 1011.0934 | 0 | 1011.0934 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.1972 | 12.9595 | 0 | 0 | 23.4039 | 23.4039 | 0
MD_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 24179.0873 | 74079.3663 | 50831.0989 | 12306.2718 | 154949.5496 | 0 | 43440.1115 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 359857.7282 | 0 | 359859.3953 | -1.6671 | -1.6671 | 2352.6252 | 7207.9223 | 4945.8659 | 1197.4002 | 15076.5912 | 0 | 4226.7229 | 7.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 35014.157 | 0 | 35014.3192 | -0.16221 | -0.16221 | 82.499 | 252.7588 | 173.4357 | 41.989 | 528.6879 | 0 | 148.2177 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.8346 | 0 | 1227.8403 | -0.0056883 | -0.0056883 | 4.0145 | 0.97192 | 12.2376 | 3.4308 | 0.0057056 | 0 | 5.8506 | 1.9096 | 0 | 0 | 0 | 28.4209 | 28.4208 | -0.00013167
MD_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 51940.3782 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 559979.8327 | 0 | 0 | 1011415.6488 | 0 | 1011415.6488 | 0 | 0 | 551.8665 | 0 | 0 | 0 | 4244.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5949.7857 | 0 | 0 | 10746.2913 | 0 | 10746.2913 | 0 | 0 | 51.9404 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 559.9798 | 0 | 0 | 1011.4156 | 0 | 1011.4156 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2023 | 12.9619 | 0 | 0 | 23.4113 | 23.4113 | 0
MD_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 2428.4673 | 4959.7415 | 8844.1778 | 1578.2259 | 13417.6985 | 0 | 4856.9346 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41089.4441 | 0 | 41091.667 | -2.2229 | -2.2229 | 236.2899 | 482.5829 | 860.5385 | 153.5614 | 1305.5421 | 0 | 472.5797 | 0 | 0 | 0 | 0 | 486.9085 | 0 | 0 | 3998.0029 | 0 | 3998.2192 | -0.21628 | -0.21628 | 8.2859 | 16.9226 | 30.1763 | 5.3849 | 45.7812 | 0 | 16.5719 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.1972 | 0 | 140.2048 | -0.0075844 | -0.0075844 | 5.4846 | 0.97872 | 8.3208 | 3.012 | 0 | 0 | 3.0757 | 1.506 | 3.1033 | 0 | 0 | 25.4825 | 25.4811 | -0.0013785
MD_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 2663.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2663.3661 | 0 | 2663.3661 | 0 | 0 | 28.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2983 | 0 | 28.2983 | 0 | 0 | 2.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6634 | 0 | 2.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48407 | 0 | 0 | 0 | 0.48407 | 0.48407 | 0
MD_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 2475.7029 | 4706.892 | 7124.245 | 1578.2259 | 13417.6985 | 0 | 4473.4924 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38780.4552 | 0 | 38782.9559 | -2.5007 | -2.5007 | 240.8859 | 457.9806 | 693.189 | 153.5614 | 1305.5421 | 0 | 435.2708 | 0 | 0 | 0 | 0 | 486.9085 | 0 | 0 | 3773.3383 | 0 | 3773.5816 | -0.24332 | -0.24332 | 8.4471 | 16.0599 | 24.3079 | 5.3849 | 45.7812 | 0 | 15.2636 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.3189 | 0 | 132.3274 | -0.0085324 | -0.0085324 | 4.418 | 0.97872 | 8.3208 | 2.7742 | 0 | 0 | 2.9189 | 1.5353 | 3.1033 | 0 | 0 | 24.0508 | 24.0492 | -0.0015508
MD_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | MD-BALTIMORE-MD | Zone4A | Zone4A(MD-BALTIMORE-MD) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 2852.9295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2852.9295 | 0 | 2852.9295 | 0 | 0 | 30.3124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.3124 | 0 | 30.3124 | 0 | 0 | 2.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8529 | 0 | 2.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51853 | 0 | 0 | 0 | 0.51853 | 0.51853 | 0
MD_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 592737.7375 | 880744.5098 | 95707.7294 | 4077910.5986 | 543457.0788 | 596983.3874 | 87799.9286 | 204555.3006 | 411705.7825 | 11358.7806 | 0 | 0 | 0 | 7502960.8339 | 0 | 7502960.2782 | 0.55571 | 543457.6346 | 0 | 57673.3819 | 85696.4408 | 9312.3621 | 396780.7012 | 52878.3738 | 58086.4836 | 8542.9331 | 19903.2307 | 40058.9726 | 1105.2094 | 0 | 0 | 0 | 730038.0891 | 0 | 730038.0351 | 0.054071 | 52878.4278 | 0 | 2022.4212 | 3005.1003 | 326.5548 | 13913.831 | 1854.2756 | 2036.9073 | 299.5734 | 697.9427 | 1404.7401 | 38.7562 | 0 | 0 | 0 | 25600.1024 | 0 | 25600.1005 | 0.0018961 | 1854.2774 | 6.0272 | 0.65496 | 27.9065 | 4.0854 | 0.60084 | 0.077732 | 4.0563 | 0 | 0 | 2.8174 | 0 | 51.3452 | 51.3452 | 3.8029e-06
MD_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 947940.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569145.2242 | 0 | 0 | 1517085.5604 | 0 | 1517085.5604 | 0 | 0 | 10071.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6047.168 | 0 | 0 | 16119.0341 | 0 | 16119.0341 | 0 | 0 | 947.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.1452 | 0 | 0 | 1517.0856 | 0 | 1517.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9012 | 1.1415 | 0 | 0 | 3.0428 | 3.0428 | 0
MD_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 556271.8284 | 716956.3396 | 95707.7294 | 4077910.5986 | 543387.6147 | 580417.5728 | 83929.3852 | 183643.8077 | 411475.1614 | 10514.0963 | 0 | 0 | 0 | 7260214.1342 | 0 | 7260210.5221 | 3.6121 | 543391.2268 | 0 | 54125.2489 | 69759.8518 | 9312.3621 | 396780.7012 | 52871.6149 | 56474.6298 | 8166.3292 | 17868.5425 | 40036.5332 | 1023.0216 | 0 | 0 | 0 | 706418.8353 | 0 | 706418.4838 | 0.35146 | 52871.9664 | 0 | 1897.9995 | 2446.255 | 326.5548 | 13913.831 | 1854.0385 | 1980.3848 | 286.3671 | 626.5927 | 1403.9533 | 35.8741 | 0 | 0 | 0 | 24771.8506 | 0 | 24771.8383 | 0.012325 | 1854.0509 | 4.9064 | 0.65496 | 27.9065 | 3.972 | 0.57436 | 0.071951 | 3.8067 | 0 | 0 | 2.8159 | 0 | 49.684 | 49.684 | 2.4719e-05
MD_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 891204.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569249.4841 | 0 | 0 | 1460453.4875 | 0 | 1460453.4875 | 0 | 0 | 9469.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6048.2758 | 0 | 0 | 15517.3183 | 0 | 15517.3183 | 0 | 0 | 891.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.2495 | 0 | 0 | 1460.4535 | 0 | 1460.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7875 | 1.1417 | 0 | 0 | 2.9292 | 2.9292 | 0
MD_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 24890.4003 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20844.8073 | 0 | 0 | 0 | 0 | 114129.6265 | 0 | 0 | 337448.5879 | 0 | 337444.9757 | 3.6121 | 3.6121 | 0 | 2421.836 | 2760.8605 | 701.0293 | 13817.0094 | 0 | 2028.1997 | 0 | 0 | 0 | 0 | 11104.8127 | 0 | 0 | 32833.7476 | 0 | 32833.3961 | 0.35146 | 0.35146 | 0 | 84.926 | 96.8146 | 24.5829 | 484.5184 | 0 | 71.1225 | 0 | 0 | 0 | 0 | 389.4103 | 0 | 0 | 1151.3746 | 0 | 1151.3623 | 0.012325 | 0.012325 | 2.8693 | 0.72858 | 14.3599 | 2.1079 | 0 | 0 | 2.517 | 0 | 11.5412 | 0 | 0 | 34.1235 | 34.1239 | 0.00036527
MD_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 113311.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113311.5367 | 0 | 113311.5367 | 0 | 0 | 1203.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.9351 | 0 | 1203.9351 | 0 | 0 | 113.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3115 | 0 | 113.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3583 | 0 | 0 | 0 | 3.3583 | 3.3583 | 0
MD_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 23770.638 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20252.9725 | 0 | 0 | 0 | 0 | 114165.7478 | 0 | 0 | 330579.971 | 0 | 330578.8596 | 1.1114 | 1.1114 | 0 | 2312.8831 | 2255.5679 | 701.0293 | 13817.0094 | 0 | 1970.6142 | 0 | 0 | 0 | 0 | 11108.3273 | 0 | 0 | 32165.4312 | 0 | 32165.323 | 0.10814 | 0.10814 | 0 | 81.1054 | 79.0956 | 24.5829 | 484.5184 | 0 | 69.1031 | 0 | 0 | 0 | 0 | 389.5335 | 0 | 0 | 1127.9389 | 0 | 1127.9351 | 0.0037922 | 0.0037922 | 2.3442 | 0.72858 | 14.3599 | 2.048 | 0 | 0 | 2.4038 | 0 | 11.5448 | 0 | 0 | 33.4292 | 33.4293 | 0.00011239
MD_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 128675.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128675.6522 | 0 | 128675.6522 | 0 | 0 | 1367.1788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.1788 | 0 | 1367.1788 | 0 | 0 | 128.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.6757 | 0 | 128.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8136 | 0 | 0 | 0 | 3.8136 | 3.8136 | 0
MD_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 92090.0356 | 96696.8991 | 7113.1307 | 317887.4784 | 4818.0346 | 91459.3009 | 914.1484 | 0 | 0 | 21833.977 | 7179.8163 | 17602.2199 | 0 | 657595.041 | 0 | 657596.4303 | -1.3893 | 4816.6453 | 0 | 8960.3605 | 9408.6083 | 692.1076 | 30930.4517 | 468.7948 | 8898.99 | 88.9466 | 0 | 0 | 2124.446 | 698.5961 | 1712.696 | 0 | 63983.9975 | 0 | 63984.1327 | -0.13518 | 468.6596 | 0 | 314.2112 | 329.9298 | 24.27 | 1084.6321 | 16.4391 | 312.0591 | 3.1191 | 0 | 0 | 74.4975 | 24.4975 | 60.0588 | 0 | 2243.7143 | 0 | 2243.719 | -0.0047402 | 16.4344 | 4.461 | 0.32815 | 14.6653 | 4.2194 | 0.042173 | 1.0073 | 4.2485 | 0 | 0.33123 | 0 | 0.81205 | 30.3373 | 30.3373 | -6.4093e-05
MD_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 442725.3768 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118970.0049 | 0 | 0 | 903885.7965 | 0 | 903885.7965 | 0 | 0 | 4703.9571 | 0 | 0 | 0 | 3635.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0563 | 0 | 0 | 9603.7866 | 0 | 9603.7866 | 0 | 0 | 442.7254 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.97 | 0 | 0 | 903.8858 | 0 | 903.8858 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.9861 | 1.6086 | 0 | 0 | 12.2214 | 12.2214 | 0
MD_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 87219.2082 | 78672.337 | 7113.1307 | 312483.1662 | 4743.0133 | 78577.8658 | 555.7133 | 0 | 0 | 22659.2113 | 7179.8163 | 12478.543 | 0 | 611682.0052 | 0 | 611683.3944 | -1.3893 | 4741.624 | 0 | 8486.429 | 7654.8184 | 692.1076 | 30404.6121 | 461.4952 | 7645.6263 | 54.0709 | 0 | 0 | 2204.7413 | 698.5961 | 1214.1622 | 0 | 59516.6591 | 0 | 59516.7943 | -0.13518 | 461.36 | 0 | 297.5919 | 268.43 | 24.27 | 1066.1926 | 16.1832 | 268.1077 | 1.8961 | 0 | 0 | 77.3132 | 24.4975 | 42.5768 | 0 | 2087.059 | 0 | 2087.0637 | -0.0047402 | 16.1784 | 3.6294 | 0.32815 | 14.416 | 3.6251 | 0.025637 | 1.0454 | 4.0237 | 0 | 0.33123 | 0 | 0.57568 | 28.2192 | 28.2191 | -6.4093e-05
MD_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 426223.8807 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118733.0506 | 0 | 0 | 887147.3461 | 0 | 887147.3461 | 0 | 0 | 4528.6287 | 0 | 0 | 0 | 3635.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.5387 | 0 | 0 | 9425.9406 | 0 | 9425.9406 | 0 | 0 | 426.2239 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.7331 | 0 | 0 | 887.1473 | 0 | 887.1473 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.763 | 1.6054 | 0 | 0 | 11.9951 | 11.9951 | 0
MD_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 31661.7673 | 83362.5576 | 10680.8103 | 53987.5506 | 0 | 43320.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223013.3191 | 0 | 223013.0412 | 0.27786 | 0.27786 | 0 | 3080.69 | 8111.1769 | 1039.2428 | 5252.9887 | 0 | 4215.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21699.1959 | 0 | 21699.1689 | 0.027035 | 0.027035 | 0 | 108.03 | 284.433 | 36.4429 | 184.2055 | 0 | 147.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.9214 | 0 | 760.9205 | 0.00094805 | 0.00094805 | 11.5192 | 1.4759 | 7.4601 | 5.9861 | 0 | 0 | 4.3751 | 0 | 0 | 0 | 0 | 30.8165 | 30.8165 | 3.8395e-05
MD_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 420129.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90620.7948 | 0 | 0 | 510750.2115 | 0 | 510750.2115 | 0 | 0 | 4463.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962.8459 | 0 | 0 | 5426.721 | 0 | 5426.721 | 0 | 0 | 420.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6208 | 0 | 0 | 510.7502 | 0 | 510.7502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0148 | 3.67 | 0 | 0 | 20.6848 | 20.6848 | 0
MD_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 0 | 29391.6784 | 65874.2589 | 10680.8103 | 53987.5506 | 0 | 41336.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201271.0348 | 0 | 201271.0348 | 0 | 0 | 0 | 2859.8103 | 6409.5654 | 1039.2428 | 5252.9887 | 0 | 4022.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19583.6717 | 0 | 19583.6717 | 0 | 0 | 0 | 100.2844 | 224.763 | 36.4429 | 184.2055 | 0 | 141.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 686.7368 | 0 | 686.7368 | 0 | 0 | 9.1027 | 1.4759 | 7.4601 | 5.712 | 0 | 0 | 4.0614 | 0 | 0 | 0 | 0 | 27.8121 | 27.8121 | 0
MD_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 448601.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90630.273 | 0 | 0 | 539232.1159 | 0 | 539232.1159 | 0 | 0 | 4766.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962.9467 | 0 | 0 | 5729.3412 | 0 | 5729.3412 | 0 | 0 | 448.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6303 | 0 | 0 | 539.2321 | 0 | 539.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1679 | 3.6704 | 0 | 0 | 21.8383 | 21.8383 | 0
MD_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 29458.364 | 65112.9316 | 79075.2292 | 12303.4933 | 154949.5496 | 0 | 45676.8577 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 386648.6681 | 0 | 386646.7231 | 1.945 | 1.945 | 2866.2988 | 6335.4882 | 7694.0198 | 1197.1299 | 15076.5912 | 0 | 4444.3583 | 7.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 37620.9154 | 0 | 37620.7262 | 0.18925 | 0.18925 | 100.5119 | 222.1653 | 269.8047 | 41.9795 | 528.6879 | 0 | 155.8494 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1319.2453 | 0 | 1319.2386 | 0.0066363 | 0.0066363 | 6.2452 | 0.9717 | 12.2376 | 3.6075 | 0.0057056 | 0 | 5.1425 | 2.3266 | 0 | 0 | 0 | 30.5365 | 30.5367 | 0.00015361
MD_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 69825.6872 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594072.8145 | 0 | 0 | 1063393.9396 | 0 | 1063393.9396 | 0 | 0 | 741.8979 | 0 | 0 | 0 | 4244.639 | 0 | 0 | 0 | 0 | 0 | 0 | 6312.0237 | 0 | 0 | 11298.5606 | 0 | 11298.5606 | 0 | 0 | 69.8257 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.0728 | 0 | 0 | 1063.3939 | 0 | 1063.3939 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6163 | 13.751 | 0 | 0 | 24.6145 | 24.6145 | 0
MD_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 33556.7498 | 60600.5393 | 50725.5134 | 12303.4933 | 154949.5496 | 0 | 43242.8333 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 355450.9214 | 0 | 355448.9764 | 1.945 | 1.945 | 3265.0718 | 5896.4325 | 4935.5924 | 1197.1299 | 15076.5912 | 0 | 4207.5277 | 7.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 34585.3747 | 0 | 34585.1854 | 0.18925 | 0.18925 | 114.4956 | 206.769 | 173.0755 | 41.9795 | 528.6879 | 0 | 147.5445 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.7985 | 0 | 1212.7919 | 0.0066363 | 0.0066363 | 4.0062 | 0.9717 | 12.2376 | 3.4152 | 0.0057056 | 0 | 4.7861 | 2.6502 | 0 | 0 | 0 | 28.0726 | 28.0727 | 0.00015361
MD_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 68953.6955 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594129.6835 | 0 | 0 | 1062578.8169 | 0 | 1062578.8169 | 0 | 0 | 732.633 | 0 | 0 | 0 | 4244.639 | 0 | 0 | 0 | 0 | 0 | 0 | 6312.6279 | 0 | 0 | 11289.8999 | 0 | 11289.8999 | 0 | 0 | 68.9537 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.1297 | 0 | 0 | 1062.5788 | 0 | 1062.5788 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5961 | 13.7524 | 0 | 0 | 24.5956 | 24.5956 | 0
MD_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 3428.7513 | 3556.5654 | 8810.8349 | 1586.5616 | 13417.6985 | 0 | 4876.3845 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40680.9948 | 0 | 40680.7169 | 0.27786 | 0.27786 | 333.6175 | 346.0538 | 857.2942 | 154.3724 | 1305.5421 | 0 | 474.4722 | 0 | 0 | 0 | 0 | 486.9085 | 0 | 0 | 3958.2608 | 0 | 3958.2338 | 0.027035 | 0.027035 | 11.6989 | 12.135 | 30.0626 | 5.4133 | 45.7812 | 0 | 16.6382 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8036 | 0 | 138.8026 | 0.00094805 | 0.00094805 | 5.4639 | 0.98389 | 8.3208 | 3.024 | 0 | 0 | 2.2056 | 2.1263 | 3.1033 | 0 | 0 | 25.2277 | 25.2278 | 0.00017231
MD_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 8028.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.011 | 0 | 8028.011 | 0 | 0 | 85.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2976 | 0 | 85.2976 | 0 | 0 | 8.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.028 | 0 | 8.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 0 | 0 | 0 | 1.4591 | 1.4591 | 0
MD_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Electricity | 3470.4298 | 3348.1729 | 7102.0164 | 1586.5616 | 13417.6985 | 0 | 4473.4924 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38402.5701 | 0 | 38406.738 | -4.1679 | -4.1679 | 337.6728 | 325.7772 | 691.0262 | 154.3724 | 1305.5421 | 0 | 435.2708 | 0 | 0 | 0 | 0 | 486.9085 | 0 | 0 | 3736.5701 | 0 | 3736.9756 | -0.40553 | -0.40553 | 11.8411 | 11.424 | 24.2321 | 5.4133 | 45.7812 | 0 | 15.2636 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.0296 | 0 | 131.0438 | -0.014221 | -0.014221 | 4.4042 | 0.98389 | 8.3208 | 2.7742 | 0 | 0 | 2.0763 | 2.1521 | 3.1033 | 0 | 0 | 23.8175 | 23.8149 | -0.0025846
MD_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | MD-PITTSBURGH-PA | Zone5A | Zone5A(MD-PITTSBURGH-PA) |  |  | MD | 0.0973 | 0.010625 |  |  |  | Natural Gas | 8407.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8407.1379 | 0 | 8407.1379 | 0 | 0 | 89.3258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3258 | 0 | 89.3258 | 0 | 0 | 8.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4071 | 0 | 8.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.528 | 0 | 0 | 0 | 1.528 | 1.528 | 0
ME_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 467204.8734 | 885092.9667 | 96905.2916 | 4077910.5986 | 543459.8574 | 577172.207 | 71909.3057 | 147358.5054 | 453067.5261 | 12334.0575 | 0 | 0 | 0 | 7332415.1895 | 0 | 7332411.8552 | 3.3343 | 543463.1917 | 0 | 58587.4911 | 110990.658 | 12151.9236 | 511369.9891 | 68149.8661 | 72377.3948 | 9017.4269 | 18478.7566 | 56814.6678 | 1546.6908 | 0 | 0 | 0 | 919484.8648 | 0 | 919484.4466 | 0.41812 | 68150.2842 | 0 | 1594.103 | 3019.9372 | 330.6409 | 13913.831 | 1854.285 | 1969.3116 | 245.3546 | 502.7872 | 1545.8664 | 42.0838 | 0 | 0 | 0 | 25018.2006 | 0 | 25018.1892 | 0.011377 | 1854.2964 | 6.057 | 0.66315 | 27.9065 | 3.9498 | 0.4921 | 0.084406 | 3.1972 | 0 | 0 | 3.1005 | 0 | 50.1781 | 50.1781 | 2.2818e-05
ME_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 1323854.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604603.0627 | 0 | 0 | 1928457.1469 | 0 | 1928457.1469 | 0 | 0 | 14669.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6699.6065 | 0 | 0 | 21369.2336 | 0 | 21369.2336 | 0 | 0 | 1323.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.6031 | 0 | 0 | 1928.4571 | 0 | 1928.4571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6552 | 1.2126 | 0 | 0 | 3.8678 | 3.8678 | 0
ME_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 433320.2527 | 720571.2549 | 96905.2916 | 4077910.5986 | 543387.6147 | 554329.6103 | 68008.1981 | 131751.2964 | 452722.9838 | 11389.3448 | 0 | 0 | 0 | 7090296.4459 | 0 | 7090298.6688 | -2.2229 | 543385.3918 | 0 | 54338.3597 | 90359.6354 | 12151.9236 | 511369.9891 | 68140.8069 | 69512.9331 | 8528.228 | 16521.6126 | 56771.4622 | 1428.2238 | 0 | 0 | 0 | 889123.1743 | 0 | 889123.4531 | -0.27875 | 68140.5281 | 0 | 1478.4887 | 2458.5891 | 330.6409 | 13913.831 | 1854.0385 | 1891.3726 | 232.044 | 449.5354 | 1544.6908 | 38.8604 | 0 | 0 | 0 | 24192.0915 | 0 | 24192.0991 | -0.0075844 | 1854.031 | 4.9311 | 0.66315 | 27.9065 | 3.7935 | 0.4654 | 0.077941 | 2.9654 | 0 | 0 | 3.0981 | 0 | 48.5212 | 48.5212 | -1.5212e-05
ME_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 1285884.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604546.1936 | 0 | 0 | 1890430.724 | 0 | 1890430.724 | 0 | 0 | 14248.8865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6698.9764 | 0 | 0 | 20947.8629 | 0 | 20947.8629 | 0 | 0 | 1285.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.5462 | 0 | 0 | 1890.4307 | 0 | 1890.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5791 | 1.2125 | 0 | 0 | 3.7916 | 3.7916 | 0
ME_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 19527.7666 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 19858.4161 | 0 | 0 | 0 | 0 | 121048.2575 | 0 | 0 | 338012.6369 | 0 | 338012.3591 | 0.27786 | 0.27786 | 0 | 2448.7819 | 3558.1903 | 902.788 | 17807.3276 | 0 | 2490.2454 | 0 | 0 | 0 | 0 | 15179.4515 | 0 | 0 | 42386.7847 | 0 | 42386.7498 | 0.034843 | 0.034843 | 0 | 66.6287 | 96.8146 | 24.5639 | 484.5184 | 0 | 67.7569 | 0 | 0 | 0 | 0 | 413.0167 | 0 | 0 | 1153.2991 | 0 | 1153.2982 | 0.00094805 | 0.00094805 | 2.8693 | 0.72801 | 14.3599 | 2.0081 | 0 | 0 | 1.9747 | 0 | 12.2408 | 0 | 0 | 34.1809 | 34.1809 | 2.8098e-05
ME_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 166569.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166569.3807 | 0 | 166569.3807 | 0 | 0 | 1845.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1845.7553 | 0 | 1845.7553 | 0 | 0 | 166.5694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.5694 | 0 | 166.5694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9367 | 0 | 0 | 0 | 4.9367 | 4.9367 | 0
ME_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 17791.1625 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 19074.8603 | 0 | 0 | 0 | 0 | 121092.7146 | 0 | 0 | 330343.7929 | 0 | 330347.1271 | -3.3343 | -3.3343 | 0 | 2231.0118 | 2906.9704 | 902.788 | 17807.3276 | 0 | 2391.9875 | 0 | 0 | 0 | 0 | 15185.0264 | 0 | 0 | 41425.1116 | 0 | 41425.5297 | -0.41812 | -0.41812 | 0 | 60.7034 | 79.0956 | 24.5639 | 484.5184 | 0 | 65.0834 | 0 | 0 | 0 | 0 | 413.1683 | 0 | 0 | 1127.133 | 0 | 1127.1444 | -0.011377 | -0.011377 | 2.3442 | 0.72801 | 14.3599 | 1.9289 | 0 | 0 | 1.7991 | 0 | 12.2453 | 0 | 0 | 33.4058 | 33.4054 | -0.00033717
ME_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 191733.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191733.9252 | 0 | 191733.9252 | 0 | 0 | 2124.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2124.6036 | 0 | 2124.6036 | 0 | 0 | 191.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.7339 | 0 | 191.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6825 | 0 | 0 | 0 | 5.6825 | 5.6825 | 0
ME_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 61000.6529 | 100703.5923 | 7193.7091 | 317887.4784 | 4818.0346 | 92445.6921 | 1089.1981 | 0 | 0 | 19052.6317 | 7179.8163 | 17613.3342 | 0 | 628984.1399 | 0 | 628986.6406 | -2.5007 | 4815.5339 | 0 | 7649.4819 | 12628.2305 | 902.0911 | 39863.0898 | 604.1815 | 11592.6898 | 136.5854 | 0 | 0 | 2389.2 | 900.349 | 2208.7121 | 0 | 78874.6111 | 0 | 78874.9247 | -0.31359 | 603.868 | 0 | 208.1342 | 343.6007 | 24.5449 | 1084.6321 | 16.4391 | 315.4247 | 3.7163 | 0 | 0 | 65.0076 | 24.4975 | 60.0967 | 0 | 2146.0939 | 0 | 2146.1024 | -0.0085324 | 16.4306 | 4.6458 | 0.33187 | 14.6653 | 4.2649 | 0.050249 | 0.87897 | 2.8142 | 0 | 0.33123 | 0 | 0.81257 | 29.0175 | 29.0173 | -0.00011537
ME_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 704957.9393 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126296.6312 | 0 | 0 | 1173444.9854 | 0 | 1173444.9854 | 0 | 0 | 7811.6389 | 0 | 0 | 0 | 3791.812 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.493 | 0 | 0 | 13002.9439 | 0 | 13002.9439 | 0 | 0 | 704.9579 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.2966 | 0 | 0 | 1173.445 | 0 | 1173.445 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.5317 | 1.7077 | 0 | 0 | 15.8662 | 15.8662 | 0
ME_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 56582.7319 | 82481.752 | 7193.7091 | 312483.1662 | 4745.7919 | 78933.5223 | 872.4699 | 0 | 0 | 22862.0467 | 7179.8163 | 12475.7644 | 0 | 585810.7708 | 0 | 585811.6044 | -0.83357 | 4744.9583 | 0 | 7095.4746 | 10343.2117 | 902.0911 | 39185.389 | 595.1223 | 9898.2637 | 109.4077 | 0 | 0 | 2866.9007 | 900.349 | 1564.4609 | 0 | 73460.6707 | 0 | 73460.7752 | -0.10453 | 595.0178 | 0 | 193.0603 | 281.4277 | 24.5449 | 1066.1926 | 16.1926 | 269.3212 | 2.9769 | 0 | 0 | 78.0053 | 24.4975 | 42.5673 | 0 | 1998.7863 | 0 | 1998.7892 | -0.0028441 | 16.1898 | 3.8052 | 0.33187 | 14.416 | 3.6415 | 0.04025 | 1.0547 | 2.6104 | 0 | 0.33123 | 0 | 0.57555 | 27.0256 | 27.0256 | -3.8456e-05
ME_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 688247.9235 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126050.1988 | 0 | 0 | 1156488.5371 | 0 | 1156488.5371 | 0 | 0 | 7626.4752 | 0 | 0 | 0 | 3791.812 | 0 | 0 | 0 | 0 | 0 | 0 | 1396.7623 | 0 | 0 | 12815.0495 | 0 | 12815.0495 | 0 | 0 | 688.2479 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.0502 | 0 | 0 | 1156.4885 | 0 | 1156.4885 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3058 | 1.7043 | 0 | 0 | 15.6369 | 15.6369 | 0
ME_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 21150.4496 | 90892.4733 | 10861.4172 | 53987.5506 | 0 | 44237.5602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221129.4509 | 0 | 221127.228 | 2.2229 | 2.2229 | 0 | 2652.2664 | 11397.9162 | 1362.0217 | 6770.0389 | 0 | 5547.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27729.6331 | 0 | 27729.3544 | 0.27875 | 0.27875 | 0 | 72.1653 | 310.1251 | 37.0592 | 184.2055 | 0 | 150.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.4937 | 0 | 754.4861 | 0.0075844 | 0.0075844 | 12.5597 | 1.5009 | 7.4601 | 6.1129 | 0 | 0 | 2.9226 | 0 | 0 | 0 | 0 | 30.5559 | 30.5562 | 0.00030716
ME_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 616763.5563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92715.4707 | 0 | 0 | 709479.027 | 0 | 709479.027 | 0 | 0 | 6834.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1027.3801 | 0 | 0 | 7861.7371 | 0 | 7861.7371 | 0 | 0 | 616.7636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7155 | 0 | 0 | 709.479 | 0 | 709.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9783 | 3.7549 | 0 | 0 | 28.7332 | 28.7332 | 0
ME_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 19911.2088 | 75388.0712 | 10861.4172 | 53987.5506 | 0 | 42375.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202524.1683 | 0 | 202523.0569 | 1.1114 | 1.1114 | 0 | 2496.8656 | 9453.6641 | 1362.0217 | 6770.0389 | 0 | 5313.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25396.5307 | 0 | 25396.3913 | 0.13937 | 0.13937 | 0 | 67.937 | 257.2241 | 37.0592 | 184.2055 | 0 | 144.5866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.0125 | 0 | 691.0087 | 0.0037922 | 0.0037922 | 10.4173 | 1.5009 | 7.4601 | 5.8556 | 0 | 0 | 2.7514 | 0 | 0 | 0 | 0 | 27.9851 | 27.9853 | 0.00015358
ME_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 649794.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92724.9488 | 0 | 0 | 742519.9318 | 0 | 742519.9318 | 0 | 0 | 7200.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1027.4852 | 0 | 0 | 8227.8634 | 0 | 8227.8634 | 0 | 0 | 649.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7249 | 0 | 0 | 742.5199 | 0 | 742.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.316 | 3.7553 | 0 | 0 | 30.0713 | 30.0713 | 0
ME_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 46927.2127 | 51986.9826 | 79564.257 | 12297.9361 | 154949.5496 | 0 | 44946.0947 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 390744.2754 | 0 | 390743.7197 | 0.55571 | 0.55571 | 5884.6725 | 6519.1676 | 9977.3578 | 1542.1612 | 19430.6735 | 0 | 5636.2403 | 9.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 48999.3321 | 0 | 48999.2624 | 0.069686 | 0.069686 | 160.1156 | 177.3796 | 271.4732 | 41.9606 | 528.6879 | 0 | 153.3561 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.2195 | 0 | 1333.2176 | 0.0018961 | 0.0018961 | 6.2838 | 0.97126 | 12.2376 | 3.5497 | 0.0057056 | 0 | 4.1058 | 3.7062 | 0 | 0 | 0 | 30.8601 | 30.8601 | 4.3889e-05
ME_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 113207.2768 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 634667.8217 | 0 | 0 | 1147370.5364 | 0 | 1147370.5364 | 0 | 0 | 1254.4498 | 0 | 0 | 0 | 4426.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 7032.7541 | 0 | 0 | 12714.0129 | 0 | 12714.0129 | 0 | 0 | 113.2073 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 634.6678 | 0 | 0 | 1147.3705 | 0 | 1147.3705 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.6204 | 14.6907 | 0 | 0 | 26.5583 | 26.5583 | 0
ME_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 52703.8528 | 47660.7543 | 51131.1841 | 12297.9361 | 154949.5496 | 0 | 46735.4916 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 365551.0113 | 0 | 365547.1213 | 3.89 | 3.89 | 6609.0631 | 5976.6586 | 6411.8505 | 1542.1612 | 19430.6735 | 0 | 5860.6306 | 9.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 45840.0968 | 0 | 45839.609 | 0.48781 | 0.48781 | 179.8255 | 162.6185 | 174.4596 | 41.9606 | 528.6879 | 0 | 159.4615 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.2601 | 0 | 1247.2468 | 0.013273 | 0.013273 | 4.0382 | 0.97126 | 12.2376 | 3.6911 | 0.0057056 | 0 | 3.7641 | 4.1624 | 0 | 0 | 0 | 28.8701 | 28.8704 | 0.00030722
ME_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 99501.8413 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 634743.6471 | 0 | 0 | 1133740.9263 | 0 | 1133740.9263 | 0 | 0 | 1102.5799 | 0 | 0 | 0 | 4426.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 7033.5944 | 0 | 0 | 12562.9832 | 0 | 12562.9832 | 0 | 0 | 99.5018 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 634.7436 | 0 | 0 | 1133.7409 | 0 | 1133.7409 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.3032 | 14.6925 | 0 | 0 | 26.2428 | 26.2428 | 0
ME_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 4748.5705 | 2534.0528 | 8913.6419 | 1594.8973 | 13417.6985 | 0 | 4687.442 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40900.5016 | 0 | 40898.8344 | 1.6671 | 1.6671 | 595.4707 | 317.7702 | 1117.7707 | 200.0001 | 1682.5794 | 0 | 587.8052 | 0 | 0 | 0 | 0 | 627.5265 | 0 | 0 | 5128.9229 | 0 | 5128.7138 | 0.20906 | 0.20906 | 16.2021 | 8.6462 | 30.4133 | 5.4418 | 45.7812 | 0 | 15.9936 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.5525 | 0 | 139.5468 | 0.0056883 | 0.0056883 | 5.5277 | 0.98906 | 8.3208 | 2.9069 | 0 | 0 | 1.5715 | 2.9448 | 3.1033 | 0 | 0 | 25.3629 | 25.364 | 0.0010339
ME_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 17733.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17733.6583 | 0 | 17733.6583 | 0 | 0 | 196.5067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.5067 | 0 | 196.5067 | 0 | 0 | 17.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7337 | 0 | 17.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2231 | 0 | 0 | 0 | 3.2231 | 3.2231 | 0
ME_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 4840.2632 | 2311.7675 | 7202.0448 | 1594.8973 | 13417.6985 | 0 | 4240.0928 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38610.9626 | 0 | 38610.129 | 0.83357 | 0.83357 | 606.969 | 289.8956 | 903.1364 | 200.0001 | 1682.5794 | 0 | 531.7076 | 0 | 0 | 0 | 0 | 627.5265 | 0 | 0 | 4841.8147 | 0 | 4841.7102 | 0.10453 | 0.10453 | 16.515 | 7.8878 | 24.5734 | 5.4418 | 45.7812 | 0 | 14.4672 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.7406 | 0 | 131.7378 | 0.0028441 | 0.0028441 | 4.4663 | 0.98906 | 8.3208 | 2.6294 | 0 | 0 | 1.4336 | 3.0016 | 3.1033 | 0 | 0 | 23.9436 | 23.9441 | 0.00051693
ME_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | ME-BANGOR-ME | Zone6A | Zone6A(ME-BANGOR-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 18833.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18833.1262 | 0 | 18833.1262 | 0 | 0 | 208.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.6899 | 0 | 208.6899 | 0 | 0 | 18.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8331 | 0 | 18.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.423 | 0 | 0 | 0 | 3.423 | 3.423 | 0
ME_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 372322.3783 | 884020.44 | 97566.5905 | 4077910.5986 | 543459.8574 | 596741.6521 | 70783.9862 | 112129.0585 | 477844.0052 | 14140.1258 | 0 | 0 | 0 | 7246918.6927 | 0 | 7246914.8027 | 3.89 | 543463.7474 | 0 | 46689.2262 | 110856.1632 | 12234.8504 | 511369.9891 | 68149.8661 | 74831.4032 | 8876.3119 | 14060.9839 | 59921.6383 | 1773.1718 | 0 | 0 | 0 | 908763.6041 | 0 | 908763.1163 | 0.48781 | 68150.3539 | 0 | 1270.364 | 3016.2777 | 332.8972 | 13913.831 | 1854.285 | 2036.0825 | 241.515 | 382.5843 | 1630.4037 | 48.2461 | 0 | 0 | 0 | 24726.4866 | 0 | 24726.4733 | 0.013273 | 1854.2983 | 6.0496 | 0.66768 | 27.9065 | 4.0837 | 0.4844 | 0.096765 | 2.5479 | 0 | 0 | 3.27 | 0 | 49.593 | 49.593 | 2.662e-05
ME_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 1766882.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645340.2425 | 0 | 0 | 2412223.0049 | 0 | 2412223.0049 | 0 | 0 | 19578.8279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7151.0152 | 0 | 0 | 26729.8431 | 0 | 26729.8431 | 0 | 0 | 1766.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.3402 | 0 | 0 | 2412.223 | 0 | 2412.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5438 | 1.2943 | 0 | 0 | 4.8381 | 4.8381 | 0
ME_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 341947.0873 | 720385.0909 | 97566.5905 | 4077910.5986 | 543387.6147 | 567780.6516 | 67485.8276 | 99667.1869 | 477746.7554 | 13037.0349 | 0 | 0 | 0 | 7006914.4383 | 0 | 7006912.4933 | 1.945 | 543389.5597 | 0 | 42880.1648 | 90336.2904 | 12234.8504 | 511369.9891 | 68140.8069 | 71199.6937 | 8462.7228 | 12498.2652 | 59909.4431 | 1634.8442 | 0 | 0 | 0 | 878667.0706 | 0 | 878666.8267 | 0.2439 | 68141.0508 | 0 | 1166.7235 | 2457.9539 | 332.8972 | 13913.831 | 1854.0385 | 1937.2676 | 230.2616 | 340.0644 | 1630.0719 | 44.4824 | 0 | 0 | 0 | 23907.5921 | 0 | 23907.5854 | 0.0066363 | 1854.0452 | 4.9298 | 0.66768 | 27.9065 | 3.8855 | 0.46183 | 0.089217 | 2.3401 | 0 | 0 | 3.2694 | 0 | 47.9506 | 47.9506 | 1.331e-05
ME_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 1691645.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645235.9826 | 0 | 0 | 2336881.022 | 0 | 2336881.022 | 0 | 0 | 18745.1187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7149.8599 | 0 | 0 | 25894.9786 | 0 | 25894.9786 | 0 | 0 | 1691.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.236 | 0 | 0 | 2336.881 | 0 | 2336.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3929 | 1.2941 | 0 | 0 | 4.687 | 4.687 | 0
ME_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 15296.0096 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 20403.0151 | 0 | 0 | 0 | 0 | 128994.9582 | 0 | 0 | 342272.1796 | 0 | 342271.3461 | 0.83357 | 0.83357 | 0 | 1918.1196 | 3558.1903 | 902.788 | 17807.3276 | 0 | 2558.5381 | 0 | 0 | 0 | 0 | 16175.9678 | 0 | 0 | 42920.9313 | 0 | 42920.8268 | 0.10453 | 0.10453 | 0 | 52.19 | 96.8146 | 24.5639 | 484.5184 | 0 | 69.6151 | 0 | 0 | 0 | 0 | 440.1308 | 0 | 0 | 1167.8327 | 0 | 1167.8298 | 0.0028441 | 0.0028441 | 2.8693 | 0.72801 | 14.3599 | 2.0632 | 0 | 0 | 1.5468 | 0 | 13.0444 | 0 | 0 | 34.6116 | 34.6117 | 8.4293e-05
ME_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 293159.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293159.8352 | 0 | 293159.8352 | 0 | 0 | 3248.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3248.5041 | 0 | 3248.5041 | 0 | 0 | 293.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.1598 | 0 | 293.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6885 | 0 | 0 | 0 | 8.6885 | 8.6885 | 0
ME_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 14176.2472 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 18977.6104 | 0 | 0 | 0 | 0 | 128983.844 | 0 | 0 | 334522.7572 | 0 | 334526.3693 | -3.6121 | -3.6121 | 0 | 1777.7014 | 2906.9704 | 902.788 | 17807.3276 | 0 | 2379.7923 | 0 | 0 | 0 | 0 | 16174.574 | 0 | 0 | 41949.1537 | 0 | 41949.6067 | -0.45296 | -0.45296 | 0 | 48.3694 | 79.0956 | 24.5639 | 484.5184 | 0 | 64.7516 | 0 | 0 | 0 | 0 | 440.0929 | 0 | 0 | 1141.3916 | 0 | 1141.404 | -0.012325 | -0.012325 | 2.3442 | 0.72801 | 14.3599 | 1.9191 | 0 | 0 | 1.4335 | 0 | 13.0433 | 0 | 0 | 33.8284 | 33.828 | -0.00036527
ME_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 275274.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275274.5262 | 0 | 275274.5262 | 0 | 0 | 3050.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3050.317 | 0 | 3050.317 | 0 | 0 | 275.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.2745 | 0 | 275.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1585 | 0 | 0 | 0 | 8.1585 | 8.1585 | 0
ME_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 46279.8067 | 98858.624 | 7221.4948 | 317887.4784 | 4818.0346 | 96216.2071 | 116.6998 | 0 | 0 | 19347.1598 | 7179.8163 | 17604.9985 | 0 | 615530.32 | 0 | 615531.7093 | -1.3893 | 4816.6453 | 0 | 5803.4878 | 12396.8714 | 905.5754 | 39863.0898 | 604.1815 | 12065.5124 | 14.6342 | 0 | 0 | 2426.1338 | 900.349 | 2207.6668 | 0 | 77187.5021 | 0 | 77187.6763 | -0.17422 | 604.0073 | 0 | 157.9067 | 337.3056 | 24.6397 | 1084.6321 | 16.4391 | 328.2897 | 0.39818 | 0 | 0 | 66.0125 | 24.4975 | 60.0683 | 0 | 2100.1895 | 0 | 2100.1942 | -0.0047402 | 16.4344 | 4.5607 | 0.33315 | 14.6653 | 4.4388 | 0.0053838 | 0.89256 | 2.1351 | 0 | 0.33123 | 0 | 0.81218 | 28.3967 | 28.3967 | -6.4093e-05
ME_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 986270.0606 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133879.1682 | 0 | 0 | 1462339.6436 | 0 | 1462339.6436 | 0 | 0 | 10928.8585 | 0 | 0 | 0 | 3791.812 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.5151 | 0 | 0 | 16204.1856 | 0 | 16204.1856 | 0 | 0 | 986.2701 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.8792 | 0 | 0 | 1462.3396 | 0 | 1462.3396 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.3354 | 1.8102 | 0 | 0 | 19.7723 | 19.7723 | 0
ME_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 41700.7288 | 81428.6752 | 7221.4948 | 312483.1662 | 4745.7919 | 80367.2627 | 1197.5622 | 0 | 0 | 22962.0751 | 7182.5949 | 12461.8716 | 0 | 571751.2234 | 0 | 571750.1119 | 1.1114 | 4746.9033 | 0 | 5229.2714 | 10211.1559 | 905.5754 | 39185.389 | 595.1223 | 10078.0547 | 150.1743 | 0 | 0 | 2879.4442 | 900.6974 | 1562.7187 | 0 | 71697.6034 | 0 | 71697.464 | 0.13937 | 595.2617 | 0 | 142.2829 | 277.8346 | 24.6397 | 1066.1926 | 16.1926 | 274.2131 | 4.0861 | 0 | 0 | 78.3466 | 24.507 | 42.5199 | 0 | 1950.8152 | 0 | 1950.8114 | 0.0037922 | 16.1964 | 3.7566 | 0.33315 | 14.416 | 3.7076 | 0.055248 | 1.0593 | 1.9238 | 0 | 0.33136 | 0 | 0.57491 | 26.3769 | 26.377 | 5.1274e-05
ME_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 945637.1406 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133575.8667 | 0 | 0 | 1421403.4222 | 0 | 1421403.4222 | 0 | 0 | 10478.6052 | 0 | 0 | 0 | 3791.812 | 0 | 0 | 0 | 0 | 0 | 0 | 1480.1542 | 0 | 0 | 15750.5713 | 0 | 15750.5713 | 0 | 0 | 945.6371 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.5759 | 0 | 0 | 1421.4034 | 0 | 1421.4034 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.786 | 1.8061 | 0 | 0 | 19.2188 | 19.2188 | 0
ME_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 16685.2929 | 89761.5967 | 10900.3171 | 53987.5506 | 0 | 44382.0456 | 0 | 0 | 0 | 5398.7551 | 0 | 0 | 0 | 221115.558 | 0 | 221112.2237 | 3.3343 | 3.3343 | 0 | 2092.3357 | 11256.1042 | 1366.8998 | 6770.0389 | 0 | 5565.5085 | 0 | 0 | 0 | 677.0039 | 0 | 0 | 0 | 27727.891 | 0 | 27727.4729 | 0.41812 | 0.41812 | 0 | 56.9302 | 306.2666 | 37.1919 | 184.2055 | 0 | 151.4315 | 0 | 0 | 0 | 18.4206 | 0 | 0 | 0 | 754.4463 | 0 | 754.4349 | 0.011377 | 0.011377 | 12.4035 | 1.5062 | 7.4601 | 6.1328 | 0 | 0.74601 | 2.3056 | 0 | 0 | 0 | 0 | 30.5538 | 30.5543 | 0.00046074
ME_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 427238.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95085.0135 | 0 | 0 | 522323.0585 | 0 | 522323.0585 | 0 | 0 | 4734.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053.637 | 0 | 0 | 5787.8618 | 0 | 5787.8618 | 0 | 0 | 427.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.085 | 0 | 0 | 522.3231 | 0 | 522.3231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.3027 | 3.8508 | 0 | 0 | 21.1535 | 21.1535 | 0
ME_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 0 | 14581.9179 | 74371.1158 | 10900.3171 | 53987.5506 | 0 | 45471.2438 | 0 | 0 | 0 | 5501.562 | 0 | 0 | 0 | 204813.7073 | 0 | 204811.4844 | 2.2229 | 2.2229 | 0 | 1828.5725 | 9326.1379 | 1366.8998 | 6770.0389 | 0 | 5702.094 | 0 | 0 | 0 | 689.8959 | 0 | 0 | 0 | 25683.6389 | 0 | 25683.3601 | 0.27875 | 0.27875 | 0 | 49.7535 | 253.7542 | 37.1919 | 184.2055 | 0 | 155.1479 | 0 | 0 | 0 | 18.7713 | 0 | 0 | 0 | 698.8244 | 0 | 698.8168 | 0.0075844 | 0.0075844 | 10.2768 | 1.5062 | 7.4601 | 6.2833 | 0 | 0.76022 | 2.015 | 0 | 0 | 0 | 0 | 28.3013 | 28.3017 | 0.00030716
ME_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 449616.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95103.9698 | 0 | 0 | 544719.977 | 0 | 544719.977 | 0 | 0 | 4982.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053.8471 | 0 | 0 | 6036.0421 | 0 | 6036.0421 | 0 | 0 | 449.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.104 | 0 | 0 | 544.72 | 0 | 544.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.209 | 3.8516 | 0 | 0 | 22.0606 | 22.0606 | 0
ME_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 68905.6752 | 42178.6422 | 79203.0433 | 12295.1576 | 154949.5496 | 0 | 55362.9411 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 412967.2517 | 0 | 412965.5846 | 1.6671 | 1.6671 | 8640.7717 | 5289.2017 | 9932.0616 | 1541.8128 | 19430.6735 | 0 | 6942.5128 | 9.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 51786.0934 | 0 | 51785.8843 | 0.20906 | 0.20906 | 235.1062 | 143.9135 | 270.2408 | 41.9511 | 528.6879 | 0 | 188.8984 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1409.0443 | 0 | 1409.0386 | 0.0056883 | 0.0056883 | 6.2553 | 0.97104 | 12.2376 | 4.3724 | 0.0057056 | 0 | 3.3312 | 5.442 | 0 | 0 | 0 | 32.6151 | 32.6153 | 0.00013167
ME_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 149935.1902 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 681205.6423 | 0 | 0 | 1230636.2704 | 0 | 1230636.2704 | 0 | 0 | 1661.4318 | 0 | 0 | 0 | 4426.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 7548.4397 | 0 | 0 | 13636.6805 | 0 | 13636.6805 | 0 | 0 | 149.9352 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 681.2056 | 0 | 0 | 1230.6363 | 0 | 1230.6363 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.4706 | 15.7679 | 0 | 0 | 28.4856 | 28.4856 | 0
ME_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 75315.8285 | 38405.3487 | 51008.9272 | 12295.1576 | 154949.5496 | 0 | 52464.8961 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 384511.9503 | 0 | 384511.1168 | 0.83357 | 0.83357 | 9444.6049 | 4816.0307 | 6396.5195 | 1541.8128 | 19430.6735 | 0 | 6579.098 | 9.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 48217.7986 | 0 | 48217.694 | 0.10453 | 0.10453 | 256.9776 | 131.039 | 174.0425 | 41.9511 | 528.6879 | 0 | 179.0102 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.9548 | 0 | 1311.9519 | 0.0028441 | 0.0028441 | 4.0286 | 0.97104 | 12.2376 | 4.1436 | 0.0057056 | 0 | 3.0332 | 5.9483 | 0 | 0 | 0 | 30.3679 | 30.3679 | 6.5834e-05
ME_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 143139.3415 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 681262.5113 | 0 | 0 | 1223897.2907 | 0 | 1223897.2907 | 0 | 0 | 1586.127 | 0 | 0 | 0 | 4426.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 7549.0699 | 0 | 0 | 13562.0059 | 0 | 13562.0059 | 0 | 0 | 143.1393 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 681.2625 | 0 | 0 | 1223.8973 | 0 | 1223.8973 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.3133 | 15.7692 | 0 | 0 | 28.3296 | 28.3296 | 0
ME_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 5537.6834 | 1817.1826 | 8816.3921 | 1603.233 | 13417.6985 | 0 | 4937.513 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41133.9012 | 0 | 41132.234 | 1.6671 | 1.6671 | 694.4255 | 227.8747 | 1105.5756 | 201.0454 | 1682.5794 | 0 | 619.1641 | 0 | 0 | 0 | 0 | 627.5265 | 0 | 0 | 5158.1912 | 0 | 5157.9821 | 0.20906 | 0.20906 | 18.8946 | 6.2002 | 30.0815 | 5.4702 | 45.7812 | 0 | 16.8468 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.3489 | 0 | 140.3432 | 0.0056883 | 0.0056883 | 5.4674 | 0.99423 | 8.3208 | 3.0619 | 0 | 0 | 1.1269 | 3.4341 | 3.1033 | 0 | 0 | 25.5077 | 25.5087 | 0.0010339
ME_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 34728.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34728.0193 | 0 | 34728.0193 | 0 | 0 | 384.8212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384.8212 | 0 | 384.8212 | 0 | 0 | 34.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.728 | 0 | 34.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3119 | 0 | 0 | 0 | 6.3119 | 6.3119 | 0
ME_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Electricity | 5534.9048 | 1553.2188 | 7160.3663 | 1603.233 | 13417.6985 | 0 | 4317.8926 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38591.5127 | 0 | 38593.7355 | -2.2229 | -2.2229 | 694.0771 | 194.7736 | 897.9099 | 201.0454 | 1682.5794 | 0 | 541.4637 | 0 | 0 | 0 | 0 | 627.5265 | 0 | 0 | 4839.3757 | 0 | 4839.6544 | -0.27875 | -0.27875 | 18.8851 | 5.2996 | 24.4312 | 5.4702 | 45.7812 | 0 | 14.7326 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.6742 | 0 | 131.6818 | -0.0075844 | -0.0075844 | 4.4404 | 0.99423 | 8.3208 | 2.6777 | 0 | 0 | 0.96321 | 3.4324 | 3.1033 | 0 | 0 | 23.9334 | 23.9321 | -0.0013785
ME_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | ME-CARIBOU-ME | Zone7 | Zone7(ME-CARIBOU-ME) |  |  | ME | 0.1254 | 0.011081 |  |  |  | Natural Gas | 36718.4352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36718.4352 | 0 | 36718.4352 | 0 | 0 | 406.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.877 | 0 | 406.877 | 0 | 0 | 36.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7184 | 0 | 36.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6737 | 0 | 0 | 0 | 6.6737 | 6.6737 | 0
MI_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 558744.7527 | 881144.6235 | 96469.0566 | 4077910.5986 | 543457.0788 | 588769.9443 | 84815.748 | 184707.9988 | 388360.2652 | 12803.6353 | 0 | 0 | 0 | 7417183.7018 | 0 | 7417183.1461 | 0.55571 | 543457.6346 | 0 | 65764.2574 | 103710.7222 | 11354.408 | 479970.0775 | 63964.8982 | 69298.2224 | 9982.8135 | 21740.1315 | 45710.0032 | 1506.9879 | 0 | 0 | 0 | 873002.5217 | 0 | 873002.4563 | 0.065407 | 63964.9636 | 0 | 1906.4371 | 3006.4655 | 329.1524 | 13913.831 | 1854.2756 | 2008.883 | 289.3913 | 630.2237 | 1325.0852 | 43.686 | 0 | 0 | 0 | 25307.4308 | 0 | 25307.4289 | 0.0018961 | 1854.2774 | 6.03 | 0.66017 | 27.9065 | 4.0291 | 0.58042 | 0.087619 | 3.8237 | 0 | 0 | 2.6577 | 0 | 50.7582 | 50.7582 | 3.8029e-06
MI_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1506128.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590158.3298 | 0 | 0 | 2096287.1243 | 0 | 2096287.1243 | 0 | 0 | 9958.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3902.1269 | 0 | 0 | 13860.6505 | 0 | 13860.6505 | 0 | 0 | 1506.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.1583 | 0 | 0 | 2096.2871 | 0 | 2096.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0208 | 1.1837 | 0 | 0 | 4.2044 | 4.2044 | 0
MI_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 523651.4555 | 717075.818 | 96469.0566 | 4077910.5986 | 543387.6147 | 570128.5404 | 80342.2556 | 165763.7311 | 388087.9657 | 11392.1234 | 0 | 0 | 0 | 7174209.1597 | 0 | 7174206.1033 | 3.0564 | 543390.6711 | 0 | 61633.7763 | 84399.8238 | 11354.408 | 479970.0775 | 63956.7222 | 67104.1292 | 9456.2835 | 19510.3912 | 45677.9536 | 1340.8529 | 0 | 0 | 0 | 844404.4181 | 0 | 844404.0584 | 0.35974 | 63957.082 | 0 | 1786.6988 | 2446.6627 | 329.1524 | 13913.831 | 1854.0385 | 1945.2786 | 274.1278 | 565.5859 | 1324.1561 | 38.8699 | 0 | 0 | 0 | 24478.4017 | 0 | 24478.3912 | 0.010429 | 1854.049 | 4.9072 | 0.66017 | 27.9065 | 3.9016 | 0.54981 | 0.07796 | 3.5835 | 0 | 0 | 2.6558 | 0 | 49.0954 | 49.0954 | 2.0916e-05
MI_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1451989.4806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590196.2425 | 0 | 0 | 2042185.7231 | 0 | 2042185.7231 | 0 | 0 | 9600.5544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3902.3776 | 0 | 0 | 13502.932 | 0 | 13502.932 | 0 | 0 | 1451.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.1962 | 0 | 0 | 2042.1857 | 0 | 2042.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9122 | 1.1837 | 0 | 0 | 4.0959 | 4.0959 | 0
MI_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 22395.2475 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20769.786 | 0 | 0 | 0 | 0 | 118253.0194 | 0 | 0 | 338999.0281 | 0 | 338998.4724 | 0.55571 | 0.55571 | 0 | 2635.9206 | 3339.7049 | 847.6807 | 16713.8952 | 0 | 2444.6038 | 0 | 0 | 0 | 0 | 13918.3804 | 0 | 0 | 39900.1856 | 0 | 39900.1202 | 0.065407 | 0.065407 | 0 | 76.4126 | 96.8146 | 24.5734 | 484.5184 | 0 | 70.8665 | 0 | 0 | 0 | 0 | 403.4793 | 0 | 0 | 1156.6647 | 0 | 1156.6628 | 0.0018961 | 0.0018961 | 2.8693 | 0.72829 | 14.3599 | 2.1003 | 0 | 0 | 2.2647 | 0 | 11.9581 | 0 | 0 | 34.2806 | 34.2807 | 5.6196e-05
MI_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 197752.5639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197752.5639 | 0 | 197752.5639 | 0 | 0 | 1307.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1307.54 | 0 | 1307.54 | 0 | 0 | 197.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.7526 | 0 | 197.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8609 | 0 | 0 | 0 | 5.8609 | 5.8609 | 0
MI_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 21411.6349 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20264.0868 | 0 | 0 | 0 | 0 | 118283.5837 | 0 | 0 | 332347.1394 | 0 | 332344.9166 | 2.2229 | 2.2229 | 0 | 2520.1494 | 2728.4722 | 847.6807 | 16713.8952 | 0 | 2385.083 | 0 | 0 | 0 | 0 | 13921.9778 | 0 | 0 | 39117.2583 | 0 | 39116.9967 | 0.26163 | 0.26163 | 0 | 73.0565 | 79.0956 | 24.5734 | 484.5184 | 0 | 69.1411 | 0 | 0 | 0 | 0 | 403.5836 | 0 | 0 | 1133.9684 | 0 | 1133.9609 | 0.0075844 | 0.0075844 | 2.3442 | 0.72829 | 14.3599 | 2.0492 | 0 | 0 | 2.1652 | 0 | 11.9612 | 0 | 0 | 33.6078 | 33.608 | 0.00022478
MI_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 218329.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218329.6736 | 0 | 218329.6736 | 0 | 0 | 1443.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.5958 | 0 | 1443.5958 | 0 | 0 | 218.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.3297 | 0 | 218.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4708 | 0 | 0 | 0 | 6.4708 | 6.4708 | 0
MI_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 87333.1294 | 96413.4853 | 7127.0235 | 317887.4784 | 4818.0346 | 94065.5965 | 1164.2194 | 0 | 0 | 19369.3883 | 7179.8163 | 17643.8984 | 0 | 653002.0703 | 0 | 653000.4032 | 1.6671 | 4819.7018 | 0 | 10279.1093 | 11347.8672 | 838.8507 | 37415.3562 | 567.0827 | 11071.5207 | 137.0286 | 0 | 0 | 2279.777 | 845.0644 | 2076.6868 | 0 | 76858.3437 | 0 | 76858.1475 | 0.19622 | 567.2789 | 0 | 297.9806 | 328.9628 | 24.3174 | 1084.6321 | 16.4391 | 320.9518 | 3.9723 | 0 | 0 | 66.0884 | 24.4975 | 60.201 | 0 | 2228.0431 | 0 | 2228.0374 | 0.0056883 | 16.4448 | 4.4479 | 0.3288 | 14.6653 | 4.3396 | 0.05371 | 0.89358 | 4.029 | 0 | 0.33123 | 0 | 0.81398 | 30.1253 | 30.1254 | 7.6911e-05
MI_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 665879.4395 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 123348.92 | 0 | 0 | 1131418.7743 | 0 | 1131418.7743 | 0 | 0 | 4402.7949 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 815.5831 | 0 | 0 | 7480.9409 | 0 | 7480.9409 | 0 | 0 | 665.8794 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3489 | 0 | 0 | 1131.4188 | 0 | 1131.4188 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.0034 | 1.6678 | 0 | 0 | 15.2979 | 15.2979 | 0
MI_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 82531.7662 | 78205.5378 | 7127.0235 | 312483.1662 | 4743.0133 | 80497.8554 | 819.6772 | 0 | 0 | 22798.1396 | 7179.8163 | 12489.6572 | 0 | 608875.6528 | 0 | 608878.4314 | -2.7786 | 4740.2348 | 0 | 9713.9889 | 9204.7918 | 838.8507 | 36779.2687 | 558.2527 | 9474.5976 | 96.476 | 0 | 0 | 2683.341 | 845.0644 | 1470.0327 | 0 | 71664.6643 | 0 | 71664.9914 | -0.32704 | 557.9256 | 0 | 281.5984 | 266.8373 | 24.3174 | 1066.1926 | 16.1832 | 274.6587 | 2.7967 | 0 | 0 | 77.7873 | 24.4975 | 42.6147 | 0 | 2077.4837 | 0 | 2077.4932 | -0.0094805 | 16.1737 | 3.6079 | 0.3288 | 14.416 | 3.7137 | 0.037815 | 1.0518 | 3.8075 | 0 | 0.33123 | 0 | 0.57619 | 28.0898 | 28.0897 | -0.00012819
MI_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 643131.8286 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 123055.0967 | 0 | 0 | 1108377.3401 | 0 | 1108377.3401 | 0 | 0 | 4252.3877 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 813.6403 | 0 | 0 | 7328.591 | 0 | 7328.591 | 0 | 0 | 643.1318 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0551 | 0 | 0 | 1108.3773 | 0 | 1108.3773 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.6958 | 1.6638 | 0 | 0 | 14.9864 | 14.9864 | 0
MI_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 29758.4492 | 84037.7493 | 10666.9175 | 53987.5506 | 0 | 44432.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222882.7264 | 0 | 222879.1143 | 3.6121 | 3.6121 | 0 | 3502.5695 | 9891.2431 | 1255.4962 | 6354.3347 | 0 | 5229.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26233.2969 | 0 | 26232.8718 | 0.42515 | 0.42515 | 0 | 101.5358 | 286.7368 | 36.3955 | 184.2055 | 0 | 151.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.4759 | 0 | 760.4635 | 0.012325 | 0.012325 | 11.6125 | 1.474 | 7.4601 | 6.1397 | 0 | 0 | 4.1121 | 0 | 0 | 0 | 0 | 30.798 | 30.7985 | 0.00049913
MI_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 599247.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91862.4353 | 0 | 0 | 691110.3312 | 0 | 691110.3312 | 0 | 0 | 3962.2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.3944 | 0 | 0 | 4569.6215 | 0 | 4569.6215 | 0 | 0 | 599.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8624 | 0 | 0 | 691.1103 | 0 | 691.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2689 | 3.7203 | 0 | 0 | 27.9892 | 27.9892 | 0
MI_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 27621.7314 | 66427.1937 | 10666.9175 | 53987.5506 | 0 | 42298.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201001.5138 | 0 | 201000.9581 | 0.55571 | 0.55571 | 0 | 3251.0778 | 7818.4807 | 1255.4962 | 6354.3347 | 0 | 4978.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23657.8782 | 0 | 23657.8128 | 0.065407 | 0.065407 | 0 | 94.2453 | 226.6496 | 36.3955 | 184.2055 | 0 | 144.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.8172 | 0 | 685.8153 | 0.0018961 | 0.0018961 | 9.1791 | 1.474 | 7.4601 | 5.8449 | 0 | 0 | 3.8168 | 0 | 0 | 0 | 0 | 27.7748 | 27.7749 | 7.679e-05
MI_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 632051.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91871.9134 | 0 | 0 | 723923.7599 | 0 | 723923.7599 | 0 | 0 | 4179.1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.4571 | 0 | 0 | 4786.5839 | 0 | 4786.5839 | 0 | 0 | 632.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8719 | 0 | 0 | 723.9238 | 0 | 723.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5974 | 3.7207 | 0 | 0 | 29.3182 | 29.3182 | 0
MI_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 46668.806 | 59508.5626 | 79191.929 | 12297.9361 | 154949.5496 | 0 | 45524.0365 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 398213.0627 | 0 | 398210.2841 | 2.7786 | 2.7786 | 5492.9185 | 7004.1578 | 9320.89 | 1447.4671 | 18237.562 | 0 | 5358.1791 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 46869.6775 | 0 | 46869.3504 | 0.32704 | 0.32704 | 159.234 | 203.0432 | 270.2029 | 41.9606 | 528.6879 | 0 | 155.328 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.703 | 0 | 1358.6935 | 0.0094805 | 0.0094805 | 6.2544 | 0.97126 | 12.2376 | 3.5954 | 0.0057056 | 0 | 4.6999 | 3.6858 | 0 | 0 | 0 | 31.4498 | 31.45 | 0.00021945
MI_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 103520.5858 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 618137.8912 | 0 | 0 | 1121153.9149 | 0 | 1121153.9149 | 0 | 0 | 684.4781 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4087.1277 | 0 | 0 | 7413.0697 | 0 | 7413.0697 | 0 | 0 | 103.5206 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 618.1379 | 0 | 0 | 1121.1539 | 0 | 1121.1539 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.3962 | 14.3081 | 0 | 0 | 25.9514 | 25.9514 | 0
MI_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 51895.2899 | 55337.934 | 50808.8704 | 12297.9361 | 154949.5496 | 0 | 43076.1193 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 368437.9421 | 0 | 368436.5528 | 1.3893 | 1.3893 | 6108.0756 | 6513.2748 | 5980.204 | 1447.4671 | 18237.562 | 0 | 5070.0592 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 43365.1458 | 0 | 43364.9823 | 0.16352 | 0.16352 | 177.0667 | 188.813 | 173.3599 | 41.9606 | 528.6879 | 0 | 146.9757 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.1103 | 0 | 1257.1055 | 0.0047402 | 0.0047402 | 4.0128 | 0.97126 | 12.2376 | 3.4021 | 0.0057056 | 0 | 4.3705 | 4.0986 | 0 | 0 | 0 | 29.0983 | 29.0984 | 0.00010972
MI_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 100411.7457 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 618213.7165 | 0 | 0 | 1118120.9001 | 0 | 1118120.9001 | 0 | 0 | 663.9225 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4087.6291 | 0 | 0 | 7393.0154 | 0 | 7393.0154 | 0 | 0 | 100.4117 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 618.2137 | 0 | 0 | 1118.1209 | 0 | 1118.1209 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.3242 | 14.3098 | 0 | 0 | 25.8812 | 25.8812 | 0
MI_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 5243.1553 | 3256.4802 | 8833.0635 | 1600.4544 | 13417.6985 | 0 | 4873.606 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42228.6564 | 0 | 42226.7114 | 1.945 | 1.945 | 617.1194 | 383.2877 | 1039.6516 | 188.3735 | 1579.2631 | 0 | 573.6234 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4970.3129 | 0 | 4970.0839 | 0.22893 | 0.22893 | 17.8896 | 11.1111 | 30.1384 | 5.4608 | 45.7812 | 0 | 16.6287 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.0842 | 0 | 144.0775 | 0.0066363 | 0.0066363 | 5.4777 | 0.9925 | 8.3208 | 3.0223 | 0 | 0 | 2.0195 | 3.2515 | 3.1033 | 0 | 0 | 26.1864 | 26.1876 | 0.0012062
MI_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 13752.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13752.8264 | 0 | 13752.8264 | 0 | 0 | 90.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9337 | 0 | 90.9337 | 0 | 0 | 13.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7528 | 0 | 13.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4996 | 0 | 0 | 0 | 2.4996 | 2.4996 | 0
MI_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 5276.4981 | 3067.5376 | 7115.9093 | 1600.4544 | 13417.6985 | 0 | 4470.7138 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39953.0103 | 0 | 39953.8439 | -0.83357 | -0.83357 | 621.0438 | 361.0492 | 837.5425 | 188.3735 | 1579.2631 | 0 | 526.203 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4702.4693 | 0 | 4702.5674 | -0.098111 | -0.098111 | 18.0034 | 10.4664 | 24.2795 | 5.4608 | 45.7812 | 0 | 15.2541 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.3197 | 0 | 136.3225 | -0.0028441 | -0.0028441 | 4.4128 | 0.9925 | 8.3208 | 2.7725 | 0 | 0 | 1.9023 | 3.2722 | 3.1033 | 0 | 0 | 24.7769 | 24.7764 | -0.00051693
MI_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | MI-LANSING-MI | Zone5A | Zone5A(MI-LANSING-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 14406.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14406.8202 | 0 | 14406.8202 | 0 | 0 | 95.2579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2579 | 0 | 95.2579 | 0 | 0 | 14.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4068 | 0 | 14.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6185 | 0 | 0 | 0 | 2.6185 | 2.6185 | 0
MI_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 451417.0575 | 880939.0095 | 96669.1134 | 4077910.5986 | 543457.0788 | 588853.3013 | 72428.8977 | 145369.0517 | 438988.5287 | 12873.0994 | 0 | 0 | 0 | 7308905.7368 | 0 | 7308909.3489 | -3.6121 | 543453.4667 | 0 | 53131.7877 | 103686.5214 | 11377.9547 | 479970.0775 | 63964.8982 | 69308.0336 | 8524.8813 | 17109.9374 | 51668.9498 | 1515.1638 | 0 | 0 | 0 | 860258.2052 | 0 | 860258.6304 | -0.42515 | 63964.473 | 0 | 1540.235 | 3005.7639 | 329.835 | 13913.831 | 1854.2756 | 2009.1675 | 247.1274 | 495.9992 | 1497.8289 | 43.923 | 0 | 0 | 0 | 24937.9864 | 0 | 24937.9987 | -0.012325 | 1854.2632 | 6.0286 | 0.66154 | 27.9065 | 4.0297 | 0.49565 | 0.088095 | 3.0892 | 0 | 0 | 3.0041 | 0 | 50.0172 | 50.0172 | -2.4719e-05
MI_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1400011.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615654.6103 | 0 | 0 | 2015665.8001 | 0 | 2015665.8001 | 0 | 0 | 9256.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4070.7083 | 0 | 0 | 13327.5823 | 0 | 13327.5823 | 0 | 0 | 1400.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615.6546 | 0 | 0 | 2015.6658 | 0 | 2015.6658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.808 | 1.2348 | 0 | 0 | 4.0427 | 4.0427 | 0
MI_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 418229.857 | 717373.1246 | 96669.1134 | 4077910.5986 | 543387.6147 | 566752.5819 | 68374.9689 | 129981.3494 | 438591.1937 | 11389.3448 | 0 | 0 | 0 | 7068659.7471 | 0 | 7068656.6907 | 3.0564 | 543390.6711 | 0 | 49225.6542 | 84434.8168 | 11377.9547 | 479970.0775 | 63956.7222 | 66706.7789 | 8047.7338 | 15298.8048 | 51622.1835 | 1340.5259 | 0 | 0 | 0 | 831981.2522 | 0 | 831980.8925 | 0.35974 | 63957.082 | 0 | 1427.0003 | 2447.6771 | 329.835 | 13913.831 | 1854.0385 | 1933.7598 | 233.2954 | 443.4964 | 1496.4732 | 38.8604 | 0 | 0 | 0 | 24118.2671 | 0 | 24118.2566 | 0.010429 | 1854.049 | 4.9092 | 0.66154 | 27.9065 | 3.8785 | 0.46791 | 0.077941 | 2.8621 | 0 | 0 | 3.0014 | 0 | 48.3731 | 48.3731 | 2.0916e-05
MI_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1357615.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615683.0448 | 0 | 0 | 1973298.3748 | 0 | 1973298.3748 | 0 | 0 | 8976.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4070.8963 | 0 | 0 | 13047.4489 | 0 | 13047.4489 | 0 | 0 | 1357.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615.683 | 0 | 0 | 1973.2984 | 0 | 1973.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7229 | 1.2349 | 0 | 0 | 3.9578 | 3.9578 | 0
MI_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 18688.6395 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20055.6943 | 0 | 0 | 0 | 0 | 123187.7539 | 0 | 0 | 339513.0629 | 0 | 339513.8965 | -0.83357 | -0.83357 | 0 | 2199.6529 | 3339.7049 | 847.6807 | 16713.8952 | 0 | 2360.5552 | 0 | 0 | 0 | 0 | 14499.1986 | 0 | 0 | 39960.6875 | 0 | 39960.7856 | -0.098111 | -0.098111 | 0 | 63.7656 | 96.8146 | 24.5734 | 484.5184 | 0 | 68.43 | 0 | 0 | 0 | 0 | 420.3166 | 0 | 0 | 1158.4186 | 0 | 1158.4214 | -0.0028441 | -0.0028441 | 2.8693 | 0.72829 | 14.3599 | 2.0281 | 0 | 0 | 1.8899 | 0 | 12.4571 | 0 | 0 | 34.3328 | 34.3327 | -8.4293e-05
MI_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 186539.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186539.8874 | 0 | 186539.8874 | 0 | 0 | 1233.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4017 | 0 | 1233.4017 | 0 | 0 | 186.5399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186.5399 | 0 | 186.5399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5286 | 0 | 0 | 0 | 5.5286 | 5.5286 | 0
MI_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 16965.9282 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 19322.1527 | 0 | 0 | 0 | 0 | 123226.6538 | 0 | 0 | 331902.5688 | 0 | 331904.5138 | -1.945 | -1.945 | 0 | 1996.8897 | 2728.4722 | 847.6807 | 16713.8952 | 0 | 2274.2174 | 0 | 0 | 0 | 0 | 14503.7772 | 0 | 0 | 39064.9323 | 0 | 39065.1613 | -0.22893 | -0.22893 | 0 | 57.8877 | 79.0956 | 24.5734 | 484.5184 | 0 | 65.9272 | 0 | 0 | 0 | 0 | 420.4493 | 0 | 0 | 1132.4516 | 0 | 1132.4582 | -0.0066363 | -0.0066363 | 2.3442 | 0.72829 | 14.3599 | 1.9539 | 0 | 0 | 1.7157 | 0 | 12.4611 | 0 | 0 | 33.5633 | 33.5631 | -0.00019668
MI_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 214860.6629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214860.6629 | 0 | 214860.6629 | 0 | 0 | 1420.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1420.6587 | 0 | 1420.6587 | 0 | 0 | 214.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8607 | 0 | 214.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3679 | 0 | 0 | 0 | 6.3679 | 6.3679 | 0
MI_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 62164.8724 | 96296.7855 | 7135.3592 | 317887.4784 | 4818.0346 | 94571.2956 | 1364.2762 | 0 | 0 | 20364.1152 | 7179.8163 | 17638.3413 | 0 | 629420.3749 | 0 | 629421.2084 | -0.83357 | 4817.2011 | 0 | 7316.8055 | 11334.1317 | 839.8318 | 37415.3562 | 567.0827 | 11131.0415 | 160.5753 | 0 | 0 | 2396.8564 | 845.0644 | 2076.0328 | 0 | 74082.7781 | 0 | 74082.8762 | -0.098111 | 566.9846 | 0 | 212.1065 | 328.5646 | 24.3458 | 1084.6321 | 16.4391 | 322.6773 | 4.6549 | 0 | 0 | 69.4824 | 24.4975 | 60.182 | 0 | 2147.5823 | 0 | 2147.5852 | -0.0028441 | 16.4363 | 4.4425 | 0.32918 | 14.6653 | 4.3629 | 0.062939 | 0.93947 | 2.8679 | 0 | 0.33123 | 0 | 0.81372 | 29.0375 | 29.0375 | -3.8456e-05
MI_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 753088.0927 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 128088.0056 | 0 | 0 | 1223366.5131 | 0 | 1223366.5131 | 0 | 0 | 4979.4185 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 846.9179 | 0 | 0 | 8088.8994 | 0 | 8088.8994 | 0 | 0 | 753.0881 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 128.088 | 0 | 0 | 1223.3665 | 0 | 1223.3665 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.1825 | 1.7319 | 0 | 0 | 16.5411 | 16.5411 | 0
MI_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 57580.2374 | 78544.523 | 7135.3592 | 312483.1662 | 4743.0133 | 80450.6197 | 939.1555 | 0 | 0 | 22770.354 | 7179.8163 | 12486.8787 | 0 | 584313.1233 | 0 | 584314.2348 | -1.1114 | 4741.9019 | 0 | 6777.1939 | 9244.6904 | 839.8318 | 36779.2687 | 558.2527 | 9469.0379 | 110.5386 | 0 | 0 | 2680.0707 | 845.0644 | 1469.7056 | 0 | 68773.6546 | 0 | 68773.7854 | -0.13081 | 558.1219 | 0 | 196.4638 | 267.9939 | 24.3458 | 1066.1926 | 16.1832 | 274.4975 | 3.2044 | 0 | 0 | 77.6924 | 24.4975 | 42.6052 | 0 | 1993.6764 | 0 | 1993.6802 | -0.0037922 | 16.1794 | 3.6235 | 0.32918 | 14.416 | 3.7115 | 0.043327 | 1.0505 | 2.6564 | 0 | 0.33123 | 0 | 0.57607 | 26.9566 | 26.9565 | -5.1274e-05
MI_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 740245.1707 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127851.0513 | 0 | 0 | 1210286.6369 | 0 | 1210286.6369 | 0 | 0 | 4894.5011 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 845.3512 | 0 | 0 | 8002.4152 | 0 | 8002.4152 | 0 | 0 | 740.2452 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.8511 | 0 | 0 | 1210.2866 | 0 | 1210.2866 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.0089 | 1.7287 | 0 | 0 | 16.3643 | 16.3643 | 0
MI_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 20447.4722 | 90720.2022 | 10680.8103 | 53987.5506 | 0 | 44518.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220354.2307 | 0 | 220353.9529 | 0.27786 | 0.27786 | 0 | 2406.6675 | 10677.7678 | 1257.1314 | 6354.3347 | 0 | 5239.7916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25935.693 | 0 | 25935.6603 | 0.032704 | 0.032704 | 0 | 69.7668 | 309.5373 | 36.4429 | 184.2055 | 0 | 151.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751.8486 | 0 | 751.8477 | 0.00094805 | 0.00094805 | 12.5359 | 1.4759 | 7.4601 | 6.1516 | 0 | 0 | 2.8255 | 0 | 0 | 0 | 0 | 30.449 | 30.4491 | 3.8395e-05
MI_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 684039.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93350.5081 | 0 | 0 | 777390.1237 | 0 | 777390.1237 | 0 | 0 | 4522.8699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2336 | 0 | 0 | 5140.1035 | 0 | 5140.1035 | 0 | 0 | 684.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3505 | 0 | 0 | 777.3901 | 0 | 777.3901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7029 | 3.7806 | 0 | 0 | 31.4835 | 31.4835 | 0
MI_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 19024.8461 | 75065.7575 | 10680.8103 | 53987.5506 | 0 | 42634.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201393.2917 | 0 | 201390.791 | 2.5007 | 2.5007 | 0 | 2239.2244 | 8835.2397 | 1257.1314 | 6354.3347 | 0 | 5018.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23703.9904 | 0 | 23703.6961 | 0.29433 | 0.29433 | 0 | 64.9128 | 256.1244 | 36.4429 | 184.2055 | 0 | 145.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.1539 | 0 | 687.1454 | 0.0085324 | 0.0085324 | 10.3728 | 1.4759 | 7.4601 | 5.8913 | 0 | 0 | 2.6289 | 0 | 0 | 0 | 0 | 27.8287 | 27.829 | 0.00034555
MI_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 716199.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93359.9863 | 0 | 0 | 809559.0367 | 0 | 809559.0367 | 0 | 0 | 4735.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2962 | 0 | 0 | 5352.8044 | 0 | 5352.8044 | 0 | 0 | 716.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.36 | 0 | 0 | 809.559 | 0 | 809.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0053 | 3.781 | 0 | 0 | 32.7863 | 32.7863 | 0
MI_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 51547.9691 | 49750.2364 | 79161.3648 | 12300.7147 | 154949.5496 | 0 | 45176.7157 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392958.7931 | 0 | 392958.2373 | 0.55571 | 0.55571 | 6067.196 | 5855.6028 | 9317.2926 | 1447.7941 | 18237.562 | 0 | 5317.2994 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 46251.2499 | 0 | 46251.1845 | 0.065407 | 0.065407 | 175.8817 | 169.7478 | 270.0986 | 41.97 | 528.6879 | 0 | 154.143 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1340.7754 | 0 | 1340.7735 | 0.0018961 | 0.0018961 | 6.252 | 0.97148 | 12.2376 | 3.568 | 0.0057056 | 0 | 3.9292 | 4.0711 | 0 | 0 | 0 | 31.035 | 31.035 | 4.3889e-05
MI_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 123652.2215 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 647235.8767 | 0 | 0 | 1170383.5361 | 0 | 1170383.5361 | 0 | 0 | 817.5885 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4279.5236 | 0 | 0 | 7738.5759 | 0 | 7738.5759 | 0 | 0 | 123.6522 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 647.2359 | 0 | 0 | 1170.3835 | 0 | 1170.3835 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.8622 | 14.9816 | 0 | 0 | 27.091 | 27.091 | 0
MI_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 57744.1728 | 45737.9862 | 50867.2203 | 12300.7147 | 154949.5496 | 0 | 42689.8985 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 364361.7848 | 0 | 364360.1176 | 1.6671 | 1.6671 | 6796.4891 | 5383.361 | 5987.0718 | 1447.7941 | 18237.562 | 0 | 5024.6011 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 42885.3821 | 0 | 42885.1858 | 0.19622 | 0.19622 | 197.0231 | 156.058 | 173.559 | 41.97 | 528.6879 | 0 | 145.6579 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.2024 | 0 | 1243.1967 | 0.0056883 | 0.0056883 | 4.0174 | 0.97148 | 12.2376 | 3.3716 | 0.0057056 | 0 | 3.6123 | 4.5605 | 0 | 0 | 0 | 28.7764 | 28.7765 | 0.00013167
MI_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 119358.6099 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 647311.7021 | 0 | 0 | 1166165.7499 | 0 | 1166165.7499 | 0 | 0 | 789.1991 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4280.025 | 0 | 0 | 7710.6879 | 0 | 7710.6879 | 0 | 0 | 119.3586 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 647.3117 | 0 | 0 | 1166.1657 | 0 | 1166.1657 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.7628 | 14.9834 | 0 | 0 | 26.9933 | 26.9933 | 0
MI_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 6065.6111 | 2384.0102 | 8819.1706 | 1603.233 | 13417.6985 | 0 | 4854.156 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42148.078 | 0 | 42149.1894 | -1.1114 | -1.1114 | 713.9224 | 280.598 | 1038.0164 | 188.7005 | 1579.2631 | 0 | 571.3342 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4960.8288 | 0 | 4960.9596 | -0.13081 | -0.13081 | 20.6959 | 8.1342 | 30.091 | 5.4702 | 45.7812 | 0 | 16.5624 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.8092 | 0 | 143.813 | -0.0037922 | -0.0037922 | 5.4691 | 0.99423 | 8.3208 | 3.0102 | 0 | 0 | 1.4784 | 3.7615 | 3.1033 | 0 | 0 | 26.1383 | 26.1376 | -0.00068924
MI_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 16302.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16302.4545 | 0 | 16302.4545 | 0 | 0 | 107.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7918 | 0 | 107.7918 | 0 | 0 | 16.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3025 | 0 | 16.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.963 | 0 | 0 | 0 | 2.963 | 2.963 | 0
MI_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 6135.0752 | 2156.1677 | 7127.0235 | 1603.233 | 13417.6985 | 0 | 4387.3568 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39830.7534 | 0 | 39831.3091 | -0.55571 | -0.55571 | 722.0984 | 253.7809 | 838.8507 | 188.7005 | 1579.2631 | 0 | 516.3919 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4688.0797 | 0 | 4688.1451 | -0.065407 | -0.065407 | 20.9329 | 7.3568 | 24.3174 | 5.4702 | 45.7812 | 0 | 14.9697 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.9025 | 0 | 135.9044 | -0.0018961 | -0.0018961 | 4.4197 | 0.99423 | 8.3208 | 2.7208 | 0 | 0 | 1.3371 | 3.8046 | 3.1033 | 0 | 0 | 24.7009 | 24.7006 | -0.00034462
MI_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | MI-ALPENACOUNTY-MI | Zone6A | Zone6A(MI-ALPENACOUNTY-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 17724.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17724.1801 | 0 | 17724.1801 | 0 | 0 | 117.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.1923 | 0 | 117.1923 | 0 | 0 | 17.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7242 | 0 | 17.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2214 | 0 | 0 | 0 | 3.2214 | 3.2214 | 0
MI_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 363144.7726 | 880430.5318 | 96919.1844 | 4077910.5986 | 543457.0788 | 604271.5678 | 70672.8436 | 111384.4026 | 441719.8598 | 12892.5494 | 0 | 0 | 0 | 7202803.3894 | 0 | 7202802.0002 | 1.3893 | 543458.4681 | 0 | 42742.1397 | 103626.6736 | 11407.388 | 479970.0775 | 63964.8982 | 71122.7635 | 8318.1937 | 13109.9442 | 51990.4275 | 1517.4531 | 0 | 0 | 0 | 847769.9589 | 0 | 847769.7954 | 0.16352 | 63965.0617 | 0 | 1239.05 | 3004.029 | 330.6883 | 13913.831 | 1854.2756 | 2061.7746 | 241.1357 | 380.0436 | 1507.1482 | 43.9894 | 0 | 0 | 0 | 24575.9652 | 0 | 24575.9604 | 0.0047402 | 1854.2803 | 6.0251 | 0.66325 | 27.9065 | 4.1352 | 0.48364 | 0.088228 | 2.4851 | 0 | 0 | 3.0228 | 0 | 49.2911 | 49.2911 | 9.5073e-06
MI_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1398978.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637027.8864 | 0 | 0 | 2036005.9555 | 0 | 2036005.9555 | 0 | 0 | 9250.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4212.0284 | 0 | 0 | 13462.0714 | 0 | 13462.0714 | 0 | 0 | 1398.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.0279 | 0 | 0 | 2036.006 | 0 | 2036.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8059 | 1.2777 | 0 | 0 | 4.0835 | 4.0835 | 0
MI_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 332866.7314 | 717431.4745 | 96919.1844 | 4077910.5986 | 543387.6147 | 576324.7441 | 66846.7572 | 99072.5736 | 441458.6745 | 11933.9439 | 0 | 0 | 0 | 6964152.2971 | 0 | 6964144.5171 | 7.78 | 543395.3947 | 0 | 39178.4143 | 84441.6846 | 11407.388 | 479970.0775 | 63956.7222 | 67833.4224 | 7867.8633 | 11660.8419 | 51959.686 | 1404.6252 | 0 | 0 | 0 | 819680.7254 | 0 | 819679.8097 | 0.9157 | 63957.638 | 0 | 1135.7413 | 2447.8762 | 330.6883 | 13913.831 | 1854.0385 | 1966.42 | 228.0811 | 338.0356 | 1506.257 | 40.7186 | 0 | 0 | 0 | 23761.6876 | 0 | 23761.6611 | 0.026545 | 1854.0651 | 4.9096 | 0.66325 | 27.9065 | 3.944 | 0.45745 | 0.081668 | 2.2779 | 0 | 0 | 3.021 | 0 | 47.6579 | 47.658 | 5.3241e-05
MI_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 1379320.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637046.8427 | 0 | 0 | 2016367.1847 | 0 | 2016367.1847 | 0 | 0 | 9120.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4212.1537 | 0 | 0 | 13332.2198 | 0 | 13332.2198 | 0 | 0 | 1379.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.0468 | 0 | 0 | 2016.3672 | 0 | 2016.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7665 | 1.2777 | 0 | 0 | 4.0442 | 4.0442 | 0
MI_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 16351.8649 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 19933.4374 | 0 | 0 | 0 | 0 | 127350.0468 | 0 | 0 | 341213.5457 | 0 | 341210.2114 | 3.3343 | 3.3343 | 0 | 1924.6145 | 3339.7049 | 847.3536 | 16713.8952 | 0 | 2346.1656 | 0 | 0 | 0 | 0 | 14989.1005 | 0 | 0 | 40160.8343 | 0 | 40160.4419 | 0.39244 | 0.39244 | 0 | 55.7926 | 96.8146 | 24.5639 | 484.5184 | 0 | 68.0129 | 0 | 0 | 0 | 0 | 434.5184 | 0 | 0 | 1164.2206 | 0 | 1164.2092 | 0.011377 | 0.011377 | 2.8693 | 0.72801 | 14.3599 | 2.0157 | 0 | 0 | 1.6536 | 0 | 12.8781 | 0 | 0 | 34.5043 | 34.5046 | 0.00033717
MI_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 225713.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225713.169 | 0 | 225713.169 | 0 | 0 | 1492.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1492.4155 | 0 | 1492.4155 | 0 | 0 | 225.7132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.7132 | 0 | 225.7132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6896 | 0 | 0 | 0 | 6.6896 | 6.6896 | 0
MI_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 15095.9528 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 18585.8325 | 0 | 0 | 0 | 0 | 127338.9325 | 0 | 0 | 333405.7734 | 0 | 333405.2176 | 0.55571 | 0.55571 | 0 | 1776.7936 | 2728.4722 | 847.3536 | 16713.8952 | 0 | 2187.5525 | 0 | 0 | 0 | 0 | 14987.7924 | 0 | 0 | 39241.8595 | 0 | 39241.7941 | 0.065407 | 0.065407 | 0 | 51.5074 | 79.0956 | 24.5639 | 484.5184 | 0 | 63.4149 | 0 | 0 | 0 | 0 | 434.4804 | 0 | 0 | 1137.5805 | 0 | 1137.5786 | 0.0018961 | 0.0018961 | 2.3442 | 0.72801 | 14.3599 | 1.8795 | 0 | 0 | 1.5266 | 0 | 12.8769 | 0 | 0 | 33.715 | 33.7151 | 5.6196e-05
MI_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 210453.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210453.3133 | 0 | 210453.3133 | 0 | 0 | 1391.5173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.5173 | 0 | 1391.5173 | 0 | 0 | 210.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.4533 | 0 | 210.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2373 | 0 | 0 | 0 | 6.2373 | 6.2373 | 0
MI_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 45960.2715 | 95063.1019 | 7138.1378 | 317887.4784 | 4818.0346 | 92273.421 | 125.0355 | 0 | 0 | 20322.4367 | 7179.8163 | 17621.6699 | 0 | 608389.4036 | 0 | 608393.0158 | -3.6121 | 4814.4225 | 0 | 5409.524 | 11188.9271 | 840.1588 | 37415.3562 | 567.0827 | 10860.5816 | 14.7167 | 0 | 0 | 2391.9508 | 845.0644 | 2074.0705 | 0 | 71607.4328 | 0 | 71607.858 | -0.42515 | 566.6575 | 0 | 156.8164 | 324.3553 | 24.3553 | 1084.6321 | 16.4391 | 314.8369 | 0.42662 | 0 | 0 | 69.3402 | 24.4975 | 60.1251 | 0 | 2075.8246 | 0 | 2075.837 | -0.012325 | 16.4268 | 4.3856 | 0.32931 | 14.6653 | 4.2569 | 0.0057683 | 0.93755 | 2.1203 | 0 | 0.33123 | 0 | 0.81295 | 28.0674 | 28.0672 | -0.00016664
MI_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 825273.8446 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 132229.9664 | 0 | 0 | 1299694.2258 | 0 | 1299694.2258 | 0 | 0 | 5456.7107 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 874.3045 | 0 | 0 | 8593.5782 | 0 | 8593.5782 | 0 | 0 | 825.2738 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 132.23 | 0 | 0 | 1299.6942 | 0 | 1299.6942 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.1585 | 1.7879 | 0 | 0 | 17.5732 | 17.5732 | 0
MI_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 41542.3505 | 77969.3597 | 7138.1378 | 312483.1662 | 4743.0133 | 77241.3752 | 989.1697 | 0 | 0 | 22787.0254 | 7182.5949 | 12478.543 | 0 | 564554.7357 | 0 | 564556.9585 | -2.2229 | 4740.7905 | 0 | 4889.5347 | 9176.9936 | 840.1588 | 36779.2687 | 558.2527 | 9091.3099 | 116.4253 | 0 | 0 | 2682.0329 | 845.3914 | 1468.7245 | 0 | 66448.0924 | 0 | 66448.354 | -0.26163 | 557.991 | 0 | 141.7425 | 266.0315 | 24.3553 | 1066.1926 | 16.1832 | 263.5476 | 3.375 | 0 | 0 | 77.7493 | 24.507 | 42.5768 | 0 | 1926.2608 | 0 | 1926.2683 | -0.0075844 | 16.1756 | 3.597 | 0.32931 | 14.416 | 3.5634 | 0.045634 | 1.0512 | 1.9165 | 0 | 0.33136 | 0 | 0.57568 | 26.0451 | 26.045 | -0.00010255
MI_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 795228.0419 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 131917.1868 | 0 | 0 | 1269335.6434 | 0 | 1269335.6434 | 0 | 0 | 5258.0478 | 0 | 0 | 0 | 2262.563 | 0 | 0 | 0 | 0 | 0 | 0 | 872.2364 | 0 | 0 | 8392.8473 | 0 | 8392.8473 | 0 | 0 | 795.228 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 131.9172 | 0 | 0 | 1269.3356 | 0 | 1269.3356 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.7523 | 1.7837 | 0 | 0 | 17.1627 | 17.1627 | 0
MI_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 16707.5215 | 89461.5115 | 10675.2532 | 53987.5506 | 0 | 42453.7203 | 0 | 0 | 0 | 5140.3484 | 0 | 0 | 0 | 218425.9055 | 0 | 218426.4612 | -0.55571 | -0.55571 | 0 | 1966.4753 | 10529.6199 | 1256.4773 | 6354.3347 | 0 | 4996.8029 | 0 | 0 | 0 | 605.019 | 0 | 0 | 0 | 25708.7291 | 0 | 25708.7945 | -0.065407 | -0.065407 | 0 | 57.0061 | 305.2427 | 36.424 | 184.2055 | 0 | 144.8521 | 0 | 0 | 0 | 17.5389 | 0 | 0 | 0 | 745.2692 | 0 | 745.2711 | -0.0018961 | -0.0018961 | 12.362 | 1.4751 | 7.4601 | 5.8664 | 0 | 0.71031 | 2.3087 | 0 | 0 | 0 | 0 | 30.1827 | 30.1826 | -7.679e-05
MI_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 372321.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94592.1486 | 0 | 0 | 466913.6697 | 0 | 466913.6697 | 0 | 0 | 2461.7899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.4433 | 0 | 0 | 3087.2332 | 0 | 3087.2332 | 0 | 0 | 372.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5921 | 0 | 0 | 466.9137 | 0 | 466.9137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0786 | 3.8309 | 0 | 0 | 18.9095 | 18.9095 | 0
MI_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 0 | 14534.6823 | 73996.0093 | 10675.2532 | 53987.5506 | 0 | 43315.076 | 0 | 0 | 0 | 5276.4981 | 0 | 0 | 0 | 201785.0696 | 0 | 201783.1246 | 1.945 | 1.945 | 0 | 1710.7321 | 8709.3303 | 1256.4773 | 6354.3347 | 0 | 5098.1844 | 0 | 0 | 0 | 621.0438 | 0 | 0 | 0 | 23750.1027 | 0 | 23749.8738 | 0.22893 | 0.22893 | 0 | 49.5923 | 252.4744 | 36.424 | 184.2055 | 0 | 147.791 | 0 | 0 | 0 | 18.0034 | 0 | 0 | 0 | 688.4907 | 0 | 688.484 | 0.0066363 | 0.0066363 | 10.2249 | 1.4751 | 7.4601 | 5.9854 | 0 | 0.72912 | 2.0084 | 0 | 0 | 0 | 0 | 27.8829 | 27.8831 | 0.00026876
MI_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 392879.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94601.6267 | 0 | 0 | 487481.3012 | 0 | 487481.3012 | 0 | 0 | 2597.7204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.506 | 0 | 0 | 3223.2264 | 0 | 3223.2264 | 0 | 0 | 392.8797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6016 | 0 | 0 | 487.4813 | 0 | 487.4813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9112 | 3.8313 | 0 | 0 | 19.7425 | 19.7425 | 0
MI_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 55640.7978 | 44684.9094 | 78939.0794 | 12295.1576 | 154949.5496 | 0 | 49300.1086 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 395881.8452 | 0 | 395881.5673 | 0.27786 | 0.27786 | 6548.9219 | 5259.4138 | 9291.1297 | 1447.14 | 18237.562 | 0 | 5802.6228 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 46595.2932 | 0 | 46595.2605 | 0.032704 | 0.032704 | 189.8464 | 152.4649 | 269.3401 | 41.9511 | 528.6879 | 0 | 168.212 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.7489 | 0 | 1350.7479 | 0.00094805 | 0.00094805 | 6.2344 | 0.97104 | 12.2376 | 3.8936 | 0.0057056 | 0 | 3.5291 | 4.3944 | 0 | 0 | 0 | 31.2659 | 31.2659 | 2.1945e-05
MI_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 132978.7419 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 671708.5148 | 0 | 0 | 1204182.6946 | 0 | 1204182.6946 | 0 | 0 | 879.2554 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4441.3367 | 0 | 0 | 7962.056 | 0 | 7962.056 | 0 | 0 | 132.9787 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 671.7085 | 0 | 0 | 1204.1827 | 0 | 1204.1827 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.0781 | 15.5481 | 0 | 0 | 27.8733 | 27.8733 | 0
MI_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 61370.2023 | 40028.0316 | 50825.5418 | 12295.1576 | 154949.5496 | 0 | 52423.2176 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371963.9432 | 0 | 371966.1661 | -2.2229 | -2.2229 | 7223.2728 | 4711.2993 | 5982.1663 | 1447.14 | 18237.562 | 0 | 6170.2127 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 43780.1561 | 0 | 43780.4177 | -0.26163 | -0.26163 | 209.3951 | 136.5756 | 173.4167 | 41.9511 | 528.6879 | 0 | 178.868 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.141 | 0 | 1269.1486 | -0.0075844 | -0.0075844 | 4.0141 | 0.97104 | 12.2376 | 4.1403 | 0.0057056 | 0 | 3.1613 | 4.8469 | 0 | 0 | 0 | 29.3771 | 29.3769 | -0.00017556
MI_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 124637.9513 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 671736.9493 | 0 | 0 | 1195870.3385 | 0 | 1195870.3385 | 0 | 0 | 824.1061 | 0 | 0 | 0 | 2641.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 4441.5247 | 0 | 0 | 7907.0947 | 0 | 7907.0947 | 0 | 0 | 124.638 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 671.7369 | 0 | 0 | 1195.8703 | 0 | 1195.8703 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.885 | 15.5487 | 0 | 0 | 27.6809 | 27.6809 | 0
MI_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 5345.9623 | 1892.2039 | 8771.935 | 1608.7901 | 13417.6985 | 0 | 4804.1418 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40844.9302 | 0 | 40845.7638 | -0.83357 | -0.83357 | 629.2198 | 222.7124 | 1032.4568 | 189.3546 | 1579.2631 | 0 | 565.4475 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4807.4483 | 0 | 4807.5464 | -0.098111 | -0.098111 | 18.2404 | 6.4562 | 29.9298 | 5.4892 | 45.7812 | 0 | 16.3917 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.3629 | 0 | 139.3657 | -0.0028441 | -0.0028441 | 5.4398 | 0.99767 | 8.3208 | 2.9792 | 0 | 0 | 1.1734 | 3.3152 | 3.1033 | 0 | 0 | 25.33 | 25.3295 | -0.00051693
MI_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 27524.6092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27524.6092 | 0 | 27524.6092 | 0 | 0 | 181.9927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181.9927 | 0 | 181.9927 | 0 | 0 | 27.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5246 | 0 | 27.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0027 | 0 | 0 | 0 | 5.0027 | 5.0027 | 0
MI_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Electricity | 5362.6337 | 1608.7901 | 7121.4664 | 1608.7901 | 13417.6985 | 0 | 4187.3 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38310.8774 | 0 | 38311.4331 | -0.55571 | -0.55571 | 631.182 | 189.3546 | 838.1966 | 189.3546 | 1579.2631 | 0 | 492.8452 | 0 | 0 | 0 | 0 | 588.9942 | 0 | 0 | 4509.1903 | 0 | 4509.2557 | -0.065407 | -0.065407 | 18.2973 | 5.4892 | 24.2984 | 5.4892 | 45.7812 | 0 | 14.2871 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.7167 | 0 | 130.7186 | -0.0018961 | -0.0018961 | 4.4163 | 0.99767 | 8.3208 | 2.5967 | 0 | 0 | 0.99767 | 3.3256 | 3.1033 | 0 | 0 | 23.7584 | 23.758 | -0.00034462
MI_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | MI-SAULTSTEMARIE-MI | Zone7 | Zone7(MI-SAULTSTEMARIE-MI) |  |  | MI | 0.1177 | 0.006612 |  |  |  | Natural Gas | 29382.3307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29382.3307 | 0 | 29382.3307 | 0 | 0 | 194.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.276 | 0 | 194.276 | 0 | 0 | 29.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.3823 | 0 | 29.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3403 | 0 | 0 | 0 | 5.3403 | 5.3403 | 0
MN_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 549280.9546 | 883309.1269 | 96193.9785 | 4077910.5986 | 543459.8574 | 585249.5003 | 83248.6364 | 187364.3085 | 403886.8958 | 12670.2641 | 0 | 0 | 0 | 7422574.1212 | 0 | 7422572.1762 | 1.945 | 543461.8024 | 0 | 58058.9969 | 93365.7747 | 10167.7035 | 431035.1503 | 57443.7069 | 61860.8722 | 8799.3809 | 19804.4074 | 42690.8449 | 1339.2469 | 0 | 0 | 0 | 784566.0846 | 0 | 784565.879 | 0.20559 | 57443.9125 | 0 | 1874.1466 | 3013.8507 | 328.2139 | 13913.831 | 1854.285 | 1996.8713 | 284.0443 | 639.287 | 1378.0621 | 43.2309 | 0 | 0 | 0 | 25325.8229 | 0 | 25325.8163 | 0.0066363 | 1854.2917 | 6.0448 | 0.65829 | 27.9065 | 4.0051 | 0.5697 | 0.086707 | 3.7589 | 0 | 0 | 2.7639 | 0 | 50.7951 | 50.7951 | 1.331e-05
MN_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1570959.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602375.6924 | 0 | 0 | 2173335.178 | 0 | 2173335.178 | 0 | 0 | 10033.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3847.3735 | 0 | 0 | 13881.0918 | 0 | 13881.0918 | 0 | 0 | 1570.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602.3757 | 0 | 0 | 2173.3352 | 0 | 2173.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1508 | 1.2082 | 0 | 0 | 4.359 | 4.359 | 0
MN_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 513979.2649 | 718654.0439 | 96193.9785 | 4077910.5986 | 543387.6147 | 567299.9595 | 79364.2001 | 168017.1487 | 403814.6531 | 11419.9091 | 0 | 0 | 0 | 7180041.3712 | 0 | 7180041.9269 | -0.55571 | 543387.059 | 0 | 54327.6083 | 75961.7324 | 10167.7035 | 431035.1503 | 57436.0709 | 59963.6057 | 8388.796 | 17759.4126 | 42683.2088 | 1207.0844 | 0 | 0 | 0 | 758930.3729 | 0 | 758930.4317 | -0.058739 | 57436.0121 | 0 | 1753.6973 | 2452.0476 | 328.2139 | 13913.831 | 1854.0385 | 1935.6275 | 270.7907 | 573.2745 | 1377.8156 | 38.9647 | 0 | 0 | 0 | 24498.3012 | 0 | 24498.3031 | -0.0018961 | 1854.0366 | 4.918 | 0.65829 | 27.9065 | 3.8822 | 0.54312 | 0.07815 | 3.5173 | 0 | 0 | 2.7634 | 0 | 49.1354 | 49.1354 | -3.8029e-06
MN_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1588797.4037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602460.996 | 0 | 0 | 2191258.3997 | 0 | 2191258.3997 | 0 | 0 | 10147.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3847.9184 | 0 | 0 | 13995.5674 | 0 | 13995.5674 | 0 | 0 | 1588.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602.461 | 0 | 0 | 2191.2584 | 0 | 2191.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1866 | 1.2083 | 0 | 0 | 4.3949 | 4.3949 | 0
MN_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 23545.5741 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 21383.8492 | 0 | 0 | 0 | 0 | 120592.5726 | 0 | 0 | 343100.1925 | 0 | 343098.2475 | 1.945 | 1.945 | 0 | 2488.7672 | 2999.2082 | 760.9624 | 15009.8447 | 0 | 2260.2729 | 0 | 0 | 0 | 0 | 12746.6349 | 0 | 0 | 36265.6903 | 0 | 36265.4848 | 0.20559 | 0.20559 | 0 | 80.3375 | 96.8146 | 24.5639 | 484.5184 | 0 | 72.9617 | 0 | 0 | 0 | 0 | 411.4619 | 0 | 0 | 1170.6579 | 0 | 1170.6512 | 0.0066363 | 0.0066363 | 2.8693 | 0.72801 | 14.3599 | 2.1624 | 0 | 0 | 2.381 | 0 | 12.1947 | 0 | 0 | 34.6952 | 34.6954 | 0.00019668
MN_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 196435.0981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196435.0981 | 0 | 196435.0981 | 0 | 0 | 1254.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.631 | 0 | 1254.631 | 0 | 0 | 196.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196.4351 | 0 | 196.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8219 | 0 | 0 | 0 | 5.8219 | 5.8219 | 0
MN_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 22553.6258 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 20883.7072 | 0 | 0 | 0 | 0 | 120623.1368 | 0 | 0 | 336445.5253 | 0 | 336449.971 | -4.4457 | -4.4457 | 0 | 2383.9182 | 2450.2932 | 760.9624 | 15009.8447 | 0 | 2207.4078 | 0 | 0 | 0 | 0 | 12749.8656 | 0 | 0 | 35562.292 | 0 | 35562.7619 | -0.46991 | -0.46991 | 0 | 76.953 | 79.0956 | 24.5639 | 484.5184 | 0 | 71.2552 | 0 | 0 | 0 | 0 | 411.5661 | 0 | 0 | 1147.9521 | 0 | 1147.9673 | -0.015169 | -0.015169 | 2.3442 | 0.72801 | 14.3599 | 2.1118 | 0 | 0 | 2.2807 | 0 | 12.1978 | 0 | 0 | 34.0229 | 34.0225 | -0.00044956
MN_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 218045.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218045.3285 | 0 | 218045.3285 | 0 | 0 | 1392.6555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.6555 | 0 | 1392.6555 | 0 | 0 | 218.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.0453 | 0 | 218.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4623 | 0 | 0 | 0 | 6.4623 | 6.4623 | 0
MN_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 82303.9237 | 99336.5375 | 7138.1378 | 317887.4784 | 4818.0346 | 98244.5608 | 1183.6694 | 0 | 0 | 20808.6859 | 7179.8163 | 17627.227 | 0 | 656528.0714 | 0 | 656529.1828 | -1.1114 | 4816.9232 | 0 | 8699.5247 | 10499.872 | 754.5012 | 33600.7065 | 509.2663 | 10384.4501 | 125.1139 | 0 | 0 | 2199.4781 | 758.9066 | 1863.1979 | 0 | 69395.0171 | 0 | 69395.1346 | -0.11748 | 509.1488 | 0 | 280.821 | 338.9363 | 24.3553 | 1084.6321 | 16.4391 | 335.2104 | 4.0387 | 0 | 0 | 70.9992 | 24.4975 | 60.1441 | 0 | 2240.0738 | 0 | 2240.0776 | -0.0037922 | 16.4353 | 4.5828 | 0.32931 | 14.6653 | 4.5324 | 0.054607 | 0.95998 | 3.797 | 0 | 0.33123 | 0 | 0.81321 | 30.2881 | 30.288 | -5.1274e-05
MN_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 884739.8907 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126220.8059 | 0 | 0 | 1353151.1114 | 0 | 1353151.1114 | 0 | 0 | 5650.8337 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 806.1723 | 0 | 0 | 8642.5761 | 0 | 8642.5761 | 0 | 0 | 884.7399 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.2208 | 0 | 0 | 1353.1511 | 0 | 1353.1511 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.9626 | 1.7066 | 0 | 0 | 18.296 | 18.296 | 0
MN_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 77791.5314 | 80717.3621 | 7138.1378 | 312483.1662 | 4745.7919 | 83401.4575 | 1089.1981 | 0 | 0 | 22767.5754 | 7182.5949 | 12464.6501 | 0 | 609781.4655 | 0 | 609782.2991 | -0.83357 | 4744.9583 | 0 | 8222.5649 | 8531.8252 | 754.5012 | 33029.4707 | 501.6302 | 8815.5341 | 115.1282 | 0 | 0 | 2406.5327 | 759.2003 | 1317.5135 | 0 | 64453.9009 | 0 | 64453.989 | -0.088108 | 501.5421 | 0 | 265.4247 | 275.4076 | 24.3553 | 1066.1926 | 16.1926 | 284.5658 | 3.7163 | 0 | 0 | 77.683 | 24.507 | 42.5294 | 0 | 2080.5744 | 0 | 2080.5772 | -0.0028441 | 16.1898 | 3.7238 | 0.32931 | 14.416 | 3.8476 | 0.050249 | 1.0504 | 3.5888 | 0 | 0.33136 | 0 | 0.57504 | 28.1315 | 28.1315 | -3.8456e-05
MN_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 848571.1894 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125936.4607 | 0 | 0 | 1316698.0649 | 0 | 1316698.0649 | 0 | 0 | 5419.8242 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 804.3562 | 0 | 0 | 8409.7505 | 0 | 8409.7505 | 0 | 0 | 848.5712 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.9365 | 0 | 0 | 1316.6981 | 0 | 1316.6981 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.4735 | 1.7028 | 0 | 0 | 17.8031 | 17.8031 | 0
MN_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 30116.8843 | 85218.6401 | 10736.3817 | 53987.5506 | 0 | 46710.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226769.9412 | 0 | 226768.8298 | 1.1114 | 1.1114 | 0 | 3183.3547 | 9007.6103 | 1134.8355 | 5706.4841 | 0 | 4937.2982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23969.5828 | 0 | 23969.4653 | 0.11748 | 0.11748 | 0 | 102.7588 | 290.766 | 36.6325 | 184.2055 | 0 | 159.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.739 | 0 | 773.7352 | 0.0037922 | 0.0037922 | 11.7757 | 1.4836 | 7.4601 | 6.4546 | 0 | 0 | 4.1616 | 0 | 0 | 0 | 0 | 31.3355 | 31.3356 | 0.00015358
MN_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 706616.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92563.8199 | 0 | 0 | 799180.4392 | 0 | 799180.4392 | 0 | 0 | 4513.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.2051 | 0 | 0 | 5104.3655 | 0 | 5104.3655 | 0 | 0 | 706.6166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5638 | 0 | 0 | 799.1804 | 0 | 799.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6172 | 3.7487 | 0 | 0 | 32.366 | 32.366 | 0
MN_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 28055.1878 | 67610.8631 | 10736.3817 | 53987.5506 | 0 | 44771.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205161.0281 | 0 | 205159.9167 | 1.1114 | 1.1114 | 0 | 2965.4333 | 7146.4682 | 1134.8355 | 5706.4841 | 0 | 4732.2995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21685.5207 | 0 | 21685.4032 | 0.11748 | 0.11748 | 0 | 95.7243 | 230.6883 | 36.6325 | 184.2055 | 0 | 152.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.0094 | 0 | 700.0056 | 0.0037922 | 0.0037922 | 9.3426 | 1.4836 | 7.4601 | 6.1866 | 0 | 0 | 3.8767 | 0 | 0 | 0 | 0 | 28.3495 | 28.3496 | 0.00015358
MN_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 739202.5719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92573.2981 | 0 | 0 | 831775.87 | 0 | 831775.87 | 0 | 0 | 4721.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.2657 | 0 | 0 | 5312.5525 | 0 | 5312.5525 | 0 | 0 | 739.2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5733 | 0 | 0 | 831.7759 | 0 | 831.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.9369 | 3.7491 | 0 | 0 | 33.686 | 33.686 | 0
MN_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 54701.6423 | 60061.4974 | 79492.0142 | 12297.9361 | 154949.5496 | 0 | 45665.7434 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 407240.6258 | 0 | 407239.2365 | 1.3893 | 1.3893 | 5781.9636 | 6348.5003 | 8402.3059 | 1299.8918 | 16378.1674 | 0 | 4826.8691 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 43045.3341 | 0 | 43045.1873 | 0.14685 | 0.14685 | 186.642 | 204.9298 | 271.2268 | 41.9606 | 528.6879 | 0 | 155.8115 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1389.505 | 0 | 1389.5003 | 0.0047402 | 0.0047402 | 6.2781 | 0.97126 | 12.2376 | 3.6066 | 0.0057056 | 0 | 4.7435 | 4.3202 | 0 | 0 | 0 | 32.1629 | 32.163 | 0.00010972
MN_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 125472.0303 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 632032.8901 | 0 | 0 | 1157000.3584 | 0 | 1157000.3584 | 0 | 0 | 801.3899 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.7941 | 0 | 0 | 7389.7613 | 0 | 7389.7613 | 0 | 0 | 125.472 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 632.0329 | 0 | 0 | 1157.0004 | 0 | 1157.0004 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.9043 | 14.6297 | 0 | 0 | 26.7812 | 26.7812 | 0
MN_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 59797.5336 | 55932.5473 | 50992.2558 | 12297.9361 | 154949.5496 | 0 | 43212.269 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 377254.3342 | 0 | 377254.8899 | -0.55571 | -0.55571 | 6320.5993 | 5912.0703 | 5389.8814 | 1299.8918 | 16378.1674 | 0 | 4567.5368 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 39875.7831 | 0 | 39875.8419 | -0.058739 | -0.058739 | 204.0292 | 190.8419 | 173.9856 | 41.9606 | 528.6879 | 0 | 147.4403 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.1918 | 0 | 1287.1937 | -0.0018961 | -0.0018961 | 4.0273 | 0.97126 | 12.2376 | 3.4128 | 0.0057056 | 0 | 4.4174 | 4.7227 | 0 | 0 | 0 | 29.7948 | 29.7947 | -4.3889e-05
MN_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 120581.294 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 632108.7155 | 0 | 0 | 1152185.4474 | 0 | 1152185.4474 | 0 | 0 | 770.1527 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.2784 | 0 | 0 | 7359.0085 | 0 | 7359.0085 | 0 | 0 | 120.5813 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 632.1087 | 0 | 0 | 1152.1854 | 0 | 1152.1854 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.7911 | 14.6315 | 0 | 0 | 26.6697 | 26.6697 | 0
MN_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 4815.2561 | 3164.7875 | 8913.6419 | 1592.1187 | 13417.6985 | 0 | 5070.8842 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41978.5854 | 0 | 41977.1962 | 1.3893 | 1.3893 | 508.9726 | 334.518 | 942.172 | 168.2869 | 1418.2507 | 0 | 535.9925 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4437.1365 | 0 | 4436.9896 | 0.14685 | 0.14685 | 16.4297 | 10.7983 | 30.4133 | 5.4323 | 45.7812 | 0 | 17.3019 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.2309 | 0 | 143.2262 | 0.0047402 | 0.0047402 | 5.5277 | 0.98733 | 8.3208 | 3.1446 | 0 | 0 | 1.9626 | 2.9861 | 3.1033 | 0 | 0 | 26.0317 | 26.0325 | 0.00086155
MN_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 26463.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26463.054 | 0 | 26463.054 | 0 | 0 | 169.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.0195 | 0 | 169.0195 | 0 | 0 | 26.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.4631 | 0 | 26.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8097 | 0 | 0 | 0 | 4.8097 | 4.8097 | 0
MN_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 4845.8203 | 2986.9592 | 7177.0377 | 1592.1187 | 13417.6985 | 0 | 4670.7706 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39694.6036 | 0 | 39694.0479 | 0.55571 | 0.55571 | 512.2032 | 315.7216 | 758.6129 | 168.2869 | 1418.2507 | 0 | 493.7005 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4195.7196 | 0 | 4195.6609 | 0.058739 | 0.058739 | 16.5339 | 10.1915 | 24.4881 | 5.4323 | 45.7812 | 0 | 15.9367 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.438 | 0 | 135.4361 | 0.0018961 | 0.0018961 | 4.4508 | 0.98733 | 8.3208 | 2.8965 | 0 | 0 | 1.8523 | 3.0051 | 3.1033 | 0 | 0 | 24.6158 | 24.6161 | 0.00034462
MN_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | MN-WINONA-MN | Zone5A | Zone5A(MN-WINONA-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 27079.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27079.1351 | 0 | 27079.1351 | 0 | 0 | 172.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.9544 | 0 | 172.9544 | 0 | 0 | 27.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0791 | 0 | 27.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9217 | 0 | 0 | 0 | 4.9217 | 4.9217 | 0
MN_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 559114.3021 | 881919.8436 | 96391.2568 | 4077910.5986 | 543459.8574 | 601140.1232 | 85068.5975 | 188095.0716 | 439577.5849 | 13084.2705 | 0 | 0 | 0 | 7485761.5061 | 0 | 7485762.6175 | -1.1114 | 543458.746 | 0 | 59098.3817 | 93218.9275 | 10188.5558 | 431035.1503 | 57443.7069 | 63540.511 | 8991.7508 | 19881.6491 | 46463.3507 | 1383.0074 | 0 | 0 | 0 | 791244.9912 | 0 | 791245.1087 | -0.11748 | 57443.5895 | 0 | 1907.698 | 3009.1105 | 328.887 | 13913.831 | 1854.285 | 2051.0901 | 290.2541 | 641.7804 | 1499.8387 | 44.6435 | 0 | 0 | 0 | 25541.4183 | 0 | 25541.4221 | -0.0037922 | 1854.2812 | 6.0353 | 0.65964 | 27.9065 | 4.1138 | 0.58215 | 0.08954 | 3.8262 | 0 | 0 | 3.0082 | 0 | 51.2275 | 51.2275 | -7.6059e-06
MN_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1667077.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601437.3535 | 0 | 0 | 2268514.9732 | 0 | 2268514.9732 | 0 | 0 | 10647.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.3804 | 0 | 0 | 14489.0051 | 0 | 14489.0051 | 0 | 0 | 1667.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.4374 | 0 | 0 | 2268.515 | 0 | 2268.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3436 | 1.2063 | 0 | 0 | 4.5499 | 4.5499 | 0
MN_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 520214.3685 | 718137.2305 | 96391.2568 | 4077910.5986 | 543387.6147 | 577313.9139 | 80236.6701 | 168458.9408 | 439263.6068 | 11619.9659 | 0 | 0 | 0 | 7232934.1665 | 0 | 7232931.1101 | 3.0564 | 543390.6711 | 0 | 54986.6588 | 75907.1053 | 10188.5558 | 431035.1503 | 57436.0709 | 61022.0807 | 8481.016 | 17806.11 | 46430.1632 | 1228.2304 | 0 | 0 | 0 | 764521.1414 | 0 | 764520.8183 | 0.32306 | 57436.3939 | 0 | 1774.9714 | 2450.2842 | 328.887 | 13913.831 | 1854.0385 | 1969.7951 | 273.7675 | 574.7819 | 1498.7674 | 39.6473 | 0 | 0 | 0 | 24678.7714 | 0 | 24678.7609 | 0.010429 | 1854.049 | 4.9144 | 0.65964 | 27.9065 | 3.9507 | 0.54909 | 0.079519 | 3.56 | 0 | 0 | 3.006 | 0 | 49.4973 | 49.4973 | 2.0916e-05
MN_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1657997.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601446.8317 | 0 | 0 | 2259444.3633 | 0 | 2259444.3633 | 0 | 0 | 10589.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.4409 | 0 | 0 | 14431.0711 | 0 | 14431.0711 | 0 | 0 | 1657.9975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.4468 | 0 | 0 | 2259.4444 | 0 | 2259.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3254 | 1.2063 | 0 | 0 | 4.5317 | 4.5317 | 0
MN_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 24268.0014 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 21556.1203 | 0 | 0 | 0 | 0 | 120442.53 | 0 | 0 | 343847.6269 | 0 | 343847.0712 | 0.55571 | 0.55571 | 0 | 2565.1277 | 2999.2082 | 761.2561 | 15009.8447 | 0 | 2278.4819 | 0 | 0 | 0 | 0 | 12730.7754 | 0 | 0 | 36344.6942 | 0 | 36344.6354 | 0.058739 | 0.058739 | 0 | 82.8024 | 96.8146 | 24.5734 | 484.5184 | 0 | 73.5495 | 0 | 0 | 0 | 0 | 410.9499 | 0 | 0 | 1173.2081 | 0 | 1173.2062 | 0.0018961 | 0.0018961 | 2.8693 | 0.72829 | 14.3599 | 2.1798 | 0 | 0 | 2.4541 | 0 | 12.1795 | 0 | 0 | 34.7709 | 34.771 | 5.6196e-05
MN_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 214500.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214500.4924 | 0 | 214500.4924 | 0 | 0 | 1370.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370.0146 | 0 | 1370.0146 | 0 | 0 | 214.5005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.5005 | 0 | 214.5005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3573 | 0 | 0 | 0 | 6.3573 | 6.3573 | 0
MN_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 22617.5328 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20803.1288 | 0 | 0 | 0 | 0 | 120478.6513 | 0 | 0 | 336287.147 | 0 | 336285.7577 | 1.3893 | 1.3893 | 0 | 2390.6732 | 2450.2932 | 761.2561 | 15009.8447 | 0 | 2198.8907 | 0 | 0 | 0 | 0 | 12734.5934 | 0 | 0 | 35545.5514 | 0 | 35545.4046 | 0.14685 | 0.14685 | 0 | 77.171 | 79.0956 | 24.5734 | 484.5184 | 0 | 70.9803 | 0 | 0 | 0 | 0 | 411.0732 | 0 | 0 | 1147.4117 | 0 | 1147.407 | 0.0047402 | 0.0047402 | 2.3442 | 0.72829 | 14.3599 | 2.1037 | 0 | 0 | 2.2872 | 0 | 12.1832 | 0 | 0 | 34.0063 | 34.0065 | 0.00014049
MN_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 241323.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241323.7169 | 0 | 241323.7169 | 0 | 0 | 1541.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1541.3346 | 0 | 1541.3346 | 0 | 0 | 241.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241.3237 | 0 | 241.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1522 | 0 | 0 | 0 | 7.1522 | 7.1522 | 0
MN_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 83445.9146 | 97674.9546 | 7140.9164 | 317887.4784 | 4818.0346 | 99467.1301 | 1217.0122 | 0 | 0 | 19558.3309 | 7179.8163 | 17596.6628 | 0 | 655986.2509 | 0 | 655986.2509 | 0 | 4818.0346 | 0 | 8820.2332 | 10324.2427 | 754.7949 | 33600.7065 | 509.2663 | 10513.6757 | 128.6382 | 0 | 0 | 2067.3156 | 758.9066 | 1859.9673 | 0 | 69337.7467 | 0 | 69337.7467 | 0 | 509.2663 | 0 | 284.7175 | 333.2669 | 24.3648 | 1084.6321 | 16.4391 | 339.3818 | 4.1524 | 0 | 0 | 66.733 | 24.4975 | 60.0398 | 0 | 2238.2251 | 0 | 2238.2251 | 0 | 16.4391 | 4.5061 | 0.32944 | 14.6653 | 4.5888 | 0.056145 | 0.9023 | 3.8497 | 0 | 0.33123 | 0 | 0.8118 | 30.2631 | 30.2631 | 0
MN_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 803872.134 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126135.5023 | 0 | 0 | 1272198.0511 | 0 | 1272198.0511 | 0 | 0 | 5134.3313 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 805.6275 | 0 | 0 | 8125.529 | 0 | 8125.529 | 0 | 0 | 803.8721 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.1355 | 0 | 0 | 1272.1981 | 0 | 1272.1981 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.8692 | 1.7055 | 0 | 0 | 17.2014 | 17.2014 | 0
MN_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 78208.3164 | 79800.4351 | 7140.9164 | 312483.1662 | 4745.7919 | 84401.7415 | 980.834 | 0 | 0 | 22875.9395 | 7182.5949 | 12456.3144 | 0 | 610276.0504 | 0 | 610278.829 | -2.7786 | 4743.0133 | 0 | 8266.619 | 8434.906 | 754.7949 | 33029.4707 | 501.6302 | 8921.2641 | 103.6742 | 0 | 0 | 2417.9868 | 759.2003 | 1316.6324 | 0 | 64506.1785 | 0 | 64506.4722 | -0.29369 | 501.3365 | 0 | 266.8468 | 272.2791 | 24.3648 | 1066.1926 | 16.1926 | 287.9787 | 3.3466 | 0 | 0 | 78.0527 | 24.507 | 42.5009 | 0 | 2082.2619 | 0 | 2082.2714 | -0.0094805 | 16.1832 | 3.6815 | 0.32944 | 14.416 | 3.8938 | 0.045249 | 1.0554 | 3.608 | 0 | 0.33136 | 0 | 0.57466 | 28.1544 | 28.1543 | -0.00012819
MN_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 781361.4774 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125898.548 | 0 | 0 | 1249450.4403 | 0 | 1249450.4403 | 0 | 0 | 4990.5558 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 804.114 | 0 | 0 | 7980.24 | 0 | 7980.24 | 0 | 0 | 781.3615 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.8985 | 0 | 0 | 1249.4504 | 0 | 1249.4504 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.5648 | 1.7023 | 0 | 0 | 16.8938 | 16.8938 | 0
MN_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 31047.7041 | 90825.7877 | 10725.2674 | 53987.5506 | 0 | 46966.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233552.4225 | 0 | 233552.9782 | -0.55571 | -0.55571 | 0 | 3281.7423 | 9600.2858 | 1133.6608 | 5706.4841 | 0 | 4964.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24686.4911 | 0 | 24686.5498 | -0.058739 | -0.058739 | 0 | 105.9348 | 309.8976 | 36.5946 | 184.2055 | 0 | 160.2484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.8809 | 0 | 796.8828 | -0.0018961 | -0.0018961 | 12.5505 | 1.482 | 7.4601 | 6.4899 | 0 | 0 | 4.2902 | 0 | 0 | 0 | 0 | 32.2729 | 32.2728 | -7.679e-05
MN_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 678058.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92525.9073 | 0 | 0 | 770584.7967 | 0 | 770584.7967 | 0 | 0 | 4330.7621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.963 | 0 | 0 | 4921.7251 | 0 | 4921.7251 | 0 | 0 | 678.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5259 | 0 | 0 | 770.5848 | 0 | 770.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4607 | 3.7472 | 0 | 0 | 31.2079 | 31.2079 | 0
MN_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 29019.3504 | 75215.8001 | 10725.2674 | 53987.5506 | 0 | 45121.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214069.1129 | 0 | 214066.0565 | 3.0564 | 3.0564 | 0 | 3067.3453 | 7950.3101 | 1133.6608 | 5706.4841 | 0 | 4769.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22627.1052 | 0 | 22626.7822 | 0.32306 | 0.32306 | 0 | 99.014 | 256.6363 | 36.5946 | 184.2055 | 0 | 153.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730.4038 | 0 | 730.3934 | 0.010429 | 0.010429 | 10.3935 | 1.482 | 7.4601 | 6.2349 | 0 | 0 | 4.01 | 0 | 0 | 0 | 0 | 29.5802 | 29.5806 | 0.00042234
MN_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 709175.7255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92535.3854 | 0 | 0 | 801711.111 | 0 | 801711.111 | 0 | 0 | 4529.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.0235 | 0 | 0 | 5120.5289 | 0 | 5120.5289 | 0 | 0 | 709.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5354 | 0 | 0 | 801.7111 | 0 | 801.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7209 | 3.7476 | 0 | 0 | 32.4685 | 32.4685 | 0
MN_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 56177.0612 | 59608.591 | 79261.3932 | 12300.7147 | 154949.5496 | 0 | 45813.0075 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 408182.5599 | 0 | 408184.227 | -1.6671 | -1.6671 | 5937.9154 | 6300.6281 | 8377.9293 | 1300.1855 | 16378.1674 | 0 | 4842.4349 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 43144.8966 | 0 | 43145.0728 | -0.17622 | -0.17622 | 191.6761 | 203.3845 | 270.4399 | 41.97 | 528.6879 | 0 | 156.314 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.7189 | 0 | 1392.7246 | -0.0056883 | -0.0056883 | 6.2599 | 0.97148 | 12.2376 | 3.6182 | 0.0057056 | 0 | 4.7078 | 4.4367 | 0 | 0 | 0 | 32.2375 | 32.2374 | -0.00013167
MN_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 124287.2589 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 631094.5512 | 0 | 0 | 1154877.248 | 0 | 1154877.248 | 0 | 0 | 793.8227 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.8009 | 0 | 0 | 7376.201 | 0 | 7376.201 | 0 | 0 | 124.2873 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 631.0946 | 0 | 0 | 1154.8772 | 0 | 1154.8772 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.8769 | 14.608 | 0 | 0 | 26.732 | 26.732 | 0
MN_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 62020.3869 | 55279.5841 | 50928.3487 | 12300.7147 | 154949.5496 | 0 | 43323.4117 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378874.2385 | 0 | 378873.6828 | 0.55571 | 0.55571 | 6555.5549 | 5843.052 | 5383.1265 | 1300.1855 | 16378.1674 | 0 | 4579.2846 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 40047.007 | 0 | 40046.9483 | 0.058739 | 0.058739 | 211.6136 | 188.6139 | 173.7675 | 41.97 | 528.6879 | 0 | 147.8195 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1292.7189 | 0 | 1292.717 | 0.0018961 | 0.0018961 | 4.0222 | 0.97148 | 12.2376 | 3.4216 | 0.0057056 | 0 | 4.3659 | 4.8982 | 0 | 0 | 0 | 29.9226 | 29.9227 | 4.3889e-05
MN_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 119661.9114 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 631170.3766 | 0 | 0 | 1150327.7259 | 0 | 1150327.7259 | 0 | 0 | 764.2806 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.2852 | 0 | 0 | 7347.1432 | 0 | 7347.1432 | 0 | 0 | 119.6619 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 631.1704 | 0 | 0 | 1150.3277 | 0 | 1150.3277 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.7698 | 14.6097 | 0 | 0 | 26.6267 | 26.6267 | 0
MN_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 5015.3129 | 3381.5157 | 8833.0635 | 1594.8973 | 13417.6985 | 0 | 5151.4626 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42398.149 | 0 | 42395.3704 | 2.7786 | 2.7786 | 530.1186 | 357.4262 | 933.6548 | 168.5806 | 1418.2507 | 0 | 544.5096 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4481.4843 | 0 | 4481.1907 | 0.29369 | 0.29369 | 17.1122 | 11.5377 | 30.1384 | 5.4418 | 45.7812 | 0 | 17.5768 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.6625 | 0 | 144.653 | 0.0094805 | 0.0094805 | 5.4777 | 0.98906 | 8.3208 | 3.1946 | 0 | 0 | 2.097 | 3.1102 | 3.1033 | 0 | 0 | 26.291 | 26.2927 | 0.0017231
MN_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 23136.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23136.2159 | 0 | 23136.2159 | 0 | 0 | 147.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.771 | 0 | 147.771 | 0 | 0 | 23.1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1362 | 0 | 23.1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2051 | 0 | 0 | 0 | 4.2051 | 4.2051 | 0
MN_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 5112.5627 | 3120.3304 | 7140.9164 | 1594.8973 | 13417.6985 | 0 | 4673.5492 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40064.153 | 0 | 40063.5973 | 0.55571 | 0.55571 | 540.3979 | 329.8189 | 754.7949 | 168.5806 | 1418.2507 | 0 | 493.9941 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4234.781 | 0 | 4234.7222 | 0.058739 | 0.058739 | 17.4441 | 10.6466 | 24.3648 | 5.4418 | 45.7812 | 0 | 15.9461 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.6989 | 0 | 136.697 | 0.0018961 | 0.0018961 | 4.4284 | 0.98906 | 8.3208 | 2.8982 | 0 | 0 | 1.935 | 3.1705 | 3.1033 | 0 | 0 | 24.845 | 24.8453 | 0.00034462
MN_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | MN-MINNEAPOLISSTPAUL-MN | Zone6A | Zone6A(MN-MINNEAPOLISSTPAUL-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 24102.9894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24102.9894 | 0 | 24102.9894 | 0 | 0 | 153.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.9458 | 0 | 153.9458 | 0 | 0 | 24.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.103 | 0 | 24.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3808 | 0 | 0 | 0 | 4.3808 | 4.3808 | 0
MN_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 377668.3406 | 880961.238 | 96777.4775 | 4077910.5986 | 543457.0788 | 621509.7955 | 74421.13 | 117361.0995 | 473640.0338 | 13100.9419 | 0 | 0 | 0 | 7276807.7345 | 0 | 7276810.7909 | -3.0564 | 543454.0224 | 0 | 39919.5436 | 93117.6029 | 10229.3794 | 431035.1503 | 57443.4132 | 65693.5854 | 7866.3134 | 12405.0682 | 50063.7516 | 1384.7696 | 0 | 0 | 0 | 769158.5775 | 0 | 769158.9006 | -0.32306 | 57443.0902 | 0 | 1288.6044 | 3005.8397 | 330.2048 | 13913.831 | 1854.2756 | 2120.5914 | 253.9249 | 400.4361 | 1616.0598 | 44.7004 | 0 | 0 | 0 | 24828.468 | 0 | 24828.4784 | -0.010429 | 1854.2651 | 6.0287 | 0.66228 | 27.9065 | 4.2532 | 0.50929 | 0.089654 | 2.5845 | 0 | 0 | 3.2413 | 0 | 49.7976 | 49.7976 | -2.0916e-05
MN_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1941044.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643672.0844 | 0 | 0 | 2584716.2426 | 0 | 2584716.2426 | 0 | 0 | 12397.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.1336 | 0 | 0 | 16508.5826 | 0 | 16508.5826 | 0 | 0 | 1941.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643.6721 | 0 | 0 | 2584.7162 | 0 | 2584.7162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8931 | 1.291 | 0 | 0 | 5.1841 | 5.1841 | 0
MN_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 346164.9516 | 717906.6094 | 96777.4775 | 4077910.5986 | 543387.6147 | 589264.5292 | 70578.3723 | 104435.2073 | 473376.07 | 12058.9794 | 0 | 0 | 0 | 7031860.41 | 0 | 7031854.2972 | 6.1128 | 543393.7275 | 0 | 36589.6354 | 75882.7286 | 10229.3794 | 431035.1503 | 57436.0709 | 62285.2607 | 7460.134 | 11038.8014 | 50035.8506 | 1274.6341 | 0 | 0 | 0 | 743267.6453 | 0 | 743266.9992 | 0.64613 | 57436.717 | 0 | 1181.1148 | 2449.4974 | 330.2048 | 13913.831 | 1854.0385 | 2010.5706 | 240.8134 | 356.3329 | 1615.1592 | 41.1452 | 0 | 0 | 0 | 23992.7077 | 0 | 23992.6869 | 0.020857 | 1854.0594 | 4.9129 | 0.66228 | 27.9065 | 4.0325 | 0.48299 | 0.082524 | 2.3689 | 0 | 0 | 3.2395 | 0 | 48.1213 | 48.1213 | 4.1832e-05
MN_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1898657.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643615.2153 | 0 | 0 | 2542272.9919 | 0 | 2542272.9919 | 0 | 0 | 12126.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4110.7704 | 0 | 0 | 16237.4976 | 0 | 16237.4976 | 0 | 0 | 1898.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643.6152 | 0 | 0 | 2542.273 | 0 | 2542.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8081 | 1.2909 | 0 | 0 | 5.0989 | 5.0989 | 0
MN_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 16646.393 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 20800.3502 | 0 | 0 | 0 | 0 | 128647.6374 | 0 | 0 | 343669.7987 | 0 | 343668.9651 | 0.83357 | 0.83357 | 0 | 1759.5237 | 2999.2082 | 760.6688 | 15009.8447 | 0 | 2198.597 | 0 | 0 | 0 | 0 | 13598.0553 | 0 | 0 | 36325.8977 | 0 | 36325.8096 | 0.088108 | 0.088108 | 0 | 56.7975 | 96.8146 | 24.5544 | 484.5184 | 0 | 70.9708 | 0 | 0 | 0 | 0 | 438.9457 | 0 | 0 | 1172.6014 | 0 | 1172.5985 | 0.0028441 | 0.0028441 | 2.8693 | 0.72773 | 14.3599 | 2.1034 | 0 | 0 | 1.6833 | 0 | 13.0093 | 0 | 0 | 34.7529 | 34.753 | 8.4293e-05
MN_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 310201.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310201.587 | 0 | 310201.587 | 0 | 0 | 1981.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1981.2575 | 0 | 1981.2575 | 0 | 0 | 310.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.2016 | 0 | 310.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1936 | 0 | 0 | 0 | 9.1936 | 9.1936 | 0
MN_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 15262.6668 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 19344.3812 | 0 | 0 | 0 | 0 | 128639.3017 | 0 | 0 | 335628.6267 | 0 | 335631.1274 | -2.5007 | -2.5007 | 0 | 1613.2639 | 2450.2932 | 760.6688 | 15009.8447 | 0 | 2044.7011 | 0 | 0 | 0 | 0 | 13597.1742 | 0 | 0 | 35475.9458 | 0 | 35476.2102 | -0.26433 | -0.26433 | 0 | 52.0762 | 79.0956 | 24.5544 | 484.5184 | 0 | 66.003 | 0 | 0 | 0 | 0 | 438.9173 | 0 | 0 | 1145.1649 | 0 | 1145.1734 | -0.0085324 | -0.0085324 | 2.3442 | 0.72773 | 14.3599 | 1.9562 | 0 | 0 | 1.5434 | 0 | 13.0084 | 0 | 0 | 33.9401 | 33.9399 | -0.00025288
MN_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 294401.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294401.4756 | 0 | 294401.4756 | 0 | 0 | 1880.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1880.3422 | 0 | 1880.3422 | 0 | 0 | 294.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4015 | 0 | 294.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7253 | 0 | 0 | 0 | 8.7253 | 8.7253 | 0
MN_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 50350.4069 | 96371.8068 | 7157.5878 | 317887.4784 | 4818.0346 | 99053.1237 | 150.0426 | 0 | 0 | 21092.0997 | 7179.8163 | 17593.8842 | 0 | 621654.281 | 0 | 621657.8931 | -3.6121 | 4814.4225 | 0 | 5322.038 | 10186.5 | 756.557 | 33600.7065 | 509.2663 | 10469.9152 | 15.8595 | 0 | 0 | 2229.4349 | 758.9066 | 1859.6736 | 0 | 65708.8575 | 0 | 65709.2393 | -0.3818 | 508.8845 | 0 | 171.7956 | 328.8206 | 24.4217 | 1084.6321 | 16.4391 | 337.9693 | 0.51195 | 0 | 0 | 71.9662 | 24.4975 | 60.0303 | 0 | 2121.0844 | 0 | 2121.0967 | -0.012325 | 16.4268 | 4.446 | 0.33021 | 14.6653 | 4.5697 | 0.006922 | 0.97306 | 2.3228 | 0 | 0.33123 | 0 | 0.81167 | 28.6794 | 28.6792 | -0.00016664
MN_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 1011567.2995 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133556.9104 | 0 | 0 | 1487314.6247 | 0 | 1487314.6247 | 0 | 0 | 6460.8803 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 853.028 | 0 | 0 | 9499.4785 | 0 | 9499.4785 | 0 | 0 | 1011.5673 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.5569 | 0 | 0 | 1487.3146 | 0 | 1487.3146 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.6774 | 1.8058 | 0 | 0 | 20.11 | 20.11 | 0
MN_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 45401.7796 | 79197.4861 | 7157.5878 | 312483.1662 | 4743.0133 | 82537.3233 | 138.9283 | 0 | 0 | 22684.2184 | 7182.5949 | 12450.7573 | 0 | 573976.8553 | 0 | 573977.6888 | -0.83357 | 4742.1798 | 0 | 4798.9681 | 8371.1743 | 756.557 | 33029.4707 | 501.3365 | 8724.1951 | 14.6847 | 0 | 0 | 2397.7219 | 759.2003 | 1316.045 | 0 | 60669.3536 | 0 | 60669.4417 | -0.088108 | 501.2484 | 0 | 154.9109 | 270.2218 | 24.4217 | 1066.1926 | 16.1832 | 281.6173 | 0.47402 | 0 | 0 | 77.3986 | 24.507 | 42.482 | 0 | 1958.409 | 0 | 1958.4119 | -0.0028441 | 16.1803 | 3.6537 | 0.33021 | 14.416 | 3.8077 | 0.0064093 | 1.0465 | 2.0946 | 0 | 0.33136 | 0 | 0.5744 | 26.4797 | 26.4797 | -3.8456e-05
MN_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 972792.1011 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133272.5652 | 0 | 0 | 1448255.0812 | 0 | 1448255.0812 | 0 | 0 | 6213.2231 | 0 | 0 | 0 | 2185.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 851.2119 | 0 | 0 | 9250.0052 | 0 | 9250.0052 | 0 | 0 | 972.7921 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.2726 | 0 | 0 | 1448.2551 | 0 | 1448.2551 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.1531 | 1.802 | 0 | 0 | 19.5819 | 19.5819 | 0
MN_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 16515.8004 | 89794.9395 | 10750.2745 | 53987.5506 | 0 | 45471.2438 | 0 | 0 | 0 | 5018.0914 | 0 | 0 | 0 | 221537.9002 | 0 | 221539.2894 | -1.3893 | -1.3893 | 0 | 1745.7201 | 9491.3251 | 1136.304 | 5706.4841 | 0 | 4806.3105 | 0 | 0 | 0 | 530.4123 | 0 | 0 | 0 | 23416.556 | 0 | 23416.7029 | -0.14685 | -0.14685 | 0 | 56.3519 | 306.3803 | 36.6799 | 184.2055 | 0 | 155.1479 | 0 | 0 | 0 | 17.1217 | 0 | 0 | 0 | 755.8873 | 0 | 755.8921 | -0.0047402 | -0.0047402 | 12.4081 | 1.4855 | 7.4601 | 6.2833 | 0 | 0.69341 | 2.2822 | 0 | 0 | 0 | 0 | 30.6128 | 30.6126 | -0.00019197
MN_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 431057.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94980.7536 | 0 | 0 | 526038.5016 | 0 | 526038.5016 | 0 | 0 | 2753.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.6421 | 0 | 0 | 3359.8079 | 0 | 3359.8079 | 0 | 0 | 431.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9808 | 0 | 0 | 526.0385 | 0 | 526.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4574 | 3.8466 | 0 | 0 | 21.304 | 21.304 | 0
MN_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 0 | 14904.2317 | 74271.0874 | 10750.2745 | 53987.5506 | 0 | 46465.9706 | 0 | 0 | 0 | 5157.0198 | 0 | 0 | 0 | 205536.1346 | 0 | 205534.4675 | 1.6671 | 1.6671 | 0 | 1575.3773 | 7850.4539 | 1136.304 | 5706.4841 | 0 | 4911.4531 | 0 | 0 | 0 | 545.097 | 0 | 0 | 0 | 21725.1694 | 0 | 21724.9932 | 0.17622 | 0.17622 | 0 | 50.8532 | 253.413 | 36.6799 | 184.2055 | 0 | 158.5419 | 0 | 0 | 0 | 17.5958 | 0 | 0 | 0 | 701.2893 | 0 | 701.2836 | 0.0056883 | 0.0056883 | 10.263 | 1.4855 | 7.4601 | 6.4208 | 0 | 0.71261 | 2.0595 | 0 | 0 | 0 | 0 | 28.4012 | 28.4015 | 0.00023037
MN_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 453331.4503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94999.7099 | 0 | 0 | 548331.1603 | 0 | 548331.1603 | 0 | 0 | 2895.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.7631 | 0 | 0 | 3502.1911 | 0 | 3502.1911 | 0 | 0 | 453.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9997 | 0 | 0 | 548.3312 | 0 | 548.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3594 | 3.8474 | 0 | 0 | 22.2068 | 22.2068 | 0
MN_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 69280.7817 | 45173.9371 | 78975.2008 | 12292.379 | 154949.5496 | 0 | 45485.1366 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 406229.2275 | 0 | 406228.1161 | 1.1114 | 1.1114 | 7322.9786 | 4774.8852 | 8347.6787 | 1299.3045 | 16378.1674 | 0 | 4807.7789 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 42938.4294 | 0 | 42938.3119 | 0.11748 | 0.11748 | 236.386 | 154.1335 | 269.4634 | 41.9416 | 528.6879 | 0 | 155.1953 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.0541 | 0 | 1386.0503 | 0.0037922 | 0.0037922 | 6.2373 | 0.97083 | 12.2376 | 3.5923 | 0.0057056 | 0 | 3.5677 | 5.4716 | 0 | 0 | 0 | 32.083 | 32.0831 | 8.7778e-05
MN_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 158986.8437 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 679347.9208 | 0 | 0 | 1237830.2024 | 0 | 1237830.2024 | 0 | 0 | 1015.449 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4338.9952 | 0 | 0 | 7906.0215 | 0 | 7906.0215 | 0 | 0 | 158.9868 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 679.3479 | 0 | 0 | 1237.8302 | 0 | 1237.8302 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.6801 | 15.7249 | 0 | 0 | 28.6522 | 28.6522 | 0
MN_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 75493.6568 | 41003.3085 | 50844.9917 | 12292.379 | 154949.5496 | 0 | 47146.7195 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 381802.8478 | 0 | 381802.57 | 0.27786 | 0.27786 | 7979.6795 | 4334.0497 | 5374.3156 | 1299.3045 | 16378.1674 | 0 | 4983.4082 | 7.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 40356.561 | 0 | 40356.5316 | 0.029369 | 0.029369 | 257.5844 | 139.9033 | 173.4831 | 41.9416 | 528.6879 | 0 | 160.8646 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.7113 | 0 | 1302.7104 | 0.00094805 | 0.00094805 | 4.0156 | 0.97083 | 12.2376 | 3.7235 | 0.0057056 | 0 | 3.2384 | 5.9623 | 0 | 0 | 0 | 30.1539 | 30.154 | 2.1945e-05
MN_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 139784.0689 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 679414.268 | 0 | 0 | 1218693.7747 | 0 | 1218693.7747 | 0 | 0 | 892.8008 | 0 | 0 | 0 | 2551.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 4339.4189 | 0 | 0 | 7783.7971 | 0 | 7783.7971 | 0 | 0 | 139.7841 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 679.4143 | 0 | 0 | 1218.6938 | 0 | 1218.6938 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.2356 | 15.7265 | 0 | 0 | 28.2092 | 28.2092 | 0
MN_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 5451.5478 | 2111.7107 | 8777.4921 | 1600.4544 | 13417.6985 | 0 | 5168.134 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41531.2362 | 0 | 41527.0684 | 4.1679 | 4.1679 | 576.2286 | 223.2078 | 927.7809 | 169.168 | 1418.2507 | 0 | 546.2718 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4389.8517 | 0 | 4389.4111 | 0.44054 | 0.44054 | 18.6007 | 7.2052 | 29.9488 | 5.4608 | 45.7812 | 0 | 17.6337 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.7046 | 0 | 141.6904 | 0.014221 | 0.014221 | 5.4433 | 0.9925 | 8.3208 | 3.205 | 0 | 0 | 1.3096 | 3.3807 | 3.1033 | 0 | 0 | 25.7525 | 25.7551 | 0.0025846
MN_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 36727.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36727.9134 | 0 | 36727.9134 | 0 | 0 | 234.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.5812 | 0 | 234.5812 | 0 | 0 | 36.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7279 | 0 | 36.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6754 | 0 | 0 | 0 | 6.6754 | 6.6754 | 0
MN_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Electricity | 5482.1121 | 1808.8469 | 7127.0235 | 1600.4544 | 13417.6985 | 0 | 4531.8423 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38972.1763 | 0 | 38969.6756 | 2.5007 | 2.5007 | 579.4592 | 191.1951 | 753.3264 | 169.168 | 1418.2507 | 0 | 479.0157 | 0 | 0 | 0 | 0 | 528.9438 | 0 | 0 | 4119.359 | 0 | 4119.0947 | 0.26433 | 0.26433 | 18.705 | 6.1718 | 24.3174 | 5.4608 | 45.7812 | 0 | 15.4626 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.9731 | 0 | 132.9645 | 0.0085324 | 0.0085324 | 4.4197 | 0.9925 | 8.3208 | 2.8104 | 0 | 0 | 1.1217 | 3.3997 | 3.1033 | 0 | 0 | 24.1666 | 24.1681 | 0.0015508
MN_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | MN-DULUTH-MN | Zone7 | Zone7(MN-DULUTH-MN) |  |  | MN | 0.1057 | 0.006387 |  |  |  | Natural Gas | 38500.3314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38500.3314 | 0 | 38500.3314 | 0 | 0 | 245.9016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245.9016 | 0 | 245.9016 | 0 | 0 | 38.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.5003 | 0 | 38.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 0 | 6.9975 | 6.9975 | 0
MO_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 920686.4059 | 883211.8771 | 94751.9024 | 4077910.5986 | 543459.8574 | 574049.098 | 126858.2405 | 346731.7792 | 258531.737 | 12172.9006 | 0 | 0 | 0 | 7838364.3967 | 0 | 7838364.3967 | 0 | 543459.8574 | 0 | 80744.1978 | 77457.6816 | 8309.7418 | 357632.7595 | 47661.4295 | 50344.1059 | 11125.4677 | 30408.377 | 22673.2333 | 1067.5634 | 0 | 0 | 0 | 687424.5576 | 0 | 687424.5576 | 0 | 47661.4295 | 0 | 3141.382 | 3013.5189 | 323.2935 | 13913.831 | 1854.285 | 1958.6555 | 432.8403 | 1183.0488 | 882.1103 | 41.5339 | 0 | 0 | 0 | 26744.4993 | 0 | 26744.4993 | 0 | 1854.285 | 6.0441 | 0.64842 | 27.9065 | 3.9284 | 0.86813 | 0.083303 | 6.3006 | 0 | 0 | 1.7692 | 0 | 53.6405 | 53.6405 | 0
MO_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 820629.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496902.6033 | 0 | 0 | 1317532.144 | 0 | 1317532.144 | 0 | 0 | 5964.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3611.4881 | 0 | 0 | 9575.8236 | 0 | 9575.8236 | 0 | 0 | 820.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.9026 | 0 | 0 | 1317.5321 | 0 | 1317.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6459 | 0.99662 | 0 | 0 | 2.6425 | 2.6425 | 0
MO_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 858004.7201 | 718198.3589 | 94751.9024 | 4077910.5986 | 543387.6147 | 558247.3893 | 118264.1337 | 313013.8725 | 258478.9442 | 12134.0007 | 0 | 0 | 0 | 7552391.5351 | 0 | 7552391.5351 | 0 | 543387.6147 | 0 | 75247.014 | 62985.9961 | 8309.7418 | 357632.7595 | 47655.0938 | 48958.296 | 10371.7645 | 27451.3166 | 22668.6034 | 1064.1519 | 0 | 0 | 0 | 662344.7376 | 0 | 662344.7376 | 0 | 47655.0938 | 0 | 2927.5121 | 2450.4928 | 323.2935 | 13913.831 | 1854.0385 | 1904.7401 | 403.5172 | 1068.0033 | 881.9302 | 41.4012 | 0 | 0 | 0 | 25768.7599 | 0 | 25768.7599 | 0 | 1854.0385 | 4.9149 | 0.64842 | 27.9065 | 3.8203 | 0.80932 | 0.083037 | 5.8716 | 0 | 0 | 1.7689 | 0 | 51.6835 | 51.6835 | 0
MO_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 470847.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496845.7343 | 0 | 0 | 967692.845 | 0 | 967692.845 | 0 | 0 | 3422.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3611.0748 | 0 | 0 | 7033.1916 | 0 | 7033.1916 | 0 | 0 | 470.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.8457 | 0 | 0 | 967.6928 | 0 | 967.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94436 | 0.99651 | 0 | 0 | 1.9409 | 1.9409 | 0
MO_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 46802.1772 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 23831.7664 | 0 | 0 | 0 | 0 | 99978.3864 | 0 | 0 | 348201.6409 | 0 | 348201.0852 | 0.55571 | 0.55571 | 0 | 4104.5509 | 2488.4632 | 632.3504 | 12453.769 | 0 | 2090.0459 | 0 | 0 | 0 | 0 | 8768.1045 | 0 | 0 | 30537.2839 | 0 | 30537.2352 | 0.048736 | 0.048736 | 0 | 159.689 | 96.8146 | 24.6018 | 484.5184 | 0 | 81.314 | 0 | 0 | 0 | 0 | 341.1263 | 0 | 0 | 1188.064 | 0 | 1188.0621 | 0.0018961 | 0.0018961 | 2.8693 | 0.72914 | 14.3599 | 2.4099 | 0 | 0 | 4.7328 | 0 | 10.1101 | 0 | 0 | 35.2112 | 35.2113 | 5.6196e-05
MO_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 134277.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134277.2514 | 0 | 134277.2514 | 0 | 0 | 975.9271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975.9271 | 0 | 975.9271 | 0 | 0 | 134.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.2773 | 0 | 134.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9796 | 0 | 0 | 0 | 3.9796 | 3.9796 | 0
MO_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 42695.4556 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 22470.2688 | 0 | 0 | 0 | 0 | 99845.0152 | 0 | 0 | 337406.9094 | 0 | 337409.4101 | -2.5007 | -2.5007 | 0 | 3744.3915 | 2033.0247 | 632.3504 | 12453.769 | 0 | 1970.6426 | 0 | 0 | 0 | 0 | 8756.4078 | 0 | 0 | 29590.586 | 0 | 29590.8053 | -0.21931 | -0.21931 | 0 | 145.6769 | 79.0956 | 24.6018 | 484.5184 | 0 | 76.6686 | 0 | 0 | 0 | 0 | 340.6712 | 0 | 0 | 1151.2324 | 0 | 1151.2409 | -0.0085324 | -0.0085324 | 2.3442 | 0.72914 | 14.3599 | 2.2723 | 0 | 0 | 4.3175 | 0 | 10.0967 | 0 | 0 | 34.1199 | 34.1197 | -0.00025288
MO_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 46774.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46774.7749 | 0 | 46774.7749 | 0 | 0 | 339.9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339.9591 | 0 | 339.9591 | 0 | 0 | 46.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7748 | 0 | 46.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3863 | 0 | 0 | 0 | 1.3863 | 1.3863 | 0
MO_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 171809.8922 | 101167.6129 | 7096.4593 | 317887.4784 | 4818.0346 | 95232.5945 | 527.9277 | 0 | 0 | 24051.2732 | 7179.8163 | 17680.0198 | 0 | 747451.109 | 0 | 747449.9975 | 1.1114 | 4819.1461 | 0 | 15067.7275 | 8872.3997 | 622.3595 | 27878.7319 | 422.5416 | 8351.8985 | 46.2993 | 0 | 0 | 2109.2967 | 629.6699 | 1550.5377 | 0 | 65551.4623 | 0 | 65551.3648 | 0.097472 | 422.6391 | 0 | 586.2154 | 345.1839 | 24.2131 | 1084.6321 | 16.4391 | 324.9336 | 1.8013 | 0 | 0 | 82.0629 | 24.4975 | 60.3242 | 0 | 2550.3032 | 0 | 2550.2994 | 0.0037922 | 16.4429 | 4.6672 | 0.32739 | 14.6653 | 4.3934 | 0.024355 | 1.1096 | 7.9262 | 0 | 0.33123 | 0 | 0.81564 | 34.4826 | 34.4827 | 5.1274e-05
MO_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 322362.0807 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 105075.0059 | 0 | 0 | 769627.5014 | 0 | 769627.5014 | 0 | 0 | 2342.9276 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 763.6851 | 0 | 0 | 5593.6527 | 0 | 5593.6527 | 0 | 0 | 322.3621 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 105.075 | 0 | 0 | 769.6275 | 0 | 769.6275 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.3587 | 1.4207 | 0 | 0 | 10.4061 | 10.4061 | 0
MO_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 157686.4378 | 81645.4034 | 7096.4593 | 312483.1662 | 4745.7919 | 83909.9352 | 391.7779 | 0 | 0 | 22650.8756 | 7179.8163 | 12517.4429 | 0 | 690307.1066 | 0 | 690309.0516 | -1.945 | 4743.8469 | 0 | 13829.1006 | 7160.3019 | 622.3595 | 27404.7737 | 416.2059 | 7358.9013 | 34.3589 | 0 | 0 | 1986.4818 | 629.6699 | 1097.7797 | 0 | 60539.9332 | 0 | 60540.1038 | -0.17058 | 416.0354 | 0 | 538.0261 | 278.5741 | 24.2131 | 1066.1926 | 16.1926 | 286.3007 | 1.3367 | 0 | 0 | 77.2848 | 24.4975 | 42.7095 | 0 | 2355.3278 | 0 | 2355.3345 | -0.0066363 | 16.186 | 3.7666 | 0.32739 | 14.416 | 3.8711 | 0.018074 | 1.045 | 7.2747 | 0 | 0.33123 | 0 | 0.57748 | 31.8465 | 31.8464 | -8.973e-05
MO_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 276468.7757 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104762.2263 | 0 | 0 | 723421.4168 | 0 | 723421.4168 | 0 | 0 | 2009.3751 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 761.4119 | 0 | 0 | 5257.8269 | 0 | 5257.8269 | 0 | 0 | 276.4688 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7622 | 0 | 0 | 723.4214 | 0 | 723.4214 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7381 | 1.4165 | 0 | 0 | 9.7814 | 9.7814 | 0
MO_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 68644.4899 | 83248.6364 | 10705.8174 | 53987.5506 | 0 | 38630.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255216.9069 | 0 | 255216.3512 | 0.55571 | 0.55571 | 0 | 6020.1218 | 7300.9054 | 938.9002 | 4734.7082 | 0 | 3387.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22382.5227 | 0 | 22382.474 | 0.048736 | 0.048736 | 0 | 234.215 | 284.0443 | 36.5282 | 184.2055 | 0 | 131.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870.8001 | 0 | 870.7982 | 0.0018961 | 0.0018961 | 11.5035 | 1.4794 | 7.4601 | 5.338 | 0 | 0 | 9.4855 | 0 | 0 | 0 | 0 | 35.2664 | 35.2665 | 7.679e-05
MO_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 182805.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86279.7924 | 0 | 0 | 269085.2804 | 0 | 269085.2804 | 0 | 0 | 1328.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.0815 | 0 | 0 | 1955.7118 | 0 | 1955.7118 | 0 | 0 | 182.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2798 | 0 | 0 | 269.0853 | 0 | 269.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4034 | 3.4942 | 0 | 0 | 10.8977 | 10.8977 | 0
MO_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 64423.8471 | 65821.4661 | 10705.8174 | 53987.5506 | 0 | 36796.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231735.2399 | 0 | 231730.5163 | 4.7236 | 4.7236 | 0 | 5649.9714 | 5772.5426 | 938.9002 | 4734.7082 | 0 | 3227.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20323.1805 | 0 | 20322.7663 | 0.41426 | 0.41426 | 0 | 219.8142 | 224.5828 | 36.5282 | 184.2055 | 0 | 125.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790.6806 | 0 | 790.6645 | 0.016117 | 0.016117 | 9.0954 | 1.4794 | 7.4601 | 5.0846 | 0 | 0 | 8.9022 | 0 | 0 | 0 | 0 | 32.0211 | 32.0217 | 0.00065271
MO_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 200093.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86289.2706 | 0 | 0 | 286382.9428 | 0 | 286382.9428 | 0 | 0 | 1454.2808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.1504 | 0 | 0 | 2081.4312 | 0 | 2081.4312 | 0 | 0 | 200.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2893 | 0 | 0 | 286.3829 | 0 | 286.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1036 | 3.4946 | 0 | 0 | 11.5982 | 11.5982 | 0
MO_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 12756.3996 | 102279.0396 | 80172.7631 | 12314.6075 | 154949.5496 | 0 | 46346.4923 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 408891.0944 | 0 | 408890.8166 | 0.27786 | 0.27786 | 1118.7362 | 8969.8718 | 7031.1513 | 1079.9911 | 13589.0755 | 0 | 4064.5874 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 35859.749 | 0 | 35859.7246 | 0.024368 | 0.024368 | 43.5248 | 348.9761 | 273.5495 | 42.0174 | 528.6879 | 0 | 158.1342 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.1364 | 0 | 1395.1355 | 0.00094805 | 0.00094805 | 6.3319 | 0.97258 | 12.2376 | 3.6603 | 0.0057056 | 0 | 8.0778 | 1.0075 | 0 | 0 | 0 | 32.2933 | 32.2933 | 2.1945e-05
MO_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 28254.4283 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511470.5525 | 0 | 0 | 939220.4187 | 0 | 939220.4187 | 0 | 0 | 205.3532 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 3717.368 | 0 | 0 | 6826.254 | 0 | 6826.254 | 0 | 0 | 28.2544 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.4706 | 0 | 0 | 939.2204 | 0 | 939.2204 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.65401 | 11.839 | 0 | 0 | 21.7402 | 21.7402 | 0
MO_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 14493.0038 | 96499.6209 | 51367.3623 | 12314.6075 | 154949.5496 | 0 | 44029.1676 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373725.5545 | 0 | 373725.5545 | 0 | 0 | 1271.0364 | 8463.0168 | 4504.9177 | 1079.9911 | 13589.0755 | 0 | 3861.358 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 32775.7311 | 0 | 32775.7311 | 0 | 0 | 49.4501 | 329.2567 | 175.2654 | 42.0174 | 528.6879 | 0 | 150.2275 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.1516 | 0 | 1275.1516 | 0 | 0 | 4.0569 | 0.97258 | 12.2376 | 3.4773 | 0.0057056 | 0 | 7.6213 | 1.1446 | 0 | 0 | 0 | 29.516 | 29.516 | 0
MO_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 29259.1145 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511508.4652 | 0 | 0 | 940263.0176 | 0 | 940263.0176 | 0 | 0 | 212.6552 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 3717.6435 | 0 | 0 | 6833.8316 | 0 | 6833.8316 | 0 | 0 | 29.2591 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.5085 | 0 | 0 | 940.263 | 0 | 940.263 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.67726 | 11.8399 | 0 | 0 | 21.7643 | 21.7643 | 0
MO_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 1839.4111 | 6740.8028 | 9027.5632 | 1569.8902 | 13417.6985 | 0 | 5162.5769 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42762.1412 | 0 | 42759.9184 | 2.2229 | 2.2229 | 161.3164 | 591.1684 | 791.7173 | 137.6794 | 1176.7322 | 0 | 452.758 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3750.2398 | 0 | 3750.0448 | 0.19494 | 0.19494 | 6.2761 | 22.9996 | 30.802 | 5.3565 | 45.7812 | 0 | 17.6147 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.9044 | 0 | 145.8968 | 0.0075844 | 0.0075844 | 5.5983 | 0.97355 | 8.3208 | 3.2015 | 0 | 0 | 4.1802 | 1.1407 | 3.1033 | 0 | 0 | 26.5171 | 26.5184 | 0.0013785
MO_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 1488.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.0729 | 0 | 1488.0729 | 0 | 0 | 10.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8153 | 0 | 10.8153 | 0 | 0 | 1.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4881 | 0 | 1.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27046 | 0 | 0 | 0 | 0.27046 | 0.27046 | 0
MO_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 1878.3111 | 6429.6033 | 7249.2805 | 1569.8902 | 13417.6985 | 0 | 4748.5705 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40297.5526 | 0 | 40297.5526 | 0 | 0 | 164.7279 | 563.8762 | 635.7619 | 137.6794 | 1176.7322 | 0 | 416.4496 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3534.0954 | 0 | 3534.0954 | 0 | 0 | 6.4088 | 21.9378 | 24.7345 | 5.3565 | 45.7812 | 0 | 16.2021 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.4952 | 0 | 137.4952 | 0 | 0 | 4.4956 | 0.97355 | 8.3208 | 2.9448 | 0 | 0 | 3.9872 | 1.1648 | 3.1033 | 0 | 0 | 24.99 | 24.99 | 0
MO_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | MO-MEMPHIS-TN | Zone3A | Zone3A(MO-MEMPHIS-TN) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 1573.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3764 | 0 | 1573.3764 | 0 | 0 | 11.4353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4353 | 0 | 11.4353 | 0 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5734 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28596 | 0 | 0 | 0 | 0.28596 | 0.28596 | 0
MO_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 783350.1905 | 880463.8746 | 95310.3943 | 4077910.5986 | 543457.0788 | 594188.1493 | 107513.8592 | 273021.9622 | 336581.6751 | 14570.8037 | 0 | 0 | 0 | 7706368.5864 | 0 | 7706371.9207 | -3.3343 | 543453.7446 | 0 | 68699.8117 | 77216.6818 | 8358.7216 | 357632.7595 | 47661.1858 | 52110.3007 | 9428.9655 | 23944.0261 | 29518.2129 | 1277.8595 | 0 | 0 | 0 | 675848.525 | 0 | 675848.8174 | -0.29242 | 47660.8934 | 0 | 2672.7908 | 3004.1427 | 325.1991 | 13913.831 | 1854.2756 | 2027.37 | 366.8373 | 931.5509 | 1148.4167 | 49.7156 | 0 | 0 | 0 | 26294.1296 | 0 | 26294.141 | -0.011377 | 1854.2642 | 6.0253 | 0.65224 | 27.9065 | 4.0662 | 0.73575 | 0.099713 | 5.3607 | 0 | 0 | 2.3033 | 0 | 52.7372 | 52.7372 | -2.2818e-05
MO_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 847016.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537526.0451 | 0 | 0 | 1384542.8144 | 0 | 1384542.8144 | 0 | 0 | 6156.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3906.7393 | 0 | 0 | 10062.8572 | 0 | 10062.8572 | 0 | 0 | 847.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.526 | 0 | 0 | 1384.5428 | 0 | 1384.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6988 | 1.0781 | 0 | 0 | 2.7769 | 2.7769 | 0
MO_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 734427.9669 | 716934.1111 | 95310.3943 | 4077910.5986 | 543387.6147 | 569922.9265 | 103576.6302 | 246383.8434 | 336462.1967 | 12917.5565 | 0 | 0 | 0 | 7437233.839 | 0 | 7437232.1719 | 1.6671 | 543389.2818 | 0 | 64409.3327 | 62875.1215 | 8358.7216 | 357632.7595 | 47655.0938 | 49982.2407 | 9083.6705 | 21607.8631 | 29507.7347 | 1132.8697 | 0 | 0 | 0 | 652245.4077 | 0 | 652245.2615 | 0.14621 | 47655.24 | 0 | 2505.8682 | 2446.1792 | 325.1991 | 13913.831 | 1854.0385 | 1944.577 | 353.4035 | 840.6617 | 1148.009 | 44.0747 | 0 | 0 | 0 | 25375.8419 | 0 | 25375.8362 | 0.0056883 | 1854.0442 | 4.9062 | 0.65224 | 27.9065 | 3.9002 | 0.70881 | 0.088399 | 5.0259 | 0 | 0 | 2.3025 | 0 | 50.8954 | 50.8954 | 1.1409e-05
MO_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 787143.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537488.1324 | 0 | 0 | 1324631.2942 | 0 | 1324631.2942 | 0 | 0 | 5720.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3906.4637 | 0 | 0 | 9627.4202 | 0 | 9627.4202 | 0 | 0 | 787.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537.4881 | 0 | 0 | 1324.6313 | 0 | 1324.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5787 | 1.078 | 0 | 0 | 2.6568 | 2.6568 | 0
MO_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 36046.3456 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 22439.7045 | 0 | 0 | 0 | 0 | 107883.4086 | 0 | 0 | 343958.7696 | 0 | 343959.0475 | -0.27786 | -0.27786 | 0 | 3161.2645 | 2488.4632 | 632.3504 | 12453.769 | 0 | 1967.9621 | 0 | 0 | 0 | 0 | 9461.3749 | 0 | 0 | 30165.1841 | 0 | 30165.2085 | -0.024368 | -0.024368 | 0 | 122.9901 | 96.8146 | 24.6018 | 484.5184 | 0 | 76.5643 | 0 | 0 | 0 | 0 | 368.0982 | 0 | 0 | 1173.5873 | 0 | 1173.5883 | -0.00094805 | -0.00094805 | 2.8693 | 0.72914 | 14.3599 | 2.2692 | 0 | 0 | 3.6451 | 0 | 10.9095 | 0 | 0 | 34.7823 | 34.7822 | -2.8098e-05
MO_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 93615.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93615.8969 | 0 | 93615.8969 | 0 | 0 | 680.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680.4003 | 0 | 680.4003 | 0 | 0 | 93.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6159 | 0 | 93.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7745 | 0 | 0 | 0 | 2.7745 | 2.7745 | 0
MO_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 35265.5683 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21981.241 | 0 | 0 | 0 | 0 | 107911.1942 | 0 | 0 | 337554.1734 | 0 | 337553.6177 | 0.55571 | 0.55571 | 0 | 3092.7903 | 2033.0247 | 632.3504 | 12453.769 | 0 | 1927.7548 | 0 | 0 | 0 | 0 | 9463.8117 | 0 | 0 | 29603.501 | 0 | 29603.4523 | 0.048736 | 0.048736 | 0 | 120.3261 | 79.0956 | 24.6018 | 484.5184 | 0 | 75 | 0 | 0 | 0 | 0 | 368.193 | 0 | 0 | 1151.7348 | 0 | 1151.7329 | 0.0018961 | 0.0018961 | 2.3442 | 0.72914 | 14.3599 | 2.2228 | 0 | 0 | 3.5662 | 0 | 10.9123 | 0 | 0 | 34.1345 | 34.1346 | 5.6196e-05
MO_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 106724.2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106724.2077 | 0 | 106724.2077 | 0 | 0 | 775.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775.6715 | 0 | 775.6715 | 0 | 0 | 106.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7242 | 0 | 106.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.163 | 0 | 0 | 0 | 3.163 | 3.163 | 0
MO_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 133332.3008 | 97780.5401 | 7115.9093 | 317887.4784 | 4818.0346 | 97747.1973 | 683.5274 | 0 | 0 | 18913.7034 | 7179.8163 | 17624.4485 | 0 | 703082.9562 | 0 | 703084.3455 | -1.3893 | 4816.6453 | 0 | 11693.2428 | 8575.3534 | 624.0652 | 27878.7319 | 422.5416 | 8572.4292 | 59.9454 | 0 | 0 | 1658.7318 | 629.6699 | 1545.6641 | 0 | 61660.3753 | 0 | 61660.4971 | -0.12184 | 422.4198 | 0 | 454.9298 | 333.6272 | 24.2795 | 1084.6321 | 16.4391 | 333.5134 | 2.3322 | 0 | 0 | 64.5336 | 24.4975 | 60.1346 | 0 | 2398.919 | 0 | 2398.9238 | -0.0047402 | 16.4344 | 4.511 | 0.32828 | 14.6653 | 4.5094 | 0.031534 | 0.87256 | 6.1511 | 0 | 0.33123 | 0 | 0.81308 | 32.4359 | 32.4358 | -6.4093e-05
MO_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 357592.443 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113321.0149 | 0 | 0 | 813103.8727 | 0 | 813103.8727 | 0 | 0 | 2598.9819 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 823.6171 | 0 | 0 | 5909.6389 | 0 | 5909.6389 | 0 | 0 | 357.5924 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.321 | 0 | 0 | 813.1039 | 0 | 813.1039 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.835 | 1.5322 | 0 | 0 | 10.994 | 10.994 | 0
MO_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 126722.0907 | 79517.0213 | 7115.9093 | 312483.1662 | 4743.0133 | 82526.209 | 439.0135 | 0 | 0 | 22989.8607 | 7179.8163 | 12489.6572 | 0 | 656205.7577 | 0 | 656210.4812 | -4.7236 | 4738.2898 | 0 | 11113.5274 | 6973.6428 | 624.0652 | 27404.7737 | 415.9623 | 7237.5485 | 38.5015 | 0 | 0 | 2016.2108 | 629.6699 | 1095.3429 | 0 | 57549.2449 | 0 | 57549.6592 | -0.41426 | 415.548 | 0 | 432.3758 | 271.3121 | 24.2795 | 1066.1926 | 16.1832 | 281.5794 | 1.4979 | 0 | 0 | 78.4414 | 24.4975 | 42.6147 | 0 | 2238.974 | 0 | 2238.9902 | -0.016117 | 16.167 | 3.6684 | 0.32828 | 14.416 | 3.8072 | 0.020253 | 1.0606 | 5.8462 | 0 | 0.33123 | 0 | 0.57619 | 30.2734 | 30.2732 | -0.00021792
MO_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 337536.6328 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113093.5388 | 0 | 0 | 792820.5864 | 0 | 792820.5864 | 0 | 0 | 2453.2162 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 821.9638 | 0 | 0 | 5762.22 | 0 | 5762.22 | 0 | 0 | 337.5366 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0935 | 0 | 0 | 792.8206 | 0 | 792.8206 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.5638 | 1.5291 | 0 | 0 | 10.7197 | 10.7197 | 0
MO_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 50978.3629 | 84223.9133 | 10722.4888 | 53987.5506 | 0 | 39950.2318 | 0 | 0 | 0 | 5709.9545 | 0 | 0 | 0 | 245572.502 | 0 | 245570.0012 | 2.5007 | 2.5007 | 0 | 4470.8024 | 7386.4372 | 940.3623 | 4734.7082 | 0 | 3503.6353 | 0 | 0 | 0 | 500.763 | 0 | 0 | 0 | 21536.7084 | 0 | 21536.4891 | 0.21931 | 0.21931 | 0 | 173.9382 | 287.372 | 36.5851 | 184.2055 | 0 | 136.3102 | 0 | 0 | 0 | 19.4824 | 0 | 0 | 0 | 837.8934 | 0 | 837.8848 | 0.0085324 | 0.0085324 | 11.6383 | 1.4817 | 7.4601 | 5.5204 | 0 | 0.78902 | 7.0443 | 0 | 0 | 0 | 0 | 33.9335 | 33.9338 | 0.00034555
MO_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 165687.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88706.2043 | 0 | 0 | 254394.115 | 0 | 254394.115 | 0 | 0 | 1204.2197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 644.7167 | 0 | 0 | 1848.9364 | 0 | 1848.9364 | 0 | 0 | 165.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7062 | 0 | 0 | 254.3941 | 0 | 254.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7102 | 3.5925 | 0 | 0 | 10.3027 | 10.3027 | 0
MO_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 47644.0829 | 66632.8076 | 10722.4888 | 53987.5506 | 0 | 38088.5921 | 0 | 0 | 0 | 5801.6472 | 0 | 0 | 0 | 222877.1693 | 0 | 222875.5022 | 1.6671 | 1.6671 | 0 | 4178.3861 | 5843.6972 | 940.3623 | 4734.7082 | 0 | 3340.3695 | 0 | 0 | 0 | 508.8045 | 0 | 0 | 0 | 19546.3277 | 0 | 19546.1815 | 0.14621 | 0.14621 | 0 | 162.5616 | 227.3511 | 36.5851 | 184.2055 | 0 | 129.9583 | 0 | 0 | 0 | 19.7952 | 0 | 0 | 0 | 760.4569 | 0 | 760.4512 | 0.0056883 | 0.0056883 | 9.2075 | 1.4817 | 7.4601 | 5.2632 | 0 | 0.80169 | 6.5836 | 0 | 0 | 0 | 0 | 30.7975 | 30.7977 | 0.00023037
MO_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 179383.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88715.6824 | 0 | 0 | 268099.5506 | 0 | 268099.5506 | 0 | 0 | 1303.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 644.7856 | 0 | 0 | 1948.5475 | 0 | 1948.5475 | 0 | 0 | 179.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7157 | 0 | 0 | 268.0996 | 0 | 268.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2649 | 3.5929 | 0 | 0 | 10.8577 | 10.8577 | 0
MO_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 26432.5048 | 84098.8778 | 79216.9361 | 12314.6075 | 154949.5496 | 0 | 46288.1424 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 403372.861 | 0 | 403371.7496 | 1.1114 | 1.1114 | 2318.1307 | 7375.4716 | 6947.3253 | 1079.9911 | 13589.0755 | 0 | 4059.4701 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 35375.7999 | 0 | 35375.7024 | 0.097472 | 0.097472 | 90.1877 | 286.9454 | 270.2882 | 42.0174 | 528.6879 | 0 | 157.9351 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.3082 | 0 | 1376.3044 | 0.0037922 | 0.0037922 | 6.2564 | 0.97258 | 12.2376 | 3.6557 | 0.0057056 | 0 | 6.6419 | 2.0876 | 0 | 0 | 0 | 31.8574 | 31.8575 | 8.7778e-05
MO_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 60603.4267 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 557553.4208 | 0 | 0 | 1017652.2854 | 0 | 1017652.2854 | 0 | 0 | 440.4657 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.2983 | 0 | 0 | 7396.2968 | 0 | 7396.2968 | 0 | 0 | 60.6034 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 557.5534 | 0 | 0 | 1017.6523 | 0 | 1017.6523 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4028 | 12.9057 | 0 | 0 | 23.5557 | 23.5557 | 0
MO_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 29914.0489 | 79008.5436 | 50811.6489 | 12314.6075 | 154949.5496 | 0 | 43904.1321 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 370974.7735 | 0 | 370972.5506 | 2.2229 | 2.2229 | 2623.4621 | 6929.0493 | 4456.1816 | 1079.9911 | 13589.0755 | 0 | 3850.3924 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 32534.4876 | 0 | 32534.2927 | 0.19494 | 0.19494 | 102.0667 | 269.5772 | 173.3693 | 42.0174 | 528.6879 | 0 | 149.8009 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.7659 | 0 | 1265.7583 | 0.0075844 | 0.0075844 | 4.013 | 0.97258 | 12.2376 | 3.4675 | 0.0057056 | 0 | 6.2399 | 2.3625 | 0 | 0 | 0 | 29.2986 | 29.2988 | 0.00017556
MO_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 59845.173 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 557629.2462 | 0 | 0 | 1016969.8571 | 0 | 1016969.8571 | 0 | 0 | 434.9547 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.8494 | 0 | 0 | 7391.3369 | 0 | 7391.3369 | 0 | 0 | 59.8452 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6292 | 0 | 0 | 1016.9699 | 0 | 1016.9699 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3852 | 12.9075 | 0 | 0 | 23.5399 | 23.5399 | 0
MO_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 2792.4595 | 5498.7835 | 8838.6206 | 1578.2259 | 13417.6985 | 0 | 5182.0269 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42312.0134 | 0 | 42310.0684 | 1.945 | 1.945 | 244.8987 | 482.2433 | 775.147 | 138.4104 | 1176.7322 | 0 | 454.4638 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3710.7636 | 0 | 3710.593 | 0.17058 | 0.17058 | 9.5279 | 18.7618 | 30.1574 | 5.3849 | 45.7812 | 0 | 17.6811 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.3686 | 0 | 144.362 | 0.0066363 | 0.0066363 | 5.4812 | 0.97872 | 8.3208 | 3.2136 | 0 | 0 | 3.41 | 1.7317 | 3.1033 | 0 | 0 | 26.2381 | 26.2393 | 0.0012062
MO_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 5592.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5592.121 | 0 | 5592.121 | 0 | 0 | 40.6435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6435 | 0 | 40.6435 | 0 | 0 | 5.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5921 | 0 | 5.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0164 | 0 | 0 | 0 | 1.0164 | 1.0164 | 0
MO_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 2845.2523 | 5240.3768 | 7118.6878 | 1578.2259 | 13417.6985 | 0 | 4768.0204 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39972.4603 | 0 | 39975.2389 | -2.7786 | -2.7786 | 249.5286 | 459.581 | 624.3089 | 138.4104 | 1176.7322 | 0 | 418.1554 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3505.5848 | 0 | 3505.8284 | -0.24368 | -0.24368 | 9.708 | 17.8802 | 24.289 | 5.3849 | 45.7812 | 0 | 16.2685 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.386 | 0 | 136.3955 | -0.0094805 | -0.0094805 | 4.4146 | 0.97872 | 8.3208 | 2.9568 | 0 | 0 | 3.2498 | 1.7644 | 3.1033 | 0 | 0 | 24.7902 | 24.7884 | -0.0017231
MO_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | MO-STLOUIS-MO | Zone4A | Zone4A(MO-STLOUIS-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 5762.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5762.7281 | 0 | 5762.7281 | 0 | 0 | 41.8835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8835 | 0 | 41.8835 | 0 | 0 | 5.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7627 | 0 | 5.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 0 | 0 | 0 | 1.0474 | 1.0474 | 0
MO_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 719340.3498 | 881519.73 | 95502.1154 | 4077910.5986 | 543457.0788 | 598400.4564 | 101250.9699 | 241568.5874 | 361588.7752 | 12364.6217 | 0 | 0 | 0 | 7632903.2833 | 0 | 7632899.6712 | 3.6121 | 543460.691 | 0 | 63086.1487 | 77309.2803 | 8375.5355 | 357632.7595 | 47661.1858 | 52479.72 | 8879.7101 | 21185.5651 | 31711.3356 | 1084.3773 | 0 | 0 | 0 | 669405.6179 | 0 | 669405.3012 | 0.31678 | 47661.5026 | 0 | 2454.3893 | 3007.7453 | 325.8532 | 13913.831 | 1854.2756 | 2041.7424 | 345.4683 | 824.232 | 1233.7409 | 42.1881 | 0 | 0 | 0 | 26043.466 | 0 | 26043.4537 | 0.012325 | 1854.2879 | 6.0325 | 0.65355 | 27.9065 | 4.095 | 0.69289 | 0.084615 | 4.9227 | 0 | 0 | 2.4745 | 0 | 52.2344 | 52.2344 | 2.4719e-05
MO_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 1538202.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573220.8378 | 0 | 0 | 2111423.7637 | 0 | 2111423.7637 | 0 | 0 | 11179.6589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4166.169 | 0 | 0 | 15345.8279 | 0 | 15345.8279 | 0 | 0 | 1538.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573.2208 | 0 | 0 | 2111.4238 | 0 | 2111.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0851 | 1.1497 | 0 | 0 | 4.2348 | 4.2348 | 0
MO_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 675211.1538 | 717434.2531 | 95502.1154 | 4077910.5986 | 543387.6147 | 578883.804 | 96471.8352 | 217536.7641 | 361394.2755 | 11014.2383 | 0 | 0 | 0 | 7374746.6529 | 0 | 7374744.43 | 2.2229 | 543389.8375 | 0 | 59216.0182 | 62918.984 | 8375.5355 | 357632.7595 | 47655.0938 | 50768.1096 | 8460.5799 | 19077.9742 | 31694.278 | 965.9487 | 0 | 0 | 0 | 646765.2815 | 0 | 646765.0865 | 0.19494 | 47655.2888 | 0 | 2303.8205 | 2447.8857 | 325.8532 | 13913.831 | 1854.0385 | 1975.1515 | 329.1619 | 742.2354 | 1233.0773 | 37.5806 | 0 | 0 | 0 | 25162.6356 | 0 | 25162.628 | 0.0075844 | 1854.0461 | 4.9096 | 0.65355 | 27.9065 | 3.9615 | 0.66019 | 0.075374 | 4.6207 | 0 | 0 | 2.4731 | 0 | 50.4678 | 50.4678 | 1.5212e-05
MO_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 1499124.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573239.7942 | 0 | 0 | 2072364.2202 | 0 | 2072364.2202 | 0 | 0 | 10895.6363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4166.3068 | 0 | 0 | 15061.9432 | 0 | 15061.9432 | 0 | 0 | 1499.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573.2398 | 0 | 0 | 2072.3642 | 0 | 2072.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0067 | 1.1497 | 0 | 0 | 4.1565 | 4.1565 | 0
MO_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 29688.985 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22303.5548 | 0 | 0 | 0 | 0 | 114899.2894 | 0 | 0 | 344475.583 | 0 | 344476.9723 | -1.3893 | -1.3893 | 0 | 2603.724 | 2488.4632 | 631.863 | 12453.769 | 0 | 1956.0218 | 0 | 0 | 0 | 0 | 10076.6677 | 0 | 0 | 30210.5086 | 0 | 30210.6305 | -0.12184 | -0.12184 | 0 | 101.2988 | 96.8146 | 24.5829 | 484.5184 | 0 | 76.0997 | 0 | 0 | 0 | 0 | 392.0364 | 0 | 0 | 1175.3507 | 0 | 1175.3554 | -0.0047402 | -0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.2554 | 0 | 0 | 3.0022 | 0 | 11.619 | 0 | 0 | 34.8346 | 34.8345 | -0.00014049
MO_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 191762.3597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191762.3597 | 0 | 191762.3597 | 0 | 0 | 1393.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1393.7288 | 0 | 1393.7288 | 0 | 0 | 191.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.7624 | 0 | 191.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6834 | 0 | 0 | 0 | 5.6834 | 5.6834 | 0
MO_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 29058.2504 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21878.4341 | 0 | 0 | 0 | 0 | 114927.0751 | 0 | 0 | 338254.3722 | 0 | 338255.7615 | -1.3893 | -1.3893 | 0 | 2548.4086 | 2033.0247 | 631.863 | 12453.769 | 0 | 1918.7387 | 0 | 0 | 0 | 0 | 10079.1045 | 0 | 0 | 29664.9084 | 0 | 29665.0303 | -0.12184 | -0.12184 | 0 | 99.1468 | 79.0956 | 24.5829 | 484.5184 | 0 | 74.6492 | 0 | 0 | 0 | 0 | 392.1312 | 0 | 0 | 1154.1239 | 0 | 1154.1287 | -0.0047402 | -0.0047402 | 2.3442 | 0.72858 | 14.3599 | 2.2124 | 0 | 0 | 2.9385 | 0 | 11.6218 | 0 | 0 | 34.2055 | 34.2054 | -0.00014049
MO_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 209979.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209979.4048 | 0 | 209979.4048 | 0 | 0 | 1526.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.1303 | 0 | 1526.1303 | 0 | 0 | 209.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.9794 | 0 | 209.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2233 | 0 | 0 | 0 | 6.2233 | 6.2233 | 0
MO_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 117688.9704 | 98050.0611 | 7113.1307 | 317887.4784 | 4818.0346 | 99700.5297 | 1058.6339 | 0 | 0 | 17541.0915 | 7179.8163 | 17649.4556 | 0 | 688687.2022 | 0 | 688688.5915 | -1.3893 | 4816.6453 | 0 | 10321.3227 | 8598.9904 | 623.8216 | 27878.7319 | 422.5416 | 8743.7365 | 92.8422 | 0 | 0 | 1538.3537 | 629.6699 | 1547.8573 | 0 | 60397.8676 | 0 | 60397.9895 | -0.12184 | 422.4198 | 0 | 401.5548 | 334.5468 | 24.27 | 1084.6321 | 16.4391 | 340.1782 | 3.6121 | 0 | 0 | 59.8502 | 24.4975 | 60.2199 | 0 | 2349.8007 | 0 | 2349.8055 | -0.0047402 | 16.4344 | 4.5234 | 0.32815 | 14.6653 | 4.5996 | 0.048839 | 0.80923 | 5.4294 | 0 | 0.33123 | 0 | 0.81423 | 31.7717 | 31.7717 | -6.4093e-05
MO_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 688228.9672 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120666.5975 | 0 | 0 | 1151085.9796 | 0 | 1151085.9796 | 0 | 0 | 5002.0481 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 877.0048 | 0 | 0 | 8366.0929 | 0 | 8366.0929 | 0 | 0 | 688.229 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.6666 | 0 | 0 | 1151.086 | 0 | 1151.086 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3055 | 1.6315 | 0 | 0 | 15.5638 | 15.5638 | 0
MO_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 111690.0449 | 79728.1924 | 7113.1307 | 312483.1662 | 4745.7919 | 83243.0792 | 844.6843 | 0 | 0 | 22598.0828 | 7182.5949 | 12486.8787 | 0 | 642115.646 | 0 | 642114.8125 | 0.83357 | 4746.6255 | 0 | 9795.2169 | 6992.1625 | 623.8216 | 27404.7737 | 416.2059 | 7300.418 | 74.0788 | 0 | 0 | 1981.8519 | 629.9136 | 1095.0993 | 0 | 56313.5422 | 0 | 56313.4691 | 0.073104 | 416.2791 | 0 | 381.0864 | 272.0326 | 24.27 | 1066.1926 | 16.1926 | 284.0254 | 2.8821 | 0 | 0 | 77.1047 | 24.507 | 42.6052 | 0 | 2190.8986 | 0 | 2190.8957 | 0.0028441 | 16.1955 | 3.6782 | 0.32815 | 14.416 | 3.8403 | 0.038968 | 1.0425 | 5.1527 | 0 | 0.33136 | 0 | 0.57607 | 29.6231 | 29.6232 | 3.8456e-05
MO_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 661159.3102 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120382.2524 | 0 | 0 | 1123731.9775 | 0 | 1123731.9775 | 0 | 0 | 4805.3059 | 0 | 0 | 0 | 2487.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 874.9382 | 0 | 0 | 8167.284 | 0 | 8167.284 | 0 | 0 | 661.1593 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.3823 | 0 | 0 | 1123.732 | 0 | 1123.732 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.9395 | 1.6277 | 0 | 0 | 15.194 | 15.194 | 0
MO_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 43954.1463 | 84646.2554 | 10703.0389 | 53987.5506 | 0 | 43534.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236825.574 | 0 | 236824.7405 | 0.83357 | 0.83357 | 0 | 3854.7786 | 7423.4766 | 938.6565 | 4734.7082 | 0 | 3817.9829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20769.6028 | 0 | 20769.5297 | 0.073104 | 0.073104 | 0 | 149.9715 | 288.813 | 36.5188 | 184.2055 | 0 | 148.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808.0489 | 0 | 808.046 | 0.0028441 | 0.0028441 | 11.6966 | 1.479 | 7.4601 | 6.0157 | 0 | 0 | 6.0737 | 0 | 0 | 0 | 0 | 32.725 | 32.7251 | 0.00011518
MO_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 564567.2675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90838.7928 | 0 | 0 | 655406.0603 | 0 | 655406.0603 | 0 | 0 | 4103.2749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.2163 | 0 | 0 | 4763.4912 | 0 | 4763.4912 | 0 | 0 | 564.5673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8388 | 0 | 0 | 655.4061 | 0 | 655.4061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8644 | 3.6789 | 0 | 0 | 26.5433 | 26.5433 | 0
MO_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 0 | 40981.08 | 67060.7069 | 10703.0389 | 53987.5506 | 0 | 44354.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217086.6363 | 0 | 217085.5249 | 1.1114 | 1.1114 | 0 | 3594.0407 | 5881.224 | 938.6565 | 4734.7082 | 0 | 3889.8686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19038.498 | 0 | 19038.4005 | 0.097472 | 0.097472 | 0 | 139.8274 | 228.8111 | 36.5188 | 184.2055 | 0 | 151.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740.6996 | 0 | 740.6958 | 0.0037922 | 0.0037922 | 9.2666 | 1.479 | 7.4601 | 6.129 | 0 | 0 | 5.6629 | 0 | 0 | 0 | 0 | 29.9974 | 29.9976 | 0.00015358
MO_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 587144.2713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90848.271 | 0 | 0 | 677992.5423 | 0 | 677992.5423 | 0 | 0 | 4267.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.2852 | 0 | 0 | 4927.6498 | 0 | 4927.6498 | 0 | 0 | 587.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8483 | 0 | 0 | 677.9925 | 0 | 677.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7787 | 3.6793 | 0 | 0 | 27.458 | 27.458 | 0
MO_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 47077.2553 | 73882.0881 | 79355.8644 | 12303.4933 | 154949.5496 | 0 | 46263.1353 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 413903.6287 | 0 | 413906.1294 | -2.5007 | -2.5007 | 4128.6753 | 6479.4591 | 6959.5093 | 1079.0164 | 13589.0755 | 0 | 4057.277 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 36299.3482 | 0 | 36299.5675 | -0.21931 | -0.21931 | 160.6276 | 252.0857 | 270.7622 | 41.9795 | 528.6879 | 0 | 157.8498 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.2392 | 0 | 1412.2477 | -0.0085324 | -0.0085324 | 6.2674 | 0.9717 | 12.2376 | 3.6538 | 0.0057056 | 0 | 5.835 | 3.7181 | 0 | 0 | 0 | 32.6894 | 32.6892 | -0.0001975
MO_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 98857.3256 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598584.424 | 0 | 0 | 1096937.1875 | 0 | 1096937.1875 | 0 | 0 | 718.495 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.5116 | 0 | 0 | 7972.5395 | 0 | 7972.5395 | 0 | 0 | 98.8573 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.5844 | 0 | 0 | 1096.9372 | 0 | 1096.9372 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.2883 | 13.8555 | 0 | 0 | 25.3909 | 25.3909 | 0
MO_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 51634.1047 | 69194.6461 | 50903.3416 | 12303.4933 | 154949.5496 | 0 | 43831.8894 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 382889.2674 | 0 | 382890.101 | -0.83357 | -0.83357 | 4528.311 | 6068.3705 | 4464.2231 | 1079.0164 | 13589.0755 | 0 | 3844.0567 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 33579.3888 | 0 | 33579.4619 | -0.073104 | -0.073104 | 176.1756 | 236.0921 | 173.6822 | 41.9795 | 528.6879 | 0 | 149.5544 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.4182 | 0 | 1306.421 | -0.0028441 | -0.0028441 | 4.0202 | 0.9717 | 12.2376 | 3.4617 | 0.0057056 | 0 | 5.4648 | 4.0779 | 0 | 0 | 0 | 30.2398 | 30.2398 | -6.5834e-05
MO_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 95388.315 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598622.3366 | 0 | 0 | 1093506.0895 | 0 | 1093506.0895 | 0 | 0 | 693.2823 | 0 | 0 | 0 | 2903.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.7871 | 0 | 0 | 7947.6023 | 0 | 7947.6023 | 0 | 0 | 95.3883 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.6223 | 0 | 0 | 1093.5061 | 0 | 1093.5061 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.208 | 13.8564 | 0 | 0 | 25.3115 | 25.3115 | 0
MO_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 4076.1573 | 4426.2567 | 8863.6277 | 1581.0044 | 13417.6985 | 0 | 5215.3697 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42584.313 | 0 | 42587.3694 | -3.0564 | -3.0564 | 357.479 | 388.1827 | 777.3402 | 138.6541 | 1176.7322 | 0 | 457.3879 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3734.6442 | 0 | 3734.9123 | -0.26805 | -0.26805 | 13.9078 | 15.1024 | 30.2427 | 5.3944 | 45.7812 | 0 | 17.7948 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.2977 | 0 | 145.3081 | -0.010429 | -0.010429 | 5.4967 | 0.98044 | 8.3208 | 3.2342 | 0 | 0 | 2.7449 | 2.5278 | 3.1033 | 0 | 0 | 26.4101 | 26.4082 | -0.0018954
MO_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 19278.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19278.6002 | 0 | 19278.6002 | 0 | 0 | 140.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.1169 | 0 | 140.1169 | 0 | 0 | 19.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2786 | 0 | 19.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5039 | 0 | 0 | 0 | 3.5039 | 3.5039 | 0
MO_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Electricity | 4109.5001 | 4195.6357 | 7140.9164 | 1581.0044 | 13417.6985 | 0 | 4801.3632 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40250.317 | 0 | 40251.7062 | -1.3893 | -1.3893 | 360.4032 | 367.9573 | 626.2584 | 138.6541 | 1176.7322 | 0 | 421.0796 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3529.9528 | 0 | 3530.0746 | -0.12184 | -0.12184 | 14.0216 | 14.3155 | 24.3648 | 5.3944 | 45.7812 | 0 | 16.3823 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.3341 | 0 | 137.3388 | -0.0047402 | -0.0047402 | 4.4284 | 0.98044 | 8.3208 | 2.9775 | 0 | 0 | 2.6019 | 2.5485 | 3.1033 | 0 | 0 | 24.9616 | 24.9608 | -0.00086155
MO_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | MO-KIRKSVILLE-MO | Zone5A | Zone5A(MO-KIRKSVILLE-MO) |  |  | MO | 0.0877 | 0.007268 |  |  |  | Natural Gas | 19667.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19667.2052 | 0 | 19667.2052 | 0 | 0 | 142.9412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.9412 | 0 | 142.9412 | 0 | 0 | 19.6672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6672 | 0 | 19.6672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5746 | 0 | 0 | 0 | 3.5746 | 3.5746 | 0
MS_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 1149304.094 | 882397.757 | 94232.3105 | 4077910.5986 | 543459.8574 | 568678.1286 | 140245.3747 | 431019.5995 | 144174.268 | 15201.5383 | 0 | 0 | 0 | 8046623.5266 | 0 | 8046626.3052 | -2.7786 | 543457.0788 | 0 | 120332.1386 | 92387.0452 | 9866.1229 | 426957.2397 | 56900.2471 | 59540.6001 | 14683.6907 | 45127.7521 | 15095.0459 | 1591.6011 | 0 | 0 | 0 | 842481.4832 | 0 | 842481.7742 | -0.29092 | 56899.9562 | 0 | 3921.4256 | 3010.7411 | 321.5206 | 13913.831 | 1854.285 | 1940.3298 | 478.5172 | 1470.6389 | 491.9226 | 51.8676 | 0 | 0 | 0 | 27455.0795 | 0 | 27455.089 | -0.0094805 | 1854.2756 | 6.0385 | 0.64486 | 27.9065 | 3.8916 | 0.95974 | 0.10403 | 7.8651 | 0 | 0 | 0.98663 | 0 | 55.0657 | 55.0657 | -1.9015e-05
MS_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 447000.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472126.6638 | 0 | 0 | 919126.6958 | 0 | 919126.6958 | 0 | 0 | 3767.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3979.0835 | 0 | 0 | 7746.3998 | 0 | 7746.3998 | 0 | 0 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.1267 | 0 | 0 | 919.1267 | 0 | 919.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89653 | 0.94693 | 0 | 0 | 1.8435 | 1.8435 | 0
MS_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 1087303.157 | 717878.8238 | 94232.3105 | 4077910.5986 | 543387.6147 | 554638.0312 | 136560.9953 | 390138.5479 | 144121.4752 | 13459.377 | 0 | 0 | 0 | 7759630.9312 | 0 | 7759630.3754 | 0.55571 | 543388.1704 | 0 | 113840.6405 | 75161.9128 | 9866.1229 | 426957.2397 | 56892.6833 | 58070.6019 | 14297.9362 | 40847.506 | 15089.5185 | 1409.1968 | 0 | 0 | 0 | 812433.3585 | 0 | 812433.3003 | 0.058183 | 56892.7414 | 0 | 3709.8784 | 2449.4025 | 321.5206 | 13913.831 | 1854.0385 | 1892.425 | 465.9461 | 1331.1527 | 491.7425 | 45.9234 | 0 | 0 | 0 | 26475.8607 | 0 | 26475.8588 | 0.0018961 | 1854.0404 | 4.9127 | 0.64486 | 27.9065 | 3.7956 | 0.93453 | 0.092107 | 7.4408 | 0 | 0 | 0.98627 | 0 | 53.1017 | 53.1017 | 3.8029e-06
MS_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 309670.8094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472088.7511 | 0 | 0 | 781759.5606 | 0 | 781759.5606 | 0 | 0 | 2609.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3978.764 | 0 | 0 | 6588.6696 | 0 | 6588.6696 | 0 | 0 | 309.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.0888 | 0 | 0 | 781.7596 | 0 | 781.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6211 | 0.94685 | 0 | 0 | 1.5679 | 1.5679 | 0
MS_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 52451.0033 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 23776.1951 | 0 | 0 | 0 | 0 | 94935.2878 | 0 | 0 | 348757.3543 | 0 | 348755.1314 | 2.2229 | 2.2229 | 0 | 5491.62 | 2970.8335 | 755.5087 | 14867.8405 | 0 | 2489.3676 | 0 | 0 | 0 | 0 | 9939.7246 | 0 | 0 | 36514.895 | 0 | 36514.6623 | 0.23273 | 0.23273 | 0 | 178.9628 | 96.8146 | 24.6208 | 484.5184 | 0 | 81.1244 | 0 | 0 | 0 | 0 | 323.9192 | 0 | 0 | 1189.9601 | 0 | 1189.9525 | 0.0075844 | 0.0075844 | 2.8693 | 0.7297 | 14.3599 | 2.4043 | 0 | 0 | 5.304 | 0 | 9.6002 | 0 | 0 | 35.2673 | 35.2675 | 0.00022478
MS_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 49286.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49286.4902 | 0 | 49286.4902 | 0 | 0 | 415.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3865 | 0 | 415.3865 | 0 | 0 | 49.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2865 | 0 | 49.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4607 | 0 | 0 | 0 | 1.4607 | 1.4607 | 0
MS_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 47908.0467 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 23126.0105 | 0 | 0 | 0 | 0 | 94832.4809 | 0 | 0 | 338268.265 | 0 | 338266.8758 | 1.3893 | 1.3893 | 0 | 5015.9725 | 2427.1116 | 755.5087 | 14867.8405 | 0 | 2421.2933 | 0 | 0 | 0 | 0 | 9928.9607 | 0 | 0 | 35416.6874 | 0 | 35416.5419 | 0.14546 | 0.14546 | 0 | 163.4623 | 79.0956 | 24.6208 | 484.5184 | 0 | 78.9059 | 0 | 0 | 0 | 0 | 323.5684 | 0 | 0 | 1154.1713 | 0 | 1154.1666 | 0.0047402 | 0.0047402 | 2.3442 | 0.7297 | 14.3599 | 2.3386 | 0 | 0 | 4.8446 | 0 | 9.5898 | 0 | 0 | 34.2067 | 34.2068 | 0.00014049
MS_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 13800.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13800.2173 | 0 | 13800.2173 | 0 | 0 | 116.3082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.3082 | 0 | 116.3082 | 0 | 0 | 13.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8002 | 0 | 13.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0.409 | 0.409 | 0
MS_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 219209.4613 | 101020.3489 | 7085.345 | 317887.4784 | 4818.0346 | 94779.6881 | 252.8496 | 0 | 0 | 22692.5541 | 7179.8163 | 17735.5911 | 0 | 792661.1674 | 0 | 792661.4453 | -0.27786 | 4817.7568 | 0 | 22951.2306 | 10576.8305 | 741.8356 | 33282.819 | 504.4482 | 9923.4333 | 26.4733 | 0 | 0 | 2375.9104 | 751.7268 | 1856.9164 | 0 | 82991.6242 | 0 | 82991.6533 | -0.029092 | 504.4191 | 0 | 747.9427 | 344.6814 | 24.1752 | 1084.6321 | 16.4391 | 323.3883 | 0.86272 | 0 | 0 | 77.427 | 24.4975 | 60.5138 | 0 | 2704.5599 | 0 | 2704.5609 | -0.00094805 | 16.4382 | 4.6604 | 0.32687 | 14.6653 | 4.3725 | 0.011665 | 1.0469 | 10.1129 | 0 | 0.33123 | 0 | 0.81821 | 36.5684 | 36.5684 | -1.2819e-05
MS_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 142712.8238 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99321.756 | 0 | 0 | 584224.9946 | 0 | 584224.9946 | 0 | 0 | 1202.7837 | 0 | 0 | 0 | 2883.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 837.0838 | 0 | 0 | 4923.8483 | 0 | 4923.8483 | 0 | 0 | 142.7128 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3218 | 0 | 0 | 584.225 | 0 | 584.225 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.9296 | 1.3429 | 0 | 0 | 7.8993 | 7.8993 | 0
MS_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 203466.1025 | 81667.6319 | 7085.345 | 312483.1662 | 4745.7919 | 84929.6692 | 208.3925 | 0 | 0 | 22992.6393 | 7179.8163 | 12542.45 | 0 | 737301.0049 | 0 | 737299.8934 | 1.1114 | 4746.9033 | 0 | 21302.9009 | 8550.6011 | 741.8356 | 32716.9875 | 496.8844 | 8892.1364 | 21.8187 | 0 | 0 | 2407.3293 | 751.7268 | 1313.1945 | 0 | 77195.4152 | 0 | 77195.2988 | 0.11637 | 497.0008 | 0 | 694.2263 | 278.65 | 24.1752 | 1066.1926 | 16.1926 | 289.78 | 0.71104 | 0 | 0 | 78.4509 | 24.4975 | 42.7948 | 0 | 2515.671 | 0 | 2515.6672 | 0.0037922 | 16.1964 | 3.7676 | 0.32687 | 14.416 | 3.9181 | 0.0096139 | 1.0607 | 9.3866 | 0 | 0.33123 | 0 | 0.57863 | 34.0143 | 34.0144 | 5.1274e-05
MS_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 119917.822 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 99075.3236 | 0 | 0 | 561183.5604 | 0 | 561183.5604 | 0 | 0 | 1010.6674 | 0 | 0 | 0 | 2883.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 835.0068 | 0 | 0 | 4729.655 | 0 | 4729.655 | 0 | 0 | 119.9178 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0753 | 0 | 0 | 561.1836 | 0 | 561.1836 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.6214 | 1.3396 | 0 | 0 | 7.5878 | 7.5878 | 0
MS_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 83245.8578 | 83145.8294 | 10708.596 | 53987.5506 | 0 | 36824.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267912.1781 | 0 | 267911.6224 | 0.55571 | 0.55571 | 0 | 8715.8413 | 8705.3683 | 1121.19 | 5652.4966 | 0 | 3855.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28050.405 | 0 | 28050.3469 | 0.058183 | 0.058183 | 0 | 284.0349 | 283.6936 | 36.5377 | 184.2055 | 0 | 125.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.1164 | 0 | 914.1145 | 0.0018961 | 0.0018961 | 11.4893 | 1.4797 | 7.4601 | 5.0885 | 0 | 0 | 11.5031 | 0 | 0 | 0 | 0 | 37.0207 | 37.0207 | 7.679e-05
MS_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 66650.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84753.8069 | 0 | 0 | 151404.3067 | 0 | 151404.3067 | 0 | 0 | 561.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.3051 | 0 | 0 | 1276.0355 | 0 | 1276.0355 | 0 | 0 | 66.6505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7538 | 0 | 0 | 151.4043 | 0 | 151.4043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6993 | 3.4324 | 0 | 0 | 6.1317 | 6.1317 | 0
MS_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 78291.6734 | 65613.0736 | 10708.596 | 53987.5506 | 0 | 34987.7117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243588.6053 | 0 | 243587.7718 | 0.83357 | 0.83357 | 0 | 8197.1382 | 6869.6888 | 1121.19 | 5652.4966 | 0 | 3663.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25503.727 | 0 | 25503.6397 | 0.087275 | 0.087275 | 0 | 267.1312 | 223.8718 | 36.5377 | 184.2055 | 0 | 119.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831.1243 | 0 | 831.1215 | 0.0028441 | 0.0028441 | 9.0666 | 1.4797 | 7.4601 | 4.8347 | 0 | 0 | 10.8185 | 0 | 0 | 0 | 0 | 33.6595 | 33.6597 | 0.00011518
MS_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 74090.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84763.285 | 0 | 0 | 158854.1493 | 0 | 158854.1493 | 0 | 0 | 624.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.385 | 0 | 0 | 1338.8228 | 0 | 1338.8228 | 0 | 0 | 74.0909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7633 | 0 | 0 | 158.8541 | 0 | 158.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0006 | 3.4328 | 0 | 0 | 6.4334 | 6.4334 | 0
MS_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 5637.7118 | 117286.0782 | 80144.9774 | 12322.9432 | 154949.5496 | 0 | 46460.4135 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 416873.9165 | 0 | 416874.1943 | -0.27786 | -0.27786 | 590.2684 | 12279.8524 | 8391.1791 | 1290.2122 | 16223.2178 | 0 | 4864.4053 | 7.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 43646.6991 | 0 | 43646.7281 | -0.029092 | -0.029092 | 19.2359 | 400.1801 | 273.4547 | 42.0459 | 528.6879 | 0 | 158.5229 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1422.3738 | 0 | 1422.3748 | -0.00094805 | -0.00094805 | 6.3297 | 0.97324 | 12.2376 | 3.6693 | 0.0057056 | 0 | 9.263 | 0.44525 | 0 | 0 | 0 | 32.9238 | 32.9238 | -2.1945e-05
MS_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 11961.4521 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 484163.9412 | 0 | 0 | 895620.8312 | 0 | 895620.8312 | 0 | 0 | 100.8111 | 0 | 0 | 0 | 3366.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 4080.5337 | 0 | 0 | 7548.2924 | 0 | 7548.2924 | 0 | 0 | 11.9615 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 484.1639 | 0 | 0 | 895.6208 | 0 | 895.6208 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.27687 | 11.207 | 0 | 0 | 20.731 | 20.731 | 0
MS_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 6437.939 | 110937.0534 | 51339.5766 | 12322.9432 | 154949.5496 | 0 | 44234.7816 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380294.0861 | 0 | 380294.0861 | 0 | 0 | 674.0522 | 11615.1095 | 5375.2537 | 1290.2122 | 16223.2178 | 0 | 4631.3816 | 7.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 39816.7908 | 0 | 39816.7908 | 0 | 0 | 21.9662 | 378.5172 | 175.1706 | 42.0459 | 528.6879 | 0 | 150.9291 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.5634 | 0 | 1297.5634 | 0 | 0 | 4.0547 | 0.97324 | 12.2376 | 3.4936 | 0.0057056 | 0 | 8.7616 | 0.50845 | 0 | 0 | 0 | 30.0348 | 30.0348 | 0
MS_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 12795.5311 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 484144.9849 | 0 | 0 | 896435.9539 | 0 | 896435.9539 | 0 | 0 | 107.8407 | 0 | 0 | 0 | 3366.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 4080.3739 | 0 | 0 | 7555.1622 | 0 | 7555.1622 | 0 | 0 | 12.7955 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 484.145 | 0 | 0 | 896.436 | 0 | 896.436 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.29618 | 11.2065 | 0 | 0 | 20.7499 | 20.7499 | 0
MS_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 647.406 | 8357.9286 | 9005.3346 | 1561.5545 | 13417.6985 | 0 | 5070.8842 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43065.005 | 0 | 43065.005 | 0 | 0 | 67.7834 | 875.0751 | 942.8585 | 163.4948 | 1404.833 | 0 | 530.9216 | 0 | 0 | 0 | 0 | 523.9396 | 0 | 0 | 4508.906 | 0 | 4508.906 | 0 | 0 | 2.2089 | 28.5173 | 30.7262 | 5.328 | 45.7812 | 0 | 17.3019 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.9378 | 0 | 146.9378 | 0 | 0 | 5.5846 | 0.96838 | 8.3208 | 3.1446 | 0 | 0 | 5.1831 | 0.40148 | 3.1033 | 0 | 0 | 26.7063 | 26.7063 | 0
MS_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 568.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.6903 | 0 | 568.6903 | 0 | 0 | 4.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7929 | 0 | 4.7929 | 0 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56869 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10336 | 0 | 0 | 0 | 0.10336 | 0.10336 | 0
MS_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 630.7346 | 8005.0506 | 7232.6091 | 1561.5545 | 13417.6985 | 0 | 4640.2064 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40492.0523 | 0 | 40489.2737 | 2.7786 | 2.7786 | 66.0379 | 838.1288 | 757.2542 | 163.4948 | 1404.833 | 0 | 485.8296 | 0 | 0 | 0 | 0 | 523.9396 | 0 | 0 | 4239.5179 | 0 | 4239.227 | 0.29092 | 0.29092 | 2.1521 | 27.3132 | 24.6777 | 5.328 | 45.7812 | 0 | 15.8324 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.1589 | 0 | 138.1494 | 0.0094805 | 0.0094805 | 4.4852 | 0.96838 | 8.3208 | 2.8776 | 0 | 0 | 4.9642 | 0.39114 | 3.1033 | 0 | 0 | 25.1089 | 25.1107 | 0.0017231
MS_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | MS-MOBILE-AL | Zone2A | Zone2A(MS-MOBILE-AL) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 559.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559.2121 | 0 | 559.2121 | 0 | 0 | 4.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.713 | 0 | 4.713 | 0 | 0 | 0.55921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55921 | 0 | 0.55921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10164 | 0 | 0 | 0 | 0.10164 | 0.10164 | 0
MS_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 1032326.4366 | 882000.422 | 94346.2317 | 4077910.5986 | 543457.0788 | 577055.5072 | 131023.3119 | 370874.7451 | 183093.6515 | 13676.1052 | 0 | 0 | 0 | 7905764.0887 | 0 | 7905763.8108 | 0.27786 | 543457.3567 | 0 | 108084.5779 | 92345.4442 | 9878.0505 | 426957.2397 | 56899.9562 | 60417.7116 | 13718.1408 | 38830.5858 | 19169.9053 | 1431.8882 | 0 | 0 | 0 | 827733.5001 | 0 | 827733.471 | 0.029092 | 56899.9852 | 0 | 3522.2978 | 3009.3854 | 321.9093 | 13913.831 | 1854.2756 | 1968.9134 | 447.0515 | 1265.4246 | 624.7155 | 46.6629 | 0 | 0 | 0 | 26974.4671 | 0 | 26974.4661 | 0.00094805 | 1854.2765 | 6.0358 | 0.64564 | 27.9065 | 3.949 | 0.89664 | 0.09359 | 7.0645 | 0 | 0 | 1.253 | 0 | 54.1017 | 54.1017 | 1.9015e-06
MS_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 434867.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488884.0705 | 0 | 0 | 923752.0433 | 0 | 923752.0433 | 0 | 0 | 3665.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.3149 | 0 | 0 | 7785.3822 | 0 | 7785.3822 | 0 | 0 | 434.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.8841 | 0 | 0 | 923.752 | 0 | 923.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8722 | 0.98054 | 0 | 0 | 1.8527 | 1.8527 | 0
MS_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 965613.0506 | 717514.8315 | 94346.2317 | 4077910.5986 | 543387.6147 | 562912.6028 | 123362.8036 | 334614.4499 | 182965.8375 | 13100.9419 | 0 | 0 | 0 | 7615728.9627 | 0 | 7615725.9063 | 3.0564 | 543390.6711 | 0 | 101099.6864 | 75123.8029 | 9878.0505 | 426957.2397 | 56892.6833 | 58936.9495 | 12916.0855 | 35034.1329 | 19156.5232 | 1371.6686 | 0 | 0 | 0 | 797366.8224 | 0 | 797366.5024 | 0.32001 | 56893.0033 | 0 | 3294.6717 | 2448.1606 | 321.9093 | 13913.831 | 1854.0385 | 1920.6578 | 420.9139 | 1141.7045 | 624.2794 | 44.7004 | 0 | 0 | 0 | 25984.8672 | 0 | 25984.8568 | 0.010429 | 1854.049 | 4.9102 | 0.64564 | 27.9065 | 3.8522 | 0.84421 | 0.089654 | 6.608 | 0 | 0 | 1.2521 | 0 | 52.1169 | 52.1169 | 2.0916e-05
MS_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 232802.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488931.4614 | 0 | 0 | 721734.3024 | 0 | 721734.3024 | 0 | 0 | 1962.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.7144 | 0 | 0 | 6082.7767 | 0 | 6082.7767 | 0 | 0 | 232.8028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.9315 | 0 | 0 | 721.7343 | 0 | 721.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46692 | 0.98063 | 0 | 0 | 1.4476 | 1.4476 | 0
MS_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 49083.3804 | 28374.723 | 7207.602 | 142004.2074 | 0 | 23523.3455 | 0 | 0 | 0 | 0 | 98322.3606 | 0 | 0 | 348515.619 | 0 | 348515.0633 | 0.55571 | 0.55571 | 0 | 5139.0299 | 2970.8335 | 754.6359 | 14867.8405 | 0 | 2462.8943 | 0 | 0 | 0 | 0 | 10294.3512 | 0 | 0 | 36489.5853 | 0 | 36489.5271 | 0.058183 | 0.058183 | 0 | 167.4725 | 96.8146 | 24.5923 | 484.5184 | 0 | 80.2617 | 0 | 0 | 0 | 0 | 335.4759 | 0 | 0 | 1189.1353 | 0 | 1189.1334 | 0.0018961 | 0.0018961 | 2.8693 | 0.72886 | 14.3599 | 2.3788 | 0 | 0 | 4.9635 | 0 | 9.9427 | 0 | 0 | 35.243 | 35.243 | 5.6196e-05
MS_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 70147.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70147.9451 | 0 | 70147.9451 | 0 | 0 | 591.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.2069 | 0 | 591.2069 | 0 | 0 | 70.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1479 | 0 | 70.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.079 | 0 | 0 | 0 | 2.079 | 2.079 | 0
MS_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 45399.001 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 22795.3611 | 0 | 0 | 0 | 0 | 98194.5466 | 0 | 0 | 338782.2999 | 0 | 338783.1335 | -0.83357 | -0.83357 | 0 | 4753.2754 | 2427.1116 | 754.6359 | 14867.8405 | 0 | 2386.6743 | 0 | 0 | 0 | 0 | 10280.969 | 0 | 0 | 35470.5068 | 0 | 35470.5941 | -0.087275 | -0.087275 | 0 | 154.9014 | 79.0956 | 24.5923 | 484.5184 | 0 | 77.7778 | 0 | 0 | 0 | 0 | 335.0398 | 0 | 0 | 1155.9252 | 0 | 1155.9281 | -0.0028441 | -0.0028441 | 2.3442 | 0.72886 | 14.3599 | 2.3051 | 0 | 0 | 4.5909 | 0 | 9.9298 | 0 | 0 | 34.2589 | 34.2588 | -8.4293e-05
MS_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 18397.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18397.1303 | 0 | 18397.1303 | 0 | 0 | 155.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.051 | 0 | 155.051 | 0 | 0 | 18.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3971 | 0 | 18.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54525 | 0 | 0 | 0 | 0.54525 | 0.54525 | 0
MS_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 194513.5606 | 100611.8996 | 7082.5665 | 317887.4784 | 4818.0346 | 93701.6042 | 319.5352 | 0 | 0 | 22370.2404 | 7179.8163 | 17713.3626 | 0 | 766198.0984 | 0 | 766198.0984 | 0 | 4818.0346 | 0 | 20365.5698 | 10534.0659 | 741.5447 | 33282.819 | 504.4482 | 9810.558 | 33.4553 | 0 | 0 | 2342.1642 | 751.7268 | 1854.5891 | 0 | 80220.9409 | 0 | 80220.9409 | 0 | 504.4482 | 0 | 663.6803 | 343.2878 | 24.1657 | 1084.6321 | 16.4391 | 319.7099 | 1.0903 | 0 | 0 | 76.3273 | 24.4975 | 60.438 | 0 | 2614.2679 | 0 | 2614.2679 | 0 | 16.4391 | 4.6416 | 0.32674 | 14.6653 | 4.3228 | 0.014741 | 1.032 | 8.9736 | 0 | 0.33123 | 0 | 0.81718 | 35.3475 | 35.3475 | 0
MS_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 188340.7399 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102923.4611 | 0 | 0 | 633454.6158 | 0 | 633454.6158 | 0 | 0 | 1587.3358 | 0 | 0 | 0 | 2883.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 867.4389 | 0 | 0 | 5338.7555 | 0 | 5338.7555 | 0 | 0 | 188.3407 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9235 | 0 | 0 | 633.4546 | 0 | 633.4546 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.5466 | 1.3916 | 0 | 0 | 8.5649 | 8.5649 | 0
MS_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 179956.6498 | 81239.7327 | 7082.5665 | 312483.1662 | 4745.7919 | 83607.0715 | 250.071 | 0 | 0 | 22928.7323 | 7179.8163 | 12534.1143 | 0 | 712007.7124 | 0 | 712007.9902 | -0.27786 | 4745.514 | 0 | 18841.4612 | 8505.8 | 741.5447 | 32716.9875 | 496.8844 | 8753.6604 | 26.1824 | 0 | 0 | 2400.6383 | 751.7268 | 1312.3218 | 0 | 74547.2075 | 0 | 74547.2366 | -0.029092 | 496.8553 | 0 | 614.0121 | 277.19 | 24.1657 | 1066.1926 | 16.1926 | 285.2673 | 0.85324 | 0 | 0 | 78.2328 | 24.4975 | 42.7664 | 0 | 2429.3703 | 0 | 2429.3713 | -0.00094805 | 16.1917 | 3.7479 | 0.32674 | 14.416 | 3.8571 | 0.011537 | 1.0578 | 8.3021 | 0 | 0.33123 | 0 | 0.57824 | 32.8475 | 32.8475 | -1.2819e-05
MS_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 159365.9706 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102658.0723 | 0 | 0 | 604214.4577 | 0 | 604214.4577 | 0 | 0 | 1343.1364 | 0 | 0 | 0 | 2883.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 865.2022 | 0 | 0 | 5092.3194 | 0 | 5092.3194 | 0 | 0 | 159.366 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6581 | 0 | 0 | 604.2145 | 0 | 604.2145 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.1548 | 1.388 | 0 | 0 | 8.1696 | 8.1696 | 0
MS_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 75010.1862 | 82909.6512 | 10689.146 | 53987.5506 | 0 | 37096.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259693.1778 | 0 | 259691.7886 | 1.3893 | 1.3893 | 0 | 7853.5665 | 8680.6405 | 1119.1536 | 5652.4966 | 0 | 3884.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27189.8757 | 0 | 27189.7303 | 0.14546 | 0.14546 | 0 | 255.9348 | 282.8877 | 36.4714 | 184.2055 | 0 | 126.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.0731 | 0 | 886.0684 | 0.0047402 | 0.0047402 | 11.4567 | 1.4771 | 7.4601 | 5.1261 | 0 | 0 | 10.3651 | 0 | 0 | 0 | 0 | 35.8848 | 35.885 | 0.00019197
MS_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 102079.9038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85777.4494 | 0 | 0 | 187857.3532 | 0 | 187857.3532 | 0 | 0 | 860.3294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722.9323 | 0 | 0 | 1583.2618 | 0 | 1583.2618 | 0 | 0 | 102.0799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7774 | 0 | 0 | 187.8574 | 0 | 187.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1341 | 3.4739 | 0 | 0 | 7.608 | 7.608 | 0
MS_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 0 | 70419.994 | 65429.6882 | 10689.146 | 53987.5506 | 0 | 35282.2397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235808.6186 | 0 | 235806.6736 | 1.945 | 1.945 | 0 | 7372.9734 | 6850.4884 | 1119.1536 | 5652.4966 | 0 | 3694.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24689.1624 | 0 | 24688.9587 | 0.20364 | 0.20364 | 0 | 240.273 | 223.2461 | 36.4714 | 184.2055 | 0 | 120.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.579 | 0 | 804.5724 | 0.0066363 | 0.0066363 | 9.0412 | 1.4771 | 7.4601 | 4.8754 | 0 | 0 | 9.7308 | 0 | 0 | 0 | 0 | 32.5843 | 32.5846 | 0.00026876
MS_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 115282.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85786.9275 | 0 | 0 | 201069.9238 | 0 | 201069.9238 | 0 | 0 | 971.6051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723.0122 | 0 | 0 | 1694.6173 | 0 | 1694.6173 | 0 | 0 | 115.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7869 | 0 | 0 | 201.0699 | 0 | 201.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6688 | 3.4743 | 0 | 0 | 8.1431 | 8.1431 | 0
MS_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 7429.8873 | 108553.0431 | 80047.7276 | 12309.0504 | 154949.5496 | 0 | 46365.9422 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 409727.443 | 0 | 409727.443 | 0 | 0 | 777.9092 | 11365.5036 | 8380.9971 | 1288.7576 | 16223.2178 | 0 | 4854.5142 | 7.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 42898.4633 | 0 | 42898.4633 | 0 | 0 | 25.3508 | 370.383 | 273.1228 | 41.9985 | 528.6879 | 0 | 158.2006 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1397.99 | 0 | 1397.99 | 0 | 0 | 6.322 | 0.97214 | 12.2376 | 3.6619 | 0.0057056 | 0 | 8.5733 | 0.5868 | 0 | 0 | 0 | 32.3594 | 32.3594 | 0
MS_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 18766.779 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 501954.4686 | 0 | 0 | 920216.6855 | 0 | 920216.6855 | 0 | 0 | 158.1664 | 0 | 0 | 0 | 3366.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 4230.4723 | 0 | 0 | 7755.5862 | 0 | 7755.5862 | 0 | 0 | 18.7668 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 501.9545 | 0 | 0 | 920.2167 | 0 | 920.2167 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.4344 | 11.6188 | 0 | 0 | 21.3003 | 21.3003 | 0
MS_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 8758.0422 | 102342.9466 | 51267.3339 | 12309.0504 | 154949.5496 | 0 | 44098.6318 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373797.7972 | 0 | 373798.0751 | -0.27786 | -0.27786 | 916.967 | 10715.3065 | 5367.6899 | 1288.7576 | 16223.2178 | 0 | 4617.1268 | 7.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 39136.6294 | 0 | 39136.6585 | -0.029092 | -0.029092 | 29.8824 | 349.1941 | 174.9241 | 41.9985 | 528.6879 | 0 | 150.4645 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.3981 | 0 | 1275.399 | -0.00094805 | -0.00094805 | 4.049 | 0.97214 | 12.2376 | 3.4828 | 0.0057056 | 0 | 8.0828 | 0.69169 | 0 | 0 | 0 | 29.5218 | 29.5217 | -2.1945e-05
MS_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 20283.2864 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 501992.3813 | 0 | 0 | 921771.1055 | 0 | 921771.1055 | 0 | 0 | 170.9475 | 0 | 0 | 0 | 3366.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 4230.7918 | 0 | 0 | 7768.6869 | 0 | 7768.6869 | 0 | 0 | 20.2833 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 501.9924 | 0 | 0 | 921.7711 | 0 | 921.7711 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.4695 | 11.6197 | 0 | 0 | 21.3363 | 21.3363 | 0
MS_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 989.1697 | 7552.1442 | 8996.9989 | 1564.333 | 13417.6985 | 0 | 5065.3271 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42589.8701 | 0 | 42589.0365 | 0.83357 | 0.83357 | 103.5661 | 790.7095 | 941.9858 | 163.7857 | 1404.833 | 0 | 530.3397 | 0 | 0 | 0 | 0 | 523.9396 | 0 | 0 | 4459.1594 | 0 | 4459.0721 | 0.087275 | 0.087275 | 3.375 | 25.7679 | 30.6978 | 5.3375 | 45.7812 | 0 | 17.2829 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.3166 | 0 | 145.3138 | 0.0028441 | 0.0028441 | 5.5794 | 0.9701 | 8.3208 | 3.1412 | 0 | 0 | 4.6834 | 0.61342 | 3.1033 | 0 | 0 | 26.4111 | 26.4116 | 0.00051693
MS_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 701.3847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 701.3847 | 0 | 701.3847 | 0 | 0 | 5.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9113 | 0 | 5.9113 | 0 | 0 | 0.70138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70138 | 0 | 0.70138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12748 | 0 | 0 | 0 | 0.12748 | 0.12748 | 0
MS_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Electricity | 1016.9554 | 7196.4877 | 7224.2734 | 1564.333 | 13417.6985 | 0 | 4654.0992 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40078.0458 | 0 | 40076.1008 | 1.945 | 1.945 | 106.4752 | 753.4723 | 756.3814 | 163.7857 | 1404.833 | 0 | 487.2842 | 0 | 0 | 0 | 0 | 523.9396 | 0 | 0 | 4196.1714 | 0 | 4195.9678 | 0.20364 | 0.20364 | 3.4699 | 24.5544 | 24.6492 | 5.3375 | 45.7812 | 0 | 15.8798 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.7463 | 0 | 136.7397 | 0.0066363 | 0.0066363 | 4.48 | 0.9701 | 8.3208 | 2.8862 | 0 | 0 | 4.4628 | 0.63065 | 3.1033 | 0 | 0 | 24.8527 | 24.8539 | 0.0012062
MS_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | MS-JACKSON-MS | Zone3A | Zone3A(MS-JACKSON-MS) |  |  | MS | 0.1047 | 0.008428 |  |  |  | Natural Gas | 758.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.2537 | 0 | 758.2537 | 0 | 0 | 6.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3906 | 0 | 6.3906 | 0 | 0 | 0.75825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75825 | 0 | 0.75825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13781 | 0 | 0 | 0 | 0.13781 | 0.13781 | 0
MT_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 402008.5847 | 881853.158 | 96833.0489 | 4077910.5986 | 543459.8574 | 691412.9761 | 70508.9081 | 118541.9904 | 677070.0149 | 0 | 0 | 0 | 0 | 7559599.1371 | 0 | 7559598.3036 | 0.83357 | 543460.691 | 0 | 42532.5083 | 93300.0641 | 10244.9366 | 431442.9413 | 57498.0529 | 73151.4929 | 7459.8425 | 12541.7426 | 71634.0076 | 0 | 0 | 0 | 0 | 799805.5887 | 0 | 799805.5005 | 0.088192 | 57498.1411 | 0 | 1371.6533 | 3008.883 | 330.3944 | 13913.831 | 1854.285 | 2359.1011 | 240.5764 | 404.4653 | 2310.1629 | 0 | 0 | 0 | 0 | 25793.3523 | 0 | 25793.3494 | 0.0028441 | 1854.2879 | 6.0348 | 0.66266 | 27.9065 | 4.7316 | 0.48252 | 0 | 2.7511 | 0 | 0 | 4.6334 | 0 | 51.7328 | 51.7328 | 5.7044e-06
MT_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 2222005.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607721.381 | 0 | 0 | 2829726.9681 | 0 | 2829726.9681 | 0 | 0 | 15171.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149.5216 | 0 | 0 | 19321.3757 | 0 | 19321.3757 | 0 | 0 | 2222.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.7214 | 0 | 0 | 2829.727 | 0 | 2829.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4566 | 1.2189 | 0 | 0 | 5.6755 | 5.6755 | 0
MT_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 370382.9388 | 718103.8877 | 96833.0489 | 4077910.5986 | 543387.6147 | 663555.0666 | 67958.1839 | 105541.0769 | 677056.1221 | 0 | 0 | 0 | 0 | 7320728.538 | 0 | 7320726.8709 | 1.6671 | 543389.2818 | 0 | 39186.5149 | 75975.3913 | 10244.9366 | 431442.9413 | 57490.4096 | 70204.126 | 7189.9759 | 11166.2459 | 71632.5377 | 0 | 0 | 0 | 0 | 774533.0793 | 0 | 774532.9029 | 0.17638 | 57490.586 | 0 | 1263.7466 | 2450.1705 | 330.3944 | 13913.831 | 1854.0385 | 2264.0499 | 231.8733 | 360.1062 | 2310.1155 | 0 | 0 | 0 | 0 | 24978.3258 | 0 | 24978.3201 | 0.0056883 | 1854.0442 | 4.9142 | 0.66266 | 27.9065 | 4.5409 | 0.46506 | 0 | 2.5347 | 0 | 0 | 4.6333 | 0 | 50.0981 | 50.0981 | 1.1409e-05
MT_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 3236615.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607636.0775 | 0 | 0 | 3844251.457 | 0 | 3844251.457 | 0 | 0 | 22099.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4148.9391 | 0 | 0 | 26248.5489 | 0 | 26248.5489 | 0 | 0 | 3236.6154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.6361 | 0 | 0 | 3844.2515 | 0 | 3844.2515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4916 | 1.2187 | 0 | 0 | 7.7103 | 7.7103 | 0
MT_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 20230.744 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 21400.5206 | 0 | 0 | 0 | 0 | 121670.6565 | 0 | 0 | 340880.1177 | 0 | 340879.562 | 0.55571 | 0.55571 | 0 | 2140.4127 | 3002.0457 | 761.6824 | 15024.0451 | 0 | 2264.1751 | 0 | 0 | 0 | 0 | 12872.7555 | 0 | 0 | 36065.1165 | 0 | 36065.0577 | 0.058794 | 0.058794 | 0 | 69.0273 | 96.8146 | 24.5639 | 484.5184 | 0 | 73.0186 | 0 | 0 | 0 | 0 | 415.1403 | 0 | 0 | 1163.083 | 0 | 1163.0811 | 0.0018961 | 0.0018961 | 2.8693 | 0.72801 | 14.3599 | 2.1641 | 0 | 0 | 2.0458 | 0 | 12.3037 | 0 | 0 | 34.4709 | 34.4709 | 5.6196e-05
MT_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 134722.7254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134722.7254 | 0 | 134722.7254 | 0 | 0 | 919.8868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919.8868 | 0 | 919.8868 | 0 | 0 | 134.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.7227 | 0 | 134.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9928 | 0 | 0 | 0 | 3.9928 | 3.9928 | 0
MT_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 19144.3244 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 20333.551 | 0 | 0 | 0 | 0 | 121662.3208 | 0 | 0 | 333525.2517 | 0 | 333529.4196 | -4.1679 | -4.1679 | 0 | 2025.4695 | 2452.6114 | 761.6824 | 15024.0451 | 0 | 2151.2897 | 0 | 0 | 0 | 0 | 12871.8735 | 0 | 0 | 35286.9716 | 0 | 35287.4126 | -0.44096 | -0.44096 | 0 | 65.3204 | 79.0956 | 24.5639 | 484.5184 | 0 | 69.3781 | 0 | 0 | 0 | 0 | 415.1118 | 0 | 0 | 1137.9882 | 0 | 1138.0024 | -0.014221 | -0.014221 | 2.3442 | 0.72801 | 14.3599 | 2.0562 | 0 | 0 | 1.9359 | 0 | 12.3029 | 0 | 0 | 33.7276 | 33.7272 | -0.00042147
MT_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 129765.6419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129765.6419 | 0 | 129765.6419 | 0 | 0 | 886.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.0398 | 0 | 886.0398 | 0 | 0 | 129.7656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7656 | 0 | 129.7656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 0 | 3.8459 | 3.8459 | 0
MT_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 50875.556 | 97035.8842 | 7143.6949 | 317887.4784 | 4818.0346 | 101514.9337 | 1044.7411 | 0 | 0 | 18288.5259 | 7179.8163 | 17499.413 | 0 | 623288.0782 | 0 | 623289.4675 | -1.3893 | 4816.6453 | 0 | 5382.6338 | 10266.3966 | 755.8029 | 33632.4952 | 509.7481 | 10740.28 | 110.5336 | 0 | 0 | 1934.926 | 759.6246 | 1851.4379 | 0 | 65943.8787 | 0 | 65944.0257 | -0.14699 | 509.6011 | 0 | 173.5874 | 331.0864 | 24.3743 | 1084.6321 | 16.4391 | 346.369 | 3.5647 | 0 | 0 | 62.4005 | 24.4975 | 59.708 | 0 | 2126.6589 | 0 | 2126.6637 | -0.0047402 | 16.4344 | 4.4766 | 0.32956 | 14.6653 | 4.6833 | 0.048198 | 0.84372 | 2.3471 | 0 | 0.33123 | 0 | 0.80731 | 28.7546 | 28.7546 | -6.4093e-05
MT_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 487566.6047 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126182.8932 | 0 | 0 | 955939.9127 | 0 | 955939.9127 | 0 | 0 | 3329.1048 | 0 | 0 | 0 | 2336.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 861.5768 | 0 | 0 | 6527.1577 | 0 | 6527.1577 | 0 | 0 | 487.5666 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.1829 | 0 | 0 | 955.9399 | 0 | 955.9399 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.5924 | 1.7061 | 0 | 0 | 12.9253 | 12.9253 | 0
MT_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 44854.402 | 79230.8289 | 7143.6949 | 312483.1662 | 4745.7919 | 80678.4622 | 958.6055 | 0 | 0 | 20311.3224 | 7179.8163 | 12431.3073 | 0 | 570017.3978 | 0 | 570021.2878 | -3.89 | 4741.9019 | 0 | 4745.5957 | 8382.6217 | 755.8029 | 33060.719 | 502.1048 | 8535.7813 | 101.4205 | 0 | 0 | 2148.9379 | 759.6246 | 1315.2323 | 0 | 60307.8407 | 0 | 60308.2522 | -0.41156 | 501.6932 | 0 | 153.0432 | 270.3356 | 24.3743 | 1066.1926 | 16.1926 | 275.2749 | 3.2708 | 0 | 0 | 69.3022 | 24.4975 | 42.4156 | 0 | 1944.8994 | 0 | 1944.9126 | -0.013273 | 16.1794 | 3.6552 | 0.32956 | 14.416 | 3.722 | 0.044224 | 0.93704 | 2.0693 | 0 | 0.33123 | 0 | 0.5735 | 26.2972 | 26.297 | -0.00017946
MT_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 607437.0359 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126097.5896 | 0 | 0 | 1075725.0403 | 0 | 1075725.0403 | 0 | 0 | 4147.5801 | 0 | 0 | 0 | 2336.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9943 | 0 | 0 | 7345.0506 | 0 | 7345.0506 | 0 | 0 | 607.437 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.0976 | 0 | 0 | 1075.725 | 0 | 1075.725 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.2132 | 1.705 | 0 | 0 | 14.5449 | 14.5449 | 0
MT_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 16915.914 | 90853.5734 | 10700.2603 | 53987.5506 | 0 | 48491.5457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220948.844 | 0 | 220948.844 | 0 | 0 | 0 | 1789.7037 | 9612.3081 | 1132.0875 | 5711.8829 | 0 | 5130.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23376.3877 | 0 | 23376.3877 | 0 | 0 | 0 | 57.7171 | 309.9924 | 36.5093 | 184.2055 | 0 | 165.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.8775 | 0 | 753.8775 | 0 | 0 | 12.5544 | 1.4786 | 7.4601 | 6.7007 | 0 | 0 | 2.3375 | 0 | 0 | 0 | 0 | 30.5312 | 30.5312 | 0
MT_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 460980.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92886.0778 | 0 | 0 | 553866.4122 | 0 | 553866.4122 | 0 | 0 | 3147.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634.2261 | 0 | 0 | 3781.7999 | 0 | 3781.7999 | 0 | 0 | 460.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8861 | 0 | 0 | 553.8664 | 0 | 553.8664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6692 | 3.7618 | 0 | 0 | 22.431 | 22.431 | 0
MT_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 0 | 15896.18 | 75271.3714 | 10700.2603 | 53987.5506 | 0 | 46338.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202193.5189 | 0 | 202192.9632 | 0.55571 | 0.55571 | 0 | 1681.8158 | 7963.7111 | 1132.0875 | 5711.8829 | 0 | 4902.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21392.0743 | 0 | 21392.0155 | 0.058794 | 0.058794 | 0 | 54.2378 | 256.8259 | 36.5093 | 184.2055 | 0 | 158.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689.8843 | 0 | 689.8824 | 0.0018961 | 0.0018961 | 10.4012 | 1.4786 | 7.4601 | 6.4031 | 0 | 0 | 2.1966 | 0 | 0 | 0 | 0 | 27.9395 | 27.9396 | 7.679e-05
MT_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 493841.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92895.5559 | 0 | 0 | 586736.71 | 0 | 586736.71 | 0 | 0 | 3371.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634.2909 | 0 | 0 | 4006.2383 | 0 | 4006.2383 | 0 | 0 | 493.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8956 | 0 | 0 | 586.7367 | 0 | 586.7367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3.7622 | 0 | 0 | 23.7622 | 23.7622 | 0
MT_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 30361.3981 | 50472.6638 | 79344.7502 | 12297.9361 | 154949.5496 | 0 | 52248.1679 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 379746.7085 | 0 | 379746.9863 | -0.27786 | -0.27786 | 3212.2359 | 5340.0078 | 8394.6746 | 1301.1216 | 16393.6623 | 0 | 5527.8562 | 7.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 40177.2018 | 0 | 40177.2312 | -0.029397 | -0.029397 | 103.5931 | 172.2127 | 270.7243 | 41.9606 | 528.6879 | 0 | 178.2707 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.6958 | 0 | 1295.6967 | -0.00094805 | -0.00094805 | 6.2665 | 0.97126 | 12.2376 | 4.1264 | 0.0057056 | 0 | 3.9862 | 2.3979 | 0 | 0 | 0 | 29.9916 | 29.9916 | -2.1945e-05
MT_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 66555.7182 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 638174.7451 | 0 | 0 | 1104225.9011 | 0 | 1104225.9011 | 0 | 0 | 454.4424 | 0 | 0 | 0 | 2727.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 4357.4572 | 0 | 0 | 7539.6545 | 0 | 7539.6545 | 0 | 0 | 66.5557 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 638.1747 | 0 | 0 | 1104.2259 | 0 | 1104.2259 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5406 | 14.7719 | 0 | 0 | 25.5596 | 25.5596 | 0
MT_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 35354.4825 | 46188.114 | 50983.9201 | 12297.9361 | 154949.5496 | 0 | 49225.0873 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 349071.3323 | 0 | 349070.7766 | 0.55571 | 0.55571 | 3740.5042 | 4886.7025 | 5394.0987 | 1301.1216 | 16393.6623 | 0 | 5208.0142 | 7.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 36931.747 | 0 | 36931.6882 | 0.058794 | 0.058794 | 120.6295 | 157.5938 | 173.9571 | 41.9606 | 528.6879 | 0 | 167.956 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1191.0314 | 0 | 1191.0295 | 0.0018961 | 0.0018961 | 4.0266 | 0.97126 | 12.2376 | 3.8877 | 0.0057056 | 0 | 3.6478 | 2.7922 | 0 | 0 | 0 | 27.5689 | 27.5689 | 4.3889e-05
MT_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 66783.1943 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 638260.0486 | 0 | 0 | 1104538.6808 | 0 | 1104538.6808 | 0 | 0 | 455.9957 | 0 | 0 | 0 | 2727.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 4358.0396 | 0 | 0 | 7541.7901 | 0 | 7541.7901 | 0 | 0 | 66.7832 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 638.26 | 0 | 0 | 1104.5387 | 0 | 1104.5387 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5458 | 14.7739 | 0 | 0 | 25.5668 | 25.5668 | 0
MT_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 4101.1644 | 2434.0244 | 8846.9563 | 1606.0115 | 13417.6985 | 0 | 5562.6905 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40972.7443 | 0 | 40970.5214 | 2.2229 | 2.2229 | 433.9032 | 257.5198 | 936.008 | 169.916 | 1419.5925 | 0 | 588.5327 | 0 | 0 | 0 | 0 | 529.4442 | 0 | 0 | 4334.9163 | 0 | 4334.6812 | 0.23518 | 0.23518 | 13.9932 | 8.3049 | 30.1858 | 5.4797 | 45.7812 | 0 | 18.9799 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.799 | 0 | 139.7914 | 0.0075844 | 0.0075844 | 5.4863 | 0.99595 | 8.3208 | 3.4496 | 0 | 0 | 1.5094 | 2.5433 | 3.1033 | 0 | 0 | 25.4074 | 25.4088 | 0.0013785
MT_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 10814.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10814.5933 | 0 | 10814.5933 | 0 | 0 | 73.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.842 | 0 | 73.842 | 0 | 0 | 10.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8146 | 0 | 10.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9656 | 0 | 0 | 0 | 1.9656 | 1.9656 | 0
MT_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Electricity | 4223.4214 | 2183.9534 | 7152.0306 | 1606.0115 | 13417.6985 | 0 | 5018.0914 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38605.4055 | 0 | 38604.2941 | 1.1114 | 1.1114 | 446.838 | 231.0623 | 756.6848 | 169.916 | 1419.5925 | 0 | 530.9141 | 0 | 0 | 0 | 0 | 529.4442 | 0 | 0 | 4084.4519 | 0 | 4084.3343 | 0.11759 | 0.11759 | 14.4103 | 7.4516 | 24.4027 | 5.4797 | 45.7812 | 0 | 17.1217 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.7216 | 0 | 131.7179 | 0.0037922 | 0.0037922 | 4.4352 | 0.99595 | 8.3208 | 3.1119 | 0 | 0 | 1.3544 | 2.6191 | 3.1033 | 0 | 0 | 23.94 | 23.9407 | 0.00068924
MT_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | MT-HELENA-MT | Zone6B | Zone6B(MT-HELENA-MT) |  |  | MT | 0.1058 | 0.006828 |  |  |  | Natural Gas | 11790.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11790.845 | 0 | 11790.845 | 0 | 0 | 80.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5079 | 0 | 80.5079 | 0 | 0 | 11.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7908 | 0 | 11.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.143 | 0 | 0 | 0 | 2.143 | 2.143 | 0
NC_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 830307.9674 | 882250.493 | 95485.444 | 4077910.5986 | 543459.8574 | 572537.5577 | 115844.0021 | 313666.8356 | 287598.323 | 11217.0737 | 0 | 0 | 0 | 7730278.1527 | 0 | 7730272.5956 | 5.5571 | 543465.4145 | 0 | 72818.0087 | 77373.3682 | 8374.0734 | 357632.7595 | 47661.4295 | 50211.5438 | 10159.519 | 27508.5815 | 25222.3729 | 983.7374 | 0 | 0 | 0 | 677945.394 | 0 | 677944.9066 | 0.48736 | 47661.9169 | 0 | 2833.0108 | 3010.2387 | 325.7963 | 13913.831 | 1854.285 | 1953.4981 | 395.2597 | 1070.2312 | 981.2855 | 38.2727 | 0 | 0 | 0 | 26375.7091 | 0 | 26375.6901 | 0.018961 | 1854.304 | 6.0375 | 0.65344 | 27.9065 | 3.9181 | 0.79276 | 0.076762 | 5.6821 | 0 | 0 | 1.9681 | 0 | 52.9008 | 52.9008 | 3.8029e-05
NC_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 615237.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508475.4504 | 0 | 0 | 1123713.0211 | 0 | 1123713.0211 | 0 | 0 | 5414.0906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4474.584 | 0 | 0 | 9888.6746 | 0 | 9888.6746 | 0 | 0 | 615.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508.4755 | 0 | 0 | 1123.713 | 0 | 1123.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.234 | 1.0198 | 0 | 0 | 2.2538 | 2.2538 | 0
NC_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 770363.1698 | 717309.2176 | 95485.444 | 4077910.5986 | 543387.6147 | 562529.1605 | 106788.6533 | 282749.7242 | 287612.2159 | 11642.1944 | 0 | 0 | 0 | 7455777.993 | 0 | 7455774.6588 | 3.3343 | 543390.949 | 0 | 67560.85 | 62908.0184 | 8374.0734 | 357632.7595 | 47655.0938 | 49333.8074 | 9365.3649 | 24797.1508 | 25223.5913 | 1021.0204 | 0 | 0 | 0 | 653871.73 | 0 | 653871.4376 | 0.29242 | 47655.3862 | 0 | 2628.4791 | 2447.4591 | 325.7963 | 13913.831 | 1854.0385 | 1919.3495 | 364.3629 | 964.7421 | 981.3329 | 39.7232 | 0 | 0 | 0 | 25439.1145 | 0 | 25439.1031 | 0.011377 | 1854.0499 | 4.9088 | 0.65344 | 27.9065 | 3.8496 | 0.73079 | 0.079671 | 5.2718 | 0 | 0 | 1.9682 | 0 | 51.0223 | 51.0223 | 2.2818e-05
NC_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 334418.3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508428.0595 | 0 | 0 | 842846.374 | 0 | 842846.374 | 0 | 0 | 2942.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4474.1669 | 0 | 0 | 7417.0481 | 0 | 7417.0481 | 0 | 0 | 334.4183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508.4281 | 0 | 0 | 842.8464 | 0 | 842.8464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67073 | 1.0197 | 0 | 0 | 1.6905 | 1.6905 | 0
NC_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 37127.208 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 21984.0196 | 0 | 0 | 0 | 0 | 102220.6897 | 0 | 0 | 338921.2282 | 0 | 338921.5061 | -0.27786 | -0.27786 | 0 | 3256.0561 | 2488.4632 | 632.3504 | 12453.769 | 0 | 1927.9985 | 0 | 0 | 0 | 0 | 8964.7545 | 0 | 0 | 29723.3917 | 0 | 29723.4161 | -0.024368 | -0.024368 | 0 | 126.678 | 96.8146 | 24.6018 | 484.5184 | 0 | 75.0095 | 0 | 0 | 0 | 0 | 348.777 | 0 | 0 | 1156.3992 | 0 | 1156.4002 | -0.00094805 | -0.00094805 | 2.8693 | 0.72914 | 14.3599 | 2.2231 | 0 | 0 | 3.7544 | 0 | 10.3369 | 0 | 0 | 34.2728 | 34.2728 | -2.8098e-05
NC_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 100440.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100440.1802 | 0 | 100440.1802 | 0 | 0 | 883.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883.8736 | 0 | 883.8736 | 0 | 0 | 100.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4402 | 0 | 100.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9768 | 0 | 0 | 0 | 2.9768 | 2.9768 | 0
NC_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 36276.9666 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21450.5348 | 0 | 0 | 0 | 0 | 102067.8685 | 0 | 0 | 332191.5397 | 0 | 332191.8176 | -0.27786 | -0.27786 | 0 | 3181.49 | 2033.0247 | 632.3504 | 12453.769 | 0 | 1881.2119 | 0 | 0 | 0 | 0 | 8951.3521 | 0 | 0 | 29133.198 | 0 | 29133.2224 | -0.024368 | -0.024368 | 0 | 123.777 | 79.0956 | 24.6018 | 484.5184 | 0 | 73.1892 | 0 | 0 | 0 | 0 | 348.2556 | 0 | 0 | 1133.4375 | 0 | 1133.4385 | -0.00094805 | -0.00094805 | 2.3442 | 0.72914 | 14.3599 | 2.1691 | 0 | 0 | 3.6684 | 0 | 10.3214 | 0 | 0 | 33.5923 | 33.5923 | -2.8098e-05
NC_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 27723.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27723.6508 | 0 | 27723.6508 | 0 | 0 | 243.9681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.9681 | 0 | 243.9681 | 0 | 0 | 27.7237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7237 | 0 | 27.7237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82166 | 0 | 0 | 0 | 0.82166 | 0.82166 | 0
NC_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 148678.3246 | 100245.1288 | 7113.1307 | 317887.4784 | 4818.0346 | 90042.2319 | 430.6778 | 0 | 0 | 24759.8077 | 7179.8163 | 17646.677 | 0 | 718801.3079 | 0 | 718802.6972 | -1.3893 | 4816.6453 | 0 | 13039.0891 | 8791.4978 | 623.8216 | 27878.7319 | 422.5416 | 7896.7037 | 37.7704 | 0 | 0 | 2171.4351 | 629.6699 | 1547.6136 | 0 | 63038.8747 | 0 | 63038.9965 | -0.12184 | 422.4198 | 0 | 507.2904 | 342.0364 | 24.27 | 1084.6321 | 16.4391 | 307.2241 | 1.4695 | 0 | 0 | 84.4805 | 24.4975 | 60.2105 | 0 | 2452.5501 | 0 | 2452.5548 | -0.0047402 | 16.4344 | 4.6247 | 0.32815 | 14.6653 | 4.154 | 0.019869 | 1.1423 | 6.8591 | 0 | 0.33123 | 0 | 0.81411 | 33.161 | 33.1609 | -6.4093e-05
NC_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 268071.116 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 106989.5965 | 0 | 0 | 717251.1274 | 0 | 717251.1274 | 0 | 0 | 2359.0258 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 941.5084 | 0 | 0 | 6311.8099 | 0 | 6311.8099 | 0 | 0 | 268.0711 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9896 | 0 | 0 | 717.2511 | 0 | 717.2511 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.6246 | 1.4466 | 0 | 0 | 9.698 | 9.698 | 0
NC_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 136791.6163 | 80642.3408 | 7113.1307 | 312483.1662 | 4745.7919 | 79266.9503 | 338.9851 | 0 | 0 | 22767.5754 | 7179.8163 | 12503.5501 | 0 | 663832.9232 | 0 | 663835.7018 | -2.7786 | 4743.0133 | 0 | 11996.6248 | 7072.3333 | 623.8216 | 27404.7737 | 416.2059 | 6951.7115 | 29.729 | 0 | 0 | 1996.7164 | 629.6699 | 1096.5613 | 0 | 58218.1474 | 0 | 58218.391 | -0.24368 | 415.9623 | 0 | 466.733 | 275.1517 | 24.27 | 1066.1926 | 16.1926 | 270.4588 | 1.1566 | 0 | 0 | 77.683 | 24.4975 | 42.6621 | 0 | 2264.9979 | 0 | 2265.0074 | -0.0094805 | 16.1832 | 3.7203 | 0.32815 | 14.416 | 3.6569 | 0.015639 | 1.0504 | 6.3107 | 0 | 0.33123 | 0 | 0.57683 | 30.6252 | 30.625 | -0.00012819
NC_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 228547.1421 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 106695.7732 | 0 | 0 | 677433.3302 | 0 | 677433.3302 | 0 | 0 | 2011.2149 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 938.9228 | 0 | 0 | 5961.4133 | 0 | 5961.4133 | 0 | 0 | 228.5471 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6958 | 0 | 0 | 677.4333 | 0 | 677.4333 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.0902 | 1.4426 | 0 | 0 | 9.1596 | 9.1596 | 0
NC_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 55871.4188 | 83040.2439 | 10686.3675 | 53987.5506 | 0 | 40003.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243588.6053 | 0 | 243586.1046 | 2.5007 | 2.5007 | 0 | 4899.9234 | 7282.6294 | 937.1944 | 4734.7082 | 0 | 3508.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21362.7207 | 0 | 21362.5014 | 0.21931 | 0.21931 | 0 | 190.6333 | 283.3333 | 36.4619 | 184.2055 | 0 | 136.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831.1243 | 0 | 831.1158 | 0.0085324 | 0.0085324 | 11.4747 | 1.4767 | 7.4601 | 5.5277 | 0 | 0 | 7.7204 | 0 | 0 | 0 | 0 | 33.6593 | 33.6597 | 0.00034555
NC_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 154588.9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86962.2208 | 0 | 0 | 241551.193 | 0 | 241551.193 | 0 | 0 | 1360.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765.2675 | 0 | 0 | 2125.6505 | 0 | 2125.6505 | 0 | 0 | 154.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9622 | 0 | 0 | 241.5512 | 0 | 241.5512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2607 | 3.5219 | 0 | 0 | 9.7826 | 9.7826 | 0
NC_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 52439.889 | 65613.0736 | 10686.3675 | 53987.5506 | 0 | 38058.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220784.9086 | 0 | 220782.4079 | 2.5007 | 2.5007 | 0 | 4598.9783 | 5754.2666 | 937.1944 | 4734.7082 | 0 | 3337.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19362.8365 | 0 | 19362.6172 | 0.21931 | 0.21931 | 0 | 178.9249 | 223.8718 | 36.4619 | 184.2055 | 0 | 129.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.3181 | 0 | 753.3096 | 0.0085324 | 0.0085324 | 9.0666 | 1.4767 | 7.4601 | 5.2589 | 0 | 0 | 7.2463 | 0 | 0 | 0 | 0 | 30.5082 | 30.5086 | 0.00034555
NC_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 173260.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86971.6989 | 0 | 0 | 260232.6685 | 0 | 260232.6685 | 0 | 0 | 1524.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765.351 | 0 | 0 | 2290.0475 | 0 | 2290.0475 | 0 | 0 | 173.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9717 | 0 | 0 | 260.2327 | 0 | 260.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0169 | 3.5223 | 0 | 0 | 10.5391 | 10.5391 | 0
NC_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 9563.8265 | 91920.543 | 80178.3202 | 12317.3861 | 154949.5496 | 0 | 46099.1998 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 395101.068 | 0 | 395100.2344 | 0.83357 | 0.83357 | 838.7476 | 8061.4316 | 7031.6387 | 1080.2348 | 13589.0755 | 0 | 4042.8998 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 34650.3637 | 0 | 34650.2906 | 0.073104 | 0.073104 | 32.6318 | 313.6329 | 273.5684 | 42.0269 | 528.6879 | 0 | 157.2905 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.0848 | 0 | 1348.082 | 0.0028441 | 0.0028441 | 6.3323 | 0.9728 | 12.2376 | 3.6408 | 0.0057056 | 0 | 7.2597 | 0.75533 | 0 | 0 | 0 | 31.2042 | 31.2042 | 6.5834e-05
NC_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 24121.9457 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 523943.8258 | 0 | 0 | 947561.2094 | 0 | 947561.2094 | 0 | 0 | 212.2731 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 4610.7057 | 0 | 0 | 8338.5386 | 0 | 8338.5386 | 0 | 0 | 24.1219 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 523.9438 | 0 | 0 | 947.5612 | 0 | 947.5612 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.55835 | 12.1278 | 0 | 0 | 21.9333 | 21.9333 | 0
NC_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 11250.4165 | 86352.2954 | 51361.8051 | 12317.3861 | 154949.5496 | 0 | 43712.411 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360016.1065 | 0 | 360012.7722 | 3.3343 | 3.3343 | 986.6615 | 7573.0963 | 4504.4303 | 1080.2348 | 13589.0755 | 0 | 3833.5784 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 31573.4125 | 0 | 31573.1201 | 0.29242 | 0.29242 | 38.3864 | 294.634 | 175.2465 | 42.0269 | 528.6879 | 0 | 149.1467 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.375 | 0 | 1228.3636 | 0.011377 | 0.011377 | 4.0564 | 0.9728 | 12.2376 | 3.4523 | 0.0057056 | 0 | 6.8199 | 0.88853 | 0 | 0 | 0 | 28.433 | 28.4333 | 0.00026333
NC_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 25809.0602 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 524019.6511 | 0 | 0 | 949324.1492 | 0 | 949324.1492 | 0 | 0 | 227.1197 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 4611.3729 | 0 | 0 | 8354.0525 | 0 | 8354.0525 | 0 | 0 | 25.8091 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 524.0197 | 0 | 0 | 949.3241 | 0 | 949.3241 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.5974 | 12.1295 | 0 | 0 | 21.9741 | 21.9741 | 0
NC_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 1519.876 | 5546.0191 | 9016.4489 | 1583.783 | 13417.6985 | 0 | 5043.0985 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41131.1226 | 0 | 41129.7333 | 1.3893 | 1.3893 | 133.2931 | 486.3859 | 790.7426 | 138.8978 | 1176.7322 | 0 | 442.2797 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3607.1995 | 0 | 3607.0776 | 0.12184 | 0.12184 | 5.1858 | 18.923 | 30.7641 | 5.4039 | 45.7812 | 0 | 17.2071 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.3394 | 0 | 140.3347 | 0.0047402 | 0.0047402 | 5.5914 | 0.98216 | 8.3208 | 3.1274 | 0 | 0 | 3.4393 | 0.94253 | 3.1033 | 0 | 0 | 25.5061 | 25.507 | 0.00086155
NC_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 1146.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.8587 | 0 | 1146.8587 | 0 | 0 | 10.0924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0924 | 0 | 10.0924 | 0 | 0 | 1.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1469 | 0 | 1.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20844 | 0 | 0 | 0 | 0.20844 | 0.20844 | 0
NC_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 1555.9973 | 5262.6053 | 7240.9448 | 1583.783 | 13417.6985 | 0 | 4637.4278 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38702.6553 | 0 | 38700.9882 | 1.6671 | 1.6671 | 136.461 | 461.5305 | 635.0309 | 138.8978 | 1176.7322 | 0 | 406.7024 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3394.2229 | 0 | 3394.0767 | 0.14621 | 0.14621 | 5.3091 | 17.956 | 24.7061 | 5.4039 | 45.7812 | 0 | 15.8229 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.0535 | 0 | 132.0478 | 0.0056883 | 0.0056883 | 4.4904 | 0.98216 | 8.3208 | 2.8758 | 0 | 0 | 3.2635 | 0.96493 | 3.1033 | 0 | 0 | 24 | 24.001 | 0.0010339
NC_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | NC-CHARLOTTE-NC | Zone3A | Zone3A(NC-CHARLOTTE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 1251.1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.1186 | 0 | 1251.1186 | 0 | 0 | 11.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0098 | 0 | 11.0098 | 0 | 0 | 1.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2511 | 0 | 1.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22739 | 0 | 0 | 0 | 0.22739 | 0.22739 | 0
NC_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 674327.5696 | 879180.1768 | 95710.5079 | 4077910.5986 | 543457.0788 | 623635.399 | 94021.1394 | 246795.0713 | 316314.8097 | 12286.8219 | 0 | 0 | 0 | 7563639.1731 | 0 | 7563637.7838 | 1.3893 | 543458.4681 | 0 | 59138.5279 | 77104.1015 | 8393.8115 | 357632.7595 | 47661.1858 | 54692.8245 | 8245.6539 | 21643.9278 | 27740.8088 | 1077.5543 | 0 | 0 | 0 | 663331.1555 | 0 | 663331.0336 | 0.12184 | 47661.3077 | 0 | 2300.8057 | 2999.7628 | 326.5643 | 13913.831 | 1854.2756 | 2127.844 | 320.8001 | 842.0648 | 1079.2661 | 41.9226 | 0 | 0 | 0 | 25807.1369 | 0 | 25807.1321 | 0.0047402 | 1854.2803 | 6.0165 | 0.65498 | 27.9065 | 4.2677 | 0.64342 | 0.084083 | 4.6146 | 0 | 0 | 2.1646 | 0 | 51.7604 | 51.7604 | 9.5073e-06
NC_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 435891.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543980.6797 | 0 | 0 | 979872.295 | 0 | 979872.295 | 0 | 0 | 3835.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4787.03 | 0 | 0 | 8622.8762 | 0 | 8622.8762 | 0 | 0 | 435.8916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543.9807 | 0 | 0 | 979.8723 | 0 | 979.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87425 | 1.091 | 0 | 0 | 1.9653 | 1.9653 | 0
NC_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 636364.013 | 715742.106 | 95710.5079 | 4077910.5986 | 543384.8361 | 599542.4473 | 91181.4442 | 222129.7349 | 316100.8601 | 11255.9736 | 0 | 0 | 0 | 7309322.5218 | 0 | 7309321.6882 | 0.83357 | 543385.6697 | 0 | 55809.1239 | 62770.5827 | 8393.8115 | 357632.7595 | 47654.8501 | 52579.8726 | 7996.6127 | 19480.7777 | 27722.0454 | 987.1489 | 0 | 0 | 0 | 641027.5852 | 0 | 641027.5121 | 0.073104 | 47654.9232 | 0 | 2171.274 | 2442.1121 | 326.5643 | 13913.831 | 1854.0291 | 2045.6388 | 311.1111 | 757.9067 | 1078.5361 | 38.4054 | 0 | 0 | 0 | 24939.4084 | 0 | 24939.4056 | 0.0028441 | 1854.0319 | 4.8981 | 0.65498 | 27.9065 | 4.1029 | 0.62398 | 0.077028 | 4.3548 | 0 | 0 | 2.1632 | 0 | 50.0201 | 50.0201 | 5.7044e-06
NC_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 396528.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544065.9832 | 0 | 0 | 940594.7535 | 0 | 940594.7535 | 0 | 0 | 3489.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4787.7807 | 0 | 0 | 8277.2338 | 0 | 8277.2338 | 0 | 0 | 396.5288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.066 | 0 | 0 | 940.5948 | 0 | 940.5948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7953 | 1.0912 | 0 | 0 | 1.8865 | 1.8865 | 0
NC_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 29666.7565 | 28374.723 | 7207.602 | 142004.2074 | 0 | 21417.192 | 0 | 0 | 0 | 0 | 109067.078 | 0 | 0 | 337737.5588 | 0 | 337737.0031 | 0.55571 | 0.55571 | 0 | 2601.7745 | 2488.4632 | 632.1067 | 12453.769 | 0 | 1878.2877 | 0 | 0 | 0 | 0 | 9565.1827 | 0 | 0 | 29619.5839 | 0 | 29619.5352 | 0.048736 | 0.048736 | 0 | 101.223 | 96.8146 | 24.5923 | 484.5184 | 0 | 73.0755 | 0 | 0 | 0 | 0 | 372.1369 | 0 | 0 | 1152.3606 | 0 | 1152.3587 | 0.0018961 | 0.0018961 | 2.8693 | 0.72886 | 14.3599 | 2.1658 | 0 | 0 | 3 | 0 | 11.0292 | 0 | 0 | 34.1531 | 34.1531 | 5.6196e-05
NC_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 40500.2255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40500.2255 | 0 | 40500.2255 | 0 | 0 | 356.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.402 | 0 | 356.402 | 0 | 0 | 40.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.5002 | 0 | 40.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2003 | 0 | 0 | 0 | 1.2003 | 1.2003 | 0
NC_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 28385.8372 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 20619.7433 | 0 | 0 | 0 | 0 | 109100.4208 | 0 | 0 | 330499.3926 | 0 | 330499.3926 | 0 | 0 | 0 | 2489.4379 | 2033.0247 | 632.1067 | 12453.769 | 0 | 1808.3515 | 0 | 0 | 0 | 0 | 9568.1069 | 0 | 0 | 28984.7967 | 0 | 28984.7967 | 0 | 0 | 0 | 96.8525 | 79.0956 | 24.5923 | 484.5184 | 0 | 70.3546 | 0 | 0 | 0 | 0 | 372.2506 | 0 | 0 | 1127.6639 | 0 | 1127.6639 | 0 | 0 | 2.3442 | 0.72886 | 14.3599 | 2.0851 | 0 | 0 | 2.8705 | 0 | 11.0326 | 0 | 0 | 33.4212 | 33.4212 | 0
NC_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 48670.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48670.4091 | 0 | 48670.4091 | 0 | 0 | 428.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.2996 | 0 | 428.2996 | 0 | 0 | 48.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.6704 | 0 | 48.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4425 | 0 | 0 | 0 | 1.4425 | 1.4425 | 0
NC_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 114618.6542 | 96302.3426 | 7115.9093 | 317887.4784 | 4818.0346 | 90361.7671 | 416.785 | 0 | 0 | 19661.1378 | 7179.8163 | 17630.0056 | 0 | 675991.931 | 0 | 675991.6532 | 0.27786 | 4818.3125 | 0 | 10052.056 | 8445.7154 | 624.0652 | 27878.7319 | 422.5416 | 7924.727 | 36.552 | 0 | 0 | 1724.2818 | 629.6699 | 1546.1515 | 0 | 59284.4924 | 0 | 59284.468 | 0.024368 | 422.566 | 0 | 391.0788 | 328.5836 | 24.2795 | 1084.6321 | 16.4391 | 308.3143 | 1.4221 | 0 | 0 | 67.0838 | 24.4975 | 60.1536 | 0 | 2306.4845 | 0 | 2306.4835 | 0.00094805 | 16.4401 | 4.4428 | 0.32828 | 14.6653 | 4.1687 | 0.019228 | 0.90704 | 5.2878 | 0 | 0.33123 | 0 | 0.81334 | 31.186 | 31.186 | 1.2819e-05
NC_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 173583.2274 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113539.0128 | 0 | 0 | 629312.655 | 0 | 629312.655 | 0 | 0 | 1527.5324 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 999.1433 | 0 | 0 | 5537.9514 | 0 | 5537.9514 | 0 | 0 | 173.5832 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.539 | 0 | 0 | 629.3127 | 0 | 629.3127 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.347 | 1.5352 | 0 | 0 | 8.5089 | 8.5089 | 0
NC_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 108666.9644 | 78055.4952 | 7115.9093 | 312483.1662 | 4743.0133 | 79100.2363 | 230.621 | 0 | 0 | 22592.5257 | 7179.8163 | 12497.9929 | 0 | 632665.7407 | 0 | 632667.6857 | -1.945 | 4741.0683 | 0 | 9530.0928 | 6845.4669 | 624.0652 | 27404.7737 | 415.9623 | 6937.0907 | 20.2255 | 0 | 0 | 1981.3645 | 629.6699 | 1096.074 | 0 | 55484.7855 | 0 | 55484.956 | -0.17058 | 415.7917 | 0 | 370.7717 | 266.3253 | 24.2795 | 1066.1926 | 16.1832 | 269.89 | 0.78688 | 0 | 0 | 77.0857 | 24.4975 | 42.6432 | 0 | 2158.6555 | 0 | 2158.6621 | -0.0066363 | 16.1765 | 3.601 | 0.32828 | 14.416 | 3.6492 | 0.010639 | 1.0423 | 5.0132 | 0 | 0.33123 | 0 | 0.57658 | 29.1873 | 29.1872 | -8.973e-05
NC_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 162673.8523 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113339.9712 | 0 | 0 | 618204.2383 | 0 | 618204.2383 | 0 | 0 | 1431.5299 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 997.3917 | 0 | 0 | 5440.1973 | 0 | 5440.1973 | 0 | 0 | 162.6739 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.34 | 0 | 0 | 618.2042 | 0 | 618.2042 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.1995 | 1.5325 | 0 | 0 | 8.3587 | 8.3587 | 0
NC_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 39605.6895 | 83862.6996 | 10678.0318 | 53987.5506 | 0 | 41503.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229637.422 | 0 | 229638.8113 | -1.3893 | -1.3893 | 0 | 3473.419 | 7354.7588 | 936.4634 | 4734.7082 | 0 | 3639.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20139.2019 | 0 | 20139.3238 | -0.12184 | -0.12184 | 0 | 135.1346 | 286.1395 | 36.4334 | 184.2055 | 0 | 141.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783.5229 | 0 | 783.5276 | -0.0047402 | -0.0047402 | 11.5883 | 1.4755 | 7.4601 | 5.735 | 0 | 0 | 5.4728 | 0 | 0 | 0 | 0 | 31.732 | 31.7319 | -0.00019197
NC_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 200700.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89085.3311 | 0 | 0 | 289785.6063 | 0 | 289785.6063 | 0 | 0 | 1766.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783.9509 | 0 | 0 | 2550.1133 | 0 | 2550.1133 | 0 | 0 | 200.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0853 | 0 | 0 | 289.7856 | 0 | 289.7856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1281 | 3.6079 | 0 | 0 | 11.736 | 11.736 | 0
NC_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 36854.9085 | 66218.8012 | 10678.0318 | 53987.5506 | 0 | 39380.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207119.9176 | 0 | 207117.9726 | 1.945 | 1.945 | 0 | 3232.1755 | 5807.3889 | 936.4634 | 4734.7082 | 0 | 3453.6809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18164.4168 | 0 | 18164.2462 | 0.17058 | 0.17058 | 0 | 125.7489 | 225.9385 | 36.4334 | 184.2055 | 0 | 134.3667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706.6932 | 0 | 706.6865 | 0.0066363 | 0.0066363 | 9.1503 | 1.4755 | 7.4601 | 5.4417 | 0 | 0 | 5.0927 | 0 | 0 | 0 | 0 | 28.6201 | 28.6203 | 0.00026876
NC_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 222301.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89094.8093 | 0 | 0 | 311395.8366 | 0 | 311395.8366 | 0 | 0 | 1956.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784.0343 | 0 | 0 | 2740.2834 | 0 | 2740.2834 | 0 | 0 | 222.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0948 | 0 | 0 | 311.3958 | 0 | 311.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.003 | 3.6082 | 0 | 0 | 12.6112 | 12.6112 | 0
NC_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 13917.8405 | 77302.5037 | 79225.2718 | 12311.829 | 154949.5496 | 0 | 46268.6924 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 384047.9297 | 0 | 384047.0961 | 0.83357 | 0.83357 | 1220.5946 | 6779.4296 | 6948.0563 | 1079.7474 | 13589.0755 | 0 | 4057.7643 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 33681.0034 | 0 | 33680.9303 | 0.073104 | 0.073104 | 47.4877 | 263.7561 | 270.3166 | 42.008 | 528.6879 | 0 | 157.8688 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.3715 | 0 | 1310.3687 | 0.0028441 | 0.0028441 | 6.257 | 0.97236 | 12.2376 | 3.6542 | 0.0057056 | 0 | 6.1052 | 1.0992 | 0 | 0 | 0 | 30.3312 | 30.3313 | 6.5834e-05
NC_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 35609.4892 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 564889.5253 | 0 | 0 | 999994.4525 | 0 | 999994.4525 | 0 | 0 | 313.3635 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 4971.0278 | 0 | 0 | 8799.9512 | 0 | 8799.9512 | 0 | 0 | 35.6095 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 564.8895 | 0 | 0 | 999.9945 | 0 | 999.9945 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.82426 | 13.0755 | 0 | 0 | 23.1469 | 23.1469 | 0
NC_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 16632.5002 | 72023.227 | 50797.7561 | 12311.829 | 154949.5496 | 0 | 43845.7822 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 350632.8868 | 0 | 350632.3311 | 0.55571 | 0.55571 | 1458.6703 | 6316.437 | 4454.9632 | 1079.7474 | 13589.0755 | 0 | 3845.2751 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 30750.5042 | 0 | 30750.4554 | 0.048736 | 0.048736 | 56.7501 | 245.7433 | 173.3219 | 42.008 | 528.6879 | 0 | 149.6018 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.3594 | 0 | 1196.3575 | 0.0018961 | 0.0018961 | 4.0119 | 0.97236 | 12.2376 | 3.4628 | 0.0057056 | 0 | 5.6882 | 1.3136 | 0 | 0 | 0 | 27.6922 | 27.6922 | 4.3889e-05
NC_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 37163.9093 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 564946.3944 | 0 | 0 | 1001605.7416 | 0 | 1001605.7416 | 0 | 0 | 327.0424 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 4971.5283 | 0 | 0 | 8814.1305 | 0 | 8814.1305 | 0 | 0 | 37.1639 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 564.9464 | 0 | 0 | 1001.6057 | 0 | 1001.6057 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.86024 | 13.0769 | 0 | 0 | 23.1842 | 23.1842 | 0
NC_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 1722.7113 | 4331.7855 | 8833.0635 | 1586.5616 | 13417.6985 | 0 | 4951.4058 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39847.4248 | 0 | 39848.2584 | -0.83357 | -0.83357 | 151.0818 | 379.8976 | 774.6597 | 139.1415 | 1176.7322 | 0 | 434.2383 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3494.6192 | 0 | 3494.6923 | -0.073104 | -0.073104 | 5.8779 | 14.7801 | 30.1384 | 5.4133 | 45.7812 | 0 | 16.8942 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.9594 | 0 | 135.9623 | -0.0028441 | -0.0028441 | 5.4777 | 0.98389 | 8.3208 | 3.0706 | 0 | 0 | 2.6863 | 1.0683 | 3.1033 | 0 | 0 | 24.7114 | 24.7109 | -0.00051693
NC_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 1213.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.2059 | 0 | 1213.2059 | 0 | 0 | 10.6762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6762 | 0 | 10.6762 | 0 | 0 | 1.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2132 | 0 | 1.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2205 | 0 | 0 | 0 | 0.2205 | 0.2205 | 0
NC_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 1775.5041 | 4076.1573 | 7113.1307 | 1586.5616 | 13417.6985 | 0 | 4542.9565 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37516.2073 | 0 | 37518.4302 | -2.2229 | -2.2229 | 155.7117 | 357.479 | 623.8216 | 139.1415 | 1176.7322 | 0 | 398.4173 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3290.1714 | 0 | 3290.3663 | -0.19494 | -0.19494 | 6.058 | 13.9078 | 24.27 | 5.4133 | 45.7812 | 0 | 15.5006 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.0053 | 0 | 128.0129 | -0.0075844 | -0.0075844 | 4.4111 | 0.98389 | 8.3208 | 2.8173 | 0 | 0 | 2.5278 | 1.1011 | 3.1033 | 0 | 0 | 23.2666 | 23.2652 | -0.0013785
NC_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | NC-ASHEVILLE-NC | Zone4A | Zone4A(NC-ASHEVILLE-NC) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 1345.9003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.9003 | 0 | 1345.9003 | 0 | 0 | 11.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8439 | 0 | 11.8439 | 0 | 0 | 1.3459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3459 | 0 | 1.3459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24462 | 0 | 0 | 0 | 0.24462 | 0.24462 | 0
NC_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 563840.644 | 880094.3252 | 95513.2297 | 4077910.5986 | 543457.0788 | 609756.4584 | 82692.923 | 189870.5757 | 380669.1926 | 9524.9266 | 0 | 0 | 0 | 7433329.9528 | 0 | 7433329.9528 | 0 | 543457.0788 | 0 | 49448.8245 | 77184.2723 | 8376.5102 | 357632.7595 | 47661.1858 | 53475.6414 | 7252.1694 | 16651.6495 | 33384.6882 | 835.3361 | 0 | 0 | 0 | 651903.0369 | 0 | 651903.0369 | 0 | 47661.1858 | 0 | 1923.8243 | 3002.8818 | 325.8911 | 13913.831 | 1854.2756 | 2080.489 | 282.1483 | 647.8384 | 1298.8433 | 32.499 | 0 | 0 | 0 | 25362.5218 | 0 | 25362.5218 | 0 | 1854.2756 | 6.0228 | 0.65363 | 27.9065 | 4.1728 | 0.56589 | 0.065182 | 3.8585 | 0 | 0 | 2.605 | 0 | 50.8687 | 50.8687 | 0
NC_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 799227.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579068.8695 | 0 | 0 | 1378296.6996 | 0 | 1378296.6996 | 0 | 0 | 7033.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5095.8061 | 0 | 0 | 12129.011 | 0 | 12129.011 | 0 | 0 | 799.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0689 | 0 | 0 | 1378.2967 | 0 | 1378.2967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.603 | 1.1614 | 0 | 0 | 2.7644 | 2.7644 | 0
NC_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 529408.6457 | 716478.4262 | 95513.2297 | 4077910.5986 | 543384.8361 | 594107.5709 | 79116.9077 | 170270.5663 | 380402.4502 | 9110.9202 | 0 | 0 | 0 | 7195704.1516 | 0 | 7195710.5423 | -6.3907 | 543378.4454 | 0 | 46429.1382 | 62835.158 | 8376.5102 | 357632.7595 | 47654.8501 | 52103.234 | 6938.5528 | 14932.7287 | 33361.2949 | 799.0277 | 0 | 0 | 0 | 631063.2541 | 0 | 631063.8146 | -0.56046 | 47654.2897 | 0 | 1806.3423 | 2444.6244 | 325.8911 | 13913.831 | 1854.0291 | 2027.095 | 269.9469 | 580.9632 | 1297.9332 | 31.0865 | 0 | 0 | 0 | 24551.7426 | 0 | 24551.7644 | -0.021805 | 1854.0073 | 4.9031 | 0.65363 | 27.9065 | 4.0657 | 0.54142 | 0.062349 | 3.6229 | 0 | 0 | 2.6032 | 0 | 49.2426 | 49.2425 | -4.3734e-05
NC_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 766840.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579078.3476 | 0 | 0 | 1345919.2667 | 0 | 1345919.2667 | 0 | 0 | 6748.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5095.8895 | 0 | 0 | 11844.0895 | 0 | 11844.0895 | 0 | 0 | 766.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0783 | 0 | 0 | 1345.9193 | 0 | 1345.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.538 | 1.1614 | 0 | 0 | 2.6995 | 2.6995 | 0
NC_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 23145.4605 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20250.194 | 0 | 0 | 0 | 0 | 116005.159 | 0 | 0 | 336984.5672 | 0 | 336983.178 | 1.3893 | 1.3893 | 0 | 2029.8569 | 2488.4632 | 631.863 | 12453.769 | 0 | 1775.942 | 0 | 0 | 0 | 0 | 10173.6524 | 0 | 0 | 29553.5465 | 0 | 29553.4247 | 0.12184 | 0.12184 | 0 | 78.9723 | 96.8146 | 24.5829 | 484.5184 | 0 | 69.0937 | 0 | 0 | 0 | 0 | 395.8096 | 0 | 0 | 1149.7913 | 0 | 1149.7866 | 0.0047402 | 0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.0478 | 0 | 0 | 2.3405 | 0 | 11.7308 | 0 | 0 | 34.0768 | 34.077 | 0.00014049
NC_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 82128.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82128.3534 | 0 | 82128.3534 | 0 | 0 | 722.7295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722.7295 | 0 | 722.7295 | 0 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1284 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4341 | 0 | 0 | 0 | 2.4341 | 2.4341 | 0
NC_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 21825.6413 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19552.7737 | 0 | 0 | 0 | 0 | 116044.0589 | 0 | 0 | 329813.0866 | 0 | 329817.5323 | -4.4457 | -4.4457 | 0 | 1914.1087 | 2033.0247 | 631.863 | 12453.769 | 0 | 1714.7783 | 0 | 0 | 0 | 0 | 10177.064 | 0 | 0 | 28924.6077 | 0 | 28924.9976 | -0.38989 | -0.38989 | 0 | 74.4691 | 79.0956 | 24.5829 | 484.5184 | 0 | 66.7141 | 0 | 0 | 0 | 0 | 395.9423 | 0 | 0 | 1125.3223 | 0 | 1125.3374 | -0.015169 | -0.015169 | 2.3442 | 0.72858 | 14.3599 | 1.9772 | 0 | 0 | 2.2071 | 0 | 11.7348 | 0 | 0 | 33.3522 | 33.3518 | -0.00044956
NC_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 95151.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95151.3607 | 0 | 95151.3607 | 0 | 0 | 837.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 837.332 | 0 | 837.332 | 0 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1514 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8201 | 0 | 0 | 0 | 2.8201 | 2.8201 | 0
NC_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 85226.9758 | 96613.5421 | 7107.5736 | 317887.4784 | 4818.0346 | 87894.3999 | 708.5345 | 0 | 0 | 19688.9235 | 7179.8163 | 17630.0056 | 0 | 644755.2844 | 0 | 644755.0065 | 0.27786 | 4818.3125 | 0 | 7474.4058 | 8473.0076 | 623.3342 | 27878.7319 | 422.5416 | 7708.3389 | 62.1385 | 0 | 0 | 1726.7186 | 629.6699 | 1546.1515 | 0 | 56545.0384 | 0 | 56545.0141 | 0.024368 | 422.566 | 0 | 290.7944 | 329.6454 | 24.251 | 1084.6321 | 16.4391 | 299.8957 | 2.4175 | 0 | 0 | 67.1786 | 24.4975 | 60.1536 | 0 | 2199.905 | 0 | 2199.9041 | 0.00094805 | 16.4401 | 4.4571 | 0.3279 | 14.6653 | 4.0549 | 0.032687 | 0.90832 | 3.9318 | 0 | 0.33123 | 0 | 0.81334 | 29.7449 | 29.7449 | 1.2819e-05
NC_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 400642.2966 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120742.4229 | 0 | 0 | 863575.1344 | 0 | 863575.1344 | 0 | 0 | 3525.6522 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.5333 | 0 | 0 | 7599.4612 | 0 | 7599.4612 | 0 | 0 | 400.6423 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7424 | 0 | 0 | 863.5751 | 0 | 863.5751 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.4171 | 1.6326 | 0 | 0 | 11.6764 | 11.6764 | 0
NC_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 80445.0626 | 78544.523 | 7107.5736 | 312483.1662 | 4743.0133 | 75635.3637 | 489.0277 | 0 | 0 | 22461.9331 | 7179.8163 | 12495.2144 | 0 | 601584.6938 | 0 | 601589.1395 | -4.4457 | 4738.5676 | 0 | 7055.032 | 6888.3547 | 623.3342 | 27404.7737 | 415.9623 | 6633.2214 | 42.8877 | 0 | 0 | 1969.9115 | 629.6699 | 1095.8303 | 0 | 52758.9776 | 0 | 52759.3675 | -0.38989 | 415.5724 | 0 | 274.4786 | 267.9939 | 24.251 | 1066.1926 | 16.1832 | 258.0679 | 1.6686 | 0 | 0 | 76.6401 | 24.4975 | 42.6337 | 0 | 2052.607 | 0 | 2052.6221 | -0.015169 | 16.168 | 3.6235 | 0.3279 | 14.416 | 3.4893 | 0.022561 | 1.0363 | 3.7112 | 0 | 0.33123 | 0 | 0.57645 | 27.7535 | 27.7533 | -0.0002051
NC_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 380747.6153 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120505.4686 | 0 | 0 | 843443.4987 | 0 | 843443.4987 | 0 | 0 | 3350.579 | 0 | 0 | 0 | 3011.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.4481 | 0 | 0 | 7422.3028 | 0 | 7422.3028 | 0 | 0 | 380.7476 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5055 | 0 | 0 | 843.4435 | 0 | 843.4435 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.1481 | 1.6294 | 0 | 0 | 11.4042 | 11.4042 | 0
NC_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 27982.9451 | 83498.7074 | 10680.8103 | 53987.5506 | 0 | 42720.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218870.4761 | 0 | 218871.0319 | -0.55571 | -0.55571 | 0 | 2454.1043 | 7322.8366 | 936.7071 | 4734.7082 | 0 | 3746.5846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19194.9408 | 0 | 19194.9895 | -0.048736 | -0.048736 | 0 | 95.4778 | 284.8976 | 36.4429 | 184.2055 | 0 | 145.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.7861 | 0 | 746.788 | -0.0018961 | -0.0018961 | 11.5381 | 1.4759 | 7.4601 | 5.9032 | 0 | 0 | 3.8668 | 0 | 0 | 0 | 0 | 30.2441 | 30.244 | -7.679e-05
NC_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 379951.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91180.0069 | 0 | 0 | 471131.4558 | 0 | 471131.4558 | 0 | 0 | 3343.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.3841 | 0 | 0 | 4145.9568 | 0 | 4145.9568 | 0 | 0 | 379.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.18 | 0 | 0 | 471.1315 | 0 | 471.1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3876 | 3.6927 | 0 | 0 | 19.0803 | 19.0803 | 0
NC_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 0 | 25637.8348 | 65952.0588 | 10680.8103 | 53987.5506 | 0 | 40605.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196864.228 | 0 | 196864.5059 | -0.27786 | -0.27786 | 0 | 2248.4381 | 5783.9956 | 936.7071 | 4734.7082 | 0 | 3561.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17264.9928 | 0 | 17265.0172 | -0.024368 | -0.024368 | 0 | 87.4763 | 225.0284 | 36.4429 | 184.2055 | 0 | 138.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 671.7007 | 0 | 671.7017 | -0.00094805 | -0.00094805 | 9.1134 | 1.4759 | 7.4601 | 5.611 | 0 | 0 | 3.5427 | 0 | 0 | 0 | 0 | 27.2032 | 27.2032 | -3.8395e-05
NC_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 408755.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91189.4851 | 0 | 0 | 499945.0963 | 0 | 499945.0963 | 0 | 0 | 3597.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.4675 | 0 | 0 | 4399.5168 | 0 | 4399.5168 | 0 | 0 | 408.7556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1895 | 0 | 0 | 499.9451 | 0 | 499.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5542 | 3.6931 | 0 | 0 | 20.2472 | 20.2472 | 0
NC_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 25423.8851 | 62926.1997 | 79094.6792 | 12306.2718 | 154949.5496 | 0 | 45768.5504 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380541.3786 | 0 | 380541.6564 | -0.27786 | -0.27786 | 2229.6747 | 5518.6277 | 6936.6034 | 1079.26 | 13589.0755 | 0 | 4013.9019 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 33373.4789 | 0 | 33373.5033 | -0.024368 | -0.024368 | 86.7463 | 214.7042 | 269.871 | 41.989 | 528.6879 | 0 | 156.1623 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.4072 | 0 | 1298.4081 | -0.00094805 | -0.00094805 | 6.2467 | 0.97192 | 12.2376 | 3.6147 | 0.0057056 | 0 | 4.9698 | 2.0079 | 0 | 0 | 0 | 30.0544 | 30.0543 | -2.1945e-05
NC_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605437.1417 | 0 | 0 | 1070682.6533 | 0 | 1070682.6533 | 0 | 0 | 578.6006 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 5327.8468 | 0 | 0 | 9422.0073 | 0 | 9422.0073 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4371 | 0 | 0 | 1070.6827 | 0 | 1070.6827 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0141 | 0 | 0 | 24.7832 | 24.7832 | 0
NC_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 29311.0999 | 58294.329 | 50731.0705 | 12306.2718 | 154949.5496 | 0 | 43317.8546 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348982.4182 | 0 | 348984.0853 | -1.6671 | -1.6671 | 2570.5835 | 5112.4127 | 4449.1149 | 1079.26 | 13589.0755 | 0 | 3798.9758 | 6.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 30605.7581 | 0 | 30605.9043 | -0.14621 | -0.14621 | 100.0095 | 198.9003 | 173.0944 | 41.989 | 528.6879 | 0 | 147.8005 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.728 | 0 | 1190.7337 | -0.0056883 | -0.0056883 | 4.0066 | 0.97192 | 12.2376 | 3.4211 | 0.0057056 | 0 | 4.604 | 2.3149 | 0 | 0 | 0 | 27.562 | 27.5619 | -0.00013167
NC_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605503.4889 | 0 | 0 | 1070749.0005 | 0 | 1070749.0005 | 0 | 0 | 578.6006 | 0 | 0 | 0 | 3515.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 5328.4307 | 0 | 0 | 9422.5912 | 0 | 9422.5912 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5035 | 0 | 0 | 1070.749 | 0 | 1070.749 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0156 | 0 | 0 | 24.7847 | 24.7847 | 0
NC_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 3103.659 | 3061.9805 | 8816.3921 | 1583.783 | 13417.6985 | 0 | 4776.3561 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39764.0678 | 0 | 39766.0128 | -1.945 | -1.945 | 272.1909 | 268.5357 | 773.1976 | 138.8978 | 1176.7322 | 0 | 418.8864 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3487.3087 | 0 | 3487.4793 | -0.17058 | -0.17058 | 10.5897 | 10.4475 | 30.0815 | 5.4039 | 45.7812 | 0 | 16.2969 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.675 | 0 | 135.6816 | -0.0066363 | -0.0066363 | 5.4674 | 0.98216 | 8.3208 | 2.962 | 0 | 0 | 1.8989 | 1.9247 | 3.1033 | 0 | 0 | 24.6604 | 24.6592 | -0.0012062
NC_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 8757.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8757.8302 | 0 | 8757.8302 | 0 | 0 | 77.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0689 | 0 | 77.0689 | 0 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7578 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5918 | 0 | 0 | 0 | 1.5918 | 1.5918 | 0
NC_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Electricity | 3162.0089 | 2861.9237 | 7104.795 | 1583.783 | 13417.6985 | 0 | 4370.6854 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37505.0931 | 0 | 37504.2595 | 0.83357 | 0.83357 | 277.3082 | 250.9907 | 623.0905 | 138.8978 | 1176.7322 | 0 | 383.3091 | 0 | 0 | 0 | 0 | 438.8682 | 0 | 0 | 3289.1967 | 0 | 3289.1236 | 0.073104 | 0.073104 | 10.7888 | 9.7649 | 24.2416 | 5.4039 | 45.7812 | 0 | 14.9128 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 127.9674 | 0 | 127.9645 | 0.0028441 | 0.0028441 | 4.406 | 0.98216 | 8.3208 | 2.7104 | 0 | 0 | 1.7748 | 1.9609 | 3.1033 | 0 | 0 | 23.2578 | 23.2583 | 0.00051693
NC_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | NC-ELKINS-WV | Zone5A | Zone5A(NC-ELKINS-WV) |  |  | NC | 0.0877 | 0.0088 |  |  |  | Natural Gas | 9127.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.4789 | 0 | 9127.4789 | 0 | 0 | 80.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3218 | 0 | 80.3218 | 0 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1275 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 0 | 0 | 0 | 1.6589 | 1.6589 | 0
ND_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 487955.2094 | 884064.897 | 97191.484 | 4077910.5986 | 543459.8574 | 620884.618 | 75446.4211 | 154285.4722 | 479755.6591 | 12811.971 | 0 | 0 | 0 | 7433766.1878 | 0 | 7433761.4642 | 4.7236 | 543464.581 | 0 | 43915.9688 | 79565.8407 | 8747.2336 | 367011.9539 | 48911.3872 | 55879.6156 | 6790.1779 | 13885.6925 | 43178.0093 | 1153.0774 | 0 | 0 | 0 | 669038.9569 | 0 | 669038.5318 | 0.42512 | 48911.8123 | 0 | 1664.9032 | 3016.4294 | 331.6173 | 13913.831 | 1854.285 | 2118.4583 | 257.4232 | 526.422 | 1636.9263 | 43.7144 | 0 | 0 | 0 | 25364.0102 | 0 | 25363.9941 | 0.016117 | 1854.3012 | 6.0499 | 0.66511 | 27.9065 | 4.2489 | 0.5163 | 0.087676 | 3.3392 | 0 | 0 | 3.2831 | 0 | 50.8716 | 50.8717 | 3.2325e-05
ND_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 1897909.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618043.1094 | 0 | 0 | 2515952.1105 | 0 | 2515952.1105 | 0 | 0 | 9362.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3048.8067 | 0 | 0 | 12411.1918 | 0 | 12411.1918 | 0 | 0 | 1897.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.0431 | 0 | 0 | 2515.9521 | 0 | 2515.9521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8066 | 1.2396 | 0 | 0 | 5.0462 | 5.0462 | 0
ND_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 452328.4274 | 720001.6487 | 97191.484 | 4077910.5986 | 543387.6147 | 595652.454 | 71737.0346 | 137883.593 | 479422.2311 | 11389.3448 | 0 | 0 | 0 | 7186904.4309 | 0 | 7186906.098 | -1.6671 | 543385.9475 | 0 | 40709.5585 | 64800.1484 | 8747.2336 | 367011.9539 | 48904.8853 | 53608.7209 | 6456.3331 | 12409.5234 | 43148.0008 | 1025.041 | 0 | 0 | 0 | 646821.3988 | 0 | 646821.5488 | -0.15004 | 48904.7353 | 0 | 1543.3446 | 2456.6456 | 331.6173 | 13913.831 | 1854.0385 | 2032.3662 | 244.7668 | 470.4588 | 1635.7887 | 38.8604 | 0 | 0 | 0 | 24521.7179 | 0 | 24521.7236 | -0.0056883 | 1854.0329 | 4.9272 | 0.66511 | 27.9065 | 4.0762 | 0.49092 | 0.077941 | 3.0954 | 0 | 0 | 3.2808 | 0 | 49.1823 | 49.1823 | -1.1409e-05
ND_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 1926466.7309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617948.3277 | 0 | 0 | 2544415.0586 | 0 | 2544415.0586 | 0 | 0 | 9503.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3048.3391 | 0 | 0 | 12551.5995 | 0 | 12551.5995 | 0 | 0 | 1926.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.9483 | 0 | 0 | 2544.4151 | 0 | 2544.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8638 | 1.2394 | 0 | 0 | 5.1032 | 5.1032 | 0
ND_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 22548.0686 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 22486.9402 | 0 | 0 | 0 | 0 | 123626.7674 | 0 | 0 | 346239.9729 | 0 | 346238.0279 | 1.945 | 1.945 | 0 | 2029.3262 | 2553.7251 | 647.934 | 12780.3787 | 0 | 2023.8246 | 0 | 0 | 0 | 0 | 11126.4091 | 0 | 0 | 31161.5976 | 0 | 31161.4225 | 0.17505 | 0.17505 | 0 | 76.934 | 96.8146 | 24.5639 | 484.5184 | 0 | 76.7254 | 0 | 0 | 0 | 0 | 421.8145 | 0 | 0 | 1181.3708 | 0 | 1181.3642 | 0.0066363 | 0.0066363 | 2.8693 | 0.72801 | 14.3599 | 2.274 | 0 | 0 | 2.2801 | 0 | 12.5015 | 0 | 0 | 35.0127 | 35.0129 | 0.00019668
ND_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 268507.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268507.1119 | 0 | 268507.1119 | 0 | 0 | 1324.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.5456 | 0 | 1324.5456 | 0 | 0 | 268.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.5071 | 0 | 268.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9579 | 0 | 0 | 0 | 7.9579 | 7.9579 | 0
ND_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 20530.8292 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 21528.3347 | 0 | 0 | 0 | 0 | 123662.8888 | 0 | 0 | 338107.1082 | 0 | 338106.2746 | 0.83357 | 0.83357 | 0 | 1847.7746 | 2086.3424 | 647.934 | 12780.3787 | 0 | 1937.5501 | 0 | 0 | 0 | 0 | 11129.66 | 0 | 0 | 30429.6397 | 0 | 30429.5647 | 0.075021 | 0.075021 | 0 | 70.0512 | 79.0956 | 24.5639 | 484.5184 | 0 | 73.4547 | 0 | 0 | 0 | 0 | 421.9378 | 0 | 0 | 1153.6215 | 0 | 1153.6186 | 0.0028441 | 0.0028441 | 2.3442 | 0.72801 | 14.3599 | 2.177 | 0 | 0 | 2.0761 | 0 | 12.5052 | 0 | 0 | 34.1904 | 34.1905 | 8.4293e-05
ND_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 294600.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294600.5172 | 0 | 294600.5172 | 0 | 0 | 1453.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.2644 | 0 | 1453.2644 | 0 | 0 | 294.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.6005 | 0 | 294.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7312 | 0 | 0 | 0 | 8.7312 | 8.7312 | 0
ND_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 75096.3217 | 98703.0243 | 7196.4877 | 317887.4784 | 4818.0346 | 104154.5721 | 1247.5764 | 0 | 0 | 22139.6193 | 7182.5949 | 17566.0986 | 0 | 655991.808 | 0 | 655989.863 | 1.945 | 4819.9796 | 0 | 6758.669 | 8883.2722 | 647.6839 | 28609.8731 | 433.6231 | 9373.9115 | 112.2819 | 0 | 0 | 1992.5657 | 646.4335 | 1580.9489 | 0 | 59039.2627 | 0 | 59039.0877 | 0.17505 | 433.7982 | 0 | 256.2286 | 336.7747 | 24.5544 | 1084.6321 | 16.4391 | 355.3754 | 4.2567 | 0 | 0 | 75.5404 | 24.507 | 59.9355 | 0 | 2238.244 | 0 | 2238.2374 | 0.0066363 | 16.4458 | 4.5535 | 0.332 | 14.6653 | 4.805 | 0.057555 | 1.0214 | 3.4645 | 0 | 0.33136 | 0 | 0.81039 | 30.2632 | 30.2633 | 8.973e-05
ND_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 946755.5648 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 129215.908 | 0 | 0 | 1418161.8876 | 0 | 1418161.8876 | 0 | 0 | 4670.3452 | 0 | 0 | 0 | 1688.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 637.4221 | 0 | 0 | 6995.7926 | 0 | 6995.7926 | 0 | 0 | 946.7556 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 129.2159 | 0 | 0 | 1418.1619 | 0 | 1418.1619 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.8011 | 1.7471 | 0 | 0 | 19.175 | 19.175 | 0
ND_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 66363.2866 | 80914.6404 | 7196.4877 | 312483.1662 | 4745.7919 | 84404.5201 | 1178.1123 | 0 | 0 | 22878.7181 | 7182.5949 | 12434.0859 | 0 | 599781.4041 | 0 | 599783.0712 | -1.6671 | 4744.1248 | 0 | 5972.6958 | 7282.3176 | 647.6839 | 28123.485 | 427.1213 | 7596.4068 | 106.0301 | 0 | 0 | 2059.0846 | 646.4335 | 1119.0677 | 0 | 53980.3264 | 0 | 53980.4764 | -0.15004 | 426.9712 | 0 | 226.4315 | 276.0808 | 24.5544 | 1066.1926 | 16.1926 | 287.9882 | 4.0197 | 0 | 0 | 78.0622 | 24.507 | 42.4251 | 0 | 2046.4542 | 0 | 2046.4598 | -0.0056883 | 16.187 | 3.7329 | 0.332 | 14.416 | 3.8939 | 0.054351 | 1.0555 | 3.0616 | 0 | 0.33136 | 0 | 0.57363 | 27.6702 | 27.6701 | -7.6911e-05
ND_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 911885.373 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 128941.041 | 0 | 0 | 1383016.8288 | 0 | 1383016.8288 | 0 | 0 | 4498.3305 | 0 | 0 | 0 | 1688.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 636.0662 | 0 | 0 | 6822.422 | 0 | 6822.422 | 0 | 0 | 911.8854 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 128.941 | 0 | 0 | 1383.0168 | 0 | 1383.0168 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.3296 | 1.7434 | 0 | 0 | 18.6998 | 18.6998 | 0
ND_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 26499.1904 | 91170.33 | 10847.5243 | 53987.5506 | 0 | 46716.0416 | 0 | 0 | 0 | 5229.2625 | 0 | 0 | 0 | 234449.8995 | 0 | 234449.8995 | 0 | 0 | 0 | 2384.9271 | 8205.3297 | 976.2772 | 4858.8796 | 0 | 4204.4437 | 0 | 0 | 0 | 470.6336 | 0 | 0 | 0 | 21100.491 | 0 | 21100.491 | 0 | 0 | 0 | 90.4152 | 311.0732 | 37.0118 | 184.2055 | 0 | 159.3951 | 0 | 0 | 0 | 17.8422 | 0 | 0 | 0 | 799.9431 | 0 | 799.9431 | 0 | 0 | 12.5981 | 1.4989 | 7.4601 | 6.4553 | 0 | 0.72259 | 3.6617 | 0 | 0 | 0 | 0 | 32.3969 | 32.3969 | 0
ND_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 385069.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93473.7244 | 0 | 0 | 478543.3857 | 0 | 478543.3857 | 0 | 0 | 1899.5486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461.1059 | 0 | 0 | 2360.6545 | 0 | 2360.6545 | 0 | 0 | 385.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4737 | 0 | 0 | 478.5434 | 0 | 478.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5949 | 3.7856 | 0 | 0 | 19.3805 | 19.3805 | 0
ND_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 23528.9027 | 75532.5567 | 10847.5243 | 53987.5506 | 0 | 46991.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210887.6541 | 0 | 210887.9319 | -0.27786 | -0.27786 | 0 | 2117.6012 | 6797.9301 | 976.2772 | 4858.8796 | 0 | 4229.2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18979.8889 | 0 | 18979.9139 | -0.025007 | -0.025007 | 0 | 80.2806 | 257.7171 | 37.0118 | 184.2055 | 0 | 160.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719.5487 | 0 | 719.5496 | -0.00094805 | -0.00094805 | 10.4373 | 1.4989 | 7.4601 | 6.4933 | 0 | 0 | 3.2513 | 0 | 0 | 0 | 0 | 29.141 | 29.141 | -3.8395e-05
ND_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 747154.7575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93492.6807 | 0 | 0 | 840647.4382 | 0 | 840647.4382 | 0 | 0 | 3685.7144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461.1994 | 0 | 0 | 4146.9138 | 0 | 4146.9138 | 0 | 0 | 747.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4927 | 0 | 0 | 840.6474 | 0 | 840.6474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.259 | 3.7864 | 0 | 0 | 34.0453 | 34.0453 | 0
ND_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 64432.1828 | 53773.601 | 79391.9858 | 12292.379 | 154949.5496 | 0 | 46310.3709 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 411222.3119 | 0 | 411220.089 | 2.2229 | 2.2229 | 5798.8965 | 4839.6241 | 7145.2787 | 1106.3141 | 13945.4595 | 0 | 4167.9334 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 37010.0081 | 0 | 37009.808 | 0.20006 | 0.20006 | 219.8426 | 183.4755 | 270.8855 | 41.9416 | 528.6879 | 0 | 158.011 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1403.0905 | 0 | 1403.0829 | 0.0075844 | 0.0075844 | 6.2702 | 0.97083 | 12.2376 | 3.6575 | 0.0057056 | 0 | 4.2469 | 5.0887 | 0 | 0 | 0 | 32.4773 | 32.4774 | 0.00017556
ND_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 135016.5487 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649908.721 | 0 | 0 | 1184420.7077 | 0 | 1184420.7077 | 0 | 0 | 666.0366 | 0 | 0 | 0 | 1970.711 | 0 | 0 | 0 | 0 | 0 | 0 | 3205.9997 | 0 | 0 | 5842.7474 | 0 | 5842.7474 | 0 | 0 | 135.0165 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.9087 | 0 | 0 | 1184.4207 | 0 | 1184.4207 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.1252 | 15.0435 | 0 | 0 | 27.4159 | 27.4159 | 0
ND_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 70511.6867 | 49572.4082 | 51025.5986 | 12292.379 | 154949.5496 | 0 | 43731.861 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 382155.7258 | 0 | 382156.8372 | -1.1114 | -1.1114 | 6346.0518 | 4461.5167 | 4592.3039 | 1106.3141 | 13945.4595 | 0 | 3935.8675 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 34394.0153 | 0 | 34394.1153 | -0.10003 | -0.10003 | 240.5859 | 169.1411 | 174.0993 | 41.9416 | 528.6879 | 0 | 149.2131 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1303.9153 | 0 | 1303.9191 | -0.0037922 | -0.0037922 | 4.0299 | 0.97083 | 12.2376 | 3.4538 | 0.0057056 | 0 | 3.9151 | 5.5689 | 0 | 0 | 0 | 30.1819 | 30.1818 | -8.7778e-05
ND_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 130495.4611 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 649984.5464 | 0 | 0 | 1179975.4454 | 0 | 1179975.4454 | 0 | 0 | 643.7341 | 0 | 0 | 0 | 1970.711 | 0 | 0 | 0 | 0 | 0 | 0 | 3206.3738 | 0 | 0 | 5820.8189 | 0 | 5820.8189 | 0 | 0 | 130.4955 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 649.9845 | 0 | 0 | 1179.9754 | 0 | 1179.9754 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.0206 | 15.0452 | 0 | 0 | 27.313 | 27.313 | 0
ND_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 4667.992 | 2981.4021 | 8852.5135 | 1600.4544 | 13417.6985 | 0 | 5482.1121 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42006.3711 | 0 | 42007.7604 | -1.3893 | -1.3893 | 420.1193 | 268.3262 | 796.7262 | 144.0409 | 1207.5929 | 0 | 493.3901 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3780.5734 | 0 | 3780.6984 | -0.12504 | -0.12504 | 15.9272 | 10.1725 | 30.2048 | 5.4608 | 45.7812 | 0 | 18.705 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.3257 | 0 | 143.3305 | -0.0047402 | -0.0047402 | 5.4898 | 0.9925 | 8.3208 | 3.3997 | 0 | 0 | 1.8489 | 2.8948 | 3.1033 | 0 | 0 | 26.0506 | 26.0498 | -0.00086155
ND_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 34737.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34737.4974 | 0 | 34737.4974 | 0 | 0 | 171.3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.3601 | 0 | 171.3601 | 0 | 0 | 34.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7375 | 0 | 34.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3136 | 0 | 0 | 0 | 6.3136 | 6.3136 | 0
ND_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 4734.6776 | 2717.4382 | 7163.1449 | 1600.4544 | 13417.6985 | 0 | 4993.0843 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39630.6966 | 0 | 39628.1959 | 2.5007 | 2.5007 | 426.121 | 244.5694 | 644.683 | 144.0409 | 1207.5929 | 0 | 449.3776 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3566.7627 | 0 | 3566.5376 | 0.22506 | 0.22506 | 16.1547 | 9.2719 | 24.4407 | 5.4608 | 45.7812 | 0 | 17.0364 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.2199 | 0 | 135.2114 | 0.0085324 | 0.0085324 | 4.4421 | 0.9925 | 8.3208 | 3.0964 | 0 | 0 | 1.6852 | 2.9362 | 3.1033 | 0 | 0 | 24.575 | 24.5765 | 0.0015508
ND_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | ND-BISMARCK-ND | Zone6A | Zone6A(ND-BISMARCK-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 35865.3998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35865.3998 | 0 | 35865.3998 | 0 | 0 | 176.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.924 | 0 | 176.924 | 0 | 0 | 35.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8654 | 0 | 35.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5186 | 0 | 0 | 0 | 6.5186 | 6.5186 | 0
ND_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 459021.9945 | 881783.6938 | 97410.9908 | 4077910.5986 | 543459.8574 | 642676.9165 | 79969.9277 | 145496.8658 | 516277.1396 | 14140.1258 | 0 | 0 | 0 | 7458148.1104 | 0 | 7458146.7211 | 1.3893 | 543461.2467 | 0 | 41311.9795 | 79360.5324 | 8766.9892 | 367011.9539 | 48911.3872 | 57840.9225 | 7197.2935 | 13094.7179 | 46464.9426 | 1272.6113 | 0 | 0 | 0 | 671233.3299 | 0 | 671233.2049 | 0.12504 | 48911.5122 | 0 | 1566.183 | 3008.646 | 332.3663 | 13913.831 | 1854.285 | 2192.8136 | 272.8574 | 496.4353 | 1761.5376 | 48.2461 | 0 | 0 | 0 | 25447.2014 | 0 | 25447.1966 | 0.0047402 | 1854.2898 | 6.0343 | 0.66662 | 27.9065 | 4.398 | 0.54726 | 0.096765 | 3.1412 | 0 | 0 | 3.5331 | 0 | 51.0385 | 51.0385 | 9.5073e-06
ND_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 2050602.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627691.8877 | 0 | 0 | 2678294.2268 | 0 | 2678294.2268 | 0 | 0 | 10115.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3096.4041 | 0 | 0 | 13212.0254 | 0 | 13212.0254 | 0 | 0 | 2050.6023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.6919 | 0 | 0 | 2678.2942 | 0 | 2678.2942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1128 | 1.2589 | 0 | 0 | 5.3718 | 5.3718 | 0
ND_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 420549.9602 | 718451.2085 | 97410.9908 | 4077910.5986 | 543387.6147 | 607630.8549 | 76221.6412 | 129336.7219 | 515982.6115 | 12611.9142 | 0 | 0 | 0 | 7199494.1165 | 0 | 7199494.1165 | 0 | 543387.6147 | 0 | 37849.4964 | 64660.6088 | 8766.9892 | 367011.9539 | 48904.8853 | 54686.7769 | 6859.9477 | 11640.305 | 46438.435 | 1135.0723 | 0 | 0 | 0 | 647954.4705 | 0 | 647954.4705 | 0 | 48904.8853 | 0 | 1434.9165 | 2451.3555 | 332.3663 | 13913.831 | 1854.0385 | 2073.2365 | 260.0682 | 441.2969 | 1760.5327 | 43.0319 | 0 | 0 | 0 | 24564.6739 | 0 | 24564.6739 | 0 | 1854.0385 | 4.9166 | 0.66662 | 27.9065 | 4.1582 | 0.52161 | 0.086307 | 2.878 | 0 | 0 | 3.531 | 0 | 49.2685 | 49.2685 | 0
ND_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 2015135.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627616.0624 | 0 | 0 | 2642751.0848 | 0 | 2642751.0848 | 0 | 0 | 9940.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3096.03 | 0 | 0 | 13036.6911 | 0 | 13036.6911 | 0 | 0 | 2015.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.6161 | 0 | 0 | 2642.7511 | 0 | 2642.7511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0417 | 1.2588 | 0 | 0 | 5.3005 | 5.3005 | 0
ND_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 21239.3637 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 23184.3604 | 0 | 0 | 0 | 0 | 125516.1927 | 0 | 0 | 347515.335 | 0 | 347515.0571 | 0.27786 | 0.27786 | 0 | 1911.5427 | 2553.7251 | 647.6839 | 12780.3787 | 0 | 2086.5924 | 0 | 0 | 0 | 0 | 11296.4573 | 0 | 0 | 31276.3801 | 0 | 31276.3551 | 0.025007 | 0.025007 | 0 | 72.4687 | 96.8146 | 24.5544 | 484.5184 | 0 | 79.105 | 0 | 0 | 0 | 0 | 428.2612 | 0 | 0 | 1185.7223 | 0 | 1185.7214 | 0.00094805 | 0.00094805 | 2.8693 | 0.72773 | 14.3599 | 2.3445 | 0 | 0 | 2.1478 | 0 | 12.6926 | 0 | 0 | 35.1419 | 35.1419 | 2.8098e-05
ND_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 330409.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330409.048 | 0 | 330409.048 | 0 | 0 | 1629.9078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1629.9078 | 0 | 1629.9078 | 0 | 0 | 330.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330.409 | 0 | 330.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7925 | 0 | 0 | 0 | 9.7925 | 9.7925 | 0
ND_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 19380.5026 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 21472.7633 | 0 | 0 | 0 | 0 | 125505.0785 | 0 | 0 | 338740.6214 | 0 | 338744.7892 | -4.1679 | -4.1679 | 0 | 1744.2452 | 2086.3424 | 647.6839 | 12780.3787 | 0 | 1932.5487 | 0 | 0 | 0 | 0 | 11295.4571 | 0 | 0 | 30486.6559 | 0 | 30487.031 | -0.37511 | -0.37511 | 0 | 66.1263 | 79.0956 | 24.5544 | 484.5184 | 0 | 73.2651 | 0 | 0 | 0 | 0 | 428.2233 | 0 | 0 | 1155.783 | 0 | 1155.7972 | -0.014221 | -0.014221 | 2.3442 | 0.72773 | 14.3599 | 2.1714 | 0 | 0 | 1.9598 | 0 | 12.6915 | 0 | 0 | 34.255 | 34.2546 | -0.00042147
ND_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 304040.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304040.7758 | 0 | 304040.7758 | 0 | 0 | 1499.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1499.8331 | 0 | 1499.8331 | 0 | 0 | 304.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.0408 | 0 | 304.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.011 | 0 | 0 | 0 | 9.011 | 9.011 | 0
ND_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 67977.6339 | 95207.5874 | 7149.2521 | 317887.4784 | 4818.0346 | 107419.3879 | 177.8283 | 0 | 0 | 19847.3018 | 7182.5949 | 17543.87 | 0 | 645210.9693 | 0 | 645212.6365 | -1.6671 | 4816.3675 | 0 | 6117.987 | 8568.6829 | 643.4327 | 28609.8731 | 433.6231 | 9667.7449 | 16.0045 | 0 | 0 | 1786.2572 | 646.4335 | 1578.9483 | 0 | 58068.9872 | 0 | 58069.1373 | -0.15004 | 433.4731 | 0 | 231.9397 | 324.8483 | 24.3932 | 1084.6321 | 16.4391 | 366.515 | 0.60675 | 0 | 0 | 67.719 | 24.507 | 59.8597 | 0 | 2201.4598 | 0 | 2201.4655 | -0.0056883 | 16.4334 | 4.3923 | 0.32982 | 14.6653 | 4.9557 | 0.0082039 | 0.91563 | 3.1361 | 0 | 0.33136 | 0 | 0.80936 | 29.766 | 29.7659 | -7.6911e-05
ND_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 1015462.8279 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130760.8499 | 0 | 0 | 1488414.0926 | 0 | 1488414.0926 | 0 | 0 | 5009.2781 | 0 | 0 | 0 | 1688.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 645.0433 | 0 | 0 | 7342.3467 | 0 | 7342.3467 | 0 | 0 | 1015.4628 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.7608 | 0 | 0 | 1488.4141 | 0 | 1488.4141 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.7301 | 1.768 | 0 | 0 | 20.1249 | 20.1249 | 0
ND_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 58897.278 | 78138.8522 | 7149.2521 | 312483.1662 | 4743.0133 | 87927.7427 | 155.5997 | 0 | 0 | 22700.8898 | 7182.5949 | 12428.5288 | 0 | 591806.9177 | 0 | 591810.8077 | -3.89 | 4739.1233 | 0 | 5300.755 | 7032.4967 | 643.4327 | 28123.485 | 426.8712 | 7913.4968 | 14.004 | 0 | 0 | 2043.0801 | 646.4335 | 1118.5676 | 0 | 53262.6226 | 0 | 53262.9727 | -0.3501 | 426.5211 | 0 | 200.9575 | 266.6098 | 24.3932 | 1066.1926 | 16.1832 | 300.0095 | 0.53091 | 0 | 0 | 77.4554 | 24.507 | 42.4061 | 0 | 2019.2452 | 0 | 2019.2585 | -0.013273 | 16.1699 | 3.6048 | 0.32982 | 14.416 | 4.0564 | 0.0071784 | 1.0473 | 2.7171 | 0 | 0.33136 | 0 | 0.57337 | 27.3024 | 27.3022 | -0.00017946
ND_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 968991.3545 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 130542.8519 | 0 | 0 | 1441724.6212 | 0 | 1441724.6212 | 0 | 0 | 4780.0344 | 0 | 0 | 0 | 1688.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 643.9679 | 0 | 0 | 7112.0276 | 0 | 7112.0276 | 0 | 0 | 968.9914 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 130.5429 | 0 | 0 | 1441.7246 | 0 | 1441.7246 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.1017 | 1.7651 | 0 | 0 | 19.4936 | 19.4936 | 0
ND_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 23014.8678 | 89950.5392 | 10672.4746 | 53987.5506 | 0 | 47174.5051 | 0 | 0 | 0 | 5120.8984 | 0 | 0 | 0 | 229920.8358 | 0 | 229917.5016 | 3.3343 | 3.3343 | 0 | 2071.3381 | 8095.5485 | 960.5227 | 4858.8796 | 0 | 4245.7055 | 0 | 0 | 0 | 460.8809 | 0 | 0 | 0 | 20692.8752 | 0 | 20692.5751 | 0.30009 | 0.30009 | 0 | 78.5267 | 306.9112 | 36.4145 | 184.2055 | 0 | 160.9594 | 0 | 0 | 0 | 17.4725 | 0 | 0 | 0 | 784.4899 | 0 | 784.4785 | 0.011377 | 0.011377 | 12.4296 | 1.4747 | 7.4601 | 6.5187 | 0 | 0.70762 | 3.1802 | 0 | 0 | 0 | 0 | 31.7706 | 31.771 | 0.00046074
ND_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 418224.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94032.9365 | 0 | 0 | 512257.2407 | 0 | 512257.2407 | 0 | 0 | 2063.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.8645 | 0 | 0 | 2526.965 | 0 | 2526.965 | 0 | 0 | 418.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0329 | 0 | 0 | 512.2572 | 0 | 512.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.9376 | 3.8082 | 0 | 0 | 20.7459 | 20.7459 | 0
ND_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 0 | 20914.2714 | 74393.3444 | 10672.4746 | 53987.5506 | 0 | 44729.3665 | 0 | 0 | 0 | 5237.5982 | 0 | 0 | 0 | 209934.6057 | 0 | 209932.6607 | 1.945 | 1.945 | 0 | 1882.2844 | 6695.401 | 960.5227 | 4858.8796 | 0 | 4025.643 | 0 | 0 | 0 | 471.3838 | 0 | 0 | 0 | 18894.1145 | 0 | 18893.9395 | 0.17505 | 0.17505 | 0 | 71.3595 | 253.8301 | 36.4145 | 184.2055 | 0 | 152.6166 | 0 | 0 | 0 | 17.8707 | 0 | 0 | 0 | 716.2969 | 0 | 716.2902 | 0.0066363 | 0.0066363 | 10.2799 | 1.4747 | 7.4601 | 6.1808 | 0 | 0.72374 | 2.89 | 0 | 0 | 0 | 0 | 29.009 | 29.0093 | 0.00026876
ND_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 444175.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94042.4146 | 0 | 0 | 538217.9516 | 0 | 538217.9516 | 0 | 0 | 2191.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.9112 | 0 | 0 | 2655.0292 | 0 | 2655.0292 | 0 | 0 | 444.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0424 | 0 | 0 | 538.218 | 0 | 538.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9886 | 3.8086 | 0 | 0 | 21.7973 | 21.7973 | 0
ND_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 68149.905 | 51067.2771 | 79094.6792 | 12289.6004 | 154949.5496 | 0 | 46368.7208 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 411991.9748 | 0 | 411991.697 | 0.27786 | 0.27786 | 6133.4915 | 4596.0549 | 7118.5211 | 1106.064 | 13945.4595 | 0 | 4173.1849 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 37079.2777 | 0 | 37079.2527 | 0.025007 | 0.025007 | 232.5275 | 174.2415 | 269.871 | 41.9321 | 528.6879 | 0 | 158.2101 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.7166 | 0 | 1405.7157 | 0.00094805 | 0.00094805 | 6.2467 | 0.97061 | 12.2376 | 3.6621 | 0.0057056 | 0 | 4.0332 | 5.3823 | 0 | 0 | 0 | 32.5382 | 32.5382 | 2.1945e-05
ND_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 149375.9781 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 660789.6616 | 0 | 0 | 1209661.0776 | 0 | 1209661.0776 | 0 | 0 | 736.8717 | 0 | 0 | 0 | 1970.711 | 0 | 0 | 0 | 0 | 0 | 0 | 3259.6754 | 0 | 0 | 5967.2581 | 0 | 5967.2581 | 0 | 0 | 149.376 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 660.7897 | 0 | 0 | 1209.6611 | 0 | 1209.6611 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.4576 | 15.2953 | 0 | 0 | 28.0001 | 28.0001 | 0
ND_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 73887.6452 | 46677.1417 | 50931.1273 | 12289.6004 | 154949.5496 | 0 | 43706.8539 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 382514.1609 | 0 | 382515.828 | -1.6671 | -1.6671 | 6649.8881 | 4200.9428 | 4583.8015 | 1106.064 | 13945.4595 | 0 | 3933.6169 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 34426.2745 | 0 | 34426.4245 | -0.15004 | -0.15004 | 252.1046 | 159.2624 | 173.777 | 41.9321 | 528.6879 | 0 | 149.1278 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.1383 | 0 | 1305.144 | -0.0056883 | -0.0056883 | 4.0224 | 0.97061 | 12.2376 | 3.4519 | 0.0057056 | 0 | 3.6865 | 5.8355 | 0 | 0 | 0 | 30.2103 | 30.2101 | -0.00013167
ND_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 141869.2665 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 660874.9651 | 0 | 0 | 1202239.6695 | 0 | 1202239.6695 | 0 | 0 | 699.8411 | 0 | 0 | 0 | 1970.711 | 0 | 0 | 0 | 0 | 0 | 0 | 3260.0962 | 0 | 0 | 5930.6483 | 0 | 5930.6483 | 0 | 0 | 141.8693 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 660.875 | 0 | 0 | 1202.2397 | 0 | 1202.2397 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 3.2839 | 15.2973 | 0 | 0 | 27.8283 | 27.8283 | 0
ND_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 4562.4065 | 2839.6951 | 8774.7136 | 1617.1258 | 13417.6985 | 0 | 5762.7473 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41978.5854 | 0 | 41976.6404 | 1.945 | 1.945 | 410.6166 | 255.5726 | 789.7242 | 145.5413 | 1207.5929 | 0 | 518.6473 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3778.0727 | 0 | 3777.8976 | 0.17505 | 0.17505 | 15.5669 | 9.689 | 29.9393 | 5.5176 | 45.7812 | 0 | 19.6625 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.2309 | 0 | 143.2243 | 0.0066363 | 0.0066363 | 5.4415 | 1.0028 | 8.3208 | 3.5737 | 0 | 0 | 1.761 | 2.8293 | 3.1033 | 0 | 0 | 26.0313 | 26.0325 | 0.0012062
ND_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 39012.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39012.1527 | 0 | 39012.1527 | 0 | 0 | 192.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.4469 | 0 | 192.4469 | 0 | 0 | 39.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.0122 | 0 | 39.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0905 | 0 | 0 | 0 | 7.0905 | 7.0905 | 0
ND_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Electricity | 4634.6492 | 2450.6958 | 7127.0235 | 1617.1258 | 13417.6985 | 0 | 5070.8842 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39322.2757 | 0 | 39316.7186 | 5.5571 | 5.5571 | 417.1184 | 220.5626 | 641.4321 | 145.5413 | 1207.5929 | 0 | 456.3796 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3539.0048 | 0 | 3538.5047 | 0.50014 | 0.50014 | 15.8134 | 8.3618 | 24.3174 | 5.5176 | 45.7812 | 0 | 17.3019 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.1676 | 0 | 134.1486 | 0.018961 | 0.018961 | 4.4197 | 1.0028 | 8.3208 | 3.1446 | 0 | 0 | 1.5198 | 2.8741 | 3.1033 | 0 | 0 | 24.3818 | 24.3852 | 0.0034462
ND_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | ND-MINOT-ND | Zone7 | Zone7(ND-MINOT-ND) |  |  | ND | 0.09 | 0.004933 |  |  |  | Natural Gas | 40187.4459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40187.4459 | 0 | 40187.4459 | 0 | 0 | 198.2447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.2447 | 0 | 198.2447 | 0 | 0 | 40.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.1874 | 0 | 40.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3042 | 0 | 0 | 0 | 7.3042 | 7.3042 | 0
NE_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 767595.7174 | 881616.9798 | 95927.2361 | 4077910.5986 | 543459.8574 | 603010.0985 | 104268.4933 | 251326.9136 | 375006.4737 | 13109.2776 | 0 | 0 | 0 | 7713231.6461 | 0 | 7713227.2004 | 4.4457 | 543464.3031 | 0 | 69774.4507 | 80138.9835 | 8719.7858 | 370682.0734 | 49400.501 | 54813.618 | 9478.006 | 22845.6164 | 34088.0885 | 1191.6333 | 0 | 0 | 0 | 701132.7566 | 0 | 701132.3525 | 0.40411 | 49400.9052 | 0 | 2619.0366 | 3008.0771 | 327.3037 | 13913.831 | 1854.285 | 2057.4705 | 355.7641 | 857.5274 | 1279.5221 | 44.7289 | 0 | 0 | 0 | 26317.5464 | 0 | 26317.5312 | 0.015169 | 1854.3002 | 6.0332 | 0.65646 | 27.9065 | 4.1266 | 0.71354 | 0.089711 | 5.2529 | 0 | 0 | 2.5663 | 0 | 52.7841 | 52.7842 | 3.0423e-05
NE_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 1158393.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563458.3215 | 0 | 0 | 1721851.971 | 0 | 1721851.971 | 0 | 0 | 5878.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2859.551 | 0 | 0 | 8738.3988 | 0 | 8738.3988 | 0 | 0 | 1158.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.4583 | 0 | 0 | 1721.852 | 0 | 1721.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3233 | 1.1301 | 0 | 0 | 3.4535 | 3.4535 | 0
NE_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 719123.6216 | 717484.2673 | 95927.2361 | 4077910.5986 | 543387.6147 | 584602.0943 | 100392.3928 | 226175.3279 | 374814.7526 | 11631.0801 | 0 | 0 | 0 | 7451448.9861 | 0 | 7451443.9847 | 5.0014 | 543392.6161 | 0 | 65368.3372 | 65219.3199 | 8719.7858 | 370682.0734 | 49393.9342 | 53140.3304 | 9125.6685 | 20559.3373 | 34070.661 | 1057.2652 | 0 | 0 | 0 | 677336.7128 | 0 | 677336.2582 | 0.45463 | 49394.3888 | 0 | 2453.6498 | 2448.0563 | 327.3037 | 13913.831 | 1854.0385 | 1994.6623 | 342.5388 | 771.7102 | 1278.8679 | 39.6852 | 0 | 0 | 0 | 25424.3439 | 0 | 25424.3269 | 0.017065 | 1854.0556 | 4.91 | 0.65646 | 27.9065 | 4.0006 | 0.68702 | 0.079595 | 4.9212 | 0 | 0 | 2.565 | 0 | 50.9927 | 50.9927 | 3.4226e-05
NE_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 1104320.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563278.2362 | 0 | 0 | 1667598.9191 | 0 | 1667598.9191 | 0 | 0 | 5604.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2858.637 | 0 | 0 | 8463.0645 | 0 | 8463.0645 | 0 | 0 | 1104.3207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.2782 | 0 | 0 | 1667.5989 | 0 | 1667.5989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2149 | 1.1297 | 0 | 0 | 3.3446 | 3.3446 | 0
NE_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 33548.4141 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22461.9331 | 0 | 0 | 0 | 0 | 113001.5284 | 0 | 0 | 346595.6294 | 0 | 346594.518 | 1.1114 | 1.1114 | 0 | 3049.5508 | 2579.2623 | 654.9184 | 12908.1825 | 0 | 2041.7897 | 0 | 0 | 0 | 0 | 10271.8389 | 0 | 0 | 31505.5427 | 0 | 31505.4417 | 0.10103 | 0.10103 | 0 | 114.4672 | 96.8146 | 24.5829 | 484.5184 | 0 | 76.6401 | 0 | 0 | 0 | 0 | 385.5612 | 0 | 0 | 1182.5843 | 0 | 1182.5805 | 0.0037922 | 0.0037922 | 2.8693 | 0.72858 | 14.3599 | 2.2714 | 0 | 0 | 3.3925 | 0 | 11.4271 | 0 | 0 | 35.0488 | 35.0489 | 0.00011239
NE_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 146797.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146797.9155 | 0 | 146797.9155 | 0 | 0 | 744.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744.9994 | 0 | 744.9994 | 0 | 0 | 146.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.7979 | 0 | 146.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3507 | 0 | 0 | 0 | 4.3507 | 4.3507 | 0
NE_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 32839.8796 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 22067.3766 | 0 | 0 | 0 | 0 | 113029.3141 | 0 | 0 | 340327.183 | 0 | 340328.2944 | -1.1114 | -1.1114 | 0 | 2985.1451 | 2107.2058 | 654.9184 | 12908.1825 | 0 | 2005.9245 | 0 | 0 | 0 | 0 | 10274.3646 | 0 | 0 | 30935.7409 | 0 | 30935.842 | -0.10103 | -0.10103 | 0 | 112.0497 | 79.0956 | 24.5829 | 484.5184 | 0 | 75.2939 | 0 | 0 | 0 | 0 | 385.656 | 0 | 0 | 1161.1963 | 0 | 1161.2001 | -0.0037922 | -0.0037922 | 2.3442 | 0.72858 | 14.3599 | 2.2315 | 0 | 0 | 3.3209 | 0 | 11.4299 | 0 | 0 | 34.4151 | 34.415 | -0.00011239
NE_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 162920.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162920.2848 | 0 | 162920.2848 | 0 | 0 | 826.8204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826.8204 | 0 | 826.8204 | 0 | 0 | 162.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.9203 | 0 | 162.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8286 | 0 | 0 | 0 | 4.8286 | 4.8286 | 0
NE_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 128639.3017 | 97363.7551 | 7118.6878 | 317887.4784 | 4818.0346 | 100436.8499 | 941.9341 | 0 | 0 | 18474.6899 | 7179.8163 | 17655.0127 | 0 | 700515.5606 | 0 | 700514.727 | 0.83357 | 4818.8682 | 0 | 11693.3125 | 8850.3653 | 647.0887 | 28895.9718 | 437.9593 | 9129.7097 | 85.6218 | 0 | 0 | 1679.3493 | 652.6453 | 1604.8407 | 0 | 63676.8645 | 0 | 63676.7887 | 0.075772 | 438.0351 | 0 | 438.9173 | 332.2051 | 24.289 | 1084.6321 | 16.4391 | 342.6905 | 3.2139 | 0 | 0 | 63.0356 | 24.4975 | 60.2389 | 0 | 2390.1591 | 0 | 2390.1562 | 0.0028441 | 16.442 | 4.4917 | 0.32841 | 14.6653 | 4.6335 | 0.043455 | 0.85231 | 5.9346 | 0 | 0.33123 | 0 | 0.81449 | 32.3173 | 32.3174 | 3.8456e-05
NE_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 529602.294 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118505.5745 | 0 | 0 | 990298.2833 | 0 | 990298.2833 | 0 | 0 | 2687.7316 | 0 | 0 | 0 | 1736.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 601.4158 | 0 | 0 | 5025.7638 | 0 | 5025.7638 | 0 | 0 | 529.6023 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.5056 | 0 | 0 | 990.2983 | 0 | 990.2983 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.1608 | 1.6023 | 0 | 0 | 13.3898 | 13.3898 | 0
NE_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 122001.3059 | 79114.1291 | 7118.6878 | 312483.1662 | 4743.0133 | 83398.679 | 650.1846 | 0 | 0 | 22745.3469 | 7179.8163 | 12495.2144 | 0 | 651929.5436 | 0 | 651933.9893 | -4.4457 | 4738.5676 | 0 | 11089.9187 | 7191.4743 | 647.0887 | 28404.7198 | 431.1399 | 7580.9399 | 59.1018 | 0 | 0 | 2067.552 | 652.6453 | 1135.815 | 0 | 59260.3955 | 0 | 59260.7996 | -0.40411 | 430.7358 | 0 | 416.2685 | 269.9374 | 24.289 | 1066.1926 | 16.1832 | 284.5563 | 2.2184 | 0 | 0 | 77.6071 | 24.4975 | 42.6337 | 0 | 2224.3836 | 0 | 2224.3988 | -0.015169 | 16.168 | 3.6498 | 0.32841 | 14.416 | 3.8475 | 0.029995 | 1.0493 | 5.6284 | 0 | 0.33123 | 0 | 0.57645 | 30.0761 | 30.0759 | -0.0002051
NE_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 508210.0616 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118240.1857 | 0 | 0 | 968640.6621 | 0 | 968640.6621 | 0 | 0 | 2579.1661 | 0 | 0 | 0 | 1736.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 600.0689 | 0 | 0 | 4915.8514 | 0 | 4915.8514 | 0 | 0 | 508.2101 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.2402 | 0 | 0 | 968.6407 | 0 | 968.6407 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.8715 | 1.5987 | 0 | 0 | 13.097 | 13.097 | 0
NE_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 48724.9453 | 84696.2696 | 10683.5889 | 53987.5506 | 0 | 42987.2051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241079.5596 | 0 | 241077.6146 | 1.945 | 1.945 | 0 | 4429.0975 | 7698.8909 | 971.1382 | 4907.4684 | 0 | 3907.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21914.132 | 0 | 21913.9552 | 0.1768 | 0.1768 | 0 | 166.2495 | 288.9837 | 36.4524 | 184.2055 | 0 | 146.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822.5635 | 0 | 822.5568 | 0.0066363 | 0.0066363 | 11.7035 | 1.4763 | 7.4601 | 5.9401 | 0 | 0 | 6.7329 | 0 | 0 | 0 | 0 | 33.3127 | 33.313 | 0.00026876
NE_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 479680.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90260.6243 | 0 | 0 | 569941.3906 | 0 | 569941.3906 | 0 | 0 | 2434.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.0727 | 0 | 0 | 2892.4526 | 0 | 2892.4526 | 0 | 0 | 479.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2606 | 0 | 0 | 569.9414 | 0 | 569.9414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4266 | 3.6555 | 0 | 0 | 23.082 | 23.082 | 0
NE_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 0 | 45849.1288 | 67035.6998 | 10683.5889 | 53987.5506 | 0 | 41067.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218623.1837 | 0 | 218622.9058 | 0.27786 | 0.27786 | 0 | 4167.6858 | 6093.5451 | 971.1382 | 4907.4684 | 0 | 3733.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19872.8474 | 0 | 19872.8221 | 0.025257 | 0.025257 | 0 | 156.4372 | 228.7258 | 36.4524 | 184.2055 | 0 | 140.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745.9423 | 0 | 745.9414 | 0.00094805 | 0.00094805 | 9.2632 | 1.4763 | 7.4601 | 5.6748 | 0 | 0 | 6.3355 | 0 | 0 | 0 | 0 | 30.2098 | 30.2099 | 3.8395e-05
NE_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 506835.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90279.5807 | 0 | 0 | 597115.3074 | 0 | 597115.3074 | 0 | 0 | 2572.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.1689 | 0 | 0 | 3030.3602 | 0 | 3030.3602 | 0 | 0 | 506.8357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2796 | 0 | 0 | 597.1153 | 0 | 597.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5263 | 3.6562 | 0 | 0 | 24.1825 | 24.1825 | 0
NE_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 36938.2655 | 77849.8813 | 79283.6217 | 12306.2718 | 154949.5496 | 0 | 46424.2921 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 407824.1248 | 0 | 407823.8469 | 0.27786 | 0.27786 | 3357.6883 | 7076.5542 | 7206.8812 | 1118.6401 | 14084.9141 | 0 | 4219.9682 | 6.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 37071.2129 | 0 | 37071.1877 | 0.025257 | 0.025257 | 126.0334 | 265.6238 | 270.5157 | 41.989 | 528.6879 | 0 | 158.3997 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.4959 | 0 | 1391.495 | 0.00094805 | 0.00094805 | 6.2616 | 0.97192 | 12.2376 | 3.6665 | 0.0057056 | 0 | 6.1484 | 2.9173 | 0 | 0 | 0 | 32.209 | 32.2091 | 2.1945e-05
NE_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 83085.6487 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 587333.8348 | 0 | 0 | 1069914.9214 | 0 | 1069914.9214 | 0 | 0 | 421.6597 | 0 | 0 | 0 | 2027.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 2980.7192 | 0 | 0 | 5429.8182 | 0 | 5429.8182 | 0 | 0 | 83.0856 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 587.3338 | 0 | 0 | 1069.9149 | 0 | 1069.9149 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.9232 | 13.5951 | 0 | 0 | 24.7654 | 24.7654 | 0
NE_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 41264.4938 | 73059.6323 | 50867.2203 | 12306.2718 | 154949.5496 | 0 | 43970.8177 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 376490.2283 | 0 | 376488.5612 | 1.6671 | 1.6671 | 3750.9425 | 6641.1206 | 4623.8303 | 1118.6401 | 14084.9141 | 0 | 3996.9473 | 6.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 34222.9618 | 0 | 34222.8102 | 0.15154 | 0.15154 | 140.7945 | 249.2795 | 173.559 | 41.989 | 528.6879 | 0 | 150.0284 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1284.5847 | 0 | 1284.579 | 0.0056883 | 0.0056883 | 4.0174 | 0.97192 | 12.2376 | 3.4727 | 0.0057056 | 0 | 5.7701 | 3.259 | 0 | 0 | 0 | 29.7342 | 29.7344 | 0.00013167
NE_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 81246.8835 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 587400.1819 | 0 | 0 | 1068142.5034 | 0 | 1068142.5034 | 0 | 0 | 412.3279 | 0 | 0 | 0 | 2027.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 2981.0559 | 0 | 0 | 5420.8232 | 0 | 5420.8232 | 0 | 0 | 81.2469 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4002 | 0 | 0 | 1068.1425 | 0 | 1068.1425 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.8806 | 13.5966 | 0 | 0 | 24.7244 | 24.7244 | 0
NE_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 4001.136 | 4945.8487 | 8852.5135 | 1589.3401 | 13417.6985 | 0 | 5218.1482 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43028.8836 | 0 | 43030.2729 | -1.3893 | -1.3893 | 363.7033 | 449.5776 | 804.6935 | 144.471 | 1219.6688 | 0 | 474.3297 | 0 | 0 | 0 | 0 | 454.8817 | 0 | 0 | 3911.3255 | 0 | 3911.4518 | -0.12629 | -0.12629 | 13.6519 | 16.8752 | 30.2048 | 5.4228 | 45.7812 | 0 | 17.8043 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.8146 | 0 | 146.8193 | -0.0047402 | -0.0047402 | 5.4898 | 0.98561 | 8.3208 | 3.236 | 0 | 0 | 3.0671 | 2.4813 | 3.1033 | 0 | 0 | 26.6847 | 26.6839 | -0.00086155
NE_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 9753.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9753.0382 | 0 | 9753.0382 | 0 | 0 | 49.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4967 | 0 | 49.4967 | 0 | 0 | 9.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.753 | 0 | 9.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7726 | 0 | 0 | 0 | 1.7726 | 1.7726 | 0
NE_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Electricity | 4051.1502 | 4704.1134 | 7132.5807 | 1589.3401 | 13417.6985 | 0 | 4798.5847 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40697.6662 | 0 | 40700.4448 | -2.7786 | -2.7786 | 368.2496 | 427.6039 | 648.3516 | 144.471 | 1219.6688 | 0 | 436.1913 | 0 | 0 | 0 | 0 | 454.8817 | 0 | 0 | 3699.4179 | 0 | 3699.6704 | -0.25257 | -0.25257 | 13.8225 | 16.0504 | 24.3364 | 5.4228 | 45.7812 | 0 | 16.3728 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8604 | 0 | 138.8699 | -0.0094805 | -0.0094805 | 4.4232 | 0.98561 | 8.3208 | 2.9758 | 0 | 0 | 2.9172 | 2.5123 | 3.1033 | 0 | 0 | 25.2399 | 25.2382 | -0.0017231
NE_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | NE-OMAHA-NE | Zone5A | Zone5A(NE-OMAHA-NE) |  |  | NE | 0.0909 | 0.005075 |  |  |  | Natural Gas | 10094.2523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10094.2523 | 0 | 10094.2523 | 0 | 0 | 51.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.2283 | 0 | 51.2283 | 0 | 0 | 10.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0943 | 0 | 10.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8347 | 0 | 0 | 0 | 1.8347 | 1.8347 | 0
NH_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 528052.7052 | 882995.1489 | 96268.9998 | 4077910.5986 | 543459.8574 | 577902.97 | 78689.0084 | 179848.2857 | 400652.6442 | 10844.7458 | 0 | 0 | 0 | 7376624.964 | 0 | 7376622.1854 | 2.7786 | 543462.636 | 0 | 81320.1166 | 135981.2529 | 14825.426 | 627998.2322 | 83692.818 | 88997.0574 | 12118.1073 | 27696.636 | 61700.5072 | 1670.0908 | 0 | 0 | 0 | 1136000.2444 | 0 | 1135999.8165 | 0.4279 | 83693.2459 | 0 | 1801.7158 | 3012.7794 | 328.4698 | 13913.831 | 1854.285 | 1971.8049 | 268.4869 | 613.6424 | 1367.0268 | 37.0023 | 0 | 0 | 0 | 25169.0444 | 0 | 25169.0349 | 0.0094805 | 1854.2945 | 6.0426 | 0.6588 | 27.9065 | 3.9548 | 0.53849 | 0.074214 | 3.6136 | 0 | 0 | 2.7418 | 0 | 50.4806 | 50.4806 | 1.9015e-05
NH_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 857679.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578376.963 | 0 | 0 | 1436056.6749 | 0 | 1436056.6749 | 0 | 0 | 9606.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6477.822 | 0 | 0 | 16083.8348 | 0 | 16083.8348 | 0 | 0 | 857.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.377 | 0 | 0 | 1436.0567 | 0 | 1436.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7202 | 1.16 | 0 | 0 | 2.8802 | 2.8802 | 0
NH_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 493259.4932 | 718804.0865 | 96268.9998 | 4077910.5986 | 543387.6147 | 560650.8495 | 75449.1997 | 161437.5028 | 400402.5732 | 10475.1964 | 0 | 0 | 0 | 7138046.1143 | 0 | 7138045.5586 | 0.55571 | 543388.1704 | 0 | 75961.9619 | 110695.8293 | 14825.426 | 627998.2322 | 83681.6927 | 86340.2308 | 11619.1768 | 24861.3754 | 61661.9963 | 1613.1802 | 0 | 0 | 0 | 1099259.1016 | 0 | 1099259.016 | 0.08558 | 83681.7782 | 0 | 1683.0014 | 2452.5595 | 328.4698 | 13913.831 | 1854.0385 | 1912.9407 | 257.4327 | 550.8248 | 1366.1736 | 35.7414 | 0 | 0 | 0 | 24355.0133 | 0 | 24355.0114 | 0.0018961 | 1854.0404 | 4.919 | 0.6588 | 27.9065 | 3.8367 | 0.51632 | 0.071685 | 3.3755 | 0 | 0 | 2.7401 | 0 | 48.848 | 48.848 | 3.8029e-06
NH_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 803587.7888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578519.1355 | 0 | 0 | 1382106.9244 | 0 | 1382106.9244 | 0 | 0 | 9000.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6479.4143 | 0 | 0 | 15479.5976 | 0 | 15479.5976 | 0 | 0 | 803.5878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578.5191 | 0 | 0 | 1382.1069 | 0 | 1382.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6117 | 1.1603 | 0 | 0 | 2.772 | 2.772 | 0
NH_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 23490.0027 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20094.5942 | 0 | 0 | 0 | 0 | 115913.4663 | 0 | 0 | 337081.8171 | 0 | 337082.6506 | -0.83357 | -0.83357 | 0 | 3617.4604 | 4369.7073 | 1109.5428 | 21868.6479 | 0 | 3094.5675 | 0 | 0 | 0 | 0 | 17850.6738 | 0 | 0 | 51910.5998 | 0 | 51910.7282 | -0.12837 | -0.12837 | 0 | 80.1479 | 96.8146 | 24.5829 | 484.5184 | 0 | 68.5628 | 0 | 0 | 0 | 0 | 395.4967 | 0 | 0 | 1150.1232 | 0 | 1150.126 | -0.0028441 | -0.0028441 | 2.8693 | 0.72858 | 14.3599 | 2.032 | 0 | 0 | 2.3754 | 0 | 11.7215 | 0 | 0 | 34.0869 | 34.0868 | -8.4293e-05
NH_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 98961.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98961.5855 | 0 | 98961.5855 | 0 | 0 | 1108.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108.3698 | 0 | 1108.3698 | 0 | 0 | 98.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9616 | 0 | 98.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.933 | 0 | 0 | 0 | 2.933 | 2.933 | 0
NH_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 22209.0835 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19449.9668 | 0 | 0 | 0 | 0 | 115955.1448 | 0 | 0 | 330004.8077 | 0 | 330003.9742 | 0.83357 | 0.83357 | 0 | 3420.1989 | 3569.9636 | 1109.5428 | 21868.6479 | 0 | 2995.2949 | 0 | 0 | 0 | 0 | 17857.0923 | 0 | 0 | 50820.7404 | 0 | 50820.612 | 0.12837 | 0.12837 | 0 | 75.7774 | 79.0956 | 24.5829 | 484.5184 | 0 | 66.3633 | 0 | 0 | 0 | 0 | 395.639 | 0 | 0 | 1125.9764 | 0 | 1125.9736 | 0.0028441 | 0.0028441 | 2.3442 | 0.72858 | 14.3599 | 1.9668 | 0 | 0 | 2.2459 | 0 | 11.7258 | 0 | 0 | 33.3711 | 33.3712 | 8.4293e-05
NH_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 114278.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114278.3102 | 0 | 114278.3102 | 0 | 0 | 1279.9171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1279.9171 | 0 | 1279.9171 | 0 | 0 | 114.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2783 | 0 | 114.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3869 | 0 | 0 | 0 | 3.3869 | 3.3869 | 0
NH_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 74329.4373 | 99522.7014 | 7163.1449 | 317887.4784 | 4818.0346 | 91234.237 | 814.12 | 0 | 0 | 19344.3812 | 7179.8163 | 17616.1128 | 0 | 639909.4641 | 0 | 639911.1312 | -1.6671 | 4816.3675 | 0 | 11446.7333 | 15326.496 | 1103.1243 | 48954.6717 | 741.9773 | 14050.0725 | 125.3745 | 0 | 0 | 2979.0347 | 1105.6917 | 2712.8814 | 0 | 98546.0575 | 0 | 98546.3142 | -0.25674 | 741.7206 | 0 | 253.612 | 339.5715 | 24.4407 | 1084.6321 | 16.4391 | 311.2912 | 2.7778 | 0 | 0 | 66.003 | 24.4975 | 60.1062 | 0 | 2183.3711 | 0 | 2183.3768 | -0.0056883 | 16.4334 | 4.5913 | 0.33046 | 14.6653 | 4.209 | 0.037558 | 0.89243 | 3.4291 | 0 | 0.33123 | 0 | 0.8127 | 29.5214 | 29.5214 | -7.6911e-05
NH_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 449653.9199 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 121093.1153 | 0 | 0 | 912937.45 | 0 | 912937.45 | 0 | 0 | 5036.1239 | 0 | 0 | 0 | 3832.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 1356.2429 | 0 | 0 | 10224.8994 | 0 | 10224.8994 | 0 | 0 | 449.6539 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0931 | 0 | 0 | 912.9374 | 0 | 912.9374 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.0798 | 1.6373 | 0 | 0 | 12.3438 | 12.3438 | 0
NH_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 70197.7087 | 81095.2472 | 7163.1449 | 312483.1662 | 4745.7919 | 77944.3526 | 561.2705 | 0 | 0 | 22759.2397 | 7179.8163 | 12486.8787 | 0 | 596616.6166 | 0 | 596614.3938 | 2.2229 | 4748.0147 | 0 | 10810.4471 | 12488.6681 | 1103.1243 | 48122.4076 | 730.852 | 12003.4303 | 86.4357 | 0 | 0 | 3504.9229 | 1105.6917 | 1922.9793 | 0 | 91878.959 | 0 | 91878.6166 | 0.34232 | 731.1943 | 0 | 239.5146 | 276.697 | 24.4407 | 1066.1926 | 16.1926 | 265.9461 | 1.9151 | 0 | 0 | 77.6545 | 24.4975 | 42.6052 | 0 | 2035.6559 | 0 | 2035.6483 | 0.0075844 | 16.2002 | 3.7412 | 0.33046 | 14.416 | 3.5959 | 0.025893 | 1.05 | 3.2385 | 0 | 0.33123 | 0 | 0.57607 | 27.524 | 27.5241 | 0.00010255
NH_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 428299.6002 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120789.8138 | 0 | 0 | 891279.8288 | 0 | 891279.8288 | 0 | 0 | 4796.9555 | 0 | 0 | 0 | 3832.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 1352.8459 | 0 | 0 | 9982.3341 | 0 | 9982.3341 | 0 | 0 | 428.2996 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7898 | 0 | 0 | 891.2798 | 0 | 891.2798 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.791 | 1.6332 | 0 | 0 | 12.051 | 12.051 | 0
NH_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 27338.3176 | 85849.3748 | 10805.8458 | 53987.5506 | 0 | 42992.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220973.8511 | 0 | 220970.239 | 3.6121 | 3.6121 | 0 | 4210.1009 | 13220.8037 | 1664.1003 | 8314.0828 | 0 | 6620.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34029.9731 | 0 | 34029.4168 | 0.55627 | 0.55627 | 0 | 93.2783 | 292.9181 | 36.8695 | 184.2055 | 0 | 146.6913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.9628 | 0 | 753.9505 | 0.012325 | 0.012325 | 11.8629 | 1.4932 | 7.4601 | 5.9408 | 0 | 0 | 3.7777 | 0 | 0 | 0 | 0 | 30.5342 | 30.5347 | 0.00049913
NH_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 446611.4269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91170.5288 | 0 | 0 | 537781.9557 | 0 | 537781.9557 | 0 | 0 | 5002.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.1099 | 0 | 0 | 6023.1579 | 0 | 6023.1579 | 0 | 0 | 446.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1705 | 0 | 0 | 537.782 | 0 | 537.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0873 | 3.6923 | 0 | 0 | 21.7796 | 21.7796 | 0
NH_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 25440.5565 | 68044.3195 | 10805.8458 | 53987.5506 | 0 | 41153.3511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199431.6236 | 0 | 199431.3458 | 0.27786 | 0.27786 | 0 | 3917.8457 | 10478.8252 | 1664.1003 | 8314.0828 | 0 | 6337.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30712.47 | 0 | 30712.4272 | 0.04279 | 0.04279 | 0 | 86.8032 | 232.1672 | 36.8695 | 184.2055 | 0 | 140.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680.4607 | 0 | 680.4598 | 0.00094805 | 0.00094805 | 9.4025 | 1.4932 | 7.4601 | 5.6867 | 0 | 0 | 3.5154 | 0 | 0 | 0 | 0 | 27.5579 | 27.5579 | 3.8395e-05
NH_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 478837.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91180.0069 | 0 | 0 | 570017.216 | 0 | 570017.216 | 0 | 0 | 5362.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.2161 | 0 | 0 | 6384.1928 | 0 | 6384.1928 | 0 | 0 | 478.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.18 | 0 | 0 | 570.0172 | 0 | 570.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.3924 | 3.6927 | 0 | 0 | 23.0851 | 23.0851 | 0
NH_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 31108.8326 | 61203.4883 | 79400.3215 | 12306.2718 | 154949.5496 | 0 | 45243.4013 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 384284.1079 | 0 | 384286.3307 | -2.2229 | -2.2229 | 4790.7602 | 9425.3372 | 12227.6495 | 1895.1659 | 23862.2306 | 0 | 6967.4838 | 11.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 59179.7526 | 0 | 59180.0949 | -0.34232 | -0.34232 | 106.1433 | 208.8263 | 270.9139 | 41.989 | 528.6879 | 0 | 154.3705 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.1774 | 0 | 1311.185 | -0.0075844 | -0.0075844 | 6.2709 | 0.97192 | 12.2376 | 3.5732 | 0.0057056 | 0 | 4.8337 | 2.4569 | 0 | 0 | 0 | 30.3501 | 30.3499 | -0.00017556
NH_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 81038.3638 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 604650.4535 | 0 | 0 | 1085184.2552 | 0 | 1085184.2552 | 0 | 0 | 907.6297 | 0 | 0 | 0 | 4474.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 6772.0851 | 0 | 0 | 12154.0637 | 0 | 12154.0637 | 0 | 0 | 81.0384 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 604.6505 | 0 | 0 | 1085.1843 | 0 | 1085.1843 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.8758 | 13.9959 | 0 | 0 | 25.1188 | 25.1188 | 0
NH_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 35329.4754 | 56841.1386 | 50953.3558 | 12306.2718 | 154949.5496 | 0 | 42845.4982 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 353297.5322 | 0 | 353296.9765 | 0.55571 | 0.55571 | 5440.7392 | 8753.5353 | 7846.8168 | 1895.1659 | 23862.2306 | 0 | 6598.2067 | 11.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 54407.82 | 0 | 54407.7344 | 0.08558 | 0.08558 | 120.5442 | 193.942 | 173.8529 | 41.989 | 528.6879 | 0 | 146.1888 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.4512 | 0 | 1205.4493 | 0.0018961 | 0.0018961 | 4.0242 | 0.97192 | 12.2376 | 3.3838 | 0.0057056 | 0 | 4.4892 | 2.7902 | 0 | 0 | 0 | 27.9026 | 27.9027 | 4.3889e-05
NH_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 79853.5924 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 604726.2789 | 0 | 0 | 1084075.3092 | 0 | 1084075.3092 | 0 | 0 | 894.3602 | 0 | 0 | 0 | 4474.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 6772.9343 | 0 | 0 | 12141.6435 | 0 | 12141.6435 | 0 | 0 | 79.8536 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 604.7263 | 0 | 0 | 1084.0753 | 0 | 1084.0753 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.8484 | 13.9976 | 0 | 0 | 25.0932 | 25.0932 | 0
NH_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 3270.373 | 2989.7378 | 8891.4134 | 1589.3401 | 13417.6985 | 0 | 4737.4562 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39900.2176 | 0 | 39901.6068 | -1.3893 | -1.3893 | 503.6374 | 460.4196 | 1369.2777 | 244.7584 | 2066.3256 | 0 | 729.5683 | 0 | 0 | 0 | 0 | 770.6466 | 0 | 0 | 6144.6335 | 0 | 6144.8475 | -0.21395 | -0.21395 | 11.1585 | 10.201 | 30.3375 | 5.4228 | 45.7812 | 0 | 16.1642 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.1395 | 0 | 136.1443 | -0.0047402 | -0.0047402 | 5.5139 | 0.98561 | 8.3208 | 2.9379 | 0 | 0 | 1.8541 | 2.0281 | 3.1033 | 0 | 0 | 24.7445 | 24.7436 | -0.00086155
NH_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 8179.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8179.6617 | 0 | 8179.6617 | 0 | 0 | 91.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6122 | 0 | 91.6122 | 0 | 0 | 8.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1797 | 0 | 8.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4867 | 0 | 0 | 0 | 1.4867 | 1.4867 | 0
NH_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 3331.5015 | 2803.5738 | 7160.3663 | 1589.3401 | 13417.6985 | 0 | 4337.3426 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37644.0214 | 0 | 37640.1314 | 3.89 | 3.89 | 513.0512 | 431.7504 | 1102.6964 | 244.7584 | 2066.3256 | 0 | 667.9508 | 0 | 0 | 0 | 0 | 770.6466 | 0 | 0 | 5797.1793 | 0 | 5796.5802 | 0.59906 | 0.59906 | 11.3671 | 9.5658 | 24.4312 | 5.4228 | 45.7812 | 0 | 14.799 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.4414 | 0 | 128.4281 | 0.013273 | 0.013273 | 4.4404 | 0.98561 | 8.3208 | 2.6898 | 0 | 0 | 1.7386 | 2.066 | 3.1033 | 0 | 0 | 23.3421 | 23.3445 | 0.0024123
NH_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | NH-MANCHESTER-NH | Zone5A | Zone5A(NH-MANCHESTER-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 8520.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8520.8759 | 0 | 8520.8759 | 0 | 0 | 95.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4338 | 0 | 95.4338 | 0 | 0 | 8.5209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5209 | 0 | 8.5209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5487 | 0 | 0 | 0 | 1.5487 | 1.5487 | 0
NH_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 495201.7113 | 883064.613 | 96288.4498 | 4077910.5986 | 543459.8574 | 586610.998 | 75407.5212 | 162015.4447 | 430483.3361 | 11347.6663 | 0 | 0 | 0 | 7361790.1964 | 0 | 7361787.6957 | 2.5007 | 543462.3581 | 0 | 76261.0635 | 135991.9504 | 14828.4213 | 627998.2322 | 83692.818 | 90338.0937 | 11612.7583 | 24950.3785 | 66294.4338 | 1747.5406 | 0 | 0 | 0 | 1133715.6903 | 0 | 1133715.3051 | 0.38511 | 83693.2032 | 0 | 1689.6282 | 3013.0165 | 328.5362 | 13913.831 | 1854.285 | 2001.5167 | 257.2905 | 552.7967 | 1468.8091 | 38.7182 | 0 | 0 | 0 | 25118.4282 | 0 | 25118.4196 | 0.0085324 | 1854.2936 | 6.0431 | 0.65893 | 27.9065 | 4.0144 | 0.51604 | 0.077656 | 3.3888 | 0 | 0 | 2.9459 | 0 | 50.3791 | 50.3791 | 1.7113e-05
NH_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 993710.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601418.3972 | 0 | 0 | 1595128.8221 | 0 | 1595128.8221 | 0 | 0 | 11129.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6735.886 | 0 | 0 | 17865.4428 | 0 | 17865.4428 | 0 | 0 | 993.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.4184 | 0 | 0 | 1595.1288 | 0 | 1595.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.993 | 1.2062 | 0 | 0 | 3.1993 | 3.1993 | 0
NH_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 460011.1642 | 719026.3718 | 96288.4498 | 4077910.5986 | 543387.6147 | 566724.7962 | 71386.9352 | 144716.0885 | 430358.3006 | 10675.2532 | 0 | 0 | 0 | 7120485.5729 | 0 | 7120483.3501 | 2.2229 | 543389.8375 | 0 | 70841.7193 | 110730.0613 | 14828.4213 | 627998.2322 | 83681.6927 | 87275.6186 | 10993.588 | 22286.2776 | 66275.1783 | 1643.989 | 0 | 0 | 0 | 1096554.7782 | 0 | 1096554.4359 | 0.34232 | 83682.035 | 0 | 1569.5581 | 2453.318 | 328.5362 | 13913.831 | 1854.0385 | 1933.665 | 243.5722 | 493.7713 | 1468.3825 | 36.424 | 0 | 0 | 0 | 24295.0968 | 0 | 24295.0892 | 0.0075844 | 1854.0461 | 4.9205 | 0.65893 | 27.9065 | 3.8783 | 0.48852 | 0.073054 | 3.148 | 0 | 0 | 2.9451 | 0 | 48.7278 | 48.7278 | 1.5212e-05
NH_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 951305.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601389.9626 | 0 | 0 | 1552695.0496 | 0 | 1552695.0496 | 0 | 0 | 10654.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6735.5676 | 0 | 0 | 17390.1846 | 0 | 17390.1846 | 0 | 0 | 951.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.39 | 0 | 0 | 1552.695 | 0 | 1552.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.908 | 1.2062 | 0 | 0 | 3.1142 | 3.1142 | 0
NH_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 21767.2914 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20033.4658 | 0 | 0 | 0 | 0 | 120373.0658 | 0 | 0 | 339754.7982 | 0 | 339753.4089 | 1.3893 | 1.3893 | 0 | 3352.1629 | 4369.7073 | 1109.1149 | 21868.6479 | 0 | 3085.1537 | 0 | 0 | 0 | 0 | 18537.4521 | 0 | 0 | 52322.2389 | 0 | 52322.025 | 0.21395 | 0.21395 | 0 | 74.27 | 96.8146 | 24.5734 | 484.5184 | 0 | 68.3542 | 0 | 0 | 0 | 0 | 410.7129 | 0 | 0 | 1159.2434 | 0 | 1159.2386 | 0.0047402 | 0.0047402 | 2.8693 | 0.72829 | 14.3599 | 2.0258 | 0 | 0 | 2.2012 | 0 | 12.1725 | 0 | 0 | 34.357 | 34.3571 | 0.00014049
NH_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 110288.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110288.0001 | 0 | 110288.0001 | 0 | 0 | 1235.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235.2256 | 0 | 1235.2256 | 0 | 0 | 110.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.288 | 0 | 110.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2687 | 0 | 0 | 0 | 3.2687 | 3.2687 | 0
NH_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 19847.3018 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 19152.6601 | 0 | 0 | 0 | 0 | 120423.08 | 0 | 0 | 331810.8761 | 0 | 331812.2654 | -1.3893 | -1.3893 | 0 | 3056.4845 | 3569.9636 | 1109.1149 | 21868.6479 | 0 | 2949.5097 | 0 | 0 | 0 | 0 | 18545.1543 | 0 | 0 | 51098.8749 | 0 | 51099.0889 | -0.21395 | -0.21395 | 0 | 67.719 | 79.0956 | 24.5734 | 484.5184 | 0 | 65.3489 | 0 | 0 | 0 | 0 | 410.8835 | 0 | 0 | 1132.1387 | 0 | 1132.1434 | -0.0047402 | -0.0047402 | 2.3442 | 0.72829 | 14.3599 | 1.9368 | 0 | 0 | 2.007 | 0 | 12.1776 | 0 | 0 | 33.5539 | 33.5538 | -0.00014049
NH_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 131187.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131187.3676 | 0 | 131187.3676 | 0 | 0 | 1469.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.2985 | 0 | 1469.2985 | 0 | 0 | 131.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.1874 | 0 | 131.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8881 | 0 | 0 | 0 | 3.8881 | 3.8881 | 0
NH_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 71431.3923 | 99042.0094 | 7157.5878 | 317887.4784 | 4818.0346 | 92217.8496 | 919.7056 | 0 | 0 | 21878.4341 | 7179.8163 | 17635.5627 | 0 | 640167.8708 | 0 | 640167.0372 | 0.83357 | 4818.8682 | 0 | 11000.4344 | 15252.4694 | 1102.2685 | 48954.6717 | 741.9773 | 14201.5488 | 141.6347 | 0 | 0 | 3369.2788 | 1105.6917 | 2715.8767 | 0 | 98585.8521 | 0 | 98585.7237 | 0.12837 | 742.1057 | 0 | 243.7239 | 337.9313 | 24.4217 | 1084.6321 | 16.4391 | 314.6473 | 3.138 | 0 | 0 | 74.6492 | 24.4975 | 60.1725 | 0 | 2184.2528 | 0 | 2184.2499 | 0.0028441 | 16.442 | 4.5692 | 0.33021 | 14.6653 | 4.2543 | 0.042429 | 1.0093 | 3.2954 | 0 | 0.33123 | 0 | 0.81359 | 29.5333 | 29.5333 | 3.8456e-05
NH_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 596812.006 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125472.0303 | 0 | 0 | 1064474.4511 | 0 | 1064474.4511 | 0 | 0 | 6684.2945 | 0 | 0 | 0 | 3832.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.2867 | 0 | 0 | 11922.1139 | 0 | 11922.1139 | 0 | 0 | 596.812 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.472 | 0 | 0 | 1064.4745 | 0 | 1064.4745 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.0695 | 1.6965 | 0 | 0 | 14.3928 | 14.3928 | 0
NH_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 66479.9864 | 81114.6972 | 7157.5878 | 312483.1662 | 4745.7919 | 78558.4158 | 747.4344 | 0 | 0 | 22773.1325 | 7179.8163 | 12489.6572 | 0 | 593729.6858 | 0 | 593731.6308 | -1.945 | 4743.8469 | 0 | 10237.9179 | 12491.6634 | 1102.2685 | 48122.4076 | 730.852 | 12097.996 | 115.1049 | 0 | 0 | 3507.0624 | 1105.6917 | 1923.4072 | 0 | 91434.3716 | 0 | 91434.6711 | -0.29953 | 730.5524 | 0 | 226.8297 | 276.7633 | 24.4217 | 1066.1926 | 16.1926 | 268.0413 | 2.5502 | 0 | 0 | 77.7019 | 24.4975 | 42.6147 | 0 | 2025.8057 | 0 | 2025.8123 | -0.0066363 | 16.186 | 3.7421 | 0.33021 | 14.416 | 3.6242 | 0.034482 | 1.0506 | 3.067 | 0 | 0.33123 | 0 | 0.57619 | 27.391 | 27.3909 | -8.973e-05
NH_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 578168.4432 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125244.5542 | 0 | 0 | 1045603.4123 | 0 | 1045603.4123 | 0 | 0 | 6475.4866 | 0 | 0 | 0 | 3832.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.739 | 0 | 0 | 11710.7582 | 0 | 11710.7582 | 0 | 0 | 578.1684 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.2446 | 0 | 0 | 1045.6034 | 0 | 1045.6034 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.8174 | 1.6934 | 0 | 0 | 14.1376 | 14.1376 | 0
NH_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 23790.0879 | 90767.4378 | 10794.7316 | 53987.5506 | 0 | 43698.5182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223038.3262 | 0 | 223035.5476 | 2.7786 | 2.7786 | 0 | 3663.6735 | 13978.1854 | 1662.3887 | 8314.0828 | 0 | 6729.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34347.9022 | 0 | 34347.4743 | 0.4279 | 0.4279 | 0 | 81.1718 | 309.6985 | 36.8316 | 184.2055 | 0 | 149.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761.0068 | 0 | 760.9973 | 0.0094805 | 0.0094805 | 12.5425 | 1.4916 | 7.4601 | 6.0384 | 0 | 0 | 3.2874 | 0 | 0 | 0 | 0 | 30.8196 | 30.82 | 0.00038395
NH_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 540445.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92506.9509 | 0 | 0 | 632952.2727 | 0 | 632952.2727 | 0 | 0 | 6052.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.0779 | 0 | 0 | 7089.0655 | 0 | 7089.0655 | 0 | 0 | 540.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.507 | 0 | 0 | 632.9523 | 0 | 632.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.8875 | 3.7464 | 0 | 0 | 25.6339 | 25.6339 | 0
NH_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 0 | 22339.6761 | 75132.4431 | 10794.7316 | 53987.5506 | 0 | 41786.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204041.2658 | 0 | 204039.3208 | 1.945 | 1.945 | 0 | 3440.3101 | 11570.3962 | 1662.3887 | 8314.0828 | 0 | 6435.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31422.3549 | 0 | 31422.0554 | 0.29953 | 0.29953 | 0 | 76.223 | 256.3519 | 36.8316 | 184.2055 | 0 | 142.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.1888 | 0 | 696.1822 | 0.0066363 | 0.0066363 | 10.382 | 1.4916 | 7.4601 | 5.7742 | 0 | 0 | 3.087 | 0 | 0 | 0 | 0 | 28.1946 | 28.1949 | 0.00026876
NH_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 572254.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92525.9073 | 0 | 0 | 664779.9716 | 0 | 664779.9716 | 0 | 0 | 6409.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.2902 | 0 | 0 | 7445.5357 | 0 | 7445.5357 | 0 | 0 | 572.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5259 | 0 | 0 | 664.78 | 0 | 664.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1757 | 3.7472 | 0 | 0 | 26.9229 | 26.9229 | 0
NH_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 37960.778 | 55901.9831 | 79353.0859 | 12300.7147 | 154949.5496 | 0 | 45201.7228 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 385740.0768 | 0 | 385739.2432 | 0.83357 | 0.83357 | 5845.9598 | 8608.9054 | 12220.3752 | 1894.3101 | 23862.2306 | 0 | 6961.0653 | 11.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 59403.9718 | 0 | 59403.8435 | 0.12837 | 0.12837 | 129.5222 | 190.7376 | 270.7527 | 41.97 | 528.6879 | 0 | 154.2283 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1316.1451 | 0 | 1316.1423 | 0.0028441 | 0.0028441 | 6.2671 | 0.97148 | 12.2376 | 3.5699 | 0.0057056 | 0 | 4.415 | 2.9981 | 0 | 0 | 0 | 30.4648 | 30.4649 | 6.5834e-05
NH_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 100743.4817 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 630914.4659 | 0 | 0 | 1131153.3855 | 0 | 1131153.3855 | 0 | 0 | 1128.327 | 0 | 0 | 0 | 4474.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 7066.242 | 0 | 0 | 12668.9179 | 0 | 12668.9179 | 0 | 0 | 100.7435 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 630.9145 | 0 | 0 | 1131.1534 | 0 | 1131.1534 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.3319 | 14.6038 | 0 | 0 | 26.1829 | 26.1829 | 0
NH_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 43037.2193 | 51467.3907 | 50981.1415 | 12300.7147 | 154949.5496 | 0 | 42751.027 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 355559.2855 | 0 | 355559.0077 | 0.27786 | 0.27786 | 6627.7318 | 7925.9782 | 7851.0958 | 1894.3101 | 23862.2306 | 0 | 6583.6582 | 11.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 54756.13 | 0 | 54756.0872 | 0.04279 | 0.04279 | 146.843 | 175.6067 | 173.9477 | 41.97 | 528.6879 | 0 | 145.8665 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.1683 | 0 | 1213.1673 | 0.00094805 | 0.00094805 | 4.0264 | 0.97148 | 12.2376 | 3.3764 | 0.0057056 | 0 | 4.0648 | 3.399 | 0 | 0 | 0 | 28.0813 | 28.0813 | 2.1945e-05
NH_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 98800.4566 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 630961.8568 | 0 | 0 | 1129257.7513 | 0 | 1129257.7513 | 0 | 0 | 1106.5651 | 0 | 0 | 0 | 4474.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 7066.7728 | 0 | 0 | 12647.6868 | 0 | 12647.6868 | 0 | 0 | 98.8005 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 630.9619 | 0 | 0 | 1129.2578 | 0 | 1129.2578 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.2869 | 14.6049 | 0 | 0 | 26.139 | 26.139 | 0
NH_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 3995.5789 | 2709.1025 | 8858.0706 | 1589.3401 | 13417.6985 | 0 | 4818.0346 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40392.0239 | 0 | 40391.746 | 0.27786 | 0.27786 | 615.3191 | 417.2018 | 1364.1429 | 244.7584 | 2066.3256 | 0 | 741.9773 | 0 | 0 | 0 | 0 | 770.6466 | 0 | 0 | 6220.3717 | 0 | 6220.3289 | 0.04279 | 0.04279 | 13.6329 | 9.2435 | 30.2237 | 5.4228 | 45.7812 | 0 | 16.4391 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.8176 | 0 | 137.8166 | 0.00094805 | 0.00094805 | 5.4932 | 0.98561 | 8.3208 | 2.9878 | 0 | 0 | 1.68 | 2.4778 | 3.1033 | 0 | 0 | 25.0485 | 25.0486 | 0.00017231
NH_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 14776.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14776.4689 | 0 | 14776.4689 | 0 | 0 | 165.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.4965 | 0 | 165.4965 | 0 | 0 | 14.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7765 | 0 | 14.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6857 | 0 | 0 | 0 | 2.6857 | 2.6857 | 0
NH_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Electricity | 4106.7216 | 2470.1458 | 7160.3663 | 1589.3401 | 13417.6985 | 0 | 4354.014 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38102.4849 | 0 | 38099.7063 | 2.7786 | 2.7786 | 632.4351 | 380.4025 | 1102.6964 | 244.7584 | 2066.3256 | 0 | 670.5182 | 0 | 0 | 0 | 0 | 770.6466 | 0 | 0 | 5867.7827 | 0 | 5867.3548 | 0.4279 | 0.4279 | 14.0121 | 8.4281 | 24.4312 | 5.4228 | 45.7812 | 0 | 14.8559 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.0057 | 0 | 129.9962 | 0.0094805 | 0.0094805 | 4.4404 | 0.98561 | 8.3208 | 2.7001 | 0 | 0 | 1.5318 | 2.5467 | 3.1033 | 0 | 0 | 23.6271 | 23.6288 | 0.0017231
NH_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | NH-LEBANON-NH | Zone6A | Zone6A(NH-LEBANON-NH) |  |  | NH | 0.154 | 0.0112 |  |  |  | Natural Gas | 15563.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15563.1571 | 0 | 15563.1571 | 0 | 0 | 174.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.3074 | 0 | 174.3074 | 0 | 0 | 15.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5632 | 0 | 15.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8286 | 0 | 0 | 0 | 2.8286 | 2.8286 | 0
NJ_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 669904.0914 | 881489.1657 | 95629.9295 | 4077910.5986 | 543457.0788 | 576044.1089 | 95916.1219 | 237975.9006 | 356501.2196 | 13876.162 | 0 | 0 | 0 | 7548704.3772 | 0 | 7548703.2657 | 1.1114 | 543458.1903 | 0 | 83336.069 | 109657.2522 | 11896.3632 | 507292.0785 | 67606.0606 | 71659.8871 | 11931.9656 | 29604.202 | 44348.7517 | 1726.1946 | 0 | 0 | 0 | 939058.8245 | 0 | 939058.6863 | 0.13826 | 67606.1989 | 0 | 2285.7128 | 3007.641 | 326.2893 | 13913.831 | 1854.2756 | 1965.4625 | 327.2658 | 811.9738 | 1216.3822 | 47.3455 | 0 | 0 | 0 | 25756.1793 | 0 | 25756.1755 | 0.0037922 | 1854.2793 | 6.0323 | 0.65443 | 27.9065 | 3.9421 | 0.65639 | 0.094959 | 4.5844 | 0 | 0 | 2.4397 | 0 | 51.6582 | 51.6582 | 7.6059e-06
NJ_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 885905.7057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547544.4721 | 0 | 0 | 1433450.1778 | 0 | 1433450.1778 | 0 | 0 | 7584.2387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4687.5282 | 0 | 0 | 12271.767 | 0 | 12271.767 | 0 | 0 | 885.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.5445 | 0 | 0 | 1433.4502 | 0 | 1433.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7768 | 1.0982 | 0 | 0 | 2.875 | 2.875 | 0
NJ_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 627839.3704 | 717687.1027 | 95629.9295 | 4077910.5986 | 543387.6147 | 550759.1521 | 91995.5643 | 214235.8269 | 356292.8271 | 12486.8787 | 0 | 0 | 0 | 7288224.865 | 0 | 7288222.6421 | 2.2229 | 543389.8375 | 0 | 78103.2177 | 89280.2756 | 11896.3632 | 507292.0785 | 67597.4193 | 68514.4385 | 11444.2482 | 26650.9369 | 44322.8277 | 1553.3677 | 0 | 0 | 0 | 906655.1732 | 0 | 906654.8967 | 0.27652 | 67597.6958 | 0 | 2142.1879 | 2448.7484 | 326.2893 | 13913.831 | 1854.0385 | 1879.1902 | 313.8889 | 730.9726 | 1215.6711 | 42.6052 | 0 | 0 | 0 | 24867.4232 | 0 | 24867.4157 | 0.0075844 | 1854.0461 | 4.9114 | 0.65443 | 27.9065 | 3.769 | 0.62956 | 0.085452 | 4.2965 | 0 | 0 | 2.4382 | 0 | 49.8757 | 49.8757 | 1.5212e-05
NJ_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 814099.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547601.3411 | 0 | 0 | 1361700.4218 | 0 | 1361700.4218 | 0 | 0 | 6969.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4688.0151 | 0 | 0 | 11657.5173 | 0 | 11657.5173 | 0 | 0 | 814.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.6013 | 0 | 0 | 1361.7004 | 0 | 1361.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6328 | 1.0983 | 0 | 0 | 2.7311 | 2.7311 | 0
NJ_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 30180.7913 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 21353.285 | 0 | 0 | 0 | 0 | 109900.648 | 0 | 0 | 339018.4781 | 0 | 339017.3666 | 1.1114 | 1.1114 | 0 | 3754.4904 | 3529.8155 | 896.28 | 17665.3234 | 0 | 2656.3486 | 0 | 0 | 0 | 0 | 13671.6406 | 0 | 0 | 42173.8987 | 0 | 42173.7604 | 0.13826 | 0.13826 | 0 | 102.9769 | 96.8146 | 24.5829 | 484.5184 | 0 | 72.8574 | 0 | 0 | 0 | 0 | 374.981 | 0 | 0 | 1156.731 | 0 | 1156.7273 | 0.0037922 | 0.0037922 | 2.8693 | 0.72858 | 14.3599 | 2.1593 | 0 | 0 | 3.052 | 0 | 11.1135 | 0 | 0 | 34.2825 | 34.2827 | 0.00011239
NJ_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 103482.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103482.6732 | 0 | 103482.6732 | 0 | 0 | 885.9152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885.9152 | 0 | 885.9152 | 0 | 0 | 103.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4827 | 0 | 103.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.067 | 0 | 0 | 0 | 3.067 | 3.067 | 0
NJ_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 29174.9502 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20853.143 | 0 | 0 | 0 | 0 | 109928.4337 | 0 | 0 | 332347.1394 | 0 | 332349.3623 | -2.2229 | -2.2229 | 0 | 3629.3638 | 2883.7888 | 896.28 | 17665.3234 | 0 | 2594.131 | 0 | 0 | 0 | 0 | 13675.0971 | 0 | 0 | 41343.9841 | 0 | 41344.2607 | -0.27652 | -0.27652 | 0 | 99.5449 | 79.0956 | 24.5829 | 484.5184 | 0 | 71.1509 | 0 | 0 | 0 | 0 | 375.0758 | 0 | 0 | 1133.9684 | 0 | 1133.976 | -0.0075844 | -0.0075844 | 2.3442 | 0.72858 | 14.3599 | 2.1087 | 0 | 0 | 2.9503 | 0 | 11.1163 | 0 | 0 | 33.6083 | 33.608 | -0.00022478
NJ_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 118164.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118164.3604 | 0 | 118164.3604 | 0 | 0 | 1011.6051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1011.6051 | 0 | 1011.6051 | 0 | 0 | 118.1644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.1644 | 0 | 118.1644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5021 | 0 | 0 | 0 | 3.5021 | 3.5021 | 0
NJ_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 113615.5916 | 98172.318 | 7129.8021 | 317887.4784 | 4818.0346 | 91656.5792 | 836.3486 | 0 | 0 | 21528.3347 | 7179.8163 | 17613.3342 | 0 | 680437.6377 | 0 | 680439.3049 | -1.6671 | 4816.3675 | 0 | 14133.7796 | 12212.6364 | 886.9474 | 39545.2023 | 599.3635 | 11402.0784 | 104.0418 | 0 | 0 | 2678.1248 | 893.1691 | 2191.0988 | 0 | 84646.4421 | 0 | 84646.6495 | -0.20739 | 599.1561 | 0 | 387.6564 | 334.9639 | 24.3269 | 1084.6321 | 16.4391 | 312.7322 | 2.8536 | 0 | 0 | 73.4547 | 24.4975 | 60.0967 | 0 | 2321.6532 | 0 | 2321.6589 | -0.0056883 | 16.4334 | 4.529 | 0.32892 | 14.6653 | 4.2285 | 0.038584 | 0.99318 | 5.2415 | 0 | 0.33123 | 0 | 0.81257 | 31.3912 | 31.3911 | -7.6911e-05
NJ_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 376501.3946 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 115159.7801 | 0 | 0 | 833851.5895 | 0 | 833851.5895 | 0 | 0 | 3223.2284 | 0 | 0 | 0 | 2929.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 985.8829 | 0 | 0 | 7138.6035 | 0 | 7138.6035 | 0 | 0 | 376.5014 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 115.1598 | 0 | 0 | 833.8516 | 0 | 833.8516 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.0907 | 1.5571 | 0 | 0 | 11.2745 | 11.2745 | 0
NJ_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 108133.4796 | 79908.7992 | 7129.8021 | 312483.1662 | 4745.7919 | 79986.5991 | 466.7992 | 0 | 0 | 22742.5683 | 7179.8163 | 12486.8787 | 0 | 635263.7006 | 0 | 635265.0899 | -1.3893 | 4744.4026 | 0 | 13451.8049 | 9940.6546 | 886.9474 | 38872.9059 | 590.3765 | 9950.3329 | 58.0698 | 0 | 0 | 2829.1755 | 893.1691 | 1553.3677 | 0 | 79026.8044 | 0 | 79026.9772 | -0.17283 | 590.2037 | 0 | 368.9514 | 272.6488 | 24.3269 | 1066.1926 | 16.1926 | 272.9143 | 1.5927 | 0 | 0 | 77.5976 | 24.4975 | 42.6052 | 0 | 2167.5197 | 0 | 2167.5245 | -0.0047402 | 16.1879 | 3.6865 | 0.32892 | 14.416 | 3.6901 | 0.021535 | 1.0492 | 4.9886 | 0 | 0.33123 | 0 | 0.57607 | 29.3071 | 29.307 | -6.4093e-05
NJ_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 362928.6534 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114922.8258 | 0 | 0 | 820041.8941 | 0 | 820041.8941 | 0 | 0 | 3107.0322 | 0 | 0 | 0 | 2929.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 983.8543 | 0 | 0 | 7020.3787 | 0 | 7020.3787 | 0 | 0 | 362.9287 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.9228 | 0 | 0 | 820.0419 | 0 | 820.0419 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.9072 | 1.5539 | 0 | 0 | 11.0878 | 11.0878 | 0
NJ_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 41586.8075 | 83762.6712 | 10744.7174 | 53987.5506 | 0 | 40033.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230115.3355 | 0 | 230117.0026 | -1.6671 | -1.6671 | 0 | 5173.3989 | 10420.0763 | 1336.6428 | 6716.0513 | 0 | 4980.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28626.3477 | 0 | 28626.5551 | -0.20739 | -0.20739 | 0 | 141.8942 | 285.7982 | 36.661 | 184.2055 | 0 | 136.5946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785.1535 | 0 | 785.1592 | -0.0056883 | -0.0056883 | 11.5745 | 1.4847 | 7.4601 | 5.5319 | 0 | 0 | 5.7466 | 0 | 0 | 0 | 0 | 31.7981 | 31.7979 | -0.00023037
NJ_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 380889.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89331.7636 | 0 | 0 | 470221.5514 | 0 | 470221.5514 | 0 | 0 | 3260.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.7692 | 0 | 0 | 4025.5667 | 0 | 4025.5667 | 0 | 0 | 380.8898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3318 | 0 | 0 | 470.2216 | 0 | 470.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4256 | 3.6178 | 0 | 0 | 19.0435 | 19.0435 | 0
NJ_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 38872.1479 | 66335.501 | 10744.7174 | 53987.5506 | 0 | 41170.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211109.9394 | 0 | 211110.4951 | -0.55571 | -0.55571 | 0 | 4835.6952 | 8252.1363 | 1336.6428 | 6716.0513 | 0 | 5121.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26262.0765 | 0 | 26262.1456 | -0.069131 | -0.069131 | 0 | 132.6318 | 226.3367 | 36.661 | 184.2055 | 0 | 140.4721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3071 | 0 | 720.309 | -0.0018961 | -0.0018961 | 9.1664 | 1.4847 | 7.4601 | 5.689 | 0 | 0 | 5.3714 | 0 | 0 | 0 | 0 | 29.1718 | 29.1717 | -7.679e-05
NJ_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 401286.8123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89341.2417 | 0 | 0 | 490628.054 | 0 | 490628.054 | 0 | 0 | 3435.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.8504 | 0 | 0 | 4200.2668 | 0 | 4200.2668 | 0 | 0 | 401.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3412 | 0 | 0 | 490.6281 | 0 | 490.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2517 | 3.6182 | 0 | 0 | 19.8699 | 19.8699 | 0
NJ_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 27552.2672 | 74601.7369 | 79205.8218 | 12306.2718 | 154949.5496 | 0 | 45754.6576 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 394442.5477 | 0 | 394443.1034 | -0.55571 | -0.55571 | 3427.502 | 9280.4561 | 9853.2042 | 1530.9002 | 19275.724 | 0 | 5691.8794 | 8.987 | 0 | 0 | 0 | 0 | 0 | 0 | 49068.6529 | 0 | 49068.7221 | -0.069131 | -0.069131 | 94.0083 | 254.5411 | 270.2503 | 41.989 | 528.6879 | 0 | 156.1149 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.838 | 0 | 1345.8399 | -0.0018961 | -0.0018961 | 6.2555 | 0.97192 | 12.2376 | 3.6136 | 0.0057056 | 0 | 5.8919 | 2.176 | 0 | 0 | 0 | 31.1523 | 31.1522 | -4.3889e-05
NJ_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 64451.5642 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 569306.3531 | 0 | 0 | 1033253.3552 | 0 | 1033253.3552 | 0 | 0 | 551.7698 | 0 | 0 | 0 | 3420.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 4873.8317 | 0 | 0 | 8845.682 | 0 | 8845.682 | 0 | 0 | 64.4516 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 569.3064 | 0 | 0 | 1033.2534 | 0 | 1033.2534 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4919 | 13.1778 | 0 | 0 | 23.9168 | 23.9168 | 0
NJ_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 31400.5821 | 69817.045 | 50814.4275 | 12306.2718 | 154949.5496 | 0 | 43376.2045 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 362736.3233 | 0 | 362736.879 | -0.55571 | -0.55571 | 3906.2324 | 8685.2404 | 6321.3148 | 1530.9002 | 19275.724 | 0 | 5395.9998 | 8.987 | 0 | 0 | 0 | 0 | 0 | 0 | 45124.3986 | 0 | 45124.4677 | -0.069131 | -0.069131 | 107.1388 | 238.2158 | 173.3788 | 41.989 | 528.6879 | 0 | 147.9996 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.6563 | 0 | 1237.6582 | -0.0018961 | -0.0018961 | 4.0132 | 0.97192 | 12.2376 | 3.4258 | 0.0057056 | 0 | 5.514 | 2.4799 | 0 | 0 | 0 | 28.6482 | 28.6481 | -4.3889e-05
NJ_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 63484.7907 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 569353.744 | 0 | 0 | 1032333.9726 | 0 | 1032333.9726 | 0 | 0 | 543.4933 | 0 | 0 | 0 | 3420.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 4874.2374 | 0 | 0 | 8837.8111 | 0 | 8837.8111 | 0 | 0 | 63.4848 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 569.3537 | 0 | 0 | 1032.334 | 0 | 1032.334 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4695 | 13.1789 | 0 | 0 | 23.8955 | 23.8955 | 0
NJ_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 3237.0302 | 4629.0921 | 8841.3992 | 1581.0044 | 13417.6985 | 0 | 4893.0559 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41603.4789 | 0 | 41606.5354 | -3.0564 | -3.0564 | 402.6866 | 575.8591 | 1099.8701 | 196.677 | 1669.1617 | 0 | 608.6962 | 0 | 0 | 0 | 0 | 622.5223 | 0 | 0 | 5175.4728 | 0 | 5175.853 | -0.38022 | -0.38022 | 11.0447 | 15.7945 | 30.1669 | 5.3944 | 45.7812 | 0 | 16.6951 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.9511 | 0 | 141.9615 | -0.010429 | -0.010429 | 5.4829 | 0.98044 | 8.3208 | 3.0344 | 0 | 0 | 2.8707 | 2.0074 | 3.1033 | 0 | 0 | 25.8018 | 25.7999 | -0.0018954
NJ_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 4795.9546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4795.9546 | 0 | 4795.9546 | 0 | 0 | 41.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.0582 | 0 | 41.0582 | 0 | 0 | 4.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.796 | 0 | 4.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87167 | 0 | 0 | 0 | 0.87167 | 0.87167 | 0
NJ_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 3287.0444 | 4390.1354 | 7127.0235 | 1581.0044 | 13417.6985 | 0 | 4504.0566 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39311.1614 | 0 | 39314.7736 | -3.6121 | -3.6121 | 408.9083 | 546.1328 | 886.6017 | 196.677 | 1669.1617 | 0 | 560.3046 | 0 | 0 | 0 | 0 | 622.5223 | 0 | 0 | 4890.3085 | 0 | 4890.7578 | -0.44935 | -0.44935 | 11.2154 | 14.9791 | 24.3174 | 5.3944 | 45.7812 | 0 | 15.3678 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.1297 | 0 | 134.142 | -0.012325 | -0.012325 | 4.4197 | 0.98044 | 8.3208 | 2.7931 | 0 | 0 | 2.7225 | 2.0384 | 3.1033 | 0 | 0 | 24.3806 | 24.3784 | -0.00224
NJ_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | NJ-NEWARK-NJ | Zone4A | Zone4A(NJ-NEWARK-NJ) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 5032.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5032.9089 | 0 | 5032.9089 | 0 | 0 | 43.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.0867 | 0 | 43.0867 | 0 | 0 | 5.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0329 | 0 | 5.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91474 | 0 | 0 | 0 | 0.91474 | 0.91474 | 0
NJ_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 615188.5563 | 880550.0102 | 95543.7939 | 4077910.5986 | 543457.0788 | 584791.0368 | 90378.4385 | 214135.7985 | 396029.1092 | 11456.0304 | 0 | 0 | 0 | 7509440.4514 | 0 | 7509437.6728 | 2.7786 | 543459.8574 | 0 | 76529.4564 | 109540.4213 | 11885.648 | 507292.0785 | 67606.0606 | 72748.005 | 11243.0777 | 26638.4933 | 49266.0212 | 1425.1302 | 0 | 0 | 0 | 934174.3922 | 0 | 934174.0465 | 0.34565 | 67606.4063 | 0 | 2099.0234 | 3004.4366 | 325.9954 | 13913.831 | 1854.2756 | 1995.307 | 308.3712 | 730.6313 | 1351.2513 | 39.088 | 0 | 0 | 0 | 25622.2108 | 0 | 25622.2013 | 0.0094805 | 1854.285 | 6.0259 | 0.65384 | 27.9065 | 4.0019 | 0.61849 | 0.078397 | 4.2099 | 0 | 0 | 2.7102 | 0 | 51.3895 | 51.3895 | 1.9015e-05
NJ_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 936424.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564889.5253 | 0 | 0 | 1501313.8836 | 0 | 1501313.8836 | 0 | 0 | 8016.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4836.0192 | 0 | 0 | 12852.7482 | 0 | 12852.7482 | 0 | 0 | 936.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.8895 | 0 | 0 | 1501.3139 | 0 | 1501.3139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8782 | 1.133 | 0 | 0 | 3.0111 | 3.0111 | 0
NJ_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 575060.4963 | 717042.4752 | 95543.7939 | 4077910.5986 | 543387.6147 | 568050.1725 | 86271.7169 | 192235.1359 | 395812.381 | 10597.4533 | 0 | 0 | 0 | 7261911.8385 | 0 | 7261905.1699 | 6.6686 | 543394.2832 | 0 | 71537.5257 | 89200.0839 | 11885.648 | 507292.0785 | 67597.4193 | 70665.4415 | 10732.2016 | 23914.0509 | 49239.0602 | 1318.3232 | 0 | 0 | 0 | 903381.8327 | 0 | 903381.0031 | 0.82957 | 67598.2488 | 0 | 1962.1064 | 2446.5489 | 325.9954 | 13913.831 | 1854.0385 | 1938.1872 | 294.3591 | 655.9063 | 1350.5118 | 36.1585 | 0 | 0 | 0 | 24777.6432 | 0 | 24777.6204 | 0.022753 | 1854.0613 | 4.907 | 0.65384 | 27.9065 | 3.8874 | 0.59039 | 0.072522 | 3.9353 | 0 | 0 | 2.7087 | 0 | 49.6956 | 49.6956 | 4.5635e-05
NJ_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 867271.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564974.8289 | 0 | 0 | 1432246.45 | 0 | 1432246.45 | 0 | 0 | 7424.7123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4836.7495 | 0 | 0 | 12261.4619 | 0 | 12261.4619 | 0 | 0 | 867.2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.9748 | 0 | 0 | 1432.2465 | 0 | 1432.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7395 | 1.1331 | 0 | 0 | 2.8726 | 2.8726 | 0
NJ_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 26065.734 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20875.3715 | 0 | 0 | 0 | 0 | 113301.6136 | 0 | 0 | 337823.6944 | 0 | 337821.7494 | 1.945 | 1.945 | 0 | 3242.5773 | 3529.8155 | 895.9344 | 17665.3234 | 0 | 2596.8962 | 0 | 0 | 0 | 0 | 14094.7207 | 0 | 0 | 42025.2676 | 0 | 42025.0256 | 0.24196 | 0.24196 | 0 | 88.9363 | 96.8146 | 24.5734 | 484.5184 | 0 | 71.2268 | 0 | 0 | 0 | 0 | 386.5851 | 0 | 0 | 1152.6544 | 0 | 1152.6478 | 0.0066363 | 0.0066363 | 2.8693 | 0.72829 | 14.3599 | 2.111 | 0 | 0 | 2.6359 | 0 | 11.4574 | 0 | 0 | 34.1616 | 34.1618 | 0.00019668
NJ_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 111681.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111681.2912 | 0 | 111681.2912 | 0 | 0 | 956.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956.1035 | 0 | 956.1035 | 0 | 0 | 111.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.6813 | 0 | 111.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 0 | 0 | 0 | 3.31 | 3.31 | 0
NJ_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 25004.3216 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20333.551 | 0 | 0 | 0 | 0 | 113332.1778 | 0 | 0 | 331057.8845 | 0 | 331058.4402 | -0.55571 | -0.55571 | 0 | 3110.5376 | 2883.7888 | 895.9344 | 17665.3234 | 0 | 2529.4937 | 0 | 0 | 0 | 0 | 14098.5229 | 0 | 0 | 41183.6008 | 0 | 41183.67 | -0.069131 | -0.069131 | 0 | 85.3147 | 79.0956 | 24.5734 | 484.5184 | 0 | 69.3781 | 0 | 0 | 0 | 0 | 386.6894 | 0 | 0 | 1129.5695 | 0 | 1129.5714 | -0.0018961 | -0.0018961 | 2.3442 | 0.72829 | 14.3599 | 2.0562 | 0 | 0 | 2.5285 | 0 | 11.4605 | 0 | 0 | 33.4777 | 33.4777 | -5.6196e-05
NJ_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 127377.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127377.1428 | 0 | 127377.1428 | 0 | 0 | 1090.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.4757 | 0 | 1090.4757 | 0 | 0 | 127.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.3771 | 0 | 127.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7751 | 0 | 0 | 0 | 3.7751 | 3.7751 | 0
NJ_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 96224.5428 | 97213.7125 | 7118.6878 | 317887.4784 | 4818.0346 | 91153.6586 | 691.8631 | 0 | 0 | 20497.4864 | 7179.8163 | 17613.3342 | 0 | 660398.6148 | 0 | 660399.7262 | -1.1114 | 4816.9232 | 0 | 11970.3331 | 12093.3858 | 885.5648 | 39545.2023 | 599.3635 | 11339.5151 | 86.0678 | 0 | 0 | 2549.8873 | 893.1691 | 2191.0988 | 0 | 82153.5877 | 0 | 82153.7259 | -0.13826 | 599.2252 | 0 | 328.3181 | 331.6932 | 24.289 | 1084.6321 | 16.4391 | 311.0163 | 2.3606 | 0 | 0 | 69.9374 | 24.4975 | 60.0967 | 0 | 2253.2801 | 0 | 2253.2839 | -0.0037922 | 16.4353 | 4.4848 | 0.32841 | 14.6653 | 4.2053 | 0.031918 | 0.94562 | 4.4392 | 0 | 0.33123 | 0 | 0.81257 | 30.4667 | 30.4666 | -5.1274e-05
NJ_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 430517.4922 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118420.271 | 0 | 0 | 891128.1781 | 0 | 891128.1781 | 0 | 0 | 3685.6603 | 0 | 0 | 0 | 2929.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 1013.7959 | 0 | 0 | 7628.9483 | 0 | 7628.9483 | 0 | 0 | 430.5175 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4203 | 0 | 0 | 891.1282 | 0 | 891.1282 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.821 | 1.6012 | 0 | 0 | 12.0489 | 12.0489 | 0
NJ_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 91395.3939 | 79191.929 | 7118.6878 | 312483.1662 | 4743.0133 | 78869.6153 | 527.9277 | 0 | 0 | 22686.997 | 7179.8163 | 12486.8787 | 0 | 616683.4252 | 0 | 616686.2038 | -2.7786 | 4740.2348 | 0 | 11369.587 | 9851.476 | 885.5648 | 38872.9059 | 590.0309 | 9811.3801 | 65.6742 | 0 | 0 | 2822.2624 | 893.1691 | 1553.3677 | 0 | 76715.4181 | 0 | 76715.7637 | -0.34565 | 589.6852 | 0 | 311.8411 | 270.2029 | 24.289 | 1066.1926 | 16.1832 | 269.1031 | 1.8013 | 0 | 0 | 77.408 | 24.4975 | 42.6052 | 0 | 2104.1238 | 0 | 2104.1333 | -0.0094805 | 16.1737 | 3.6534 | 0.32841 | 14.416 | 3.6385 | 0.024355 | 1.0466 | 4.2164 | 0 | 0.33123 | 0 | 0.57607 | 28.45 | 28.4499 | -0.00012819
NJ_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 408973.6091 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118154.8822 | 0 | 0 | 869318.9061 | 0 | 869318.9061 | 0 | 0 | 3501.2231 | 0 | 0 | 0 | 2929.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 1011.5239 | 0 | 0 | 7442.2392 | 0 | 7442.2392 | 0 | 0 | 408.9736 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.1549 | 0 | 0 | 869.3189 | 0 | 869.3189 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.5297 | 1.5976 | 0 | 0 | 11.7541 | 11.7541 | 0
NJ_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 33931.8563 | 83632.0786 | 10725.2674 | 53987.5506 | 0 | 42584.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224861.0659 | 0 | 224859.3988 | 1.6671 | 1.6671 | 0 | 4221.1229 | 10403.8306 | 1334.2233 | 6716.0513 | 0 | 5297.4885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27972.7166 | 0 | 27972.5092 | 0.20739 | 0.20739 | 0 | 115.7755 | 285.3527 | 36.5946 | 184.2055 | 0 | 145.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.226 | 0 | 767.2203 | 0.0056883 | 0.0056883 | 11.5565 | 1.482 | 7.4601 | 5.8844 | 0 | 0 | 4.6888 | 0 | 0 | 0 | 0 | 31.0716 | 31.0718 | 0.00023037
NJ_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 421712.2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90355.406 | 0 | 0 | 512067.6773 | 0 | 512067.6773 | 0 | 0 | 3610.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.5326 | 0 | 0 | 4383.8114 | 0 | 4383.8114 | 0 | 0 | 421.7123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3554 | 0 | 0 | 512.0677 | 0 | 512.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0789 | 3.6593 | 0 | 0 | 20.7382 | 20.7382 | 0
NJ_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 0 | 31553.4032 | 66149.337 | 10725.2674 | 53987.5506 | 0 | 40747.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203163.2387 | 0 | 203160.738 | 2.5007 | 2.5007 | 0 | 3925.2434 | 8228.9775 | 1334.2233 | 6716.0513 | 0 | 5069.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25273.5069 | 0 | 25273.1958 | 0.31109 | 0.31109 | 0 | 107.6602 | 225.7015 | 36.5946 | 184.2055 | 0 | 139.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 693.193 | 0 | 693.1844 | 0.0085324 | 0.0085324 | 9.1407 | 1.482 | 7.4601 | 5.6306 | 0 | 0 | 4.3601 | 0 | 0 | 0 | 0 | 28.0732 | 28.0736 | 0.00034555
NJ_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 448241.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90364.8842 | 0 | 0 | 538606.5566 | 0 | 538606.5566 | 0 | 0 | 3837.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.6138 | 0 | 0 | 4611.0107 | 0 | 4611.0107 | 0 | 0 | 448.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3649 | 0 | 0 | 538.6066 | 0 | 538.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1533 | 3.6597 | 0 | 0 | 21.813 | 21.813 | 0
NJ_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 30197.4627 | 66721.7217 | 79061.3364 | 12300.7147 | 154949.5496 | 0 | 45501.808 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 388804.8359 | 0 | 388805.9473 | -1.1114 | -1.1114 | 3756.5644 | 8300.1822 | 9835.2302 | 1530.2089 | 19275.724 | 0 | 5660.4249 | 8.987 | 0 | 0 | 0 | 0 | 0 | 0 | 48367.3216 | 0 | 48367.4598 | -0.13826 | -0.13826 | 103.0337 | 227.6545 | 269.7573 | 41.97 | 528.6879 | 0 | 155.2522 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1326.6021 | 0 | 1326.6059 | -0.0037922 | -0.0037922 | 6.2441 | 0.97148 | 12.2376 | 3.5936 | 0.0057056 | 0 | 5.2695 | 2.3849 | 0 | 0 | 0 | 30.707 | 30.707 | -8.7778e-05
NJ_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 71854.0159 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 589324.2507 | 0 | 0 | 1060673.7045 | 0 | 1060673.7045 | 0 | 0 | 615.1422 | 0 | 0 | 0 | 3420.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 5045.2049 | 0 | 0 | 9080.4276 | 0 | 9080.4276 | 0 | 0 | 71.854 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 589.3243 | 0 | 0 | 1060.6737 | 0 | 1060.6737 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6632 | 13.6411 | 0 | 0 | 24.5515 | 24.5515 | 0
NJ_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 34343.0842 | 62162.0938 | 50717.1777 | 12300.7147 | 154949.5496 | 0 | 43109.4621 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 357654.3248 | 0 | 357655.4362 | -1.1114 | -1.1114 | 4272.2797 | 7732.9645 | 6309.2169 | 1530.2089 | 19275.724 | 0 | 5362.8171 | 8.987 | 0 | 0 | 0 | 0 | 0 | 0 | 44492.198 | 0 | 44492.3363 | -0.13826 | -0.13826 | 117.1786 | 212.0971 | 173.047 | 41.97 | 528.6879 | 0 | 147.0895 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.3166 | 0 | 1220.3203 | -0.0037922 | -0.0037922 | 4.0055 | 0.97148 | 12.2376 | 3.4047 | 0.0057056 | 0 | 4.9094 | 2.7123 | 0 | 0 | 0 | 28.2468 | 28.2468 | -8.7778e-05
NJ_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 70527.0719 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 589390.5979 | 0 | 0 | 1059413.1077 | 0 | 1059413.1077 | 0 | 0 | 603.7823 | 0 | 0 | 0 | 3420.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 5045.7729 | 0 | 0 | 9069.6356 | 0 | 9069.6356 | 0 | 0 | 70.5271 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 589.3906 | 0 | 0 | 1059.4131 | 0 | 1059.4131 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6325 | 13.6427 | 0 | 0 | 24.5223 | 24.5223 | 0
NJ_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 3578.7939 | 3803.8578 | 8796.9421 | 1581.0044 | 13417.6985 | 0 | 4801.3632 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40983.8586 | 0 | 40984.4143 | -0.55571 | -0.55571 | 445.202 | 473.1999 | 1094.3396 | 196.677 | 1669.1617 | 0 | 597.2896 | 0 | 0 | 0 | 0 | 622.5223 | 0 | 0 | 5098.392 | 0 | 5098.4611 | -0.069131 | -0.069131 | 12.2108 | 12.9788 | 30.0152 | 5.3944 | 45.7812 | 0 | 16.3823 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.8369 | 0 | 139.8388 | -0.0018961 | -0.0018961 | 5.4553 | 0.98044 | 8.3208 | 2.9775 | 0 | 0 | 2.3589 | 2.2193 | 3.1033 | 0 | 0 | 25.416 | 25.4157 | -0.00034462
NJ_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 5895.4225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5895.4225 | 0 | 5895.4225 | 0 | 0 | 50.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4707 | 0 | 50.4707 | 0 | 0 | 5.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8954 | 0 | 5.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0715 | 0 | 0 | 0 | 1.0715 | 1.0715 | 0
NJ_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Electricity | 3626.0295 | 3592.6867 | 7096.4593 | 1581.0044 | 13417.6985 | 0 | 4412.3639 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38730.441 | 0 | 38730.441 | 0 | 0 | 451.0781 | 446.9302 | 882.7995 | 196.677 | 1669.1617 | 0 | 548.8981 | 0 | 0 | 0 | 0 | 622.5223 | 0 | 0 | 4818.0669 | 0 | 4818.0669 | 0 | 0 | 12.372 | 12.2582 | 24.2131 | 5.3944 | 45.7812 | 0 | 15.055 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.1483 | 0 | 132.1483 | 0 | 0 | 4.4008 | 0.98044 | 8.3208 | 2.7363 | 0 | 0 | 2.228 | 2.2486 | 3.1033 | 0 | 0 | 24.0182 | 24.0182 | 0
NJ_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | NJ-ALLENTOWN-PA | Zone5A | Zone5A(NJ-ALLENTOWN-PA) |  |  | NJ | 0.1244 | 0.008561 |  |  |  | Natural Gas | 6236.6366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6236.6366 | 0 | 6236.6366 | 0 | 0 | 53.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.3918 | 0 | 53.3918 | 0 | 0 | 6.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2366 | 0 | 6.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1335 | 0 | 0 | 0 | 1.1335 | 1.1335 | 0
NM_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 886949.0492 | 881711.4511 | 94571.2956 | 4077910.5986 | 543457.0788 | 694233.2213 | 118761.4971 | 290026.7903 | 492523.173 | 0 | 0 | 0 | 0 | 8080144.1551 | 0 | 8080142.2101 | 1.945 | 543459.0238 | 0 | 92508.7858 | 91962.5043 | 9863.7861 | 425326.0754 | 56682.5733 | 72408.525 | 12386.8242 | 30249.7942 | 51370.1669 | 0 | 0 | 0 | 0 | 842759.0354 | 0 | 842758.8325 | 0.20286 | 56682.7762 | 0 | 3026.2702 | 3008.3995 | 322.6773 | 13913.831 | 1854.2756 | 2368.7238 | 405.2142 | 989.5714 | 1680.4891 | 0 | 0 | 0 | 0 | 27569.4519 | 0 | 27569.4452 | 0.0066363 | 1854.2822 | 6.0338 | 0.64718 | 27.9065 | 4.7509 | 0.81272 | 0 | 6.0697 | 0 | 0 | 3.3705 | 0 | 55.295 | 55.2951 | 1.331e-05
NM_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 459729.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497803.0296 | 0 | 0 | 957532.2455 | 0 | 957532.2455 | 0 | 0 | 2218.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2401.8996 | 0 | 0 | 4620.0931 | 0 | 4620.0931 | 0 | 0 | 459.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497.803 | 0 | 0 | 957.5322 | 0 | 957.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92206 | 0.99843 | 0 | 0 | 1.9205 | 1.9205 | 0
NM_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 836751.4636 | 717375.9032 | 94571.2956 | 4077910.5986 | 543387.6147 | 674391.4766 | 115563.3669 | 260371.1481 | 492592.6372 | 0 | 0 | 0 | 0 | 7812915.5044 | 0 | 7812914.6709 | 0.83357 | 543388.4482 | 0 | 87273.1776 | 74822.3067 | 9863.7861 | 425326.0754 | 56675.3282 | 70339.031 | 12053.2592 | 27156.7107 | 51377.4121 | 0 | 0 | 0 | 0 | 814887.0871 | 0 | 814887.0002 | 0.086941 | 56675.4152 | 0 | 2854.996 | 2447.6866 | 322.6773 | 13913.831 | 1854.0385 | 2301.0237 | 394.3022 | 888.3864 | 1680.7261 | 0 | 0 | 0 | 0 | 26657.6677 | 0 | 26657.6649 | 0.0028441 | 1854.0414 | 4.9092 | 0.64718 | 27.9065 | 4.6151 | 0.79084 | 0 | 5.7262 | 0 | 0 | 3.371 | 0 | 53.4663 | 53.4663 | 5.7044e-06
NM_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 774878.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497727.2042 | 0 | 0 | 1272605.6125 | 0 | 1272605.6125 | 0 | 0 | 3738.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2401.5338 | 0 | 0 | 6140.3221 | 0 | 6140.3221 | 0 | 0 | 774.8784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497.7272 | 0 | 0 | 1272.6056 | 0 | 1272.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5541 | 0.99827 | 0 | 0 | 2.5524 | 2.5524 | 0
NM_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 39369.5113 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 24893.1789 | 0 | 0 | 0 | 0 | 100089.529 | 0 | 0 | 341944.3088 | 0 | 341942.0859 | 2.2229 | 2.2229 | 0 | 4106.24 | 2959.4836 | 752.3325 | 14811.0388 | 0 | 2596.3586 | 0 | 0 | 0 | 0 | 10439.3379 | 0 | 0 | 35664.7914 | 0 | 35664.5596 | 0.23184 | 0.23184 | 0 | 134.3288 | 96.8146 | 24.6113 | 484.5184 | 0 | 84.9355 | 0 | 0 | 0 | 0 | 341.5055 | 0 | 0 | 1166.714 | 0 | 1166.7064 | 0.0075844 | 0.0075844 | 2.8693 | 0.72942 | 14.3599 | 2.5173 | 0 | 0 | 3.9812 | 0 | 10.1214 | 0 | 0 | 34.5783 | 34.5785 | 0.00022478
NM_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 60508.6449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60508.6449 | 0 | 60508.6449 | 0 | 0 | 291.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291.9542 | 0 | 291.9542 | 0 | 0 | 60.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5086 | 0 | 60.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7933 | 0 | 0 | 0 | 1.7933 | 1.7933 | 0
NM_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 39922.4461 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 25251.614 | 0 | 0 | 0 | 0 | 99970.0507 | 0 | 0 | 337543.0591 | 0 | 337546.1156 | -3.0564 | -3.0564 | 0 | 4163.9111 | 2417.839 | 752.3325 | 14811.0388 | 0 | 2633.7433 | 0 | 0 | 0 | 0 | 10426.8763 | 0 | 0 | 35205.7411 | 0 | 35206.0599 | -0.31878 | -0.31878 | 0 | 136.2154 | 79.0956 | 24.6113 | 484.5184 | 0 | 86.1585 | 0 | 0 | 0 | 0 | 341.0978 | 0 | 0 | 1151.6969 | 0 | 1151.7073 | -0.010429 | -0.010429 | 2.3442 | 0.72942 | 14.3599 | 2.5535 | 0 | 0 | 4.0371 | 0 | 10.1093 | 0 | 0 | 34.1338 | 34.1335 | -0.00030908
NM_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 24974.9811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24974.9811 | 0 | 24974.9811 | 0 | 0 | 120.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5043 | 0 | 120.5043 | 0 | 0 | 24.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.975 | 0 | 24.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7402 | 0 | 0 | 0 | 0.7402 | 0.7402 | 0
NM_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 158431.0937 | 101345.4412 | 7093.6807 | 317887.4784 | 4818.0346 | 102548.5605 | 325.0923 | 0 | 0 | 0 | 7179.8163 | 17477.1844 | 0 | 717106.3822 | 0 | 717111.1058 | -4.7236 | 4813.3111 | 0 | 16524.3631 | 10570.3295 | 739.8709 | 33155.664 | 502.521 | 10695.8149 | 33.9071 | 0 | 0 | 0 | 748.8548 | 1822.8703 | 0 | 74794.1957 | 0 | 74794.6883 | -0.49267 | 502.0283 | 0 | 540.5669 | 345.7906 | 24.2036 | 1084.6321 | 16.4391 | 349.8957 | 1.1092 | 0 | 0 | 0 | 24.4975 | 59.6322 | 0 | 2446.767 | 0 | 2446.7831 | -0.016117 | 16.423 | 4.6754 | 0.32726 | 14.6653 | 4.7309 | 0.014998 | 0 | 7.309 | 0 | 0.33123 | 0 | 0.80629 | 33.083 | 33.0827 | -0.00021792
NM_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 203411.0321 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104743.2699 | 0 | 0 | 650344.7169 | 0 | 650344.7169 | 0 | 0 | 981.4582 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 505.3863 | 0 | 0 | 3137.9133 | 0 | 3137.9133 | 0 | 0 | 203.411 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7433 | 0 | 0 | 650.3447 | 0 | 650.3447 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.7503 | 1.4162 | 0 | 0 | 8.7933 | 8.7933 | 0
NM_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 159411.9277 | 81717.6461 | 7093.6807 | 312483.1662 | 4745.7919 | 85071.3761 | 466.7992 | 0 | 0 | 0 | 7179.8163 | 12422.9716 | 0 | 670593.176 | 0 | 670593.4538 | -0.27786 | 4745.514 | 0 | 16626.6641 | 8523.1505 | 739.8709 | 32591.9942 | 494.9861 | 8872.9445 | 48.6872 | 0 | 0 | 0 | 748.8548 | 1295.7159 | 0 | 69942.8683 | 0 | 69942.8972 | -0.02898 | 494.9571 | 0 | 543.9135 | 278.8206 | 24.2036 | 1066.1926 | 16.1926 | 290.2635 | 1.5927 | 0 | 0 | 0 | 24.4975 | 42.3872 | 0 | 2288.0639 | 0 | 2288.0649 | -0.00094805 | 16.1917 | 3.7699 | 0.32726 | 14.416 | 3.9247 | 0.021535 | 0 | 7.3543 | 0 | 0.33123 | 0 | 0.57312 | 30.9369 | 30.9369 | -1.2819e-05
NM_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 280421.1731 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104676.9227 | 0 | 0 | 727288.5107 | 0 | 727288.5107 | 0 | 0 | 1353.0322 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 505.0662 | 0 | 0 | 3509.1671 | 0 | 3509.1671 | 0 | 0 | 280.4212 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6769 | 0 | 0 | 727.2885 | 0 | 727.2885 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7916 | 1.4153 | 0 | 0 | 9.8337 | 9.8337 | 0
NM_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 56463.2536 | 85218.6401 | 10708.596 | 53987.5506 | 0 | 43520.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249898.7303 | 0 | 249895.1181 | 3.6121 | 3.6121 | 0 | 5889.1173 | 8888.3042 | 1116.9066 | 5630.9015 | 0 | 4539.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26064.4376 | 0 | 26064.0608 | 0.37675 | 0.37675 | 0 | 192.6526 | 290.766 | 36.5377 | 184.2055 | 0 | 148.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 852.6545 | 0 | 852.6421 | 0.012325 | 0.012325 | 11.7757 | 1.4797 | 7.4601 | 6.0138 | 0 | 0 | 7.8022 | 0 | 0 | 0 | 0 | 34.5311 | 34.5316 | 0.00049913
NM_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 76365.6254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86289.2706 | 0 | 0 | 162654.896 | 0 | 162654.896 | 0 | 0 | 368.4641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.3457 | 0 | 0 | 784.8099 | 0 | 784.8099 | 0 | 0 | 76.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2893 | 0 | 0 | 162.6549 | 0 | 162.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0927 | 3.4946 | 0 | 0 | 6.5874 | 6.5874 | 0
NM_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 52812.2169 | 67460.8205 | 10708.596 | 53987.5506 | 0 | 41356.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226325.3705 | 0 | 226324.8148 | 0.55571 | 0.55571 | 0 | 5508.3142 | 7036.1636 | 1116.9066 | 5630.9015 | 0 | 4313.4503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23605.7361 | 0 | 23605.6782 | 0.057961 | 0.057961 | 0 | 180.1953 | 230.1763 | 36.5377 | 184.2055 | 0 | 141.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772.2222 | 0 | 772.2203 | 0.0018961 | 0.0018961 | 9.3219 | 1.4797 | 7.4601 | 5.7147 | 0 | 0 | 7.2977 | 0 | 0 | 0 | 0 | 31.2741 | 31.2742 | 7.679e-05
NM_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 90469.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86308.2269 | 0 | 0 | 176777.3711 | 0 | 176777.3711 | 0 | 0 | 436.5136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.4372 | 0 | 0 | 852.9508 | 0 | 852.9508 | 0 | 0 | 90.4691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3082 | 0 | 0 | 176.7774 | 0 | 176.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6639 | 3.4954 | 0 | 0 | 7.1593 | 7.1593 | 0
NM_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 6568.5316 | 90536.8168 | 80420.0555 | 12320.1647 | 154949.5496 | 0 | 48033.0822 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392900.4432 | 0 | 392899.6096 | 0.83357 | 0.83357 | 685.0978 | 9442.99 | 8387.8118 | 1284.9932 | 16161.238 | 0 | 5009.8505 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 40979.5162 | 0 | 40979.4293 | 0.086941 | 0.086941 | 22.4118 | 308.9116 | 274.3932 | 42.0364 | 528.6879 | 0 | 163.8889 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1340.5763 | 0 | 1340.5735 | 0.0028441 | 0.0028441 | 6.3514 | 0.97302 | 12.2376 | 3.7935 | 0.0057056 | 0 | 7.1504 | 0.51877 | 0 | 0 | 0 | 31.0304 | 31.0304 | 6.5834e-05
NM_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 14406.8202 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 512010.8082 | 0 | 0 | 925913.0664 | 0 | 925913.0664 | 0 | 0 | 69.5129 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2470.4521 | 0 | 0 | 4467.5305 | 0 | 4467.5305 | 0 | 0 | 14.4068 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 512.0108 | 0 | 0 | 925.9131 | 0 | 925.9131 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.33348 | 11.8516 | 0 | 0 | 21.4322 | 21.4322 | 0
NM_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 7910.5793 | 84857.4265 | 51514.6263 | 12320.1647 | 154949.5496 | 0 | 45510.1437 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 357134.7328 | 0 | 357137.7892 | -3.0564 | -3.0564 | 825.0734 | 8850.6296 | 5372.9755 | 1284.9932 | 16161.238 | 0 | 4746.708 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 37249.1526 | 0 | 37249.4714 | -0.31878 | -0.31878 | 26.9909 | 289.5335 | 175.7679 | 42.0364 | 528.6879 | 0 | 155.2806 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.5437 | 0 | 1218.5541 | -0.010429 | -0.010429 | 4.0685 | 0.97302 | 12.2376 | 3.5943 | 0.0057056 | 0 | 6.7019 | 0.62476 | 0 | 0 | 0 | 28.206 | 28.2057 | -0.00024139
NM_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 16624.7123 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 512020.2864 | 0 | 0 | 928140.4366 | 0 | 928140.4366 | 0 | 0 | 80.2142 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2470.4979 | 0 | 0 | 4478.2776 | 0 | 4478.2776 | 0 | 0 | 16.6247 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 512.0203 | 0 | 0 | 928.1404 | 0 | 928.1404 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.38481 | 11.8518 | 0 | 0 | 21.4837 | 21.4837 | 0
NM_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 980.834 | 6282.3393 | 9030.3417 | 1567.1116 | 13417.6985 | 0 | 5898.8971 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42181.4208 | 0 | 42180.5872 | 0.83357 | 0.83357 | 102.301 | 655.248 | 941.8646 | 163.4497 | 1399.466 | 0 | 615.255 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 4399.5222 | 0 | 4399.4352 | 0.086941 | 0.086941 | 3.3466 | 21.4353 | 30.8115 | 5.347 | 45.7812 | 0 | 20.127 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.923 | 0 | 143.9202 | 0.0028441 | 0.0028441 | 5.6001 | 0.97183 | 8.3208 | 3.6581 | 0 | 0 | 3.8959 | 0.60825 | 3.1033 | 0 | 0 | 26.1578 | 26.1583 | 0.00051693
NM_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 729.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729.8192 | 0 | 729.8192 | 0 | 0 | 3.5214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5214 | 0 | 3.5214 | 0 | 0 | 0.72982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72982 | 0 | 0.72982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13265 | 0 | 0 | 0 | 0.13265 | 0.13265 | 0
NM_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 1003.0626 | 5943.3541 | 7254.8376 | 1567.1116 | 13417.6985 | 0 | 5429.3193 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39619.5823 | 0 | 39617.3595 | 2.2229 | 2.2229 | 104.6194 | 619.8918 | 756.6796 | 163.4497 | 1399.466 | 0 | 566.278 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 4132.3224 | 0 | 4132.0906 | 0.23184 | 0.23184 | 3.4224 | 20.2787 | 24.7535 | 5.347 | 45.7812 | 0 | 18.5248 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.182 | 0 | 135.1744 | 0.0075844 | 0.0075844 | 4.499 | 0.97183 | 8.3208 | 3.3669 | 0 | 0 | 3.6857 | 0.62204 | 3.1033 | 0 | 0 | 24.5682 | 24.5696 | 0.0013785
NM_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | NM-ROSWELL-NM | Zone3B | Zone3B(NM-ROSWELL-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 805.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805.6446 | 0 | 805.6446 | 0 | 0 | 3.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8872 | 0 | 3.8872 | 0 | 0 | 0.80564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80564 | 0 | 0.80564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14643 | 0 | 0 | 0 | 0.14643 | 0.14643 | 0
NM_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 694233.2213 | 878827.2988 | 94774.131 | 4077910.5986 | 543457.0788 | 713277.5173 | 91995.5643 | 215327.8036 | 603190.7054 | 0 | 0 | 0 | 0 | 7912993.9192 | 0 | 7912990.8628 | 3.0564 | 543460.1353 | 0 | 72408.525 | 91661.6873 | 9884.9419 | 425326.0754 | 56682.5733 | 74394.8451 | 9595.1374 | 22458.6899 | 62912.7906 | 0 | 0 | 0 | 0 | 825325.2658 | 0 | 825324.947 | 0.31878 | 56682.8921 | 0 | 2368.7238 | 2998.5587 | 323.3693 | 13913.831 | 1854.2756 | 2433.7029 | 313.8889 | 734.6985 | 2058.0867 | 0 | 0 | 0 | 0 | 26999.1353 | 0 | 26999.1248 | 0.010429 | 1854.286 | 6.0141 | 0.64857 | 27.9065 | 4.8812 | 0.62956 | 0 | 4.7509 | 0 | 0 | 4.1278 | 0 | 54.1512 | 54.1512 | 2.0916e-05
NM_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 582935.9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534075.9908 | 0 | 0 | 1117011.9541 | 0 | 1117011.9541 | 0 | 0 | 2812.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2576.9167 | 0 | 0 | 5389.5827 | 0 | 5389.5827 | 0 | 0 | 582.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534.076 | 0 | 0 | 1117.012 | 0 | 1117.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1692 | 1.0712 | 0 | 0 | 2.2404 | 2.2404 | 0
NM_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 646083.4393 | 715869.92 | 94774.131 | 4077910.5986 | 543384.8361 | 697003.4523 | 90317.31 | 192290.7073 | 603601.9332 | 0 | 0 | 0 | 0 | 7661236.3278 | 0 | 7661235.2164 | 1.1114 | 543385.9475 | 0 | 67386.5027 | 74665.2327 | 9884.9419 | 425326.0754 | 56675.0384 | 72697.4601 | 9420.0954 | 20055.9208 | 62955.6816 | 0 | 0 | 0 | 0 | 799066.949 | 0 | 799066.8331 | 0.11592 | 56675.1543 | 0 | 2204.4367 | 2442.5482 | 323.3693 | 13913.831 | 1854.0291 | 2378.1758 | 308.1627 | 656.0959 | 2059.4898 | 0 | 0 | 0 | 0 | 26140.1384 | 0 | 26140.1346 | 0.0037922 | 1854.0329 | 4.8989 | 0.64857 | 27.9065 | 4.7698 | 0.61807 | 0 | 4.4214 | 0 | 0 | 4.1306 | 0 | 52.4283 | 52.4283 | 7.6059e-06
NM_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 997994.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534085.4689 | 0 | 0 | 1532080.0273 | 0 | 1532080.0273 | 0 | 0 | 4815.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2576.9624 | 0 | 0 | 7392.2861 | 0 | 7392.2861 | 0 | 0 | 997.9946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534.0855 | 0 | 0 | 1532.08 | 0 | 1532.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0016 | 1.0712 | 0 | 0 | 3.0728 | 3.0728 | 0
NM_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 31461.7105 | 28374.723 | 7207.602 | 142004.2074 | 0 | 23909.5663 | 0 | 0 | 0 | 0 | 107266.5668 | 0 | 0 | 340224.376 | 0 | 340222.7089 | 1.6671 | 1.6671 | 0 | 3281.4564 | 2959.4836 | 751.7529 | 14811.0388 | 0 | 2493.7678 | 0 | 0 | 0 | 0 | 11187.9029 | 0 | 0 | 35485.4024 | 0 | 35485.2285 | 0.17388 | 0.17388 | 0 | 107.3474 | 96.8146 | 24.5923 | 484.5184 | 0 | 81.5794 | 0 | 0 | 0 | 0 | 365.9935 | 0 | 0 | 1160.8456 | 0 | 1160.8399 | 0.0056883 | 0.0056883 | 2.8693 | 0.72886 | 14.3599 | 2.4178 | 0 | 0 | 3.1815 | 0 | 10.8471 | 0 | 0 | 34.4044 | 34.4046 | 0.00016859
NM_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 77379.7897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77379.7897 | 0 | 77379.7897 | 0 | 0 | 373.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.3575 | 0 | 373.3575 | 0 | 0 | 77.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3798 | 0 | 77.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2933 | 0 | 0 | 0 | 2.2933 | 2.2933 | 0
NM_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 33834.6065 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 24176.3087 | 0 | 0 | 0 | 0 | 107141.5313 | 0 | 0 | 337545.8377 | 0 | 337547.7827 | -1.945 | -1.945 | 0 | 3528.9495 | 2417.839 | 751.7529 | 14811.0388 | 0 | 2521.589 | 0 | 0 | 0 | 0 | 11174.8617 | 0 | 0 | 35206.0309 | 0 | 35206.2337 | -0.20286 | -0.20286 | 0 | 115.4437 | 79.0956 | 24.5923 | 484.5184 | 0 | 82.4896 | 0 | 0 | 0 | 0 | 365.5669 | 0 | 0 | 1151.7064 | 0 | 1151.713 | -0.0066363 | -0.0066363 | 2.3442 | 0.72886 | 14.3599 | 2.4448 | 0 | 0 | 3.4215 | 0 | 10.8345 | 0 | 0 | 34.1339 | 34.1337 | -0.00019668
NM_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 30832.4909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30832.4909 | 0 | 30832.4909 | 0 | 0 | 148.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148.7668 | 0 | 148.7668 | 0 | 0 | 30.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8325 | 0 | 30.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9138 | 0 | 0 | 0 | 0.9138 | 0.9138 | 0
NM_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 115905.1306 | 97627.719 | 7093.6807 | 317887.4784 | 4818.0346 | 107630.559 | 402.8922 | 0 | 0 | 0 | 7179.8163 | 17427.1702 | 0 | 675972.4811 | 0 | 675967.2018 | 5.2793 | 4823.3139 | 0 | 12088.9051 | 10182.5711 | 739.8709 | 33155.664 | 502.521 | 11225.8673 | 42.0217 | 0 | 0 | 0 | 748.8548 | 1817.6539 | 0 | 70503.9298 | 0 | 70503.3791 | 0.55063 | 503.0716 | 0 | 395.4683 | 333.1058 | 24.2036 | 1084.6321 | 16.4391 | 367.2355 | 1.3747 | 0 | 0 | 0 | 24.4975 | 59.4615 | 0 | 2306.4181 | 0 | 2306.4001 | 0.018013 | 16.4571 | 4.5039 | 0.32726 | 14.6653 | 4.9654 | 0.018587 | 0 | 5.3471 | 0 | 0.33123 | 0 | 0.80398 | 31.1848 | 31.1851 | 0.00024355
NM_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 244754.8149 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111738.1603 | 0 | 0 | 698683.39 | 0 | 698683.39 | 0 | 0 | 1180.942 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 539.1366 | 0 | 0 | 3371.1474 | 0 | 3371.1474 | 0 | 0 | 244.7548 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.7382 | 0 | 0 | 698.6834 | 0 | 698.6834 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.3093 | 1.5108 | 0 | 0 | 9.4469 | 9.4469 | 0
NM_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 114196.3121 | 79216.9361 | 7093.6807 | 312483.1662 | 4743.0133 | 87741.5787 | 730.763 | 0 | 0 | 0 | 7179.8163 | 12400.7431 | 0 | 625786.0096 | 0 | 625787.9546 | -1.945 | 4741.0683 | 0 | 11910.6753 | 8262.3264 | 739.8709 | 32591.9942 | 494.6963 | 9151.4467 | 76.2186 | 0 | 0 | 0 | 748.8548 | 1293.3975 | 0 | 65269.4808 | 0 | 65269.6837 | -0.20286 | 494.4934 | 0 | 389.6378 | 270.2882 | 24.2036 | 1066.1926 | 16.1832 | 299.3743 | 2.4934 | 0 | 0 | 0 | 24.4975 | 42.3113 | 0 | 2135.1819 | 0 | 2135.1885 | -0.0066363 | 16.1765 | 3.6546 | 0.32726 | 14.416 | 4.0478 | 0.033713 | 0 | 5.2683 | 0 | 0.33123 | 0 | 0.57209 | 28.8699 | 28.8698 | -8.973e-05
NM_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 433408.3345 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111671.8131 | 0 | 0 | 887270.5624 | 0 | 887270.5624 | 0 | 0 | 2091.1952 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 538.8165 | 0 | 0 | 4281.0805 | 0 | 4281.0805 | 0 | 0 | 433.4083 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.6718 | 0 | 0 | 887.2706 | 0 | 887.2706 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.8601 | 1.5099 | 0 | 0 | 11.9968 | 11.9968 | 0
NM_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 40314.224 | 84243.3632 | 10689.146 | 53987.5506 | 0 | 46854.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236089.2539 | 0 | 236091.1989 | -1.945 | -1.945 | 0 | 4204.7736 | 8786.5828 | 1114.8779 | 5630.9015 | 0 | 4886.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24624.1092 | 0 | 24624.312 | -0.20286 | -0.20286 | 0 | 137.5521 | 287.4384 | 36.4714 | 184.2055 | 0 | 159.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805.5365 | 0 | 805.5432 | -0.0066363 | -0.0066363 | 11.641 | 1.4771 | 7.4601 | 6.4745 | 0 | 0 | 5.5707 | 0 | 0 | 0 | 0 | 32.6237 | 32.6234 | -0.00026876
NM_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 117301.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88497.6845 | 0 | 0 | 205799.5313 | 0 | 205799.5313 | 0 | 0 | 565.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427.0013 | 0 | 0 | 992.9827 | 0 | 992.9827 | 0 | 0 | 117.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4977 | 0 | 0 | 205.7995 | 0 | 205.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7506 | 3.5841 | 0 | 0 | 8.3347 | 8.3347 | 0
NM_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 37746.8284 | 66938.4499 | 10689.146 | 53987.5506 | 0 | 44834.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214196.927 | 0 | 214196.927 | 0 | 0 | 0 | 3936.9942 | 6981.6803 | 1114.8779 | 5630.9015 | 0 | 4676.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22340.7395 | 0 | 22340.7395 | 0 | 0 | 0 | 128.7922 | 228.394 | 36.4714 | 184.2055 | 0 | 152.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730.8399 | 0 | 730.8399 | 0 | 0 | 9.2497 | 1.4771 | 7.4601 | 6.1954 | 0 | 0 | 5.2159 | 0 | 0 | 0 | 0 | 29.5982 | 29.5982 | 0
NM_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 134893.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88516.6408 | 0 | 0 | 223409.9734 | 0 | 223409.9734 | 0 | 0 | 650.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427.0928 | 0 | 0 | 1077.9531 | 0 | 1077.9531 | 0 | 0 | 134.8933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5166 | 0 | 0 | 223.41 | 0 | 223.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.463 | 3.5848 | 0 | 0 | 9.0479 | 9.0479 | 0
NM_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 8319.0286 | 76821.8116 | 79422.55 | 12311.829 | 154949.5496 | 0 | 48474.8743 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380371.886 | 0 | 380372.4417 | -0.55571 | -0.55571 | 867.6747 | 8012.515 | 8283.772 | 1284.1238 | 16161.238 | 0 | 5055.9294 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 39672.7877 | 0 | 39672.8457 | -0.057961 | -0.057961 | 28.3845 | 262.116 | 270.9897 | 42.008 | 528.6879 | 0 | 165.3963 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.8289 | 0 | 1297.8308 | -0.0018961 | -0.0018961 | 6.2726 | 0.97236 | 12.2376 | 3.8284 | 0.0057056 | 0 | 6.0672 | 0.65702 | 0 | 0 | 0 | 30.041 | 30.0409 | -4.3889e-05
NM_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 21866.141 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 553468.3291 | 0 | 0 | 974829.9079 | 0 | 974829.9079 | 0 | 0 | 105.5041 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2670.4847 | 0 | 0 | 4703.5543 | 0 | 4703.5543 | 0 | 0 | 21.8661 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 553.4683 | 0 | 0 | 974.8299 | 0 | 974.8299 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.50614 | 12.8112 | 0 | 0 | 22.5645 | 22.5645 | 0
NM_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 10505.7606 | 71398.0495 | 50933.9059 | 12311.829 | 154949.5496 | 0 | 51528.5191 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 351699.8564 | 0 | 351700.4121 | -0.55571 | -0.55571 | 1095.7508 | 7446.8166 | 5312.4064 | 1284.1238 | 16161.238 | 0 | 5374.4245 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 36682.295 | 0 | 36682.353 | -0.057961 | -0.057961 | 35.8457 | 243.6101 | 173.7865 | 42.008 | 528.6879 | 0 | 175.8153 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.9999 | 0 | 1200.0018 | -0.0018961 | -0.0018961 | 4.0226 | 0.97236 | 12.2376 | 4.0696 | 0.0057056 | 0 | 5.6389 | 0.82972 | 0 | 0 | 0 | 27.7765 | 27.7765 | -4.3889e-05
NM_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 16852.1884 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 553534.6763 | 0 | 0 | 969882.3026 | 0 | 969882.3026 | 0 | 0 | 81.3118 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2670.8048 | 0 | 0 | 4679.6821 | 0 | 4679.6821 | 0 | 0 | 16.8522 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 553.5347 | 0 | 0 | 969.8823 | 0 | 969.8823 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.39008 | 12.8127 | 0 | 0 | 22.4499 | 22.4499 | 0
NM_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 1100.3124 | 5098.6699 | 8846.9563 | 1569.8902 | 13417.6985 | 0 | 5887.7828 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40925.5087 | 0 | 40926.8979 | -1.3893 | -1.3893 | 114.7626 | 531.7913 | 922.7375 | 163.7395 | 1399.466 | 0 | 614.0957 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 4268.5306 | 0 | 4268.6755 | -0.1449 | -0.1449 | 3.7543 | 17.3967 | 30.1858 | 5.3565 | 45.7812 | 0 | 20.0891 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.6378 | 0 | 139.6426 | -0.0047402 | -0.0047402 | 5.4863 | 0.97355 | 8.3208 | 3.6512 | 0 | 0 | 3.1619 | 0.68235 | 3.1033 | 0 | 0 | 25.3803 | 25.3795 | -0.00086155
NM_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 312.7796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.7796 | 0 | 312.7796 | 0 | 0 | 1.5092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5092 | 0 | 1.5092 | 0 | 0 | 0.31278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31278 | 0 | 0.31278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056848 | 0 | 0 | 0 | 0.056848 | 0.056848 | 0
NM_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 1141.9909 | 4806.9204 | 7127.0235 | 1569.8902 | 13417.6985 | 0 | 5418.205 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38485.9271 | 0 | 38487.0385 | -1.1114 | -1.1114 | 119.1097 | 501.3618 | 743.3486 | 163.7395 | 1399.466 | 0 | 565.1188 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 4014.0822 | 0 | 4014.1981 | -0.11592 | -0.11592 | 3.8965 | 16.4012 | 24.3174 | 5.3565 | 45.7812 | 0 | 18.4869 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.314 | 0 | 131.3178 | -0.0037922 | -0.0037922 | 4.4197 | 0.97355 | 8.3208 | 3.36 | 0 | 0 | 2.981 | 0.70819 | 3.1033 | 0 | 0 | 23.8673 | 23.8666 | -0.00068924
NM_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | NM-ALBUQUERQUE-NM | Zone4B | Zone4B(NM-ALBUQUERQUE-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 369.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6487 | 0 | 369.6487 | 0 | 0 | 1.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7836 | 0 | 1.7836 | 0 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36965 | 0 | 0.36965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067184 | 0 | 0 | 0 | 0.067184 | 0.067184 | 0
NM_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 548703.0127 | 879624.7475 | 95093.6661 | 4077910.5986 | 543457.0788 | 749076.5705 | 80333.9199 | 161759.8165 | 679517.9321 | 0 | 0 | 0 | 0 | 7815477.3429 | 0 | 7815477.065 | 0.27786 | 543457.3567 | 0 | 57229.7242 | 91744.8612 | 9918.2694 | 425326.0754 | 56682.5733 | 78128.6863 | 8378.8278 | 16871.5489 | 70873.7203 | 0 | 0 | 0 | 0 | 815154.2869 | 0 | 815154.2579 | 0.02898 | 56682.6023 | 0 | 1872.1747 | 3001.2796 | 324.4596 | 13913.831 | 1854.2756 | 2555.8493 | 274.0993 | 551.9245 | 2318.5152 | 0 | 0 | 0 | 0 | 26666.4087 | 0 | 26666.4077 | 0.00094805 | 1854.2765 | 6.0196 | 0.65076 | 27.9065 | 5.1262 | 0.54975 | 0 | 3.755 | 0 | 0 | 4.6502 | 0 | 53.4839 | 53.4839 | 1.9015e-06
NM_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 994260.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577609.2311 | 0 | 0 | 1571869.39 | 0 | 1571869.39 | 0 | 0 | 4797.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2786.9645 | 0 | 0 | 7584.2698 | 0 | 7584.2698 | 0 | 0 | 994.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.6092 | 0 | 0 | 1571.8694 | 0 | 1571.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9942 | 1.1585 | 0 | 0 | 3.1526 | 3.1526 | 0
NM_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 512903.9596 | 716553.4475 | 95093.6661 | 4077910.5986 | 543384.8361 | 718634.5939 | 77919.3455 | 144227.0608 | 680115.324 | 0 | 0 | 0 | 0 | 7566742.8321 | 0 | 7566744.2213 | -1.3893 | 543383.4468 | 0 | 53495.883 | 74736.5246 | 9918.2694 | 425326.0754 | 56675.0384 | 74953.5881 | 8126.9877 | 15042.8824 | 70936.0283 | 0 | 0 | 0 | 0 | 789211.2774 | 0 | 789211.4223 | -0.1449 | 56674.8935 | 0 | 1750.0283 | 2444.8804 | 324.4596 | 13913.831 | 1854.0291 | 2451.9812 | 265.8608 | 492.1027 | 2320.5535 | 0 | 0 | 0 | 0 | 25817.7265 | 0 | 25817.7313 | -0.0047402 | 1854.0243 | 4.9036 | 0.65076 | 27.9065 | 4.9179 | 0.53323 | 0 | 3.51 | 0 | 0 | 4.6543 | 0 | 51.7817 | 51.7817 | -9.5073e-06
NM_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 1500119.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577552.3621 | 0 | 0 | 2077671.9961 | 0 | 2077671.9961 | 0 | 0 | 7238.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2786.6901 | 0 | 0 | 10024.7674 | 0 | 10024.7674 | 0 | 0 | 1500.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5524 | 0 | 0 | 2077.672 | 0 | 2077.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0087 | 1.1584 | 0 | 0 | 4.1671 | 4.1671 | 0
NM_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 22056.2623 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 21317.1636 | 0 | 0 | 0 | 0 | 115830.1093 | 0 | 0 | 336792.8461 | 0 | 336794.7911 | -1.945 | -1.945 | 0 | 2300.4682 | 2959.4836 | 752.0427 | 14811.0388 | 0 | 2223.3802 | 0 | 0 | 0 | 0 | 12081.0804 | 0 | 0 | 35127.4939 | 0 | 35127.6967 | -0.20286 | -0.20286 | 0 | 75.256 | 96.8146 | 24.6018 | 484.5184 | 0 | 72.7342 | 0 | 0 | 0 | 0 | 395.2123 | 0 | 0 | 1149.1372 | 0 | 1149.1438 | -0.0066363 | -0.0066363 | 2.8693 | 0.72914 | 14.3599 | 2.1557 | 0 | 0 | 2.2304 | 0 | 11.7131 | 0 | 0 | 34.0578 | 34.0576 | -0.00019668
NM_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 129433.9059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129433.9059 | 0 | 129433.9059 | 0 | 0 | 624.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624.5186 | 0 | 624.5186 | 0 | 0 | 129.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4339 | 0 | 129.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8361 | 0 | 0 | 0 | 3.8361 | 3.8361 | 0
NM_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 26110.1911 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21742.2843 | 0 | 0 | 0 | 0 | 115680.0667 | 0 | 0 | 335928.7119 | 0 | 335931.4905 | -2.7786 | -2.7786 | 0 | 2723.2929 | 2417.839 | 752.0427 | 14811.0388 | 0 | 2267.7203 | 0 | 0 | 0 | 0 | 12065.431 | 0 | 0 | 35037.3647 | 0 | 35037.6545 | -0.2898 | -0.2898 | 0 | 89.088 | 79.0956 | 24.6018 | 484.5184 | 0 | 74.1847 | 0 | 0 | 0 | 0 | 394.7004 | 0 | 0 | 1146.1888 | 0 | 1146.1982 | -0.0094805 | -0.0094805 | 2.3442 | 0.72914 | 14.3599 | 2.1987 | 0 | 0 | 2.6403 | 0 | 11.6979 | 0 | 0 | 33.9705 | 33.9702 | -0.00028098
NM_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 52319.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52319.505 | 0 | 52319.505 | 0 | 0 | 252.4416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.4416 | 0 | 252.4416 | 0 | 0 | 52.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.3195 | 0 | 52.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5506 | 0 | 0 | 0 | 1.5506 | 1.5506 | 0
NM_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 78619.5443 | 97049.7771 | 7102.0164 | 317887.4784 | 4818.0346 | 104126.7864 | 614.0632 | 0 | 0 | 0 | 7179.8163 | 17443.8416 | 0 | 634841.3585 | 0 | 634839.9692 | 1.3893 | 4819.4239 | 0 | 8200.0185 | 10122.2917 | 740.7403 | 33155.664 | 502.521 | 10860.4238 | 64.0468 | 0 | 0 | 0 | 748.8548 | 1819.3927 | 0 | 66213.9537 | 0 | 66213.8088 | 0.1449 | 502.6659 | 0 | 268.2499 | 331.1338 | 24.2321 | 1084.6321 | 16.4391 | 355.2806 | 2.0952 | 0 | 0 | 0 | 24.4975 | 59.5184 | 0 | 2166.0787 | 0 | 2166.074 | 0.0047402 | 16.4439 | 4.4773 | 0.32764 | 14.6653 | 4.8038 | 0.028329 | 0 | 3.627 | 0 | 0.33123 | 0 | 0.80475 | 29.2875 | 29.2876 | 6.4093e-05
NM_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 391931.8573 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120012.6037 | 0 | 0 | 854134.8759 | 0 | 854134.8759 | 0 | 0 | 1891.0712 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0608 | 0 | 0 | 4121.2008 | 0 | 4121.2008 | 0 | 0 | 391.9319 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0126 | 0 | 0 | 854.1349 | 0 | 854.1349 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.2993 | 1.6227 | 0 | 0 | 11.5488 | 11.5488 | 0
NM_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 75535.3353 | 78847.3867 | 7102.0164 | 312483.1662 | 4743.0133 | 82976.3368 | 1005.8411 | 0 | 0 | 0 | 7179.8163 | 12411.8574 | 0 | 582284.7697 | 0 | 582285.3254 | -0.55571 | 4742.4576 | 0 | 7878.3355 | 8223.7824 | 740.7403 | 32591.9942 | 494.6963 | 8654.4319 | 104.9092 | 0 | 0 | 0 | 748.8548 | 1294.5567 | 0 | 60732.3015 | 0 | 60732.3594 | -0.057961 | 494.6383 | 0 | 257.7266 | 269.0273 | 24.2321 | 1066.1926 | 16.1832 | 283.1153 | 3.4319 | 0 | 0 | 0 | 24.4975 | 42.3493 | 0 | 1986.7556 | 0 | 1986.7575 | -0.0018961 | 16.1813 | 3.6375 | 0.32764 | 14.416 | 3.828 | 0.046403 | 0 | 3.4847 | 0 | 0.33123 | 0 | 0.5726 | 26.863 | 26.8629 | -2.5637e-05
NM_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 632620.5367 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119927.3002 | 0 | 0 | 1094738.2518 | 0 | 1094738.2518 | 0 | 0 | 3052.3941 | 0 | 0 | 0 | 1651.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 578.6492 | 0 | 0 | 5282.1121 | 0 | 5282.1121 | 0 | 0 | 632.6205 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.9273 | 0 | 0 | 1094.7383 | 0 | 1094.7383 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.5537 | 1.6215 | 0 | 0 | 14.802 | 14.802 | 0
NM_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 27894.0309 | 84726.8338 | 10686.3675 | 53987.5506 | 0 | 46713.2631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224008.0459 | 0 | 224003.6002 | 4.4457 | 4.4457 | 0 | 2909.3474 | 8837.0088 | 1114.5881 | 5630.9015 | 0 | 4872.1933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23364.0392 | 0 | 23363.5755 | 0.46369 | 0.46369 | 0 | 95.1744 | 289.088 | 36.4619 | 184.2055 | 0 | 159.3857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.3155 | 0 | 764.3003 | 0.015169 | 0.015169 | 11.7078 | 1.4767 | 7.4601 | 6.455 | 0 | 0 | 3.8545 | 0 | 0 | 0 | 0 | 30.9534 | 30.954 | 0.00061432
NM_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 189819.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91085.2252 | 0 | 0 | 280904.5599 | 0 | 280904.5599 | 0 | 0 | 915.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.4862 | 0 | 0 | 1355.3645 | 0 | 1355.3645 | 0 | 0 | 189.8193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0852 | 0 | 0 | 280.9046 | 0 | 280.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6875 | 3.6889 | 0 | 0 | 11.3763 | 11.3763 | 0
NM_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 0 | 25287.7354 | 67269.0994 | 10686.3675 | 53987.5506 | 0 | 48247.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205477.7847 | 0 | 205474.4504 | 3.3343 | 3.3343 | 0 | 2637.5108 | 7016.1671 | 1114.5881 | 5630.9015 | 0 | 5032.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21431.3329 | 0 | 21430.9852 | 0.34777 | 0.34777 | 0 | 86.2818 | 229.5222 | 36.4619 | 184.2055 | 0 | 164.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 701.0902 | 0 | 701.0788 | 0.011377 | 0.011377 | 9.2954 | 1.4767 | 7.4601 | 6.6669 | 0 | 0 | 3.4943 | 0 | 0 | 0 | 0 | 28.393 | 28.3934 | 0.00046074
NM_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 211107.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91094.7034 | 0 | 0 | 302202.0105 | 0 | 302202.0105 | 0 | 0 | 1018.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.5319 | 0 | 0 | 1458.1247 | 0 | 1458.1247 | 0 | 0 | 211.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0947 | 0 | 0 | 302.202 | 0 | 302.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5496 | 3.6892 | 0 | 0 | 12.2389 | 12.2389 | 0
NM_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 14856.9961 | 62356.5935 | 79450.3357 | 12314.6075 | 154949.5496 | 0 | 54282.0787 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 378282.4038 | 0 | 378285.1824 | -2.7786 | -2.7786 | 1549.5847 | 6503.7927 | 8286.67 | 1284.4136 | 16161.238 | 0 | 5661.6208 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 39454.8547 | 0 | 39455.1445 | -0.2898 | -0.2898 | 50.6921 | 212.7607 | 271.0845 | 42.0174 | 528.6879 | 0 | 185.2105 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.6996 | 0 | 1290.709 | -0.0094805 | -0.0094805 | 6.2748 | 0.97258 | 12.2376 | 4.2871 | 0.0057056 | 0 | 4.9248 | 1.1734 | 0 | 0 | 0 | 29.8761 | 29.8759 | -0.00021945
NM_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 28140.6903 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 603484.6385 | 0 | 0 | 1031120.7667 | 0 | 1031120.7667 | 0 | 0 | 135.7788 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2911.8134 | 0 | 0 | 4975.1577 | 0 | 4975.1577 | 0 | 0 | 28.1407 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 603.4846 | 0 | 0 | 1031.1208 | 0 | 1031.1208 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.65137 | 13.9689 | 0 | 0 | 23.8674 | 23.8674 | 0
NM_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 18030.1192 | 57588.5731 | 50967.2487 | 12314.6075 | 154949.5496 | 0 | 51189.534 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 345111.8748 | 0 | 345110.7634 | 1.1114 | 1.1114 | 1880.5414 | 6006.4882 | 5315.884 | 1284.4136 | 16161.238 | 0 | 5339.0684 | 7.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 35995.1685 | 0 | 35995.0526 | 0.11592 | 0.11592 | 61.5188 | 196.4922 | 173.9003 | 42.0174 | 528.6879 | 0 | 174.6587 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.5217 | 0 | 1177.5179 | 0.0037922 | 0.0037922 | 4.0253 | 0.97258 | 12.2376 | 4.0428 | 0.0057056 | 0 | 4.5482 | 1.424 | 0 | 0 | 0 | 27.2561 | 27.2562 | 8.7778e-05
NM_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 31628.6573 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 603550.9857 | 0 | 0 | 1034675.0809 | 0 | 1034675.0809 | 0 | 0 | 152.6083 | 0 | 0 | 0 | 1927.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2912.1335 | 0 | 0 | 4992.3073 | 0 | 4992.3073 | 0 | 0 | 31.6287 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 603.551 | 0 | 0 | 1034.6751 | 0 | 1034.6751 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.73211 | 13.9704 | 0 | 0 | 23.9497 | 23.9497 | 0
NM_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 1995.0109 | 3570.4582 | 8841.3992 | 1578.2259 | 13417.6985 | 0 | 5704.3974 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40111.3886 | 0 | 40107.4986 | 3.89 | 3.89 | 208.0796 | 372.3988 | 922.1579 | 164.609 | 1399.466 | 0 | 594.9686 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 4183.6178 | 0 | 4183.2121 | 0.40573 | 0.40573 | 6.807 | 12.1824 | 30.1669 | 5.3849 | 45.7812 | 0 | 19.4634 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.8601 | 0 | 136.8468 | 0.013273 | 0.013273 | 5.4829 | 0.97872 | 8.3208 | 3.5375 | 0 | 0 | 2.2142 | 1.2372 | 3.1033 | 0 | 0 | 24.8722 | 24.8746 | 0.0024123
NM_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 2701.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2701.2788 | 0 | 2701.2788 | 0 | 0 | 13.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0337 | 0 | 13.0337 | 0 | 0 | 2.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7013 | 0 | 2.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49096 | 0 | 0 | 0 | 0.49096 | 0.49096 | 0
NM_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Electricity | 2045.0251 | 3328.7229 | 7124.245 | 1578.2259 | 13417.6985 | 0 | 5201.4768 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37699.5927 | 0 | 37699.5927 | 0 | 0 | 213.2961 | 347.1858 | 743.0588 | 164.609 | 1399.466 | 0 | 542.514 | 0 | 0 | 0 | 0 | 521.9379 | 0 | 0 | 3932.0675 | 0 | 3932.0675 | 0 | 0 | 6.9776 | 11.3576 | 24.3079 | 5.3849 | 45.7812 | 0 | 17.7474 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.631 | 0 | 128.631 | 0 | 0 | 4.418 | 0.97872 | 8.3208 | 3.2256 | 0 | 0 | 2.0643 | 1.2682 | 3.1033 | 0 | 0 | 23.379 | 23.379 | 0
NM_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | NM-GALLUP-NM | Zone5B | Zone5B(NM-GALLUP-NM) |  |  | NM | 0.1043 | 0.004825 |  |  |  | Natural Gas | 2919.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.2767 | 0 | 2919.2767 | 0 | 0 | 14.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.0855 | 0 | 14.0855 | 0 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9193 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53058 | 0 | 0 | 0 | 0.53058 | 0.53058 | 0
NV_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 1014376.8959 | 883086.8416 | 94976.9663 | 4077910.5986 | 543459.8574 | 639239.8295 | 125113.3006 | 317631.8503 | 565168.7989 | 0 | 0 | 0 | 0 | 8260964.9391 | 0 | 8260959.382 | 5.5571 | 543465.4145 | 0 | 76889.7687 | 66937.9826 | 7199.254 | 309105.6234 | 41194.2572 | 48454.3791 | 9483.5882 | 24076.4943 | 42839.795 | 0 | 0 | 0 | 0 | 626181.1424 | 0 | 626180.7212 | 0.42123 | 41194.6784 | 0 | 3461.054 | 3013.0923 | 324.0614 | 13913.831 | 1854.285 | 2181.0863 | 426.8866 | 1083.7599 | 1928.3559 | 0 | 0 | 0 | 0 | 28186.4124 | 0 | 28186.3934 | 0.018961 | 1854.304 | 6.0433 | 0.64996 | 27.9065 | 4.3745 | 0.85619 | 0 | 6.9417 | 0 | 0 | 3.8676 | 0 | 56.5324 | 56.5325 | 3.8029e-05
NV_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 274402.5344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465937.418 | 0 | 0 | 740339.9524 | 0 | 740339.9524 | 0 | 0 | 1915.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.7772 | 0 | 0 | 5166.8325 | 0 | 5166.8325 | 0 | 0 | 274.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465.9374 | 0 | 0 | 740.34 | 0 | 740.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55036 | 0.93451 | 0 | 0 | 1.4849 | 1.4849 | 0
NV_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 957310.6933 | 718481.7727 | 94976.9663 | 4077910.5986 | 543387.6147 | 624293.9193 | 120748.1723 | 285086.4987 | 565141.0132 | 0 | 0 | 0 | 0 | 7987337.2493 | 0 | 7987336.9715 | 0.27786 | 543387.8925 | 0 | 72564.1506 | 54460.9184 | 7199.254 | 309105.6234 | 41188.7812 | 47321.4791 | 9152.7115 | 21609.5566 | 42837.6888 | 0 | 0 | 0 | 0 | 605440.1635 | 0 | 605440.1424 | 0.021062 | 41188.8023 | 0 | 3266.3441 | 2451.4598 | 324.0614 | 13913.831 | 1854.0385 | 2130.0909 | 411.9928 | 972.7151 | 1928.2611 | 0 | 0 | 0 | 0 | 27252.7947 | 0 | 27252.7937 | 0.00094805 | 1854.0395 | 4.9168 | 0.64996 | 27.9065 | 4.2722 | 0.82632 | 0 | 6.5512 | 0 | 0 | 3.8674 | 0 | 54.6599 | 54.6599 | 1.9015e-06
NV_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 534293.9887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465984.8089 | 0 | 0 | 1000278.7976 | 0 | 1000278.7976 | 0 | 0 | 3728.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3252.108 | 0 | 0 | 6980.9457 | 0 | 6980.9457 | 0 | 0 | 534.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465.9848 | 0 | 0 | 1000.2788 | 0 | 1000.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0716 | 0.93461 | 0 | 0 | 2.0062 | 2.0062 | 0
NV_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 55179.5557 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 28157.9948 | 0 | 0 | 0 | 0 | 93762.7327 | 0 | 0 | 354684.037 | 0 | 354682.3699 | 1.6671 | 1.6671 | 0 | 4182.6103 | 2150.804 | 546.1256 | 10763.9189 | 0 | 2134.376 | 0 | 0 | 0 | 0 | 7107.2151 | 0 | 0 | 26885.05 | 0 | 26884.9236 | 0.12637 | 0.12637 | 0 | 188.2726 | 96.8146 | 24.5829 | 484.5184 | 0 | 96.0751 | 0 | 0 | 0 | 0 | 319.9184 | 0 | 0 | 1210.1819 | 0 | 1210.1762 | 0.0056883 | 0.0056883 | 2.8693 | 0.72858 | 14.3599 | 2.8474 | 0 | 0 | 5.5799 | 0 | 9.4816 | 0 | 0 | 35.8666 | 35.8668 | 0.00016859
NV_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 41144.7412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41144.7412 | 0 | 41144.7412 | 0 | 0 | 287.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287.1491 | 0 | 287.1491 | 0 | 0 | 41.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.1447 | 0 | 41.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2194 | 0 | 0 | 0 | 1.2194 | 1.2194 | 0
NV_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 52339.8606 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 27593.9457 | 0 | 0 | 0 | 0 | 93659.9257 | 0 | 0 | 345984.3447 | 0 | 345987.1233 | -2.7786 | -2.7786 | 0 | 3967.3614 | 1757.1639 | 546.1256 | 10763.9189 | 0 | 2091.6211 | 0 | 0 | 0 | 0 | 7099.4224 | 0 | 0 | 26225.6133 | 0 | 26225.8239 | -0.21062 | -0.21062 | 0 | 178.5836 | 79.0956 | 24.5829 | 484.5184 | 0 | 94.1505 | 0 | 0 | 0 | 0 | 319.5677 | 0 | 0 | 1180.4986 | 0 | 1180.5081 | -0.0094805 | -0.0094805 | 2.3442 | 0.72858 | 14.3599 | 2.7904 | 0 | 0 | 5.2928 | 0 | 9.4712 | 0 | 0 | 34.9873 | 34.9871 | -0.00028098
NV_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 16823.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16823.7539 | 0 | 16823.7539 | 0 | 0 | 117.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.413 | 0 | 117.413 | 0 | 0 | 16.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8238 | 0 | 16.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49861 | 0 | 0 | 0 | 0.49861 | 0.49861 | 0
NV_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 208798.1719 | 102926.4456 | 7115.9093 | 317887.4784 | 4818.0346 | 113737.8486 | 219.5068 | 0 | 0 | 0 | 7179.8163 | 17393.8274 | 0 | 780077.0389 | 0 | 780079.2618 | -2.2229 | 4815.8118 | 0 | 15826.9014 | 7801.8246 | 539.3859 | 24095.8709 | 365.207 | 8621.3289 | 16.6386 | 0 | 0 | 0 | 544.2301 | 1318.4521 | 0 | 59129.8396 | 0 | 59130.008 | -0.16849 | 365.0385 | 0 | 712.4194 | 351.185 | 24.2795 | 1084.6321 | 16.4391 | 388.0735 | 0.74896 | 0 | 0 | 0 | 24.4975 | 59.3477 | 0 | 2661.6229 | 0 | 2661.6304 | -0.0075844 | 16.4315 | 4.7484 | 0.32828 | 14.6653 | 5.2471 | 0.010127 | 0 | 9.6326 | 0 | 0.33123 | 0 | 0.80244 | 35.9879 | 35.9878 | -0.00010255
NV_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 129016.8664 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 98895.2383 | 0 | 0 | 570102.5195 | 0 | 570102.5195 | 0 | 0 | 900.4087 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 690.1899 | 0 | 0 | 3978.7455 | 0 | 3978.7455 | 0 | 0 | 129.0169 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8952 | 0 | 0 | 570.1025 | 0 | 570.1025 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.7444 | 1.3372 | 0 | 0 | 7.7084 | 7.7084 | 0
NV_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 213794.0348 | 83123.6009 | 7115.9093 | 312483.1662 | 4745.7919 | 96844.1631 | 369.5494 | 0 | 0 | 0 | 7179.8163 | 12384.0717 | 0 | 738040.1036 | 0 | 738040.6593 | -0.55571 | 4745.2362 | 0 | 16205.5878 | 6300.7689 | 539.3859 | 23686.224 | 359.731 | 7340.7876 | 28.0118 | 0 | 0 | 0 | 544.2301 | 938.7126 | 0 | 55943.4399 | 0 | 55943.482 | -0.042123 | 359.6889 | 0 | 729.4652 | 283.6177 | 24.2795 | 1066.1926 | 16.1926 | 330.4323 | 1.2609 | 0 | 0 | 0 | 24.4975 | 42.2545 | 0 | 2518.1928 | 0 | 2518.1947 | -0.0018961 | 16.1907 | 3.8348 | 0.32828 | 14.416 | 4.4678 | 0.017049 | 0 | 9.8631 | 0 | 0.33123 | 0 | 0.57132 | 34.0485 | 34.0485 | -2.5637e-05
NV_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 210178.4464 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 98828.8911 | 0 | 0 | 651197.7523 | 0 | 651197.7523 | 0 | 0 | 1466.8354 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 689.7268 | 0 | 0 | 4544.7091 | 0 | 4544.7091 | 0 | 0 | 210.1784 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8289 | 0 | 0 | 651.1978 | 0 | 651.1978 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.8418 | 1.3363 | 0 | 0 | 8.8048 | 8.8048 | 0
NV_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 75096.3217 | 85496.4968 | 10761.3888 | 53987.5506 | 0 | 41111.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266453.4306 | 0 | 266454.542 | -1.1114 | -1.1114 | 0 | 5692.3012 | 6480.6345 | 815.7133 | 4092.2563 | 0 | 3116.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20197.17 | 0 | 20197.2543 | -0.084246 | -0.084246 | 0 | 256.2286 | 291.714 | 36.7179 | 184.2055 | 0 | 140.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909.1391 | 0 | 909.1429 | -0.0037922 | -0.0037922 | 11.8141 | 1.487 | 7.4601 | 5.6809 | 0 | 0 | 10.377 | 0 | 0 | 0 | 0 | 36.8193 | 36.8192 | -0.00015358
NV_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 52945.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84355.7237 | 0 | 0 | 137300.788 | 0 | 137300.788 | 0 | 0 | 369.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.7186 | 0 | 0 | 958.2222 | 0 | 958.2222 | 0 | 0 | 52.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3557 | 0 | 0 | 137.3008 | 0 | 137.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1442 | 3.4163 | 0 | 0 | 5.5605 | 5.5605 | 0
NV_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 71000.7144 | 67924.8411 | 10761.3888 | 53987.5506 | 0 | 39083.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242757.8139 | 0 | 242758.3696 | -0.55571 | -0.55571 | 0 | 5381.8542 | 5148.703 | 815.7133 | 4092.2563 | 0 | 2962.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18401.0423 | 0 | 18401.0844 | -0.042123 | -0.042123 | 0 | 242.2544 | 231.7596 | 36.7179 | 184.2055 | 0 | 133.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.2897 | 0 | 828.2916 | -0.0018961 | -0.0018961 | 9.386 | 1.487 | 7.4601 | 5.4006 | 0 | 0 | 9.811 | 0 | 0 | 0 | 0 | 33.5449 | 33.5449 | -7.679e-05
NV_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 64584.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84374.68 | 0 | 0 | 148958.9386 | 0 | 148958.9386 | 0 | 0 | 450.7335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.8509 | 0 | 0 | 1039.5844 | 0 | 1039.5844 | 0 | 0 | 64.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3747 | 0 | 0 | 148.9589 | 0 | 148.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6156 | 3.4171 | 0 | 0 | 6.0327 | 6.0327 | 0
NV_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 4067.8216 | 105916.1834 | 80642.3408 | 12306.2718 | 154949.5496 | 0 | 48416.5244 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 406370.9344 | 0 | 406371.4901 | -0.55571 | -0.55571 | 308.3409 | 8028.4467 | 6112.6894 | 932.8154 | 11745.1759 | 0 | 3669.9726 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 30802.9168 | 0 | 30802.959 | -0.042123 | -0.042123 | 13.8794 | 361.386 | 275.1517 | 41.989 | 528.6879 | 0 | 165.1972 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.5376 | 0 | 1386.5395 | -0.0018961 | -0.0018961 | 6.369 | 0.97192 | 12.2376 | 3.8238 | 0.0057056 | 0 | 8.365 | 0.32127 | 0 | 0 | 0 | 32.0943 | 32.0943 | -4.3889e-05
NV_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 9402.3458 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 481367.8807 | 0 | 0 | 890265.6645 | 0 | 890265.6645 | 0 | 0 | 65.619 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 3359.4664 | 0 | 0 | 6213.1641 | 0 | 6213.1641 | 0 | 0 | 9.4023 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 481.3679 | 0 | 0 | 890.2657 | 0 | 890.2657 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.21764 | 11.1423 | 0 | 0 | 20.607 | 20.607 | 0
NV_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 5126.4555 | 99967.2721 | 51650.7761 | 12306.2718 | 154949.5496 | 0 | 45990.8357 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 370063.4036 | 0 | 370065.3486 | -1.945 | -1.945 | 388.5853 | 7577.5192 | 3915.1288 | 932.8154 | 11745.1759 | 0 | 3486.1053 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28050.806 | 0 | 28050.9534 | -0.14743 | -0.14743 | 17.4915 | 341.0883 | 176.2324 | 41.989 | 528.6879 | 0 | 156.9207 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6563 | 0 | 1262.663 | -0.0066363 | -0.0066363 | 4.0793 | 0.97192 | 12.2376 | 3.6323 | 0.0057056 | 0 | 7.8952 | 0.40488 | 0 | 0 | 0 | 29.227 | 29.2268 | -0.00015361
NV_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 11497.0217 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 481443.7061 | 0 | 0 | 892436.1657 | 0 | 892436.1657 | 0 | 0 | 80.2377 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 3359.9956 | 0 | 0 | 6228.312 | 0 | 6228.312 | 0 | 0 | 11.497 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 481.4437 | 0 | 0 | 892.4362 | 0 | 892.4362 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.26612 | 11.144 | 0 | 0 | 20.6573 | 20.6573 | 0
NV_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 444.5707 | 8602.4424 | 9063.6845 | 1569.8902 | 13417.6985 | 0 | 6193.4251 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 44295.9101 | 0 | 44293.6872 | 2.2229 | 2.2229 | 33.6985 | 652.0651 | 687.0273 | 118.9977 | 1017.0615 | 0 | 469.4616 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 3357.63 | 0 | 3357.4615 | 0.16849 | 0.16849 | 1.5169 | 29.3515 | 30.9253 | 5.3565 | 45.7812 | 0 | 21.132 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 151.1376 | 0 | 151.1301 | 0.0075844 | 0.0075844 | 5.6207 | 0.97355 | 8.3208 | 3.8408 | 0 | 0 | 5.3347 | 0.2757 | 3.1033 | 0 | 0 | 27.4682 | 27.4696 | 0.0013785
NV_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 56.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.869 | 0 | 56.869 | 0 | 0 | 0.39689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39689 | 0 | 0.39689 | 0 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056869 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010336 | 0 | 0 | 0 | 0.010336 | 0.010336 | 0
NV_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 466.7992 | 8230.1145 | 7288.1804 | 1569.8902 | 13417.6985 | 0 | 5754.4116 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41731.293 | 0 | 41727.9587 | 3.3343 | 3.3343 | 35.3834 | 623.8427 | 552.4441 | 118.9977 | 1017.0615 | 0 | 436.1844 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 3163.232 | 0 | 3162.9793 | 0.25274 | 0.25274 | 1.5927 | 28.0812 | 24.8673 | 5.3565 | 45.7812 | 0 | 19.6341 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.3872 | 0 | 142.3758 | 0.011377 | 0.011377 | 4.5197 | 0.97355 | 8.3208 | 3.5685 | 0 | 0 | 5.1038 | 0.28948 | 3.1033 | 0 | 0 | 25.8771 | 25.8792 | 0.0020677
NV_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | NV-LASVEGAS-NV | Zone3B | Zone3B(NV-LASVEGAS-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 66.3472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3472 | 0 | 66.3472 | 0 | 0 | 0.46304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46304 | 0 | 0.46304 | 0 | 0 | 0.066347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066347 | 0 | 0.066347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012059 | 0 | 0 | 0 | 0.012059 | 0.012059 | 0
NV_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 588717.1515 | 880124.8895 | 95238.1516 | 4077910.5986 | 543457.0788 | 704808.4461 | 81934.3743 | 161923.752 | 738631.9383 | 0 | 0 | 0 | 0 | 7872746.3808 | 0 | 7872744.7137 | 1.6671 | 543458.746 | 0 | 44624.7601 | 66713.4666 | 7219.0519 | 309105.6234 | 41194.0466 | 53424.4802 | 6210.6256 | 12273.8204 | 55988.3009 | 0 | 0 | 0 | 0 | 596754.1757 | 0 | 596754.0493 | 0.12637 | 41194.1729 | 0 | 2008.7029 | 3002.9861 | 324.9526 | 13913.831 | 1854.2756 | 2404.8064 | 279.5601 | 552.4838 | 2520.2122 | 0 | 0 | 0 | 0 | 26861.8107 | 0 | 26861.805 | 0.0056883 | 1854.2812 | 6.023 | 0.65175 | 27.9065 | 4.8232 | 0.5607 | 0 | 4.0288 | 0 | 0 | 5.0547 | 0 | 53.8758 | 53.8758 | 1.1409e-05
NV_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 987151.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562320.941 | 0 | 0 | 1549472.4714 | 0 | 1549472.4714 | 0 | 0 | 6889.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3924.4378 | 0 | 0 | 10813.7684 | 0 | 10813.7684 | 0 | 0 | 987.1515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.3209 | 0 | 0 | 1549.4725 | 0 | 1549.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9799 | 1.1278 | 0 | 0 | 3.1077 | 3.1077 | 0
NV_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 547916.6784 | 717064.7037 | 95238.1516 | 4077910.5986 | 543387.6147 | 686914.4767 | 79650.3925 | 144271.5178 | 739312.6871 | 0 | 0 | 0 | 0 | 7631666.8212 | 0 | 7631664.8762 | 1.945 | 543389.5597 | 0 | 41532.0842 | 54353.5045 | 7219.0519 | 309105.6234 | 41188.7812 | 52068.1173 | 6037.4998 | 10935.7811 | 56039.9017 | 0 | 0 | 0 | 0 | 578480.345 | 0 | 578480.1976 | 0.14743 | 41188.9286 | 0 | 1869.4917 | 2446.6248 | 324.9526 | 13913.831 | 1854.0385 | 2343.7522 | 271.7671 | 492.2544 | 2522.5349 | 0 | 0 | 0 | 0 | 26039.2472 | 0 | 26039.2406 | 0.0066363 | 1854.0452 | 4.9071 | 0.65175 | 27.9065 | 4.7008 | 0.54507 | 0 | 3.7496 | 0 | 0 | 5.0594 | 0 | 52.226 | 52.226 | 1.331e-05
NV_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 1569461.9345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562396.7663 | 0 | 0 | 2131858.7008 | 0 | 2131858.7008 | 0 | 0 | 10953.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3924.967 | 0 | 0 | 14878.2419 | 0 | 14878.2419 | 0 | 0 | 1569.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.3968 | 0 | 0 | 2131.8587 | 0 | 2131.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1478 | 1.128 | 0 | 0 | 4.2758 | 4.2758 | 0
NV_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 24684.7864 | 28374.723 | 7207.602 | 142004.2074 | 0 | 22548.0686 | 0 | 0 | 0 | 0 | 112912.6143 | 0 | 0 | 337732.0017 | 0 | 337732.2795 | -0.27786 | -0.27786 | 0 | 1871.1068 | 2150.804 | 546.3362 | 10763.9189 | 0 | 1709.1436 | 0 | 0 | 0 | 0 | 8558.7762 | 0 | 0 | 25600.0857 | 0 | 25600.1068 | -0.021062 | -0.021062 | 0 | 84.2245 | 96.8146 | 24.5923 | 484.5184 | 0 | 76.934 | 0 | 0 | 0 | 0 | 385.2578 | 0 | 0 | 1152.3416 | 0 | 1152.3425 | -0.00094805 | -0.00094805 | 2.8693 | 0.72886 | 14.3599 | 2.2801 | 0 | 0 | 2.4962 | 0 | 11.4181 | 0 | 0 | 34.1526 | 34.1526 | -2.8098e-05
NV_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 148380.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148380.7701 | 0 | 148380.7701 | 0 | 0 | 1035.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.5494 | 0 | 1035.5494 | 0 | 0 | 148.3808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148.3808 | 0 | 148.3808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3976 | 0 | 0 | 0 | 4.3976 | 4.3976 | 0
NV_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 27007.6682 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 22311.8905 | 0 | 0 | 0 | 0 | 112770.9074 | 0 | 0 | 334483.8572 | 0 | 334487.4694 | -3.6121 | -3.6121 | 0 | 2047.1812 | 1757.1639 | 546.3362 | 10763.9189 | 0 | 1691.2413 | 0 | 0 | 0 | 0 | 8548.0348 | 0 | 0 | 25353.8764 | 0 | 25354.1502 | -0.2738 | -0.2738 | 0 | 92.1502 | 79.0956 | 24.5923 | 484.5184 | 0 | 76.1282 | 0 | 0 | 0 | 0 | 384.7743 | 0 | 0 | 1141.2589 | 0 | 1141.2712 | -0.012325 | -0.012325 | 2.3442 | 0.72886 | 14.3599 | 2.2563 | 0 | 0 | 2.7311 | 0 | 11.4038 | 0 | 0 | 33.8245 | 33.8241 | -0.00036527
NV_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 66062.8533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66062.8533 | 0 | 66062.8533 | 0 | 0 | 461.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461.0527 | 0 | 461.0527 | 0 | 0 | 66.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0629 | 0 | 66.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9579 | 0 | 0 | 0 | 1.9579 | 1.9579 | 0
NV_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 93215.3551 | 98828.0598 | 7121.4664 | 317887.4784 | 4818.0346 | 106655.2821 | 614.0632 | 0 | 0 | 0 | 7179.8163 | 17407.7203 | 0 | 653727.2762 | 0 | 653725.0533 | 2.2229 | 4820.2575 | 0 | 7065.7239 | 7491.1669 | 539.8072 | 24095.8709 | 365.207 | 8084.4704 | 46.546 | 0 | 0 | 0 | 544.2301 | 1319.5052 | 0 | 49552.5275 | 0 | 49552.359 | 0.16849 | 365.3755 | 0 | 318.0508 | 337.2013 | 24.2984 | 1084.6321 | 16.4391 | 363.9078 | 2.0952 | 0 | 0 | 0 | 24.4975 | 59.3951 | 0 | 2230.5175 | 0 | 2230.5099 | 0.0075844 | 16.4467 | 4.5593 | 0.32854 | 14.6653 | 4.9204 | 0.028329 | 0 | 4.3004 | 0 | 0.33123 | 0 | 0.80308 | 30.1587 | 30.1588 | 0.00010255
NV_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 388121.6325 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117415.5848 | 0 | 0 | 847727.6321 | 0 | 847727.6321 | 0 | 0 | 2708.7009 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 819.4434 | 0 | 0 | 5916.2911 | 0 | 5916.2911 | 0 | 0 | 388.1216 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.4156 | 0 | 0 | 847.7276 | 0 | 847.7276 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.2478 | 1.5876 | 0 | 0 | 11.4621 | 11.4621 | 0
NV_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 92417.9064 | 80345.0342 | 7121.4664 | 312483.1662 | 4745.7919 | 82937.4369 | 1055.8553 | 0 | 0 | 0 | 7179.8163 | 12395.186 | 0 | 600681.6597 | 0 | 600685.2718 | -3.6121 | 4742.1798 | 0 | 7005.2773 | 6090.1536 | 539.8072 | 23686.224 | 359.731 | 6286.6577 | 80.0338 | 0 | 0 | 0 | 544.2301 | 939.5551 | 0 | 45531.6698 | 0 | 45531.9436 | -0.2738 | 359.4572 | 0 | 315.3299 | 274.1373 | 24.2984 | 1066.1926 | 16.1926 | 282.9825 | 3.6026 | 0 | 0 | 0 | 24.4975 | 42.2924 | 0 | 2049.5258 | 0 | 2049.5381 | -0.012325 | 16.1803 | 3.7066 | 0.32854 | 14.416 | 3.8262 | 0.04871 | 0 | 4.2636 | 0 | 0.33123 | 0 | 0.57184 | 27.7118 | 27.7116 | -0.00016664
NV_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 659292.1105 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117320.8031 | 0 | 0 | 1118803.3284 | 0 | 1118803.3284 | 0 | 0 | 4601.1996 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 818.7819 | 0 | 0 | 7808.1284 | 0 | 7808.1284 | 0 | 0 | 659.2921 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3208 | 0 | 0 | 1118.8033 | 0 | 1118.8033 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.9143 | 1.5863 | 0 | 0 | 15.1273 | 15.1273 | 0
NV_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 32951.0223 | 86116.1172 | 10755.8316 | 53987.5506 | 0 | 46832.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230643.2632 | 0 | 230641.3182 | 1.945 | 1.945 | 0 | 2497.6875 | 6527.6017 | 815.292 | 4092.2563 | 0 | 3549.9218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17482.7593 | 0 | 17482.6119 | 0.14743 | 0.14743 | 0 | 112.4289 | 293.8282 | 36.6989 | 184.2055 | 0 | 159.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786.9548 | 0 | 786.9482 | 0.0066363 | 0.0066363 | 11.8997 | 1.4863 | 7.4601 | 6.4715 | 0 | 0 | 4.5533 | 0 | 0 | 0 | 0 | 31.8706 | 31.8708 | 0.00026876
NV_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 209979.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90213.2335 | 0 | 0 | 300192.6382 | 0 | 300192.6382 | 0 | 0 | 1465.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 629.5982 | 0 | 0 | 2095.0444 | 0 | 2095.0444 | 0 | 0 | 209.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2132 | 0 | 0 | 300.1926 | 0 | 300.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5039 | 3.6535 | 0 | 0 | 12.1575 | 12.1575 | 0
NV_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 31136.6182 | 68388.8618 | 10755.8316 | 53987.5506 | 0 | 44634.8952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208903.7574 | 0 | 208902.3682 | 1.3893 | 1.3893 | 0 | 2360.1557 | 5183.8757 | 815.292 | 4092.2563 | 0 | 3383.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15834.9048 | 0 | 15834.7995 | 0.10531 | 0.10531 | 0 | 106.2381 | 233.3428 | 36.6989 | 184.2055 | 0 | 152.2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.7796 | 0 | 712.7749 | 0.0047402 | 0.0047402 | 9.4501 | 1.4863 | 7.4601 | 6.1678 | 0 | 0 | 4.3025 | 0 | 0 | 0 | 0 | 28.8666 | 28.8668 | 0.00019197
NV_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 235608.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90222.7117 | 0 | 0 | 325831.0913 | 0 | 325831.0913 | 0 | 0 | 1644.3109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 629.6643 | 0 | 0 | 2273.9752 | 0 | 2273.9752 | 0 | 0 | 235.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2227 | 0 | 0 | 325.8311 | 0 | 325.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5419 | 3.6539 | 0 | 0 | 13.1958 | 13.1958 | 0
NV_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 15504.4021 | 62862.2926 | 79569.8141 | 12311.829 | 154949.5496 | 0 | 48094.2107 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373364.3408 | 0 | 373359.6172 | 4.7236 | 4.7236 | 1175.2337 | 4764.9618 | 6031.3919 | 933.2366 | 11745.1759 | 0 | 3645.5412 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28301.017 | 0 | 28300.659 | 0.35805 | 0.35805 | 52.901 | 214.4861 | 271.4922 | 42.008 | 528.6879 | 0 | 164.0974 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.9191 | 0 | 1273.903 | 0.016117 | 0.016117 | 6.2843 | 0.97236 | 12.2376 | 3.7984 | 0.0057056 | 0 | 4.9647 | 1.2245 | 0 | 0 | 0 | 29.4871 | 29.4875 | 0.00037306
NV_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 38538.2441 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 586101.6725 | 0 | 0 | 1024135.3545 | 0 | 1024135.3545 | 0 | 0 | 268.9584 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 4090.4036 | 0 | 0 | 7147.4406 | 0 | 7147.4406 | 0 | 0 | 38.5382 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 586.1017 | 0 | 0 | 1024.1354 | 0 | 1024.1354 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.89205 | 13.5665 | 0 | 0 | 23.7057 | 23.7057 | 0
NV_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 18949.8248 | 58208.1934 | 51050.6057 | 12311.829 | 154949.5496 | 0 | 51011.7057 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 346553.9509 | 0 | 346553.1173 | 0.83357 | 0.83357 | 1436.3967 | 4412.1811 | 3869.6359 | 933.2366 | 11745.1759 | 0 | 3866.6873 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 26268.7895 | 0 | 26268.7263 | 0.063185 | 0.063185 | 64.6568 | 198.6064 | 174.1847 | 42.008 | 528.6879 | 0 | 174.0519 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.4421 | 0 | 1182.4392 | 0.0028441 | 0.0028441 | 4.0319 | 0.97236 | 12.2376 | 4.0288 | 0.0057056 | 0 | 4.5972 | 1.4966 | 0 | 0 | 0 | 27.37 | 27.3701 | 6.5834e-05
NV_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 30927.2726 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 586158.5415 | 0 | 0 | 1016581.2521 | 0 | 1016581.2521 | 0 | 0 | 215.8414 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 4090.8005 | 0 | 0 | 7094.7206 | 0 | 7094.7206 | 0 | 0 | 30.9273 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 586.1585 | 0 | 0 | 1016.5813 | 0 | 1016.5813 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.71588 | 13.5679 | 0 | 0 | 23.5309 | 23.5309 | 0
NV_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 2153.3892 | 3956.679 | 8888.6348 | 1575.4473 | 13417.6985 | 0 | 5643.2689 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40639.3163 | 0 | 40637.3713 | 1.945 | 1.945 | 163.2269 | 299.9163 | 673.7585 | 119.4189 | 1017.0615 | 0 | 427.7598 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 3080.4602 | 0 | 3080.3127 | 0.14743 | 0.14743 | 7.3474 | 13.5002 | 30.328 | 5.3754 | 45.7812 | 0 | 19.2548 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.6613 | 0 | 138.6547 | 0.0066363 | 0.0066363 | 5.5122 | 0.97699 | 8.3208 | 3.4996 | 0 | 0 | 2.4537 | 1.3354 | 3.1033 | 0 | 0 | 25.2008 | 25.202 | 0.0012062
NV_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 1497.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.551 | 0 | 1497.551 | 0 | 0 | 10.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4514 | 0 | 10.4514 | 0 | 0 | 1.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4976 | 0 | 1.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27218 | 0 | 0 | 0 | 0.27218 | 0.27218 | 0
NV_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 2220.0748 | 3723.2794 | 7160.3663 | 1575.4473 | 13417.6985 | 0 | 5190.3626 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38291.4274 | 0 | 38288.371 | 3.0564 | 3.0564 | 168.2817 | 282.2246 | 542.7558 | 119.4189 | 1017.0615 | 0 | 393.4295 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 2902.4902 | 0 | 2902.2585 | 0.23168 | 0.23168 | 7.5749 | 12.7038 | 24.4312 | 5.3754 | 45.7812 | 0 | 17.7095 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.6504 | 0 | 130.6399 | 0.010429 | 0.010429 | 4.4404 | 0.97699 | 8.3208 | 3.2187 | 0 | 0 | 2.3089 | 1.3768 | 3.1033 | 0 | 0 | 23.7441 | 23.746 | 0.0018954
NV_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | NV-TONOPAH-NV | Zone4B | Zone4B(NV-TONOPAH-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 1696.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1696.5926 | 0 | 1696.5926 | 0 | 0 | 11.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8405 | 0 | 11.8405 | 0 | 0 | 1.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6966 | 0 | 1.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30836 | 0 | 0 | 0 | 0.30836 | 0.30836 | 0
NV_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 567672.2875 | 880144.3394 | 95749.4079 | 4077910.5986 | 543457.0788 | 691990.918 | 81248.0684 | 156502.7684 | 701971.5295 | 0 | 0 | 0 | 0 | 7796646.9965 | 0 | 7796649.2194 | -2.2229 | 543454.856 | 0 | 43029.5594 | 66714.9409 | 7257.8051 | 309105.6234 | 41194.0466 | 52452.9116 | 6158.6036 | 11862.9098 | 53209.4419 | 0 | 0 | 0 | 0 | 590985.8423 | 0 | 590986.0108 | -0.16849 | 41193.8781 | 0 | 1936.8978 | 3003.0525 | 326.697 | 13913.831 | 1854.2756 | 2361.073 | 277.2184 | 533.9874 | 2395.1269 | 0 | 0 | 0 | 0 | 26602.1596 | 0 | 26602.1671 | -0.0075844 | 1854.268 | 6.0231 | 0.65524 | 27.9065 | 4.7355 | 0.55601 | 0 | 3.8848 | 0 | 0 | 4.8038 | 0 | 53.355 | 53.355 | -1.5212e-05
NV_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 1329834.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572557.3658 | 0 | 0 | 1902392.1761 | 0 | 1902392.1761 | 0 | 0 | 9280.9171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.8779 | 0 | 0 | 13276.795 | 0 | 13276.795 | 0 | 0 | 1329.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5574 | 0 | 0 | 1902.3922 | 0 | 1902.3922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6672 | 1.1484 | 0 | 0 | 3.8156 | 3.8156 | 0
NV_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 530278.3371 | 716995.2396 | 95749.4079 | 4077910.5986 | 543387.6147 | 699042.9202 | 83290.3149 | 140703.8382 | 702585.5927 | 0 | 0 | 0 | 0 | 7589943.8639 | 0 | 7589943.586 | 0.27786 | 543387.8925 | 0 | 40195.0979 | 54348.2392 | 7257.8051 | 309105.6234 | 41188.7812 | 52987.4534 | 6313.4059 | 10665.3509 | 53255.9879 | 0 | 0 | 0 | 0 | 575317.7449 | 0 | 575317.7238 | 0.021062 | 41188.8023 | 0 | 1809.3097 | 2446.3878 | 326.697 | 13913.831 | 1854.0385 | 2385.1344 | 284.1866 | 480.0815 | 2397.222 | 0 | 0 | 0 | 0 | 25896.8885 | 0 | 25896.8875 | 0.00094805 | 1854.0395 | 4.9066 | 0.65524 | 27.9065 | 4.7838 | 0.56998 | 0 | 3.6289 | 0 | 0 | 4.808 | 0 | 51.9405 | 51.9405 | 1.9015e-06
NV_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 2016139.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572557.3658 | 0 | 0 | 2588697.0745 | 0 | 2588697.0745 | 0 | 0 | 14070.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.8779 | 0 | 0 | 18066.5169 | 0 | 18066.5169 | 0 | 0 | 2016.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5574 | 0 | 0 | 2588.6971 | 0 | 2588.6971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0437 | 1.1484 | 0 | 0 | 5.1921 | 5.1921 | 0
NV_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 24173.5301 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22670.3256 | 0 | 0 | 0 | 0 | 114952.0822 | 0 | 0 | 339379.6917 | 0 | 339379.4139 | 0.27786 | 0.27786 | 0 | 1832.3536 | 2150.804 | 546.1256 | 10763.9189 | 0 | 1718.4107 | 0 | 0 | 0 | 0 | 8713.3678 | 0 | 0 | 25724.9806 | 0 | 25724.9596 | 0.021062 | 0.021062 | 0 | 82.4801 | 96.8146 | 24.5829 | 484.5184 | 0 | 77.3512 | 0 | 0 | 0 | 0 | 392.2165 | 0 | 0 | 1157.9635 | 0 | 1157.9626 | 0.00094805 | 0.00094805 | 2.8693 | 0.72858 | 14.3599 | 2.2925 | 0 | 0 | 2.4445 | 0 | 11.6243 | 0 | 0 | 34.3192 | 34.3192 | 2.8098e-05
NV_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 181905.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181905.0617 | 0 | 181905.0617 | 0 | 0 | 1269.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.5154 | 0 | 1269.5154 | 0 | 0 | 181.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181.9051 | 0 | 181.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3912 | 0 | 0 | 0 | 5.3912 | 5.3912 | 0
NV_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 26746.4829 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 22259.0977 | 0 | 0 | 0 | 0 | 114802.0396 | 0 | 0 | 336198.2329 | 0 | 336201.5671 | -3.3343 | -3.3343 | 0 | 2027.3834 | 1757.1639 | 546.1256 | 10763.9189 | 0 | 1687.2396 | 0 | 0 | 0 | 0 | 8701.9946 | 0 | 0 | 25483.8261 | 0 | 25484.0788 | -0.25274 | -0.25274 | 0 | 91.259 | 79.0956 | 24.5829 | 484.5184 | 0 | 75.948 | 0 | 0 | 0 | 0 | 391.7046 | 0 | 0 | 1147.1084 | 0 | 1147.1197 | -0.011377 | -0.011377 | 2.3442 | 0.72858 | 14.3599 | 2.2509 | 0 | 0 | 2.7047 | 0 | 11.6092 | 0 | 0 | 33.9978 | 33.9975 | -0.00033717
NV_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 78858.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78858.3844 | 0 | 78858.3844 | 0 | 0 | 550.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550.3527 | 0 | 550.3527 | 0 | 0 | 78.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8584 | 0 | 78.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3372 | 0 | 0 | 0 | 2.3372 | 2.3372 | 0
NV_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 90297.86 | 97933.3613 | 7138.1378 | 317887.4784 | 4818.0346 | 104090.6651 | 808.5629 | 0 | 0 | 0 | 7179.8163 | 17441.0631 | 0 | 647594.9795 | 0 | 647595.8131 | -0.83357 | 4817.2011 | 0 | 6844.5778 | 7423.3488 | 541.0708 | 24095.8709 | 365.207 | 7890.0724 | 61.2891 | 0 | 0 | 0 | 544.2301 | 1322.0326 | 0 | 49087.6994 | 0 | 49087.7626 | -0.063185 | 365.1438 | 0 | 308.0963 | 334.1486 | 24.3553 | 1084.6321 | 16.4391 | 355.1573 | 2.7588 | 0 | 0 | 0 | 24.4975 | 59.5089 | 0 | 2209.5941 | 0 | 2209.5969 | -0.0028441 | 16.4363 | 4.518 | 0.32931 | 14.6653 | 4.8021 | 0.037302 | 0 | 4.1658 | 0 | 0.33123 | 0 | 0.80462 | 29.876 | 29.8759 | -3.8456e-05
NV_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 529005.1692 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119443.9135 | 0 | 0 | 990639.4975 | 0 | 990639.4975 | 0 | 0 | 3691.9271 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 833.5991 | 0 | 0 | 6913.6731 | 0 | 6913.6731 | 0 | 0 | 529.0052 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4439 | 0 | 0 | 990.6395 | 0 | 990.6395 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.1527 | 1.615 | 0 | 0 | 13.3944 | 13.3944 | 0
NV_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 89878.2965 | 79744.8638 | 7138.1378 | 312483.1662 | 4743.0133 | 81136.9257 | 1255.9121 | 0 | 0 | 0 | 7179.8163 | 12411.8574 | 0 | 595971.9891 | 0 | 595974.212 | -2.2229 | 4740.7905 | 0 | 6812.7749 | 6044.6607 | 541.0708 | 23686.224 | 359.5204 | 6150.179 | 95.1981 | 0 | 0 | 0 | 544.2301 | 940.8188 | 0 | 45174.6768 | 0 | 45174.8453 | -0.16849 | 359.3519 | 0 | 306.6647 | 272.0895 | 24.3553 | 1066.1926 | 16.1832 | 276.8392 | 4.2852 | 0 | 0 | 0 | 24.4975 | 42.3493 | 0 | 2033.4564 | 0 | 2033.464 | -0.0075844 | 16.1756 | 3.6789 | 0.32931 | 14.416 | 3.7431 | 0.05794 | 0 | 4.1464 | 0 | 0.33123 | 0 | 0.5726 | 27.4945 | 27.4944 | -0.00010255
NV_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 794232.8339 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119387.0444 | 0 | 0 | 1255810.2931 | 0 | 1255810.2931 | 0 | 0 | 5542.9509 | 0 | 0 | 0 | 2388.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 833.2022 | 0 | 0 | 8764.3 | 0 | 8764.3 | 0 | 0 | 794.2328 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.387 | 0 | 0 | 1255.8103 | 0 | 1255.8103 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.7388 | 1.6142 | 0 | 0 | 16.9798 | 16.9798 | 0
NV_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 31850.7099 | 85782.6892 | 10766.9459 | 53987.5506 | 0 | 45832.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228220.353 | 0 | 228220.0752 | 0.27786 | 0.27786 | 0 | 2414.2838 | 6502.3278 | 816.1345 | 4092.2563 | 0 | 3474.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17299.1028 | 0 | 17299.0817 | 0.021062 | 0.021062 | 0 | 108.6746 | 292.6905 | 36.7368 | 184.2055 | 0 | 156.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778.6878 | 0 | 778.6869 | 0.00094805 | 0.00094805 | 11.8537 | 1.4878 | 7.4601 | 6.3332 | 0 | 0 | 4.4012 | 0 | 0 | 0 | 0 | 31.536 | 31.536 | 3.8395e-05
NV_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 267066.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90810.3583 | 0 | 0 | 357876.7882 | 0 | 357876.7882 | 0 | 0 | 1863.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633.7655 | 0 | 0 | 2497.6221 | 0 | 2497.6221 | 0 | 0 | 267.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8104 | 0 | 0 | 357.8768 | 0 | 357.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8159 | 3.6777 | 0 | 0 | 14.4936 | 14.4936 | 0
NV_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 0 | 29688.985 | 68116.5622 | 10766.9459 | 53987.5506 | 0 | 43651.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206211.3263 | 0 | 206209.3813 | 1.945 | 1.945 | 0 | 2250.4251 | 5163.2354 | 816.1345 | 4092.2563 | 0 | 3308.7672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15630.8185 | 0 | 15630.6711 | 0.14743 | 0.14743 | 0 | 101.2988 | 232.4137 | 36.7368 | 184.2055 | 0 | 148.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703.593 | 0 | 703.5864 | 0.0066363 | 0.0066363 | 9.4125 | 1.4878 | 7.4601 | 6.0318 | 0 | 0 | 4.1025 | 0 | 0 | 0 | 0 | 28.4945 | 28.4948 | 0.00026876
NV_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 293747.4818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90829.3146 | 0 | 0 | 384576.7964 | 0 | 384576.7964 | 0 | 0 | 2050.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633.8978 | 0 | 0 | 2683.9615 | 0 | 2683.9615 | 0 | 0 | 293.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8293 | 0 | 0 | 384.5768 | 0 | 384.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8965 | 3.6785 | 0 | 0 | 15.575 | 15.575 | 0
NV_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 19469.4167 | 61364.6452 | 79297.5145 | 12306.2718 | 154949.5496 | 0 | 47488.4832 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 374948.1238 | 0 | 374947.0124 | 1.1114 | 1.1114 | 1475.7818 | 4651.4401 | 6010.7516 | 932.8154 | 11745.1759 | 0 | 3599.627 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28421.0678 | 0 | 28420.9835 | 0.084246 | 0.084246 | 66.4296 | 209.3762 | 270.5631 | 41.989 | 528.6879 | 0 | 162.0307 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1279.323 | 0 | 1279.3192 | 0.0037922 | 0.0037922 | 6.2627 | 0.97192 | 12.2376 | 3.7505 | 0.0057056 | 0 | 4.8464 | 1.5377 | 0 | 0 | 0 | 29.6125 | 29.6126 | 8.7778e-05
NV_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 49684.5734 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 597949.3865 | 0 | 0 | 1047129.3978 | 0 | 1047129.3978 | 0 | 0 | 346.7486 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 4173.0888 | 0 | 0 | 7307.9161 | 0 | 7307.9161 | 0 | 0 | 49.6846 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 597.9494 | 0 | 0 | 1047.1294 | 0 | 1047.1294 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.1501 | 13.8408 | 0 | 0 | 24.238 | 24.238 | 0
NV_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 23226.0389 | 56793.903 | 50867.2203 | 12306.2718 | 154949.5496 | 0 | 50183.6929 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348398.9192 | 0 | 348401.9756 | -3.0564 | -3.0564 | 1760.5337 | 4304.9778 | 3855.7353 | 932.8154 | 11745.1759 | 0 | 3803.9239 | 5.476 | 0 | 0 | 0 | 0 | 0 | 0 | 26408.6381 | 0 | 26408.8698 | -0.23168 | -0.23168 | 79.2472 | 193.7808 | 173.559 | 41.989 | 528.6879 | 0 | 171.2268 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.7371 | 0 | 1188.7475 | -0.010429 | -0.010429 | 4.0174 | 0.97192 | 12.2376 | 3.9634 | 0.0057056 | 0 | 4.4855 | 1.8343 | 0 | 0 | 0 | 27.516 | 27.5158 | -0.00024139
NV_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 41201.6102 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 598015.7337 | 0 | 0 | 1038712.7818 | 0 | 1038712.7818 | 0 | 0 | 287.546 | 0 | 0 | 0 | 2788.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 4173.5518 | 0 | 0 | 7249.1765 | 0 | 7249.1765 | 0 | 0 | 41.2016 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 598.0157 | 0 | 0 | 1038.7128 | 0 | 1038.7128 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.9537 | 13.8423 | 0 | 0 | 24.0432 | 24.0432 | 0
NV_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 2559.0599 | 3778.8507 | 8830.2849 | 1581.0044 | 13417.6985 | 0 | 5532.1263 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40703.2233 | 0 | 40705.724 | -2.5007 | -2.5007 | 193.9767 | 286.4369 | 669.3356 | 119.8401 | 1017.0615 | 0 | 419.3352 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 3085.3043 | 0 | 3085.4939 | -0.18955 | -0.18955 | 8.7315 | 12.8934 | 30.1289 | 5.3944 | 45.7812 | 0 | 18.8756 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8794 | 0 | 138.8879 | -0.0085324 | -0.0085324 | 5.476 | 0.98044 | 8.3208 | 3.4307 | 0 | 0 | 2.3434 | 1.587 | 3.1033 | 0 | 0 | 25.2432 | 25.2416 | -0.0015508
NV_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 2919.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.2767 | 0 | 2919.2767 | 0 | 0 | 20.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3736 | 0 | 20.3736 | 0 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9193 | 0 | 2.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53058 | 0 | 0 | 0 | 0.53058 | 0.53058 | 0
NV_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Electricity | 2617.4098 | 3553.7868 | 7118.6878 | 1581.0044 | 13417.6985 | 0 | 5084.777 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38377.563 | 0 | 38380.6194 | -3.0564 | -3.0564 | 198.3997 | 269.377 | 539.5965 | 119.8401 | 1017.0615 | 0 | 385.4261 | 0 | 0 | 0 | 0 | 379.3183 | 0 | 0 | 2909.0193 | 0 | 2909.251 | -0.23168 | -0.23168 | 8.9306 | 12.1255 | 24.289 | 5.3944 | 45.7812 | 0 | 17.3493 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.9442 | 0 | 130.9547 | -0.010429 | -0.010429 | 4.4146 | 0.98044 | 8.3208 | 3.1533 | 0 | 0 | 2.2038 | 1.6232 | 3.1033 | 0 | 0 | 23.8013 | 23.7994 | -0.0018954
NV_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | NV-WINNERMUCCA-NV | Zone5B | Zone5B(NV-WINNERMUCCA-NV) |  |  | NV | 0.0758 | 0.006979 |  |  |  | Natural Gas | 3213.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213.1 | 0 | 3213.1 | 0 | 0 | 22.4242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4242 | 0 | 22.4242 | 0 | 0 | 3.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2131 | 0 | 3.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58399 | 0 | 0 | 0 | 0.58399 | 0.58399 | 0
NY_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 657486.6769 | 882214.3716 | 95579.9153 | 4077910.5986 | 543459.8574 | 575671.781 | 93712.7185 | 234658.292 | 351455.3425 | 13817.8121 | 0 | 0 | 0 | 7525967.366 | 0 | 7525964.8653 | 2.5007 | 543462.3581 | 0 | 95598.5628 | 128273.9696 | 13897.3197 | 592928.201 | 79019.0633 | 83702.677 | 13625.8293 | 34119.3157 | 51101.6068 | 2009.1099 | 0 | 0 | 0 | 1094275.655 | 0 | 1094275.2914 | 0.3636 | 79019.4269 | 0 | 2243.3445 | 3010.1154 | 326.1187 | 13913.831 | 1854.285 | 1964.1921 | 319.7478 | 800.6541 | 1199.1656 | 47.1464 | 0 | 0 | 0 | 25678.6007 | 0 | 25678.5921 | 0.0085324 | 1854.2936 | 6.0373 | 0.65408 | 27.9065 | 3.9395 | 0.64131 | 0.09456 | 4.4994 | 0 | 0 | 2.4051 | 0 | 51.5026 | 51.5026 | 1.7113e-05
NY_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 840581.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547222.2142 | 0 | 0 | 1387803.3053 | 0 | 1387803.3053 | 0 | 0 | 5640.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3671.8611 | 0 | 0 | 9312.1602 | 0 | 9312.1602 | 0 | 0 | 840.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.2222 | 0 | 0 | 1387.8033 | 0 | 1387.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6859 | 1.0975 | 0 | 0 | 2.7835 | 2.7835 | 0
NY_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 615296.9204 | 718140.009 | 95579.9153 | 4077910.5986 | 543387.6147 | 550461.8454 | 86721.8447 | 208800.9505 | 351249.7286 | 12461.8716 | 0 | 0 | 0 | 7260011.2989 | 0 | 7260007.4089 | 3.89 | 543391.5047 | 0 | 89464.1722 | 104417.5573 | 13897.3197 | 592928.201 | 79008.5592 | 80037.1523 | 12609.3562 | 30359.6582 | 51071.7105 | 1811.9561 | 0 | 0 | 0 | 1055605.6429 | 0 | 1055605.0772 | 0.56561 | 79009.1248 | 0 | 2099.3931 | 2450.2937 | 326.1187 | 13913.831 | 1854.0385 | 1878.1758 | 295.8949 | 712.4288 | 1198.4641 | 42.5199 | 0 | 0 | 0 | 24771.1586 | 0 | 24771.1453 | 0.013273 | 1854.0518 | 4.9145 | 0.65408 | 27.9065 | 3.767 | 0.59347 | 0.085281 | 4.2107 | 0 | 0 | 2.4037 | 0 | 49.6826 | 49.6826 | 2.662e-05
NY_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 740766.4701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547279.0833 | 0 | 0 | 1288045.5534 | 0 | 1288045.5534 | 0 | 0 | 4970.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3672.2426 | 0 | 0 | 8642.7857 | 0 | 8642.7857 | 0 | 0 | 740.7665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.2791 | 0 | 0 | 1288.0456 | 0 | 1288.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4857 | 1.0977 | 0 | 0 | 2.5834 | 2.5834 | 0
NY_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 28199.6733 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20691.9861 | 0 | 0 | 0 | 0 | 109836.741 | 0 | 0 | 336309.3755 | 0 | 336308.8198 | 0.55571 | 0.55571 | 0 | 4100.2325 | 4125.6847 | 1047.1773 | 20647.4118 | 0 | 3008.6148 | 0 | 0 | 0 | 0 | 15970.2621 | 0 | 0 | 48899.3832 | 0 | 48899.3024 | 0.080801 | 0.080801 | 0 | 96.2173 | 96.8146 | 24.5734 | 484.5184 | 0 | 70.6011 | 0 | 0 | 0 | 0 | 374.763 | 0 | 0 | 1147.4876 | 0 | 1147.4857 | 0.0018961 | 0.0018961 | 2.8693 | 0.72829 | 14.3599 | 2.0924 | 0 | 0 | 2.8516 | 0 | 11.107 | 0 | 0 | 34.0086 | 34.0087 | 5.6196e-05
NY_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 97302.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97302.9055 | 0 | 97302.9055 | 0 | 0 | 652.9025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 652.9025 | 0 | 652.9025 | 0 | 0 | 97.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3029 | 0 | 97.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8838 | 0 | 0 | 0 | 2.8838 | 2.8838 | 0
NY_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 27307.7534 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20186.2869 | 0 | 0 | 0 | 0 | 109867.3052 | 0 | 0 | 329749.1796 | 0 | 329751.9582 | -2.7786 | -2.7786 | 0 | 3970.5473 | 3370.602 | 1047.1773 | 20647.4118 | 0 | 2935.0861 | 0 | 0 | 0 | 0 | 15974.7062 | 0 | 0 | 47945.5307 | 0 | 47945.9347 | -0.404 | -0.404 | 0 | 93.1741 | 79.0956 | 24.5734 | 484.5184 | 0 | 68.8756 | 0 | 0 | 0 | 0 | 374.8672 | 0 | 0 | 1125.1042 | 0 | 1125.1137 | -0.0094805 | -0.0094805 | 2.3442 | 0.72829 | 14.3599 | 2.0413 | 0 | 0 | 2.7614 | 0 | 11.1101 | 0 | 0 | 33.3456 | 33.3453 | -0.00028098
NY_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 111681.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111681.2912 | 0 | 111681.2912 | 0 | 0 | 749.3815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 749.3815 | 0 | 749.3815 | 0 | 0 | 111.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.6813 | 0 | 111.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 0 | 0 | 0 | 3.31 | 3.31 | 0
NY_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 108905.9211 | 98569.6531 | 7127.0235 | 317887.4784 | 4818.0346 | 91100.8658 | 672.4131 | 0 | 0 | 20219.6297 | 7179.8163 | 17635.5627 | 0 | 674116.3985 | 0 | 674116.1207 | 0.27786 | 4818.3125 | 0 | 15834.9209 | 14332.0276 | 1036.2692 | 46220.8394 | 700.5422 | 13246.0659 | 97.7689 | 0 | 0 | 2939.9342 | 1043.9453 | 2564.2108 | 0 | 98016.5243 | 0 | 98016.4839 | 0.0404 | 700.5826 | 0 | 371.587 | 336.3197 | 24.3174 | 1084.6321 | 16.4391 | 310.8362 | 2.2943 | 0 | 0 | 68.9894 | 24.4975 | 60.1725 | 0 | 2300.0852 | 0 | 2300.0842 | 0.00094805 | 16.4401 | 4.5474 | 0.3288 | 14.6653 | 4.2028 | 0.031021 | 0.93281 | 5.0242 | 0 | 0.33123 | 0 | 0.81359 | 31.0994 | 31.0995 | 1.2819e-05
NY_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 310618.6266 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114780.6532 | 0 | 0 | 767589.6946 | 0 | 767589.6946 | 0 | 0 | 2084.251 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 770.1782 | 0 | 0 | 5150.5269 | 0 | 5150.5269 | 0 | 0 | 310.6186 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7807 | 0 | 0 | 767.5897 | 0 | 767.5897 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.1999 | 1.5519 | 0 | 0 | 10.3786 | 10.3786 | 0
NY_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 104071.2151 | 80256.1201 | 7127.0235 | 312483.1662 | 4745.7919 | 80189.4345 | 394.5565 | 0 | 0 | 22981.525 | 7179.8163 | 12497.9929 | 0 | 631926.642 | 0 | 631927.7534 | -1.1114 | 4744.6805 | 0 | 15131.9547 | 11669.2399 | 1036.2692 | 45435.0524 | 690.0381 | 11659.5438 | 57.3685 | 0 | 0 | 3341.5137 | 1043.9453 | 1817.2082 | 0 | 91882.1337 | 0 | 91882.2953 | -0.1616 | 689.8765 | 0 | 355.091 | 273.8339 | 24.3174 | 1066.1926 | 16.1926 | 273.6064 | 1.3462 | 0 | 0 | 78.413 | 24.4975 | 42.6432 | 0 | 2156.1337 | 0 | 2156.1375 | -0.0037922 | 16.1888 | 3.7025 | 0.3288 | 14.416 | 3.6994 | 0.018202 | 1.0602 | 4.8012 | 0 | 0.33123 | 0 | 0.57658 | 29.1531 | 29.1531 | -5.1274e-05
NY_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 306268.146 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114524.7426 | 0 | 0 | 762983.3034 | 0 | 762983.3034 | 0 | 0 | 2055.0593 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 768.461 | 0 | 0 | 5119.618 | 0 | 5119.618 | 0 | 0 | 306.2681 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.5247 | 0 | 0 | 762.9833 | 0 | 762.9833 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.1411 | 1.5485 | 0 | 0 | 10.3163 | 10.3163 | 0
NY_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 39850.2034 | 84182.2348 | 10744.7174 | 53987.5506 | 0 | 42195.3136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230960.0198 | 0 | 230958.9083 | 1.1114 | 1.1114 | 0 | 5794.2196 | 12240.0969 | 1562.2819 | 7849.7899 | 0 | 6135.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33581.5869 | 0 | 33581.4253 | 0.1616 | 0.1616 | 0 | 135.9689 | 287.2298 | 36.661 | 184.2055 | 0 | 143.9704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.0356 | 0 | 788.0318 | 0.0037922 | 0.0037922 | 11.6325 | 1.4847 | 7.4601 | 5.8307 | 0 | 0 | 5.5066 | 0 | 0 | 0 | 0 | 31.9145 | 31.9146 | 0.00015358
NY_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 351592.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89322.2854 | 0 | 0 | 440915.0461 | 0 | 440915.0461 | 0 | 0 | 2359.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.3525 | 0 | 0 | 2958.54 | 0 | 2958.54 | 0 | 0 | 351.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3223 | 0 | 0 | 440.915 | 0 | 440.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2391 | 3.6175 | 0 | 0 | 17.8566 | 17.8566 | 0
NY_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 37405.0647 | 66732.836 | 10744.7174 | 53987.5506 | 0 | 40428.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209298.3139 | 0 | 209297.2025 | 1.1114 | 1.1114 | 0 | 5438.6964 | 9702.9544 | 1562.2819 | 7849.7899 | 0 | 5878.2523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30431.9748 | 0 | 30431.8132 | 0.1616 | 0.1616 | 0 | 127.6261 | 227.6924 | 36.661 | 184.2055 | 0 | 137.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.1258 | 0 | 714.1221 | 0.0037922 | 0.0037922 | 9.2213 | 1.4847 | 7.4601 | 5.5865 | 0 | 0 | 5.1687 | 0 | 0 | 0 | 0 | 28.9212 | 28.9213 | 0.00015358
NY_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 378425.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89331.7636 | 0 | 0 | 467757.2269 | 0 | 467757.2269 | 0 | 0 | 2539.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.4161 | 0 | 0 | 3138.651 | 0 | 3138.651 | 0 | 0 | 378.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3318 | 0 | 0 | 467.7572 | 0 | 467.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3258 | 3.6178 | 0 | 0 | 18.9437 | 18.9437 | 0
NY_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 23823.4307 | 73126.3179 | 79336.4145 | 12300.7147 | 154949.5496 | 0 | 45435.1224 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 389043.7926 | 0 | 389044.6262 | -0.83357 | -0.83357 | 3463.9268 | 10632.5666 | 11535.5147 | 1788.5239 | 22529.6645 | 0 | 6606.2668 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 56566.9674 | 0 | 56567.0886 | -0.1212 | -0.1212 | 81.2855 | 249.507 | 270.6958 | 41.97 | 528.6879 | 0 | 155.0246 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1327.4174 | 0 | 1327.4203 | -0.0028441 | -0.0028441 | 6.2658 | 0.97148 | 12.2376 | 3.5884 | 0.0057056 | 0 | 5.7754 | 1.8815 | 0 | 0 | 0 | 30.7259 | 30.7258 | -6.5834e-05
NY_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 58186.493 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 568841.9227 | 0 | 0 | 1026523.8536 | 0 | 1026523.8536 | 0 | 0 | 390.4314 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 3816.9293 | 0 | 0 | 6887.9751 | 0 | 6887.9751 | 0 | 0 | 58.1865 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 568.8419 | 0 | 0 | 1026.5239 | 0 | 1026.5239 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3468 | 13.167 | 0 | 0 | 23.761 | 23.761 | 0
NY_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 27768.9954 | 68386.0832 | 50897.7845 | 12300.7147 | 154949.5496 | 0 | 43092.7907 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 357468.1608 | 0 | 357466.4937 | 1.6671 | 1.6671 | 4037.6119 | 9943.3365 | 7400.5379 | 1788.5239 | 22529.6645 | 0 | 6265.6918 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 51975.8706 | 0 | 51975.6282 | 0.2424 | 0.2424 | 94.7478 | 233.3333 | 173.6632 | 41.97 | 528.6879 | 0 | 147.0326 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.6814 | 0 | 1219.6757 | 0.0056883 | 0.0056883 | 4.0198 | 0.97148 | 12.2376 | 3.4034 | 0.0057056 | 0 | 5.401 | 2.1931 | 0 | 0 | 0 | 28.2319 | 28.2321 | 0.00013167
NY_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 57968.4951 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 568917.7481 | 0 | 0 | 1026381.6811 | 0 | 1026381.6811 | 0 | 0 | 388.9686 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 3817.4381 | 0 | 0 | 6887.0211 | 0 | 6887.0211 | 0 | 0 | 57.9685 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 568.9177 | 0 | 0 | 1026.3817 | 0 | 1026.3817 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3418 | 13.1688 | 0 | 0 | 23.7577 | 23.7577 | 0
NY_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 2770.231 | 4401.2496 | 8855.292 | 1581.0044 | 13417.6985 | 0 | 4706.892 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40736.5661 | 0 | 40735.1768 | 1.3893 | 1.3893 | 402.7916 | 639.9417 | 1287.5595 | 229.878 | 1950.9334 | 0 | 684.3821 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 5923.0967 | 0 | 5922.8947 | 0.202 | 0.202 | 9.452 | 15.0171 | 30.2143 | 5.3944 | 45.7812 | 0 | 16.0599 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.9932 | 0 | 138.9884 | 0.0047402 | 0.0047402 | 5.4915 | 0.98044 | 8.3208 | 2.9189 | 0 | 0 | 2.7294 | 1.7179 | 3.1033 | 0 | 0 | 25.2614 | 25.2623 | 0.00086155
NY_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 2720.2351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2720.2351 | 0 | 2720.2351 | 0 | 0 | 18.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.2528 | 0 | 18.2528 | 0 | 0 | 2.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7202 | 0 | 2.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49441 | 0 | 0 | 0 | 0.49441 | 0.49441 | 0
NY_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 2842.4737 | 4178.9643 | 7138.1378 | 1581.0044 | 13417.6985 | 0 | 4323.4498 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38485.9271 | 0 | 38483.9821 | 1.945 | 1.945 | 413.2957 | 607.6214 | 1037.8852 | 229.878 | 1950.9334 | 0 | 628.6296 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 5595.8538 | 0 | 5595.571 | 0.2828 | 0.2828 | 9.6985 | 14.2586 | 24.3553 | 5.3944 | 45.7812 | 0 | 14.7516 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.314 | 0 | 131.3073 | 0.0066363 | 0.0066363 | 4.4266 | 0.98044 | 8.3208 | 2.6811 | 0 | 0 | 2.5915 | 1.7627 | 3.1033 | 0 | 0 | 23.8654 | 23.8666 | 0.0012062
NY_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | NY-NEWYORK-NY | Zone4A | Zone4A(NY-NEWYORK-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 2928.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2928.7549 | 0 | 2928.7549 | 0 | 0 | 19.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6519 | 0 | 19.6519 | 0 | 0 | 2.9288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9288 | 0 | 2.9288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53231 | 0 | 0 | 0 | 0.53231 | 0.53231 | 0
NY_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 519519.7269 | 881325.2303 | 96032.8217 | 4077910.5986 | 543457.0788 | 579834.0738 | 82295.588 | 179620.4432 | 405212.2721 | 11719.9943 | 0 | 0 | 0 | 7376927.8277 | 0 | 7376927.8277 | 0 | 543457.0788 | 0 | 75538.1683 | 128144.6885 | 13963.1723 | 592928.201 | 79018.6593 | 84307.8743 | 11965.7785 | 26116.8124 | 58917.8644 | 1704.0872 | 0 | 0 | 0 | 1072605.3062 | 0 | 1072605.3062 | 0 | 79018.6593 | 0 | 1772.6013 | 3007.0817 | 327.664 | 13913.831 | 1854.2756 | 1978.3939 | 280.7925 | 612.865 | 1382.5843 | 39.9886 | 0 | 0 | 0 | 25170.0777 | 0 | 25170.0777 | 0 | 1854.2756 | 6.0312 | 0.65718 | 27.9065 | 3.968 | 0.56318 | 0.080204 | 3.5552 | 0 | 0 | 2.773 | 0 | 50.4827 | 50.4827 | 0
NY_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 1259933.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587153.7495 | 0 | 0 | 1847087.0471 | 0 | 1847087.0471 | 0 | 0 | 8454.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3939.8017 | 0 | 0 | 12393.9541 | 0 | 12393.9541 | 0 | 0 | 1259.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.1537 | 0 | 0 | 1847.087 | 0 | 1847.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.527 | 1.1776 | 0 | 0 | 3.7046 | 3.7046 | 0
NY_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 486204.7123 | 717667.6527 | 96032.8217 | 4077910.5986 | 543387.6147 | 562757.003 | 78208.3164 | 161092.9605 | 404912.1869 | 10583.5605 | 0 | 0 | 0 | 7138757.4274 | 0 | 7138758.8167 | -1.3893 | 543386.2254 | 0 | 70694.1652 | 104348.8767 | 13963.1723 | 592928.201 | 79008.5592 | 81824.8682 | 11371.4892 | 23422.9165 | 58874.232 | 1538.8497 | 0 | 0 | 0 | 1037975.3299 | 0 | 1037975.5319 | -0.202 | 79008.3572 | 0 | 1658.9305 | 2448.682 | 327.664 | 13913.831 | 1854.0385 | 1920.1269 | 266.8468 | 549.6492 | 1381.5604 | 36.1111 | 0 | 0 | 0 | 24357.4403 | 0 | 24357.4451 | -0.0047402 | 1854.0338 | 4.9112 | 0.65718 | 27.9065 | 3.8511 | 0.5352 | 0.072427 | 3.3273 | 0 | 0 | 2.7709 | 0 | 48.8529 | 48.8528 | -9.5073e-06
NY_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 1209187.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587201.1404 | 0 | 0 | 1796388.3094 | 0 | 1796388.3094 | 0 | 0 | 8113.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.1197 | 0 | 0 | 12053.7656 | 0 | 12053.7656 | 0 | 0 | 1209.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.2011 | 0 | 0 | 1796.3883 | 0 | 1796.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4252 | 1.1777 | 0 | 0 | 3.603 | 3.603 | 0
NY_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 22020.141 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20255.7511 | 0 | 0 | 0 | 0 | 117641.7348 | 0 | 0 | 337501.3806 | 0 | 337500.5471 | 0.83357 | 0.83357 | 0 | 3201.7285 | 4125.6847 | 1047.5813 | 20647.4118 | 0 | 2945.1862 | 0 | 0 | 0 | 0 | 17105.1082 | 0 | 0 | 49072.7007 | 0 | 49072.5795 | 0.1212 | 0.1212 | 0 | 75.1327 | 96.8146 | 24.5829 | 484.5184 | 0 | 69.1126 | 0 | 0 | 0 | 0 | 401.3936 | 0 | 0 | 1151.5547 | 0 | 1151.5519 | 0.0028441 | 0.0028441 | 2.8693 | 0.72858 | 14.3599 | 2.0483 | 0 | 0 | 2.2267 | 0 | 11.8963 | 0 | 0 | 34.1292 | 34.1292 | 8.4293e-05
NY_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 167261.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167261.2872 | 0 | 167261.2872 | 0 | 0 | 1122.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.3232 | 0 | 1122.3232 | 0 | 0 | 167.2613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.2613 | 0 | 167.2613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9572 | 0 | 0 | 0 | 4.9572 | 4.9572 | 0
NY_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 20892.0429 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19705.5949 | 0 | 0 | 0 | 0 | 117675.0776 | 0 | 0 | 330663.328 | 0 | 330663.328 | 0 | 0 | 0 | 3037.703 | 3370.602 | 1047.5813 | 20647.4118 | 0 | 2865.1935 | 0 | 0 | 0 | 0 | 17109.9563 | 0 | 0 | 48078.4479 | 0 | 48078.4479 | 0 | 0 | 0 | 71.2837 | 79.0956 | 24.5829 | 484.5184 | 0 | 67.2355 | 0 | 0 | 0 | 0 | 401.5074 | 0 | 0 | 1128.2233 | 0 | 1128.2233 | 0 | 0 | 2.3442 | 0.72858 | 14.3599 | 1.9927 | 0 | 0 | 2.1127 | 0 | 11.8997 | 0 | 0 | 33.4378 | 33.4378 | 0
NY_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 187023.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187023.2741 | 0 | 187023.2741 | 0 | 0 | 1254.9262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.9262 | 0 | 1254.9262 | 0 | 0 | 187.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.0233 | 0 | 187.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5429 | 0 | 0 | 0 | 5.5429 | 5.5429 | 0
NY_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 79725.4138 | 97741.6402 | 7143.6949 | 317887.4784 | 4818.0346 | 93112.5481 | 1061.4125 | 0 | 0 | 19324.9313 | 7179.8163 | 17627.227 | 0 | 645622.1972 | 0 | 645622.7529 | -0.55571 | 4817.4789 | 0 | 11592.0752 | 14211.6345 | 1038.6932 | 46220.8394 | 700.5422 | 13538.5645 | 154.3294 | 0 | 0 | 2809.845 | 1043.9453 | 2562.9988 | 0 | 93873.4675 | 0 | 93873.5483 | -0.080801 | 700.4614 | 0 | 272.0231 | 333.4945 | 24.3743 | 1084.6321 | 16.4391 | 317.7 | 3.6215 | 0 | 0 | 65.9367 | 24.4975 | 60.1441 | 0 | 2202.8629 | 0 | 2202.8648 | -0.0018961 | 16.4372 | 4.5092 | 0.32956 | 14.6653 | 4.2956 | 0.048967 | 0.89153 | 3.678 | 0 | 0.33123 | 0 | 0.81321 | 29.7849 | 29.7849 | -2.5637e-05
NY_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 587618.1799 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122799.1861 | 0 | 0 | 1052607.7808 | 0 | 1052607.7808 | 0 | 0 | 3942.918 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 823.9825 | 0 | 0 | 7062.9982 | 0 | 7062.9982 | 0 | 0 | 587.6182 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.7992 | 0 | 0 | 1052.6078 | 0 | 1052.6078 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.9452 | 1.6604 | 0 | 0 | 14.2323 | 14.2323 | 0
NY_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 75499.2139 | 79703.1853 | 7143.6949 | 312483.1662 | 4743.0133 | 80378.377 | 727.9845 | 0 | 0 | 22636.9828 | 7179.8163 | 12484.1001 | 0 | 602979.5343 | 0 | 602982.3129 | -2.7786 | 4740.2348 | 0 | 10977.5857 | 11588.8431 | 1038.6932 | 45435.0524 | 689.6341 | 11687.016 | 105.8489 | 0 | 0 | 3291.4173 | 1043.9453 | 1815.1882 | 0 | 87673.2243 | 0 | 87673.6283 | -0.404 | 689.2301 | 0 | 257.6033 | 271.9473 | 24.3743 | 1066.1926 | 16.1832 | 274.251 | 2.4839 | 0 | 0 | 77.2374 | 24.4975 | 42.5957 | 0 | 2057.3662 | 0 | 2057.3757 | -0.0094805 | 16.1737 | 3.677 | 0.32956 | 14.416 | 3.7081 | 0.033585 | 1.0443 | 3.4831 | 0 | 0.33123 | 0 | 0.57594 | 27.8178 | 27.8177 | -0.00012819
NY_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 569088.3552 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122543.2754 | 0 | 0 | 1033822.0455 | 0 | 1033822.0455 | 0 | 0 | 3818.5829 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 822.2654 | 0 | 0 | 6936.9459 | 0 | 6936.9459 | 0 | 0 | 569.0884 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.5433 | 0 | 0 | 1033.822 | 0 | 1033.822 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.6946 | 1.6569 | 0 | 0 | 13.9783 | 13.9783 | 0
NY_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 27399.4461 | 83720.9927 | 10764.1673 | 53987.5506 | 0 | 43242.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219114.99 | 0 | 219115.5457 | -0.55571 | -0.55571 | 0 | 3983.8795 | 12173.0323 | 1565.1099 | 7849.7899 | 0 | 6287.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31859.3195 | 0 | 31859.4003 | -0.080801 | -0.080801 | 0 | 93.4869 | 285.656 | 36.7273 | 184.2055 | 0 | 147.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.6203 | 0 | 747.6222 | -0.0018961 | -0.0018961 | 11.5688 | 1.4874 | 7.4601 | 5.9754 | 0 | 0 | 3.7861 | 0 | 0 | 0 | 0 | 30.2779 | 30.2778 | -7.679e-05
NY_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 550454.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91672.8718 | 0 | 0 | 642127.1425 | 0 | 642127.1425 | 0 | 0 | 3693.5482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615.125 | 0 | 0 | 4308.6731 | 0 | 4308.6731 | 0 | 0 | 550.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6729 | 0 | 0 | 642.1271 | 0 | 642.1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2928 | 3.7127 | 0 | 0 | 26.0055 | 26.0055 | 0
NY_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 25318.2996 | 66288.2653 | 10764.1673 | 53987.5506 | 0 | 41353.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197711.6909 | 0 | 197713.358 | -1.6671 | -1.6671 | 0 | 3681.2808 | 9638.3138 | 1565.1099 | 7849.7899 | 0 | 6012.7855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28747.2798 | 0 | 28747.5223 | -0.2424 | -0.2424 | 0 | 86.386 | 226.1756 | 36.7273 | 184.2055 | 0 | 141.0978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.5923 | 0 | 674.598 | -0.0056883 | -0.0056883 | 9.1599 | 1.4874 | 7.4601 | 5.7143 | 0 | 0 | 3.4985 | 0 | 0 | 0 | 0 | 27.3205 | 27.3203 | -0.00023037
NY_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 580519.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91682.35 | 0 | 0 | 672201.3797 | 0 | 672201.3797 | 0 | 0 | 3895.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615.1886 | 0 | 0 | 4510.4713 | 0 | 4510.4713 | 0 | 0 | 580.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6824 | 0 | 0 | 672.2014 | 0 | 672.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5104 | 3.713 | 0 | 0 | 27.2234 | 27.2234 | 0
NY_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 42356.4705 | 58469.3787 | 79100.2363 | 12303.4933 | 154949.5496 | 0 | 45154.4872 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392405.8583 | 0 | 392406.1361 | -0.27786 | -0.27786 | 6158.6308 | 8501.4477 | 11501.1744 | 1788.9279 | 22529.6645 | 0 | 6565.4624 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 57055.8118 | 0 | 57055.8522 | -0.0404 | -0.0404 | 144.5203 | 199.4975 | 269.89 | 41.9795 | 528.6879 | 0 | 154.0671 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.8888 | 0 | 1338.8897 | -0.00094805 | -0.00094805 | 6.2472 | 0.9717 | 12.2376 | 3.5662 | 0.0057056 | 0 | 4.6178 | 3.3452 | 0 | 0 | 0 | 30.9914 | 30.9914 | -2.1945e-05
NY_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 97416.6436 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 614782.6185 | 0 | 0 | 1111694.7 | 0 | 1111694.7 | 0 | 0 | 653.6657 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.1914 | 0 | 0 | 7459.4714 | 0 | 7459.4714 | 0 | 0 | 97.4166 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 614.7826 | 0 | 0 | 1111.6947 | 0 | 1111.6947 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.2549 | 14.2304 | 0 | 0 | 25.7325 | 25.7325 | 0
NY_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 47277.3121 | 54315.4215 | 50750.5205 | 12303.4933 | 154949.5496 | 0 | 42764.9198 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 362433.4595 | 0 | 362434.5709 | -1.1114 | -1.1114 | 6874.1212 | 7897.4623 | 7379.1257 | 1788.9279 | 22529.6645 | 0 | 6218.0193 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 52697.825 | 0 | 52697.9866 | -0.1616 | -0.1616 | 161.3102 | 185.3242 | 173.1608 | 41.9795 | 528.6879 | 0 | 145.9139 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.623 | 0 | 1236.6268 | -0.0037922 | -0.0037922 | 4.0082 | 0.9717 | 12.2376 | 3.3775 | 0.0057056 | 0 | 4.2897 | 3.7339 | 0 | 0 | 0 | 28.6243 | 28.6242 | -8.7778e-05
NY_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 94772.2338 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 614848.9657 | 0 | 0 | 1109116.6375 | 0 | 1109116.6375 | 0 | 0 | 635.9217 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.6366 | 0 | 0 | 7442.1726 | 0 | 7442.1726 | 0 | 0 | 94.7722 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 614.849 | 0 | 0 | 1109.1166 | 0 | 1109.1166 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.1937 | 14.232 | 0 | 0 | 25.6728 | 25.6728 | 0
NY_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 4620.7564 | 3125.8875 | 8805.2778 | 1586.5616 | 13417.6985 | 0 | 4687.442 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41247.8224 | 0 | 41247.5445 | 0.27786 | 0.27786 | 671.858 | 454.504 | 1280.2874 | 230.6861 | 1950.9334 | 0 | 681.5541 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 5997.4334 | 0 | 5997.393 | 0.0404 | 0.0404 | 15.766 | 10.6655 | 30.0436 | 5.4133 | 45.7812 | 0 | 15.9936 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.7376 | 0 | 140.7366 | 0.00094805 | 0.00094805 | 5.4605 | 0.98389 | 8.3208 | 2.9069 | 0 | 0 | 1.9385 | 2.8655 | 3.1033 | 0 | 0 | 25.5792 | 25.5793 | 0.00017231
NY_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 10397.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10397.5538 | 0 | 10397.5538 | 0 | 0 | 69.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.7676 | 0 | 69.7676 | 0 | 0 | 10.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3976 | 0 | 10.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8898 | 0 | 0 | 0 | 1.8898 | 1.8898 | 0
NY_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 4648.5421 | 2942.5021 | 7102.0164 | 1586.5616 | 13417.6985 | 0 | 4306.7784 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39008.2977 | 0 | 39011.0762 | -2.7786 | -2.7786 | 675.898 | 427.8398 | 1032.6332 | 230.6861 | 1950.9334 | 0 | 626.2056 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 5671.8065 | 0 | 5672.2105 | -0.404 | -0.404 | 15.8608 | 10.0398 | 24.2321 | 5.4133 | 45.7812 | 0 | 14.6947 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.0963 | 0 | 133.1058 | -0.0094805 | -0.0094805 | 4.4042 | 0.98389 | 8.3208 | 2.6708 | 0 | 0 | 1.8248 | 2.8827 | 3.1033 | 0 | 0 | 24.1923 | 24.1905 | -0.0017231
NY_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | NY-ALBANY-NY | Zone5A | Zone5A(NY-ALBANY-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 11042.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.0694 | 0 | 11042.0694 | 0 | 0 | 74.0923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0923 | 0 | 74.0923 | 0 | 0 | 11.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0421 | 0 | 11.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0069 | 0 | 0 | 0 | 2.0069 | 2.0069 | 0
NY_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 489044.4075 | 880875.1025 | 96399.5925 | 4077910.5986 | 543457.0788 | 584543.7444 | 78058.2738 | 159973.1982 | 426846.1923 | 12172.9006 | 0 | 0 | 0 | 7349281.0892 | 0 | 7349284.1457 | -3.0564 | 543454.0224 | 0 | 71107.0569 | 128079.2399 | 14016.5007 | 592928.201 | 79018.6593 | 84992.6604 | 11349.673 | 23260.103 | 62063.4364 | 1769.9398 | 0 | 0 | 0 | 1068585.4704 | 0 | 1068585.9148 | -0.4444 | 79018.2149 | 0 | 1668.6195 | 3005.5458 | 328.9154 | 13913.831 | 1854.2756 | 1994.4633 | 266.3348 | 545.8286 | 1456.3992 | 41.5339 | 0 | 0 | 0 | 25075.7471 | 0 | 25075.7575 | -0.010429 | 1854.2651 | 6.0281 | 0.65969 | 27.9065 | 4.0002 | 0.53418 | 0.083303 | 3.3467 | 0 | 0 | 2.921 | 0 | 50.2935 | 50.2935 | -2.0916e-05
NY_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 1514659.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609598.0589 | 0 | 0 | 2124257.2075 | 0 | 2124257.2075 | 0 | 0 | 10163.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4090.403 | 0 | 0 | 14253.7659 | 0 | 14253.7659 | 0 | 0 | 1514.6591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.5981 | 0 | 0 | 2124.2572 | 0 | 2124.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0379 | 1.2226 | 0 | 0 | 4.2605 | 4.2605 | 0
NY_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 454470.7023 | 717531.5029 | 96399.5925 | 4077910.5986 | 543387.6147 | 562443.025 | 73684.8099 | 143146.1983 | 426590.5642 | 10869.7529 | 0 | 0 | 0 | 7106434.3612 | 0 | 7106431.8605 | 2.5007 | 543390.1154 | 0 | 66080.0401 | 104329.0805 | 14016.5007 | 592928.201 | 79008.5592 | 81779.2158 | 10713.7714 | 20813.4572 | 62026.268 | 1580.4621 | 0 | 0 | 0 | 1033275.5561 | 0 | 1033275.1925 | 0.3636 | 79008.9228 | 0 | 1550.654 | 2448.2175 | 328.9154 | 13913.831 | 1854.0385 | 1919.0556 | 251.4126 | 488.4148 | 1455.527 | 37.0876 | 0 | 0 | 0 | 24247.154 | 0 | 24247.1455 | 0.0085324 | 1854.0471 | 4.9103 | 0.65969 | 27.9065 | 3.849 | 0.50425 | 0.074385 | 3.1101 | 0 | 0 | 2.9193 | 0 | 48.6316 | 48.6316 | 1.7113e-05
NY_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 1546211.9805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609588.5807 | 0 | 0 | 2155800.5613 | 0 | 2155800.5613 | 0 | 0 | 10375.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4090.3394 | 0 | 0 | 14465.4218 | 0 | 14465.4218 | 0 | 0 | 1546.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.5886 | 0 | 0 | 2155.8006 | 0 | 2155.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1012 | 1.2226 | 0 | 0 | 4.3238 | 4.3238 | 0
NY_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 20603.0719 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 20264.0868 | 0 | 0 | 0 | 0 | 121992.9702 | 0 | 0 | 340438.3256 | 0 | 340436.1028 | 2.2229 | 2.2229 | 0 | 2995.6867 | 4125.6847 | 1046.7733 | 20647.4118 | 0 | 2946.3982 | 0 | 0 | 0 | 0 | 17737.7779 | 0 | 0 | 49499.7325 | 0 | 49499.4093 | 0.3232 | 0.3232 | 0 | 70.2977 | 96.8146 | 24.5639 | 484.5184 | 0 | 69.1411 | 0 | 0 | 0 | 0 | 416.24 | 0 | 0 | 1161.5756 | 0 | 1161.568 | 0.0075844 | 0.0075844 | 2.8693 | 0.72801 | 14.3599 | 2.0492 | 0 | 0 | 2.0834 | 0 | 12.3363 | 0 | 0 | 34.426 | 34.4262 | 0.00022478
NY_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 206425.0906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206425.0906 | 0 | 206425.0906 | 0 | 0 | 1385.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1385.1124 | 0 | 1385.1124 | 0 | 0 | 206.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.4251 | 0 | 206.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1179 | 0 | 0 | 0 | 6.1179 | 6.1179 | 0
NY_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 18949.8248 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 19508.3167 | 0 | 0 | 0 | 0 | 122029.0916 | 0 | 0 | 332872.2885 | 0 | 332870.6214 | 1.6671 | 1.6671 | 0 | 2755.3045 | 3370.602 | 1046.7733 | 20647.4118 | 0 | 2836.5092 | 0 | 0 | 0 | 0 | 17743.0299 | 0 | 0 | 48399.6308 | 0 | 48399.3884 | 0.2424 | 0.2424 | 0 | 64.6568 | 79.0956 | 24.5639 | 484.5184 | 0 | 66.5624 | 0 | 0 | 0 | 0 | 416.3633 | 0 | 0 | 1135.7602 | 0 | 1135.7546 | 0.0056883 | 0.0056883 | 2.3442 | 0.72801 | 14.3599 | 1.9727 | 0 | 0 | 1.9163 | 0 | 12.34 | 0 | 0 | 33.661 | 33.6611 | 0.00016859
NY_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 234120.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234120.3068 | 0 | 234120.3068 | 0 | 0 | 1570.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1570.9473 | 0 | 1570.9473 | 0 | 0 | 234.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.1203 | 0 | 234.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9387 | 0 | 0 | 0 | 6.9387 | 6.9387 | 0
NY_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 67135.7282 | 97674.9546 | 7152.0306 | 317887.4784 | 4818.0346 | 95471.5512 | 1225.3479 | 0 | 0 | 20305.7653 | 7179.8163 | 17624.4485 | 0 | 636475.1557 | 0 | 636478.2121 | -3.0564 | 4814.9782 | 0 | 9761.5349 | 14201.9384 | 1039.9053 | 46220.8394 | 700.5422 | 13881.5635 | 178.1656 | 0 | 0 | 2952.4583 | 1043.9453 | 2562.5948 | 0 | 92543.4876 | 0 | 92543.932 | -0.4444 | 700.0978 | 0 | 229.0671 | 333.2669 | 24.4027 | 1084.6321 | 16.4391 | 325.7489 | 4.1809 | 0 | 0 | 69.2833 | 24.4975 | 60.1346 | 0 | 2171.6532 | 0 | 2171.6637 | -0.010429 | 16.4287 | 4.5061 | 0.32995 | 14.6653 | 4.4045 | 0.05653 | 0.93678 | 3.0972 | 0 | 0.33123 | 0 | 0.81308 | 29.3631 | 29.3629 | -0.000141
NY_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 776195.8741 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127092.7976 | 0 | 0 | 1245479.0865 | 0 | 1245479.0865 | 0 | 0 | 5208.2743 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 852.7927 | 0 | 0 | 8357.1647 | 0 | 8357.1647 | 0 | 0 | 776.1959 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.0928 | 0 | 0 | 1245.4791 | 0 | 1245.4791 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.4949 | 1.7184 | 0 | 0 | 16.8401 | 16.8401 | 0
NY_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 62564.986 | 79878.235 | 7152.0306 | 312483.1662 | 4745.7919 | 81717.6461 | 975.2769 | 0 | 0 | 22728.6755 | 7182.5949 | 12472.9858 | 0 | 591901.3889 | 0 | 591899.444 | 1.945 | 4747.7369 | 0 | 9096.949 | 11614.2954 | 1039.9053 | 45435.0524 | 690.0381 | 11881.7457 | 141.8053 | 0 | 0 | 3304.7494 | 1044.3493 | 1813.5721 | 0 | 86062.462 | 0 | 86062.1792 | 0.2828 | 690.3209 | 0 | 213.4717 | 272.5445 | 24.4027 | 1066.1926 | 16.1926 | 278.8206 | 3.3276 | 0 | 0 | 77.5502 | 24.507 | 42.5578 | 0 | 2019.5675 | 0 | 2019.5609 | 0.0066363 | 16.1993 | 3.6851 | 0.32995 | 14.416 | 3.7699 | 0.044993 | 1.0486 | 2.8864 | 0 | 0.33136 | 0 | 0.57542 | 27.3065 | 27.3066 | 8.973e-05
NY_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 760746.455 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126808.4525 | 0 | 0 | 1229745.3223 | 0 | 1229745.3223 | 0 | 0 | 5104.6087 | 0 | 0 | 0 | 2296.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 850.8847 | 0 | 0 | 8251.5911 | 0 | 8251.5911 | 0 | 0 | 760.7465 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.8085 | 0 | 0 | 1229.7453 | 0 | 1229.7453 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.2861 | 1.7146 | 0 | 0 | 16.6274 | 16.6274 | 0
NY_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 23951.2448 | 91025.8445 | 10764.1673 | 53987.5506 | 0 | 44979.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224708.2447 | 0 | 224704.3547 | 3.89 | 3.89 | 0 | 3482.511 | 13235.1578 | 1565.1099 | 7849.7899 | 0 | 6540.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32672.5788 | 0 | 32672.0132 | 0.56561 | 0.56561 | 0 | 81.7216 | 310.5802 | 36.7273 | 184.2055 | 0 | 153.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766.7045 | 0 | 766.6913 | 0.013273 | 0.013273 | 12.5782 | 1.4874 | 7.4601 | 6.2154 | 0 | 0 | 3.3096 | 0 | 0 | 0 | 0 | 31.0502 | 31.0507 | 0.00053753
NY_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 684541.9586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92990.3376 | 0 | 0 | 777532.2962 | 0 | 777532.2962 | 0 | 0 | 4593.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.9652 | 0 | 0 | 5217.2417 | 0 | 5217.2417 | 0 | 0 | 684.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9903 | 0 | 0 | 777.5323 | 0 | 777.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7232 | 3.766 | 0 | 0 | 31.4892 | 31.4892 | 0
NY_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 0 | 22086.8266 | 75288.0428 | 10764.1673 | 53987.5506 | 0 | 43067.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205194.3709 | 0 | 205191.8702 | 2.5007 | 2.5007 | 0 | 3211.4246 | 10946.8814 | 1565.1099 | 7849.7899 | 0 | 6262.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29835.2615 | 0 | 29834.8979 | 0.3636 | 0.3636 | 0 | 75.3603 | 256.8828 | 36.7273 | 184.2055 | 0 | 146.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.1232 | 0 | 700.1147 | 0.0085324 | 0.0085324 | 10.4035 | 1.4874 | 7.4601 | 5.9512 | 0 | 0 | 3.052 | 0 | 0 | 0 | 0 | 28.3539 | 28.3543 | 0.00034555
NY_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 716445.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92999.8158 | 0 | 0 | 809445.2987 | 0 | 809445.2987 | 0 | 0 | 4807.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624.0288 | 0 | 0 | 5431.378 | 0 | 5431.378 | 0 | 0 | 716.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9998 | 0 | 0 | 809.4453 | 0 | 809.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0153 | 3.7664 | 0 | 0 | 32.7817 | 32.7817 | 0
NY_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 55318.4841 | 53759.7082 | 79155.8076 | 12292.379 | 154949.5496 | 0 | 45048.9016 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 400597.0729 | 0 | 400597.9064 | -0.83357 | -0.83357 | 8043.3076 | 7816.6616 | 11509.2544 | 1787.3119 | 22529.6645 | 0 | 6550.1103 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 58246.8144 | 0 | 58246.9356 | -0.1212 | -0.1212 | 188.7467 | 183.4281 | 270.0796 | 41.9416 | 528.6879 | 0 | 153.7069 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.8372 | 0 | 1366.8401 | -0.0028441 | -0.0028441 | 6.2516 | 0.97083 | 12.2376 | 3.5579 | 0.0057056 | 0 | 4.2458 | 4.3689 | 0 | 0 | 0 | 31.6384 | 31.6383 | -6.5834e-05
NY_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 127670.9661 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 640307.3336 | 0 | 0 | 1167473.7376 | 0 | 1167473.7376 | 0 | 0 | 856.6722 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 4296.4622 | 0 | 0 | 7833.7488 | 0 | 7833.7488 | 0 | 0 | 127.671 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 640.3073 | 0 | 0 | 1167.4737 | 0 | 1167.4737 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.9552 | 14.8212 | 0 | 0 | 27.0236 | 27.0236 | 0
NY_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 61189.5955 | 49589.0796 | 50864.4417 | 12292.379 | 154949.5496 | 0 | 42620.4343 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371577.7224 | 0 | 371576.8889 | 0.83357 | 0.83357 | 8896.9672 | 7210.2522 | 7395.6898 | 1787.3119 | 22529.6645 | 0 | 6197.0112 | 10.5041 | 0 | 0 | 0 | 0 | 0 | 0 | 54027.4008 | 0 | 54027.2796 | 0.1212 | 0.1212 | 208.7789 | 169.1979 | 173.5495 | 41.9416 | 528.6879 | 0 | 145.4209 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.8232 | 0 | 1267.8203 | 0.0028441 | 0.0028441 | 4.0172 | 0.97083 | 12.2376 | 3.3661 | 0.0057056 | 0 | 3.9164 | 4.8326 | 0 | 0 | 0 | 29.3463 | 29.3464 | 6.5834e-05
NY_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 122751.7952 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 640383.159 | 0 | 0 | 1162630.3921 | 0 | 1162630.3921 | 0 | 0 | 823.6645 | 0 | 0 | 0 | 2680.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 4296.971 | 0 | 0 | 7801.2499 | 0 | 7801.2499 | 0 | 0 | 122.7518 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 640.3832 | 0 | 0 | 1162.6304 | 0 | 1162.6304 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.8413 | 14.823 | 0 | 0 | 26.9115 | 26.9115 | 0
NY_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 5265.3839 | 2711.8811 | 8821.9492 | 1592.1187 | 13417.6985 | 0 | 4818.0346 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41631.2646 | 0 | 41629.5975 | 1.6671 | 1.6671 | 765.5868 | 394.3075 | 1282.7114 | 231.4941 | 1950.9334 | 0 | 700.5422 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 6053.1859 | 0 | 6052.9435 | 0.2424 | 0.2424 | 17.9655 | 9.2529 | 30.1005 | 5.4323 | 45.7812 | 0 | 16.4391 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.0459 | 0 | 142.0402 | 0.0056883 | 0.0056883 | 5.4708 | 0.98733 | 8.3208 | 2.9878 | 0 | 0 | 1.6817 | 3.2653 | 3.1033 | 0 | 0 | 25.8161 | 25.8171 | 0.0010339
NY_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 20956.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20956.2365 | 0 | 20956.2365 | 0 | 0 | 140.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.6163 | 0 | 140.6163 | 0 | 0 | 20.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9562 | 0 | 20.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8088 | 0 | 0 | 0 | 3.8088 | 3.8088 | 0
NY_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Electricity | 5329.2909 | 2472.9243 | 7129.8021 | 1592.1187 | 13417.6985 | 0 | 4367.9068 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39313.94 | 0 | 39315.6071 | -1.6671 | -1.6671 | 774.8789 | 359.5632 | 1036.6732 | 231.4941 | 1950.9334 | 0 | 635.0937 | 0 | 0 | 0 | 0 | 727.6105 | 0 | 0 | 5716.2469 | 0 | 5716.4893 | -0.2424 | -0.2424 | 18.1835 | 8.4376 | 24.3269 | 5.4323 | 45.7812 | 0 | 14.9033 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.1392 | 0 | 134.1449 | -0.0056883 | -0.0056883 | 4.4215 | 0.98733 | 8.3208 | 2.7087 | 0 | 0 | 1.5336 | 3.3049 | 3.1033 | 0 | 0 | 24.3811 | 24.3801 | -0.0010339
NY_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | NY-MASSENA-NY | Zone6A | Zone6A(NY-MASSENA-NY) |  |  | NY | 0.1454 | 0.00671 |  |  |  | Natural Gas | 22235.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22235.7896 | 0 | 22235.7896 | 0 | 0 | 149.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.2021 | 0 | 149.2021 | 0 | 0 | 22.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2358 | 0 | 22.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0414 | 0 | 0 | 0 | 4.0414 | 4.0414 | 0
OH_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 598375.4493 | 880666.71 | 95952.2432 | 4077910.5986 | 543457.0788 | 586355.3698 | 89989.4391 | 223210.5973 | 356320.6128 | 13206.5274 | 0 | 0 | 0 | 7465444.6265 | 0 | 7465447.6829 | -3.0564 | 543454.0224 | 0 | 56307.1298 | 82870.7374 | 9029.1061 | 383731.3873 | 51139.3111 | 55176.0403 | 8468.0062 | 21004.1172 | 33529.7697 | 1242.7342 | 0 | 0 | 0 | 702498.3394 | 0 | 702498.627 | -0.28761 | 51139.0235 | 0 | 2041.657 | 3004.8348 | 327.3891 | 13913.831 | 1854.2756 | 2000.6445 | 307.044 | 761.5946 | 1215.7659 | 45.0607 | 0 | 0 | 0 | 25472.0971 | 0 | 25472.1075 | -0.010429 | 1854.2651 | 6.0267 | 0.65663 | 27.9065 | 4.0126 | 0.61583 | 0.090377 | 4.0949 | 0 | 0 | 2.4384 | 0 | 51.0885 | 51.0885 | -2.0916e-05
OH_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 910075.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563941.7082 | 0 | 0 | 1474016.7505 | 0 | 1474016.7505 | 0 | 0 | 4870.7216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3018.216 | 0 | 0 | 7888.9376 | 0 | 7888.9376 | 0 | 0 | 910.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.9417 | 0 | 0 | 1474.0168 | 0 | 1474.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8253 | 1.1311 | 0 | 0 | 2.9564 | 2.9564 | 0
OH_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 562459.6964 | 716675.7044 | 95952.2432 | 4077910.5986 | 543384.8361 | 561178.7771 | 86944.1301 | 200770.8928 | 356051.0918 | 11903.3797 | 0 | 0 | 0 | 7213231.3502 | 0 | 7213229.9609 | 1.3893 | 543386.2254 | 0 | 52927.4574 | 67439.1838 | 9029.1061 | 383731.3873 | 51132.5131 | 52806.9229 | 8181.4426 | 18892.541 | 33504.4077 | 1120.108 | 0 | 0 | 0 | 678765.0701 | 0 | 678764.9393 | 0.13073 | 51132.6438 | 0 | 1919.1125 | 2445.2975 | 327.3891 | 13913.831 | 1854.0291 | 1914.742 | 296.6534 | 685.0303 | 1214.8463 | 40.6143 | 0 | 0 | 0 | 24611.5454 | 0 | 24611.5406 | 0.0047402 | 1854.0338 | 4.9044 | 0.65663 | 27.9065 | 3.8403 | 0.59499 | 0.081459 | 3.8491 | 0 | 0 | 2.4366 | 0 | 49.3625 | 49.3625 | 9.5073e-06
OH_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 856788.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563932.2301 | 0 | 0 | 1420720.9939 | 0 | 1420720.9939 | 0 | 0 | 4585.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3018.1653 | 0 | 0 | 7603.6988 | 0 | 7603.6988 | 0 | 0 | 856.7888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563.9322 | 0 | 0 | 1420.721 | 0 | 1420.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7184 | 1.1311 | 0 | 0 | 2.8495 | 2.8495 | 0
OH_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 25318.2996 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20650.3076 | 0 | 0 | 0 | 0 | 113073.7711 | 0 | 0 | 336623.3536 | 0 | 336623.9093 | -0.55571 | -0.55571 | 0 | 2382.452 | 2670.0614 | 677.7124 | 13362.5959 | 0 | 1943.1939 | 0 | 0 | 0 | 0 | 10640.2419 | 0 | 0 | 31676.2576 | 0 | 31676.3099 | -0.052293 | -0.052293 | 0 | 86.386 | 96.8146 | 24.5734 | 484.5184 | 0 | 70.4588 | 0 | 0 | 0 | 0 | 385.8077 | 0 | 0 | 1148.5589 | 0 | 1148.5608 | -0.0018961 | -0.0018961 | 2.8693 | 0.72829 | 14.3599 | 2.0882 | 0 | 0 | 2.5603 | 0 | 11.4344 | 0 | 0 | 34.0405 | 34.0405 | -5.6196e-05
OH_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 110477.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110477.5635 | 0 | 110477.5635 | 0 | 0 | 591.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.2759 | 0 | 591.2759 | 0 | 0 | 110.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4776 | 0 | 110.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2743 | 0 | 0 | 0 | 3.2743 | 3.2743 | 0
OH_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 24284.6728 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20083.48 | 0 | 0 | 0 | 0 | 113107.1139 | 0 | 0 | 329863.1008 | 0 | 329867.5465 | -4.4457 | -4.4457 | 0 | 2285.1877 | 2181.3869 | 677.7124 | 13362.5959 | 0 | 1889.8555 | 0 | 0 | 0 | 0 | 10643.3794 | 0 | 0 | 31040.1178 | 0 | 31040.5361 | -0.41834 | -0.41834 | 0 | 82.8593 | 79.0956 | 24.5734 | 484.5184 | 0 | 68.5248 | 0 | 0 | 0 | 0 | 385.9215 | 0 | 0 | 1125.4929 | 0 | 1125.5081 | -0.015169 | -0.015169 | 2.3442 | 0.72829 | 14.3599 | 2.0309 | 0 | 0 | 2.4557 | 0 | 11.4378 | 0 | 0 | 33.3573 | 33.3568 | -0.00044956
OH_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 125254.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125254.0324 | 0 | 125254.0324 | 0 | 0 | 670.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670.3596 | 0 | 670.3596 | 0 | 0 | 125.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.254 | 0 | 125.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7122 | 0 | 0 | 0 | 3.7122 | 3.7122 | 0
OH_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 98125.0824 | 96894.1773 | 7115.9093 | 317887.4784 | 4818.0346 | 91481.5295 | 752.9916 | 0 | 0 | 18702.5323 | 7179.8163 | 17627.227 | 0 | 660584.7788 | 0 | 660587.8352 | -3.0564 | 4814.9782 | 0 | 9233.5703 | 9117.7421 | 669.6071 | 29913.2117 | 453.3771 | 8608.4119 | 70.8565 | 0 | 0 | 1759.9083 | 675.6207 | 1658.7221 | 0 | 62161.0277 | 0 | 62161.3153 | -0.28761 | 453.0894 | 0 | 334.8028 | 330.6029 | 24.2795 | 1084.6321 | 16.4391 | 312.135 | 2.5692 | 0 | 0 | 63.813 | 24.4975 | 60.1441 | 0 | 2253.9153 | 0 | 2253.9257 | -0.010429 | 16.4287 | 4.4701 | 0.32828 | 14.6653 | 4.2204 | 0.034738 | 0.86282 | 4.5269 | 0 | 0.33123 | 0 | 0.81321 | 30.4753 | 30.4752 | -0.000141
OH_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 431825.4799 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118022.1878 | 0 | 0 | 892038.0825 | 0 | 892038.0825 | 0 | 0 | 2311.13 | 0 | 0 | 0 | 1831.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 631.6547 | 0 | 0 | 4774.1878 | 0 | 4774.1878 | 0 | 0 | 431.8255 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.0222 | 0 | 0 | 892.0381 | 0 | 892.0381 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.8387 | 1.5958 | 0 | 0 | 12.0613 | 12.0613 | 0
OH_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 92615.1847 | 78541.7444 | 7115.9093 | 312483.1662 | 4743.0133 | 78802.9297 | 536.2634 | 0 | 0 | 22912.0609 | 7179.8163 | 12489.6572 | 0 | 617419.7454 | 0 | 617425.0246 | -5.2793 | 4737.7341 | 0 | 8715.0889 | 7390.7781 | 669.6071 | 29404.6659 | 446.3176 | 7415.3557 | 50.4624 | 0 | 0 | 2156.0249 | 675.6207 | 1175.2767 | 0 | 58099.198 | 0 | 58099.6948 | -0.49678 | 445.8208 | 0 | 316.003 | 267.9844 | 24.2795 | 1066.1926 | 16.1832 | 268.8756 | 1.8297 | 0 | 0 | 78.176 | 24.4975 | 42.6147 | 0 | 2106.6362 | 0 | 2106.6542 | -0.018013 | 16.1651 | 3.6234 | 0.32828 | 14.416 | 3.6355 | 0.02474 | 1.057 | 4.2727 | 0 | 0.33123 | 0 | 0.57619 | 28.4841 | 28.4838 | -0.00024355
OH_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 410546.9855 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 117794.7117 | 0 | 0 | 870532.112 | 0 | 870532.112 | 0 | 0 | 2197.2475 | 0 | 0 | 0 | 1831.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 630.4373 | 0 | 0 | 4659.0879 | 0 | 4659.0879 | 0 | 0 | 410.547 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 117.7947 | 0 | 0 | 870.5321 | 0 | 870.5321 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.551 | 1.5927 | 0 | 0 | 11.7705 | 11.7705 | 0
OH_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 34565.3695 | 83704.3213 | 10669.6961 | 53987.5506 | 0 | 42445.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225372.3222 | 0 | 225372.3222 | 0 | 0 | 0 | 3252.6013 | 7876.5766 | 1004.0184 | 5080.2285 | 0 | 3994.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21207.5355 | 0 | 21207.5355 | 0 | 0 | 0 | 117.937 | 285.5991 | 36.405 | 184.2055 | 0 | 144.8237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768.9704 | 0 | 768.9704 | 0 | 0 | 11.5665 | 1.4744 | 7.4601 | 5.8652 | 0 | 0 | 4.7763 | 0 | 0 | 0 | 0 | 31.1425 | 31.1425 | 0
OH_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 419446.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90298.537 | 0 | 0 | 509745.5253 | 0 | 509745.5253 | 0 | 0 | 2244.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.2778 | 0 | 0 | 2728.1581 | 0 | 2728.1581 | 0 | 0 | 419.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2985 | 0 | 0 | 509.7455 | 0 | 509.7455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.9872 | 3.657 | 0 | 0 | 20.6442 | 20.6442 | 0
OH_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 32228.5949 | 66040.9729 | 10669.6961 | 53987.5506 | 0 | 40692.1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203618.9236 | 0 | 203617.8122 | 1.1114 | 1.1114 | 0 | 3032.7108 | 6214.4556 | 1004.0184 | 5080.2285 | 0 | 3829.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19160.5407 | 0 | 19160.4361 | 0.10459 | 0.10459 | 0 | 109.964 | 225.3318 | 36.405 | 184.2055 | 0 | 138.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694.7478 | 0 | 694.744 | 0.0037922 | 0.0037922 | 9.1257 | 1.4744 | 7.4601 | 5.6229 | 0 | 0 | 4.4534 | 0 | 0 | 0 | 0 | 28.1364 | 28.1366 | 0.00015358
OH_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 446213.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90308.0152 | 0 | 0 | 536521.3589 | 0 | 536521.3589 | 0 | 0 | 2388.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.3285 | 0 | 0 | 2871.4623 | 0 | 2871.4623 | 0 | 0 | 446.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.308 | 0 | 0 | 536.5214 | 0 | 536.5214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0712 | 3.6574 | 0 | 0 | 21.7286 | 21.7286 | 0
OH_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 30161.3413 | 68041.5409 | 79222.4932 | 12300.7147 | 154949.5496 | 0 | 45701.8648 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 390449.7473 | 0 | 390450.0252 | -0.27786 | -0.27786 | 2838.1822 | 6402.709 | 7454.8366 | 1157.4973 | 14580.7526 | 0 | 4300.5455 | 6.798 | 0 | 0 | 0 | 0 | 0 | 0 | 36741.3212 | 0 | 36741.3474 | -0.026146 | -0.026146 | 102.9105 | 232.1577 | 270.3071 | 41.97 | 528.6879 | 0 | 155.9348 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1332.2145 | 0 | 1332.2155 | -0.00094805 | -0.00094805 | 6.2568 | 0.97148 | 12.2376 | 3.6094 | 0.0057056 | 0 | 5.3738 | 2.3821 | 0 | 0 | 0 | 30.8369 | 30.8369 | -2.1945e-05
OH_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 70792.4607 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 588073.1321 | 0 | 0 | 1058361.0307 | 0 | 1058361.0307 | 0 | 0 | 378.8812 | 0 | 0 | 0 | 2138.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 3147.3674 | 0 | 0 | 5664.3482 | 0 | 5664.3482 | 0 | 0 | 70.7925 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 588.0731 | 0 | 0 | 1058.361 | 0 | 1058.361 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6386 | 13.6122 | 0 | 0 | 24.498 | 24.498 | 0
OH_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 34070.7847 | 63370.7703 | 50811.6489 | 12300.7147 | 154949.5496 | 0 | 43276.1761 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 358851.887 | 0 | 358854.1099 | -2.2229 | -2.2229 | 3206.0608 | 5963.1895 | 4781.3762 | 1157.4973 | 14580.7526 | 0 | 4072.2882 | 6.798 | 0 | 0 | 0 | 0 | 0 | 0 | 33767.9626 | 0 | 33768.1717 | -0.20917 | -0.20917 | 116.2495 | 216.2211 | 173.3693 | 41.97 | 528.6879 | 0 | 147.6583 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1224.4026 | 0 | 1224.4102 | -0.0075844 | -0.0075844 | 4.013 | 0.97148 | 12.2376 | 3.4179 | 0.0057056 | 0 | 5.0049 | 2.6908 | 0 | 0 | 0 | 28.3415 | 28.3413 | -0.00017556
OH_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 69474.9949 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 588177.392 | 0 | 0 | 1057147.8248 | 0 | 1057147.8248 | 0 | 0 | 371.8302 | 0 | 0 | 0 | 2138.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 3147.9254 | 0 | 0 | 5657.8552 | 0 | 5657.8552 | 0 | 0 | 69.475 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 588.1774 | 0 | 0 | 1057.1478 | 0 | 1057.1478 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6081 | 13.6146 | 0 | 0 | 24.4699 | 24.4699 | 0
OH_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 3526.0011 | 3753.8436 | 8849.7349 | 1592.1187 | 13417.6985 | 0 | 4951.4058 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41095.0012 | 0 | 41093.0562 | 1.945 | 1.945 | 331.7967 | 353.2367 | 832.7601 | 149.8184 | 1262.6054 | 0 | 465.9273 | 0 | 0 | 0 | 0 | 470.8951 | 0 | 0 | 3867.0396 | 0 | 3866.8566 | 0.18302 | 0.18302 | 12.0307 | 12.8081 | 30.1953 | 5.4323 | 45.7812 | 0 | 16.8942 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.2161 | 0 | 140.2095 | 0.0066363 | 0.0066363 | 5.4881 | 0.98733 | 8.3208 | 3.0706 | 0 | 0 | 2.3279 | 2.1866 | 3.1033 | 0 | 0 | 25.4834 | 25.4846 | 0.0012062
OH_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 7421.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7421.408 | 0 | 7421.408 | 0 | 0 | 39.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7194 | 0 | 39.7194 | 0 | 0 | 7.4214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4214 | 0 | 7.4214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3489 | 0 | 0 | 0 | 1.3489 | 1.3489 | 0
OH_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 3573.2368 | 3534.3368 | 7127.0235 | 1592.1187 | 13417.6985 | 0 | 4542.9565 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38791.5695 | 0 | 38794.0702 | -2.5007 | -2.5007 | 336.2416 | 332.5811 | 670.6529 | 149.8184 | 1262.6054 | 0 | 427.4922 | 0 | 0 | 0 | 0 | 470.8951 | 0 | 0 | 3650.2867 | 0 | 3650.522 | -0.23532 | -0.23532 | 12.1919 | 12.0592 | 24.3174 | 5.4323 | 45.7812 | 0 | 15.5006 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.3568 | 0 | 132.3654 | -0.0085324 | -0.0085324 | 4.4197 | 0.98733 | 8.3208 | 2.8173 | 0 | 0 | 2.1918 | 2.2159 | 3.1033 | 0 | 0 | 24.0577 | 24.0561 | -0.0015508
OH_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | OH-COLUMBUS-OH | Zone4A | Zone4A(OH-COLUMBUS-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 7828.9694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7828.9694 | 0 | 7828.9694 | 0 | 0 | 41.9006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.9006 | 0 | 41.9006 | 0 | 0 | 7.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.829 | 0 | 7.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4229 | 0 | 0 | 0 | 1.4229 | 1.4229 | 0
OH_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 609689.7728 | 880977.9094 | 95968.9146 | 4077910.5986 | 543457.0788 | 588544.8804 | 90183.9388 | 212802.0865 | 382133.4973 | 12181.2363 | 0 | 0 | 0 | 7493849.9137 | 0 | 7493851.8587 | -1.945 | 543455.1338 | 0 | 57371.8076 | 82900.0213 | 9030.6749 | 383731.3873 | 51139.3111 | 55382.0732 | 8486.3086 | 20024.6763 | 35958.7621 | 1146.2543 | 0 | 0 | 0 | 705171.2769 | 0 | 705171.4599 | -0.18302 | 51139.1281 | 0 | 2080.2615 | 3005.8966 | 327.4459 | 13913.831 | 1854.2756 | 2008.1151 | 307.7076 | 726.0807 | 1303.8395 | 41.5624 | 0 | 0 | 0 | 25569.0159 | 0 | 25569.0225 | -0.0066363 | 1854.2689 | 6.0288 | 0.65675 | 27.9065 | 4.0276 | 0.61716 | 0.08336 | 4.1723 | 0 | 0 | 2.6151 | 0 | 51.2829 | 51.2829 | -1.331e-05
OH_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 1217423.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571950.7629 | 0 | 0 | 1789374.4627 | 0 | 1789374.4627 | 0 | 0 | 6515.6516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3061.0805 | 0 | 0 | 9576.7321 | 0 | 9576.7321 | 0 | 0 | 1217.4237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.9508 | 0 | 0 | 1789.3745 | 0 | 1789.3745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4417 | 1.1471 | 0 | 0 | 3.5889 | 3.5889 | 0
OH_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 570850.9678 | 717028.5824 | 95968.9146 | 4077910.5986 | 543387.6147 | 570742.6037 | 85929.9532 | 191315.4303 | 381880.6477 | 10925.3242 | 0 | 0 | 0 | 7245940.6372 | 0 | 7245941.1929 | -0.55571 | 543387.059 | 0 | 53717.0761 | 67472.3896 | 9030.6749 | 383731.3873 | 51132.7745 | 53706.879 | 8086.0086 | 18002.782 | 35934.9689 | 1028.073 | 0 | 0 | 0 | 681843.014 | 0 | 681843.0663 | -0.052293 | 51132.7222 | 0 | 1947.7435 | 2446.5015 | 327.4459 | 13913.831 | 1854.0385 | 1947.3738 | 293.193 | 652.7682 | 1302.9768 | 37.2772 | 0 | 0 | 0 | 24723.1495 | 0 | 24723.1514 | -0.0018961 | 1854.0366 | 4.9069 | 0.65675 | 27.9065 | 3.9058 | 0.58805 | 0.074766 | 3.9065 | 0 | 0 | 2.6133 | 0 | 49.5863 | 49.5863 | -3.8029e-06
OH_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 1140859.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571988.6756 | 0 | 0 | 1712847.7084 | 0 | 1712847.7084 | 0 | 0 | 6105.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3061.2834 | 0 | 0 | 9167.1609 | 0 | 9167.1609 | 0 | 0 | 1140.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.9887 | 0 | 0 | 1712.8477 | 0 | 1712.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2882 | 1.1472 | 0 | 0 | 3.4354 | 3.4354 | 0
OH_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 24990.4287 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20908.7143 | 0 | 0 | 0 | 0 | 114702.0112 | 0 | 0 | 338182.1295 | 0 | 338185.4638 | -3.3343 | -3.3343 | 0 | 2351.5993 | 2670.0614 | 677.7124 | 13362.5959 | 0 | 1967.51 | 0 | 0 | 0 | 0 | 10793.4593 | 0 | 0 | 31822.9384 | 0 | 31823.2521 | -0.31376 | -0.31376 | 0 | 85.2673 | 96.8146 | 24.5734 | 484.5184 | 0 | 71.3405 | 0 | 0 | 0 | 0 | 391.3633 | 0 | 0 | 1153.8774 | 0 | 1153.8888 | -0.011377 | -0.011377 | 2.8693 | 0.72829 | 14.3599 | 2.1144 | 0 | 0 | 2.5271 | 0 | 11.599 | 0 | 0 | 34.1984 | 34.1981 | -0.00033717
OH_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 153944.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153944.4566 | 0 | 153944.4566 | 0 | 0 | 823.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823.9107 | 0 | 823.9107 | 0 | 0 | 153.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.9445 | 0 | 153.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5625 | 0 | 0 | 0 | 4.5625 | 4.5625 | 0
OH_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 24042.9375 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20400.2366 | 0 | 0 | 0 | 0 | 114732.5754 | 0 | 0 | 331563.5836 | 0 | 331563.0279 | 0.55571 | 0.55571 | 0 | 2262.4404 | 2181.3869 | 677.7124 | 13362.5959 | 0 | 1919.6623 | 0 | 0 | 0 | 0 | 10796.3353 | 0 | 0 | 31200.1332 | 0 | 31200.0809 | 0.052293 | 0.052293 | 0 | 82.0345 | 79.0956 | 24.5734 | 484.5184 | 0 | 69.6056 | 0 | 0 | 0 | 0 | 391.4675 | 0 | 0 | 1131.2949 | 0 | 1131.2931 | 0.0018961 | 0.0018961 | 2.3442 | 0.72829 | 14.3599 | 2.0629 | 0 | 0 | 2.4313 | 0 | 11.6021 | 0 | 0 | 33.5287 | 33.5288 | 5.6196e-05
OH_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 172123.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172123.589 | 0 | 172123.589 | 0 | 0 | 921.2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 921.2054 | 0 | 921.2054 | 0 | 0 | 172.1236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.1236 | 0 | 172.1236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1013 | 0 | 0 | 0 | 5.1013 | 5.1013 | 0
OH_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 95424.3156 | 96646.8849 | 7118.6878 | 317887.4784 | 4818.0346 | 92487.3706 | 903.0342 | 0 | 0 | 19163.7744 | 7179.8163 | 17630.0056 | 0 | 659259.4025 | 0 | 659259.6803 | -0.27786 | 4817.7568 | 0 | 8979.4281 | 9094.4719 | 669.8685 | 29913.2117 | 453.3771 | 8703.0616 | 84.9755 | 0 | 0 | 1803.3112 | 675.6207 | 1658.9835 | 0 | 62036.3098 | 0 | 62036.3359 | -0.026146 | 453.3509 | 0 | 325.5878 | 329.7592 | 24.289 | 1084.6321 | 16.4391 | 315.5669 | 3.0812 | 0 | 0 | 65.3868 | 24.4975 | 60.1536 | 0 | 2249.3931 | 0 | 2249.394 | -0.00094805 | 16.4382 | 4.4587 | 0.32841 | 14.6653 | 4.2668 | 0.04166 | 0.8841 | 4.4023 | 0 | 0.33123 | 0 | 0.81334 | 30.4141 | 30.4141 | -1.2819e-05
OH_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 546046.921 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119804.084 | 0 | 0 | 1008041.4198 | 0 | 1008041.4198 | 0 | 0 | 2922.4431 | 0 | 0 | 0 | 1831.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 641.1915 | 0 | 0 | 5395.0377 | 0 | 5395.0377 | 0 | 0 | 546.0469 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8041 | 0 | 0 | 1008.0414 | 0 | 1008.0414 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.3831 | 1.6199 | 0 | 0 | 13.6297 | 13.6297 | 0
OH_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 90686.8594 | 78541.7444 | 7118.6878 | 312483.1662 | 4743.0133 | 79886.5707 | 666.856 | 0 | 0 | 22634.2042 | 7179.8163 | 12492.4358 | 0 | 616433.3542 | 0 | 616430.2978 | 3.0564 | 4746.0698 | 0 | 8533.6335 | 7390.7781 | 669.8685 | 29404.6659 | 446.3176 | 7517.3263 | 62.7511 | 0 | 0 | 2129.8786 | 675.6207 | 1175.5382 | 0 | 58006.3786 | 0 | 58006.091 | 0.28761 | 446.6052 | 0 | 309.4236 | 267.9844 | 24.289 | 1066.1926 | 16.1832 | 272.573 | 2.2753 | 0 | 0 | 77.2279 | 24.4975 | 42.6242 | 0 | 2103.2706 | 0 | 2103.2602 | 0.010429 | 16.1936 | 3.6234 | 0.32841 | 14.416 | 3.6855 | 0.030765 | 1.0442 | 4.1837 | 0 | 0.33123 | 0 | 0.57632 | 28.4382 | 28.4383 | 0.000141
OH_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 523830.0877 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119567.1297 | 0 | 0 | 985587.6322 | 0 | 985587.6322 | 0 | 0 | 2803.5386 | 0 | 0 | 0 | 1831.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 639.9233 | 0 | 0 | 5274.865 | 0 | 5274.865 | 0 | 0 | 523.8301 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.5671 | 0 | 0 | 985.5876 | 0 | 985.5876 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.0827 | 1.6167 | 0 | 0 | 13.3261 | 13.3261 | 0
OH_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 33934.6349 | 83670.9785 | 10675.2532 | 53987.5506 | 0 | 43845.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226114.1995 | 0 | 226116.978 | -2.7786 | -2.7786 | 0 | 3193.2491 | 7873.4391 | 1004.5413 | 5080.2285 | 0 | 4125.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21277.3462 | 0 | 21277.6076 | -0.26146 | -0.26146 | 0 | 115.785 | 285.4854 | 36.424 | 184.2055 | 0 | 149.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 771.5016 | 0 | 771.5111 | -0.0094805 | -0.0094805 | 11.5619 | 1.4751 | 7.4601 | 6.0587 | 0 | 0 | 4.6892 | 0 | 0 | 0 | 0 | 31.2454 | 31.245 | -0.00038395
OH_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 507641.3713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90781.9238 | 0 | 0 | 598423.2951 | 0 | 598423.2951 | 0 | 0 | 2716.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485.8649 | 0 | 0 | 3202.7615 | 0 | 3202.7615 | 0 | 0 | 507.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7819 | 0 | 0 | 598.4233 | 0 | 598.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5589 | 3.6766 | 0 | 0 | 24.2355 | 24.2355 | 0
OH_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 0 | 31578.4103 | 66024.3015 | 10675.2532 | 53987.5506 | 0 | 41836.8785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204102.3942 | 0 | 204101.8385 | 0.55571 | 0.55571 | 0 | 2971.5284 | 6212.8868 | 1004.5413 | 5080.2285 | 0 | 3936.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19206.0353 | 0 | 19205.983 | 0.052293 | 0.052293 | 0 | 107.7455 | 225.2749 | 36.424 | 184.2055 | 0 | 142.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.3974 | 0 | 696.3955 | 0.0018961 | 0.0018961 | 9.1234 | 1.4751 | 7.4601 | 5.7811 | 0 | 0 | 4.3636 | 0 | 0 | 0 | 0 | 28.2033 | 28.2034 | 7.679e-05
OH_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 536928.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90791.4019 | 0 | 0 | 627720.3222 | 0 | 627720.3222 | 0 | 0 | 2873.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485.9156 | 0 | 0 | 3359.5592 | 0 | 3359.5592 | 0 | 0 | 536.9289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7914 | 0 | 0 | 627.7203 | 0 | 627.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.7451 | 3.677 | 0 | 0 | 25.422 | 25.422 | 0
OH_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 36624.2874 | 65526.9381 | 79141.9148 | 12300.7147 | 154949.5496 | 0 | 45549.0436 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 394164.691 | 0 | 394165.5246 | -0.83357 | -0.83357 | 3446.3454 | 6166.0849 | 7447.2542 | 1157.4973 | 14580.7526 | 0 | 4286.165 | 6.798 | 0 | 0 | 0 | 0 | 0 | 0 | 37090.8974 | 0 | 37090.9759 | -0.078439 | -0.078439 | 124.9621 | 223.5779 | 270.0322 | 41.97 | 528.6879 | 0 | 155.4133 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8899 | 0 | 1344.8928 | -0.0028441 | -0.0028441 | 6.2505 | 0.97148 | 12.2376 | 3.5974 | 0.0057056 | 0 | 5.1752 | 2.8925 | 0 | 0 | 0 | 31.1303 | 31.1303 | -6.5834e-05
OH_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 84204.0729 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 597323.8272 | 0 | 0 | 1081023.338 | 0 | 1081023.338 | 0 | 0 | 450.6602 | 0 | 0 | 0 | 2138.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 3196.8771 | 0 | 0 | 5785.6369 | 0 | 5785.6369 | 0 | 0 | 84.2041 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 597.3238 | 0 | 0 | 1081.0233 | 0 | 1081.0233 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.9491 | 13.8263 | 0 | 0 | 25.0225 | 25.0225 | 0
OH_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 41267.2724 | 61114.5742 | 50764.4133 | 12300.7147 | 154949.5496 | 0 | 43131.6906 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 363600.4575 | 0 | 363601.0132 | -0.55571 | -0.55571 | 3883.2503 | 5750.8814 | 4776.9313 | 1157.4973 | 14580.7526 | 0 | 4058.6921 | 6.798 | 0 | 0 | 0 | 0 | 0 | 0 | 34214.803 | 0 | 34214.8553 | -0.052293 | -0.052293 | 140.8039 | 208.5229 | 173.2082 | 41.97 | 528.6879 | 0 | 147.1653 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.6048 | 0 | 1240.6067 | -0.0018961 | -0.0018961 | 4.0093 | 0.97148 | 12.2376 | 3.4064 | 0.0057056 | 0 | 4.8267 | 3.2592 | 0 | 0 | 0 | 28.7164 | 28.7164 | -4.3889e-05
OH_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 81739.7484 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 597409.1307 | 0 | 0 | 1078644.3171 | 0 | 1078644.3171 | 0 | 0 | 437.4711 | 0 | 0 | 0 | 2138.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 3197.3337 | 0 | 0 | 5772.9044 | 0 | 5772.9044 | 0 | 0 | 81.7397 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 597.4091 | 0 | 0 | 1078.6443 | 0 | 1078.6443 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.892 | 13.8283 | 0 | 0 | 24.9675 | 24.9675 | 0
OH_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 4465.1567 | 3692.7151 | 8821.9492 | 1592.1187 | 13417.6985 | 0 | 4826.3703 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41820.2071 | 0 | 41819.3736 | 0.83357 | 0.83357 | 420.1712 | 347.4845 | 830.1454 | 149.8184 | 1262.6054 | 0 | 454.1614 | 0 | 0 | 0 | 0 | 470.8951 | 0 | 0 | 3935.2815 | 0 | 3935.2031 | 0.078439 | 0.078439 | 15.2351 | 12.5995 | 30.1005 | 5.4323 | 45.7812 | 0 | 16.4676 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.6905 | 0 | 142.6877 | 0.0028441 | 0.0028441 | 5.4708 | 0.98733 | 8.3208 | 2.993 | 0 | 0 | 2.29 | 2.769 | 3.1033 | 0 | 0 | 25.9338 | 25.9343 | 0.00051693
OH_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 9307.5641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9307.5641 | 0 | 9307.5641 | 0 | 0 | 49.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.8141 | 0 | 49.8141 | 0 | 0 | 9.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3076 | 0 | 9.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6917 | 0 | 0 | 0 | 1.6917 | 1.6917 | 0
OH_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Electricity | 4506.8352 | 3487.1012 | 7113.1307 | 1592.1187 | 13417.6985 | 0 | 4429.0353 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39550.1182 | 0 | 39548.7289 | 1.3893 | 1.3893 | 424.0932 | 328.1362 | 669.3456 | 149.8184 | 1262.6054 | 0 | 416.7722 | 0 | 0 | 0 | 0 | 470.8951 | 0 | 0 | 3721.6661 | 0 | 3721.5354 | 0.13073 | 0.13073 | 15.3773 | 11.898 | 24.27 | 5.4323 | 45.7812 | 0 | 15.1119 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.945 | 0 | 134.9403 | 0.0047402 | 0.0047402 | 4.4111 | 0.98733 | 8.3208 | 2.7466 | 0 | 0 | 2.1625 | 2.7949 | 3.1033 | 0 | 0 | 24.5257 | 24.5265 | 0.00086155
OH_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | OH-CLEVELAND-OH | Zone5A | Zone5A(OH-CLEVELAND-OH) |  |  | OH | 0.0941 | 0.005352 |  |  |  | Natural Gas | 9866.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.7762 | 0 | 9866.7762 | 0 | 0 | 52.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.807 | 0 | 52.807 | 0 | 0 | 9.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8668 | 0 | 9.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7933 | 0 | 0 | 0 | 1.7933 | 1.7933 | 0
OK_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 885990.4437 | 881261.3233 | 95766.0793 | 4077910.5986 | 543457.0788 | 591990.3031 | 117630.6205 | 318126.4352 | 297223.278 | 12973.1278 | 0 | 0 | 0 | 7822329.2883 | 0 | 7822329.0105 | 0.27786 | 543457.3567 | 0 | 67069.4766 | 66711.4822 | 7249.4922 | 308697.8323 | 41139.7009 | 44813.6659 | 8904.638 | 24082.1711 | 22499.8021 | 982.0658 | 0 | 0 | 0 | 592150.3271 | 0 | 592150.3061 | 0.021034 | 41139.7219 | 0 | 3022.9994 | 3006.8636 | 326.7539 | 13913.831 | 1854.2756 | 2019.8709 | 401.3557 | 1085.4474 | 1014.1258 | 44.2643 | 0 | 0 | 0 | 26689.7875 | 0 | 26689.7866 | 0.00094805 | 1854.2765 | 6.0308 | 0.65536 | 27.9065 | 4.0512 | 0.80498 | 0.088779 | 6.0631 | 0 | 0 | 2.034 | 0 | 53.5307 | 53.5307 | 1.9015e-06
OK_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 1186316.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510740.7333 | 0 | 0 | 1697057.0752 | 0 | 1697057.0752 | 0 | 0 | 8585.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696.2307 | 0 | 0 | 12281.6021 | 0 | 12281.6021 | 0 | 0 | 1186.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510.7407 | 0 | 0 | 1697.0571 | 0 | 1697.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3794 | 1.0244 | 0 | 0 | 3.4037 | 3.4037 | 0
OK_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 824759.1698 | 716692.3758 | 95766.0793 | 4077910.5986 | 543384.8361 | 575588.424 | 111245.4743 | 286800.8744 | 297153.8138 | 12864.7637 | 0 | 0 | 0 | 7542166.4098 | 0 | 7542161.6862 | 4.7236 | 543389.5597 | 0 | 62434.2692 | 54253.6128 | 7249.4922 | 308697.8323 | 41134.2321 | 43572.0437 | 8421.2824 | 21710.8262 | 22494.5437 | 973.8626 | 0 | 0 | 0 | 570941.9972 | 0 | 570941.6396 | 0.35757 | 41134.5897 | 0 | 2814.0783 | 2445.3544 | 326.7539 | 13913.831 | 1854.0291 | 1963.9077 | 379.5696 | 978.5646 | 1013.8888 | 43.8946 | 0 | 0 | 0 | 25733.8718 | 0 | 25733.8557 | 0.016117 | 1854.0452 | 4.9046 | 0.65536 | 27.9065 | 3.9389 | 0.76129 | 0.088038 | 5.6441 | 0 | 0 | 2.0335 | 0 | 51.6135 | 51.6135 | 3.2325e-05
OK_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 711791.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510835.515 | 0 | 0 | 1222627.2158 | 0 | 1222627.2158 | 0 | 0 | 5151.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696.9166 | 0 | 0 | 8848.1532 | 0 | 8848.1532 | 0 | 0 | 711.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510.8355 | 0 | 0 | 1222.6272 | 0 | 1222.6272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4276 | 1.0246 | 0 | 0 | 2.4522 | 2.4522 | 0
OK_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 42128.628 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 24712.5721 | 0 | 0 | 0 | 0 | 102745.8388 | 0 | 0 | 347176.3498 | 0 | 347176.3498 | 0 | 0 | 0 | 3189.1371 | 2147.9665 | 545.8258 | 10749.7185 | 0 | 1870.7417 | 0 | 0 | 0 | 0 | 7777.86 | 0 | 0 | 26281.2497 | 0 | 26281.2497 | 0 | 0 | 0 | 143.7429 | 96.8146 | 24.6018 | 484.5184 | 0 | 84.3193 | 0 | 0 | 0 | 0 | 350.5688 | 0 | 0 | 1184.5657 | 0 | 1184.5657 | 0 | 0 | 2.8693 | 0.72914 | 14.3599 | 2.499 | 0 | 0 | 4.2602 | 0 | 10.39 | 0 | 0 | 35.1076 | 35.1076 | 0
OK_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 199960.9778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199960.9778 | 0 | 199960.9778 | 0 | 0 | 1447.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.1176 | 0 | 1447.1176 | 0 | 0 | 199.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.961 | 0 | 199.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9264 | 0 | 0 | 0 | 5.9264 | 5.9264 | 0
OK_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 39513.9968 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 23301.0602 | 0 | 0 | 0 | 0 | 102615.2461 | 0 | 0 | 337826.4729 | 0 | 337827.8622 | -1.3893 | -1.3893 | 0 | 2991.2096 | 1754.8457 | 545.8258 | 10749.7185 | 0 | 1763.8903 | 0 | 0 | 0 | 0 | 7767.9741 | 0 | 0 | 25573.464 | 0 | 25573.5692 | -0.10517 | -0.10517 | 0 | 134.8218 | 79.0956 | 24.6018 | 484.5184 | 0 | 79.5032 | 0 | 0 | 0 | 0 | 350.1232 | 0 | 0 | 1152.6639 | 0 | 1152.6687 | -0.0047402 | -0.0047402 | 2.3442 | 0.72914 | 14.3599 | 2.3563 | 0 | 0 | 3.9958 | 0 | 10.3768 | 0 | 0 | 34.1623 | 34.1621 | -0.00014049
OK_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 82374.7859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82374.7859 | 0 | 82374.7859 | 0 | 0 | 596.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596.1463 | 0 | 596.1463 | 0 | 0 | 82.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3748 | 0 | 82.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4414 | 0 | 0 | 0 | 2.4414 | 2.4414 | 0
OK_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 170265.0092 | 99753.3225 | 7118.6878 | 317887.4784 | 4818.0346 | 99278.1876 | 711.3131 | 0 | 0 | 21839.5341 | 7179.8163 | 17646.677 | 0 | 746498.0606 | 0 | 746497.227 | 0.83357 | 4818.8682 | 0 | 12889.0612 | 7551.3265 | 538.8847 | 24064.0821 | 364.7252 | 7515.3588 | 53.8464 | 0 | 0 | 1653.2527 | 543.5121 | 1335.8534 | 0 | 56509.9032 | 0 | 56509.8401 | 0.063101 | 364.7883 | 0 | 580.9442 | 340.3583 | 24.289 | 1084.6321 | 16.4391 | 338.7372 | 2.427 | 0 | 0 | 74.5165 | 24.4975 | 60.2105 | 0 | 2547.0514 | 0 | 2547.0485 | 0.0028441 | 16.442 | 4.602 | 0.32841 | 14.6653 | 4.5801 | 0.032815 | 1.0075 | 7.8549 | 0 | 0.33123 | 0 | 0.81411 | 34.4387 | 34.4387 | 3.8456e-05
OK_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 446289.1691 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 108098.5425 | 0 | 0 | 896578.1265 | 0 | 896578.1265 | 0 | 0 | 3229.7947 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 782.3092 | 0 | 0 | 6488.5359 | 0 | 6488.5359 | 0 | 0 | 446.2892 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0985 | 0 | 0 | 896.5781 | 0 | 896.5781 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.0343 | 1.4616 | 0 | 0 | 12.1226 | 12.1226 | 0
OK_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 149645.2658 | 80183.8773 | 7118.6878 | 312483.1662 | 4745.7919 | 85632.6466 | 525.1491 | 0 | 0 | 22956.5179 | 7179.8163 | 12495.2144 | 0 | 682966.1334 | 0 | 682967.2448 | -1.1114 | 4744.6805 | 0 | 11328.1466 | 6069.9195 | 538.8847 | 23654.9757 | 359.2564 | 6482.3913 | 39.7538 | 0 | 0 | 1737.8084 | 543.5121 | 945.8877 | 0 | 51700.5363 | 0 | 51700.6204 | -0.084135 | 359.1723 | 0 | 510.5896 | 273.5874 | 24.289 | 1066.1926 | 16.1926 | 292.1786 | 1.7918 | 0 | 0 | 78.3276 | 24.4975 | 42.6337 | 0 | 2330.2804 | 0 | 2330.2842 | -0.0037922 | 16.1888 | 3.6992 | 0.32841 | 14.416 | 3.9505 | 0.024227 | 1.0591 | 6.9037 | 0 | 0.33123 | 0 | 0.57645 | 31.5078 | 31.5077 | -5.1274e-05
OK_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 372492.1282 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 107795.2411 | 0 | 0 | 822477.7841 | 0 | 822477.7841 | 0 | 0 | 2695.7255 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 780.1142 | 0 | 0 | 5952.2717 | 0 | 5952.2717 | 0 | 0 | 372.4921 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7952 | 0 | 0 | 822.4778 | 0 | 822.4778 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.0365 | 1.4575 | 0 | 0 | 11.1207 | 11.1207 | 0
OK_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 58813.921 | 83657.0857 | 10683.5889 | 53987.5506 | 0 | 39105.5475 | 0 | 0 | 0 | 5643.2689 | 0 | 0 | 0 | 251890.9626 | 0 | 251889.8512 | 1.1114 | 1.1114 | 0 | 4452.2138 | 6332.8414 | 808.7477 | 4086.8576 | 0 | 2960.2899 | 0 | 0 | 0 | 427.1955 | 0 | 0 | 0 | 19068.1459 | 0 | 19068.0617 | 0.084135 | 0.084135 | 0 | 200.6731 | 285.438 | 36.4524 | 184.2055 | 0 | 133.4281 | 0 | 0 | 0 | 19.2548 | 0 | 0 | 0 | 859.452 | 0 | 859.4482 | 0.0037922 | 0.0037922 | 11.5599 | 1.4763 | 7.4601 | 5.4037 | 0 | 0.7798 | 8.127 | 0 | 0 | 0 | 0 | 34.8067 | 34.8069 | 0.00015358
OK_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 116050.7282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87113.8715 | 0 | 0 | 203164.5997 | 0 | 203164.5997 | 0 | 0 | 839.8591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630.4431 | 0 | 0 | 1470.3022 | 0 | 1470.3022 | 0 | 0 | 116.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1139 | 0 | 0 | 203.1646 | 0 | 203.1646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 3.528 | 0 | 0 | 8.228 | 8.228 | 0
OK_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 54810.0064 | 66088.2085 | 10683.5889 | 53987.5506 | 0 | 39936.3389 | 0 | 0 | 0 | 5790.533 | 0 | 0 | 0 | 231296.2263 | 0 | 231295.3928 | 0.83357 | 0.83357 | 0 | 4149.1175 | 5002.8774 | 808.7477 | 4086.8576 | 0 | 3023.1809 | 0 | 0 | 0 | 438.3433 | 0 | 0 | 0 | 17509.1243 | 0 | 17509.0612 | 0.063101 | 0.063101 | 0 | 187.0117 | 225.493 | 36.4524 | 184.2055 | 0 | 136.2628 | 0 | 0 | 0 | 19.7573 | 0 | 0 | 0 | 789.1827 | 0 | 789.1799 | 0.0028441 | 0.0028441 | 9.1322 | 1.4763 | 7.4601 | 5.5185 | 0 | 0.80015 | 7.5738 | 0 | 0 | 0 | 0 | 31.961 | 31.9611 | 0.00011518
OK_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 123879.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87123.3497 | 0 | 0 | 211003.0473 | 0 | 211003.0473 | 0 | 0 | 896.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630.5117 | 0 | 0 | 1527.0291 | 0 | 1527.0291 | 0 | 0 | 123.8797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1233 | 0 | 0 | 211.003 | 0 | 211.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.017 | 3.5284 | 0 | 0 | 8.5454 | 8.5454 | 0
OK_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 19850.0804 | 94888.0522 | 80228.3344 | 12314.6075 | 154949.5496 | 0 | 46985.5626 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 409288.4294 | 0 | 409284.8173 | 3.6121 | 3.6121 | 1502.6511 | 7183.0256 | 6073.2849 | 932.2158 | 11729.6809 | 0 | 3556.8071 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 30983.1341 | 0 | 30982.8607 | 0.27344 | 0.27344 | 67.7285 | 323.758 | 273.7391 | 42.0174 | 528.6879 | 0 | 160.3147 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1396.4921 | 0 | 1396.4798 | 0.012325 | 0.012325 | 6.3363 | 0.97258 | 12.2376 | 3.7108 | 0.0057056 | 0 | 7.4941 | 1.5677 | 0 | 0 | 0 | 32.3244 | 32.3247 | 0.00028528
OK_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 38822.5892 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 527024.2314 | 0 | 0 | 965342.2585 | 0 | 965342.2585 | 0 | 0 | 280.9591 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3814.0744 | 0 | 0 | 6986.1819 | 0 | 6986.1819 | 0 | 0 | 38.8226 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 527.0242 | 0 | 0 | 965.3423 | 0 | 965.3423 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.89863 | 12.1991 | 0 | 0 | 22.3449 | 22.3449 | 0
OK_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 21972.9053 | 89375.3759 | 51378.4765 | 12314.6075 | 154949.5496 | 0 | 44532.0882 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 374595.2459 | 0 | 374594.4123 | 0.83357 | 0.83357 | 1663.3489 | 6765.716 | 3889.3507 | 932.2158 | 11729.6809 | 0 | 3371.0791 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 28356.8601 | 0 | 28356.797 | 0.063101 | 0.063101 | 74.9716 | 304.9488 | 175.3034 | 42.0174 | 528.6879 | 0 | 151.9435 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1278.119 | 0 | 1278.1161 | 0.0028441 | 0.0028441 | 4.0578 | 0.97258 | 12.2376 | 3.517 | 0.0057056 | 0 | 7.0587 | 1.7354 | 0 | 0 | 0 | 29.5847 | 29.5847 | 6.5834e-05
OK_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 39448.1485 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 527081.1004 | 0 | 0 | 966024.6869 | 0 | 966024.6869 | 0 | 0 | 285.4863 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3814.4859 | 0 | 0 | 6991.1207 | 0 | 6991.1207 | 0 | 0 | 39.4481 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 527.0811 | 0 | 0 | 966.0247 | 0 | 966.0247 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.91311 | 12.2004 | 0 | 0 | 22.3606 | 22.3606 | 0
OK_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 2422.9101 | 6240.6608 | 9022.006 | 1589.3401 | 13417.6985 | 0 | 5537.6834 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43234.4976 | 0 | 43235.0533 | -0.55571 | -0.55571 | 183.4143 | 472.418 | 682.9659 | 120.313 | 1015.7198 | 0 | 419.2026 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 3272.8515 | 0 | 3272.8935 | -0.042067 | -0.042067 | 8.267 | 21.2931 | 30.7831 | 5.4228 | 45.7812 | 0 | 18.8946 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 147.5161 | 0 | 147.518 | -0.0018961 | -0.0018961 | 5.5949 | 0.98561 | 8.3208 | 3.4341 | 0 | 0 | 3.8701 | 1.5025 | 3.1033 | 0 | 0 | 26.8117 | 26.8114 | -0.00034462
OK_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 5099.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5099.2561 | 0 | 5099.2561 | 0 | 0 | 36.9033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9033 | 0 | 36.9033 | 0 | 0 | 5.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0993 | 0 | 5.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9268 | 0 | 0 | 0 | 0.9268 | 0.9268 | 0
OK_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 2459.0315 | 5940.5756 | 7243.7233 | 1589.3401 | 13417.6985 | 0 | 5098.6699 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40753.2375 | 0 | 40754.349 | -1.1114 | -1.1114 | 186.1487 | 449.7016 | 548.3499 | 120.313 | 1015.7198 | 0 | 385.9693 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 3085.0201 | 0 | 3085.1042 | -0.084135 | -0.084135 | 8.3902 | 20.2692 | 24.7156 | 5.4228 | 45.7812 | 0 | 17.3967 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.05 | 0 | 139.0538 | -0.0037922 | -0.0037922 | 4.4921 | 0.98561 | 8.3208 | 3.1619 | 0 | 0 | 3.684 | 1.5249 | 3.1033 | 0 | 0 | 25.2733 | 25.2726 | -0.00068924
OK_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | OK-OKLAHOMA-OK | Zone3A | Zone3A(OK-OKLAHOMA-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 5241.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5241.4287 | 0 | 5241.4287 | 0 | 0 | 37.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9322 | 0 | 37.9322 | 0 | 0 | 5.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2414 | 0 | 5.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95264 | 0 | 0 | 0 | 0.95264 | 0.95264 | 0
OK_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 943103.8819 | 879466.3692 | 95777.1935 | 4077910.5986 | 543457.0788 | 621729.3023 | 119556.1672 | 325925.8718 | 304978.2576 | 14701.3963 | 0 | 0 | 0 | 7926606.1174 | 0 | 7926601.1159 | 5.0014 | 543462.0803 | 0 | 71392.9639 | 66575.6041 | 7250.3336 | 308697.8323 | 41139.7009 | 47064.9082 | 9050.4019 | 24672.5885 | 23086.8541 | 1112.8957 | 0 | 0 | 0 | 600044.0831 | 0 | 600043.7045 | 0.37861 | 41140.0795 | 0 | 3217.8704 | 3000.7393 | 326.7918 | 13913.831 | 1854.2756 | 2121.3404 | 407.9256 | 1112.0591 | 1040.5858 | 50.1612 | 0 | 0 | 0 | 27045.5801 | 0 | 27045.563 | 0.017065 | 1854.2926 | 6.0185 | 0.65543 | 27.9065 | 4.2547 | 0.81816 | 0.10061 | 6.454 | 0 | 0 | 2.0871 | 0 | 54.2443 | 54.2443 | 3.4226e-05
OK_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 501992.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506361.8182 | 0 | 0 | 1008354.1995 | 0 | 1008354.1995 | 0 | 0 | 3632.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3664.5405 | 0 | 0 | 7297.4593 | 0 | 7297.4593 | 0 | 0 | 501.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506.3618 | 0 | 0 | 1008.3542 | 0 | 1008.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0068 | 1.0156 | 0 | 0 | 2.0224 | 2.0224 | 0
OK_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 887729.8265 | 716006.0698 | 95777.1935 | 4077910.5986 | 543384.8361 | 595605.2183 | 115869.0092 | 294016.8121 | 304767.0866 | 12923.1136 | 0 | 0 | 0 | 7643989.7644 | 0 | 7643989.7644 | 0 | 543384.8361 | 0 | 67201.1479 | 54201.6595 | 7250.3336 | 308697.8323 | 41134.2321 | 45087.315 | 8771.284 | 22257.0727 | 23070.8685 | 978.2797 | 0 | 0 | 0 | 578650.0252 | 0 | 578650.0252 | 0 | 41134.2321 | 0 | 3028.9342 | 2443.0127 | 326.7918 | 13913.831 | 1854.0291 | 2032.205 | 395.3451 | 1003.1854 | 1039.8653 | 44.0937 | 0 | 0 | 0 | 26081.2931 | 0 | 26081.2931 | 0 | 1854.0291 | 4.8999 | 0.65543 | 27.9065 | 4.0759 | 0.79293 | 0.088437 | 6.075 | 0 | 0 | 2.0856 | 0 | 52.3103 | 52.3103 | 0
OK_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 438422.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506447.1217 | 0 | 0 | 944869.4088 | 0 | 944869.4088 | 0 | 0 | 3172.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3665.1578 | 0 | 0 | 6838.0199 | 0 | 6838.0199 | 0 | 0 | 438.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506.4471 | 0 | 0 | 944.8694 | 0 | 944.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87933 | 1.0158 | 0 | 0 | 1.8951 | 1.8951 | 0
OK_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 49161.1803 | 28374.723 | 7207.602 | 142004.2074 | 0 | 25462.7851 | 0 | 0 | 0 | 0 | 101726.1048 | 0 | 0 | 353936.6026 | 0 | 353938.2697 | -1.6671 | -1.6671 | 0 | 3721.5013 | 2147.9665 | 545.6155 | 10749.7185 | 0 | 1927.5328 | 0 | 0 | 0 | 0 | 7700.6661 | 0 | 0 | 26793.0008 | 0 | 26793.127 | -0.1262 | -0.1262 | 0 | 167.7379 | 96.8146 | 24.5923 | 484.5184 | 0 | 86.879 | 0 | 0 | 0 | 0 | 347.0895 | 0 | 0 | 1207.6317 | 0 | 1207.6374 | -0.0056883 | -0.0056883 | 2.8693 | 0.72886 | 14.3599 | 2.5749 | 0 | 0 | 4.9713 | 0 | 10.2869 | 0 | 0 | 35.7914 | 35.7912 | -0.00016859
OK_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 49495.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49495.01 | 0 | 49495.01 | 0 | 0 | 358.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358.1954 | 0 | 358.1954 | 0 | 0 | 49.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.495 | 0 | 49.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4669 | 0 | 0 | 0 | 1.4669 | 1.4669 | 0
OK_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 48430.4173 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 25004.3216 | 0 | 0 | 0 | 0 | 101753.8905 | 0 | 0 | 347582.0206 | 0 | 347582.8541 | -0.83357 | -0.83357 | 0 | 3666.1826 | 1754.8457 | 545.6155 | 10749.7185 | 0 | 1892.8271 | 0 | 0 | 0 | 0 | 7702.7695 | 0 | 0 | 26311.959 | 0 | 26312.0221 | -0.063101 | -0.063101 | 0 | 165.2446 | 79.0956 | 24.5923 | 484.5184 | 0 | 85.3147 | 0 | 0 | 0 | 0 | 347.1843 | 0 | 0 | 1185.9499 | 0 | 1185.9527 | -0.0028441 | -0.0028441 | 2.3442 | 0.72886 | 14.3599 | 2.5285 | 0 | 0 | 4.8974 | 0 | 10.2897 | 0 | 0 | 35.1487 | 35.1486 | -8.4293e-05
OK_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 56451.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56451.9877 | 0 | 56451.9877 | 0 | 0 | 408.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408.543 | 0 | 408.543 | 0 | 0 | 56.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.452 | 0 | 56.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6731 | 0 | 0 | 0 | 1.6731 | 1.6731 | 0
OK_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 185294.2763 | 96566.3065 | 7115.9093 | 317887.4784 | 4818.0346 | 105227.0988 | 486.2492 | 0 | 0 | 19163.7744 | 7179.8163 | 17641.1199 | 0 | 761380.0637 | 0 | 761382.5644 | -2.5007 | 4815.5339 | 0 | 14026.7767 | 7310.0694 | 538.6743 | 24064.0821 | 364.7252 | 7965.6914 | 36.8091 | 0 | 0 | 1450.6977 | 543.5121 | 1335.4328 | 0 | 57636.4708 | 0 | 57636.6601 | -0.1893 | 364.5359 | 0 | 632.2241 | 329.4842 | 24.2795 | 1084.6321 | 16.4391 | 359.0349 | 1.6591 | 0 | 0 | 65.3868 | 24.4975 | 60.1915 | 0 | 2597.8288 | 0 | 2597.8373 | -0.0085324 | 16.4306 | 4.455 | 0.32828 | 14.6653 | 4.8545 | 0.022432 | 0.8841 | 8.5483 | 0 | 0.33123 | 0 | 0.81385 | 35.1254 | 35.1253 | -0.00011537
OK_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 199742.9799 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 107236.029 | 0 | 0 | 649169.4237 | 0 | 649169.4237 | 0 | 0 | 1445.5399 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 776.0671 | 0 | 0 | 4698.0391 | 0 | 4698.0391 | 0 | 0 | 199.743 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 107.236 | 0 | 0 | 649.1694 | 0 | 649.1694 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.7007 | 1.4499 | 0 | 0 | 8.7774 | 8.7774 | 0
OK_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 171807.1137 | 78277.7806 | 7115.9093 | 312483.1662 | 4743.0133 | 89511.5257 | 361.2137 | 0 | 0 | 22884.2752 | 7179.8163 | 12500.7715 | 0 | 706864.5854 | 0 | 706867.6419 | -3.0564 | 4739.9569 | 0 | 13005.7985 | 5925.628 | 538.6743 | 23654.9757 | 359.0461 | 6776.0225 | 27.3439 | 0 | 0 | 1732.3396 | 543.5121 | 946.3084 | 0 | 53509.6491 | 0 | 53509.8805 | -0.23137 | 358.8147 | 0 | 586.2059 | 267.0838 | 24.2795 | 1066.1926 | 16.1832 | 305.4133 | 1.2325 | 0 | 0 | 78.0811 | 24.4975 | 42.6526 | 0 | 2411.822 | 0 | 2411.8324 | -0.010429 | 16.1727 | 3.6112 | 0.32828 | 14.416 | 4.1295 | 0.016664 | 1.0557 | 7.9261 | 0 | 0.33123 | 0 | 0.57671 | 32.6104 | 32.6103 | -0.000141
OK_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 181469.0658 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 107046.4655 | 0 | 0 | 630705.9462 | 0 | 630705.9462 | 0 | 0 | 1313.2916 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 774.6953 | 0 | 0 | 4564.4189 | 0 | 4564.4189 | 0 | 0 | 181.4691 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0465 | 0 | 0 | 630.7059 | 0 | 630.7059 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.4536 | 1.4474 | 0 | 0 | 8.5278 | 8.5278 | 0
OK_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 66763.4002 | 84543.4484 | 10680.8103 | 53987.5506 | 0 | 39925.2247 | 0 | 0 | 0 | 5659.9403 | 0 | 0 | 0 | 261560.3746 | 0 | 261558.7075 | 1.6671 | 1.6671 | 0 | 5053.9894 | 6399.939 | 808.5373 | 4086.8576 | 0 | 3022.3395 | 0 | 0 | 0 | 428.4575 | 0 | 0 | 0 | 19800.1204 | 0 | 19799.9942 | 0.1262 | 0.1262 | 0 | 227.7967 | 288.4622 | 36.4429 | 184.2055 | 0 | 136.2249 | 0 | 0 | 0 | 19.3117 | 0 | 0 | 0 | 892.444 | 0 | 892.4383 | 0.0056883 | 0.0056883 | 11.6824 | 1.4759 | 7.4601 | 5.517 | 0 | 0.7821 | 9.2255 | 0 | 0 | 0 | 0 | 36.1428 | 36.143 | 0.00023037
OK_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 85000.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86839.0045 | 0 | 0 | 171839.2439 | 0 | 171839.2439 | 0 | 0 | 615.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628.4539 | 0 | 0 | 1243.6006 | 0 | 1243.6006 | 0 | 0 | 85.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.839 | 0 | 0 | 171.8392 | 0 | 171.8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4424 | 3.5169 | 0 | 0 | 6.9593 | 6.9593 | 0
OK_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 63156.8207 | 66799.5216 | 10680.8103 | 53987.5506 | 0 | 37841.2996 | 0 | 0 | 0 | 5768.3044 | 0 | 0 | 0 | 238234.3073 | 0 | 238230.6952 | 3.6121 | 3.6121 | 0 | 4780.9713 | 5056.7238 | 808.5373 | 4086.8576 | 0 | 2864.5864 | 0 | 0 | 0 | 436.6606 | 0 | 0 | 0 | 18034.3371 | 0 | 18034.0636 | 0.27344 | 0.27344 | 0 | 215.4911 | 227.92 | 36.4429 | 184.2055 | 0 | 129.1145 | 0 | 0 | 0 | 19.6815 | 0 | 0 | 0 | 812.8555 | 0 | 812.8431 | 0.012325 | 0.012325 | 9.2305 | 1.4759 | 7.4601 | 5.229 | 0 | 0.79708 | 8.7272 | 0 | 0 | 0 | 0 | 32.9193 | 32.9198 | 0.00049913
OK_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 93767.5477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86848.4827 | 0 | 0 | 180616.0304 | 0 | 180616.0304 | 0 | 0 | 678.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628.5225 | 0 | 0 | 1307.1182 | 0 | 1307.1182 | 0 | 0 | 93.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8485 | 0 | 0 | 180.616 | 0 | 180.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 3.5173 | 0 | 0 | 7.3148 | 7.3148 | 0
OK_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 14348.5183 | 105474.3913 | 79316.9645 | 12311.829 | 154949.5496 | 0 | 47266.1978 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 413739.6933 | 0 | 413740.5268 | -0.83357 | -0.83357 | 1086.1828 | 7984.4114 | 6004.2942 | 932.0055 | 11729.6809 | 0 | 3578.0512 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 31320.0948 | 0 | 31320.1579 | -0.063101 | -0.063101 | 48.9571 | 359.8786 | 270.6295 | 42.008 | 528.6879 | 0 | 161.2723 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1411.6798 | 0 | 1411.6827 | -0.0028441 | -0.0028441 | 6.2643 | 0.97236 | 12.2376 | 3.733 | 0.0057056 | 0 | 8.3301 | 1.1332 | 0 | 0 | 0 | 32.6763 | 32.6763 | -6.5834e-05
OK_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 35486.273 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 522218.7986 | 0 | 0 | 957200.5095 | 0 | 957200.5095 | 0 | 0 | 256.8142 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.2974 | 0 | 0 | 6927.2601 | 0 | 6927.2601 | 0 | 0 | 35.4863 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 522.2188 | 0 | 0 | 957.2005 | 0 | 957.2005 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.8214 | 12.0878 | 0 | 0 | 22.1564 | 22.1564 | 0
OK_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 16885.3497 | 99664.4083 | 50869.9988 | 12311.829 | 154949.5496 | 0 | 44876.6305 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 379630.0087 | 0 | 379629.1751 | 0.83357 | 0.83357 | 1278.221 | 7544.5957 | 3850.8589 | 932.0055 | 11729.6809 | 0 | 3397.1609 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 28737.9917 | 0 | 28737.9286 | 0.063101 | 0.063101 | 57.6128 | 340.055 | 173.5684 | 42.008 | 528.6879 | 0 | 153.1191 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.2976 | 0 | 1295.2947 | 0.0028441 | 0.0028441 | 4.0176 | 0.97236 | 12.2376 | 3.5443 | 0.0057056 | 0 | 7.8713 | 1.3336 | 0 | 0 | 0 | 29.9823 | 29.9824 | 6.5834e-05
OK_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 36557.3063 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 522285.1458 | 0 | 0 | 958337.89 | 0 | 958337.89 | 0 | 0 | 264.5652 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.7776 | 0 | 0 | 6935.4913 | 0 | 6935.4913 | 0 | 0 | 36.5573 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 522.2851 | 0 | 0 | 958.3379 | 0 | 958.3379 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.84619 | 12.0894 | 0 | 0 | 22.1827 | 22.1827 | 0
OK_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 1711.5971 | 7354.866 | 8846.9563 | 1589.3401 | 13417.6985 | 0 | 5437.655 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43362.3116 | 0 | 43365.9238 | -3.6121 | -3.6121 | 129.5679 | 556.7634 | 669.7146 | 120.313 | 1015.7198 | 0 | 411.6305 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 3282.527 | 0 | 3282.8004 | -0.27344 | -0.27344 | 5.84 | 25.0948 | 30.1858 | 5.4228 | 45.7812 | 0 | 18.5533 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 147.9522 | 0 | 147.9645 | -0.012325 | -0.012325 | 5.4863 | 0.98561 | 8.3208 | 3.3721 | 0 | 0 | 4.561 | 1.0614 | 3.1033 | 0 | 0 | 26.8929 | 26.8906 | -0.00224
OK_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 1298.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.5095 | 0 | 1298.5095 | 0 | 0 | 9.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3973 | 0 | 9.3973 | 0 | 0 | 1.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2985 | 0 | 1.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23601 | 0 | 0 | 0 | 0.23601 | 0.23601 | 0
OK_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 1758.8327 | 7026.9951 | 7127.0235 | 1589.3401 | 13417.6985 | 0 | 5015.3129 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40939.4015 | 0 | 40938.8458 | 0.55571 | 0.55571 | 133.1436 | 531.9435 | 539.5157 | 120.313 | 1015.7198 | 0 | 379.6592 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 3099.1127 | 0 | 3099.0706 | 0.042067 | 0.042067 | 6.0011 | 23.9761 | 24.3174 | 5.4228 | 45.7812 | 0 | 17.1122 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.6852 | 0 | 139.6833 | 0.0018961 | 0.0018961 | 4.4197 | 0.98561 | 8.3208 | 3.1102 | 0 | 0 | 4.3577 | 1.0907 | 3.1033 | 0 | 0 | 25.3877 | 25.3881 | 0.00034462
OK_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | OK-PONCACITY-OK | Zone4A | Zone4A(OK-PONCACITY-OK) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 1383.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1383.813 | 0 | 1383.813 | 0 | 0 | 10.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0147 | 0 | 10.0147 | 0 | 0 | 1.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3838 | 0 | 1.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25151 | 0 | 0 | 0 | 0.25151 | 0.25151 | 0
OK_4B_LO_2016_EL | 4B | LO | EL |  |  | OfficeLarge | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 792302.7323 | 878399.3996 | 96460.7209 | 4077910.5986 | 543457.0788 | 667372.8172 | 102142.8898 | 254597.2865 | 450780.7657 | 0 | 0 | 0 | 0 | 7863424.2896 | 0 | 7863425.401 | -1.1114 | 543455.9674 | 0 | 59977.3168 | 66494.8345 | 7302.0766 | 308697.8323 | 41139.7009 | 50520.1223 | 7732.2168 | 19273.0146 | 34124.104 | 0 | 0 | 0 | 0 | 595261.2187 | 0 | 595261.3029 | -0.084135 | 41139.6167 | 0 | 2703.3369 | 2997.0988 | 329.124 | 13913.831 | 1854.2756 | 2277.0761 | 348.5115 | 868.6859 | 1538.064 | 0 | 0 | 0 | 0 | 26830.0037 | 0 | 26830.0075 | -0.0037922 | 1854.2718 | 6.0112 | 0.66011 | 27.9065 | 4.567 | 0.699 | 0 | 5.422 | 0 | 0 | 3.0848 | 0 | 53.812 | 53.812 | -7.6059e-06
OK_4B_LO_2016_NG | 4B | LO | NG |  |  | OfficeLarge | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 998913.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532692.1778 | 0 | 0 | 1531606.1187 | 0 | 1531606.1187 | 0 | 0 | 7229.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3855.0933 | 0 | 0 | 11084.2335 | 0 | 11084.2335 | 0 | 0 | 998.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.6922 | 0 | 0 | 1531.6061 | 0 | 1531.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0035 | 1.0684 | 0 | 0 | 3.0719 | 3.0719 | 0
OK_4B_LO_2019_EL | 4B | LO | EL |  |  | OfficeLarge | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 745467.2123 | 715278.0853 | 96460.7209 | 4077910.5986 | 543384.8361 | 642749.1592 | 98586.3245 | 228073.089 | 450411.2163 | 0 | 0 | 0 | 0 | 7598321.2424 | 0 | 7598320.4088 | 0.83357 | 543385.6697 | 0 | 56431.868 | 54146.5511 | 7302.0766 | 308697.8323 | 41134.2321 | 48656.1114 | 7462.9848 | 17265.1328 | 34096.1291 | 0 | 0 | 0 | 0 | 575192.9181 | 0 | 575192.8549 | 0.063101 | 41134.2952 | 0 | 2543.5341 | 2440.5288 | 329.124 | 13913.831 | 1854.0291 | 2193.0601 | 336.3765 | 778.1854 | 1536.8031 | 0 | 0 | 0 | 0 | 25925.4721 | 0 | 25925.4692 | 0.0028441 | 1854.0319 | 4.8949 | 0.66011 | 27.9065 | 4.3985 | 0.67466 | 0 | 5.1015 | 0 | 0 | 3.0823 | 0 | 51.9978 | 51.9978 | 5.7044e-06
OK_4B_LO_2019_NG | 4B | LO | NG |  |  | OfficeLarge | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 1531037.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532692.1778 | 0 | 0 | 2063729.6062 | 0 | 2063729.6062 | 0 | 0 | 11080.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3855.0933 | 0 | 0 | 14935.2112 | 0 | 14935.2112 | 0 | 0 | 1531.0374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.6922 | 0 | 0 | 2063.7296 | 0 | 2063.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0707 | 1.0684 | 0 | 0 | 4.1391 | 4.1391 | 0
OK_4B_MA_2016_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 33195.5362 | 28374.723 | 7207.602 | 142004.2074 | 0 | 24306.9013 | 0 | 0 | 0 | 0 | 107058.1743 | 0 | 0 | 342147.1441 | 0 | 342147.6998 | -0.55571 | -0.55571 | 0 | 2512.9021 | 2147.9665 | 545.6155 | 10749.7185 | 0 | 1840.0324 | 0 | 0 | 0 | 0 | 8104.3038 | 0 | 0 | 25900.5388 | 0 | 25900.5809 | -0.042067 | -0.042067 | 0 | 113.2632 | 96.8146 | 24.5923 | 484.5184 | 0 | 82.9351 | 0 | 0 | 0 | 0 | 365.2825 | 0 | 0 | 1167.4061 | 0 | 1167.408 | -0.0018961 | -0.0018961 | 2.8693 | 0.72886 | 14.3599 | 2.458 | 0 | 0 | 3.3568 | 0 | 10.8261 | 0 | 0 | 34.5991 | 34.599 | -5.6196e-05
OK_4B_MA_2016_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 132779.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132779.7003 | 0 | 132779.7003 | 0 | 0 | 960.9267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960.9267 | 0 | 960.9267 | 0 | 0 | 132.7797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.7797 | 0 | 132.7797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9353 | 0 | 0 | 0 | 3.9353 | 3.9353 | 0
OK_4B_MA_2019_EL | 4B | MA | EL |  |  | ApartmentMidRise | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 33979.092 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 24029.0447 | 0 | 0 | 0 | 0 | 106941.4745 | 0 | 0 | 337343.0023 | 0 | 337346.3366 | -3.3343 | -3.3343 | 0 | 2572.2173 | 1754.8457 | 545.6155 | 10749.7185 | 0 | 1818.9987 | 0 | 0 | 0 | 0 | 8095.4696 | 0 | 0 | 25536.8653 | 0 | 25537.1177 | -0.2524 | -0.2524 | 0 | 115.9367 | 79.0956 | 24.5923 | 484.5184 | 0 | 81.9871 | 0 | 0 | 0 | 0 | 364.8843 | 0 | 0 | 1151.0143 | 0 | 1151.0257 | -0.011377 | -0.011377 | 2.3442 | 0.72886 | 14.3599 | 2.4299 | 0 | 0 | 3.4361 | 0 | 10.8143 | 0 | 0 | 34.1136 | 34.1132 | -0.00033717
OK_4B_MA_2019_NG | 4B | MA | NG |  |  | ApartmentMidRise | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 62489.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62489.5827 | 0 | 62489.5827 | 0 | 0 | 452.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.2371 | 0 | 452.2371 | 0 | 0 | 62.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4896 | 0 | 62.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.852 | 0 | 0 | 0 | 1.852 | 1.852 | 0
OK_4B_PS_2016_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 138911.6627 | 95482.6655 | 7138.1378 | 317887.4784 | 4818.0346 | 104310.1718 | 558.4919 | 0 | 0 | 0 | 7179.8163 | 17535.5343 | 0 | 693821.9934 | 0 | 693823.1049 | -1.1114 | 4816.9232 | 0 | 10515.6129 | 7228.0378 | 540.357 | 24064.0821 | 364.7252 | 7896.28 | 42.2778 | 0 | 0 | 0 | 543.5121 | 1327.4399 | 0 | 52522.3249 | 0 | 52522.409 | -0.084135 | 364.6411 | 0 | 473.9666 | 325.7869 | 24.3553 | 1084.6321 | 16.4391 | 355.9063 | 1.9056 | 0 | 0 | 0 | 24.4975 | 59.8312 | 0 | 2367.3206 | 0 | 2367.3244 | -0.0037922 | 16.4353 | 4.405 | 0.32931 | 14.6653 | 4.8122 | 0.025765 | 0 | 6.4085 | 0 | 0.33123 | 0 | 0.80898 | 32.0086 | 32.0086 | -5.1274e-05
OK_4B_PS_2016_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 350351.1202 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111463.2933 | 0 | 0 | 804004.8284 | 0 | 804004.8284 | 0 | 0 | 2535.4911 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 806.6599 | 0 | 0 | 5818.5829 | 0 | 5818.5829 | 0 | 0 | 350.3511 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.4633 | 0 | 0 | 804.0048 | 0 | 804.0048 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.7371 | 1.5071 | 0 | 0 | 10.871 | 10.871 | 0
OK_4B_PS_2019_EL | 4B | PS | EL |  |  | SchoolPrimary | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 139559.0688 | 77152.4611 | 7138.1378 | 312483.1662 | 4743.0133 | 85879.939 | 903.0342 | 0 | 0 | 0 | 7179.8163 | 12453.5359 | 0 | 647492.1726 | 0 | 647495.7847 | -3.6121 | 4739.4012 | 0 | 10564.6215 | 5840.4413 | 540.357 | 23654.9757 | 359.0461 | 6501.1114 | 68.3597 | 0 | 0 | 0 | 543.5121 | 942.7327 | 0 | 49015.1575 | 0 | 49015.4309 | -0.27344 | 358.7727 | 0 | 476.1755 | 263.2442 | 24.3553 | 1066.1926 | 16.1832 | 293.0224 | 3.0812 | 0 | 0 | 0 | 24.4975 | 42.4915 | 0 | 2209.2433 | 0 | 2209.2556 | -0.012325 | 16.1708 | 3.5593 | 0.32931 | 14.416 | 3.962 | 0.04166 | 0 | 6.4384 | 0 | 0.33123 | 0 | 0.57453 | 29.8714 | 29.8712 | -0.00016664
OK_4B_PS_2019_NG | 4B | PS | NG |  |  | SchoolPrimary | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 540464.2782 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 111387.4679 | 0 | 0 | 994042.1609 | 0 | 994042.1609 | 0 | 0 | 3911.34 | 0 | 0 | 0 | 2476.432 | 0 | 0 | 0 | 0 | 0 | 0 | 806.1111 | 0 | 0 | 7193.8831 | 0 | 7193.8831 | 0 | 0 | 540.4643 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3875 | 0 | 0 | 994.0422 | 0 | 994.0422 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.3076 | 1.5061 | 0 | 0 | 13.4404 | 13.4404 | 0
OK_4B_RS_2016_EL | 4B | RS | EL |  |  | RetailStandalone | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 47496.8189 | 84785.1837 | 10678.0318 | 53987.5506 | 0 | 45285.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242232.6648 | 0 | 242232.3869 | 0.27786 | 0.27786 | 0 | 3595.5092 | 6418.2384 | 808.327 | 4086.8576 | 0 | 3428.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18337.0127 | 0 | 18336.9917 | 0.021034 | 0.021034 | 0 | 162.0591 | 289.287 | 36.4334 | 184.2055 | 0 | 154.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826.4979 | 0 | 826.4969 | 0.00094805 | 0.00094805 | 11.7158 | 1.4755 | 7.4601 | 6.2576 | 0 | 0 | 6.5632 | 0 | 0 | 0 | 0 | 33.4723 | 33.4723 | 3.8395e-05
OK_4B_RS_2016_NG | 4B | RS | NG |  |  | RetailStandalone | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 178455.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88431.3373 | 0 | 0 | 266886.3446 | 0 | 266886.3446 | 0 | 0 | 1291.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 639.9776 | 0 | 0 | 1931.4565 | 0 | 1931.4565 | 0 | 0 | 178.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4313 | 0 | 0 | 266.8863 | 0 | 266.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2272 | 3.5814 | 0 | 0 | 10.8086 | 10.8086 | 0
OK_4B_RS_2019_EL | 4B | RS | EL |  |  | RetailStandalone | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 0 | 44757.1521 | 66871.7643 | 10678.0318 | 53987.5506 | 0 | 43048.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219342.8325 | 0 | 219342.5546 | 0.27786 | 0.27786 | 0 | 3388.1164 | 5062.1926 | 808.327 | 4086.8576 | 0 | 3258.7589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16604.2524 | 0 | 16604.2314 | 0.021034 | 0.021034 | 0 | 152.7114 | 228.1665 | 36.4334 | 184.2055 | 0 | 146.8809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.3977 | 0 | 748.3968 | 0.00094805 | 0.00094805 | 9.2405 | 1.4755 | 7.4601 | 5.9485 | 0 | 0 | 6.1847 | 0 | 0 | 0 | 0 | 30.3093 | 30.3093 | 3.8395e-05
OK_4B_RS_2019_NG | 4B | RS | NG |  |  | RetailStandalone | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 197847.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88440.8155 | 0 | 0 | 286288.1611 | 0 | 286288.1611 | 0 | 0 | 1431.8212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.0462 | 0 | 0 | 2071.8674 | 0 | 2071.8674 | 0 | 0 | 197.8473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4408 | 0 | 0 | 286.2882 | 0 | 286.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0126 | 3.5818 | 0 | 0 | 11.5944 | 11.5944 | 0
OK_4B_SH_2016_EL | 4B | SH | EL |  |  | HotelSmall | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 14092.8902 | 81517.5893 | 79330.8573 | 12309.0504 | 154949.5496 | 0 | 47871.9254 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 390144.105 | 0 | 390140.7707 | 3.3343 | 3.3343 | 1066.8318 | 6170.8815 | 6005.3459 | 931.7951 | 11729.6809 | 0 | 3623.9048 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 29533.9087 | 0 | 29533.6563 | 0.2524 | 0.2524 | 48.0849 | 278.138 | 270.6769 | 41.9985 | 528.6879 | 0 | 163.339 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1331.1717 | 0 | 1331.1603 | 0.011377 | 0.011377 | 6.2654 | 0.97214 | 12.2376 | 3.7808 | 0.0057056 | 0 | 6.4381 | 1.113 | 0 | 0 | 0 | 30.8125 | 30.8127 | 0.00026333
OK_4B_SH_2016_NG | 4B | SH | NG |  |  | HotelSmall | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 32367.9546 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 552027.647 | 0 | 0 | 983891.0396 | 0 | 983891.0396 | 0 | 0 | 234.2469 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.0241 | 0 | 0 | 7120.4195 | 0 | 7120.4195 | 0 | 0 | 32.368 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 552.0276 | 0 | 0 | 983.891 | 0 | 983.891 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.74922 | 12.7778 | 0 | 0 | 22.7742 | 22.7742 | 0
OK_4B_SH_2019_EL | 4B | SH | EL |  |  | HotelSmall | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 16849.2284 | 76149.3985 | 50875.556 | 12309.0504 | 154949.5496 | 0 | 45265.6298 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 356470.6554 | 0 | 356471.7668 | -1.1114 | -1.1114 | 1275.4866 | 5764.5095 | 3851.2796 | 931.7951 | 11729.6809 | 0 | 3426.6082 | 5.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 26984.8286 | 0 | 26984.9127 | -0.084135 | -0.084135 | 57.4896 | 259.8217 | 173.5874 | 41.9985 | 528.6879 | 0 | 154.4463 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.2779 | 0 | 1216.2817 | -0.0037922 | -0.0037922 | 4.018 | 0.97214 | 12.2376 | 3.575 | 0.0057056 | 0 | 6.0141 | 1.3307 | 0 | 0 | 0 | 28.1534 | 28.1533 | -8.7778e-05
OK_4B_SH_2019_NG | 4B | SH | NG |  |  | HotelSmall | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 34282.5452 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 552084.5161 | 0 | 0 | 985862.4992 | 0 | 985862.4992 | 0 | 0 | 248.1028 | 0 | 0 | 0 | 2891.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.4356 | 0 | 0 | 7134.6869 | 0 | 7134.6869 | 0 | 0 | 34.2825 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 552.0845 | 0 | 0 | 985.8625 | 0 | 985.8625 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.79354 | 12.7791 | 0 | 0 | 22.8198 | 22.8198 | 0
OK_4B_SO_2016_EL | 4B | SO | EL |  |  | OfficeSmall | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 1650.4686 | 5268.1624 | 8830.2849 | 1600.4544 | 13417.6985 | 0 | 5715.5117 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41486.7791 | 0 | 41489.002 | -2.2229 | -2.2229 | 124.9405 | 398.7999 | 668.4526 | 121.1544 | 1015.7198 | 0 | 432.6642 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 3140.5492 | 0 | 3140.7175 | -0.16827 | -0.16827 | 5.6314 | 17.975 | 30.1289 | 5.4608 | 45.7812 | 0 | 19.5013 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.5529 | 0 | 141.5605 | -0.0075844 | -0.0075844 | 5.476 | 0.9925 | 8.3208 | 3.5444 | 0 | 0 | 3.267 | 1.0235 | 3.1033 | 0 | 0 | 25.7289 | 25.7275 | -0.0013785
OK_4B_SO_2016_NG | 4B | SO | NG |  |  | OfficeSmall | STD2016 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 985.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 985.7298 | 0 | 985.7298 | 0 | 0 | 7.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1337 | 0 | 7.1337 | 0 | 0 | 0.98573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98573 | 0 | 0.98573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17916 | 0 | 0 | 0 | 0.17916 | 0.17916 | 0
OK_4B_SO_2019_EL | 4B | SO | EL |  |  | OfficeSmall | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Electricity | 1700.4828 | 4976.4129 | 7113.1307 | 1600.4544 | 13417.6985 | 0 | 5251.491 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39063.869 | 0 | 39062.2018 | 1.6671 | 1.6671 | 128.7265 | 376.7145 | 538.464 | 121.1544 | 1015.7198 | 0 | 397.5379 | 0 | 0 | 0 | 0 | 378.8178 | 0 | 0 | 2957.1349 | 0 | 2957.0087 | 0.1262 | 0.1262 | 5.802 | 16.9795 | 24.27 | 5.4608 | 45.7812 | 0 | 17.9181 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.2859 | 0 | 133.2802 | 0.0056883 | 0.0056883 | 4.4111 | 0.9925 | 8.3208 | 3.2566 | 0 | 0 | 3.0861 | 1.0545 | 3.1033 | 0 | 0 | 24.224 | 24.225 | 0.0010339
OK_4B_SO_2019_NG | 4B | SO | NG |  |  | OfficeSmall | STD2019 | OK-AMARILLO-TX | Zone4B | Zone4B(OK-AMARILLO-TX) |  |  | OK | 0.0757 | 0.007237 |  |  |  | Natural Gas | 1108.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108.946 | 0 | 1108.946 | 0 | 0 | 8.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0254 | 0 | 8.0254 | 0 | 0 | 1.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1089 | 0 | 1.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20155 | 0 | 0 | 0 | 0.20155 | 0.20155 | 0
OR_4C_LO_2016_EL | 4C | LO | EL |  |  | OfficeLarge | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 419955.3469 | 884209.3825 | 96463.4995 | 4077910.5986 | 543459.8574 | 572431.9722 | 71239.6712 | 151117.9062 | 248937.3462 | 0 | 0 | 0 | 0 | 7065725.5807 | 0 | 7065725.025 | 0.55571 | 543460.4131 | 0 | 37795.9812 | 79578.8444 | 8681.715 | 367011.9539 | 48911.3872 | 51518.8775 | 6411.5704 | 13600.6116 | 22404.3612 | 0 | 0 | 0 | 0 | 635915.3023 | 0 | 635915.2523 | 0.050014 | 48911.4372 | 0 | 1432.8876 | 3016.9224 | 329.1335 | 13913.831 | 1854.285 | 1953.1379 | 243.0698 | 515.6143 | 849.3742 | 0 | 0 | 0 | 0 | 24108.2557 | 0 | 24108.2538 | 0.0018961 | 1854.2869 | 6.0509 | 0.66013 | 27.9065 | 3.9173 | 0.48752 | 0 | 2.8739 | 0 | 0 | 1.7036 | 0 | 48.3531 | 48.3531 | 3.8029e-06
OR_4C_LO_2016_NG | 4C | LO | NG |  |  | OfficeLarge | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 809701.2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549838.1895 | 0 | 0 | 1359539.3988 | 0 | 1359539.3988 | 0 | 0 | 6384.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4335.4741 | 0 | 0 | 10719.9682 | 0 | 10719.9682 | 0 | 0 | 809.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549.8382 | 0 | 0 | 1359.5394 | 0 | 1359.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.624 | 1.1028 | 0 | 0 | 2.7268 | 2.7268 | 0
OR_4C_LO_2019_EL | 4C | LO | EL |  |  | OfficeLarge | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 392505.8867 | 719198.6429 | 96463.4995 | 4077910.5986 | 543387.6147 | 545385.4041 | 68600.0328 | 134999.4408 | 248687.2752 | 0 | 0 | 0 | 0 | 6827138.3954 | 0 | 6827137.0061 | 1.3893 | 543389.004 | 0 | 35325.5298 | 64727.8779 | 8681.715 | 367011.9539 | 48904.8853 | 49084.6864 | 6174.003 | 12149.9497 | 22381.8548 | 0 | 0 | 0 | 0 | 614442.4556 | 0 | 614442.3306 | 0.12504 | 48905.0104 | 0 | 1339.2301 | 2453.9058 | 329.1335 | 13913.831 | 1854.0385 | 1860.855 | 234.0633 | 460.6181 | 848.521 | 0 | 0 | 0 | 0 | 23294.1962 | 0 | 23294.1915 | 0.0047402 | 1854.0433 | 4.9217 | 0.66013 | 27.9065 | 3.7322 | 0.46945 | 0 | 2.686 | 0 | 0 | 1.7018 | 0 | 46.7203 | 46.7203 | 9.5073e-06
OR_4C_LO_2019_NG | 4C | LO | NG |  |  | OfficeLarge | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 1551017.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549819.2331 | 0 | 0 | 2100836.6465 | 0 | 2100836.6465 | 0 | 0 | 12229.7723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4335.3247 | 0 | 0 | 16565.097 | 0 | 16565.097 | 0 | 0 | 1551.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549.8192 | 0 | 0 | 2100.8366 | 0 | 2100.8366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1108 | 1.1028 | 0 | 0 | 4.2136 | 4.2136 | 0
OR_4C_MA_2016_EL | 4C | MA | EL |  |  | ApartmentMidRise | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 16199.0438 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 18616.3968 | 0 | 0 | 0 | 0 | 110520.2684 | 0 | 0 | 322911.127 | 0 | 322911.6827 | -0.55571 | -0.55571 | 0 | 1457.9139 | 2553.7251 | 647.6839 | 12780.3787 | 0 | 1675.4757 | 0 | 0 | 0 | 0 | 9946.8242 | 0 | 0 | 29062.0014 | 0 | 29062.0514 | -0.050014 | -0.050014 | 0 | 55.2711 | 96.8146 | 24.5544 | 484.5184 | 0 | 63.5191 | 0 | 0 | 0 | 0 | 377.0952 | 0 | 0 | 1101.7728 | 0 | 1101.7747 | -0.0018961 | -0.0018961 | 2.8693 | 0.72773 | 14.3599 | 1.8826 | 0 | 0 | 1.6381 | 0 | 11.1762 | 0 | 0 | 32.6539 | 32.6538 | -5.6196e-05
OR_4C_MA_2016_NG | 4C | MA | NG |  |  | ApartmentMidRise | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 113747.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113747.5326 | 0 | 113747.5326 | 0 | 0 | 896.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 896.8993 | 0 | 896.8993 | 0 | 0 | 113.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.7475 | 0 | 113.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3712 | 0 | 0 | 0 | 3.3712 | 3.3712 | 0
OR_4C_MA_2019_EL | 4C | MA | EL |  |  | ApartmentMidRise | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 20258.5297 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 18997.0604 | 0 | 0 | 0 | 0 | 110334.1044 | 0 | 0 | 321971.9715 | 0 | 321971.4157 | 0.55571 | 0.55571 | 0 | 1823.2677 | 2086.3424 | 647.6839 | 12780.3787 | 0 | 1709.7354 | 0 | 0 | 0 | 0 | 9930.0694 | 0 | 0 | 28977.4774 | 0 | 28977.4274 | 0.050014 | 0.050014 | 0 | 69.1221 | 79.0956 | 24.5544 | 484.5184 | 0 | 64.818 | 0 | 0 | 0 | 0 | 376.46 | 0 | 0 | 1098.5684 | 0 | 1098.5665 | 0.0018961 | 0.0018961 | 2.3442 | 0.72773 | 14.3599 | 1.921 | 0 | 0 | 2.0486 | 0 | 11.1573 | 0 | 0 | 32.5588 | 32.5589 | 5.6196e-05
OR_4C_MA_2019_NG | 4C | MA | NG |  |  | ApartmentMidRise | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 33514.8134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33514.8134 | 0 | 33514.8134 | 0 | 0 | 264.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264.2643 | 0 | 264.2643 | 0 | 0 | 33.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5148 | 0 | 33.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9933 | 0 | 0 | 0 | 0.9933 | 0.9933 | 0
OR_4C_PS_2016_EL | 4C | PS | EL |  |  | SchoolPrimary | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 63929.2622 | 99342.0946 | 7143.6949 | 317887.4784 | 4818.0346 | 88841.8911 | 886.3628 | 0 | 0 | 0 | 7179.8163 | 17610.5556 | 0 | 607639.1906 | 0 | 607639.4685 | -0.27786 | 4817.7568 | 0 | 5753.6336 | 8940.7885 | 642.9325 | 28609.8731 | 433.6231 | 7995.7702 | 79.7726 | 0 | 0 | 0 | 646.1835 | 1584.95 | 0 | 54687.5272 | 0 | 54687.5522 | -0.025007 | 433.5981 | 0 | 218.1266 | 338.9552 | 24.3743 | 1084.6321 | 16.4391 | 303.1285 | 3.0243 | 0 | 0 | 0 | 24.4975 | 60.0872 | 0 | 2073.2649 | 0 | 2073.2659 | -0.00094805 | 16.4382 | 4.583 | 0.32956 | 14.6653 | 4.0986 | 0.040891 | 0 | 2.9493 | 0 | 0.33123 | 0 | 0.81244 | 28.0326 | 28.0326 | -1.2819e-05
OR_4C_PS_2016_NG | 4C | PS | NG |  |  | SchoolPrimary | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 550056.1874 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114183.5284 | 0 | 0 | 1006430.1307 | 0 | 1006430.1307 | 0 | 0 | 4337.193 | 0 | 0 | 0 | 2698.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 900.3371 | 0 | 0 | 7935.7016 | 0 | 7935.7016 | 0 | 0 | 550.0562 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1835 | 0 | 0 | 1006.4301 | 0 | 1006.4301 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.4373 | 1.5439 | 0 | 0 | 13.6079 | 13.6079 | 0
OR_4C_PS_2019_EL | 4C | PS | EL |  |  | SchoolPrimary | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 64229.3474 | 80670.1265 | 7143.6949 | 312483.1662 | 4745.7919 | 81073.0187 | 983.6126 | 0 | 0 | 0 | 7179.8163 | 12486.8787 | 0 | 570995.4532 | 0 | 570994.8975 | 0.55571 | 4746.3476 | 0 | 5780.6413 | 7260.3114 | 642.9325 | 28123.485 | 427.1213 | 7296.5717 | 88.5251 | 0 | 0 | 0 | 646.1835 | 1123.8191 | 0 | 51389.5908 | 0 | 51389.5408 | 0.050014 | 427.1713 | 0 | 219.1505 | 275.2465 | 24.3743 | 1066.1926 | 16.1926 | 276.6211 | 3.3561 | 0 | 0 | 0 | 24.4975 | 42.6052 | 0 | 1948.2365 | 0 | 1948.2346 | 0.0018961 | 16.1945 | 3.7216 | 0.32956 | 14.416 | 3.7402 | 0.045378 | 0 | 2.9631 | 0 | 0.33123 | 0 | 0.57607 | 26.3421 | 26.3421 | 2.5637e-05
OR_4C_PS_2019_NG | 4C | PS | NG |  |  | SchoolPrimary | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 630099.3432 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113927.6178 | 0 | 0 | 1086217.3759 | 0 | 1086217.3759 | 0 | 0 | 4968.3333 | 0 | 0 | 0 | 2698.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 898.3193 | 0 | 0 | 8564.824 | 0 | 8564.824 | 0 | 0 | 630.0993 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.9276 | 0 | 0 | 1086.2174 | 0 | 1086.2174 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 8.5196 | 1.5404 | 0 | 0 | 14.6868 | 14.6868 | 0
OR_4C_RS_2016_EL | 4C | RS | EL |  |  | RetailStandalone | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 19822.2947 | 84668.4839 | 10733.6031 | 53987.5506 | 0 | 39633.4752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208845.4075 | 0 | 208842.0733 | 3.3343 | 3.3343 | 0 | 1784.0065 | 7620.1636 | 966.0243 | 4858.8796 | 0 | 3567.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18796.0867 | 0 | 18795.7866 | 0.30009 | 0.30009 | 0 | 67.6337 | 288.8889 | 36.6231 | 184.2055 | 0 | 135.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.5805 | 0 | 712.5692 | 0.011377 | 0.011377 | 11.6997 | 1.4832 | 7.4601 | 5.4766 | 0 | 0 | 2.7391 | 0 | 0 | 0 | 0 | 28.8583 | 28.8588 | 0.00046074
OR_4C_RS_2016_NG | 4C | RS | NG |  |  | RetailStandalone | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 200254.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89473.9361 | 0 | 0 | 289728.7372 | 0 | 289728.7372 | 0 | 0 | 1579.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.502 | 0 | 0 | 2284.5111 | 0 | 2284.5111 | 0 | 0 | 200.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4739 | 0 | 0 | 289.7287 | 0 | 289.7287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1101 | 3.6236 | 0 | 0 | 11.7337 | 11.7337 | 0
OR_4C_RS_2019_EL | 4C | RS | EL |  |  | RetailStandalone | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 18002.3335 | 67249.6494 | 10733.6031 | 53987.5506 | 0 | 37746.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187719.9651 | 0 | 187715.5194 | 4.4457 | 4.4457 | 0 | 1620.21 | 6052.4684 | 966.0243 | 4858.8796 | 0 | 3397.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16894.7969 | 0 | 16894.3967 | 0.40011 | 0.40011 | 0 | 61.424 | 229.4558 | 36.6231 | 184.2055 | 0 | 128.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.5005 | 0 | 640.4854 | 0.015169 | 0.015169 | 9.2927 | 1.4832 | 7.4601 | 5.2159 | 0 | 0 | 2.4876 | 0 | 0 | 0 | 0 | 25.939 | 25.9396 | 0.00061432
OR_4C_RS_2019_NG | 4C | RS | NG |  |  | RetailStandalone | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 227333.9362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89483.4143 | 0 | 0 | 316817.3505 | 0 | 316817.3505 | 0 | 0 | 1792.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.5767 | 0 | 0 | 2498.1048 | 0 | 2498.1048 | 0 | 0 | 227.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4834 | 0 | 0 | 316.8174 | 0 | 316.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2068 | 3.624 | 0 | 0 | 12.8308 | 12.8308 | 0
OR_4C_SH_2016_EL | 4C | SH | EL |  |  | HotelSmall | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 8977.549 | 60995.0958 | 79650.3925 | 12292.379 | 154949.5496 | 0 | 50180.9143 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 367118.1229 | 0 | 367117.5672 | 0.55571 | 0.55571 | 807.9794 | 5489.5586 | 7168.5353 | 1106.3141 | 13945.4595 | 0 | 4516.2823 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 33040.6311 | 0 | 33040.581 | 0.050014 | 0.050014 | 30.6314 | 208.1153 | 271.7671 | 41.9416 | 528.6879 | 0 | 171.2173 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.607 | 0 | 1252.6051 | 0.0018961 | 0.0018961 | 6.2906 | 0.97083 | 12.2376 | 3.9632 | 0.0057056 | 0 | 4.8173 | 0.70903 | 0 | 0 | 0 | 28.9941 | 28.9942 | 4.3889e-05
OR_4C_SH_2016_NG | 4C | SH | NG |  |  | HotelSmall | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 21420.6669 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 571874.9375 | 0 | 0 | 992791.0423 | 0 | 992791.0423 | 0 | 0 | 168.902 | 0 | 0 | 0 | 3150.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 4509.2339 | 0 | 0 | 7828.1574 | 0 | 7828.1574 | 0 | 0 | 21.4207 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 571.8749 | 0 | 0 | 992.791 | 0 | 992.791 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.49583 | 13.2372 | 0 | 0 | 22.9802 | 22.9802 | 0
OR_4C_SH_2019_EL | 4C | SH | EL |  |  | HotelSmall | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 11689.43 | 56199.2897 | 51078.3913 | 12292.379 | 154949.5496 | 0 | 47460.6975 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 333741.9799 | 0 | 333739.4792 | 2.5007 | 2.5007 | 1052.0487 | 5057.9361 | 4597.0552 | 1106.3141 | 13945.4595 | 0 | 4271.4628 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 30036.7782 | 0 | 30036.5531 | 0.22506 | 0.22506 | 39.8843 | 191.752 | 174.2795 | 41.9416 | 528.6879 | 0 | 161.9359 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.7276 | 0 | 1138.7191 | 0.0085324 | 0.0085324 | 4.0341 | 0.97083 | 12.2376 | 3.7483 | 0.0057056 | 0 | 4.4385 | 0.92321 | 0 | 0 | 0 | 26.358 | 26.3582 | 0.0001975
OR_4C_SH_2019_NG | 4C | SH | NG |  |  | HotelSmall | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 24188.2929 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 571931.8066 | 0 | 0 | 995615.5374 | 0 | 995615.5374 | 0 | 0 | 190.7247 | 0 | 0 | 0 | 3150.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 4509.6823 | 0 | 0 | 7850.4285 | 0 | 7850.4285 | 0 | 0 | 24.1883 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 571.9318 | 0 | 0 | 995.6155 | 0 | 995.6155 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.55989 | 13.2385 | 0 | 0 | 23.0456 | 23.0456 | 0
OR_4C_SO_2016_EL | 4C | SO | EL |  |  | OfficeSmall | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 1444.8547 | 2834.138 | 8924.7562 | 1594.8973 | 13417.6985 | 0 | 5051.4342 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38271.9775 | 0 | 38270.8661 | 1.1114 | 1.1114 | 130.0369 | 255.0724 | 803.2281 | 143.5408 | 1207.5929 | 0 | 454.6291 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3444.478 | 0 | 3444.3779 | 0.10003 | 0.10003 | 4.9298 | 9.6701 | 30.4513 | 5.4418 | 45.7812 | 0 | 17.2355 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.584 | 0 | 130.5802 | 0.0037922 | 0.0037922 | 5.5346 | 0.98906 | 8.3208 | 3.1326 | 0 | 0 | 1.7576 | 0.89601 | 3.1033 | 0 | 0 | 23.7332 | 23.7339 | 0.00068924
OR_4C_SO_2016_NG | 4C | SO | NG |  |  | OfficeSmall | STD2016 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 331.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.736 | 0 | 331.736 | 0 | 0 | 2.6157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6157 | 0 | 2.6157 | 0 | 0 | 0.33174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33174 | 0 | 0.33174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060294 | 0 | 0 | 0 | 0.060294 | 0.060294 | 0
OR_4C_SO_2019_EL | 4C | SO | EL |  |  | OfficeSmall | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 1542.1045 | 2628.5241 | 7182.5949 | 1594.8973 | 13417.6985 | 0 | 4623.535 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 35993.5528 | 0 | 35994.6642 | -1.1114 | -1.1114 | 138.7894 | 236.5672 | 646.4335 | 143.5408 | 1207.5929 | 0 | 416.1181 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3239.4198 | 0 | 3239.5198 | -0.10003 | -0.10003 | 5.2617 | 8.9685 | 24.507 | 5.4418 | 45.7812 | 0 | 15.7755 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 122.81 | 0 | 122.8138 | -0.0037922 | -0.0037922 | 4.4542 | 0.98906 | 8.3208 | 2.8672 | 0 | 0 | 1.63 | 0.95632 | 3.1033 | 0 | 0 | 22.3217 | 22.321 | -0.00068924
OR_4C_SO_2019_NG | 4C | SO | NG |  |  | OfficeSmall | STD2019 | OR-PORTLAND-OR | Zone4C | Zone4C(OR-PORTLAND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 388.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.605 | 0 | 388.605 | 0 | 0 | 3.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0642 | 0 | 3.0642 | 0 | 0 | 0.38861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38861 | 0 | 0.38861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07063 | 0 | 0 | 0 | 0.07063 | 0.07063 | 0
OR_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 406354.263 | 881389.1373 | 96163.4143 | 4077910.5986 | 543457.0788 | 664888.7786 | 70039.3304 | 116716.4721 | 669312.2567 | 0 | 0 | 0 | 0 | 7526231.3298 | 0 | 7526235.2198 | -3.89 | 543453.1888 | 0 | 36571.8837 | 79325.0224 | 8654.7073 | 367011.9539 | 48911.1371 | 59839.9901 | 6303.5397 | 10504.4825 | 60238.1031 | 0 | 0 | 0 | 0 | 677360.8197 | 0 | 677361.1698 | -0.3501 | 48910.787 | 0 | 1386.4807 | 3007.2997 | 328.1096 | 13913.831 | 1854.2756 | 2268.6005 | 238.9742 | 398.2366 | 2283.6934 | 0 | 0 | 0 | 0 | 25679.5013 | 0 | 25679.5146 | -0.013273 | 1854.2623 | 6.0316 | 0.65808 | 27.9065 | 4.5501 | 0.4793 | 0 | 2.7808 | 0 | 0 | 4.5803 | 0 | 51.5045 | 51.5045 | -2.662e-05
OR_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 1440786.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589381.1197 | 0 | 0 | 2030167.402 | 0 | 2030167.402 | 0 | 0 | 11360.5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4647.2701 | 0 | 0 | 16007.87 | 0 | 16007.87 | 0 | 0 | 1440.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589.3811 | 0 | 0 | 2030.1674 | 0 | 2030.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8897 | 1.1821 | 0 | 0 | 4.0718 | 4.0718 | 0
OR_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 378910.3599 | 717689.8812 | 96163.4143 | 4077910.5986 | 543387.6147 | 642399.0598 | 67919.284 | 103957.2939 | 669651.2419 | 0 | 0 | 0 | 0 | 7297988.7483 | 0 | 7297990.4154 | -1.6671 | 543385.9475 | 0 | 34101.9324 | 64592.0893 | 8654.7073 | 367011.9539 | 48904.8853 | 57815.9154 | 6112.7356 | 9356.1564 | 60268.6118 | 0 | 0 | 0 | 0 | 656818.9873 | 0 | 656819.1374 | -0.15004 | 48904.7353 | 0 | 1292.8421 | 2448.7579 | 328.1096 | 13913.831 | 1854.0385 | 2191.8656 | 231.7406 | 354.7023 | 2284.85 | 0 | 0 | 0 | 0 | 24900.7376 | 0 | 24900.7433 | -0.0056883 | 1854.0329 | 4.9114 | 0.65808 | 27.9065 | 4.3961 | 0.46479 | 0 | 2.593 | 0 | 0 | 4.5826 | 0 | 49.9425 | 49.9425 | -1.1409e-05
OR_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 2286457.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589362.1634 | 0 | 0 | 2875819.3146 | 0 | 2875819.3146 | 0 | 0 | 18028.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4647.1207 | 0 | 0 | 22675.8353 | 0 | 22675.8353 | 0 | 0 | 2286.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589.3622 | 0 | 0 | 2875.8193 | 0 | 2875.8193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5859 | 1.1821 | 0 | 0 | 5.7679 | 5.7679 | 0
OR_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 15337.6881 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 19713.9306 | 0 | 0 | 0 | 0 | 118269.6908 | 0 | 0 | 330896.7276 | 0 | 330897.8391 | -1.1114 | -1.1114 | 0 | 1380.3919 | 2553.7251 | 647.6839 | 12780.3787 | 0 | 1774.2538 | 0 | 0 | 0 | 0 | 10644.2722 | 0 | 0 | 29780.7055 | 0 | 29780.8055 | -0.10003 | -0.10003 | 0 | 52.3322 | 96.8146 | 24.5544 | 484.5184 | 0 | 67.2639 | 0 | 0 | 0 | 0 | 403.5362 | 0 | 0 | 1129.0196 | 0 | 1129.0234 | -0.0037922 | -0.0037922 | 2.8693 | 0.72773 | 14.3599 | 1.9935 | 0 | 0 | 1.551 | 0 | 11.9598 | 0 | 0 | 33.4615 | 33.4614 | -0.00011239
OR_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 198946.8135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198946.8135 | 0 | 198946.8135 | 0 | 0 | 1568.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1568.6956 | 0 | 1568.6956 | 0 | 0 | 198.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9468 | 0 | 198.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8963 | 0 | 0 | 0 | 5.8963 | 5.8963 | 0
OR_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 19311.0384 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 19544.438 | 0 | 0 | 0 | 0 | 118083.5269 | 0 | 0 | 329321.2803 | 0 | 329320.4468 | 0.83357 | 0.83357 | 0 | 1737.9935 | 2086.3424 | 647.6839 | 12780.3787 | 0 | 1758.9994 | 0 | 0 | 0 | 0 | 10627.5174 | 0 | 0 | 29638.9152 | 0 | 29638.8402 | 0.075021 | 0.075021 | 0 | 65.8893 | 79.0956 | 24.5544 | 484.5184 | 0 | 66.6856 | 0 | 0 | 0 | 0 | 402.901 | 0 | 0 | 1123.6442 | 0 | 1123.6414 | 0.0028441 | 0.0028441 | 2.3442 | 0.72773 | 14.3599 | 1.9764 | 0 | 0 | 1.9528 | 0 | 11.941 | 0 | 0 | 33.302 | 33.302 | 8.4293e-05
OR_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 77332.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77332.3988 | 0 | 77332.3988 | 0 | 0 | 609.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.766 | 0 | 609.766 | 0 | 0 | 77.3324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3324 | 0 | 77.3324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2919 | 0 | 0 | 0 | 2.2919 | 2.2919 | 0
OR_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 58122.0579 | 97597.1547 | 7138.1378 | 317887.4784 | 4818.0346 | 94046.1465 | 1130.8766 | 0 | 0 | 0 | 7179.8163 | 17496.6344 | 0 | 605416.3373 | 0 | 605415.5037 | 0.83357 | 4818.8682 | 0 | 5230.9852 | 8783.7439 | 642.4324 | 28609.8731 | 433.6231 | 8464.1532 | 101.7789 | 0 | 0 | 0 | 646.1835 | 1574.6971 | 0 | 54487.4704 | 0 | 54487.3953 | 0.075021 | 433.6981 | 0 | 198.3125 | 333.0015 | 24.3553 | 1084.6321 | 16.4391 | 320.8855 | 3.8586 | 0 | 0 | 0 | 24.4975 | 59.6985 | 0 | 2065.6805 | 0 | 2065.6777 | 0.0028441 | 16.442 | 4.5025 | 0.32931 | 14.6653 | 4.3387 | 0.052171 | 0 | 2.6814 | 0 | 0.33123 | 0 | 0.80718 | 27.93 | 27.9301 | 3.8456e-05
OR_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 716047.3996 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122230.4958 | 0 | 0 | 1180468.3103 | 0 | 1180468.3103 | 0 | 0 | 5646.0337 | 0 | 0 | 0 | 2698.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 963.7875 | 0 | 0 | 9307.9926 | 0 | 9307.9926 | 0 | 0 | 716.0474 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.2305 | 0 | 0 | 1180.4683 | 0 | 1180.4683 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.6817 | 1.6527 | 0 | 0 | 15.9611 | 15.9611 | 0
OR_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 54712.7565 | 79436.4429 | 7138.1378 | 312483.1662 | 4743.0133 | 75640.9208 | 1367.0548 | 0 | 0 | 0 | 7179.8163 | 12439.643 | 0 | 555140.9517 | 0 | 555144.8417 | -3.89 | 4739.1233 | 0 | 4924.1481 | 7149.2799 | 642.4324 | 28123.485 | 426.8712 | 6807.6829 | 123.0349 | 0 | 0 | 0 | 646.1835 | 1119.5679 | 0 | 49962.6857 | 0 | 49963.0358 | -0.3501 | 426.5211 | 0 | 186.6799 | 271.0371 | 24.3553 | 1066.1926 | 16.1832 | 258.0868 | 4.6644 | 0 | 0 | 0 | 24.4975 | 42.4441 | 0 | 1894.1409 | 0 | 1894.1542 | -0.013273 | 16.1699 | 3.6647 | 0.32931 | 14.416 | 3.4896 | 0.063067 | 0 | 2.5241 | 0 | 0.33123 | 0 | 0.57389 | 25.6109 | 25.6107 | -0.00017946
OR_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 895232.2262 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 121955.6288 | 0 | 0 | 1359378.2698 | 0 | 1359378.2698 | 0 | 0 | 7058.9061 | 0 | 0 | 0 | 2698.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 961.6201 | 0 | 0 | 10718.6977 | 0 | 10718.6977 | 0 | 0 | 895.2322 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 121.9556 | 0 | 0 | 1359.3783 | 0 | 1359.3783 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 12.1044 | 1.649 | 0 | 0 | 18.3802 | 18.3802 | 0
OR_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 18449.6828 | 84787.9623 | 10736.3817 | 53987.5506 | 0 | 47268.9764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215230.5538 | 0 | 215231.9431 | -1.3893 | -1.3893 | 0 | 1660.4714 | 7630.9166 | 966.2743 | 4858.8796 | 0 | 4254.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19370.7498 | 0 | 19370.8749 | -0.12504 | -0.12504 | 0 | 62.9503 | 289.2965 | 36.6325 | 184.2055 | 0 | 161.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.3666 | 0 | 734.3714 | -0.0047402 | -0.0047402 | 11.7162 | 1.4836 | 7.4601 | 6.5317 | 0 | 0 | 2.5494 | 0 | 0 | 0 | 0 | 29.7413 | 29.7411 | -0.00019197
OR_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 317878.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91815.0444 | 0 | 0 | 409693.9501 | 0 | 409693.9501 | 0 | 0 | 2506.4752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723.9616 | 0 | 0 | 3230.4368 | 0 | 3230.4368 | 0 | 0 | 317.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.815 | 0 | 0 | 409.694 | 0 | 409.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8738 | 3.7184 | 0 | 0 | 16.5922 | 16.5922 | 0
OR_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 0 | 16838.1141 | 67346.8992 | 10736.3817 | 53987.5506 | 0 | 44851.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193760.569 | 0 | 193759.7355 | 0.83357 | 0.83357 | 0 | 1515.4303 | 6061.2209 | 966.2743 | 4858.8796 | 0 | 4036.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17438.4512 | 0 | 17438.3762 | 0.075021 | 0.075021 | 0 | 57.4516 | 229.7876 | 36.6325 | 184.2055 | 0 | 153.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 661.1111 | 0 | 661.1082 | 0.0028441 | 0.0028441 | 9.3062 | 1.4836 | 7.4601 | 6.1977 | 0 | 0 | 2.3267 | 0 | 0 | 0 | 0 | 26.7742 | 26.7743 | 0.00011518
OR_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 349450.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91824.5226 | 0 | 0 | 441275.2166 | 0 | 441275.2166 | 0 | 0 | 2755.4187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724.0364 | 0 | 0 | 3479.4551 | 0 | 3479.4551 | 0 | 0 | 349.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8245 | 0 | 0 | 441.2752 | 0 | 441.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1524 | 3.7188 | 0 | 0 | 17.8712 | 17.8712 | 0
OR_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 19013.7318 | 50908.8988 | 79311.4074 | 12292.379 | 154949.5496 | 0 | 51592.4262 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 368140.6354 | 0 | 368139.2462 | 1.3893 | 1.3893 | 1711.2359 | 4581.8009 | 7138.0267 | 1106.3141 | 13945.4595 | 0 | 4643.3184 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 33132.6572 | 0 | 33132.5322 | 0.12504 | 0.12504 | 64.8749 | 173.7012 | 270.6105 | 41.9416 | 528.6879 | 0 | 176.0334 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.0958 | 0 | 1256.0911 | 0.0047402 | 0.0047402 | 6.2638 | 0.97083 | 12.2376 | 4.0747 | 0.0057056 | 0 | 4.0207 | 1.5017 | 0 | 0 | 0 | 29.0748 | 29.0749 | 0.00010972
OR_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 43040.3754 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 617284.8557 | 0 | 0 | 1059820.6691 | 0 | 1059820.6691 | 0 | 0 | 339.3734 | 0 | 0 | 0 | 3150.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 4867.2911 | 0 | 0 | 8356.686 | 0 | 8356.686 | 0 | 0 | 43.0404 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2849 | 0 | 0 | 1059.8207 | 0 | 1059.8207 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.99626 | 14.2883 | 0 | 0 | 24.5318 | 24.5318 | 0
OR_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 23181.5818 | 46735.4916 | 50895.0059 | 12292.379 | 154949.5496 | 0 | 48672.1526 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 336798.4033 | 0 | 336798.1254 | 0.27786 | 0.27786 | 2086.3424 | 4206.1942 | 4580.5505 | 1106.3141 | 13945.4595 | 0 | 4380.4937 | 6.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 30311.8563 | 0 | 30311.8313 | 0.025007 | 0.025007 | 79.0956 | 159.4615 | 173.6538 | 41.9416 | 528.6879 | 0 | 166.0694 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1149.1562 | 0 | 1149.1552 | 0.00094805 | 0.00094805 | 4.0196 | 0.97083 | 12.2376 | 3.844 | 0.0057056 | 0 | 3.6911 | 1.8308 | 0 | 0 | 0 | 26.5996 | 26.5996 | 2.1945e-05
OR_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 45438.3527 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 617341.7248 | 0 | 0 | 1062275.5154 | 0 | 1062275.5154 | 0 | 0 | 358.2814 | 0 | 0 | 0 | 3150.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 4867.7395 | 0 | 0 | 8376.0424 | 0 | 8376.0424 | 0 | 0 | 45.4384 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 617.3417 | 0 | 0 | 1062.2755 | 0 | 1062.2755 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.0518 | 14.2897 | 0 | 0 | 24.5886 | 24.5886 | 0
OR_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 3039.752 | 2528.4957 | 8835.842 | 1589.3401 | 13417.6985 | 0 | 5145.9055 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39561.2324 | 0 | 39565.4003 | -4.1679 | -4.1679 | 273.5777 | 227.5646 | 795.2258 | 143.0406 | 1207.5929 | 0 | 463.1315 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3560.5109 | 0 | 3560.886 | -0.37511 | -0.37511 | 10.3716 | 8.6272 | 30.1479 | 5.4228 | 45.7812 | 0 | 17.5578 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.9829 | 0 | 134.9971 | -0.014221 | -0.014221 | 5.4794 | 0.98561 | 8.3208 | 3.1912 | 0 | 0 | 1.568 | 1.8851 | 3.1033 | 0 | 0 | 24.536 | 24.5334 | -0.0025846
OR_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 2559.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2559.1062 | 0 | 2559.1062 | 0 | 0 | 20.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1786 | 0 | 20.1786 | 0 | 0 | 2.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5591 | 0 | 2.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46512 | 0 | 0 | 0 | 0.46512 | 0.46512 | 0
OR_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Electricity | 3120.3304 | 2347.8888 | 7124.245 | 1589.3401 | 13417.6985 | 0 | 4704.1134 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37307.8148 | 0 | 37309.2041 | -1.3893 | -1.3893 | 280.8297 | 211.31 | 641.182 | 143.0406 | 1207.5929 | 0 | 423.3702 | 0 | 0 | 0 | 0 | 450.3779 | 0 | 0 | 3357.7033 | 0 | 3357.8284 | -0.12504 | -0.12504 | 10.6466 | 8.011 | 24.3079 | 5.4228 | 45.7812 | 0 | 16.0504 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 127.2943 | 0 | 127.299 | -0.0047402 | -0.0047402 | 4.418 | 0.98561 | 8.3208 | 2.9172 | 0 | 0 | 1.456 | 1.935 | 3.1033 | 0 | 0 | 23.1369 | 23.136 | -0.00086155
OR_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | OR-REDMOND-OR | Zone5B | Zone5B(OR-REDMOND-OR) |  |  | OR | 0.09 | 0.007885 |  |  |  | Natural Gas | 2890.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2890.8422 | 0 | 2890.8422 | 0 | 0 | 22.7943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7943 | 0 | 22.7943 | 0 | 0 | 2.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8908 | 0 | 2.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52542 | 0 | 0 | 0 | 0.52542 | 0.52542 | 0
PA_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 682674.3839 | 881114.0592 | 95382.6371 | 4077910.5986 | 543457.0788 | 578333.6478 | 99997.8363 | 242627.2213 | 353083.5826 | 13337.1201 | 0 | 0 | 0 | 7567918.1658 | 0 | 7567918.9993 | -0.83357 | 543456.2453 | 0 | 58027.3226 | 74894.695 | 8107.5242 | 346622.4009 | 46193.8517 | 49158.3601 | 8499.8161 | 20623.3138 | 30012.1045 | 1133.6552 | 0 | 0 | 0 | 643273.0441 | 0 | 643273.1149 | -0.070853 | 46193.7808 | 0 | 2329.285 | 3006.3612 | 325.4456 | 13913.831 | 1854.2756 | 1973.2744 | 341.1926 | 827.8441 | 1204.7212 | 45.5063 | 0 | 0 | 0 | 25821.7368 | 0 | 25821.7396 | -0.0028441 | 1854.2727 | 6.0298 | 0.65273 | 27.9065 | 3.9577 | 0.68432 | 0.09127 | 4.6718 | 0 | 0 | 2.4163 | 0 | 51.7897 | 51.7897 | -5.7044e-06
PA_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 774963.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544937.975 | 0 | 0 | 1319901.6868 | 0 | 1319901.6868 | 0 | 0 | 6989.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4914.7956 | 0 | 0 | 11904.1933 | 0 | 11904.1933 | 0 | 0 | 774.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.938 | 0 | 0 | 1319.9017 | 0 | 1319.9017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543 | 1.093 | 0 | 0 | 2.6473 | 2.6473 | 0
PA_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 641107.0263 | 717325.889 | 95382.6371 | 4077910.5986 | 543387.6147 | 553676.6471 | 95635.4866 | 218548.1624 | 352864.0758 | 11989.5152 | 0 | 0 | 0 | 7307827.6529 | 0 | 7307820.4286 | 7.2243 | 543394.8389 | 0 | 54494.0972 | 60972.7006 | 8107.5242 | 346622.4009 | 46187.9472 | 47062.515 | 8129.0164 | 18576.5938 | 29993.4464 | 1019.1088 | 0 | 0 | 0 | 621165.3505 | 0 | 621164.7364 | 0.61406 | 46188.5613 | 0 | 2187.4572 | 2447.5159 | 325.4456 | 13913.831 | 1854.0385 | 1889.1447 | 326.3083 | 745.6863 | 1203.9722 | 40.9082 | 0 | 0 | 0 | 24934.308 | 0 | 24934.2833 | 0.024649 | 1854.0632 | 4.9089 | 0.65273 | 27.9065 | 3.789 | 0.65446 | 0.082048 | 4.3873 | 0 | 0 | 2.4148 | 0 | 50.0098 | 50.0098 | 4.9438e-05
PA_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 705431.8479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545023.2785 | 0 | 0 | 1250455.1264 | 0 | 1250455.1264 | 0 | 0 | 6362.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4915.5649 | 0 | 0 | 11277.8548 | 0 | 11277.8548 | 0 | 0 | 705.4318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.0233 | 0 | 0 | 1250.4551 | 0 | 1250.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4149 | 1.0931 | 0 | 0 | 2.508 | 2.508 | 0
PA_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 30894.8829 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 21156.0067 | 0 | 0 | 0 | 0 | 109342.1561 | 0 | 0 | 338974.021 | 0 | 338975.1324 | -1.1114 | -1.1114 | 0 | 2626.0651 | 2411.8515 | 612.1738 | 12070.3576 | 0 | 1798.2606 | 0 | 0 | 0 | 0 | 9294.0833 | 0 | 0 | 28812.7918 | 0 | 28812.8863 | -0.094471 | -0.094471 | 0 | 105.4133 | 96.8146 | 24.5734 | 484.5184 | 0 | 72.1843 | 0 | 0 | 0 | 0 | 373.0754 | 0 | 0 | 1156.5794 | 0 | 1156.5832 | -0.0037922 | -0.0037922 | 2.8693 | 0.72829 | 14.3599 | 2.1394 | 0 | 0 | 3.1242 | 0 | 11.057 | 0 | 0 | 34.2783 | 34.2782 | -0.00011239
PA_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 84156.6821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84156.6821 | 0 | 84156.6821 | 0 | 0 | 759.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759.0091 | 0 | 759.0091 | 0 | 0 | 84.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1567 | 0 | 84.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4942 | 0 | 0 | 0 | 2.4942 | 2.4942 | 0
PA_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 30016.8559 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 20650.3076 | 0 | 0 | 0 | 0 | 109375.4989 | 0 | 0 | 332430.4964 | 0 | 332432.7193 | -2.2229 | -2.2229 | 0 | 2551.4327 | 1970.4345 | 612.1738 | 12070.3576 | 0 | 1755.2761 | 0 | 0 | 0 | 0 | 9296.9174 | 0 | 0 | 28256.5922 | 0 | 28256.7811 | -0.18894 | -0.18894 | 0 | 102.4175 | 79.0956 | 24.5734 | 484.5184 | 0 | 70.4588 | 0 | 0 | 0 | 0 | 373.1892 | 0 | 0 | 1134.2529 | 0 | 1134.2604 | -0.0075844 | -0.0075844 | 2.3442 | 0.72829 | 14.3599 | 2.0882 | 0 | 0 | 3.0354 | 0 | 11.0604 | 0 | 0 | 33.6167 | 33.6165 | -0.00022478
PA_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 97141.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97141.7766 | 0 | 97141.7766 | 0 | 0 | 876.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 876.1217 | 0 | 876.1217 | 0 | 0 | 97.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1418 | 0 | 97.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.879 | 0 | 0 | 0 | 2.879 | 2.879 | 0
PA_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 118622.5688 | 98019.4969 | 7115.9093 | 317887.4784 | 4818.0346 | 92826.3557 | 658.5203 | 0 | 0 | 20958.7285 | 7179.8163 | 17624.4485 | 0 | 685711.3573 | 0 | 685708.5787 | 2.7786 | 4820.8132 | 0 | 10082.9183 | 8331.6572 | 604.8523 | 27020.4357 | 409.5329 | 7890.2402 | 55.9742 | 0 | 0 | 1781.4919 | 610.2844 | 1498.0781 | 0 | 58285.4654 | 0 | 58285.2292 | 0.23618 | 409.7691 | 0 | 404.7402 | 334.4425 | 24.2795 | 1084.6321 | 16.4391 | 316.7235 | 2.2469 | 0 | 0 | 71.5112 | 24.4975 | 60.1346 | 0 | 2339.6472 | 0 | 2339.6377 | 0.0094805 | 16.4486 | 4.522 | 0.32828 | 14.6653 | 4.2824 | 0.03038 | 0.9669 | 5.4725 | 0 | 0.33123 | 0 | 0.81308 | 31.6343 | 31.6344 | 0.00012819
PA_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 321357.3945 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114515.2644 | 0 | 0 | 778063.0738 | 0 | 778063.0738 | 0 | 0 | 2898.3223 | 0 | 0 | 0 | 3086.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.8132 | 0 | 0 | 7017.3509 | 0 | 7017.3509 | 0 | 0 | 321.3574 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.5153 | 0 | 0 | 778.0631 | 0 | 778.0631 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.3451 | 1.5484 | 0 | 0 | 10.5202 | 10.5202 | 0
PA_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 113084.8854 | 79753.1995 | 7115.9093 | 312483.1662 | 4745.7919 | 81592.6106 | 405.6707 | 0 | 0 | 22812.0325 | 7179.8163 | 12492.4358 | 0 | 641665.5182 | 0 | 641662.7397 | 2.7786 | 4748.5705 | 0 | 9612.2153 | 6779.022 | 604.8523 | 26561.0691 | 403.3923 | 6935.3719 | 34.482 | 0 | 0 | 1939.0228 | 610.2844 | 1061.857 | 0 | 54541.569 | 0 | 54541.3329 | 0.23618 | 403.6285 | 0 | 385.8456 | 272.1179 | 24.2795 | 1066.1926 | 16.1926 | 278.394 | 1.3841 | 0 | 0 | 77.8347 | 24.4975 | 42.6242 | 0 | 2189.3627 | 0 | 2189.3533 | 0.0094805 | 16.2021 | 3.6793 | 0.32828 | 14.416 | 3.7642 | 0.018715 | 1.0524 | 5.217 | 0 | 0.33123 | 0 | 0.57632 | 29.6023 | 29.6024 | 0.00012819
PA_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 316779.4378 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114278.3102 | 0 | 0 | 773248.1628 | 0 | 773248.1628 | 0 | 0 | 2857.0337 | 0 | 0 | 0 | 3086.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 1030.6761 | 0 | 0 | 6973.9252 | 0 | 6973.9252 | 0 | 0 | 316.7794 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2783 | 0 | 0 | 773.2482 | 0 | 773.2482 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.2832 | 1.5452 | 0 | 0 | 10.4551 | 10.4551 | 0
PA_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 44101.4104 | 84065.535 | 10719.7103 | 53987.5506 | 0 | 39322.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232196.4819 | 0 | 232195.0927 | 1.3893 | 1.3893 | 0 | 3748.6199 | 7145.5705 | 911.1754 | 4588.9418 | 0 | 3342.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19736.701 | 0 | 19736.5829 | 0.11809 | 0.11809 | 0 | 150.474 | 286.8316 | 36.5757 | 184.2055 | 0 | 134.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792.2544 | 0 | 792.2497 | 0.0047402 | 0.0047402 | 11.6164 | 1.4813 | 7.4601 | 5.4336 | 0 | 0 | 6.094 | 0 | 0 | 0 | 0 | 32.0853 | 32.0855 | 0.00019197
PA_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 342446.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89170.6346 | 0 | 0 | 431616.9601 | 0 | 431616.9601 | 0 | 0 | 3088.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.23 | 0 | 0 | 3892.7534 | 0 | 3892.7534 | 0 | 0 | 342.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1706 | 0 | 0 | 431.617 | 0 | 431.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8687 | 3.6113 | 0 | 0 | 17.48 | 17.48 | 0
PA_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 41156.1297 | 66591.1291 | 10719.7103 | 53987.5506 | 0 | 40478.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212932.6791 | 0 | 212933.7906 | -1.1114 | -1.1114 | 0 | 3498.271 | 5660.246 | 911.1754 | 4588.9418 | 0 | 3440.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18099.2777 | 0 | 18099.3722 | -0.094471 | -0.094471 | 0 | 140.4247 | 227.2089 | 36.5757 | 184.2055 | 0 | 138.1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.5263 | 0 | 726.5301 | -0.0037922 | -0.0037922 | 9.2017 | 1.4813 | 7.4601 | 5.5934 | 0 | 0 | 5.6871 | 0 | 0 | 0 | 0 | 29.4237 | 29.4236 | -0.00015358
PA_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 363260.3894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89180.1128 | 0 | 0 | 452440.5022 | 0 | 452440.5022 | 0 | 0 | 3276.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.3154 | 0 | 0 | 4080.5609 | 0 | 4080.5609 | 0 | 0 | 363.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1801 | 0 | 0 | 452.4405 | 0 | 452.4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7117 | 3.6117 | 0 | 0 | 18.3234 | 18.3234 | 0
PA_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 23840.1021 | 76391.1338 | 79255.836 | 12300.7147 | 154949.5496 | 0 | 45682.4148 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392491.9939 | 0 | 392490.0489 | 1.945 | 1.945 | 2026.4087 | 6493.2464 | 6736.7461 | 1045.5607 | 13170.7117 | 0 | 3883.0053 | 6.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 33361.8195 | 0 | 33361.6542 | 0.16532 | 0.16532 | 81.3424 | 260.6465 | 270.4209 | 41.97 | 528.6879 | 0 | 155.8684 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.1827 | 0 | 1339.176 | 0.0066363 | 0.0066363 | 6.2595 | 0.97148 | 12.2376 | 3.6079 | 0.0057056 | 0 | 6.0332 | 1.8828 | 0 | 0 | 0 | 30.998 | 30.9982 | 0.00015361
PA_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 58366.5782 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 566112.2094 | 0 | 0 | 1023974.2256 | 0 | 1023974.2256 | 0 | 0 | 526.4082 | 0 | 0 | 0 | 3603.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5105.766 | 0 | 0 | 9235.2235 | 0 | 9235.2235 | 0 | 0 | 58.3666 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 566.1122 | 0 | 0 | 1023.9742 | 0 | 1023.9742 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.351 | 13.1038 | 0 | 0 | 23.702 | 23.702 | 0
PA_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 27457.796 | 71475.8493 | 50833.8775 | 12300.7147 | 154949.5496 | 0 | 43328.9688 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360418.9986 | 0 | 360418.4429 | 0.55571 | 0.55571 | 2333.9127 | 6075.4472 | 4320.8796 | 1045.5607 | 13170.7117 | 0 | 3682.9624 | 6.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 30635.6149 | 0 | 30635.5676 | 0.047236 | 0.047236 | 93.686 | 243.8756 | 173.4452 | 41.97 | 528.6879 | 0 | 147.8384 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.7496 | 0 | 1229.7477 | 0.0018961 | 0.0018961 | 4.0147 | 0.97148 | 12.2376 | 3.422 | 0.0057056 | 0 | 5.645 | 2.1686 | 0 | 0 | 0 | 28.4651 | 28.4651 | 4.3889e-05
PA_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 58053.7986 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 566159.6003 | 0 | 0 | 1023708.8368 | 0 | 1023708.8368 | 0 | 0 | 523.5872 | 0 | 0 | 0 | 3603.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5106.1934 | 0 | 0 | 9232.83 | 0 | 9232.83 | 0 | 0 | 58.0538 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 566.1596 | 0 | 0 | 1023.7088 | 0 | 1023.7088 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3438 | 13.1049 | 0 | 0 | 23.6959 | 23.6959 | 0
PA_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 2836.9166 | 4770.799 | 8841.3992 | 1578.2259 | 13417.6985 | 0 | 4829.1489 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41278.3866 | 0 | 41281.7209 | -3.3343 | -3.3343 | 241.1379 | 405.5179 | 751.5189 | 134.1492 | 1140.5044 | 0 | 410.4777 | 0 | 0 | 0 | 0 | 425.3569 | 0 | 0 | 3508.6629 | 0 | 3508.9463 | -0.28341 | -0.28341 | 9.6796 | 16.278 | 30.1669 | 5.3849 | 45.7812 | 0 | 16.4771 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.8419 | 0 | 140.8532 | -0.011377 | -0.011377 | 5.4829 | 0.97872 | 8.3208 | 2.9947 | 0 | 0 | 2.9586 | 1.7593 | 3.1033 | 0 | 0 | 25.6004 | 25.5983 | -0.0020677
PA_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 3033.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3033.0148 | 0 | 3033.0148 | 0 | 0 | 27.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3548 | 0 | 27.3548 | 0 | 0 | 3.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.033 | 0 | 3.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55126 | 0 | 0 | 0 | 0.55126 | 0.55126 | 0
PA_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 2892.4879 | 4531.8423 | 7127.0235 | 1578.2259 | 13417.6985 | 0 | 4448.4853 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38999.962 | 0 | 38999.6841 | 0.27786 | 0.27786 | 245.8615 | 385.2066 | 605.797 | 134.1492 | 1140.5044 | 0 | 378.1212 | 0 | 0 | 0 | 0 | 425.3569 | 0 | 0 | 3314.9968 | 0 | 3314.9731 | 0.023618 | 0.023618 | 9.8692 | 15.4626 | 24.3174 | 5.3849 | 45.7812 | 0 | 15.1782 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.0679 | 0 | 133.0669 | 0.00094805 | 0.00094805 | 4.4197 | 0.97872 | 8.3208 | 2.7587 | 0 | 0 | 2.8104 | 1.7937 | 3.1033 | 0 | 0 | 24.1852 | 24.1854 | 0.00017231
PA_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | PA-PHILADELPHIA-PA | Zone4A | Zone4A(PA-PHILADELPHIA-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 3269.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3269.9691 | 0 | 3269.9691 | 0 | 0 | 29.4919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.4919 | 0 | 29.4919 | 0 | 0 | 3.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 0 | 3.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59432 | 0 | 0 | 0 | 0.59432 | 0.59432 | 0
PA_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 592737.7375 | 880744.5098 | 95707.7294 | 4077910.5986 | 543457.0788 | 596983.3874 | 87799.9286 | 204555.3006 | 411705.7825 | 11358.7806 | 0 | 0 | 0 | 7502960.8339 | 0 | 7502960.2782 | 0.55571 | 543457.6346 | 0 | 50382.7077 | 74863.2833 | 8135.157 | 346622.4009 | 46193.8517 | 50743.5879 | 7462.9939 | 17387.2006 | 34994.9915 | 965.4964 | 0 | 0 | 0 | 637751.6709 | 0 | 637751.6236 | 0.047236 | 46193.8989 | 0 | 2022.4212 | 3005.1003 | 326.5548 | 13913.831 | 1854.2756 | 2036.9073 | 299.5734 | 697.9427 | 1404.7401 | 38.7562 | 0 | 0 | 0 | 25600.1024 | 0 | 25600.1005 | 0.0018961 | 1854.2774 | 6.0272 | 0.65496 | 27.9065 | 4.0854 | 0.60084 | 0.077732 | 4.0563 | 0 | 0 | 2.8174 | 0 | 51.3452 | 51.3452 | 3.8029e-06
PA_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 947940.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569145.2242 | 0 | 0 | 1517085.5604 | 0 | 1517085.5604 | 0 | 0 | 8549.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5133.1208 | 0 | 0 | 13682.5947 | 0 | 13682.5947 | 0 | 0 | 947.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.1452 | 0 | 0 | 1517.0856 | 0 | 1517.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9012 | 1.1415 | 0 | 0 | 3.0428 | 3.0428 | 0
PA_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 556271.8284 | 716956.3396 | 95707.7294 | 4077910.5986 | 543387.6147 | 580417.5728 | 83929.3852 | 183643.8077 | 411475.1614 | 10514.0963 | 0 | 0 | 0 | 7260214.1342 | 0 | 7260210.5221 | 3.6121 | 543391.2268 | 0 | 47283.1054 | 60941.2889 | 8135.157 | 346622.4009 | 46187.9472 | 49335.4937 | 7133.9977 | 15609.7237 | 34975.3887 | 893.6982 | 0 | 0 | 0 | 617118.2014 | 0 | 617117.8944 | 0.30703 | 46188.2543 | 0 | 1897.9995 | 2446.255 | 326.5548 | 13913.831 | 1854.0385 | 1980.3848 | 286.3671 | 626.5927 | 1403.9533 | 35.8741 | 0 | 0 | 0 | 24771.8506 | 0 | 24771.8383 | 0.012325 | 1854.0509 | 4.9064 | 0.65496 | 27.9065 | 3.972 | 0.57436 | 0.071951 | 3.8067 | 0 | 0 | 2.8159 | 0 | 49.684 | 49.684 | 2.4719e-05
PA_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 891204.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569249.4841 | 0 | 0 | 1460453.4875 | 0 | 1460453.4875 | 0 | 0 | 8037.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5134.0611 | 0 | 0 | 13171.83 | 0 | 13171.83 | 0 | 0 | 891.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.2495 | 0 | 0 | 1460.4535 | 0 | 1460.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7875 | 1.1417 | 0 | 0 | 2.9292 | 2.9292 | 0
PA_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 24890.4003 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20844.8073 | 0 | 0 | 0 | 0 | 114129.6265 | 0 | 0 | 337448.5879 | 0 | 337444.9757 | 3.6121 | 3.6121 | 0 | 2115.684 | 2411.8515 | 612.41 | 12070.3576 | 0 | 1771.8086 | 0 | 0 | 0 | 0 | 9701.0183 | 0 | 0 | 28683.13 | 0 | 28682.8229 | 0.30703 | 0.30703 | 0 | 84.926 | 96.8146 | 24.5829 | 484.5184 | 0 | 71.1225 | 0 | 0 | 0 | 0 | 389.4103 | 0 | 0 | 1151.3746 | 0 | 1151.3623 | 0.012325 | 0.012325 | 2.8693 | 0.72858 | 14.3599 | 2.1079 | 0 | 0 | 2.517 | 0 | 11.5412 | 0 | 0 | 34.1235 | 34.1239 | 0.00036527
PA_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 113311.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113311.5367 | 0 | 113311.5367 | 0 | 0 | 1021.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.9567 | 0 | 1021.9567 | 0 | 0 | 113.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3115 | 0 | 113.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3583 | 0 | 0 | 0 | 3.3583 | 3.3583 | 0
PA_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 23770.638 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 20252.9725 | 0 | 0 | 0 | 0 | 114165.7478 | 0 | 0 | 330579.971 | 0 | 330578.8596 | 1.1114 | 1.1114 | 0 | 2020.5042 | 1970.4345 | 612.41 | 12070.3576 | 0 | 1721.5027 | 0 | 0 | 0 | 0 | 9704.0886 | 0 | 0 | 28099.2975 | 0 | 28099.2031 | 0.094471 | 0.094471 | 0 | 81.1054 | 79.0956 | 24.5829 | 484.5184 | 0 | 69.1031 | 0 | 0 | 0 | 0 | 389.5335 | 0 | 0 | 1127.9389 | 0 | 1127.9351 | 0.0037922 | 0.0037922 | 2.3442 | 0.72858 | 14.3599 | 2.048 | 0 | 0 | 2.4038 | 0 | 11.5448 | 0 | 0 | 33.4292 | 33.4293 | 0.00011239
PA_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 128675.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128675.6522 | 0 | 128675.6522 | 0 | 0 | 1160.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160.5257 | 0 | 1160.5257 | 0 | 0 | 128.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.6757 | 0 | 128.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8136 | 0 | 0 | 0 | 3.8136 | 3.8136 | 0
PA_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 92090.0356 | 96696.8991 | 7113.1307 | 317887.4784 | 4818.0346 | 91459.3009 | 914.1484 | 0 | 0 | 21833.977 | 7179.8163 | 17602.2199 | 0 | 657595.041 | 0 | 657596.4303 | -1.3893 | 4816.6453 | 0 | 7827.653 | 8219.2364 | 604.6161 | 27020.4357 | 409.5329 | 7774.0406 | 77.7026 | 0 | 0 | 1855.888 | 610.2844 | 1496.1887 | 0 | 55895.5785 | 0 | 55895.6966 | -0.11809 | 409.4149 | 0 | 314.2112 | 329.9298 | 24.27 | 1084.6321 | 16.4391 | 312.0591 | 3.1191 | 0 | 0 | 74.4975 | 24.4975 | 60.0588 | 0 | 2243.7143 | 0 | 2243.719 | -0.0047402 | 16.4344 | 4.461 | 0.32815 | 14.6653 | 4.2194 | 0.042173 | 1.0073 | 4.2485 | 0 | 0.33123 | 0 | 0.81205 | 30.3373 | 30.3373 | -6.4093e-05
PA_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 442725.3768 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118970.0049 | 0 | 0 | 903885.7965 | 0 | 903885.7965 | 0 | 0 | 3992.9402 | 0 | 0 | 0 | 3086.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 1072.9905 | 0 | 0 | 8152.146 | 0 | 8152.146 | 0 | 0 | 442.7254 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.97 | 0 | 0 | 903.8858 | 0 | 903.8858 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.9861 | 1.6086 | 0 | 0 | 12.2214 | 12.2214 | 0
PA_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 87219.2082 | 78672.337 | 7113.1307 | 312483.1662 | 4743.0133 | 78577.8658 | 555.7133 | 0 | 0 | 22659.2113 | 7179.8163 | 12478.543 | 0 | 611682.0052 | 0 | 611683.3944 | -1.3893 | 4741.624 | 0 | 7413.6327 | 6687.1486 | 604.6161 | 26561.0691 | 403.1561 | 6679.1186 | 47.2356 | 0 | 0 | 1926.033 | 610.2844 | 1060.6762 | 0 | 51992.9704 | 0 | 51993.0885 | -0.11809 | 403.038 | 0 | 297.5919 | 268.43 | 24.27 | 1066.1926 | 16.1832 | 268.1077 | 1.8961 | 0 | 0 | 77.3132 | 24.4975 | 42.5768 | 0 | 2087.059 | 0 | 2087.0637 | -0.0047402 | 16.1784 | 3.6294 | 0.32815 | 14.416 | 3.6251 | 0.025637 | 1.0454 | 4.0237 | 0 | 0.33123 | 0 | 0.57568 | 28.2192 | 28.2191 | -6.4093e-05
PA_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 426223.8807 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118733.0506 | 0 | 0 | 887147.3461 | 0 | 887147.3461 | 0 | 0 | 3844.1132 | 0 | 0 | 0 | 3086.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.8534 | 0 | 0 | 8001.1819 | 0 | 8001.1819 | 0 | 0 | 426.2239 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.7331 | 0 | 0 | 887.1473 | 0 | 887.1473 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.763 | 1.6054 | 0 | 0 | 11.9951 | 11.9951 | 0
PA_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 31661.7673 | 83362.5576 | 10680.8103 | 53987.5506 | 0 | 43320.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223013.3191 | 0 | 223013.0412 | 0.27786 | 0.27786 | 0 | 2691.2502 | 7085.8174 | 907.8689 | 4588.9418 | 0 | 3682.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18956.1321 | 0 | 18956.1085 | 0.023618 | 0.023618 | 0 | 108.03 | 284.433 | 36.4429 | 184.2055 | 0 | 147.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.9214 | 0 | 760.9205 | 0.00094805 | 0.00094805 | 11.5192 | 1.4759 | 7.4601 | 5.9861 | 0 | 0 | 4.3751 | 0 | 0 | 0 | 0 | 30.8165 | 30.8165 | 3.8395e-05
PA_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 420129.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90620.7948 | 0 | 0 | 510750.2115 | 0 | 510750.2115 | 0 | 0 | 3789.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 817.3089 | 0 | 0 | 4606.4562 | 0 | 4606.4562 | 0 | 0 | 420.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6208 | 0 | 0 | 510.7502 | 0 | 510.7502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0148 | 3.67 | 0 | 0 | 20.6848 | 20.6848 | 0
PA_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 0 | 29391.6784 | 65874.2589 | 10680.8103 | 53987.5506 | 0 | 41336.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201271.0348 | 0 | 201271.0348 | 0 | 0 | 0 | 2498.2927 | 5599.312 | 907.8689 | 4588.9418 | 0 | 3513.6226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17108.038 | 0 | 17108.038 | 0 | 0 | 0 | 100.2844 | 224.763 | 36.4429 | 184.2055 | 0 | 141.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 686.7368 | 0 | 686.7368 | 0 | 0 | 9.1027 | 1.4759 | 7.4601 | 5.712 | 0 | 0 | 4.0614 | 0 | 0 | 0 | 0 | 27.8121 | 27.8121 | 0
PA_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 448601.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90630.273 | 0 | 0 | 539232.1159 | 0 | 539232.1159 | 0 | 0 | 4045.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 817.3944 | 0 | 0 | 4863.3345 | 0 | 4863.3345 | 0 | 0 | 448.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6303 | 0 | 0 | 539.2321 | 0 | 539.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1679 | 3.6704 | 0 | 0 | 21.8383 | 21.8383 | 0
PA_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 29458.364 | 65112.9316 | 79075.2292 | 12303.4933 | 154949.5496 | 0 | 45676.8577 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 386648.6681 | 0 | 386646.7231 | 1.945 | 1.945 | 2503.9609 | 5534.5992 | 6721.3945 | 1045.7969 | 13170.7117 | 0 | 3882.5329 | 6.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 32865.1368 | 0 | 32864.9715 | 0.16532 | 0.16532 | 100.5119 | 222.1653 | 269.8047 | 41.9795 | 528.6879 | 0 | 155.8494 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1319.2453 | 0 | 1319.2386 | 0.0066363 | 0.0066363 | 6.2452 | 0.9717 | 12.2376 | 3.6075 | 0.0057056 | 0 | 5.1425 | 2.3266 | 0 | 0 | 0 | 30.5365 | 30.5367 | 0.00015361
PA_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 69825.6872 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594072.8145 | 0 | 0 | 1063393.9396 | 0 | 1063393.9396 | 0 | 0 | 629.7579 | 0 | 0 | 0 | 3603.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5357.9427 | 0 | 0 | 9590.7499 | 0 | 9590.7499 | 0 | 0 | 69.8257 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.0728 | 0 | 0 | 1063.3939 | 0 | 1063.3939 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6163 | 13.751 | 0 | 0 | 24.6145 | 24.6145 | 0
PA_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 33556.7498 | 60600.5393 | 50725.5134 | 12303.4933 | 154949.5496 | 0 | 43242.8333 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 355450.9214 | 0 | 355448.9764 | 1.945 | 1.945 | 2852.3237 | 5151.0458 | 4311.6686 | 1045.7969 | 13170.7117 | 0 | 3675.6408 | 6.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 30213.3283 | 0 | 30213.163 | 0.16532 | 0.16532 | 114.4956 | 206.769 | 173.0755 | 41.9795 | 528.6879 | 0 | 147.5445 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.7985 | 0 | 1212.7919 | 0.0066363 | 0.0066363 | 4.0062 | 0.9717 | 12.2376 | 3.4152 | 0.0057056 | 0 | 4.7861 | 2.6502 | 0 | 0 | 0 | 28.0726 | 28.0727 | 0.00015361
PA_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 68953.6955 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594129.6835 | 0 | 0 | 1062578.8169 | 0 | 1062578.8169 | 0 | 0 | 621.8934 | 0 | 0 | 0 | 3603.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5358.4556 | 0 | 0 | 9583.3983 | 0 | 9583.3983 | 0 | 0 | 68.9537 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.1297 | 0 | 0 | 1062.5788 | 0 | 1062.5788 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5961 | 13.7524 | 0 | 0 | 24.5956 | 24.5956 | 0
PA_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 3428.7513 | 3556.5654 | 8810.8349 | 1586.5616 | 13417.6985 | 0 | 4876.3845 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40680.9948 | 0 | 40680.7169 | 0.27786 | 0.27786 | 291.4439 | 302.3081 | 748.921 | 134.8577 | 1140.5044 | 0 | 414.4927 | 0 | 0 | 0 | 0 | 425.3569 | 0 | 0 | 3457.8846 | 0 | 3457.8609 | 0.023618 | 0.023618 | 11.6989 | 12.135 | 30.0626 | 5.4133 | 45.7812 | 0 | 16.6382 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8036 | 0 | 138.8026 | 0.00094805 | 0.00094805 | 5.4639 | 0.98389 | 8.3208 | 3.024 | 0 | 0 | 2.2056 | 2.1263 | 3.1033 | 0 | 0 | 25.2277 | 25.2278 | 0.00017231
PA_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 8028.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.011 | 0 | 8028.011 | 0 | 0 | 72.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.4046 | 0 | 72.4046 | 0 | 0 | 8.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.028 | 0 | 8.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 0 | 0 | 0 | 1.4591 | 1.4591 | 0
PA_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Electricity | 3470.4298 | 3348.1729 | 7102.0164 | 1586.5616 | 13417.6985 | 0 | 4473.4924 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38402.5701 | 0 | 38406.738 | -4.1679 | -4.1679 | 294.9865 | 284.5947 | 603.6714 | 134.8577 | 1140.5044 | 0 | 380.2469 | 0 | 0 | 0 | 0 | 425.3569 | 0 | 0 | 3264.2185 | 0 | 3264.5727 | -0.35427 | -0.35427 | 11.8411 | 11.424 | 24.2321 | 5.4133 | 45.7812 | 0 | 15.2636 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.0296 | 0 | 131.0438 | -0.014221 | -0.014221 | 4.4042 | 0.98389 | 8.3208 | 2.7742 | 0 | 0 | 2.0763 | 2.1521 | 3.1033 | 0 | 0 | 23.8175 | 23.8149 | -0.0025846
PA_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | PA-PITTSBURGH-PA | Zone5A | Zone5A(PA-PITTSBURGH-PA) |  |  | PA | 0.085 | 0.009019 |  |  |  | Natural Gas | 8407.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8407.1379 | 0 | 8407.1379 | 0 | 0 | 75.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.824 | 0 | 75.824 | 0 | 0 | 8.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4071 | 0 | 8.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.528 | 0 | 0 | 0 | 1.528 | 1.528 | 0
RI_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 567561.1448 | 881675.3297 | 95930.0147 | 4077910.5986 | 543457.0788 | 573515.6132 | 85465.9326 | 196375.2003 | 386837.6107 | 11172.6166 | 0 | 0 | 0 | 7419901.14 | 0 | 7419901.9736 | -0.83357 | 543456.2453 | 0 | 90526.0026 | 140627.2151 | 15300.8373 | 650426.7405 | 86681.4041 | 91475.7403 | 13631.8162 | 31321.8444 | 61700.5989 | 1782.0324 | 0 | 0 | 0 | 1183474.2318 | 0 | 1183474.3648 | -0.13295 | 86681.2711 | 0 | 1936.5186 | 3008.2762 | 327.3132 | 13913.831 | 1854.2756 | 1956.8353 | 291.6098 | 670.0322 | 1319.8899 | 38.121 | 0 | 0 | 0 | 25316.7027 | 0 | 25316.7055 | -0.0028441 | 1854.2727 | 6.0336 | 0.65648 | 27.9065 | 3.9248 | 0.58487 | 0.076458 | 3.884 | 0 | 0 | 2.6473 | 0 | 50.7768 | 50.7768 | -5.7044e-06
RI_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 889061.9367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569638.0891 | 0 | 0 | 1458700.0259 | 0 | 1458700.0259 | 0 | 0 | 10704.3057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6858.4426 | 0 | 0 | 17562.7483 | 0 | 17562.7483 | 0 | 0 | 889.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.6381 | 0 | 0 | 1458.7 | 0 | 1458.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7832 | 1.1425 | 0 | 0 | 2.9257 | 2.9257 | 0
RI_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 531584.2634 | 717962.1808 | 95930.0147 | 4077910.5986 | 543387.6147 | 556269.0498 | 81625.9534 | 176516.7842 | 386601.4325 | 10441.8536 | 0 | 0 | 0 | 7178229.7457 | 0 | 7178229.19 | 0.55571 | 543388.1704 | 0 | 84787.69 | 114514.9678 | 15300.8373 | 650426.7405 | 86670.3245 | 88724.9134 | 13019.3396 | 28154.4271 | 61662.9285 | 1665.4756 | 0 | 0 | 0 | 1144927.6444 | 0 | 1144927.5558 | 0.088636 | 86670.4132 | 0 | 1813.7655 | 2449.687 | 327.3132 | 13913.831 | 1854.0385 | 1897.99 | 278.5078 | 602.2753 | 1319.0841 | 35.6276 | 0 | 0 | 0 | 24492.1199 | 0 | 24492.118 | 0.0018961 | 1854.0404 | 4.9132 | 0.65648 | 27.9065 | 3.8067 | 0.55859 | 0.071457 | 3.6378 | 0 | 0 | 2.6456 | 0 | 49.123 | 49.123 | 3.8029e-06
RI_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 808184.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569590.6983 | 0 | 0 | 1377775.4001 | 0 | 1377775.4001 | 0 | 0 | 9730.5438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6857.872 | 0 | 0 | 16588.4158 | 0 | 16588.4158 | 0 | 0 | 808.1847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.5907 | 0 | 0 | 1377.7754 | 0 | 1377.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6209 | 1.1424 | 0 | 0 | 2.7634 | 2.7634 | 0
RI_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 23870.6664 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 19980.673 | 0 | 0 | 0 | 0 | 114237.9906 | 0 | 0 | 335670.3052 | 0 | 335670.5831 | -0.27786 | -0.27786 | 0 | 3807.3713 | 4525.7683 | 1148.7262 | 22649.6711 | 0 | 3186.9173 | 0 | 0 | 0 | 0 | 18220.9595 | 0 | 0 | 53539.4137 | 0 | 53539.458 | -0.044318 | -0.044318 | 0 | 81.4467 | 96.8146 | 24.5734 | 484.5184 | 0 | 68.1741 | 0 | 0 | 0 | 0 | 389.78 | 0 | 0 | 1145.3071 | 0 | 1145.308 | -0.00094805 | -0.00094805 | 2.8693 | 0.72829 | 14.3599 | 2.0205 | 0 | 0 | 2.4139 | 0 | 11.5521 | 0 | 0 | 33.9441 | 33.9441 | -2.8098e-05
RI_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 106942.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106942.2056 | 0 | 106942.2056 | 0 | 0 | 1287.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.5842 | 0 | 1287.5842 | 0 | 0 | 106.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9422 | 0 | 106.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1695 | 0 | 0 | 0 | 3.1695 | 3.1695 | 0
RI_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 22787.0254 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 19436.0739 | 0 | 0 | 0 | 0 | 114271.3334 | 0 | 0 | 328882.2668 | 0 | 328882.2668 | 0 | 0 | 0 | 3634.5305 | 3697.4623 | 1148.7262 | 22649.6711 | 0 | 3100.0538 | 0 | 0 | 0 | 0 | 18226.2777 | 0 | 0 | 52456.7216 | 0 | 52456.7216 | 0 | 0 | 0 | 77.7493 | 79.0956 | 24.5734 | 484.5184 | 0 | 66.3159 | 0 | 0 | 0 | 0 | 389.8938 | 0 | 0 | 1122.1463 | 0 | 1122.1463 | 0 | 0 | 2.3442 | 0.72829 | 14.3599 | 1.9654 | 0 | 0 | 2.3043 | 0 | 11.5555 | 0 | 0 | 33.2576 | 33.2576 | 0
RI_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 123510.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123510.0489 | 0 | 123510.0489 | 0 | 0 | 1487.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1487.061 | 0 | 1487.061 | 0 | 0 | 123.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.51 | 0 | 123.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6605 | 0 | 0 | 0 | 3.6605 | 3.6605 | 0
RI_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 85910.5033 | 98389.0462 | 7146.4735 | 317887.4784 | 4818.0346 | 89894.9679 | 780.7772 | 0 | 0 | 20597.5148 | 7179.8163 | 17624.4485 | 0 | 650229.0607 | 0 | 650229.6165 | -0.55571 | 4817.4789 | 0 | 13702.7253 | 15693.0529 | 1139.8625 | 50703.0528 | 768.4765 | 14338.2474 | 124.534 | 0 | 0 | 3285.3036 | 1145.1807 | 2811.0995 | 0 | 103711.5352 | 0 | 103711.6238 | -0.088636 | 768.3879 | 0 | 293.1266 | 335.7034 | 24.3838 | 1084.6321 | 16.4391 | 306.7216 | 2.664 | 0 | 0 | 70.2787 | 24.4975 | 60.1346 | 0 | 2218.5816 | 0 | 2218.5835 | -0.0018961 | 16.4372 | 4.539 | 0.32969 | 14.6653 | 4.1472 | 0.03602 | 0.95024 | 3.9634 | 0 | 0.33123 | 0 | 0.81308 | 29.9975 | 29.9975 | -2.5637e-05
RI_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 412110.8838 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119055.3084 | 0 | 0 | 873356.6071 | 0 | 873356.6071 | 0 | 0 | 4961.815 | 0 | 0 | 0 | 4119.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.4259 | 0 | 0 | 10515.2135 | 0 | 10515.2135 | 0 | 0 | 412.1109 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.0553 | 0 | 0 | 873.3566 | 0 | 873.3566 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.5722 | 1.6097 | 0 | 0 | 11.8087 | 11.8087 | 0
RI_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 81831.5674 | 80289.4629 | 7146.4735 | 312483.1662 | 4745.7919 | 77988.8096 | 497.3634 | 0 | 0 | 22506.3901 | 7179.8163 | 12492.4358 | 0 | 607161.2772 | 0 | 607163.2222 | -1.945 | 4743.8469 | 0 | 13052.135 | 12806.1693 | 1139.8625 | 49841.065 | 756.9538 | 12439.2151 | 79.3295 | 0 | 0 | 3589.7692 | 1145.1807 | 1992.5435 | 0 | 96842.2237 | 0 | 96842.5339 | -0.31023 | 756.6436 | 0 | 279.2093 | 273.9476 | 24.3838 | 1066.1926 | 16.1926 | 266.0978 | 1.697 | 0 | 0 | 76.7918 | 24.4975 | 42.6242 | 0 | 2071.6343 | 0 | 2071.6409 | -0.0066363 | 16.186 | 3.704 | 0.32969 | 14.416 | 3.5979 | 0.022945 | 1.0383 | 3.7752 | 0 | 0.33123 | 0 | 0.57632 | 28.0107 | 28.0106 | -8.973e-05
RI_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 394557.3107 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 118770.9633 | 0 | 0 | 855518.6889 | 0 | 855518.6889 | 0 | 0 | 4750.47 | 0 | 0 | 0 | 4119.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.0024 | 0 | 0 | 10300.445 | 0 | 10300.445 | 0 | 0 | 394.5573 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 118.771 | 0 | 0 | 855.5187 | 0 | 855.5187 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.3348 | 1.6059 | 0 | 0 | 11.5675 | 11.5675 | 0
RI_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 30705.9404 | 84699.0482 | 10789.1744 | 53987.5506 | 0 | 42267.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222449.27 | 0 | 222444.8243 | 4.4457 | 4.4457 | 0 | 4897.5975 | 13509.4982 | 1720.8733 | 8611.0143 | 0 | 6741.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35480.6586 | 0 | 35479.9495 | 0.70909 | 0.70909 | 0 | 104.7687 | 288.9932 | 36.8127 | 184.2055 | 0 | 144.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.9969 | 0 | 758.9817 | 0.015169 | 0.015169 | 11.7039 | 1.4909 | 7.4601 | 5.8406 | 0 | 0 | 4.243 | 0 | 0 | 0 | 0 | 30.738 | 30.7386 | 0.00061432
RI_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 422726.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90649.2294 | 0 | 0 | 513375.6649 | 0 | 513375.6649 | 0 | 0 | 5089.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.4167 | 0 | 0 | 6181.043 | 0 | 6181.043 | 0 | 0 | 422.7264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6492 | 0 | 0 | 513.3757 | 0 | 513.3757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.12 | 3.6712 | 0 | 0 | 20.7912 | 20.7912 | 0
RI_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 0 | 28513.6513 | 67088.4925 | 10789.1744 | 53987.5506 | 0 | 40442.0381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200820.907 | 0 | 200821.1848 | -0.27786 | -0.27786 | 0 | 4547.9274 | 10700.6146 | 1720.8733 | 8611.0143 | 0 | 6450.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32030.9347 | 0 | 32030.979 | -0.044318 | -0.044318 | 0 | 97.2886 | 228.9059 | 36.8127 | 184.2055 | 0 | 137.9882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.2009 | 0 | 685.2019 | -0.00094805 | -0.00094805 | 9.2704 | 1.4909 | 7.4601 | 5.5884 | 0 | 0 | 3.9401 | 0 | 0 | 0 | 0 | 27.75 | 27.7499 | -3.8395e-05
RI_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 452194.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90658.7075 | 0 | 0 | 542852.7773 | 0 | 542852.7773 | 0 | 0 | 5444.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.5308 | 0 | 0 | 6535.9474 | 0 | 6535.9474 | 0 | 0 | 452.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6587 | 0 | 0 | 542.8528 | 0 | 542.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3134 | 3.6716 | 0 | 0 | 21.985 | 21.985 | 0
RI_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 29400.0141 | 63579.1628 | 79136.3577 | 12300.7147 | 154949.5496 | 0 | 45193.3871 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 384631.4287 | 0 | 384631.9844 | -0.55571 | -0.55571 | 4689.3022 | 10140.8765 | 12622.2491 | 1961.964 | 24714.4532 | 0 | 7208.3452 | 11.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 61348.7129 | 0 | 61348.8015 | -0.088636 | -0.088636 | 100.3128 | 216.9321 | 270.0133 | 41.97 | 528.6879 | 0 | 154.1998 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.3624 | 0 | 1312.3643 | -0.0018961 | -0.0018961 | 6.25 | 0.97148 | 12.2376 | 3.5693 | 0.0057056 | 0 | 5.0213 | 2.3219 | 0 | 0 | 0 | 30.3774 | 30.3774 | -4.3889e-05
RI_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 74280.4277 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594660.4611 | 0 | 0 | 1068436.3267 | 0 | 1068436.3267 | 0 | 0 | 894.3363 | 0 | 0 | 0 | 4809.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 7159.712 | 0 | 0 | 12863.9734 | 0 | 12863.9734 | 0 | 0 | 74.2804 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.6605 | 0 | 0 | 1068.4363 | 0 | 1068.4363 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.7194 | 13.7647 | 0 | 0 | 24.7312 | 24.7312 | 0
RI_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 33773.478 | 59152.9061 | 50772.749 | 12300.7147 | 154949.5496 | 0 | 42823.2697 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 353844.9099 | 0 | 353846.577 | -1.6671 | -1.6671 | 5386.8697 | 9434.8885 | 8098.2535 | 1961.964 | 24714.4532 | 0 | 6830.3115 | 11.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 56438.2631 | 0 | 56438.529 | -0.26591 | -0.26591 | 115.2351 | 201.8297 | 173.2366 | 41.97 | 528.6879 | 0 | 146.113 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.3188 | 0 | 1207.3245 | -0.0056883 | -0.0056883 | 4.0099 | 0.97148 | 12.2376 | 3.3821 | 0.0057056 | 0 | 4.6718 | 2.6674 | 0 | 0 | 0 | 27.946 | 27.9459 | -0.00013167
RI_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 73380.0014 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 594736.2865 | 0 | 0 | 1067611.7258 | 0 | 1067611.7258 | 0 | 0 | 883.4952 | 0 | 0 | 0 | 4809.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 7160.6249 | 0 | 0 | 12854.0452 | 0 | 12854.0452 | 0 | 0 | 73.38 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 594.7363 | 0 | 0 | 1067.6117 | 0 | 1067.6117 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6985 | 13.7664 | 0 | 0 | 24.7121 | 24.7121 | 0
RI_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 3714.9437 | 3489.8798 | 8824.7278 | 1583.783 | 13417.6985 | 0 | 4595.7493 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40630.9806 | 0 | 40630.4249 | 0.55571 | 0.55571 | 592.5335 | 556.6358 | 1407.5441 | 252.6134 | 2140.1229 | 0 | 733.022 | 0 | 0 | 0 | 0 | 798.1697 | 0 | 0 | 6480.6414 | 0 | 6480.5528 | 0.088636 | 0.088636 | 12.6754 | 11.9075 | 30.11 | 5.4039 | 45.7812 | 0 | 15.6807 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.6329 | 0 | 138.631 | 0.0018961 | 0.0018961 | 5.4726 | 0.98216 | 8.3208 | 2.85 | 0 | 0 | 2.1642 | 2.3038 | 3.1033 | 0 | 0 | 25.1965 | 25.1968 | 0.00034462
RI_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 4274.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4274.6552 | 0 | 4274.6552 | 0 | 0 | 51.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.4668 | 0 | 51.4668 | 0 | 0 | 4.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2747 | 0 | 4.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77693 | 0 | 0 | 0 | 0.77693 | 0.77693 | 0
RI_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Electricity | 3773.2936 | 3292.6015 | 7115.9093 | 1583.783 | 13417.6985 | 0 | 4212.3071 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38399.7916 | 0 | 38401.1808 | -1.3893 | -1.3893 | 601.8403 | 525.1699 | 1134.9875 | 252.6134 | 2140.1229 | 0 | 671.863 | 0 | 0 | 0 | 0 | 798.1697 | 0 | 0 | 6124.7668 | 0 | 6124.9883 | -0.22159 | -0.22159 | 12.8745 | 11.2344 | 24.2795 | 5.4039 | 45.7812 | 0 | 14.3724 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.0201 | 0 | 131.0248 | -0.0047402 | -0.0047402 | 4.4128 | 0.98216 | 8.3208 | 2.6122 | 0 | 0 | 2.0419 | 2.34 | 3.1033 | 0 | 0 | 23.814 | 23.8132 | -0.00086155
RI_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | RI-PROVIDENCE-RI | Zone5A | Zone5A(RI-PROVIDENCE-RI) |  |  | RI | 0.1595 | 0.01204 |  |  |  | Natural Gas | 4644.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644.3039 | 0 | 4644.3039 | 0 | 0 | 55.9174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9174 | 0 | 55.9174 | 0 | 0 | 4.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6443 | 0 | 4.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84411 | 0 | 0 | 0 | 0.84411 | 0.84411 | 0
SC_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 1027719.5731 | 881353.016 | 95268.7158 | 4077910.5986 | 543457.0788 | 561217.6771 | 134549.313 | 380538.6 | 190784.7241 | 13320.4487 | 0 | 0 | 0 | 7906119.7452 | 0 | 7906119.1895 | 0.55571 | 543457.6346 | 0 | 105238.4843 | 90250.5488 | 9755.5165 | 417578.0453 | 55650.0049 | 57468.6901 | 13777.8497 | 38967.1526 | 19536.3557 | 1364.0139 | 0 | 0 | 0 | 809586.6619 | 0 | 809586.605 | 0.056905 | 55650.0618 | 0 | 3506.5792 | 3007.1765 | 325.0569 | 13913.831 | 1854.2756 | 1914.8747 | 459.0823 | 1298.3977 | 650.9575 | 45.4494 | 0 | 0 | 0 | 26975.6806 | 0 | 26975.6787 | 0.0018961 | 1854.2774 | 6.0314 | 0.65195 | 27.9065 | 3.8406 | 0.92076 | 0.091156 | 7.033 | 0 | 0 | 1.3056 | 0 | 54.1041 | 54.1042 | 3.8029e-06
SC_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 451246.2527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483737.4235 | 0 | 0 | 934983.6762 | 0 | 934983.6762 | 0 | 0 | 3757.5275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.0815 | 0 | 0 | 7785.6091 | 0 | 7785.6091 | 0 | 0 | 451.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.7374 | 0 | 0 | 934.9837 | 0 | 934.9837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90505 | 0.97021 | 0 | 0 | 1.8753 | 1.8753 | 0
SC_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 972781.7526 | 716900.7683 | 95268.7158 | 4077910.5986 | 543384.8361 | 547002.5299 | 130528.727 | 344225.512 | 190743.0456 | 12578.5714 | 0 | 0 | 0 | 7631325.0575 | 0 | 7631327.5582 | -2.5007 | 543382.3354 | 0 | 99612.8515 | 73410.6387 | 9755.5165 | 417578.0453 | 55642.6072 | 56013.0591 | 13366.1416 | 35248.6924 | 19532.0879 | 1288.0457 | 0 | 0 | 0 | 781447.6859 | 0 | 781447.942 | -0.25607 | 55642.3511 | 0 | 3319.1313 | 2446.0654 | 325.0569 | 13913.831 | 1854.0291 | 1866.3726 | 445.364 | 1174.4974 | 650.8153 | 42.9181 | 0 | 0 | 0 | 26038.0811 | 0 | 26038.0896 | -0.0085324 | 1854.0205 | 4.906 | 0.65195 | 27.9065 | 3.7433 | 0.89325 | 0.086079 | 6.6571 | 0 | 0 | 1.3053 | 0 | 52.2237 | 52.2236 | -1.7113e-05
SC_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 284117.6599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483718.4672 | 0 | 0 | 767836.1271 | 0 | 767836.1271 | 0 | 0 | 2365.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.9237 | 0 | 0 | 6393.7714 | 0 | 6393.7714 | 0 | 0 | 284.1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.7185 | 0 | 0 | 767.8361 | 0 | 767.8361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56984 | 0.97018 | 0 | 0 | 1.54 | 1.54 | 0
SC_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 48274.8175 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 22775.9111 | 0 | 0 | 0 | 0 | 97269.2839 | 0 | 0 | 345912.102 | 0 | 345910.157 | 1.945 | 1.945 | 0 | 4943.3413 | 2905.5716 | 738.6275 | 14541.2308 | 0 | 2332.2533 | 0 | 0 | 0 | 0 | 9960.3747 | 0 | 0 | 35421.3992 | 0 | 35421.2001 | 0.19917 | 0.19917 | 0 | 164.7137 | 96.8146 | 24.6113 | 484.5184 | 0 | 77.7114 | 0 | 0 | 0 | 0 | 331.8828 | 0 | 0 | 1180.2521 | 0 | 1180.2455 | 0.0066363 | 0.0066363 | 2.8693 | 0.72942 | 14.3599 | 2.3032 | 0 | 0 | 4.8817 | 0 | 9.8362 | 0 | 0 | 34.9796 | 34.9798 | 0.00019668
SC_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 48869.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48869.4507 | 0 | 48869.4507 | 0 | 0 | 406.9359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.9359 | 0 | 406.9359 | 0 | 0 | 48.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8695 | 0 | 48.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4484 | 0 | 0 | 0 | 1.4484 | 1.4484 | 0
SC_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 44632.1166 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 22222.9763 | 0 | 0 | 0 | 0 | 97138.6912 | 0 | 0 | 336392.7325 | 0 | 336394.6775 | -1.945 | -1.945 | 0 | 4570.3287 | 2373.794 | 738.6275 | 14541.2308 | 0 | 2275.6328 | 0 | 0 | 0 | 0 | 9947.002 | 0 | 0 | 34446.6158 | 0 | 34446.815 | -0.19917 | -0.19917 | 0 | 152.2848 | 79.0956 | 24.6113 | 484.5184 | 0 | 75.8248 | 0 | 0 | 0 | 0 | 331.4372 | 0 | 0 | 1147.772 | 0 | 1147.7786 | -0.0066363 | -0.0066363 | 2.3442 | 0.72942 | 14.3599 | 2.2473 | 0 | 0 | 4.5133 | 0 | 9.823 | 0 | 0 | 34.0173 | 34.0171 | -0.00019668
SC_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 10899.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10899.8969 | 0 | 10899.8969 | 0 | 0 | 90.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7634 | 0 | 90.7634 | 0 | 0 | 10.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8999 | 0 | 10.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32305 | 0 | 0 | 0 | 0.32305 | 0.32305 | 0
SC_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 198386.8826 | 99542.1514 | 7107.5736 | 317887.4784 | 4818.0346 | 93451.5332 | 286.1924 | 0 | 0 | 23453.8814 | 7179.8163 | 17705.0269 | 0 | 769818.5708 | 0 | 769818.8486 | -0.27786 | 4817.7568 | 0 | 20314.8168 | 10193.1163 | 727.8155 | 32551.6778 | 493.3667 | 9569.437 | 29.3061 | 0 | 0 | 2401.6775 | 735.2132 | 1812.9948 | 0 | 78829.4216 | 0 | 78829.4501 | -0.028453 | 493.3383 | 0 | 676.896 | 339.6378 | 24.251 | 1084.6321 | 16.4391 | 318.8566 | 0.97649 | 0 | 0 | 80.0246 | 24.4975 | 60.4096 | 0 | 2626.621 | 0 | 2626.6219 | -0.00094805 | 16.4382 | 4.5922 | 0.3279 | 14.6653 | 4.3113 | 0.013203 | 1.082 | 9.1523 | 0 | 0.33123 | 0 | 0.8168 | 35.5146 | 35.5146 | -1.2819e-05
SC_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 158001.1139 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 101672.3425 | 0 | 0 | 601863.8712 | 0 | 601863.8712 | 0 | 0 | 1315.6753 | 0 | 0 | 0 | 2849.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 846.6256 | 0 | 0 | 5011.7205 | 0 | 5011.7205 | 0 | 0 | 158.0011 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6723 | 0 | 0 | 601.8639 | 0 | 601.8639 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.1363 | 1.3747 | 0 | 0 | 8.1378 | 8.1378 | 0
SC_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 183654.922 | 80144.9774 | 7107.5736 | 312483.1662 | 4745.7919 | 83018.0153 | 227.8425 | 0 | 0 | 22820.3682 | 7179.8163 | 12528.5572 | 0 | 713911.0305 | 0 | 713913.2534 | -2.2229 | 4743.569 | 0 | 18806.264 | 8206.8457 | 727.8155 | 31998.2762 | 485.9691 | 8501.0448 | 23.3311 | 0 | 0 | 2336.8057 | 735.2132 | 1282.9243 | 0 | 73104.4895 | 0 | 73104.7171 | -0.22762 | 485.7415 | 0 | 626.6306 | 273.4547 | 24.251 | 1066.1926 | 16.1926 | 283.2575 | 0.7774 | 0 | 0 | 77.8631 | 24.4975 | 42.7474 | 0 | 2435.8644 | 0 | 2435.872 | -0.0075844 | 16.1851 | 3.6974 | 0.3279 | 14.416 | 3.8299 | 0.010511 | 1.0528 | 8.4727 | 0 | 0.33123 | 0 | 0.57799 | 32.9354 | 32.9353 | -0.00010255
SC_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 128884.172 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 101387.9973 | 0 | 0 | 572462.5841 | 0 | 572462.5841 | 0 | 0 | 1073.2185 | 0 | 0 | 0 | 2849.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 844.2579 | 0 | 0 | 4766.8959 | 0 | 4766.8959 | 0 | 0 | 128.8842 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 101.388 | 0 | 0 | 572.4626 | 0 | 572.4626 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.7426 | 1.3709 | 0 | 0 | 7.7403 | 7.7403 | 0
SC_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 74496.1513 | 82417.8449 | 10689.146 | 53987.5506 | 0 | 36954.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258545.6298 | 0 | 258542.5734 | 3.0564 | 3.0564 | 0 | 7628.4059 | 8439.5873 | 1094.5686 | 5528.3252 | 0 | 3784.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26475.0725 | 0 | 26474.7595 | 0.31298 | 0.31298 | 0 | 254.1809 | 281.2097 | 36.4714 | 184.2055 | 0 | 126.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882.1577 | 0 | 882.1473 | 0.010429 | 0.010429 | 11.3887 | 1.4771 | 7.4601 | 5.1065 | 0 | 0 | 10.2941 | 0 | 0 | 0 | 0 | 35.726 | 35.7265 | 0.00042234
SC_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 76602.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85464.6697 | 0 | 0 | 162067.2493 | 0 | 162067.2493 | 0 | 0 | 637.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.6643 | 0 | 0 | 1349.534 | 0 | 1349.534 | 0 | 0 | 76.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4647 | 0 | 0 | 162.0672 | 0 | 162.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1023 | 3.4612 | 0 | 0 | 6.5636 | 6.5636 | 0
SC_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 69950.4162 | 64965.6676 | 10689.146 | 53987.5506 | 0 | 35146.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234738.8705 | 0 | 234736.9255 | 1.945 | 1.945 | 0 | 7162.9226 | 6652.4844 | 1094.5686 | 5528.3252 | 0 | 3598.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24037.2603 | 0 | 24037.0612 | 0.19917 | 0.19917 | 0 | 238.6708 | 221.6629 | 36.4714 | 184.2055 | 0 | 119.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800.929 | 0 | 800.9224 | 0.0066363 | 0.0066363 | 8.9771 | 1.4771 | 7.4601 | 4.8566 | 0 | 0 | 9.6659 | 0 | 0 | 0 | 0 | 32.4365 | 32.4368 | 0.00026876
SC_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 88402.9028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85483.6261 | 0 | 0 | 173886.5288 | 0 | 173886.5288 | 0 | 0 | 736.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.8222 | 0 | 0 | 1447.9531 | 0 | 1447.9531 | 0 | 0 | 88.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4836 | 0 | 0 | 173.8865 | 0 | 173.8865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5802 | 3.462 | 0 | 0 | 7.0422 | 7.0422 | 0
SC_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 5621.0404 | 108603.0573 | 79906.0207 | 12317.3861 | 154949.5496 | 0 | 46215.8996 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 407685.1965 | 0 | 407686.5858 | -1.3893 | -1.3893 | 575.5945 | 11120.9531 | 8182.3765 | 1261.3003 | 15866.8339 | 0 | 4732.5081 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 41746.9641 | 0 | 41747.1064 | -0.14226 | -0.14226 | 19.179 | 370.5536 | 272.6393 | 42.0269 | 528.6879 | 0 | 157.6886 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.0219 | 0 | 1391.0266 | -0.0047402 | -0.0047402 | 6.3108 | 0.9728 | 12.2376 | 3.65 | 0.0057056 | 0 | 8.5772 | 0.44394 | 0 | 0 | 0 | 32.1982 | 32.1981 | -0.00010972
SC_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 13544.3066 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 496106.437 | 0 | 0 | 909146.1815 | 0 | 909146.1815 | 0 | 0 | 112.7834 | 0 | 0 | 0 | 3326.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 4131.0783 | 0 | 0 | 7570.4603 | 0 | 7570.4603 | 0 | 0 | 13.5443 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 496.1064 | 0 | 0 | 909.1462 | 0 | 909.1462 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.31351 | 11.4834 | 0 | 0 | 21.0441 | 21.0441 | 0
SC_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 6576.8673 | 102662.4818 | 51211.7625 | 12317.3861 | 154949.5496 | 0 | 43956.9249 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 371747.215 | 0 | 371746.6593 | 0.55571 | 0.55571 | 673.4712 | 10512.6381 | 5244.0845 | 1261.3003 | 15866.8339 | 0 | 4501.1891 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 38066.9148 | 0 | 38066.8579 | 0.056905 | 0.056905 | 22.4403 | 350.2844 | 174.7345 | 42.0269 | 528.6879 | 0 | 149.981 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.4015 | 0 | 1268.3996 | 0.0018961 | 0.0018961 | 4.0446 | 0.9728 | 12.2376 | 3.4716 | 0.0057056 | 0 | 8.1081 | 0.51943 | 0 | 0 | 0 | 29.3597 | 29.3598 | 4.3889e-05
SC_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 14842.8161 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 496096.9588 | 0 | 0 | 910435.2128 | 0 | 910435.2128 | 0 | 0 | 123.5961 | 0 | 0 | 0 | 3326.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.9994 | 0 | 0 | 7581.194 | 0 | 7581.194 | 0 | 0 | 14.8428 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 496.097 | 0 | 0 | 910.4352 | 0 | 910.4352 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.34357 | 11.4832 | 0 | 0 | 21.0739 | 21.0739 | 0
SC_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 611.2847 | 7541.03 | 8991.4418 | 1581.0044 | 13417.6985 | 0 | 5084.777 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42231.435 | 0 | 42231.435 | 0 | 0 | 62.5956 | 772.2015 | 920.7236 | 161.8949 | 1373.9723 | 0 | 520.6812 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4324.4989 | 0 | 4324.4989 | 0 | 0 | 2.0857 | 25.73 | 30.6788 | 5.3944 | 45.7812 | 0 | 17.3493 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.0937 | 0 | 144.0937 | 0 | 0 | 5.5759 | 0.98044 | 8.3208 | 3.1533 | 0 | 0 | 4.6765 | 0.37908 | 3.1033 | 0 | 0 | 26.1893 | 26.1893 | 0
SC_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 142.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.1726 | 0 | 142.1726 | 0 | 0 | 1.1839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1839 | 0 | 1.1839 | 0 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14217 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02584 | 0 | 0 | 0 | 0.02584 | 0.02584 | 0
SC_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 597.3918 | 7229.8305 | 7221.4948 | 1581.0044 | 13417.6985 | 0 | 4651.3206 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39702.9393 | 0 | 39701.2722 | 1.6671 | 1.6671 | 61.1729 | 740.3346 | 739.4811 | 161.8949 | 1373.9723 | 0 | 476.2952 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4065.581 | 0 | 4065.4103 | 0.17072 | 0.17072 | 2.0383 | 24.6682 | 24.6397 | 5.3944 | 45.7812 | 0 | 15.8703 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.4664 | 0 | 135.4607 | 0.0056883 | 0.0056883 | 4.4783 | 0.98044 | 8.3208 | 2.8845 | 0 | 0 | 4.4835 | 0.37047 | 3.1033 | 0 | 0 | 24.6203 | 24.6213 | 0.0010339
SC_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | SC-BEAUFORT-SC | Zone2A | Zone2A(SC-BEAUFORT-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 142.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.1726 | 0 | 142.1726 | 0 | 0 | 1.1839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1839 | 0 | 1.1839 | 0 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14217 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02584 | 0 | 0 | 0 | 0.02584 | 0.02584 | 0
SC_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 956880.0155 | 882050.4362 | 95371.5228 | 4077910.5986 | 543459.8574 | 571859.5875 | 125807.9422 | 360399.5487 | 204141.2942 | 13225.9774 | 0 | 0 | 0 | 7831106.7805 | 0 | 7831102.8905 | 3.89 | 543463.7474 | 0 | 97984.5136 | 90321.9647 | 9766.0439 | 417578.0453 | 55650.2894 | 58558.4218 | 12882.7333 | 36904.9138 | 20904.0685 | 1354.3401 | 0 | 0 | 0 | 801905.3343 | 0 | 801904.936 | 0.39834 | 55650.6877 | 0 | 3264.8746 | 3009.5561 | 325.4076 | 13913.831 | 1854.285 | 1951.1849 | 429.2567 | 1229.6833 | 696.5301 | 45.127 | 0 | 0 | 0 | 26719.7363 | 0 | 26719.7231 | 0.013273 | 1854.2983 | 6.0362 | 0.65266 | 27.9065 | 3.9134 | 0.86094 | 0.09051 | 6.5482 | 0 | 0 | 1.397 | 0 | 53.5908 | 53.5908 | 2.662e-05
SC_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 450307.9137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493784.285 | 0 | 0 | 944092.1987 | 0 | 944092.1987 | 0 | 0 | 3749.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.7417 | 0 | 0 | 7861.4557 | 0 | 7861.4557 | 0 | 0 | 450.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7843 | 0 | 0 | 944.0922 | 0 | 944.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90317 | 0.99037 | 0 | 0 | 1.8935 | 1.8935 | 0
SC_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 894303.9153 | 717214.7463 | 95371.5228 | 4077910.5986 | 543387.6147 | 559797.8295 | 118211.3409 | 325422.9513 | 204094.0585 | 12675.8212 | 0 | 0 | 0 | 7548390.3991 | 0 | 7548387.6206 | 2.7786 | 543390.3932 | 0 | 91576.7209 | 73442.79 | 9766.0439 | 417578.0453 | 55642.8917 | 57323.2977 | 12104.8413 | 33323.3102 | 20899.2316 | 1298.0041 | 0 | 0 | 0 | 772955.1769 | 0 | 772954.8923 | 0.28453 | 55643.1763 | 0 | 3051.365 | 2447.1367 | 325.4076 | 13913.831 | 1854.0385 | 1910.0302 | 403.3371 | 1110.3431 | 696.3689 | 43.2499 | 0 | 0 | 0 | 25755.108 | 0 | 25755.0986 | 0.0094805 | 1854.048 | 4.9081 | 0.65266 | 27.9065 | 3.8309 | 0.80896 | 0.086745 | 6.12 | 0 | 0 | 1.3967 | 0 | 51.6561 | 51.6561 | 1.9015e-05
SC_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 256801.5705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493746.3723 | 0 | 0 | 750547.9428 | 0 | 750547.9428 | 0 | 0 | 2138.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.426 | 0 | 0 | 6249.8127 | 0 | 6249.8127 | 0 | 0 | 256.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7464 | 0 | 0 | 750.5479 | 0 | 750.5479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51506 | 0.99029 | 0 | 0 | 1.5053 | 1.5053 | 0
SC_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 44965.5446 | 28374.723 | 7207.602 | 142004.2074 | 0 | 23192.6961 | 0 | 0 | 0 | 0 | 99305.9732 | 0 | 0 | 345050.7463 | 0 | 345049.9127 | 0.83357 | 0.83357 | 0 | 4604.4718 | 2905.5716 | 738.0584 | 14541.2308 | 0 | 2374.9321 | 0 | 0 | 0 | 0 | 10168.9317 | 0 | 0 | 35333.1964 | 0 | 35333.1111 | 0.085358 | 0.085358 | 0 | 153.4224 | 96.8146 | 24.5923 | 484.5184 | 0 | 79.1335 | 0 | 0 | 0 | 0 | 338.832 | 0 | 0 | 1177.3131 | 0 | 1177.3103 | 0.0028441 | 0.0028441 | 2.8693 | 0.72886 | 14.3599 | 2.3453 | 0 | 0 | 4.5471 | 0 | 10.0421 | 0 | 0 | 34.8926 | 34.8927 | 8.4293e-05
SC_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 73503.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73503.2177 | 0 | 73503.2177 | 0 | 0 | 612.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612.0613 | 0 | 612.0613 | 0 | 0 | 73.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5032 | 0 | 73.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1785 | 0 | 0 | 0 | 2.1785 | 2.1785 | 0
SC_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 42731.577 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 22631.4256 | 0 | 0 | 0 | 0 | 99164.2663 | 0 | 0 | 336920.6602 | 0 | 336921.7716 | -1.1114 | -1.1114 | 0 | 4375.7135 | 2373.794 | 738.0584 | 14541.2308 | 0 | 2317.458 | 0 | 0 | 0 | 0 | 10154.4209 | 0 | 0 | 34500.6756 | 0 | 34500.7894 | -0.11381 | -0.11381 | 0 | 145.8001 | 79.0956 | 24.5923 | 484.5184 | 0 | 77.2184 | 0 | 0 | 0 | 0 | 338.3485 | 0 | 0 | 1149.5733 | 0 | 1149.5771 | -0.0037922 | -0.0037922 | 2.3442 | 0.72886 | 14.3599 | 2.2886 | 0 | 0 | 4.3212 | 0 | 10.0278 | 0 | 0 | 34.0706 | 34.0705 | -0.00011239
SC_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 18435.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18435.043 | 0 | 18435.043 | 0 | 0 | 153.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.5086 | 0 | 153.5086 | 0 | 0 | 18.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.435 | 0 | 18.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54637 | 0 | 0 | 0 | 0.54637 | 0.54637 | 0
SC_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 182321.21 | 100025.622 | 7107.5736 | 317887.4784 | 4818.0346 | 92592.9561 | 338.9851 | 0 | 0 | 23339.9601 | 7179.8163 | 17685.5769 | 0 | 753297.2133 | 0 | 753296.1018 | 1.1114 | 4819.1461 | 0 | 18669.6919 | 10242.6237 | 727.8155 | 32551.6778 | 493.3667 | 9481.5187 | 34.7121 | 0 | 0 | 2390.0119 | 735.2132 | 1811.0031 | 0 | 77137.6346 | 0 | 77137.5208 | 0.11381 | 493.4806 | 0 | 622.08 | 341.2874 | 24.251 | 1084.6321 | 16.4391 | 315.9272 | 1.1566 | 0 | 0 | 79.6359 | 24.4975 | 60.3432 | 0 | 2570.2501 | 0 | 2570.2463 | 0.0037922 | 16.4429 | 4.6145 | 0.3279 | 14.6653 | 4.2717 | 0.015639 | 1.0768 | 8.4111 | 0 | 0.33123 | 0 | 0.8159 | 34.7523 | 34.7524 | 5.1274e-05
SC_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 203193.0342 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104003.9726 | 0 | 0 | 649387.4216 | 0 | 649387.4216 | 0 | 0 | 1691.9884 | 0 | 0 | 0 | 2849.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 866.0411 | 0 | 0 | 5407.4491 | 0 | 5407.4491 | 0 | 0 | 203.193 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.004 | 0 | 0 | 649.3874 | 0 | 649.3874 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.7474 | 1.4062 | 0 | 0 | 8.7804 | 8.7804 | 0
SC_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 168072.7201 | 80467.2911 | 7107.5736 | 312483.1662 | 4745.7919 | 82059.4098 | 261.1853 | 0 | 0 | 22989.8607 | 7179.8163 | 12520.2215 | 0 | 697887.0365 | 0 | 697885.3693 | 1.6671 | 4747.459 | 0 | 17210.6465 | 8239.8506 | 727.8155 | 31998.2762 | 485.9691 | 8402.8836 | 26.7454 | 0 | 0 | 2354.1617 | 735.2132 | 1282.0707 | 0 | 71463.6325 | 0 | 71463.4618 | 0.17072 | 486.1398 | 0 | 573.4641 | 274.5544 | 24.251 | 1066.1926 | 16.1926 | 279.9867 | 0.89116 | 0 | 0 | 78.4414 | 24.4975 | 42.719 | 0 | 2381.1906 | 0 | 2381.1849 | 0.0056883 | 16.1983 | 3.7123 | 0.3279 | 14.416 | 3.7857 | 0.012049 | 1.0606 | 7.7538 | 0 | 0.33123 | 0 | 0.5776 | 32.196 | 32.1961 | 7.6911e-05
SC_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 171213.6846 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 103672.2366 | 0 | 0 | 617076.336 | 0 | 617076.336 | 0 | 0 | 1425.6964 | 0 | 0 | 0 | 2849.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 863.2787 | 0 | 0 | 5138.3946 | 0 | 5138.3946 | 0 | 0 | 171.2137 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6722 | 0 | 0 | 617.0763 | 0 | 617.0763 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.315 | 1.4018 | 0 | 0 | 8.3435 | 8.3435 | 0
SC_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 69208.5389 | 83101.3723 | 10680.8103 | 53987.5506 | 0 | 36752.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253730.3737 | 0 | 253728.9845 | 1.3893 | 1.3893 | 0 | 7086.9544 | 8509.5805 | 1093.715 | 5528.3252 | 0 | 3763.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25981.9903 | 0 | 25981.848 | 0.14226 | 0.14226 | 0 | 236.1395 | 283.5419 | 36.4429 | 184.2055 | 0 | 125.3982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.728 | 0 | 865.7233 | 0.0047402 | 0.0047402 | 11.4831 | 1.4759 | 7.4601 | 5.0785 | 0 | 0 | 9.5634 | 0 | 0 | 0 | 0 | 35.0609 | 35.0611 | 0.00019197
SC_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 111776.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86071.2727 | 0 | 0 | 197847.3456 | 0 | 197847.3456 | 0 | 0 | 930.7594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7155 | 0 | 0 | 1647.4748 | 0 | 1647.4748 | 0 | 0 | 111.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0713 | 0 | 0 | 197.8473 | 0 | 197.8473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5268 | 3.4858 | 0 | 0 | 8.0126 | 8.0126 | 0
SC_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 0 | 64548.8826 | 65540.8309 | 10680.8103 | 53987.5506 | 0 | 37785.7283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232543.8028 | 0 | 232543.5249 | 0.27786 | 0.27786 | 0 | 6609.8056 | 6711.3811 | 1093.715 | 5528.3252 | 0 | 3869.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23812.4854 | 0 | 23812.457 | 0.028453 | 0.028453 | 0 | 220.2408 | 223.6253 | 36.4429 | 184.2055 | 0 | 128.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793.4395 | 0 | 793.4385 | 0.00094805 | 0.00094805 | 9.0566 | 1.4759 | 7.4601 | 5.2213 | 0 | 0 | 8.9195 | 0 | 0 | 0 | 0 | 32.1334 | 32.1335 | 3.8395e-05
SC_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 124135.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86080.7508 | 0 | 0 | 210216.359 | 0 | 210216.359 | 0 | 0 | 1033.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7944 | 0 | 0 | 1750.4716 | 0 | 1750.4716 | 0 | 0 | 124.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0808 | 0 | 0 | 210.2164 | 0 | 210.2164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0274 | 3.4862 | 0 | 0 | 8.5135 | 8.5135 | 0
SC_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 8007.8292 | 103648.873 | 80133.8631 | 12311.829 | 154949.5496 | 0 | 46288.1424 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 405412.3289 | 0 | 405411.4954 | 0.83357 | 0.83357 | 820.0017 | 10613.6446 | 8205.7076 | 1260.7313 | 15866.8339 | 0 | 4739.9058 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 41514.2225 | 0 | 41514.1371 | 0.085358 | 0.085358 | 27.3227 | 353.65 | 273.4167 | 42.008 | 528.6879 | 0 | 157.9351 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1383.2669 | 0 | 1383.264 | 0.0028441 | 0.0028441 | 6.3288 | 0.97236 | 12.2376 | 3.6557 | 0.0057056 | 0 | 8.186 | 0.63244 | 0 | 0 | 0 | 32.0185 | 32.0186 | 6.5834e-05
SC_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 20160.0701 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 507385.4607 | 0 | 0 | 927040.9687 | 0 | 927040.9687 | 0 | 0 | 167.8729 | 0 | 0 | 0 | 3326.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 4224.9987 | 0 | 0 | 7719.4701 | 0 | 7719.4701 | 0 | 0 | 20.1601 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 507.3855 | 0 | 0 | 927.041 | 0 | 927.041 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.46665 | 11.7445 | 0 | 0 | 21.4583 | 21.4583 | 0
SC_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 9394.334 | 97588.819 | 51331.2409 | 12311.829 | 154949.5496 | 0 | 43965.2606 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 369613.2758 | 0 | 369614.9429 | -1.6671 | -1.6671 | 961.9798 | 9993.0951 | 5256.3191 | 1260.7313 | 15866.8339 | 0 | 4502.0427 | 7.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 37848.3994 | 0 | 37848.5702 | -0.17072 | -0.17072 | 32.0535 | 332.9731 | 175.1422 | 42.008 | 528.6879 | 0 | 150.0095 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.1205 | 0 | 1261.1262 | -0.0056883 | -0.0056883 | 4.054 | 0.97236 | 12.2376 | 3.4723 | 0.0057056 | 0 | 7.7074 | 0.74194 | 0 | 0 | 0 | 29.1914 | 29.1913 | -0.00013167
SC_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 21742.9247 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 507442.3297 | 0 | 0 | 928680.6923 | 0 | 928680.6923 | 0 | 0 | 181.0533 | 0 | 0 | 0 | 3326.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 4225.4723 | 0 | 0 | 7733.1241 | 0 | 7733.1241 | 0 | 0 | 21.7429 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 507.4423 | 0 | 0 | 928.6807 | 0 | 928.6807 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.50329 | 11.7458 | 0 | 0 | 21.4962 | 21.4962 | 0
SC_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 1089.1981 | 6810.2669 | 9016.4489 | 1581.0044 | 13417.6985 | 0 | 5087.5556 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42006.3711 | 0 | 42003.3147 | 3.0564 | 3.0564 | 111.5339 | 697.3713 | 923.2844 | 161.8949 | 1373.9723 | 0 | 520.9657 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4301.4524 | 0 | 4301.1394 | 0.31298 | 0.31298 | 3.7163 | 23.2366 | 30.7641 | 5.3944 | 45.7812 | 0 | 17.3587 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.3257 | 0 | 143.3153 | 0.010429 | 0.010429 | 5.5914 | 0.98044 | 8.3208 | 3.155 | 0 | 0 | 4.2233 | 0.67545 | 3.1033 | 0 | 0 | 26.0479 | 26.0498 | 0.0018954
SC_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 928.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928.8608 | 0 | 928.8608 | 0 | 0 | 7.7346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7346 | 0 | 7.7346 | 0 | 0 | 0.92886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92886 | 0 | 0.92886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16882 | 0 | 0 | 0 | 0.16882 | 0.16882 | 0
SC_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Electricity | 1119.7624 | 6487.9532 | 7238.1662 | 1581.0044 | 13417.6985 | 0 | 4687.442 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39536.2253 | 0 | 39534.5582 | 1.6671 | 1.6671 | 114.6637 | 664.3664 | 741.1882 | 161.8949 | 1373.9723 | 0 | 479.9941 | 0 | 0 | 0 | 0 | 512.4299 | 0 | 0 | 4048.5095 | 0 | 4048.3388 | 0.17072 | 0.17072 | 3.8206 | 22.1369 | 24.6966 | 5.3944 | 45.7812 | 0 | 15.9936 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.8976 | 0 | 134.8919 | 0.0056883 | 0.0056883 | 4.4887 | 0.98044 | 8.3208 | 2.9069 | 0 | 0 | 4.0234 | 0.69441 | 3.1033 | 0 | 0 | 24.5169 | 24.5179 | 0.0010339
SC_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | SC-COLUMBIA-SC | Zone3A | Zone3A(SC-COLUMBIA-SC) |  |  | SC | 0.1024 | 0.008327 |  |  |  | Natural Gas | 995.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.208 | 0 | 995.208 | 0 | 0 | 8.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2871 | 0 | 8.2871 | 0 | 0 | 0.99521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99521 | 0 | 0.99521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18088 | 0 | 0 | 0 | 0.18088 | 0.18088 | 0
SD_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 655286.0521 | 880263.8178 | 96091.1716 | 4077910.5986 | 543457.0788 | 607666.9763 | 96377.3639 | 213538.4067 | 406173.6562 | 12864.7637 | 0 | 0 | 0 | 7589629.8858 | 0 | 7589630.9973 | -1.1114 | 543455.9674 | 0 | 62645.3466 | 84153.221 | 9186.316 | 389848.2532 | 51954.4967 | 58092.9629 | 9213.676 | 20414.2717 | 38830.2015 | 1229.8714 | 0 | 0 | 0 | 725568.6171 | 0 | 725568.7233 | -0.10625 | 51954.3905 | 0 | 2235.836 | 3003.4601 | 327.8631 | 13913.831 | 1854.2756 | 2073.3597 | 328.8396 | 728.593 | 1385.8645 | 43.8946 | 0 | 0 | 0 | 25895.8172 | 0 | 25895.821 | -0.0037922 | 1854.2718 | 6.0239 | 0.65758 | 27.9065 | 4.1585 | 0.65954 | 0.088038 | 4.4843 | 0 | 0 | 2.7796 | 0 | 51.9383 | 51.9383 | -7.6059e-06
SD_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 1737272.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581476.3249 | 0 | 0 | 2318749.2805 | 0 | 2318749.2805 | 0 | 0 | 8526.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2853.8858 | 0 | 0 | 11380.4215 | 0 | 11380.4215 | 0 | 0 | 1737.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.4763 | 0 | 0 | 2318.7493 | 0 | 2318.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4844 | 1.1662 | 0 | 0 | 4.6506 | 4.6506 | 0
SD_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 614357.7649 | 716622.9116 | 96091.1716 | 4077910.5986 | 543384.8361 | 587953.0457 | 91587.115 | 192032.3006 | 405948.5923 | 11342.1092 | 0 | 0 | 0 | 7337230.4455 | 0 | 7337230.1677 | 0.27786 | 543385.114 | 0 | 58732.6023 | 68509.1504 | 9186.316 | 389848.2532 | 51947.5903 | 56208.3112 | 8755.7282 | 18358.2879 | 38808.6854 | 1084.3056 | 0 | 0 | 0 | 701439.2306 | 0 | 701439.204 | 0.026563 | 51947.6169 | 0 | 2096.1887 | 2445.1174 | 327.8631 | 13913.831 | 1854.0291 | 2006.0958 | 312.4952 | 655.2142 | 1385.0966 | 38.6993 | 0 | 0 | 0 | 25034.6303 | 0 | 25034.6293 | 0.00094805 | 1854.03 | 4.9041 | 0.65758 | 27.9065 | 4.0236 | 0.62676 | 0.077618 | 4.2043 | 0 | 0 | 2.778 | 0 | 50.2111 | 50.2111 | 1.9015e-06
SD_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 1684868.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581656.4102 | 0 | 0 | 2266524.5572 | 0 | 2266524.5572 | 0 | 0 | 8269.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2854.7697 | 0 | 0 | 11124.1025 | 0 | 11124.1025 | 0 | 0 | 1684.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581.6564 | 0 | 0 | 2266.5246 | 0 | 2266.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3793 | 1.1666 | 0 | 0 | 4.5459 | 4.5459 | 0
SD_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 28471.9728 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22514.7258 | 0 | 0 | 0 | 0 | 116585.8794 | 0 | 0 | 345156.3319 | 0 | 345153.8311 | 2.5007 | 2.5007 | 0 | 2721.9206 | 2712.6235 | 688.7811 | 13575.6022 | 0 | 2152.4078 | 0 | 0 | 0 | 0 | 11145.6101 | 0 | 0 | 32996.9453 | 0 | 32996.7063 | 0.23907 | 0.23907 | 0 | 97.1464 | 96.8146 | 24.5829 | 484.5184 | 0 | 76.8202 | 0 | 0 | 0 | 0 | 397.791 | 0 | 0 | 1177.6734 | 0 | 1177.6649 | 0.0085324 | 0.0085324 | 2.8693 | 0.72858 | 14.3599 | 2.2768 | 0 | 0 | 2.8792 | 0 | 11.7895 | 0 | 0 | 34.9031 | 34.9033 | 0.00025288
SD_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 237921.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237921.0535 | 0 | 237921.0535 | 0 | 0 | 1167.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.7165 | 0 | 1167.7165 | 0 | 0 | 237.9211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.9211 | 0 | 237.9211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0514 | 0 | 0 | 0 | 7.0514 | 7.0514 | 0
SD_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 27538.3744 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21847.8698 | 0 | 0 | 0 | 0 | 116610.8865 | 0 | 0 | 338387.7434 | 0 | 338388.8548 | -1.1114 | -1.1114 | 0 | 2632.6686 | 2216.1592 | 688.7811 | 13575.6022 | 0 | 2088.6564 | 0 | 0 | 0 | 0 | 11148.0008 | 0 | 0 | 32349.8683 | 0 | 32349.9745 | -0.10625 | -0.10625 | 0 | 93.9609 | 79.0956 | 24.5829 | 484.5184 | 0 | 74.5449 | 0 | 0 | 0 | 0 | 397.8763 | 0 | 0 | 1154.579 | 0 | 1154.5828 | -0.0037922 | -0.0037922 | 2.3442 | 0.72858 | 14.3599 | 2.2093 | 0 | 0 | 2.7848 | 0 | 11.7921 | 0 | 0 | 34.219 | 34.2189 | -0.00011239
SD_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 257379.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257379.7389 | 0 | 257379.7389 | 0 | 0 | 1263.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2198 | 0 | 1263.2198 | 0 | 0 | 257.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.3797 | 0 | 257.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6281 | 0 | 0 | 0 | 7.6281 | 7.6281 | 0
SD_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 104004.5295 | 96763.5847 | 7121.4664 | 317887.4784 | 4818.0346 | 102329.0538 | 1186.448 | 0 | 0 | 19541.6595 | 7179.8163 | 17610.5556 | 0 | 678442.6268 | 0 | 678447.6283 | -5.0014 | 4813.0332 | 0 | 9942.833 | 9250.5987 | 680.8122 | 30390.0429 | 460.6041 | 9782.6575 | 113.4244 | 0 | 0 | 1868.1826 | 686.3904 | 1683.5691 | 0 | 64859.1151 | 0 | 64859.5933 | -0.47814 | 460.126 | 0 | 354.8635 | 330.1574 | 24.2984 | 1084.6321 | 16.4391 | 349.1467 | 4.0482 | 0 | 0 | 66.6761 | 24.4975 | 60.0872 | 0 | 2314.8462 | 0 | 2314.8633 | -0.017065 | 16.4221 | 4.4641 | 0.32854 | 14.6653 | 4.7208 | 0.054735 | 0.90153 | 4.7981 | 0 | 0.33123 | 0 | 0.81244 | 31.2993 | 31.299 | -0.00023073
SD_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 715393.4058 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122192.5831 | 0 | 0 | 1179776.4038 | 0 | 1179776.4038 | 0 | 0 | 3511.1508 | 0 | 0 | 0 | 1679.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 599.7212 | 0 | 0 | 5790.3426 | 0 | 5790.3426 | 0 | 0 | 715.3934 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1926 | 0 | 0 | 1179.7764 | 0 | 1179.7764 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.6728 | 1.6522 | 0 | 0 | 15.9518 | 15.9518 | 0
SD_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 98327.9178 | 78572.3086 | 7121.4664 | 312483.1662 | 4743.0133 | 84560.1198 | 880.8056 | 0 | 0 | 22773.1325 | 7182.5949 | 12464.6501 | 0 | 629109.1754 | 0 | 629110.8425 | -1.6671 | 4741.3462 | 0 | 9400.1489 | 7511.5127 | 680.8122 | 29873.3907 | 453.4321 | 8083.9475 | 84.205 | 0 | 0 | 2177.1115 | 686.6561 | 1191.6206 | 0 | 60142.8372 | 0 | 60142.9965 | -0.15938 | 453.2727 | 0 | 335.4949 | 268.0887 | 24.2984 | 1066.1926 | 16.1832 | 288.5191 | 3.0053 | 0 | 0 | 77.7019 | 24.507 | 42.5294 | 0 | 2146.5205 | 0 | 2146.5262 | -0.0056883 | 16.1775 | 3.6248 | 0.32854 | 14.416 | 3.9011 | 0.040635 | 1.0506 | 4.5362 | 0 | 0.33136 | 0 | 0.57504 | 29.0232 | 29.0231 | -7.6911e-05
SD_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 691243.0256 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 121965.107 | 0 | 0 | 1155398.5475 | 0 | 1155398.5475 | 0 | 0 | 3392.6208 | 0 | 0 | 0 | 1679.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 598.6047 | 0 | 0 | 5670.6961 | 0 | 5670.6961 | 0 | 0 | 691.243 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 121.9651 | 0 | 0 | 1155.3985 | 0 | 1155.3985 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3463 | 1.6491 | 0 | 0 | 15.6221 | 15.6221 | 0
SD_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 39430.6398 | 84985.2405 | 10683.5889 | 53987.5506 | 0 | 46607.6775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235694.6974 | 0 | 235691.3631 | 3.3343 | 3.3343 | 0 | 3769.5692 | 8124.589 | 1021.3511 | 5161.2098 | 0 | 4455.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22532.4131 | 0 | 22532.0943 | 0.31876 | 0.31876 | 0 | 134.5373 | 289.9696 | 36.4524 | 184.2055 | 0 | 159.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.1903 | 0 | 804.1789 | 0.011377 | 0.011377 | 11.7435 | 1.4763 | 7.4601 | 6.4404 | 0 | 0 | 5.4486 | 0 | 0 | 0 | 0 | 32.5684 | 32.5689 | 0.00046074
SD_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 593760.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91350.614 | 0 | 0 | 685110.6488 | 0 | 685110.6488 | 0 | 0 | 2914.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448.3488 | 0 | 0 | 3362.5231 | 0 | 3362.5231 | 0 | 0 | 593.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3506 | 0 | 0 | 685.1106 | 0 | 685.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0467 | 3.6996 | 0 | 0 | 27.7463 | 27.7463 | 0
SD_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 37018.8439 | 67307.9993 | 10683.5889 | 53987.5506 | 0 | 44476.5169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213474.4996 | 0 | 213472.8325 | 1.6671 | 1.6671 | 0 | 3539.0015 | 6434.6447 | 1021.3511 | 5161.2098 | 0 | 4251.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20408.1622 | 0 | 20408.0028 | 0.15938 | 0.15938 | 0 | 126.3083 | 229.6549 | 36.4524 | 184.2055 | 0 | 151.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.375 | 0 | 728.3693 | 0.0056883 | 0.0056883 | 9.3008 | 1.4763 | 7.4601 | 6.1459 | 0 | 0 | 5.1154 | 0 | 0 | 0 | 0 | 29.4982 | 29.4984 | 0.00023037
SD_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 622554.7189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91360.0922 | 0 | 0 | 713914.8111 | 0 | 713914.8111 | 0 | 0 | 3055.4986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448.3953 | 0 | 0 | 3503.8939 | 0 | 3503.8939 | 0 | 0 | 622.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3601 | 0 | 0 | 713.9148 | 0 | 713.9148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2128 | 3.7 | 0 | 0 | 28.9128 | 28.9128 | 0
SD_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 52745.5313 | 67791.4699 | 79241.9432 | 12303.4933 | 154949.5496 | 0 | 46282.5852 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 413386.8153 | 0 | 413386.2596 | 0.55571 | 0.55571 | 5042.4728 | 6480.8645 | 7575.5298 | 1176.214 | 14813.1769 | 0 | 4424.6151 | 6.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 39519.7795 | 0 | 39519.7264 | 0.053126 | 0.053126 | 179.9678 | 231.3045 | 270.3735 | 41.9795 | 528.6879 | 0 | 157.9162 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1410.4758 | 0 | 1410.4739 | 0.0018961 | 0.0018961 | 6.2584 | 0.9717 | 12.2376 | 3.6553 | 0.0057056 | 0 | 5.354 | 4.1657 | 0 | 0 | 0 | 32.6483 | 32.6484 | 4.3889e-05
SD_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 106923.2493 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 608375.3748 | 0 | 0 | 1114794.062 | 0 | 1114794.062 | 0 | 0 | 524.7793 | 0 | 0 | 0 | 1960.7236 | 0 | 0 | 0 | 0 | 0 | 0 | 2985.9063 | 0 | 0 | 5471.4093 | 0 | 5471.4093 | 0 | 0 | 106.9232 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 608.3754 | 0 | 0 | 1114.7941 | 0 | 1114.7941 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.475 | 14.0821 | 0 | 0 | 25.8042 | 25.8042 | 0
SD_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 57738.6157 | 63420.7845 | 50828.3203 | 12303.4933 | 154949.5496 | 0 | 43798.5466 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 383111.5527 | 0 | 383111.5527 | 0 | 0 | 5519.8117 | 6063.027 | 4859.1874 | 1176.214 | 14813.1769 | 0 | 4187.1411 | 6.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 36625.4644 | 0 | 36625.4644 | 0 | 0 | 197.0042 | 216.3917 | 173.4262 | 41.9795 | 528.6879 | 0 | 149.4406 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1307.1766 | 0 | 1307.1766 | 0 | 0 | 4.0143 | 0.9717 | 12.2376 | 3.4591 | 0.0057056 | 0 | 5.0088 | 4.5601 | 0 | 0 | 0 | 30.2573 | 30.2573 | 0
SD_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 103131.9808 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 608451.2002 | 0 | 0 | 1111078.6189 | 0 | 1111078.6189 | 0 | 0 | 506.1718 | 0 | 0 | 0 | 1960.7236 | 0 | 0 | 0 | 0 | 0 | 0 | 2986.2785 | 0 | 0 | 5453.1739 | 0 | 5453.1739 | 0 | 0 | 103.132 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 608.4512 | 0 | 0 | 1111.0786 | 0 | 1111.0786 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.3872 | 14.0839 | 0 | 0 | 25.7182 | 25.7182 | 0
SD_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 4695.7777 | 4117.8358 | 8833.0635 | 1592.1187 | 13417.6985 | 0 | 5254.2696 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42914.9624 | 0 | 42914.1288 | 0.83357 | 0.83357 | 448.9163 | 393.6651 | 844.4409 | 152.2065 | 1282.732 | 0 | 502.3082 | 0 | 0 | 0 | 0 | 478.4014 | 0 | 0 | 4102.6704 | 0 | 4102.5907 | 0.079689 | 0.079689 | 16.022 | 14.0501 | 30.1384 | 5.4323 | 45.7812 | 0 | 17.9276 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 146.4259 | 0 | 146.423 | 0.0028441 | 0.0028441 | 5.4777 | 0.98733 | 8.3208 | 3.2584 | 0 | 0 | 2.5536 | 2.912 | 3.1033 | 0 | 0 | 26.6127 | 26.6132 | 0.00051693
SD_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 17705.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17705.2238 | 0 | 17705.2238 | 0 | 0 | 86.8972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8972 | 0 | 86.8972 | 0 | 0 | 17.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7052 | 0 | 17.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.218 | 0 | 0 | 0 | 3.218 | 3.218 | 0
SD_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 4726.3419 | 3903.8862 | 7118.6878 | 1592.1187 | 13417.6985 | 0 | 4837.4846 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40600.4164 | 0 | 40602.6392 | -2.2229 | -2.2229 | 451.8383 | 373.2115 | 680.5466 | 152.2065 | 1282.732 | 0 | 462.4635 | 0 | 0 | 0 | 0 | 478.4014 | 0 | 0 | 3881.3998 | 0 | 3881.6123 | -0.2125 | -0.2125 | 16.1263 | 13.3201 | 24.289 | 5.4323 | 45.7812 | 0 | 16.5055 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.5286 | 0 | 138.5362 | -0.0075844 | -0.0075844 | 4.4146 | 0.98733 | 8.3208 | 2.9999 | 0 | 0 | 2.4209 | 2.931 | 3.1033 | 0 | 0 | 25.1792 | 25.1779 | -0.0013785
SD_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | SD-SIOUXCITY-IA | Zone5A | Zone5A(SD-SIOUXCITY-IA) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 18122.2633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18122.2633 | 0 | 18122.2633 | 0 | 0 | 88.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9441 | 0 | 88.9441 | 0 | 0 | 18.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1223 | 0 | 18.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2938 | 0 | 0 | 0 | 3.2938 | 3.2938 | 0
SD_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 585652.3925 | 880233.2536 | 96310.6783 | 4077910.5986 | 543457.0788 | 616825.1321 | 89364.2616 | 188397.9353 | 431469.7273 | 12639.6998 | 0 | 0 | 0 | 7522260.758 | 0 | 7522264.648 | -3.89 | 543453.1888 | 0 | 55988.3687 | 84150.299 | 9207.3008 | 389848.2532 | 51954.4967 | 58968.4826 | 8543.2234 | 18010.8426 | 41248.5059 | 1208.3553 | 0 | 0 | 0 | 719128.1285 | 0 | 719128.5004 | -0.37188 | 51954.1249 | 0 | 1998.246 | 3003.3559 | 328.612 | 13913.831 | 1854.2756 | 2104.6074 | 304.9109 | 642.8138 | 1472.1747 | 43.1267 | 0 | 0 | 0 | 25665.9537 | 0 | 25665.967 | -0.013273 | 1854.2623 | 6.0237 | 0.65909 | 27.9065 | 4.2211 | 0.61155 | 0.086498 | 4.0078 | 0 | 0 | 2.9527 | 0 | 51.4773 | 51.4773 | -2.662e-05
SD_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 1750267.5283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600176.7567 | 0 | 0 | 2350444.285 | 0 | 2350444.285 | 0 | 0 | 8590.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2945.6675 | 0 | 0 | 11535.9806 | 0 | 11535.9806 | 0 | 0 | 1750.2675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600.1768 | 0 | 0 | 2350.4443 | 0 | 2350.4443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5104 | 1.2038 | 0 | 0 | 4.7142 | 4.7142 | 0
SD_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 543259.8006 | 716911.8826 | 96310.6783 | 4077910.5986 | 543387.6147 | 592045.8744 | 84821.3051 | 168747.9118 | 431136.2993 | 11203.1809 | 0 | 0 | 0 | 7265735.1462 | 0 | 7265732.3677 | 2.7786 | 543390.3932 | 0 | 51935.6369 | 68536.776 | 9207.3008 | 389848.2532 | 51947.856 | 56599.5856 | 8108.9168 | 16132.3004 | 41216.6302 | 1071.0241 | 0 | 0 | 0 | 694604.28 | 0 | 694604.0143 | 0.26563 | 51948.1216 | 0 | 1853.6024 | 2446.1033 | 328.612 | 13913.831 | 1854.0385 | 2020.0605 | 289.4103 | 575.7679 | 1471.0371 | 38.2253 | 0 | 0 | 0 | 24790.6883 | 0 | 24790.6788 | 0.0094805 | 1854.048 | 4.9061 | 0.65909 | 27.9065 | 4.0516 | 0.58046 | 0.076667 | 3.7177 | 0 | 0 | 2.9504 | 0 | 49.7218 | 49.7218 | 1.9015e-05
SD_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 1774749.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600129.3659 | 0 | 0 | 2374879.0104 | 0 | 2374879.0104 | 0 | 0 | 8710.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2945.4349 | 0 | 0 | 11655.9062 | 0 | 11655.9062 | 0 | 0 | 1774.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600.1294 | 0 | 0 | 2374.879 | 0 | 2374.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5596 | 1.2037 | 0 | 0 | 4.7632 | 4.7632 | 0
SD_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 25893.4629 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22289.6619 | 0 | 0 | 0 | 0 | 120164.6733 | 0 | 0 | 345931.552 | 0 | 345929.0512 | 2.5007 | 2.5007 | 0 | 2475.4151 | 2712.6235 | 688.7811 | 13575.6022 | 0 | 2130.8917 | 0 | 0 | 0 | 0 | 11487.7428 | 0 | 0 | 33071.0564 | 0 | 33070.8173 | 0.23907 | 0.23907 | 0 | 88.3485 | 96.8146 | 24.5829 | 484.5184 | 0 | 76.0523 | 0 | 0 | 0 | 0 | 410.0019 | 0 | 0 | 1180.3185 | 0 | 1180.3099 | 0.0085324 | 0.0085324 | 2.8693 | 0.72858 | 14.3599 | 2.254 | 0 | 0 | 2.6184 | 0 | 12.1514 | 0 | 0 | 34.9815 | 34.9817 | 0.00025288
SD_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 233864.3962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233864.3962 | 0 | 233864.3962 | 0 | 0 | 1147.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.8065 | 0 | 1147.8065 | 0 | 0 | 233.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.8644 | 0 | 233.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9312 | 0 | 0 | 0 | 6.9312 | 6.9312 | 0
SD_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 24192.9801 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21489.4347 | 0 | 0 | 0 | 0 | 120198.0161 | 0 | 0 | 338271.0436 | 0 | 338274.1 | -3.0564 | -3.0564 | 0 | 2312.8489 | 2216.1592 | 688.7811 | 13575.6022 | 0 | 2054.39 | 0 | 0 | 0 | 0 | 11490.9303 | 0 | 0 | 32338.7118 | 0 | 32339.004 | -0.29219 | -0.29219 | 0 | 82.5464 | 79.0956 | 24.5829 | 484.5184 | 0 | 73.322 | 0 | 0 | 0 | 0 | 410.1156 | 0 | 0 | 1154.1808 | 0 | 1154.1912 | -0.010429 | -0.010429 | 2.3442 | 0.72858 | 14.3599 | 2.1731 | 0 | 0 | 2.4465 | 0 | 12.1548 | 0 | 0 | 34.2074 | 34.2071 | -0.00030908
SD_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 258924.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258924.6808 | 0 | 258924.6808 | 0 | 0 | 1270.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.8023 | 0 | 1270.8023 | 0 | 0 | 258.9247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.9247 | 0 | 258.9247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6739 | 0 | 0 | 0 | 7.6739 | 7.6739 | 0
SD_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 88622.3843 | 96249.5499 | 7129.8021 | 317887.4784 | 4818.0346 | 102195.6826 | 1186.448 | 0 | 0 | 19349.9384 | 7179.8163 | 17599.4414 | 0 | 662218.576 | 0 | 662217.4646 | 1.1114 | 4819.1461 | 0 | 8472.2999 | 9201.457 | 681.6091 | 30390.0429 | 460.6041 | 9769.9073 | 113.4244 | 0 | 0 | 1849.8541 | 686.3904 | 1682.5066 | 0 | 63308.0959 | 0 | 63307.9896 | 0.10625 | 460.7104 | 0 | 302.3796 | 328.4035 | 24.3269 | 1084.6321 | 16.4391 | 348.6917 | 4.0482 | 0 | 0 | 66.022 | 24.4975 | 60.0493 | 0 | 2259.4898 | 0 | 2259.486 | 0.0037922 | 16.4429 | 4.4403 | 0.32892 | 14.6653 | 4.7147 | 0.054735 | 0.89268 | 4.0885 | 0 | 0.33123 | 0 | 0.81193 | 30.5505 | 30.5506 | 5.1274e-05
SD_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 810904.937 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125690.0283 | 0 | 0 | 1278785.3801 | 0 | 1278785.3801 | 0 | 0 | 3979.9214 | 0 | 0 | 0 | 1679.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 616.8867 | 0 | 0 | 6276.2786 | 0 | 6276.2786 | 0 | 0 | 810.9049 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.69 | 0 | 0 | 1278.7854 | 0 | 1278.7854 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.9642 | 1.6995 | 0 | 0 | 17.2905 | 17.2905 | 0
SD_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 82142.7668 | 78605.6514 | 7129.8021 | 312483.1662 | 4743.0133 | 83306.9863 | 986.3912 | 0 | 0 | 22817.5896 | 7182.5949 | 12456.3144 | 0 | 611854.2763 | 0 | 611854.832 | -0.55571 | 4742.4576 | 0 | 7852.8485 | 7514.7003 | 681.6091 | 29873.3907 | 453.4321 | 7964.1479 | 94.299 | 0 | 0 | 2181.3616 | 686.6561 | 1190.8237 | 0 | 58493.2688 | 0 | 58493.3219 | -0.053126 | 453.3789 | 0 | 280.2711 | 268.2025 | 24.3269 | 1066.1926 | 16.1832 | 284.2434 | 3.3656 | 0 | 0 | 77.8536 | 24.507 | 42.5009 | 0 | 2087.6468 | 0 | 2087.6487 | -0.0018961 | 16.1813 | 3.6264 | 0.32892 | 14.416 | 3.8433 | 0.045506 | 1.0527 | 3.7895 | 0 | 0.33136 | 0 | 0.57466 | 28.2271 | 28.2271 | -2.5637e-05
SD_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 784081.7125 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125453.074 | 0 | 0 | 1251725.2014 | 0 | 1251725.2014 | 0 | 0 | 3848.273 | 0 | 0 | 0 | 1679.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 615.7237 | 0 | 0 | 6143.4673 | 0 | 6143.4673 | 0 | 0 | 784.0817 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.4531 | 0 | 0 | 1251.7252 | 0 | 1251.7252 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.6016 | 1.6963 | 0 | 0 | 16.9246 | 16.9246 | 0
SD_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 32086.888 | 90692.4165 | 10686.3675 | 53987.5506 | 0 | 46974.4483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234427.671 | 0 | 234424.8924 | 2.7786 | 2.7786 | 0 | 3067.5065 | 8670.195 | 1021.6167 | 5161.2098 | 0 | 4490.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22411.2853 | 0 | 22411.0197 | 0.26563 | 0.26563 | 0 | 109.4805 | 309.4425 | 36.4619 | 184.2055 | 0 | 160.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.8672 | 0 | 799.8577 | 0.0094805 | 0.0094805 | 12.5321 | 1.4767 | 7.4601 | 6.491 | 0 | 0 | 4.4338 | 0 | 0 | 0 | 0 | 32.3934 | 32.3938 | 0.00038395
SD_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 635947.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92431.1255 | 0 | 0 | 728378.5004 | 0 | 728378.5004 | 0 | 0 | 3121.2297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.652 | 0 | 0 | 3574.8817 | 0 | 3574.8817 | 0 | 0 | 635.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4311 | 0 | 0 | 728.3785 | 0 | 728.3785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.7552 | 3.7434 | 0 | 0 | 29.4986 | 29.4986 | 0
SD_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 0 | 30039.0844 | 75079.6503 | 10686.3675 | 53987.5506 | 0 | 45087.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214880.4544 | 0 | 214881.288 | -0.83357 | -0.83357 | 0 | 2871.7365 | 7177.6146 | 1021.6167 | 5161.2098 | 0 | 4310.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20542.5714 | 0 | 20542.6511 | -0.079689 | -0.079689 | 0 | 102.4934 | 256.1718 | 36.4619 | 184.2055 | 0 | 153.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733.1721 | 0 | 733.175 | -0.0028441 | -0.0028441 | 10.3747 | 1.4767 | 7.4601 | 6.2303 | 0 | 0 | 4.1509 | 0 | 0 | 0 | 0 | 29.6928 | 29.6927 | -0.00011518
SD_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 664381.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92440.6037 | 0 | 0 | 756822.4921 | 0 | 756822.4921 | 0 | 0 | 3260.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6985 | 0 | 0 | 3714.4848 | 0 | 3714.4848 | 0 | 0 | 664.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4406 | 0 | 0 | 756.8225 | 0 | 756.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9068 | 3.7437 | 0 | 0 | 30.6505 | 30.6505 | 0
SD_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 56396.568 | 61917.58 | 79125.2434 | 12306.2718 | 154949.5496 | 0 | 46282.5852 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 411050.0407 | 0 | 411050.8743 | -0.83357 | -0.83357 | 5391.5119 | 5919.3206 | 7564.3733 | 1176.4796 | 14813.1769 | 0 | 4424.6151 | 6.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 39296.3839 | 0 | 39296.4636 | -0.079689 | -0.079689 | 192.4251 | 211.2628 | 269.9753 | 41.989 | 528.6879 | 0 | 157.9162 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.5027 | 0 | 1402.5056 | -0.0028441 | -0.0028441 | 6.2491 | 0.97192 | 12.2376 | 3.6553 | 0.0057056 | 0 | 4.8901 | 4.4541 | 0 | 0 | 0 | 32.4639 | 32.4638 | -6.5834e-05
SD_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 119406.0008 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 629473.7839 | 0 | 0 | 1148375.2226 | 0 | 1148375.2226 | 0 | 0 | 586.0447 | 0 | 0 | 0 | 1960.7236 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.4573 | 0 | 0 | 5636.2256 | 0 | 5636.2256 | 0 | 0 | 119.406 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 629.4738 | 0 | 0 | 1148.3752 | 0 | 1148.3752 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.7639 | 14.5705 | 0 | 0 | 26.5815 | 26.5815 | 0
SD_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 62006.4941 | 57402.4091 | 50839.4346 | 12306.2718 | 154949.5496 | 0 | 43720.7467 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 381297.1487 | 0 | 381296.0373 | 1.1114 | 1.1114 | 5927.8208 | 5487.6703 | 4860.2499 | 1176.4796 | 14813.1769 | 0 | 4179.7034 | 6.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 36452.0074 | 0 | 36451.9012 | 0.10625 | 0.10625 | 211.5662 | 195.857 | 173.4642 | 41.989 | 528.6879 | 0 | 149.1752 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1300.9859 | 0 | 1300.9821 | 0.0037922 | 0.0037922 | 4.0152 | 0.97192 | 12.2376 | 3.453 | 0.0057056 | 0 | 4.5335 | 4.8971 | 0 | 0 | 0 | 30.1139 | 30.114 | 8.7778e-05
SD_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 115282.9963 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 629540.1311 | 0 | 0 | 1144318.5653 | 0 | 1144318.5653 | 0 | 0 | 565.8089 | 0 | 0 | 0 | 1960.7236 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.783 | 0 | 0 | 5616.3155 | 0 | 5616.3155 | 0 | 0 | 115.283 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 629.5401 | 0 | 0 | 1144.3186 | 0 | 1144.3186 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.6685 | 14.572 | 0 | 0 | 26.4876 | 26.4876 | 0
SD_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 4759.6847 | 3598.2439 | 8802.4992 | 1597.6758 | 13417.6985 | 0 | 5354.298 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42534.2988 | 0 | 42533.1873 | 1.1114 | 1.1114 | 455.0259 | 343.9921 | 841.5189 | 152.7378 | 1282.732 | 0 | 511.8709 | 0 | 0 | 0 | 0 | 478.4014 | 0 | 0 | 4066.279 | 0 | 4066.1727 | 0.10625 | 0.10625 | 16.24 | 12.2772 | 30.0341 | 5.4513 | 45.7812 | 0 | 18.2689 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.127 | 0 | 145.1232 | 0.0037922 | 0.0037922 | 5.4588 | 0.99078 | 8.3208 | 3.3204 | 0 | 0 | 2.2314 | 2.9517 | 3.1033 | 0 | 0 | 26.3765 | 26.3771 | 0.00068924
SD_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 23780.7315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23780.7315 | 0 | 23780.7315 | 0 | 0 | 116.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.7158 | 0 | 116.7158 | 0 | 0 | 23.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7807 | 0 | 23.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3222 | 0 | 0 | 0 | 4.3222 | 4.3222 | 0
SD_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Electricity | 4854.156 | 3320.3872 | 7118.6878 | 1597.6758 | 13417.6985 | 0 | 4865.2703 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40178.0742 | 0 | 40174.7399 | 3.3343 | 3.3343 | 464.0573 | 317.429 | 680.5466 | 152.7378 | 1282.732 | 0 | 465.1198 | 0 | 0 | 0 | 0 | 478.4014 | 0 | 0 | 3841.0239 | 0 | 3840.7051 | 0.31876 | 0.31876 | 16.5624 | 11.3292 | 24.289 | 5.4513 | 45.7812 | 0 | 16.6003 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.0876 | 0 | 137.0762 | 0.011377 | 0.011377 | 4.4146 | 0.99078 | 8.3208 | 3.0171 | 0 | 0 | 2.0591 | 3.0102 | 3.1033 | 0 | 0 | 24.9139 | 24.916 | 0.0020677
SD_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | SD-SIOUXFALLS-SD | Zone6A | Zone6A(SD-SIOUXFALLS-SD) |  |  | SD | 0.0956 | 0.004908 |  |  |  | Natural Gas | 24671.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24671.6796 | 0 | 24671.6796 | 0 | 0 | 121.0886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0886 | 0 | 121.0886 | 0 | 0 | 24.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.6717 | 0 | 24.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4841 | 0 | 0 | 0 | 4.4841 | 4.4841 | 0
TN_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 920686.4059 | 883211.8771 | 94751.9024 | 4077910.5986 | 543459.8574 | 574049.098 | 126858.2405 | 346731.7792 | 258531.737 | 12172.9006 | 0 | 0 | 0 | 7838364.3967 | 0 | 7838364.3967 | 0 | 543459.8574 | 0 | 96764.1413 | 92825.5683 | 9958.4249 | 428588.4039 | 57117.631 | 60332.5602 | 13332.8011 | 36441.51 | 27171.6856 | 1279.3719 | 0 | 0 | 0 | 823812.0981 | 0 | 823812.0981 | 0 | 57117.631 | 0 | 3141.382 | 3013.5189 | 323.2935 | 13913.831 | 1854.285 | 1958.6555 | 432.8403 | 1183.0488 | 882.1103 | 41.5339 | 0 | 0 | 0 | 26744.4993 | 0 | 26744.4993 | 0 | 1854.285 | 6.0441 | 0.64842 | 27.9065 | 3.9284 | 0.86813 | 0.083303 | 6.3006 | 0 | 0 | 1.7692 | 0 | 53.6405 | 53.6405 | 0
TN_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 820629.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496902.6033 | 0 | 0 | 1317532.144 | 0 | 1317532.144 | 0 | 0 | 6162.9279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.7386 | 0 | 0 | 9894.6664 | 0 | 9894.6664 | 0 | 0 | 820.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.9026 | 0 | 0 | 1317.5321 | 0 | 1317.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6459 | 0.99662 | 0 | 0 | 2.6425 | 2.6425 | 0
TN_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 858004.7201 | 718198.3589 | 94751.9024 | 4077910.5986 | 543387.6147 | 558247.3893 | 118264.1337 | 313013.8725 | 258478.9442 | 12134.0007 | 0 | 0 | 0 | 7552391.5351 | 0 | 7552391.5351 | 0 | 543387.6147 | 0 | 90176.2961 | 75482.6475 | 9958.4249 | 428588.4039 | 57110.0383 | 58671.8006 | 12429.5605 | 32897.758 | 27166.137 | 1275.2835 | 0 | 0 | 0 | 793756.3503 | 0 | 793756.3503 | 0 | 57110.0383 | 0 | 2927.5121 | 2450.4928 | 323.2935 | 13913.831 | 1854.0385 | 1904.7401 | 403.5172 | 1068.0033 | 881.9302 | 41.4012 | 0 | 0 | 0 | 25768.7599 | 0 | 25768.7599 | 0 | 1854.0385 | 4.9149 | 0.64842 | 27.9065 | 3.8203 | 0.80932 | 0.083037 | 5.8716 | 0 | 0 | 1.7689 | 0 | 51.6835 | 51.6835 | 0
TN_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 470847.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496845.7343 | 0 | 0 | 967692.845 | 0 | 967692.845 | 0 | 0 | 3536.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.3115 | 0 | 0 | 7267.3733 | 0 | 7267.3733 | 0 | 0 | 470.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.8457 | 0 | 0 | 967.6928 | 0 | 967.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94436 | 0.99651 | 0 | 0 | 1.9409 | 1.9409 | 0
TN_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 46802.1772 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 23831.7664 | 0 | 0 | 0 | 0 | 99978.3864 | 0 | 0 | 348201.6409 | 0 | 348201.0852 | 0.55571 | 0.55571 | 0 | 4918.9088 | 2982.1834 | 757.811 | 14924.6422 | 0 | 2504.7187 | 0 | 0 | 0 | 0 | 10507.7284 | 0 | 0 | 36595.9925 | 0 | 36595.9341 | 0.058405 | 0.058405 | 0 | 159.689 | 96.8146 | 24.6018 | 484.5184 | 0 | 81.314 | 0 | 0 | 0 | 0 | 341.1263 | 0 | 0 | 1188.064 | 0 | 1188.0621 | 0.0018961 | 0.0018961 | 2.8693 | 0.72914 | 14.3599 | 2.4099 | 0 | 0 | 4.7328 | 0 | 10.1101 | 0 | 0 | 35.2112 | 35.2113 | 5.6196e-05
TN_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 134277.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134277.2514 | 0 | 134277.2514 | 0 | 0 | 1008.4222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008.4222 | 0 | 1008.4222 | 0 | 0 | 134.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.2773 | 0 | 134.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9796 | 0 | 0 | 0 | 3.9796 | 3.9796 | 0
TN_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 42695.4556 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 22470.2688 | 0 | 0 | 0 | 0 | 99845.0152 | 0 | 0 | 337406.9094 | 0 | 337409.4101 | -2.5007 | -2.5007 | 0 | 4487.2924 | 2436.3843 | 757.811 | 14924.6422 | 0 | 2361.6252 | 0 | 0 | 0 | 0 | 10493.7111 | 0 | 0 | 35461.4662 | 0 | 35461.729 | -0.26282 | -0.26282 | 0 | 145.6769 | 79.0956 | 24.6018 | 484.5184 | 0 | 76.6686 | 0 | 0 | 0 | 0 | 340.6712 | 0 | 0 | 1151.2324 | 0 | 1151.2409 | -0.0085324 | -0.0085324 | 2.3442 | 0.72914 | 14.3599 | 2.2723 | 0 | 0 | 4.3175 | 0 | 10.0967 | 0 | 0 | 34.1199 | 34.1197 | -0.00025288
TN_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 46774.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46774.7749 | 0 | 46774.7749 | 0 | 0 | 351.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351.2786 | 0 | 351.2786 | 0 | 0 | 46.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.7748 | 0 | 46.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3863 | 0 | 0 | 0 | 1.3863 | 1.3863 | 0
TN_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 171809.8922 | 101167.6129 | 7096.4593 | 317887.4784 | 4818.0346 | 95232.5945 | 527.9277 | 0 | 0 | 24051.2732 | 7179.8163 | 17680.0198 | 0 | 747451.109 | 0 | 747449.9975 | 1.1114 | 4819.1461 | 0 | 18057.2197 | 10632.7161 | 745.8379 | 33409.974 | 506.3754 | 10008.9457 | 55.4852 | 0 | 0 | 2527.7888 | 754.5987 | 1858.1701 | 0 | 78557.1116 | 0 | 78556.9947 | 0.11681 | 506.4923 | 0 | 586.2154 | 345.1839 | 24.2131 | 1084.6321 | 16.4391 | 324.9336 | 1.8013 | 0 | 0 | 82.0629 | 24.4975 | 60.3242 | 0 | 2550.3032 | 0 | 2550.2994 | 0.0037922 | 16.4429 | 4.6672 | 0.32739 | 14.6653 | 4.3934 | 0.024355 | 1.1096 | 7.9262 | 0 | 0.33123 | 0 | 0.81564 | 34.4826 | 34.4827 | 5.1274e-05
TN_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 322362.0807 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 105075.0059 | 0 | 0 | 769627.5014 | 0 | 769627.5014 | 0 | 0 | 2420.9392 | 0 | 0 | 0 | 2569.85 | 0 | 0 | 0 | 0 | 0 | 0 | 789.1133 | 0 | 0 | 5779.9025 | 0 | 5779.9025 | 0 | 0 | 322.3621 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 105.075 | 0 | 0 | 769.6275 | 0 | 769.6275 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.3587 | 1.4207 | 0 | 0 | 10.4061 | 10.4061 | 0
TN_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 157686.4378 | 81645.4034 | 7096.4593 | 312483.1662 | 4745.7919 | 83909.9352 | 391.7779 | 0 | 0 | 22650.8756 | 7179.8163 | 12517.4429 | 0 | 690307.1066 | 0 | 690309.0516 | -1.945 | 4743.8469 | 0 | 16572.8446 | 8580.9319 | 745.8379 | 32841.9808 | 498.7827 | 8818.9342 | 41.1759 | 0 | 0 | 2380.607 | 754.5987 | 1315.5832 | 0 | 72551.2769 | 0 | 72551.4813 | -0.20442 | 498.5783 | 0 | 538.0261 | 278.5741 | 24.2131 | 1066.1926 | 16.1926 | 286.3007 | 1.3367 | 0 | 0 | 77.2848 | 24.4975 | 42.7095 | 0 | 2355.3278 | 0 | 2355.3345 | -0.0066363 | 16.186 | 3.7666 | 0.32739 | 14.416 | 3.8711 | 0.018074 | 1.045 | 7.2747 | 0 | 0.33123 | 0 | 0.57748 | 31.8465 | 31.8464 | -8.973e-05
TN_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 276468.7757 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104762.2263 | 0 | 0 | 723421.4168 | 0 | 723421.4168 | 0 | 0 | 2076.2805 | 0 | 0 | 0 | 2569.85 | 0 | 0 | 0 | 0 | 0 | 0 | 786.7643 | 0 | 0 | 5432.8948 | 0 | 5432.8948 | 0 | 0 | 276.4688 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7622 | 0 | 0 | 723.4214 | 0 | 723.4214 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.7381 | 1.4165 | 0 | 0 | 9.7814 | 9.7814 | 0
TN_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 68644.4899 | 83248.6364 | 10705.8174 | 53987.5506 | 0 | 38630.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255216.9069 | 0 | 255216.3512 | 0.55571 | 0.55571 | 0 | 7214.5359 | 8749.4317 | 1125.1814 | 5674.0916 | 0 | 4060.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26823.2969 | 0 | 26823.2385 | 0.058405 | 0.058405 | 0 | 234.215 | 284.0443 | 36.5282 | 184.2055 | 0 | 131.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870.8001 | 0 | 870.7982 | 0.0018961 | 0.0018961 | 11.5035 | 1.4794 | 7.4601 | 5.338 | 0 | 0 | 9.4855 | 0 | 0 | 0 | 0 | 35.2664 | 35.2665 | 7.679e-05
TN_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 182805.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86279.7924 | 0 | 0 | 269085.2804 | 0 | 269085.2804 | 0 | 0 | 1372.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 647.9612 | 0 | 0 | 2020.8305 | 0 | 2020.8305 | 0 | 0 | 182.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2798 | 0 | 0 | 269.0853 | 0 | 269.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4034 | 3.4942 | 0 | 0 | 10.8977 | 10.8977 | 0
TN_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 64423.8471 | 65821.4661 | 10705.8174 | 53987.5506 | 0 | 36796.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231735.2399 | 0 | 231730.5163 | 4.7236 | 4.7236 | 0 | 6770.9463 | 6917.8361 | 1125.1814 | 5674.0916 | 0 | 3867.3183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24355.3737 | 0 | 24354.8773 | 0.49645 | 0.49645 | 0 | 219.8142 | 224.5828 | 36.5282 | 184.2055 | 0 | 125.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790.6806 | 0 | 790.6645 | 0.016117 | 0.016117 | 9.0954 | 1.4794 | 7.4601 | 5.0846 | 0 | 0 | 8.9022 | 0 | 0 | 0 | 0 | 32.0211 | 32.0217 | 0.00065271
TN_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 200093.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86289.2706 | 0 | 0 | 286382.9428 | 0 | 286382.9428 | 0 | 0 | 1502.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 648.0324 | 0 | 0 | 2150.7359 | 0 | 2150.7359 | 0 | 0 | 200.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2893 | 0 | 0 | 286.3829 | 0 | 286.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1036 | 3.4946 | 0 | 0 | 11.5982 | 11.5982 | 0
TN_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 12756.3996 | 102279.0396 | 80172.7631 | 12314.6075 | 154949.5496 | 0 | 46346.4923 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 408891.0944 | 0 | 408890.8166 | 0.27786 | 0.27786 | 1340.6976 | 10749.5271 | 8426.1574 | 1294.2653 | 16285.1977 | 0 | 4871.0163 | 7.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 42974.454 | 0 | 42974.4248 | 0.029203 | 0.029203 | 43.5248 | 348.9761 | 273.5495 | 42.0174 | 528.6879 | 0 | 158.1342 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.1364 | 0 | 1395.1355 | 0.00094805 | 0.00094805 | 6.3319 | 0.97258 | 12.2376 | 3.6603 | 0.0057056 | 0 | 8.0778 | 1.0075 | 0 | 0 | 0 | 32.2933 | 32.2933 | 2.1945e-05
TN_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 28254.4283 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511470.5525 | 0 | 0 | 939220.4187 | 0 | 939220.4187 | 0 | 0 | 212.1908 | 0 | 0 | 0 | 3000.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.1438 | 0 | 0 | 7053.5453 | 0 | 7053.5453 | 0 | 0 | 28.2544 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.4706 | 0 | 0 | 939.2204 | 0 | 939.2204 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.65401 | 11.839 | 0 | 0 | 21.7402 | 21.7402 | 0
TN_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 14493.0038 | 96499.6209 | 51367.3623 | 12314.6075 | 154949.5496 | 0 | 44029.1676 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373725.5545 | 0 | 373725.5545 | 0 | 0 | 1523.2147 | 10142.1102 | 5398.7098 | 1294.2653 | 16285.1977 | 0 | 4627.4655 | 7.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 39278.5558 | 0 | 39278.5558 | 0 | 0 | 49.4501 | 329.2567 | 175.2654 | 42.0174 | 528.6879 | 0 | 150.2275 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.1516 | 0 | 1275.1516 | 0 | 0 | 4.0569 | 0.97258 | 12.2376 | 3.4773 | 0.0057056 | 0 | 7.6213 | 1.1446 | 0 | 0 | 0 | 29.516 | 29.516 | 0
TN_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 29259.1145 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 511508.4652 | 0 | 0 | 940263.0176 | 0 | 940263.0176 | 0 | 0 | 219.7359 | 0 | 0 | 0 | 3000.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.4286 | 0 | 0 | 7061.3753 | 0 | 7061.3753 | 0 | 0 | 29.2591 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 511.5085 | 0 | 0 | 940.263 | 0 | 940.263 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.67726 | 11.8399 | 0 | 0 | 21.7643 | 21.7643 | 0
TN_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 1839.4111 | 6740.8028 | 9027.5632 | 1569.8902 | 13417.6985 | 0 | 5162.5769 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42762.1412 | 0 | 42759.9184 | 2.2229 | 2.2229 | 193.3221 | 708.4584 | 948.7969 | 164.9955 | 1410.2001 | 0 | 542.5868 | 0 | 0 | 0 | 0 | 525.9413 | 0 | 0 | 4494.301 | 0 | 4494.0674 | 0.23362 | 0.23362 | 6.2761 | 22.9996 | 30.802 | 5.3565 | 45.7812 | 0 | 17.6147 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 145.9044 | 0 | 145.8968 | 0.0075844 | 0.0075844 | 5.5983 | 0.97355 | 8.3208 | 3.2015 | 0 | 0 | 4.1802 | 1.1407 | 3.1033 | 0 | 0 | 26.5171 | 26.5184 | 0.0013785
TN_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 1488.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.0729 | 0 | 1488.0729 | 0 | 0 | 11.1754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.1754 | 0 | 11.1754 | 0 | 0 | 1.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4881 | 0 | 1.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27046 | 0 | 0 | 0 | 0.27046 | 0.27046 | 0
TN_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 1878.3111 | 6429.6033 | 7249.2805 | 1569.8902 | 13417.6985 | 0 | 4748.5705 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40297.5526 | 0 | 40297.5526 | 0 | 0 | 197.4105 | 675.7513 | 761.8994 | 164.9955 | 1410.2001 | 0 | 499.0748 | 0 | 0 | 0 | 0 | 525.9413 | 0 | 0 | 4235.2728 | 0 | 4235.2728 | 0 | 0 | 6.4088 | 21.9378 | 24.7345 | 5.3565 | 45.7812 | 0 | 16.2021 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.4952 | 0 | 137.4952 | 0 | 0 | 4.4956 | 0.97355 | 8.3208 | 2.9448 | 0 | 0 | 3.9872 | 1.1648 | 3.1033 | 0 | 0 | 24.99 | 24.99 | 0
TN_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | TN-MEMPHIS-TN | Zone3A | Zone3A(TN-MEMPHIS-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 1573.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3764 | 0 | 1573.3764 | 0 | 0 | 11.8161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8161 | 0 | 11.8161 | 0 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5734 | 0 | 1.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28596 | 0 | 0 | 0 | 0.28596 | 0.28596 | 0
TN_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 694152.6429 | 879099.5984 | 95757.7436 | 4077910.5986 | 543457.0788 | 610956.7993 | 96683.0063 | 258901.2863 | 331174.5843 | 12903.6637 | 0 | 0 | 0 | 7600997.0021 | 0 | 7600997.0021 | 0 | 543457.0788 | 0 | 72955.4428 | 92393.3678 | 10064.1388 | 428588.4039 | 57117.339 | 64211.5596 | 10161.384 | 27210.5252 | 34806.4488 | 1356.1751 | 0 | 0 | 0 | 798864.7849 | 0 | 798864.7849 | 0 | 57117.339 | 0 | 2368.4488 | 2999.4878 | 326.7254 | 13913.831 | 1854.2756 | 2084.5846 | 329.8824 | 883.3712 | 1129.9677 | 44.0273 | 0 | 0 | 0 | 25934.6018 | 0 | 25934.6018 | 0 | 1854.2756 | 6.016 | 0.6553 | 27.9065 | 4.181 | 0.66163 | 0.088304 | 4.7503 | 0 | 0 | 2.2663 | 0 | 52.0161 | 52.0161 | 0
TN_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 497708.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542388.3469 | 0 | 0 | 1040096.5948 | 0 | 1040096.5948 | 0 | 0 | 3737.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.3365 | 0 | 0 | 7811.1254 | 0 | 7811.1254 | 0 | 0 | 497.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542.3883 | 0 | 0 | 1040.0966 | 0 | 1040.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99824 | 1.0878 | 0 | 0 | 2.0861 | 2.0861 | 0
TN_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 655049.8739 | 715744.8845 | 95757.7436 | 4077910.5986 | 543384.8361 | 587208.3898 | 93004.184 | 232829.9952 | 330977.3061 | 11561.616 | 0 | 0 | 0 | 7343429.4278 | 0 | 7343428.8721 | 0.55571 | 543385.3918 | 0 | 68845.7418 | 75224.7874 | 10064.1388 | 428588.4039 | 57109.7463 | 61715.6018 | 9774.7397 | 24470.4325 | 34785.7149 | 1215.1258 | 0 | 0 | 0 | 771794.4329 | 0 | 771794.3745 | 0.058405 | 57109.8047 | 0 | 2235.0302 | 2442.1215 | 326.7254 | 13913.831 | 1854.0291 | 2003.555 | 317.3303 | 794.4159 | 1129.2946 | 39.4482 | 0 | 0 | 0 | 25055.7812 | 0 | 25055.7793 | 0.0018961 | 1854.031 | 4.8981 | 0.6553 | 27.9065 | 4.0185 | 0.63646 | 0.07912 | 4.4827 | 0 | 0 | 2.265 | 0 | 50.2535 | 50.2535 | 3.8029e-06
TN_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 477955.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542445.2159 | 0 | 0 | 1020400.955 | 0 | 1020400.955 | 0 | 0 | 3589.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.7636 | 0 | 0 | 7663.2112 | 0 | 7663.2112 | 0 | 0 | 477.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542.4452 | 0 | 0 | 1020.401 | 0 | 1020.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95862 | 1.088 | 0 | 0 | 2.0466 | 2.0466 | 0
TN_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 31595.0817 | 28374.723 | 7207.602 | 142004.2074 | 0 | 21934.0054 | 0 | 0 | 0 | 0 | 108741.9857 | 0 | 0 | 339857.6052 | 0 | 339861.2173 | -3.6121 | -3.6121 | 0 | 3320.6431 | 2982.1834 | 757.519 | 14924.6422 | 0 | 2305.264 | 0 | 0 | 0 | 0 | 11428.7827 | 0 | 0 | 35719.0343 | 0 | 35719.4139 | -0.37964 | -0.37964 | 0 | 107.8024 | 96.8146 | 24.5923 | 484.5184 | 0 | 74.8388 | 0 | 0 | 0 | 0 | 371.0277 | 0 | 0 | 1159.5941 | 0 | 1159.6065 | -0.012325 | -0.012325 | 2.8693 | 0.72886 | 14.3599 | 2.218 | 0 | 0 | 3.195 | 0 | 10.9963 | 0 | 0 | 34.3679 | 34.3675 | -0.00036527
TN_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 46234.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46234.5191 | 0 | 46234.5191 | 0 | 0 | 347.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347.2212 | 0 | 347.2212 | 0 | 0 | 46.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.2345 | 0 | 46.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3703 | 0 | 0 | 0 | 1.3703 | 1.3703 | 0
TN_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 30405.8552 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 21261.5923 | 0 | 0 | 0 | 0 | 108775.3285 | 0 | 0 | 332836.1672 | 0 | 332838.39 | -2.2229 | -2.2229 | 0 | 3195.6554 | 2436.3843 | 757.519 | 14924.6422 | 0 | 2234.5933 | 0 | 0 | 0 | 0 | 11432.287 | 0 | 0 | 34981.0812 | 0 | 34981.3148 | -0.23362 | -0.23362 | 0 | 103.7448 | 79.0956 | 24.5923 | 484.5184 | 0 | 72.5446 | 0 | 0 | 0 | 0 | 371.1414 | 0 | 0 | 1135.637 | 0 | 1135.6446 | -0.0075844 | -0.0075844 | 2.3442 | 0.72886 | 14.3599 | 2.15 | 0 | 0 | 3.0747 | 0 | 10.9997 | 0 | 0 | 33.6577 | 33.6575 | -0.00022478
TN_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 55267.2163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55267.2163 | 0 | 55267.2163 | 0 | 0 | 415.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.0568 | 0 | 415.0568 | 0 | 0 | 55.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2672 | 0 | 55.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.638 | 0 | 0 | 0 | 1.638 | 1.638 | 0
TN_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 116980.4359 | 95991.1432 | 7115.9093 | 317887.4784 | 4818.0346 | 91175.8871 | 455.6849 | 0 | 0 | 18910.9248 | 7179.8163 | 17621.6699 | 0 | 678136.9845 | 0 | 678135.5952 | 1.3893 | 4819.4239 | 0 | 12294.6438 | 10088.6691 | 747.8821 | 33409.974 | 506.3754 | 9582.5857 | 47.8925 | 0 | 0 | 1987.5382 | 754.5987 | 1852.0375 | 0 | 71272.1971 | 0 | 71272.0511 | 0.14601 | 506.5215 | 0 | 399.1372 | 327.5218 | 24.2795 | 1084.6321 | 16.4391 | 311.0921 | 1.5548 | 0 | 0 | 64.5241 | 24.4975 | 60.1251 | 0 | 2313.8034 | 0 | 2313.7987 | 0.0047402 | 16.4439 | 4.4284 | 0.32828 | 14.6653 | 4.2063 | 0.021022 | 0.87243 | 5.3967 | 0 | 0.33123 | 0 | 0.81295 | 31.2849 | 31.2849 | 6.4093e-05
TN_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 241219.457 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113349.4494 | 0 | 0 | 696759.3213 | 0 | 696759.3213 | 0 | 0 | 1811.5581 | 0 | 0 | 0 | 2569.85 | 0 | 0 | 0 | 0 | 0 | 0 | 851.2544 | 0 | 0 | 5232.6625 | 0 | 5232.6625 | 0 | 0 | 241.2195 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3494 | 0 | 0 | 696.7593 | 0 | 696.7593 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.2615 | 1.5326 | 0 | 0 | 9.4209 | 9.4209 | 0
TN_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 110931.4962 | 77891.5598 | 7115.9093 | 312483.1662 | 4743.0133 | 79906.0207 | 305.6423 | 0 | 0 | 22461.9331 | 7179.8163 | 12492.4358 | 0 | 635510.993 | 0 | 635510.7152 | 0.27786 | 4743.2912 | 0 | 11658.9003 | 8186.4029 | 747.8821 | 32841.9808 | 498.4907 | 8398.1228 | 32.123 | 0 | 0 | 2360.7492 | 754.5987 | 1312.955 | 0 | 66792.2054 | 0 | 66792.1762 | 0.029203 | 498.5199 | 0 | 378.4983 | 265.766 | 24.2795 | 1066.1926 | 16.1832 | 272.6393 | 1.0429 | 0 | 0 | 76.6401 | 24.4975 | 42.6242 | 0 | 2168.3635 | 0 | 2168.3626 | 0.00094805 | 16.1841 | 3.5934 | 0.32828 | 14.416 | 3.6864 | 0.0141 | 1.0363 | 5.1177 | 0 | 0.33123 | 0 | 0.57632 | 29.3184 | 29.3185 | 1.2819e-05
TN_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 228414.4477 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 113084.0606 | 0 | 0 | 683688.9232 | 0 | 683688.9232 | 0 | 0 | 1715.3925 | 0 | 0 | 0 | 2569.85 | 0 | 0 | 0 | 0 | 0 | 0 | 849.2613 | 0 | 0 | 5134.5038 | 0 | 5134.5038 | 0 | 0 | 228.4144 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0841 | 0 | 0 | 683.6889 | 0 | 683.6889 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.0884 | 1.529 | 0 | 0 | 9.2442 | 9.2442 | 0
TN_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 42289.7849 | 83243.0792 | 10680.8103 | 53987.5506 | 0 | 41356.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231557.4116 | 0 | 231557.4116 | 0 | 0 | 0 | 4444.6564 | 8748.8476 | 1122.5532 | 5674.0916 | 0 | 4346.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24336.684 | 0 | 24336.684 | 0 | 0 | 0 | 144.2927 | 284.0254 | 36.4429 | 184.2055 | 0 | 141.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790.0739 | 0 | 790.0739 | 0 | 0 | 11.5027 | 1.4759 | 7.4601 | 5.7147 | 0 | 0 | 5.8437 | 0 | 0 | 0 | 0 | 31.9972 | 31.9972 | 0
TN_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 246934.7943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88971.5931 | 0 | 0 | 335906.3873 | 0 | 335906.3873 | 0 | 0 | 1854.4803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668.1767 | 0 | 0 | 2522.657 | 0 | 2522.657 | 0 | 0 | 246.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9716 | 0 | 0 | 335.9064 | 0 | 335.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0006 | 3.6033 | 0 | 0 | 13.6039 | 13.6039 | 0
TN_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 0 | 39430.6398 | 65665.8664 | 10680.8103 | 53987.5506 | 0 | 39355.6185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209120.4856 | 0 | 209120.4856 | 0 | 0 | 0 | 4144.1602 | 6901.4826 | 1122.5532 | 5674.0916 | 0 | 4136.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21978.563 | 0 | 21978.563 | 0 | 0 | 0 | 134.5373 | 224.0519 | 36.4429 | 184.2055 | 0 | 134.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 713.5191 | 0 | 713.5191 | 0 | 0 | 9.0739 | 1.4759 | 7.4601 | 5.4383 | 0 | 0 | 5.4486 | 0 | 0 | 0 | 0 | 28.8968 | 28.8968 | 0
TN_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 267540.3385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88990.5494 | 0 | 0 | 356530.8879 | 0 | 356530.8879 | 0 | 0 | 2009.2279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668.319 | 0 | 0 | 2677.547 | 0 | 2677.547 | 0 | 0 | 267.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9905 | 0 | 0 | 356.5309 | 0 | 356.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8351 | 3.604 | 0 | 0 | 14.4391 | 14.4391 | 0
TN_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 16279.6222 | 78847.3867 | 79100.2363 | 12311.829 | 154949.5496 | 0 | 46046.4071 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 387607.2736 | 0 | 387604.7729 | 2.5007 | 2.5007 | 1710.9883 | 8286.8603 | 8313.4348 | 1293.9732 | 16285.1977 | 0 | 4839.4774 | 7.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 40737.5245 | 0 | 40737.2616 | 0.26282 | 0.26282 | 55.5461 | 269.0273 | 269.89 | 42.008 | 528.6879 | 0 | 157.1103 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1322.516 | 0 | 1322.5075 | 0.0085324 | 0.0085324 | 6.2472 | 0.97236 | 12.2376 | 3.6366 | 0.0057056 | 0 | 6.2272 | 1.2857 | 0 | 0 | 0 | 30.6122 | 30.6124 | 0.0001975
TN_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 42092.5583 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 562955.9784 | 0 | 0 | 1004543.9746 | 0 | 1004543.9746 | 0 | 0 | 316.1151 | 0 | 0 | 0 | 3000.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 4227.7994 | 0 | 0 | 7544.1252 | 0 | 7544.1252 | 0 | 0 | 42.0926 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 562.956 | 0 | 0 | 1004.544 | 0 | 1004.544 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.97432 | 13.0308 | 0 | 0 | 23.2523 | 23.2523 | 0
TN_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 19013.7318 | 73584.7814 | 50719.9562 | 12311.829 | 154949.5496 | 0 | 43662.3968 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 354314.4876 | 0 | 354313.0984 | 1.3893 | 1.3893 | 1998.3432 | 7733.7605 | 5330.6674 | 1293.9732 | 16285.1977 | 0 | 4588.9179 | 7.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 37238.4527 | 0 | 37238.3066 | 0.14601 | 0.14601 | 64.8749 | 251.0713 | 173.0565 | 42.008 | 528.6879 | 0 | 148.9761 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.921 | 0 | 1208.9163 | 0.0047402 | 0.0047402 | 4.0058 | 0.97236 | 12.2376 | 3.4484 | 0.0057056 | 0 | 5.8116 | 1.5017 | 0 | 0 | 0 | 27.9829 | 27.983 | 0.00010972
TN_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 42765.5085 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 563012.8475 | 0 | 0 | 1005273.7938 | 0 | 1005273.7938 | 0 | 0 | 321.169 | 0 | 0 | 0 | 3000.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 4228.2265 | 0 | 0 | 7549.6062 | 0 | 7549.6062 | 0 | 0 | 42.7655 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 563.0128 | 0 | 0 | 1005.2738 | 0 | 1005.2738 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.9899 | 13.0321 | 0 | 0 | 23.2691 | 23.2691 | 0
TN_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 2092.2607 | 4542.9565 | 8808.0564 | 1589.3401 | 13417.6985 | 0 | 4884.7202 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40339.2311 | 0 | 40338.3975 | 0.83357 | 0.83357 | 219.8966 | 477.4647 | 925.7267 | 167.0396 | 1410.2001 | 0 | 513.3841 | 0 | 0 | 0 | 0 | 525.9413 | 0 | 0 | 4239.6532 | 0 | 4239.5656 | 0.087608 | 0.087608 | 7.1388 | 15.5006 | 30.0531 | 5.4228 | 45.7812 | 0 | 16.6667 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 137.6375 | 0 | 137.6346 | 0.0028441 | 0.0028441 | 5.4622 | 0.98561 | 8.3208 | 3.0292 | 0 | 0 | 2.8173 | 1.2975 | 3.1033 | 0 | 0 | 25.0154 | 25.0159 | 0.00051693
TN_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 2862.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2862.4077 | 0 | 2862.4077 | 0 | 0 | 21.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4967 | 0 | 21.4967 | 0 | 0 | 2.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8624 | 0 | 2.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52025 | 0 | 0 | 0 | 0.52025 | 0.52025 | 0
TN_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Electricity | 2131.1606 | 4287.3284 | 7096.4593 | 1589.3401 | 13417.6985 | 0 | 4490.1638 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38016.3493 | 0 | 38015.2379 | 1.1114 | 1.1114 | 223.985 | 450.5982 | 745.8379 | 167.0396 | 1410.2001 | 0 | 471.9162 | 0 | 0 | 0 | 0 | 525.9413 | 0 | 0 | 3995.5183 | 0 | 3995.4015 | 0.11681 | 0.11681 | 7.2715 | 14.6284 | 24.2131 | 5.4228 | 45.7812 | 0 | 15.3204 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 129.7118 | 0 | 129.708 | 0.0037922 | 0.0037922 | 4.4008 | 0.98561 | 8.3208 | 2.7845 | 0 | 0 | 2.6587 | 1.3216 | 3.1033 | 0 | 0 | 23.5747 | 23.5754 | 0.00068924
TN_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | TN-BRISTOL-TN | Zone4A | Zone4A(TN-BRISTOL-TN) |  |  | TN | 0.1051 | 0.00751 |  |  |  | Natural Gas | 3061.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3061.4493 | 0 | 3061.4493 | 0 | 0 | 22.9915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9915 | 0 | 22.9915 | 0 | 0 | 3.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0614 | 0 | 3.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55642 | 0 | 0 | 0 | 0.55642 | 0.55642 | 0
TX_1A_LO_2016_EL | 1A | LO | EL |  |  | OfficeLarge | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1697045.7226 | 880097.1038 | 95415.9799 | 4077910.5986 | 543457.0788 | 604805.0526 | 183688.2648 | 590895.5478 | 1091.9767 | 32414.7589 | 0 | 0 | 0 | 8706822.0846 | 0 | 8706822.6404 | -0.55571 | 543456.5231 | 0 | 131351.3389 | 68119.5158 | 7385.1968 | 315630.2803 | 42063.5779 | 46811.9111 | 14217.4717 | 45735.3154 | 84.519 | 2508.9023 | 0 | 0 | 0 | 673908.0294 | 0 | 673908.0724 | -0.043012 | 42063.5349 | 0 | 5790.32 | 3002.8913 | 325.5593 | 13913.831 | 1854.2756 | 2063.5948 | 626.7444 | 2016.1356 | 3.7258 | 110.5992 | 0 | 0 | 0 | 29707.677 | 0 | 29707.6788 | -0.0018961 | 1854.2737 | 6.0228 | 0.65296 | 27.9065 | 4.1389 | 1.257 | 0.22182 | 11.6134 | 0 | 0 | 0.0074728 | 0 | 59.5836 | 59.5836 | -3.8029e-06
TX_1A_LO_2016_NG | 1A | LO | NG |  |  | OfficeLarge | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 338531.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434337.1952 | 0 | 0 | 772869.036 | 0 | 772869.036 | 0 | 0 | 2180.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2797.5659 | 0 | 0 | 4978.0495 | 0 | 4978.0495 | 0 | 0 | 338.5318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.3372 | 0 | 0 | 772.869 | 0 | 772.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67898 | 0.87113 | 0 | 0 | 1.5501 | 1.5501 | 0
TX_1A_LO_2019_EL | 1A | LO | EL |  |  | OfficeLarge | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1599198.4969 | 716564.5617 | 95415.9799 | 4077910.5986 | 543384.8361 | 587805.7817 | 177066.9404 | 534857.415 | 1094.7553 | 26699.2473 | 0 | 0 | 0 | 8359998.6128 | 0 | 8359994.4449 | 4.1679 | 543389.004 | 0 | 123777.9637 | 55462.0971 | 7385.1968 | 315630.2803 | 42057.9863 | 45496.1675 | 13704.9812 | 41397.9639 | 84.7341 | 2066.5217 | 0 | 0 | 0 | 647063.8926 | 0 | 647063.57 | 0.32259 | 42058.3089 | 0 | 5456.4653 | 2444.9183 | 325.5593 | 13913.831 | 1854.0291 | 2005.5933 | 604.1524 | 1824.9335 | 3.7353 | 91.0978 | 0 | 0 | 0 | 28524.3153 | 0 | 28524.301 | 0.014221 | 1854.0433 | 4.9037 | 0.65296 | 27.9065 | 4.0225 | 1.2117 | 0.18271 | 10.9438 | 0 | 0 | 0.0074918 | 0 | 57.2102 | 57.2102 | 2.8522e-05
TX_1A_LO_2019_NG | 1A | LO | NG |  |  | OfficeLarge | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 166038.6031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434346.6734 | 0 | 0 | 600385.2765 | 0 | 600385.2765 | 0 | 0 | 1069.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2797.6269 | 0 | 0 | 3867.0816 | 0 | 3867.0816 | 0 | 0 | 166.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.3467 | 0 | 0 | 600.3853 | 0 | 600.3853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33302 | 0.87115 | 0 | 0 | 1.2042 | 1.2042 | 0
TX_1A_MA_2016_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 87149.744 | 28374.723 | 7221.4948 | 142004.2074 | 0 | 30700.3833 | 0 | 0 | 0 | 0 | 87341.4651 | 0 | 0 | 382792.0176 | 0 | 382788.9611 | 3.0564 | 3.0564 | 0 | 6745.3902 | 2196.2036 | 558.9437 | 10991.1257 | 0 | 2376.2097 | 0 | 0 | 0 | 0 | 6760.2294 | 0 | 0 | 29628.1022 | 0 | 29627.8656 | 0.23657 | 0.23657 | 0 | 297.3549 | 96.8146 | 24.6397 | 484.5184 | 0 | 104.7497 | 0 | 0 | 0 | 0 | 298.0091 | 0 | 0 | 1306.0864 | 0 | 1306.0759 | 0.010429 | 0.010429 | 2.8693 | 0.73026 | 14.3599 | 3.1045 | 0 | 0 | 8.8129 | 0 | 8.8323 | 0 | 0 | 38.7089 | 38.7092 | 0.00030908
TX_1A_MA_2016_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 15288.2901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15288.2901 | 0 | 15288.2901 | 0 | 0 | 98.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4719 | 0 | 98.4719 | 0 | 0 | 15.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2883 | 0 | 15.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45311 | 0 | 0 | 0 | 0.45311 | 0.45311 | 0
TX_1A_MA_2019_EL | 1A | MA | EL |  |  | ApartmentMidRise | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 73315.2605 | 23181.5818 | 7221.4948 | 142004.2074 | 0 | 28538.6584 | 0 | 0 | 0 | 0 | 87288.6723 | 0 | 0 | 361549.8753 | 0 | 361549.5974 | 0.27786 | 0.27786 | 0 | 5674.6012 | 1794.2544 | 558.9437 | 10991.1257 | 0 | 2208.8922 | 0 | 0 | 0 | 0 | 6756.1432 | 0 | 0 | 27983.9603 | 0 | 27983.9388 | 0.021506 | 0.021506 | 0 | 250.1517 | 79.0956 | 24.6397 | 484.5184 | 0 | 97.3739 | 0 | 0 | 0 | 0 | 297.8289 | 0 | 0 | 1233.6082 | 0 | 1233.6072 | 0.00094805 | 0.00094805 | 2.3442 | 0.73026 | 14.3599 | 2.8859 | 0 | 0 | 7.4139 | 0 | 8.8269 | 0 | 0 | 36.5611 | 36.5611 | 2.8098e-05
TX_1A_MA_2019_NG | 1A | MA | NG |  |  | ApartmentMidRise | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 5383.6012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5383.6012 | 0 | 5383.6012 | 0 | 0 | 34.6758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.6758 | 0 | 34.6758 | 0 | 0 | 5.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3836 | 0 | 5.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15956 | 0 | 0 | 0 | 0.15956 | 0.15956 | 0
TX_1A_PS_2016_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 335973.169 | 98069.5111 | 7124.245 | 317887.4784 | 4818.0346 | 113696.1701 | 152.8212 | 0 | 0 | 31800.6957 | 7177.0377 | 17843.9552 | 0 | 934543.118 | 0 | 934542.2844 | 0.83357 | 4818.8682 | 0 | 26004.3233 | 7590.5802 | 551.4166 | 24604.4908 | 372.9159 | 8800.0836 | 11.8284 | 0 | 0 | 2461.3738 | 555.5027 | 1381.1221 | 0 | 72333.6373 | 0 | 72333.5728 | 0.064518 | 372.9804 | 0 | 1146.3405 | 334.6132 | 24.3079 | 1084.6321 | 16.4391 | 387.9313 | 0.52143 | 0 | 0 | 108.504 | 24.4881 | 60.8836 | 0 | 3188.6611 | 0 | 3188.6583 | 0.0028441 | 16.442 | 4.5243 | 0.32867 | 14.6653 | 5.2452 | 0.0070502 | 1.4671 | 15.4997 | 0 | 0.3311 | 0 | 0.82321 | 43.1139 | 43.1139 | 3.8456e-05
TX_1A_PS_2016_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 81787.1393 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 90990.4435 | 0 | 0 | 514967.9976 | 0 | 514967.9976 | 0 | 0 | 526.791 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 586.0694 | 0 | 0 | 3316.9089 | 0 | 3316.9089 | 0 | 0 | 81.7871 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9904 | 0 | 0 | 514.968 | 0 | 514.968 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.1058 | 1.2303 | 0 | 0 | 6.9629 | 6.9629 | 0
TX_1A_PS_2019_EL | 1A | PS | EL |  |  | SchoolPrimary | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 308921.0437 | 79628.164 | 7124.245 | 312483.1662 | 4745.7919 | 100356.2714 | 116.6998 | 0 | 0 | 31100.4969 | 7177.0377 | 12595.2428 | 0 | 864248.1595 | 0 | 864249.2709 | -1.1114 | 4744.6805 | 0 | 23910.4888 | 6163.2199 | 551.4166 | 24186.1971 | 367.3243 | 7767.5754 | 9.0326 | 0 | 0 | 2407.1785 | 555.5027 | 974.8718 | 0 | 66892.8075 | 0 | 66892.8936 | -0.086024 | 367.2383 | 0 | 1054.0386 | 271.6913 | 24.3079 | 1066.1926 | 16.1926 | 342.4156 | 0.39818 | 0 | 0 | 106.1149 | 24.4881 | 42.975 | 0 | 2948.8147 | 0 | 2948.8185 | -0.0037922 | 16.1888 | 3.6735 | 0.32867 | 14.416 | 4.6298 | 0.0053838 | 1.4348 | 14.2517 | 0 | 0.3311 | 0 | 0.58106 | 39.871 | 39.8709 | -5.1274e-05
TX_1A_PS_2019_NG | 1A | PS | NG |  |  | SchoolPrimary | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 57485.1083 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 90800.8801 | 0 | 0 | 490476.4033 | 0 | 490476.4033 | 0 | 0 | 370.2616 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8485 | 0 | 0 | 3159.1585 | 0 | 3159.1585 | 0 | 0 | 57.4851 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8009 | 0 | 0 | 490.4764 | 0 | 490.4764 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.77726 | 1.2277 | 0 | 0 | 6.6317 | 6.6317 | 0
TX_1A_RS_2016_EL | 1A | RS | EL |  |  | RetailStandalone | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 126886.0261 | 81264.7398 | 10703.0389 | 53987.5506 | 0 | 41033.8728 | 0 | 0 | 0 | 7424.3302 | 0 | 0 | 0 | 321299.5583 | 0 | 321299.8362 | -0.27786 | -0.27786 | 0 | 9820.9784 | 6289.8909 | 828.4152 | 4178.6364 | 0 | 3176.0218 | 0 | 0 | 0 | 574.6432 | 0 | 0 | 0 | 24868.5858 | 0 | 24868.6073 | -0.021506 | -0.021506 | 0 | 432.9351 | 277.2753 | 36.5188 | 184.2055 | 0 | 140.0076 | 0 | 0 | 0 | 25.3318 | 0 | 0 | 0 | 1096.2741 | 0 | 1096.275 | -0.00094805 | -0.00094805 | 11.2294 | 1.479 | 7.4601 | 5.6702 | 0 | 1.0259 | 17.5334 | 0 | 0 | 0 | 0 | 44.398 | 44.3979 | -3.8395e-05
TX_1A_RS_2016_NG | 1A | RS | NG |  |  | RetailStandalone | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 23714.3843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82488.524 | 0 | 0 | 106202.9083 | 0 | 106202.9083 | 0 | 0 | 152.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.3086 | 0 | 0 | 684.0529 | 0 | 684.0529 | 0 | 0 | 23.7144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4885 | 0 | 0 | 106.2029 | 0 | 106.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96041 | 3.3407 | 0 | 0 | 4.3011 | 4.3011 | 0
TX_1A_RS_2019_EL | 1A | RS | EL |  |  | RetailStandalone | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 135524.5899 | 63887.5837 | 10703.0389 | 53987.5506 | 0 | 41864.6642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305967.4274 | 0 | 305968.8166 | -1.3893 | -1.3893 | 0 | 10489.6033 | 4944.899 | 828.4152 | 4178.6364 | 0 | 3240.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23681.8789 | 0 | 23681.9864 | -0.10753 | -0.10753 | 0 | 462.4099 | 217.9844 | 36.5188 | 184.2055 | 0 | 142.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.9609 | 0 | 1043.9656 | -0.0047402 | -0.0047402 | 8.8281 | 1.479 | 7.4601 | 5.785 | 0 | 0 | 18.7271 | 0 | 0 | 0 | 0 | 42.2795 | 42.2793 | -0.00019197
TX_1A_RS_2019_NG | 1A | RS | NG |  |  | RetailStandalone | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 50622.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82488.524 | 0 | 0 | 133111.4363 | 0 | 133111.4363 | 0 | 0 | 326.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.3086 | 0 | 0 | 857.3708 | 0 | 857.3708 | 0 | 0 | 50.6229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4885 | 0 | 0 | 133.1114 | 0 | 133.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0502 | 3.3407 | 0 | 0 | 5.3909 | 5.3909 | 0
TX_1A_SH_2016_EL | 1A | SH | EL |  |  | HotelSmall | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 1867.1968 | 157433.5882 | 79814.328 | 12331.2789 | 154949.5496 | 0 | 48222.0248 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 454690.209 | 0 | 454691.5983 | -1.3893 | -1.3893 | 144.521 | 12185.3597 | 6177.629 | 954.441 | 11993.0951 | 0 | 3732.3847 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 35193.0222 | 0 | 35193.1297 | -0.10753 | -0.10753 | 6.3709 | 537.1634 | 272.3265 | 42.0743 | 528.6879 | 0 | 164.5335 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1551.403 | 0 | 1551.4077 | -0.0047402 | -0.0047402 | 6.3036 | 0.9739 | 12.2376 | 3.8085 | 0.0057056 | 0 | 12.4338 | 0.14747 | 0 | 0 | 0 | 35.9106 | 35.9104 | -0.00010972
TX_1A_SH_2016_NG | 1A | SH | NG |  |  | HotelSmall | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 2796.0605 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 445966.9113 | 0 | 0 | 848258.4097 | 0 | 848258.4097 | 0 | 0 | 18.0094 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 2872.4729 | 0 | 0 | 5463.6324 | 0 | 5463.6324 | 0 | 0 | 2.7961 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 445.9669 | 0 | 0 | 848.2584 | 0 | 848.2584 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.064721 | 10.3228 | 0 | 0 | 19.6347 | 19.6347 | 0
TX_1A_SH_2019_EL | 1A | SH | EL |  |  | HotelSmall | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 2306.2103 | 149467.4375 | 51331.2409 | 12331.2789 | 154949.5496 | 0 | 46040.8499 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 416498.81 | 0 | 416494.6421 | 4.1679 | 4.1679 | 178.5007 | 11568.7797 | 3973.038 | 954.441 | 11993.0951 | 0 | 3563.5618 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 32237.0079 | 0 | 32236.6853 | 0.32259 | 0.32259 | 7.8688 | 509.9829 | 175.1422 | 42.0743 | 528.6879 | 0 | 157.0914 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.0939 | 0 | 1421.0797 | 0.014221 | 0.014221 | 4.054 | 0.9739 | 12.2376 | 3.6362 | 0.0057056 | 0 | 11.8046 | 0.18214 | 0 | 0 | 0 | 32.8938 | 32.8942 | 0.00032917
TX_1A_SH_2019_NG | 1A | SH | NG |  |  | HotelSmall | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 3364.7508 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 445995.3458 | 0 | 0 | 848855.5345 | 0 | 848855.5345 | 0 | 0 | 21.6724 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 2872.656 | 0 | 0 | 5467.4785 | 0 | 5467.4785 | 0 | 0 | 3.3648 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 445.9953 | 0 | 0 | 848.8555 | 0 | 848.8555 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.077884 | 10.3235 | 0 | 0 | 19.6485 | 19.6485 | 0
TX_1A_SO_2016_EL | 1A | SO | EL |  |  | OfficeSmall | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 72.2427 | 12134.0007 | 8969.2133 | 1581.0044 | 13417.6985 | 0 | 5487.6692 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 46666.0274 | 0 | 46664.916 | 1.1114 | 1.1114 | 5.5916 | 939.1717 | 694.2171 | 122.3697 | 1038.5299 | 0 | 424.7456 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3611.9505 | 0 | 3611.8645 | 0.086024 | 0.086024 | 0.24649 | 41.4012 | 30.603 | 5.3944 | 45.7812 | 0 | 18.7239 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 159.2245 | 0 | 159.2207 | 0.0037922 | 0.0037922 | 5.5622 | 0.98044 | 8.3208 | 3.4031 | 0 | 0 | 7.5248 | 0.0448 | 3.1033 | 0 | 0 | 28.9387 | 28.9394 | 0.00068924
TX_1A_SO_2016_NG | 1A | SO | NG |  |  | OfficeSmall | STD2016 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TX_1A_SO_2019_EL | 1A | SO | EL |  |  | OfficeSmall | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 72.2427 | 11525.4946 | 7235.3876 | 1581.0044 | 13417.6985 | 0 | 5009.7557 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43845.7822 | 0 | 43845.7822 | 0 | 0 | 5.5916 | 892.0733 | 560.019 | 122.3697 | 1038.5299 | 0 | 387.7551 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3393.6635 | 0 | 3393.6635 | 0 | 0 | 0.24649 | 39.325 | 24.6871 | 5.3944 | 45.7812 | 0 | 17.0933 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 149.6018 | 0 | 149.6018 | 0 | 0 | 4.4869 | 0.98044 | 8.3208 | 3.1067 | 0 | 0 | 7.1474 | 0.0448 | 3.1033 | 0 | 0 | 27.1904 | 27.1904 | 0
TX_1A_SO_2019_NG | 1A | SO | NG |  |  | OfficeSmall | STD2019 | TX-BROWNSVILLE-TX | Zone1A | Zone1A(TX-BROWNSVILLE-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TX_2A_LO_2016_EL | 2A | LO | EL |  |  | OfficeLarge | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1208206.9291 | 880586.1315 | 95160.3517 | 4077910.5986 | 543457.0788 | 575505.067 | 145524.6514 | 446896.3295 | 127547.325 | 15326.5738 | 0 | 0 | 0 | 8116121.0365 | 0 | 8116120.4808 | 0.55571 | 543457.6346 | 0 | 93515.2163 | 68157.3666 | 7365.4112 | 315630.2803 | 42063.5779 | 44544.0922 | 11263.608 | 34589.7759 | 9872.163 | 1186.2768 | 0 | 0 | 0 | 628187.7682 | 0 | 628187.7252 | 0.043012 | 42063.6209 | 0 | 4122.402 | 3004.5599 | 324.6871 | 13913.831 | 1854.2756 | 1963.6233 | 496.5301 | 1524.8103 | 435.1915 | 52.2943 | 0 | 0 | 0 | 27692.205 | 0 | 27692.2031 | 0.0018961 | 1854.2774 | 6.0261 | 0.65121 | 27.9065 | 3.9384 | 0.99587 | 0.10488 | 8.2682 | 0 | 0 | 0.87285 | 0 | 55.5413 | 55.5413 | 3.8029e-06
TX_2A_LO_2016_NG | 2A | LO | NG |  |  | OfficeLarge | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 312627.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460032.5174 | 0 | 0 | 772660.5162 | 0 | 772660.5162 | 0 | 0 | 2013.6369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.0694 | 0 | 0 | 4976.7064 | 0 | 4976.7064 | 0 | 0 | 312.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460.0325 | 0 | 0 | 772.6605 | 0 | 772.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62703 | 0.92267 | 0 | 0 | 1.5497 | 1.5497 | 0
TX_2A_LO_2019_EL | 2A | LO | EL |  |  | OfficeLarge | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1144377.6952 | 716347.8335 | 95160.3517 | 4077910.5986 | 543384.8361 | 560984.2775 | 141203.9802 | 403631.2677 | 127475.0823 | 13467.7127 | 0 | 0 | 0 | 7823943.6356 | 0 | 7823945.0249 | -1.3893 | 543383.4468 | 0 | 88574.8336 | 55445.3223 | 7365.4112 | 315630.2803 | 42057.9863 | 43420.1831 | 10929.1881 | 31241.0601 | 9866.5714 | 1042.401 | 0 | 0 | 0 | 605573.2374 | 0 | 605573.3449 | -0.10753 | 42057.8788 | 0 | 3904.6167 | 2444.1788 | 324.6871 | 13913.831 | 1854.0291 | 1914.0784 | 481.788 | 1377.1899 | 434.945 | 45.9518 | 0 | 0 | 0 | 26695.2957 | 0 | 26695.3004 | -0.0047402 | 1854.0243 | 4.9022 | 0.65121 | 27.9065 | 3.839 | 0.9663 | 0.092164 | 7.8313 | 0 | 0 | 0.87235 | 0 | 53.5418 | 53.5418 | -9.5073e-06
TX_2A_LO_2019_NG | 2A | LO | NG |  |  | OfficeLarge | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 190719.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460032.5174 | 0 | 0 | 650752.2782 | 0 | 650752.2782 | 0 | 0 | 1228.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.0694 | 0 | 0 | 4191.4954 | 0 | 4191.4954 | 0 | 0 | 190.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460.0325 | 0 | 0 | 650.7523 | 0 | 650.7523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38252 | 0.92267 | 0 | 0 | 1.3052 | 1.3052 | 0
TX_2A_MA_2016_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 62517.7504 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 25876.7915 | 0 | 0 | 0 | 0 | 92487.3706 | 0 | 0 | 358476.7805 | 0 | 358474.002 | 2.7786 | 2.7786 | 0 | 4838.8739 | 2196.2036 | 558.5136 | 10991.1257 | 0 | 2002.8637 | 0 | 0 | 0 | 0 | 7158.5225 | 0 | 0 | 27746.1028 | 0 | 27745.8878 | 0.21506 | 0.21506 | 0 | 213.3106 | 96.8146 | 24.6208 | 484.5184 | 0 | 88.2916 | 0 | 0 | 0 | 0 | 315.5669 | 0 | 0 | 1223.1228 | 0 | 1223.1133 | 0.0094805 | 0.0094805 | 2.8693 | 0.7297 | 14.3599 | 2.6167 | 0 | 0 | 6.322 | 0 | 9.3526 | 0 | 0 | 36.2501 | 36.2503 | 0.00028098
TX_2A_MA_2016_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 29287.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29287.549 | 0 | 29287.549 | 0 | 0 | 188.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.6411 | 0 | 188.6411 | 0 | 0 | 29.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2875 | 0 | 29.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86801 | 0 | 0 | 0 | 0.86801 | 0.86801 | 0
TX_2A_MA_2019_EL | 2A | MA | EL |  |  | ApartmentMidRise | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 55251.7985 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 24882.0646 | 0 | 0 | 0 | 0 | 92395.6779 | 0 | 0 | 344931.268 | 0 | 344932.3794 | -1.1114 | -1.1114 | 0 | 4276.4892 | 1794.2544 | 558.5136 | 10991.1257 | 0 | 1925.8718 | 0 | 0 | 0 | 0 | 7151.4255 | 0 | 0 | 26697.6801 | 0 | 26697.7662 | -0.086024 | -0.086024 | 0 | 188.5191 | 79.0956 | 24.6208 | 484.5184 | 0 | 84.8976 | 0 | 0 | 0 | 0 | 315.2541 | 0 | 0 | 1176.9055 | 0 | 1176.9093 | -0.0037922 | -0.0037922 | 2.3442 | 0.7297 | 14.3599 | 2.5162 | 0 | 0 | 5.5872 | 0 | 9.3434 | 0 | 0 | 34.8807 | 34.8806 | -0.00011239
TX_2A_MA_2019_NG | 2A | MA | NG |  |  | ApartmentMidRise | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 6900.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6900.1086 | 0 | 6900.1086 | 0 | 0 | 44.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.4436 | 0 | 44.4436 | 0 | 0 | 6.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9001 | 0 | 6.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2045 | 0 | 0 | 0 | 0.2045 | 0.2045 | 0
TX_2A_PS_2016_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 240862.8314 | 99314.3089 | 7110.3521 | 317887.4784 | 4818.0346 | 100436.8499 | 205.6139 | 0 | 0 | 21450.5348 | 7179.8163 | 17757.8197 | 0 | 817023.6401 | 0 | 817024.4737 | -0.83357 | 4817.2011 | 0 | 18642.7832 | 7686.9275 | 550.3413 | 24604.4908 | 372.9159 | 7773.8122 | 15.9145 | 0 | 0 | 1660.2714 | 555.7178 | 1374.4552 | 0 | 63237.6297 | 0 | 63237.6943 | -0.064518 | 372.8514 | 0 | 821.824 | 338.8604 | 24.2605 | 1084.6321 | 16.4391 | 342.6905 | 0.70155 | 0 | 0 | 73.1892 | 24.4975 | 60.5897 | 0 | 2787.6847 | 0 | 2787.6875 | -0.0028441 | 16.4363 | 4.5817 | 0.32803 | 14.6653 | 4.6335 | 0.0094857 | 0.98959 | 11.1119 | 0 | 0.33123 | 0 | 0.81923 | 37.6923 | 37.6923 | -3.8456e-05
TX_2A_PS_2016_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 106648.3823 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96705.7808 | 0 | 0 | 545544.5779 | 0 | 545544.5779 | 0 | 0 | 686.9222 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 622.8819 | 0 | 0 | 3513.8526 | 0 | 3513.8526 | 0 | 0 | 106.6484 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7058 | 0 | 0 | 545.5446 | 0 | 545.5446 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.442 | 1.3076 | 0 | 0 | 7.3763 | 7.3763 | 0
TX_2A_PS_2019_EL | 2A | PS | EL |  |  | SchoolPrimary | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 221826.8711 | 79939.3635 | 7110.3521 | 312483.1662 | 4745.7919 | 89364.2616 | 163.9354 | 0 | 0 | 22917.618 | 7179.8163 | 12553.5643 | 0 | 758284.7405 | 0 | 758284.7405 | 0 | 4745.7919 | 0 | 17169.3998 | 6187.3067 | 550.3413 | 24186.1971 | 367.3243 | 6916.7939 | 12.6886 | 0 | 0 | 1773.8236 | 555.7178 | 971.6459 | 0 | 58691.2389 | 0 | 58691.2389 | 0 | 367.3243 | 0 | 756.8733 | 272.7531 | 24.2605 | 1066.1926 | 16.1926 | 304.9109 | 0.55935 | 0 | 0 | 78.1949 | 24.4975 | 42.8328 | 0 | 2587.2675 | 0 | 2587.2675 | 0 | 16.1926 | 3.6879 | 0.32803 | 14.416 | 4.1227 | 0.0075629 | 1.0573 | 10.2337 | 0 | 0.33123 | 0 | 0.57914 | 34.9825 | 34.9825 | 0
TX_2A_PS_2019_NG | 2A | PS | NG |  |  | SchoolPrimary | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 83085.6487 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 96506.7392 | 0 | 0 | 521782.8027 | 0 | 521782.8027 | 0 | 0 | 535.1547 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 621.5999 | 0 | 0 | 3360.803 | 0 | 3360.803 | 0 | 0 | 83.0856 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5067 | 0 | 0 | 521.7828 | 0 | 521.7828 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.1234 | 1.3049 | 0 | 0 | 7.055 | 7.055 | 0
TX_2A_RS_2016_EL | 2A | RS | EL |  |  | RetailStandalone | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 94810.2523 | 82509.5376 | 10694.7032 | 53987.5506 | 0 | 37716.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279718.3079 | 0 | 279717.1965 | 1.1114 | 1.1114 | 0 | 7338.3135 | 6386.2382 | 827.77 | 4178.6364 | 0 | 2919.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21650.197 | 0 | 21650.111 | 0.086024 | 0.086024 | 0 | 323.4926 | 281.5225 | 36.4903 | 184.2055 | 0 | 128.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954.3989 | 0 | 954.3951 | 0.0037922 | 0.0037922 | 11.4014 | 1.4778 | 7.4601 | 5.2117 | 0 | 0 | 13.1011 | 0 | 0 | 0 | 0 | 38.652 | 38.6521 | 0.00015358
TX_2A_RS_2016_NG | 2A | RS | NG |  |  | RetailStandalone | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 42528.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84014.5095 | 0 | 0 | 126543.0637 | 0 | 126543.0637 | 0 | 0 | 273.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 541.1375 | 0 | 0 | 815.0639 | 0 | 815.0639 | 0 | 0 | 42.5286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0145 | 0 | 0 | 126.5431 | 0 | 126.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7224 | 3.4025 | 0 | 0 | 5.1249 | 5.1249 | 0
TX_2A_RS_2019_EL | 2A | RS | EL |  |  | RetailStandalone | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 89555.9827 | 64871.1963 | 10694.7032 | 53987.5506 | 0 | 35782.3817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254891.8146 | 0 | 254892.3703 | -0.55571 | -0.55571 | 0 | 6931.6331 | 5021.0306 | 827.77 | 4178.6364 | 0 | 2769.5563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19728.6265 | 0 | 19728.6695 | -0.043012 | -0.043012 | 0 | 305.565 | 221.3405 | 36.4903 | 184.2055 | 0 | 122.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.6909 | 0 | 869.6928 | -0.0018961 | -0.0018961 | 8.9641 | 1.4778 | 7.4601 | 4.9445 | 0 | 0 | 12.3751 | 0 | 0 | 0 | 0 | 35.2216 | 35.2216 | -7.679e-05
TX_2A_RS_2019_NG | 2A | RS | NG |  |  | RetailStandalone | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 49381.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84014.5095 | 0 | 0 | 133395.7815 | 0 | 133395.7815 | 0 | 0 | 318.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 541.1375 | 0 | 0 | 859.2022 | 0 | 859.2022 | 0 | 0 | 49.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0145 | 0 | 0 | 133.3958 | 0 | 133.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9999 | 3.4025 | 0 | 0 | 5.4024 | 5.4024 | 0
TX_2A_SH_2016_EL | 2A | SH | EL |  |  | HotelSmall | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 3637.1438 | 128617.0732 | 79953.2563 | 12322.9432 | 154949.5496 | 0 | 46902.2056 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 426454.4144 | 0 | 426455.5258 | -1.1114 | -1.1114 | 281.5149 | 9954.9615 | 6188.382 | 953.7958 | 11993.0951 | 0 | 3630.2307 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 33007.5717 | 0 | 33007.6577 | -0.086024 | -0.086024 | 12.4099 | 438.8415 | 272.8005 | 42.0459 | 528.6879 | 0 | 160.0303 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1455.0625 | 0 | 1455.0663 | -0.0037922 | -0.0037922 | 6.3145 | 0.97324 | 12.2376 | 3.7042 | 0.0057056 | 0 | 10.1579 | 0.28725 | 0 | 0 | 0 | 33.6805 | 33.6804 | -8.7778e-05
TX_2A_SH_2016_NG | 2A | SH | NG |  |  | HotelSmall | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 7828.9694 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 471690.6679 | 0 | 0 | 879015.0753 | 0 | 879015.0753 | 0 | 0 | 50.4264 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3038.1596 | 0 | 0 | 5661.7361 | 0 | 5661.7361 | 0 | 0 | 7.829 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 471.6907 | 0 | 0 | 879.0151 | 0 | 879.0151 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.18122 | 10.9183 | 0 | 0 | 20.3466 | 20.3466 | 0
TX_2A_SH_2019_EL | 2A | SH | EL |  |  | HotelSmall | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 4270.657 | 121937.3989 | 51211.7625 | 12322.9432 | 154949.5496 | 0 | 44673.7951 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 389438.3491 | 0 | 389438.0712 | 0.27786 | 0.27786 | 330.5489 | 9437.9547 | 3963.7904 | 953.7958 | 11993.0951 | 0 | 3457.7517 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 30142.5282 | 0 | 30142.5067 | 0.021506 | 0.021506 | 14.5715 | 416.0504 | 174.7345 | 42.0459 | 528.6879 | 0 | 152.427 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.7636 | 0 | 1328.7627 | 0.00094805 | 0.00094805 | 4.0446 | 0.97324 | 12.2376 | 3.5282 | 0.0057056 | 0 | 9.6304 | 0.33729 | 0 | 0 | 0 | 30.757 | 30.757 | 2.1945e-05
TX_2A_SH_2019_NG | 2A | SH | NG |  |  | HotelSmall | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 8691.483 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 471690.6679 | 0 | 0 | 879877.5888 | 0 | 879877.5888 | 0 | 0 | 55.9818 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3038.1596 | 0 | 0 | 5667.2915 | 0 | 5667.2915 | 0 | 0 | 8.6915 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 471.6907 | 0 | 0 | 879.8776 | 0 | 879.8776 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.20118 | 10.9183 | 0 | 0 | 20.3666 | 20.3666 | 0
TX_2A_SO_2016_EL | 2A | SO | EL |  |  | OfficeSmall | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 361.2137 | 9405.4482 | 8983.1061 | 1578.2259 | 13417.6985 | 0 | 5282.0553 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 44031.9462 | 0 | 44032.5019 | -0.55571 | -0.55571 | 27.9579 | 727.9817 | 695.2924 | 122.1547 | 1038.5299 | 0 | 408.8311 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3408.0726 | 0 | 3408.1156 | -0.043012 | -0.043012 | 1.2325 | 32.0914 | 30.6504 | 5.3849 | 45.7812 | 0 | 18.0224 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 150.237 | 0 | 150.2389 | -0.0018961 | -0.0018961 | 5.5708 | 0.97872 | 8.3208 | 3.2756 | 0 | 0 | 5.8327 | 0.224 | 3.1033 | 0 | 0 | 27.3062 | 27.3059 | -0.00034462
TX_2A_SO_2016_NG | 2A | SO | NG |  |  | OfficeSmall | STD2016 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 104.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2599 | 0 | 104.2599 | 0 | 0 | 0.67154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67154 | 0 | 0.67154 | 0 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10426 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018949 | 0 | 0 | 0 | 0.018949 | 0.018949 | 0
TX_2A_SO_2019_EL | 2A | SO | EL |  |  | OfficeSmall | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 350.0994 | 9024.7846 | 7210.3805 | 1578.2259 | 13417.6985 | 0 | 4843.0417 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41428.4292 | 0 | 41428.4292 | 0 | 0 | 27.0977 | 698.5183 | 558.0835 | 122.1547 | 1038.5299 | 0 | 374.8514 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3206.5604 | 0 | 3206.5604 | 0 | 0 | 1.1945 | 30.7926 | 24.6018 | 5.3849 | 45.7812 | 0 | 16.5245 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 141.3538 | 0 | 141.3538 | 0 | 0 | 4.4714 | 0.97872 | 8.3208 | 3.0034 | 0 | 0 | 5.5966 | 0.21711 | 3.1033 | 0 | 0 | 25.6913 | 25.6913 | 0
TX_2A_SO_2019_NG | 2A | SO | NG |  |  | OfficeSmall | STD2019 | TX-HOUSTON-TX | Zone2A | Zone2A(TX-HOUSTON-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 104.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2599 | 0 | 104.2599 | 0 | 0 | 0.67154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67154 | 0 | 0.67154 | 0 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10426 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018949 | 0 | 0 | 0 | 0.018949 | 0.018949 | 0
TX_2B_LO_2016_EL | 2B | LO | EL |  |  | OfficeLarge | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1411539.6603 | 881058.4879 | 95771.6364 | 4077910.5986 | 543457.0788 | 610792.8638 | 163877.0844 | 474959.853 | 226717.1484 | 0 | 0 | 0 | 0 | 8486084.4117 | 0 | 8486083.3003 | 1.1114 | 543458.1903 | 0 | 109253.1697 | 68193.927 | 7412.7247 | 315630.2803 | 42063.5779 | 47275.3677 | 12684.0863 | 36761.8926 | 17547.9073 | 0 | 0 | 0 | 0 | 656822.9335 | 0 | 656822.8474 | 0.086024 | 42063.6639 | 0 | 4816.1733 | 3006.1716 | 326.7728 | 13913.831 | 1854.2756 | 2084.0253 | 559.1486 | 1620.563 | 773.5589 | 0 | 0 | 0 | 0 | 28954.52 | 0 | 28954.5162 | 0.0037922 | 1854.2793 | 6.0294 | 0.6554 | 27.9065 | 4.1799 | 1.1215 | 0 | 9.6596 | 0 | 0 | 1.5515 | 0 | 58.073 | 58.073 | 7.6059e-06
TX_2B_LO_2016_NG | 2B | LO | NG |  |  | OfficeLarge | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 312495.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437446.0354 | 0 | 0 | 749941.3399 | 0 | 749941.3399 | 0 | 0 | 2012.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2817.5899 | 0 | 0 | 4830.3722 | 0 | 4830.3722 | 0 | 0 | 312.4953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.446 | 0 | 0 | 749.9413 | 0 | 749.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62676 | 0.87737 | 0 | 0 | 1.5041 | 1.5041 | 0
TX_2B_LO_2019_EL | 2B | LO | EL |  |  | OfficeLarge | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 1346696.2497 | 716514.5475 | 95771.6364 | 4077910.5986 | 543384.8361 | 595802.4966 | 157083.4888 | 427229.6345 | 226583.7772 | 0 | 0 | 0 | 0 | 8186977.2655 | 0 | 8186975.3205 | 1.945 | 543386.7811 | 0 | 104234.2897 | 55458.226 | 7412.7247 | 315630.2803 | 42057.9863 | 46115.1132 | 12158.262 | 33067.5737 | 17537.5844 | 0 | 0 | 0 | 0 | 633672.0403 | 0 | 633671.8898 | 0.15054 | 42058.1369 | 0 | 4594.9276 | 2444.7476 | 326.7728 | 13913.831 | 1854.0291 | 2032.8781 | 535.9689 | 1457.7075 | 773.1038 | 0 | 0 | 0 | 0 | 27933.9664 | 0 | 27933.9598 | 0.0066363 | 1854.0357 | 4.9033 | 0.6554 | 27.9065 | 4.0773 | 1.075 | 0 | 9.2159 | 0 | 0 | 1.5506 | 0 | 56.0261 | 56.0262 | 1.331e-05
TX_2B_LO_2019_NG | 2B | LO | NG |  |  | OfficeLarge | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 434033.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437417.6009 | 0 | 0 | 871451.4946 | 0 | 871451.4946 | 0 | 0 | 2795.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2817.4068 | 0 | 0 | 5613.0191 | 0 | 5613.0191 | 0 | 0 | 434.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.4176 | 0 | 0 | 871.4515 | 0 | 871.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.87731 | 0 | 0 | 1.7478 | 1.7478 | 0
TX_2B_MA_2016_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 75393.6284 | 28374.723 | 7215.9377 | 142004.2074 | 0 | 30344.7267 | 0 | 0 | 0 | 0 | 87986.0926 | 0 | 0 | 371319.3157 | 0 | 371317.6486 | 1.6671 | 1.6671 | 0 | 5835.4668 | 2196.2036 | 558.5136 | 10991.1257 | 0 | 2348.6818 | 0 | 0 | 0 | 0 | 6810.1236 | 0 | 0 | 28740.115 | 0 | 28739.986 | 0.12904 | 0.12904 | 0 | 257.2431 | 96.8146 | 24.6208 | 484.5184 | 0 | 103.5362 | 0 | 0 | 0 | 0 | 300.2085 | 0 | 0 | 1266.9415 | 0 | 1266.9358 | 0.0056883 | 0.0056883 | 2.8693 | 0.7297 | 14.3599 | 3.0686 | 0 | 0 | 7.624 | 0 | 8.8974 | 0 | 0 | 37.5489 | 37.549 | 0.00016859
TX_2B_MA_2016_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 32282.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32282.6511 | 0 | 32282.6511 | 0 | 0 | 207.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.9326 | 0 | 207.9326 | 0 | 0 | 32.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2827 | 0 | 32.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95678 | 0 | 0 | 0 | 0.95678 | 0.95678 | 0
TX_2B_MA_2019_EL | 2B | MA | EL |  |  | ApartmentMidRise | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 66880.1 | 23181.5818 | 7215.9377 | 142004.2074 | 0 | 28819.2936 | 0 | 0 | 0 | 0 | 87922.1855 | 0 | 0 | 356023.3061 | 0 | 356023.3061 | 0 | 0 | 0 | 5176.5197 | 1794.2544 | 558.5136 | 10991.1257 | 0 | 2230.6133 | 0 | 0 | 0 | 0 | 6805.1772 | 0 | 0 | 27556.2039 | 0 | 27556.2039 | 0 | 0 | 0 | 228.1949 | 79.0956 | 24.6208 | 484.5184 | 0 | 98.3314 | 0 | 0 | 0 | 0 | 299.9905 | 0 | 0 | 1214.7515 | 0 | 1214.7515 | 0 | 0 | 2.3442 | 0.7297 | 14.3599 | 2.9143 | 0 | 0 | 6.7631 | 0 | 8.891 | 0 | 0 | 36.0022 | 36.0022 | 0
TX_2B_MA_2019_NG | 2B | MA | NG |  |  | ApartmentMidRise | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 11790.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11790.845 | 0 | 11790.845 | 0 | 0 | 75.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9448 | 0 | 75.9448 | 0 | 0 | 11.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7908 | 0 | 11.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34945 | 0 | 0 | 0 | 0.34945 | 0.34945 | 0
TX_2B_PS_2016_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 302160.791 | 99355.9874 | 7129.8021 | 317887.4784 | 4818.0346 | 113532.2346 | 177.8283 | 0 | 0 | 19355.4955 | 7179.8163 | 17663.3484 | 0 | 889260.8167 | 0 | 889257.7603 | 3.0564 | 4821.0911 | 0 | 23387.2452 | 7690.1534 | 551.8467 | 24604.4908 | 372.9159 | 8787.395 | 13.7639 | 0 | 0 | 1498.1154 | 555.7178 | 1367.1432 | 0 | 68828.7872 | 0 | 68828.5506 | 0.23657 | 373.1524 | 0 | 1030.9726 | 339.0026 | 24.3269 | 1084.6321 | 16.4391 | 387.372 | 0.60675 | 0 | 0 | 66.041 | 24.4975 | 60.2673 | 0 | 3034.1579 | 0 | 3034.1475 | 0.010429 | 16.4496 | 4.5837 | 0.32892 | 14.6653 | 5.2377 | 0.0082039 | 0.89294 | 13.9398 | 0 | 0.33123 | 0 | 0.81488 | 41.0247 | 41.0249 | 0.000141
TX_2B_PS_2016_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 77484.0496 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 92203.6494 | 0 | 0 | 511878.1138 | 0 | 511878.1138 | 0 | 0 | 499.0748 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 593.8837 | 0 | 0 | 3297.0069 | 0 | 3297.0069 | 0 | 0 | 77.484 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2036 | 0 | 0 | 511.8781 | 0 | 511.8781 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.0477 | 1.2467 | 0 | 0 | 6.9211 | 6.9211 | 0
TX_2B_PS_2019_EL | 2B | PS | EL |  |  | SchoolPrimary | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 273180.3405 | 79686.5139 | 7129.8021 | 312483.1662 | 4745.7919 | 96910.8487 | 144.4855 | 0 | 0 | 20116.8228 | 7179.8163 | 12506.3286 | 0 | 814083.9166 | 0 | 814081.138 | 2.7786 | 4748.5705 | 0 | 21144.1584 | 6167.7362 | 551.8467 | 24186.1971 | 367.3243 | 7500.8997 | 11.1832 | 0 | 0 | 1557.0421 | 555.7178 | 967.9898 | 0 | 63010.0951 | 0 | 63009.8801 | 0.21506 | 367.5394 | 0 | 932.0913 | 271.8904 | 24.3269 | 1066.1926 | 16.1926 | 330.6598 | 0.49298 | 0 | 0 | 68.6386 | 24.4975 | 42.6716 | 0 | 2777.6543 | 0 | 2777.6448 | 0.0094805 | 16.2021 | 3.6762 | 0.32892 | 14.416 | 4.4709 | 0.0066656 | 0.92806 | 12.6028 | 0 | 0.33123 | 0 | 0.57696 | 37.5565 | 37.5567 | 0.00012819
TX_2B_PS_2019_NG | 2B | PS | NG |  |  | SchoolPrimary | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 64821.2128 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 92146.7804 | 0 | 0 | 499158.4081 | 0 | 499158.4081 | 0 | 0 | 417.5134 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 593.5174 | 0 | 0 | 3215.0793 | 0 | 3215.0793 | 0 | 0 | 64.8212 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1468 | 0 | 0 | 499.1584 | 0 | 499.1584 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 0.87645 | 1.2459 | 0 | 0 | 6.7491 | 6.7491 | 0
TX_2B_RS_2016_EL | 2B | RS | EL |  |  | RetailStandalone | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 107344.3666 | 83543.1644 | 10694.7032 | 53987.5506 | 0 | 39241.6973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294811.4821 | 0 | 294809.815 | 1.6671 | 1.6671 | 0 | 8308.454 | 6466.2409 | 827.77 | 4178.6364 | 0 | 3037.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22818.4087 | 0 | 22818.2797 | 0.12904 | 0.12904 | 0 | 366.259 | 285.0493 | 36.4903 | 184.2055 | 0 | 133.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.8968 | 0 | 1005.8911 | 0.0056883 | 0.0056883 | 11.5442 | 1.4778 | 7.4601 | 5.4225 | 0 | 0 | 14.8331 | 0 | 0 | 0 | 0 | 40.7375 | 40.7378 | 0.00023037
TX_2B_RS_2016_NG | 2B | RS | NG |  |  | RetailStandalone | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 43381.5896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82573.8275 | 0 | 0 | 125955.4171 | 0 | 125955.4171 | 0 | 0 | 279.4208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.858 | 0 | 0 | 811.2788 | 0 | 811.2788 | 0 | 0 | 43.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5738 | 0 | 0 | 125.9554 | 0 | 125.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7569 | 3.3442 | 0 | 0 | 5.1011 | 5.1011 | 0
TX_2B_RS_2019_EL | 2B | RS | EL |  |  | RetailStandalone | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 101948.3901 | 65838.1375 | 10694.7032 | 53987.5506 | 0 | 37129.9866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269598.7681 | 0 | 269596.2673 | 2.5007 | 2.5007 | 0 | 7890.8054 | 5095.8718 | 827.77 | 4178.6364 | 0 | 2873.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20866.9446 | 0 | 20866.7511 | 0.19355 | 0.19355 | 0 | 347.8479 | 224.6397 | 36.4903 | 184.2055 | 0 | 126.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919.871 | 0 | 919.8625 | 0.0085324 | 0.0085324 | 9.0977 | 1.4778 | 7.4601 | 5.1307 | 0 | 0 | 14.0875 | 0 | 0 | 0 | 0 | 37.2535 | 37.2538 | 0.00034555
TX_2B_RS_2019_NG | 2B | RS | NG |  |  | RetailStandalone | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 48528.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82583.3057 | 0 | 0 | 131111.5422 | 0 | 131111.5422 | 0 | 0 | 312.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.9191 | 0 | 0 | 844.4894 | 0 | 844.4894 | 0 | 0 | 48.5282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5833 | 0 | 0 | 131.1115 | 0 | 131.1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9653 | 3.3445 | 0 | 0 | 5.3099 | 5.3099 | 0
TX_2B_SH_2016_EL | 2B | SH | EL |  |  | HotelSmall | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 3403.7442 | 141590.201 | 80278.3486 | 12322.9432 | 154949.5496 | 0 | 48302.6032 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 440919.6326 | 0 | 440918.799 | 0.83357 | 0.83357 | 263.4498 | 10959.0816 | 6213.5442 | 953.7958 | 11993.0951 | 0 | 3738.6215 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 34127.1796 | 0 | 34127.115 | 0.064518 | 0.064518 | 11.6136 | 483.1058 | 273.9097 | 42.0459 | 528.6879 | 0 | 164.8085 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1504.4178 | 0 | 1504.4149 | 0.0028441 | 0.0028441 | 6.3402 | 0.97324 | 12.2376 | 3.8148 | 0.0057056 | 0 | 11.1825 | 0.26882 | 0 | 0 | 0 | 34.8228 | 34.8229 | 6.5834e-05
TX_2B_SH_2016_NG | 2B | SH | NG |  |  | HotelSmall | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 5838.5535 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 451483.2069 | 0 | 0 | 856817.1983 | 0 | 856817.1983 | 0 | 0 | 37.6061 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.0033 | 0 | 0 | 5518.7596 | 0 | 5518.7596 | 0 | 0 | 5.8386 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 451.4832 | 0 | 0 | 856.8172 | 0 | 856.8172 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.13515 | 10.4505 | 0 | 0 | 19.8328 | 19.8328 | 0
TX_2B_SH_2019_EL | 2B | SH | EL |  |  | HotelSmall | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 3931.6719 | 134688.2414 | 51442.3836 | 12322.9432 | 154949.5496 | 0 | 46024.1785 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 403431.2109 | 0 | 403430.0995 | 1.1114 | 1.1114 | 304.3114 | 10424.8699 | 3981.6405 | 953.7958 | 11993.0951 | 0 | 3562.2714 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 31225.5757 | 0 | 31225.4897 | 0.086024 | 0.086024 | 13.4149 | 459.5563 | 175.5214 | 42.0459 | 528.6879 | 0 | 157.0345 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.5073 | 0 | 1376.5035 | 0.0037922 | 0.0037922 | 4.0628 | 0.97324 | 12.2376 | 3.6349 | 0.0057056 | 0 | 10.6374 | 0.31051 | 0 | 0 | 0 | 31.862 | 31.8621 | 8.7778e-05
TX_2B_SH_2019_NG | 2B | SH | NG |  |  | HotelSmall | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 6293.5057 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 451483.2069 | 0 | 0 | 857272.1505 | 0 | 857272.1505 | 0 | 0 | 40.5365 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.0033 | 0 | 0 | 5521.6899 | 0 | 5521.6899 | 0 | 0 | 6.2935 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 451.4832 | 0 | 0 | 857.2722 | 0 | 857.2722 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.14568 | 10.4505 | 0 | 0 | 19.8433 | 19.8433 | 0
TX_2B_SO_2016_EL | 2B | SO | EL |  |  | OfficeSmall | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 322.3137 | 11289.3164 | 9030.3417 | 1589.3401 | 13417.6985 | 0 | 6023.9326 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 46677.1417 | 0 | 46675.1967 | 1.945 | 1.945 | 24.9471 | 873.7931 | 698.9484 | 123.0149 | 1038.5299 | 0 | 466.2524 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3612.8108 | 0 | 3612.6602 | 0.15054 | 0.15054 | 1.0997 | 38.5191 | 30.8115 | 5.4228 | 45.7812 | 0 | 20.5537 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 159.2624 | 0 | 159.2558 | 0.0066363 | 0.0066363 | 5.6001 | 0.98561 | 8.3208 | 3.7357 | 0 | 0 | 7.0009 | 0.19988 | 3.1033 | 0 | 0 | 28.9451 | 28.9463 | 0.0012062
TX_2B_SO_2016_NG | 2B | SO | NG |  |  | OfficeSmall | STD2016 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 56.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.869 | 0 | 56.869 | 0 | 0 | 0.36629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36629 | 0 | 0.36629 | 0 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056869 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010336 | 0 | 0 | 0 | 0.010336 | 0.010336 | 0
TX_2B_SO_2019_EL | 2B | SO | EL |  |  | OfficeSmall | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 313.978 | 10836.4101 | 7240.9448 | 1589.3401 | 13417.6985 | 0 | 5546.0191 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43948.5892 | 0 | 43947.1999 | 1.3893 | 1.3893 | 24.3019 | 838.7381 | 560.4491 | 123.0149 | 1038.5299 | 0 | 429.2619 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3401.6208 | 0 | 3401.5133 | 0.10753 | 0.10753 | 1.0713 | 36.9738 | 24.7061 | 5.4228 | 45.7812 | 0 | 18.923 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 149.9526 | 0 | 149.9478 | 0.0047402 | 0.0047402 | 4.4904 | 0.98561 | 8.3208 | 3.4393 | 0 | 0 | 6.7201 | 0.19471 | 3.1033 | 0 | 0 | 27.2533 | 27.2542 | 0.00086155
TX_2B_SO_2019_NG | 2B | SO | NG |  |  | OfficeSmall | STD2019 | TX-LAREDO-TX | Zone2B | Zone2B(TX-LAREDO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 56.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.869 | 0 | 56.869 | 0 | 0 | 0.36629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36629 | 0 | 0.36629 | 0 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056869 | 0 | 0.056869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010336 | 0 | 0 | 0 | 0.010336 | 0.010336 | 0
TX_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 954790.5334 | 880625.0315 | 95735.515 | 4077910.5986 | 543457.0788 | 592351.5168 | 121734.5635 | 341580.3165 | 279157.0374 | 12667.4855 | 0 | 0 | 0 | 7900009.6771 | 0 | 7900011.6221 | -1.945 | 543455.1338 | 0 | 73900.7873 | 68160.3774 | 7409.9289 | 315630.2803 | 42063.5779 | 45848.0074 | 9422.2552 | 26438.3165 | 21606.7547 | 980.4634 | 0 | 0 | 0 | 611460.749 | 0 | 611460.8995 | -0.15054 | 42063.4274 | 0 | 3257.7453 | 3004.6926 | 326.6496 | 13913.831 | 1854.2756 | 2021.1034 | 415.3583 | 1165.472 | 952.4838 | 43.2215 | 0 | 0 | 0 | 26954.833 | 0 | 26954.8397 | -0.0066363 | 1854.2689 | 6.0264 | 0.65515 | 27.9065 | 4.0537 | 0.83307 | 0.086688 | 6.5339 | 0 | 0 | 1.9104 | 0 | 54.0624 | 54.0623 | -1.331e-05
TX_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 787721.3303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493490.4617 | 0 | 0 | 1281211.792 | 0 | 1281211.792 | 0 | 0 | 5073.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3178.5721 | 0 | 0 | 8252.2852 | 0 | 8252.2852 | 0 | 0 | 787.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.4905 | 0 | 0 | 1281.2118 | 0 | 1281.2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5799 | 0.98978 | 0 | 0 | 2.5697 | 2.5697 | 0
TX_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 890388.9148 | 716347.8335 | 95735.515 | 4077910.5986 | 543384.8361 | 576994.3787 | 114688.1184 | 307353.9321 | 279043.1162 | 12486.8787 | 0 | 0 | 0 | 7614334.1222 | 0 | 7614332.4551 | 1.6671 | 543386.5032 | 0 | 68916.102 | 55445.3223 | 7409.9289 | 315630.2803 | 42057.9863 | 44659.3649 | 8876.8604 | 23789.1943 | 21597.9372 | 966.4844 | 0 | 0 | 0 | 589349.4611 | 0 | 589349.332 | 0.12904 | 42058.1154 | 0 | 3038.007 | 2444.1788 | 326.6496 | 13913.831 | 1854.0291 | 1968.7048 | 391.3159 | 1048.6916 | 952.0951 | 42.6052 | 0 | 0 | 0 | 25980.108 | 0 | 25980.1023 | 0.0056883 | 1854.0347 | 4.9022 | 0.65515 | 27.9065 | 3.9486 | 0.78485 | 0.085452 | 6.0932 | 0 | 0 | 1.9096 | 0 | 52.1074 | 52.1074 | 1.1409e-05
TX_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 427797.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493566.2871 | 0 | 0 | 921363.5442 | 0 | 921363.5442 | 0 | 0 | 2755.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3179.0605 | 0 | 0 | 5934.5026 | 0 | 5934.5026 | 0 | 0 | 427.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.5663 | 0 | 0 | 921.3635 | 0 | 921.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85802 | 0.98993 | 0 | 0 | 1.8479 | 1.8479 | 0
TX_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 47771.897 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 25204.3784 | 0 | 0 | 0 | 0 | 99305.9732 | 0 | 0 | 349866.0024 | 0 | 349864.3352 | 1.6671 | 1.6671 | 0 | 3697.5448 | 2196.2036 | 557.6533 | 10991.1257 | 0 | 1950.8189 | 0 | 0 | 0 | 0 | 7686.2823 | 0 | 0 | 27079.6286 | 0 | 27079.4995 | 0.12904 | 0.12904 | 0 | 162.9977 | 96.8146 | 24.5829 | 484.5184 | 0 | 85.9973 | 0 | 0 | 0 | 0 | 338.832 | 0 | 0 | 1193.7428 | 0 | 1193.7371 | 0.0056883 | 0.0056883 | 2.8693 | 0.72858 | 14.3599 | 2.5487 | 0 | 0 | 4.8309 | 0 | 10.0421 | 0 | 0 | 35.3794 | 35.3796 | 0.00016859
TX_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 117064.8925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117064.8925 | 0 | 117064.8925 | 0 | 0 | 754.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.015 | 0 | 754.015 | 0 | 0 | 117.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0649 | 0 | 117.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4695 | 0 | 0 | 0 | 3.4695 | 3.4695 | 0
TX_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 44476.5169 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 24212.4301 | 0 | 0 | 0 | 0 | 99183.7163 | 0 | 0 | 340263.2759 | 0 | 340262.9981 | 0.27786 | 0.27786 | 0 | 3442.4824 | 1794.2544 | 557.6533 | 10991.1257 | 0 | 1874.0421 | 0 | 0 | 0 | 0 | 7676.8196 | 0 | 0 | 26336.3776 | 0 | 26336.3561 | 0.021506 | 0.021506 | 0 | 151.7539 | 79.0956 | 24.5829 | 484.5184 | 0 | 82.6128 | 0 | 0 | 0 | 0 | 338.4148 | 0 | 0 | 1160.9783 | 0 | 1160.9773 | 0.00094805 | 0.00094805 | 2.3442 | 0.72858 | 14.3599 | 2.4484 | 0 | 0 | 4.4976 | 0 | 10.0298 | 0 | 0 | 34.4085 | 34.4085 | 2.8098e-05
TX_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 41192.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41192.132 | 0 | 41192.132 | 0 | 0 | 265.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.3185 | 0 | 265.3185 | 0 | 0 | 41.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.1921 | 0 | 41.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2208 | 0 | 0 | 0 | 1.2208 | 1.2208 | 0
TX_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 191190.3948 | 99358.766 | 7115.9093 | 317887.4784 | 4818.0346 | 100317.3715 | 486.2492 | 0 | 0 | 20711.4361 | 7179.8163 | 17649.4556 | 0 | 766714.9118 | 0 | 766716.5789 | -1.6671 | 4816.3675 | 0 | 14798.1366 | 7690.3685 | 550.7714 | 24604.4908 | 372.9159 | 7764.5646 | 37.6357 | 0 | 0 | 1603.0652 | 555.7178 | 1366.0679 | 0 | 59343.7342 | 0 | 59343.8632 | -0.12904 | 372.7868 | 0 | 652.3416 | 339.0121 | 24.2795 | 1084.6321 | 16.4391 | 342.2829 | 1.6591 | 0 | 0 | 70.6674 | 24.4975 | 60.2199 | 0 | 2616.0313 | 0 | 2616.037 | -0.0056883 | 16.4334 | 4.5838 | 0.32828 | 14.6653 | 4.628 | 0.022432 | 0.95549 | 8.8203 | 0 | 0.33123 | 0 | 0.81423 | 35.3714 | 35.3714 | -7.6911e-05
TX_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 303870.1687 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104430.4903 | 0 | 0 | 750491.0738 | 0 | 750491.0738 | 0 | 0 | 1957.2278 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 672.6368 | 0 | 0 | 4833.913 | 0 | 4833.913 | 0 | 0 | 303.8702 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4305 | 0 | 0 | 750.4911 | 0 | 750.4911 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.1086 | 1.412 | 0 | 0 | 10.1474 | 10.1474 | 0
TX_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 169242.4966 | 79778.2066 | 7115.9093 | 312483.1662 | 4745.7919 | 84857.4265 | 363.9922 | 0 | 0 | 22856.4895 | 7179.8163 | 12503.5501 | 0 | 701126.8452 | 0 | 701125.1781 | 1.6671 | 4747.459 | 0 | 13099.3692 | 6174.8332 | 550.7714 | 24186.1971 | 367.3243 | 6567.9648 | 28.173 | 0 | 0 | 1769.0923 | 555.7178 | 967.7748 | 0 | 54267.2178 | 0 | 54267.0888 | 0.12904 | 367.4533 | 0 | 577.4554 | 272.2032 | 24.2795 | 1066.1926 | 16.1926 | 289.5335 | 1.2419 | 0 | 0 | 77.9863 | 24.4975 | 42.6621 | 0 | 2392.2448 | 0 | 2392.2391 | 0.0056883 | 16.1983 | 3.6805 | 0.32828 | 14.416 | 3.9148 | 0.016792 | 1.0545 | 7.8078 | 0 | 0.33123 | 0 | 0.57683 | 32.3455 | 32.3456 | 7.6911e-05
TX_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 253920.2064 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 104136.667 | 0 | 0 | 700247.2883 | 0 | 700247.2883 | 0 | 0 | 1635.5 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 670.7443 | 0 | 0 | 4510.2928 | 0 | 4510.2928 | 0 | 0 | 253.9202 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1367 | 0 | 0 | 700.2473 | 0 | 700.2473 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 3.4333 | 1.408 | 0 | 0 | 9.468 | 9.468 | 0
TX_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 66985.6856 | 83851.5853 | 10675.2532 | 53987.5506 | 0 | 38569.2841 | 0 | 0 | 0 | 5546.0191 | 0 | 0 | 0 | 259615.378 | 0 | 259613.1551 | 2.2229 | 2.2229 | 0 | 5184.6921 | 6490.1127 | 826.2646 | 4178.6364 | 0 | 2985.2626 | 0 | 0 | 0 | 429.2619 | 0 | 0 | 0 | 20094.2303 | 0 | 20094.0582 | 0.17205 | 0.17205 | 0 | 228.5552 | 286.1016 | 36.424 | 184.2055 | 0 | 131.5984 | 0 | 0 | 0 | 18.923 | 0 | 0 | 0 | 885.8077 | 0 | 885.8001 | 0.0075844 | 0.0075844 | 11.5868 | 1.4751 | 7.4601 | 5.3296 | 0 | 0.76636 | 9.2562 | 0 | 0 | 0 | 0 | 35.874 | 35.8743 | 0.00030716
TX_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 65854.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86061.7945 | 0 | 0 | 151916.128 | 0 | 151916.128 | 0 | 0 | 424.1678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554.324 | 0 | 0 | 978.4918 | 0 | 978.4918 | 0 | 0 | 65.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0618 | 0 | 0 | 151.9161 | 0 | 151.9161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.667 | 3.4854 | 0 | 0 | 6.1524 | 6.1524 | 0
TX_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 62459.4005 | 66168.787 | 10675.2532 | 53987.5506 | 0 | 39422.3041 | 0 | 0 | 0 | 5665.4975 | 0 | 0 | 0 | 238378.7928 | 0 | 238377.1257 | 1.6671 | 1.6671 | 0 | 4834.3576 | 5121.4641 | 826.2646 | 4178.6364 | 0 | 3051.2863 | 0 | 0 | 0 | 438.5095 | 0 | 0 | 0 | 18450.5186 | 0 | 18450.3895 | 0.12904 | 0.12904 | 0 | 213.1115 | 225.7679 | 36.424 | 184.2055 | 0 | 134.5089 | 0 | 0 | 0 | 19.3307 | 0 | 0 | 0 | 813.3484 | 0 | 813.3428 | 0.0056883 | 0.0056883 | 9.1434 | 1.4751 | 7.4601 | 5.4475 | 0 | 0.78287 | 8.6308 | 0 | 0 | 0 | 0 | 32.9395 | 32.9398 | 0.00023037
TX_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 71266.3693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86080.7508 | 0 | 0 | 157347.1201 | 0 | 157347.1201 | 0 | 0 | 459.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554.4461 | 0 | 0 | 1013.4728 | 0 | 1013.4728 | 0 | 0 | 71.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0808 | 0 | 0 | 157.3471 | 0 | 157.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8862 | 3.4862 | 0 | 0 | 6.3724 | 6.3724 | 0
TX_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 11739.4442 | 103398.802 | 80219.9987 | 12306.2718 | 154949.5496 | 0 | 47193.9551 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 409880.2642 | 0 | 409880.542 | -0.27786 | -0.27786 | 908.633 | 8003.0673 | 6209.0279 | 952.5054 | 11993.0951 | 0 | 3652.8121 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 31724.7324 | 0 | 31724.754 | -0.021506 | -0.021506 | 40.055 | 352.7967 | 273.7106 | 41.989 | 528.6879 | 0 | 161.0258 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.5115 | 0 | 1398.5124 | -0.00094805 | -0.00094805 | 6.3356 | 0.97192 | 12.2376 | 3.7273 | 0.0057056 | 0 | 8.1662 | 0.92716 | 0 | 0 | 0 | 32.3715 | 32.3715 | -2.1945e-05
TX_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 25230.8917 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 508162.6707 | 0 | 0 | 932889.0004 | 0 | 932889.0004 | 0 | 0 | 162.5122 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3273.0758 | 0 | 0 | 6008.7381 | 0 | 6008.7381 | 0 | 0 | 25.2309 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 508.1627 | 0 | 0 | 932.889 | 0 | 932.889 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.58402 | 11.7625 | 0 | 0 | 21.5937 | 21.5937 | 0
TX_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 13423.2556 | 97461.005 | 51386.8122 | 12306.2718 | 154949.5496 | 0 | 44790.4949 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 374389.6319 | 0 | 374387.9648 | 1.6671 | 1.6671 | 1038.96 | 7543.4818 | 3977.3393 | 952.5054 | 11993.0951 | 0 | 3466.7843 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 28977.7575 | 0 | 28977.6285 | 0.12904 | 0.12904 | 45.8001 | 332.5369 | 175.3318 | 41.989 | 528.6879 | 0 | 152.8252 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1277.4174 | 0 | 1277.4117 | 0.0056883 | 0.0056883 | 4.0584 | 0.97192 | 12.2376 | 3.5375 | 0.0057056 | 0 | 7.6973 | 1.0601 | 0 | 0 | 0 | 29.5683 | 29.5685 | 0.00013167
TX_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 26548.3575 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 508200.5834 | 0 | 0 | 934244.3788 | 0 | 934244.3788 | 0 | 0 | 170.998 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3273.32 | 0 | 0 | 6017.468 | 0 | 6017.468 | 0 | 0 | 26.5484 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 508.2006 | 0 | 0 | 934.2444 | 0 | 934.2444 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.61452 | 11.7634 | 0 | 0 | 21.625 | 21.625 | 0
TX_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 1597.6758 | 7204.8234 | 9013.6703 | 1589.3401 | 13417.6985 | 0 | 5601.5904 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43428.9972 | 0 | 43427.0522 | 1.945 | 1.945 | 123.6601 | 557.6533 | 697.6581 | 123.0149 | 1038.5299 | 0 | 433.5631 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3361.4044 | 0 | 3361.2538 | 0.15054 | 0.15054 | 5.4513 | 24.5829 | 30.7546 | 5.4228 | 45.7812 | 0 | 19.1126 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 148.1797 | 0 | 148.1731 | 0.0066363 | 0.0066363 | 5.5897 | 0.98561 | 8.3208 | 3.4738 | 0 | 0 | 4.468 | 0.99078 | 3.1033 | 0 | 0 | 26.9308 | 26.932 | 0.0012062
TX_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 1440.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.682 | 0 | 1440.682 | 0 | 0 | 9.2794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2794 | 0 | 9.2794 | 0 | 0 | 1.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4407 | 0 | 1.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26185 | 0 | 0 | 0 | 0.26185 | 0.26185 | 0
TX_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 1622.6829 | 6863.0597 | 7238.1662 | 1589.3401 | 13417.6985 | 0 | 5162.5769 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40897.723 | 0 | 40898.2787 | -0.55571 | -0.55571 | 125.5957 | 531.2008 | 560.2341 | 123.0149 | 1038.5299 | 0 | 399.5835 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3165.4838 | 0 | 3165.5268 | -0.043012 | -0.043012 | 5.5366 | 23.4168 | 24.6966 | 5.4228 | 45.7812 | 0 | 17.6147 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.543 | 0 | 139.5449 | -0.0018961 | -0.0018961 | 4.4887 | 0.98561 | 8.3208 | 3.2015 | 0 | 0 | 4.256 | 1.0063 | 3.1033 | 0 | 0 | 25.3626 | 25.3622 | -0.00034462
TX_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | TX-WICHITAFALLS-TX | Zone3A | Zone3A(TX-WICHITAFALLS-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 1544.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.9419 | 0 | 1544.9419 | 0 | 0 | 9.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.951 | 0 | 9.951 | 0 | 0 | 1.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5449 | 0 | 1.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2808 | 0 | 0 | 0 | 0.2808 | 0.2808 | 0
TX_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 919624.9934 | 880422.1961 | 94551.8456 | 4077910.5986 | 543457.0788 | 710154.4084 | 121078.8218 | 306342.5339 | 495193.3756 | 0 | 0 | 0 | 0 | 8148735.8522 | 0 | 8148735.0187 | 0.83357 | 543457.9124 | 0 | 71178.9745 | 68144.678 | 7318.3129 | 315630.2803 | 42063.5779 | 54965.9512 | 9371.5008 | 23710.9121 | 38327.9673 | 0 | 0 | 0 | 0 | 630712.155 | 0 | 630712.0904 | 0.064518 | 42063.6424 | 0 | 3137.7605 | 3004.0005 | 322.6109 | 13913.831 | 1854.2756 | 2423.0468 | 413.1209 | 1045.2407 | 1689.5998 | 0 | 0 | 0 | 0 | 27803.4867 | 0 | 27803.4839 | 0.0028441 | 1854.2784 | 6.025 | 0.64705 | 27.9065 | 4.8598 | 0.82858 | 0 | 6.2933 | 0 | 0 | 3.3888 | 0 | 55.7644 | 55.7645 | 5.7044e-06
TX_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 268431.2866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486230.1826 | 0 | 0 | 754661.4691 | 0 | 754661.4691 | 0 | 0 | 1728.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3131.8086 | 0 | 0 | 4860.7745 | 0 | 4860.7745 | 0 | 0 | 268.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.2302 | 0 | 0 | 754.6615 | 0 | 754.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53838 | 0.97521 | 0 | 0 | 1.5136 | 1.5136 | 0
TX_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 867218.4472 | 716686.8187 | 94551.8456 | 4077910.5986 | 543384.8361 | 691046.2053 | 118008.5056 | 275222.587 | 495524.025 | 0 | 0 | 0 | 0 | 7879553.8692 | 0 | 7879554.7027 | -0.83357 | 543384.0025 | 0 | 67122.7078 | 55471.5598 | 7318.3129 | 315630.2803 | 42057.9863 | 53486.9763 | 9133.8583 | 21302.2282 | 38353.5595 | 0 | 0 | 0 | 0 | 609877.4695 | 0 | 609877.534 | -0.064518 | 42057.9218 | 0 | 2958.9493 | 2445.3354 | 322.6109 | 13913.831 | 1854.0291 | 2357.8497 | 402.645 | 939.0595 | 1690.728 | 0 | 0 | 0 | 0 | 26885.0378 | 0 | 26885.0406 | -0.0028441 | 1854.0262 | 4.9045 | 0.64705 | 27.9065 | 4.7291 | 0.80757 | 0 | 5.9347 | 0 | 0 | 3.391 | 0 | 53.9224 | 53.9224 | -5.7044e-06
TX_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 516086.4218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486249.1389 | 0 | 0 | 1002335.5607 | 0 | 1002335.5607 | 0 | 0 | 3324.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3131.9307 | 0 | 0 | 6456.0433 | 0 | 6456.0433 | 0 | 0 | 516.0864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.2491 | 0 | 0 | 1002.3356 | 0 | 1002.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0351 | 0.97525 | 0 | 0 | 2.0103 | 2.0103 | 0
TX_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 42945.5266 | 28374.723 | 7213.1591 | 142004.2074 | 0 | 25660.0633 | 0 | 0 | 0 | 0 | 97752.7545 | 0 | 0 | 343950.4339 | 0 | 343948.2111 | 2.2229 | 2.2229 | 0 | 3323.9838 | 2196.2036 | 558.2985 | 10991.1257 | 0 | 1986.0889 | 0 | 0 | 0 | 0 | 7566.0632 | 0 | 0 | 26621.7636 | 0 | 26621.5915 | 0.17205 | 0.17205 | 0 | 146.5301 | 96.8146 | 24.6113 | 484.5184 | 0 | 87.5521 | 0 | 0 | 0 | 0 | 333.5324 | 0 | 0 | 1173.5589 | 0 | 1173.5513 | 0.0075844 | 0.0075844 | 2.8693 | 0.72942 | 14.3599 | 2.5948 | 0 | 0 | 4.3428 | 0 | 9.8851 | 0 | 0 | 34.7812 | 34.7814 | 0.00022478
TX_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 33353.6845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33353.6845 | 0 | 33353.6845 | 0 | 0 | 214.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8311 | 0 | 214.8311 | 0 | 0 | 33.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.3537 | 0 | 33.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98852 | 0 | 0 | 0 | 0.98852 | 0.98852 | 0
TX_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 43437.3329 | 23181.5818 | 7213.1591 | 142004.2074 | 0 | 26276.9051 | 0 | 0 | 0 | 0 | 97636.0547 | 0 | 0 | 339749.2411 | 0 | 339751.4639 | -2.2229 | -2.2229 | 0 | 3362.0496 | 1794.2544 | 558.2985 | 10991.1257 | 0 | 2033.8325 | 0 | 0 | 0 | 0 | 7557.0306 | 0 | 0 | 26296.5913 | 0 | 26296.7633 | -0.17205 | -0.17205 | 0 | 148.2082 | 79.0956 | 24.6113 | 484.5184 | 0 | 89.6568 | 0 | 0 | 0 | 0 | 333.1342 | 0 | 0 | 1159.2244 | 0 | 1159.232 | -0.0075844 | -0.0075844 | 2.3442 | 0.72942 | 14.3599 | 2.6572 | 0 | 0 | 4.3925 | 0 | 9.8733 | 0 | 0 | 34.3568 | 34.3566 | -0.00022478
TX_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 10776.6807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776.6807 | 0 | 10776.6807 | 0 | 0 | 69.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.4126 | 0 | 69.4126 | 0 | 0 | 10.7767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7767 | 0 | 10.7767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31939 | 0 | 0 | 0 | 0.31939 | 0.31939 | 0
TX_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 167080.7717 | 100261.8002 | 7088.1236 | 317887.4784 | 4818.0346 | 106388.5397 | 236.1782 | 0 | 0 | 0 | 7179.8163 | 17457.7345 | 0 | 728398.4772 | 0 | 728402.6451 | -4.1679 | 4813.8668 | 0 | 12932.0517 | 7760.2633 | 548.6208 | 24604.4908 | 372.9159 | 8234.473 | 18.2802 | 0 | 0 | 0 | 555.7178 | 1351.2286 | 0 | 56378.0421 | 0 | 56378.3647 | -0.32259 | 372.5933 | 0 | 570.0796 | 342.0933 | 24.1847 | 1084.6321 | 16.4391 | 362.9977 | 0.80584 | 0 | 0 | 0 | 24.4975 | 59.5658 | 0 | 2485.2956 | 0 | 2485.3098 | -0.014221 | 16.4249 | 4.6254 | 0.327 | 14.6653 | 4.9081 | 0.010896 | 0 | 7.708 | 0 | 0.33123 | 0 | 0.80539 | 33.6039 | 33.6037 | -0.00019228
TX_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 135300.8939 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102174.6855 | 0 | 0 | 579665.9942 | 0 | 579665.9942 | 0 | 0 | 871.4731 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 658.1071 | 0 | 0 | 3733.6287 | 0 | 3733.6287 | 0 | 0 | 135.3009 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1747 | 0 | 0 | 579.666 | 0 | 579.666 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 1.8294 | 1.3815 | 0 | 0 | 7.8377 | 7.8377 | 0
TX_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 165477.5388 | 80778.4906 | 7088.1236 | 312483.1662 | 4745.7919 | 88508.4631 | 372.3279 | 0 | 0 | 0 | 7179.8163 | 12411.8574 | 0 | 679045.5758 | 0 | 679045.8537 | -0.27786 | 4745.514 | 0 | 12807.9615 | 6252.2552 | 548.6208 | 24186.1971 | 367.3243 | 6850.555 | 28.8182 | 0 | 0 | 0 | 555.7178 | 960.6778 | 0 | 52558.1276 | 0 | 52558.1491 | -0.021506 | 367.3028 | 0 | 564.6094 | 275.6162 | 24.1847 | 1066.1926 | 16.1926 | 301.9909 | 1.2704 | 0 | 0 | 0 | 24.4975 | 42.3493 | 0 | 2316.9035 | 0 | 2316.9045 | -0.00094805 | 16.1917 | 3.7266 | 0.327 | 14.416 | 4.0832 | 0.017177 | 0 | 7.6341 | 0 | 0.33123 | 0 | 0.5726 | 31.3269 | 31.3269 | -1.2819e-05
TX_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 208804.1115 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102117.8165 | 0 | 0 | 653112.3429 | 0 | 653112.3429 | 0 | 0 | 1344.9073 | 0 | 0 | 0 | 2204.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 657.7409 | 0 | 0 | 4206.6966 | 0 | 4206.6966 | 0 | 0 | 208.8041 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1178 | 0 | 0 | 653.1123 | 0 | 653.1123 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.8232 | 1.3807 | 0 | 0 | 8.8307 | 8.8307 | 0
TX_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 58819.4781 | 84540.6699 | 10689.146 | 53987.5506 | 0 | 43695.7396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251732.5843 | 0 | 251732.3064 | 0.27786 | 0.27786 | 0 | 4552.6276 | 6543.4478 | 827.3399 | 4178.6364 | 0 | 3382.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19484.102 | 0 | 19484.0805 | 0.021506 | 0.021506 | 0 | 200.6921 | 288.4528 | 36.4714 | 184.2055 | 0 | 149.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858.9116 | 0 | 858.9106 | 0.00094805 | 0.00094805 | 11.682 | 1.4771 | 7.4601 | 6.038 | 0 | 0 | 8.1278 | 0 | 0 | 0 | 0 | 34.785 | 34.785 | 3.8395e-05
TX_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 43808.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85578.4078 | 0 | 0 | 129386.5151 | 0 | 129386.5151 | 0 | 0 | 282.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551.2105 | 0 | 0 | 833.3785 | 0 | 833.3785 | 0 | 0 | 43.8081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5784 | 0 | 0 | 129.3865 | 0 | 129.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7742 | 3.4658 | 0 | 0 | 5.24 | 5.24 | 0
TX_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 0 | 55076.7488 | 66821.7501 | 10689.146 | 53987.5506 | 0 | 41514.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228089.7604 | 0 | 228089.2047 | 0.55571 | 0.55571 | 0 | 4262.9404 | 5172.0035 | 827.3399 | 4178.6364 | 0 | 3213.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17654.1475 | 0 | 17654.1044 | 0.043012 | 0.043012 | 0 | 187.9219 | 227.9958 | 36.4714 | 184.2055 | 0 | 141.6477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778.2423 | 0 | 778.2404 | 0.0018961 | 0.0018961 | 9.2336 | 1.4771 | 7.4601 | 5.7366 | 0 | 0 | 7.6106 | 0 | 0 | 0 | 0 | 31.5179 | 31.518 | 7.679e-05
TX_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 55286.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85587.8859 | 0 | 0 | 140874.0585 | 0 | 140874.0585 | 0 | 0 | 356.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551.2716 | 0 | 0 | 907.3698 | 0 | 907.3698 | 0 | 0 | 55.2862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5879 | 0 | 0 | 140.8741 | 0 | 140.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.239 | 3.4662 | 0 | 0 | 5.7053 | 5.7053 | 0
TX_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 3687.158 | 96366.2497 | 80186.6559 | 12320.1647 | 154949.5496 | 0 | 48322.0532 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 395904.0737 | 0 | 395903.7959 | 0.27786 | 0.27786 | 285.386 | 7458.7477 | 6206.4472 | 953.5807 | 11993.0951 | 0 | 3740.1269 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 30642.9753 | 0 | 30642.9538 | 0.021506 | 0.021506 | 12.5806 | 328.8016 | 273.5969 | 42.0364 | 528.6879 | 0 | 164.8748 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.8247 | 0 | 1350.8238 | 0.00094805 | 0.00094805 | 6.333 | 0.97302 | 12.2376 | 3.8164 | 0.0057056 | 0 | 7.6108 | 0.2912 | 0 | 0 | 0 | 31.2676 | 31.2676 | 2.1945e-05
TX_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 8084.88 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 499148.9299 | 0 | 0 | 906729.2478 | 0 | 906729.2478 | 0 | 0 | 52.0747 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.0183 | 0 | 0 | 5840.2431 | 0 | 5840.2431 | 0 | 0 | 8.0849 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 499.1489 | 0 | 0 | 906.7292 | 0 | 906.7292 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.18714 | 11.5538 | 0 | 0 | 20.9881 | 20.9881 | 0
TX_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 4617.9778 | 90542.3739 | 51400.7051 | 12320.1647 | 154949.5496 | 0 | 45782.4432 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 359685.457 | 0 | 359682.9563 | 2.5007 | 2.5007 | 357.4315 | 7007.9797 | 3978.4146 | 953.5807 | 11993.0951 | 0 | 3543.5611 | 5.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 27839.6544 | 0 | 27839.4608 | 0.19355 | 0.19355 | 15.7565 | 308.9306 | 175.3792 | 42.0364 | 528.6879 | 0 | 156.2097 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.2468 | 0 | 1227.2382 | 0.0085324 | 0.0085324 | 4.0595 | 0.97302 | 12.2376 | 3.6158 | 0.0057056 | 0 | 7.1508 | 0.36472 | 0 | 0 | 0 | 28.407 | 28.4072 | 0.0001975
TX_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 9999.4706 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 499215.2771 | 0 | 0 | 908710.1856 | 0 | 908710.1856 | 0 | 0 | 64.4066 | 0 | 0 | 0 | 2573.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.4456 | 0 | 0 | 5853.0023 | 0 | 5853.0023 | 0 | 0 | 9.9995 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 499.2153 | 0 | 0 | 908.7102 | 0 | 908.7102 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.23146 | 11.5554 | 0 | 0 | 21.034 | 21.034 | 0
TX_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 541.8205 | 6779.7027 | 9002.5561 | 1567.1116 | 13417.6985 | 0 | 5998.9255 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42312.0134 | 0 | 42312.0134 | 0 | 0 | 41.9369 | 524.749 | 696.7978 | 121.2944 | 1038.5299 | 0 | 464.3168 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3274.9498 | 0 | 3274.9498 | 0 | 0 | 1.8487 | 23.1323 | 30.7167 | 5.347 | 45.7812 | 0 | 20.4683 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.3686 | 0 | 144.3686 | 0 | 0 | 5.5828 | 0.97183 | 8.3208 | 3.7202 | 0 | 0 | 4.2044 | 0.336 | 3.1033 | 0 | 0 | 26.2393 | 26.2393 | 0
TX_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 142.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.1726 | 0 | 142.1726 | 0 | 0 | 0.91573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91573 | 0 | 0.91573 | 0 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14217 | 0 | 0.14217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02584 | 0 | 0 | 0 | 0.02584 | 0.02584 | 0
TX_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Electricity | 558.4919 | 6432.3819 | 7232.6091 | 1567.1116 | 13417.6985 | 0 | 5543.2405 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39755.7321 | 0 | 39757.9549 | -2.2229 | -2.2229 | 43.2273 | 497.8664 | 559.8039 | 121.2944 | 1038.5299 | 0 | 429.0468 | 0 | 0 | 0 | 0 | 387.325 | 0 | 0 | 3077.0937 | 0 | 3077.2657 | -0.17205 | -0.17205 | 1.9056 | 21.9473 | 24.6777 | 5.347 | 45.7812 | 0 | 18.9135 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.6466 | 0 | 135.6541 | -0.0075844 | -0.0075844 | 4.4852 | 0.97183 | 8.3208 | 3.4376 | 0 | 0 | 3.989 | 0.34634 | 3.1033 | 0 | 0 | 24.6554 | 24.654 | -0.0013785
TX_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | TX-ELPASO-TX | Zone3B | Zone3B(TX-ELPASO-TX) |  |  | TX | 0.0774 | 0.006441 |  |  |  | Natural Gas | 161.1289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.1289 | 0 | 161.1289 | 0 | 0 | 1.0378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0378 | 0 | 1.0378 | 0 | 0 | 0.16113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16113 | 0 | 0.16113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029286 | 0 | 0 | 0 | 0.029286 | 0.029286 | 0
UT_3B_LO_2016_EL | 3B | LO | EL |  |  | OfficeLarge | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 923081.5304 | 882497.7854 | 95982.8075 | 4077910.5986 | 543459.8574 | 697812.0152 | 119242.1892 | 278142.8606 | 568019.6083 | 0 | 0 | 0 | 0 | 8186149.2526 | 0 | 8186148.9747 | 0.27786 | 543460.1353 | 0 | 77723.4649 | 74306.3135 | 8081.7524 | 343360.0724 | 45759.32 | 58755.7717 | 10040.1923 | 23419.6289 | 47827.251 | 0 | 0 | 0 | 0 | 689273.7671 | 0 | 689273.7437 | 0.023396 | 45759.3434 | 0 | 3149.5542 | 3011.0824 | 327.4933 | 13913.831 | 1854.285 | 2380.9346 | 406.8543 | 949.0234 | 1938.0829 | 0 | 0 | 0 | 0 | 27931.1412 | 0 | 27931.1403 | 0.00094805 | 1854.286 | 6.0392 | 0.65684 | 27.9065 | 4.7754 | 0.81601 | 0 | 6.3169 | 0 | 0 | 3.8871 | 0 | 56.0205 | 56.0205 | 1.9015e-06
UT_3B_LO_2016_NG | 3B | LO | NG |  |  | OfficeLarge | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 371847.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480448.4981 | 0 | 0 | 852296.1106 | 0 | 852296.1106 | 0 | 0 | 1988.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2569.4386 | 0 | 0 | 4558.0796 | 0 | 4558.0796 | 0 | 0 | 371.8476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480.4485 | 0 | 0 | 852.2961 | 0 | 852.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7458 | 0.96362 | 0 | 0 | 1.7094 | 1.7094 | 0
UT_3B_LO_2019_EL | 3B | LO | EL |  |  | OfficeLarge | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 870310.992 | 717778.7954 | 95982.8075 | 4077910.5986 | 543387.6147 | 682018.6422 | 115802.3236 | 248898.4463 | 568047.394 | 0 | 0 | 0 | 0 | 7920137.6141 | 0 | 7920137.892 | -0.27786 | 543387.3368 | 0 | 73280.1855 | 60436.9746 | 8081.7524 | 343360.0724 | 45753.2372 | 57425.9697 | 9750.5556 | 20957.2492 | 47829.5906 | 0 | 0 | 0 | 0 | 666875.5871 | 0 | 666875.6105 | -0.023396 | 45753.2138 | 0 | 2969.5011 | 2449.0612 | 327.4933 | 13913.831 | 1854.0385 | 2327.0476 | 395.1175 | 849.2415 | 1938.1777 | 0 | 0 | 0 | 0 | 27023.5095 | 0 | 27023.5105 | -0.00094805 | 1854.0376 | 4.912 | 0.65684 | 27.9065 | 4.6673 | 0.79247 | 0 | 5.9558 | 0 | 0 | 3.8873 | 0 | 54.2001 | 54.2001 | -1.9015e-06
UT_3B_LO_2019_NG | 3B | LO | NG |  |  | OfficeLarge | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 702607.3529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480505.3672 | 0 | 0 | 1183112.72 | 0 | 1183112.72 | 0 | 0 | 3757.5441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2569.7427 | 0 | 0 | 6327.2868 | 0 | 6327.2868 | 0 | 0 | 702.6074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480.5054 | 0 | 0 | 1183.1127 | 0 | 1183.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4092 | 0.96373 | 0 | 0 | 2.3729 | 2.3729 | 0
UT_3B_MA_2016_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 50931.1273 | 28374.723 | 7207.602 | 142004.2074 | 0 | 27921.8166 | 0 | 0 | 0 | 0 | 96649.6635 | 0 | 0 | 353089.1397 | 0 | 353090.2512 | -1.1114 | -1.1114 | 0 | 4288.4009 | 2389.1517 | 606.8801 | 11956.7543 | 0 | 2351.017 | 0 | 0 | 0 | 0 | 8137.9017 | 0 | 0 | 29730.1056 | 0 | 29730.1991 | -0.093582 | -0.093582 | 0 | 173.777 | 96.8146 | 24.5923 | 484.5184 | 0 | 95.2692 | 0 | 0 | 0 | 0 | 329.7687 | 0 | 0 | 1204.7401 | 0 | 1204.7439 | -0.0037922 | -0.0037922 | 2.8693 | 0.72886 | 14.3599 | 2.8235 | 0 | 0 | 5.1503 | 0 | 9.7735 | 0 | 0 | 35.7056 | 35.7055 | -0.00011239
UT_3B_MA_2016_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 42841.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42841.3338 | 0 | 42841.3338 | 0 | 0 | 229.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.1155 | 0 | 229.1155 | 0 | 0 | 42.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.8413 | 0 | 42.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2697 | 0 | 0 | 0 | 1.2697 | 1.2697 | 0
UT_3B_MA_2019_EL | 3B | MA | EL |  |  | ApartmentMidRise | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 49841.9291 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 27710.6455 | 0 | 0 | 0 | 0 | 96544.0779 | 0 | 0 | 346490.0439 | 0 | 346490.8774 | -0.83357 | -0.83357 | 0 | 4196.6904 | 1951.8892 | 606.8801 | 11956.7543 | 0 | 2333.2364 | 0 | 0 | 0 | 0 | 8129.0114 | 0 | 0 | 29174.4617 | 0 | 29174.5319 | -0.070187 | -0.070187 | 0 | 170.0607 | 79.0956 | 24.5923 | 484.5184 | 0 | 94.5487 | 0 | 0 | 0 | 0 | 329.4084 | 0 | 0 | 1182.224 | 0 | 1182.2269 | -0.0028441 | -0.0028441 | 2.3442 | 0.72886 | 14.3599 | 2.8022 | 0 | 0 | 5.0402 | 0 | 9.7629 | 0 | 0 | 35.0383 | 35.0382 | -8.4293e-05
UT_3B_MA_2019_NG | 3B | MA | NG |  |  | ApartmentMidRise | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 17686.2675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17686.2675 | 0 | 17686.2675 | 0 | 0 | 94.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5862 | 0 | 94.5862 | 0 | 0 | 17.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6863 | 0 | 17.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52418 | 0 | 0 | 0 | 0.52418 | 0.52418 | 0
UT_3B_PS_2016_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 177155.8545 | 100556.3282 | 7121.4664 | 317887.4784 | 4818.0346 | 112559.7363 | 344.5423 | 0 | 0 | 0 | 7179.8163 | 17410.4988 | 0 | 745033.7559 | 0 | 745035.9788 | -2.2229 | 4815.8118 | 0 | 14916.523 | 8466.8428 | 599.6275 | 26766.1257 | 405.6785 | 9477.5298 | 29.0105 | 0 | 0 | 0 | 604.5405 | 1465.964 | 0 | 62731.8423 | 0 | 62732.0294 | -0.18716 | 405.4914 | 0 | 604.4558 | 343.0982 | 24.2984 | 1084.6321 | 16.4391 | 384.0538 | 1.1756 | 0 | 0 | 0 | 24.4975 | 59.4046 | 0 | 2542.0552 | 0 | 2542.0628 | -0.0075844 | 16.4315 | 4.639 | 0.32854 | 14.6653 | 5.1928 | 0.015895 | 0 | 8.1728 | 0 | 0.33123 | 0 | 0.80321 | 34.3712 | 34.3711 | -0.00010255
UT_3B_PS_2016_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 211050.4381 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 102060.9475 | 0 | 0 | 655301.8004 | 0 | 655301.8004 | 0 | 0 | 1128.6977 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 545.8219 | 0 | 0 | 3504.554 | 0 | 3504.554 | 0 | 0 | 211.0504 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0609 | 0 | 0 | 655.3018 | 0 | 655.3018 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.8536 | 1.38 | 0 | 0 | 8.8603 | 8.8603 | 0
UT_3B_PS_2019_EL | 3B | PS | EL |  |  | SchoolPrimary | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 182437.9098 | 80711.805 | 7121.4664 | 312483.1662 | 4745.7919 | 94446.2601 | 555.7133 | 0 | 0 | 0 | 7179.8163 | 12392.4074 | 0 | 702074.3365 | 0 | 702077.6708 | -3.3343 | 4742.4576 | 0 | 15361.272 | 6795.934 | 599.6275 | 26311.0826 | 399.5957 | 7952.3751 | 46.7911 | 0 | 0 | 0 | 604.5405 | 1043.4407 | 0 | 59114.6591 | 0 | 59114.9399 | -0.28075 | 399.3149 | 0 | 622.4781 | 275.3887 | 24.2984 | 1066.1926 | 16.1926 | 322.2506 | 1.8961 | 0 | 0 | 0 | 24.4975 | 42.2829 | 0 | 2395.4776 | 0 | 2395.489 | -0.011377 | 16.1813 | 3.7235 | 0.32854 | 14.416 | 4.3572 | 0.025637 | 0 | 8.4165 | 0 | 0.33123 | 0 | 0.57171 | 32.3894 | 32.3893 | -0.00015382
UT_3B_PS_2019_NG | 3B | PS | NG |  |  | SchoolPrimary | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 333944.4059 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 101994.6003 | 0 | 0 | 778129.421 | 0 | 778129.421 | 0 | 0 | 1785.9347 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 545.4671 | 0 | 0 | 4161.4361 | 0 | 4161.4361 | 0 | 0 | 333.9444 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9946 | 0 | 0 | 778.1294 | 0 | 778.1294 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.5153 | 1.3791 | 0 | 0 | 10.5211 | 10.5211 | 0
UT_3B_RS_2016_EL | 3B | RS | EL |  |  | RetailStandalone | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 63934.8194 | 85438.1469 | 10675.2532 | 53987.5506 | 0 | 41397.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255433.6351 | 0 | 255435.858 | -2.2229 | -2.2229 | 0 | 5383.3118 | 7193.892 | 898.8563 | 4545.7518 | 0 | 3485.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21507.5121 | 0 | 21507.6992 | -0.18716 | -0.18716 | 0 | 218.1456 | 291.515 | 36.424 | 184.2055 | 0 | 141.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 871.5396 | 0 | 871.5471 | -0.0075844 | -0.0075844 | 11.806 | 1.4751 | 7.4601 | 5.7205 | 0 | 0 | 8.8347 | 0 | 0 | 0 | 0 | 35.2967 | 35.2964 | -0.00030716
UT_3B_RS_2016_NG | 3B | RS | NG |  |  | RetailStandalone | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 87862.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85237.1936 | 0 | 0 | 173099.8406 | 0 | 173099.8406 | 0 | 0 | 469.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455.8485 | 0 | 0 | 925.7379 | 0 | 925.7379 | 0 | 0 | 87.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2372 | 0 | 0 | 173.0998 | 0 | 173.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5583 | 3.452 | 0 | 0 | 7.0104 | 7.0104 | 0
UT_3B_RS_2019_EL | 3B | RS | EL |  |  | RetailStandalone | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 60381.0326 | 67694.2201 | 10675.2532 | 53987.5506 | 0 | 39325.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232063.1107 | 0 | 232063.3886 | -0.27786 | -0.27786 | 0 | 5084.0829 | 5699.8533 | 898.8563 | 4545.7518 | 0 | 3311.1696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19539.7139 | 0 | 19539.7373 | -0.023396 | -0.023396 | 0 | 206.0201 | 230.9727 | 36.424 | 184.2055 | 0 | 134.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 791.7993 | 0 | 791.8003 | -0.00094805 | -0.00094805 | 9.3542 | 1.4751 | 7.4601 | 5.434 | 0 | 0 | 8.3436 | 0 | 0 | 0 | 0 | 32.0671 | 32.067 | -3.8395e-05
UT_3B_RS_2019_NG | 3B | RS | NG |  |  | RetailStandalone | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 104240.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85256.1499 | 0 | 0 | 189497.0768 | 0 | 189497.0768 | 0 | 0 | 557.4805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455.9499 | 0 | 0 | 1013.4304 | 0 | 1013.4304 | 0 | 0 | 104.2409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2561 | 0 | 0 | 189.4971 | 0 | 189.4971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2216 | 3.4528 | 0 | 0 | 7.6744 | 7.6744 | 0
UT_3B_SH_2016_EL | 3B | SH | EL |  |  | HotelSmall | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 4359.5711 | 99778.3296 | 80645.1194 | 12309.0504 | 154949.5496 | 0 | 48747.1739 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 400861.0367 | 0 | 400862.426 | -1.3893 | -1.3893 | 367.0759 | 8401.3353 | 6790.3191 | 1036.422 | 13046.7521 | 0 | 4104.512 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 33752.4993 | 0 | 33752.6163 | -0.11698 | -0.11698 | 14.8749 | 340.4437 | 275.1611 | 41.9985 | 528.6879 | 0 | 166.3254 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.7379 | 0 | 1367.7426 | -0.0047402 | -0.0047402 | 6.3692 | 0.97214 | 12.2376 | 3.8499 | 0.0057056 | 0 | 7.8803 | 0.34431 | 0 | 0 | 0 | 31.6592 | 31.6591 | -0.00010972
UT_3B_SH_2016_NG | 3B | SH | NG |  |  | HotelSmall | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 11023.1131 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 496248.6095 | 0 | 0 | 906767.1605 | 0 | 906767.1605 | 0 | 0 | 58.9516 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 2653.9376 | 0 | 0 | 4849.3908 | 0 | 4849.3908 | 0 | 0 | 11.0231 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 496.2486 | 0 | 0 | 906.7672 | 0 | 906.7672 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.25515 | 11.4867 | 0 | 0 | 20.989 | 20.989 | 0
UT_3B_SH_2019_EL | 3B | SH | EL |  |  | HotelSmall | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 5465.4407 | 94082.2679 | 51670.226 | 12309.0504 | 154949.5496 | 0 | 46215.8996 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 364764.6769 | 0 | 364763.2876 | 1.3893 | 1.3893 | 460.1901 | 7921.727 | 4350.633 | 1036.422 | 13046.7521 | 0 | 3891.3787 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 30713.1858 | 0 | 30713.0688 | 0.11698 | 0.11698 | 18.6481 | 321.0087 | 176.2988 | 41.9985 | 528.6879 | 0 | 157.6886 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.5771 | 0 | 1244.5723 | 0.0047402 | 0.0047402 | 4.0808 | 0.97214 | 12.2376 | 3.65 | 0.0057056 | 0 | 7.4304 | 0.43165 | 0 | 0 | 0 | 28.8082 | 28.8083 | 0.00010972
UT_3B_SH_2019_NG | 3B | SH | NG |  |  | HotelSmall | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 13316.8305 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 496286.5222 | 0 | 0 | 909098.7906 | 0 | 909098.7906 | 0 | 0 | 71.2184 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 2654.1403 | 0 | 0 | 4861.8603 | 0 | 4861.8603 | 0 | 0 | 13.3168 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 496.2865 | 0 | 0 | 909.0988 | 0 | 909.0988 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.30825 | 11.4876 | 0 | 0 | 21.043 | 21.043 | 0
UT_3B_SO_2016_EL | 3B | SO | EL |  |  | OfficeSmall | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 711.3131 | 7307.6304 | 9063.6845 | 1592.1187 | 13417.6985 | 0 | 6296.2321 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 43392.8759 | 0 | 43396.2102 | -3.3343 | -3.3343 | 59.8926 | 615.3025 | 763.1622 | 134.0564 | 1129.7702 | 0 | 530.1427 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3653.6801 | 0 | 3653.9609 | -0.28075 | -0.28075 | 2.427 | 24.9336 | 30.9253 | 5.4323 | 45.7812 | 0 | 21.4827 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 148.0565 | 0 | 148.0679 | -0.011377 | -0.011377 | 5.6207 | 0.98733 | 8.3208 | 3.9045 | 0 | 0 | 4.5317 | 0.44111 | 3.1033 | 0 | 0 | 26.9116 | 26.9096 | -0.0020677
UT_3B_SO_2016_NG | 3B | SO | NG |  |  | OfficeSmall | STD2016 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 104.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2599 | 0 | 104.2599 | 0 | 0 | 0.55758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55758 | 0 | 0.55758 | 0 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10426 | 0 | 0.10426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018949 | 0 | 0 | 0 | 0.018949 | 0.018949 | 0
UT_3B_SO_2019_EL | 3B | SO | EL |  |  | OfficeSmall | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 744.6559 | 6960.3095 | 7285.4018 | 1592.1187 | 13417.6985 | 0 | 5832.2115 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40836.5945 | 0 | 40835.4831 | 1.1114 | 1.1114 | 62.7 | 586.0581 | 613.4308 | 134.0564 | 1129.7702 | 0 | 491.0722 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3438.4413 | 0 | 3438.3477 | 0.093582 | 0.093582 | 2.5408 | 23.7486 | 24.8578 | 5.4323 | 45.7812 | 0 | 19.8995 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.3345 | 0 | 139.3307 | 0.0037922 | 0.0037922 | 4.518 | 0.98733 | 8.3208 | 3.6168 | 0 | 0 | 4.3164 | 0.46179 | 3.1033 | 0 | 0 | 25.3236 | 25.3243 | 0.00068924
UT_3B_SO_2019_NG | 3B | SO | NG |  |  | OfficeSmall | STD2019 | UT-SAINTGEORGE-UT | Zone3B | Zone3B(UT-SAINTGEORGE-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 132.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.6944 | 0 | 132.6944 | 0 | 0 | 0.70965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70965 | 0 | 0.70965 | 0 | 0 | 0.13269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13269 | 0 | 0.13269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024117 | 0 | 0 | 0 | 0.024117 | 0.024117 | 0
UT_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 607500.2623 | 880152.6751 | 95985.586 | 4077910.5986 | 543457.0788 | 724469.5839 | 91926.1001 | 178978.5943 | 603490.7906 | 0 | 0 | 0 | 0 | 7803871.2699 | 0 | 7803872.3813 | -1.1114 | 543455.9674 | 0 | 51151.5221 | 74108.8552 | 8081.9863 | 343360.0724 | 45759.086 | 61000.339 | 7740.1776 | 15069.9976 | 50813.9246 | 0 | 0 | 0 | 0 | 657085.9609 | 0 | 657086.0545 | -0.093582 | 45758.9925 | 0 | 2072.7909 | 3003.0809 | 327.5028 | 13913.831 | 1854.2756 | 2471.8902 | 313.6519 | 610.675 | 2059.1106 | 0 | 0 | 0 | 0 | 26626.8088 | 0 | 26626.8126 | -0.0037922 | 1854.2718 | 6.0232 | 0.65686 | 27.9065 | 4.9578 | 0.62908 | 0 | 4.1573 | 0 | 0 | 4.1299 | 0 | 53.4044 | 53.4044 | -7.6059e-06
UT_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 1227574.8211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554814.2294 | 0 | 0 | 1782389.0505 | 0 | 1782389.0505 | 0 | 0 | 6565.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2967.1465 | 0 | 0 | 9532.2166 | 0 | 9532.2166 | 0 | 0 | 1227.5748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554.8142 | 0 | 0 | 1782.3891 | 0 | 1782.3891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4621 | 1.1128 | 0 | 0 | 3.5749 | 3.5749 | 0
UT_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 571567.838 | 716611.7974 | 95985.586 | 4077910.5986 | 543384.8361 | 690037.5856 | 88675.1771 | 160025.9909 | 603776.9829 | 0 | 0 | 0 | 0 | 7547976.3927 | 0 | 7547975.837 | 0.55571 | 543385.3918 | 0 | 48126.012 | 60338.7133 | 8081.9863 | 343360.0724 | 45753.0032 | 58101.1647 | 7466.4499 | 13474.1884 | 50838.022 | 0 | 0 | 0 | 0 | 635539.6123 | 0 | 635539.5655 | 0.046791 | 45753.05 | 0 | 1950.1895 | 2445.0795 | 327.5028 | 13913.831 | 1854.0291 | 2354.4082 | 302.5597 | 546.0087 | 2060.0871 | 0 | 0 | 0 | 0 | 25753.6955 | 0 | 25753.6936 | 0.0018961 | 1854.031 | 4.904 | 0.65686 | 27.9065 | 4.7222 | 0.60683 | 0 | 3.9114 | 0 | 0 | 4.1318 | 0 | 51.6533 | 51.6533 | 3.8029e-06
UT_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 1923528.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554719.4477 | 0 | 0 | 2478247.9455 | 0 | 2478247.9455 | 0 | 0 | 10287.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2966.6396 | 0 | 0 | 13253.67 | 0 | 13253.67 | 0 | 0 | 1923.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554.7194 | 0 | 0 | 2478.2479 | 0 | 2478.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.858 | 1.1126 | 0 | 0 | 4.9705 | 4.9705 | 0
UT_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 27202.1678 | 28374.723 | 7207.602 | 142004.2074 | 0 | 24001.259 | 0 | 0 | 0 | 0 | 111426.0811 | 0 | 0 | 340216.0403 | 0 | 340214.651 | 1.3893 | 1.3893 | 0 | 2290.4225 | 2389.1517 | 606.8801 | 11956.7543 | 0 | 2020.906 | 0 | 0 | 0 | 0 | 9382.076 | 0 | 0 | 28646.1906 | 0 | 28646.0736 | 0.11698 | 0.11698 | 0 | 92.8138 | 96.8146 | 24.5923 | 484.5184 | 0 | 81.8923 | 0 | 0 | 0 | 0 | 380.1858 | 0 | 0 | 1160.8171 | 0 | 1160.8124 | 0.0047402 | 0.0047402 | 2.8693 | 0.72886 | 14.3599 | 2.4271 | 0 | 0 | 2.7508 | 0 | 11.2678 | 0 | 0 | 34.4036 | 34.4038 | 0.00014049
UT_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 159754.5756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159754.5756 | 0 | 159754.5756 | 0 | 0 | 854.3675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854.3675 | 0 | 854.3675 | 0 | 0 | 159.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159.7546 | 0 | 159.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7347 | 0 | 0 | 0 | 4.7347 | 4.7347 | 0
UT_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 28969.3362 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 23109.3391 | 0 | 0 | 0 | 0 | 111287.1528 | 0 | 0 | 335759.2193 | 0 | 335760.0529 | -0.83357 | -0.83357 | 0 | 2439.2181 | 1951.8892 | 606.8801 | 11956.7543 | 0 | 1945.8064 | 0 | 0 | 0 | 0 | 9370.3783 | 0 | 0 | 28270.9263 | 0 | 28270.9965 | -0.070187 | -0.070187 | 0 | 98.8434 | 79.0956 | 24.5923 | 484.5184 | 0 | 78.8491 | 0 | 0 | 0 | 0 | 379.7118 | 0 | 0 | 1145.6105 | 0 | 1145.6133 | -0.0028441 | -0.0028441 | 2.3442 | 0.72886 | 14.3599 | 2.3369 | 0 | 0 | 2.9295 | 0 | 11.2537 | 0 | 0 | 33.9532 | 33.9531 | -8.4293e-05
UT_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 68460.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68460.8306 | 0 | 68460.8306 | 0 | 0 | 366.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366.1285 | 0 | 366.1285 | 0 | 0 | 68.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4608 | 0 | 68.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.029 | 0 | 0 | 0 | 2.029 | 2.029 | 0
UT_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 96685.7848 | 96043.9359 | 7121.4664 | 317887.4784 | 4818.0346 | 105152.0775 | 783.5558 | 0 | 0 | 0 | 7179.8163 | 17482.7416 | 0 | 653154.8915 | 0 | 653151.2793 | 3.6121 | 4821.6468 | 0 | 8140.9431 | 8086.8994 | 599.6275 | 26766.1257 | 405.6785 | 8853.8049 | 65.9754 | 0 | 0 | 0 | 604.5405 | 1472.0468 | 0 | 54995.6419 | 0 | 54995.3377 | 0.30414 | 405.9827 | 0 | 329.8919 | 327.7019 | 24.2984 | 1084.6321 | 16.4391 | 358.7789 | 2.6735 | 0 | 0 | 0 | 24.4975 | 59.6511 | 0 | 2228.5645 | 0 | 2228.5522 | 0.012325 | 16.4515 | 4.4309 | 0.32854 | 14.6653 | 4.8511 | 0.036148 | 0 | 4.4605 | 0 | 0.33123 | 0 | 0.80654 | 30.1323 | 30.1324 | 0.00016664
UT_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 507385.4607 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 116173.9444 | 0 | 0 | 965749.8199 | 0 | 965749.8199 | 0 | 0 | 2713.4974 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 621.2983 | 0 | 0 | 5164.83 | 0 | 5164.83 | 0 | 0 | 507.3855 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1739 | 0 | 0 | 965.7498 | 0 | 965.7498 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 6.8604 | 1.5708 | 0 | 0 | 13.0579 | 13.0579 | 0
UT_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 96549.6351 | 77994.3668 | 7121.4664 | 312483.1662 | 4743.0133 | 83162.5008 | 1236.4622 | 0 | 0 | 0 | 7179.8163 | 12431.3073 | 0 | 602901.7344 | 0 | 602903.1237 | -1.3893 | 4741.624 | 0 | 8129.4793 | 6567.1257 | 599.6275 | 26311.0826 | 399.3617 | 7002.2826 | 104.1101 | 0 | 0 | 0 | 604.5405 | 1046.7161 | 0 | 50764.326 | 0 | 50764.443 | -0.11698 | 399.2447 | 0 | 329.4274 | 266.1168 | 24.2984 | 1066.1926 | 16.1832 | 283.7505 | 4.2188 | 0 | 0 | 0 | 24.4975 | 42.4156 | 0 | 2057.1007 | 0 | 2057.1055 | -0.0047402 | 16.1784 | 3.5982 | 0.32854 | 14.416 | 3.8366 | 0.057043 | 0 | 4.4542 | 0 | 0.33123 | 0 | 0.5735 | 27.8141 | 27.8141 | -6.4093e-05
UT_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 817312.1807 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 116107.5972 | 0 | 0 | 1275610.1928 | 0 | 1275610.1928 | 0 | 0 | 4370.9855 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 620.9434 | 0 | 0 | 6821.9633 | 0 | 6821.9633 | 0 | 0 | 817.3122 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1076 | 0 | 0 | 1275.6102 | 0 | 1275.6102 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 11.0509 | 1.5699 | 0 | 0 | 17.2475 | 17.2475 | 0
UT_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 33751.2495 | 84701.8267 | 10680.8103 | 53987.5506 | 0 | 47199.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230320.9494 | 0 | 230319.0044 | 1.945 | 1.945 | 0 | 2841.8552 | 7131.8938 | 899.3242 | 4545.7518 | 0 | 3974.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19393.0239 | 0 | 19392.8602 | 0.16377 | 0.16377 | 0 | 115.1593 | 289.0026 | 36.4429 | 184.2055 | 0 | 161.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785.8551 | 0 | 785.8484 | 0.0066363 | 0.0066363 | 11.7043 | 1.4759 | 7.4601 | 6.5221 | 0 | 0 | 4.6638 | 0 | 0 | 0 | 0 | 31.826 | 31.8263 | 0.00026876
UT_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 260564.4045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89739.3249 | 0 | 0 | 350303.7294 | 0 | 350303.7294 | 0 | 0 | 1393.4984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479.9259 | 0 | 0 | 1873.4243 | 0 | 1873.4243 | 0 | 0 | 260.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7393 | 0 | 0 | 350.3037 | 0 | 350.3037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5526 | 3.6343 | 0 | 0 | 14.1869 | 14.1869 | 0
UT_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 31561.7389 | 67013.4712 | 10680.8103 | 53987.5506 | 0 | 45093.3587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208336.9298 | 0 | 208336.9298 | 0 | 0 | 0 | 2657.4984 | 5642.5343 | 899.3242 | 4545.7518 | 0 | 3796.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17541.9695 | 0 | 17541.9695 | 0 | 0 | 0 | 107.6887 | 228.65 | 36.4429 | 184.2055 | 0 | 153.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.8456 | 0 | 710.8456 | 0 | 0 | 9.2601 | 1.4759 | 7.4601 | 6.2311 | 0 | 0 | 4.3613 | 0 | 0 | 0 | 0 | 28.7885 | 28.7885 | 0
UT_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 286070.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89758.2813 | 0 | 0 | 375828.4444 | 0 | 375828.4444 | 0 | 0 | 1529.9032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480.0273 | 0 | 0 | 2009.9305 | 0 | 2009.9305 | 0 | 0 | 286.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7583 | 0 | 0 | 375.8284 | 0 | 375.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5855 | 3.6351 | 0 | 0 | 15.2207 | 15.2207 | 0
UT_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 14909.7888 | 68308.2833 | 79191.929 | 12311.829 | 154949.5496 | 0 | 47755.2256 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 377498.848 | 0 | 377494.958 | 3.89 | 3.89 | 1255.4042 | 5751.5575 | 6667.9604 | 1036.656 | 13046.7521 | 0 | 4020.99 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 31785.403 | 0 | 31785.0755 | 0.32754 | 0.32754 | 50.8722 | 233.0679 | 270.2029 | 42.008 | 528.6879 | 0 | 162.9408 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1288.0261 | 0 | 1288.0128 | 0.013273 | 0.013273 | 6.2544 | 0.97236 | 12.2376 | 3.7716 | 0.0057056 | 0 | 5.3948 | 1.1775 | 0 | 0 | 0 | 29.8137 | 29.814 | 0.00030722
UT_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 40016.8388 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 577220.6261 | 0 | 0 | 1016732.9028 | 0 | 1016732.9028 | 0 | 0 | 214.0101 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.9759 | 0 | 0 | 5437.4876 | 0 | 5437.4876 | 0 | 0 | 40.0168 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 577.2206 | 0 | 0 | 1016.7329 | 0 | 1016.7329 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.92627 | 13.361 | 0 | 0 | 23.5344 | 23.5344 | 0
UT_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 18157.9333 | 63515.2558 | 50814.4275 | 12311.829 | 154949.5496 | 0 | 45151.7086 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 344972.9465 | 0 | 344970.7236 | 2.2229 | 2.2229 | 1528.898 | 5347.9845 | 4278.5748 | 1036.656 | 13046.7521 | 0 | 3801.7739 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 29046.7221 | 0 | 29046.5349 | 0.18716 | 0.18716 | 61.9549 | 216.7141 | 173.3788 | 42.008 | 528.6879 | 0 | 154.0576 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.0477 | 0 | 1177.0401 | 0.0075844 | 0.0075844 | 4.0132 | 0.97236 | 12.2376 | 3.566 | 0.0057056 | 0 | 5.0163 | 1.4341 | 0 | 0 | 0 | 27.245 | 27.2452 | 0.00017556
UT_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 41542.8244 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 577286.9733 | 0 | 0 | 1018325.2356 | 0 | 1018325.2356 | 0 | 0 | 222.171 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 3087.3307 | 0 | 0 | 5446.0034 | 0 | 5446.0034 | 0 | 0 | 41.5428 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 577.287 | 0 | 0 | 1018.3252 | 0 | 1018.3252 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.96159 | 13.3625 | 0 | 0 | 23.5713 | 23.5713 | 0
UT_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 2411.7959 | 4226.1999 | 8816.3921 | 1592.1187 | 13417.6985 | 0 | 5732.1831 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41200.5868 | 0 | 41198.3639 | 2.2229 | 2.2229 | 203.0732 | 355.846 | 742.3402 | 134.0564 | 1129.7702 | 0 | 482.6498 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3469.0894 | 0 | 3468.9022 | 0.18716 | 0.18716 | 8.229 | 14.4198 | 30.0815 | 5.4323 | 45.7812 | 0 | 19.5582 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.5764 | 0 | 140.5688 | 0.0075844 | 0.0075844 | 5.4674 | 0.98733 | 8.3208 | 3.5547 | 0 | 0 | 2.6208 | 1.4956 | 3.1033 | 0 | 0 | 25.5487 | 25.5501 | 0.0013785
UT_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 1611.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1611.2891 | 0 | 1611.2891 | 0 | 0 | 8.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6172 | 0 | 8.6172 | 0 | 0 | 1.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6113 | 0 | 1.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29286 | 0 | 0 | 0 | 0.29286 | 0.29286 | 0
UT_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 2484.0386 | 3984.4646 | 7104.795 | 1592.1187 | 13417.6985 | 0 | 5262.6053 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38849.9194 | 0 | 38847.6965 | 2.2229 | 2.2229 | 209.1561 | 335.4919 | 598.2237 | 134.0564 | 1129.7702 | 0 | 443.1114 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3271.1632 | 0 | 3270.976 | 0.18716 | 0.18716 | 8.4755 | 13.595 | 24.2416 | 5.4323 | 45.7812 | 0 | 17.956 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.5559 | 0 | 132.5483 | 0.0075844 | 0.0075844 | 4.406 | 0.98733 | 8.3208 | 3.2635 | 0 | 0 | 2.4709 | 1.5404 | 3.1033 | 0 | 0 | 24.0909 | 24.0923 | 0.0013785
UT_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | UT-SALTLAKECITY-UT | Zone5B | Zone5B(UT-SALTLAKECITY-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 1829.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1829.287 | 0 | 1829.287 | 0 | 0 | 9.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.783 | 0 | 9.783 | 0 | 0 | 1.8293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8293 | 0 | 1.8293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33248 | 0 | 0 | 0 | 0.33248 | 0.33248 | 0
UT_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 530108.8445 | 879588.6261 | 95721.6222 | 4077910.5986 | 543457.0788 | 729623.8251 | 79911.5778 | 147333.4983 | 661490.5915 | 0 | 0 | 0 | 0 | 7745146.263 | 0 | 7745146.8188 | -0.55571 | 543456.5231 | 0 | 44635.1647 | 74061.3623 | 8059.7606 | 343360.0724 | 45759.086 | 61434.3261 | 6728.5548 | 12405.4806 | 55697.5078 | 0 | 0 | 0 | 0 | 652141.3153 | 0 | 652141.3621 | -0.046791 | 45759.0392 | 0 | 1808.7314 | 3001.1564 | 326.6022 | 13913.831 | 1854.2756 | 2489.4765 | 272.6583 | 502.7019 | 2257.0059 | 0 | 0 | 0 | 0 | 26426.439 | 0 | 26426.4409 | -0.0018961 | 1854.2737 | 6.0193 | 0.65505 | 27.9065 | 4.9931 | 0.54686 | 0 | 3.6277 | 0 | 0 | 4.5268 | 0 | 53.0026 | 53.0026 | -3.8029e-06
UT_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 1390106.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586888.3607 | 0 | 0 | 1976994.8616 | 0 | 1976994.8616 | 0 | 0 | 7434.2896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3138.679 | 0 | 0 | 10572.9685 | 0 | 10572.9685 | 0 | 0 | 1390.1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.8884 | 0 | 0 | 1976.9949 | 0 | 1976.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7881 | 1.1771 | 0 | 0 | 3.9652 | 3.9652 | 0
UT_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 489080.5289 | 716672.9258 | 95721.6222 | 4077910.5986 | 543384.8361 | 702418.8787 | 77452.5463 | 131240.0401 | 661754.5553 | 0 | 0 | 0 | 0 | 7495636.5321 | 0 | 7495640.1442 | -3.6121 | 543381.224 | 0 | 41180.5805 | 60343.8604 | 8059.7606 | 343360.0724 | 45753.0032 | 59143.6696 | 6521.5044 | 11050.4114 | 55719.7336 | 0 | 0 | 0 | 0 | 631132.596 | 0 | 631132.9001 | -0.30414 | 45752.6991 | 0 | 1668.7428 | 2445.288 | 326.6022 | 13913.831 | 1854.0291 | 2396.6532 | 264.2681 | 447.791 | 2257.9065 | 0 | 0 | 0 | 0 | 25575.1118 | 0 | 25575.1242 | -0.012325 | 1854.0167 | 4.9044 | 0.65505 | 27.9065 | 4.8069 | 0.53003 | 0 | 3.3469 | 0 | 0 | 4.5286 | 0 | 51.2951 | 51.2951 | -2.4719e-05
UT_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 2113423.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586926.2734 | 0 | 0 | 2700349.9312 | 0 | 2700349.9312 | 0 | 0 | 11302.5897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3138.8817 | 0 | 0 | 14441.4714 | 0 | 14441.4714 | 0 | 0 | 2113.4237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.9263 | 0 | 0 | 2700.3499 | 0 | 2700.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2388 | 1.1772 | 0 | 0 | 5.416 | 5.416 | 0
UT_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 28649.8011 | 28374.723 | 7207.602 | 142004.2074 | 0 | 23681.7238 | 0 | 0 | 0 | 0 | 117497.2493 | 0 | 0 | 347415.3066 | 0 | 347415.3066 | 0 | 0 | 0 | 2412.3132 | 2389.1517 | 606.8801 | 11956.7543 | 0 | 1994.0011 | 0 | 0 | 0 | 0 | 9893.2684 | 0 | 0 | 29252.3688 | 0 | 29252.3688 | 0 | 0 | 0 | 97.7531 | 96.8146 | 24.5923 | 484.5184 | 0 | 80.802 | 0 | 0 | 0 | 0 | 400.9006 | 0 | 0 | 1185.381 | 0 | 1185.381 | 0 | 0 | 2.8693 | 0.72886 | 14.3599 | 2.3948 | 0 | 0 | 2.8972 | 0 | 11.8817 | 0 | 0 | 35.1318 | 35.1318 | 0
UT_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 71038.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71038.8931 | 0 | 71038.8931 | 0 | 0 | 379.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.916 | 0 | 379.916 | 0 | 0 | 71.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0389 | 0 | 71.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1054 | 0 | 0 | 0 | 2.1054 | 2.1054 | 0
UT_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 27216.0607 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 22545.2901 | 0 | 0 | 0 | 0 | 117488.9136 | 0 | 0 | 339643.6556 | 0 | 339645.0448 | -1.3893 | -1.3893 | 0 | 2291.5923 | 1951.8892 | 606.8801 | 11956.7543 | 0 | 1898.3134 | 0 | 0 | 0 | 0 | 9892.5665 | 0 | 0 | 28597.9958 | 0 | 28598.1128 | -0.11698 | -0.11698 | 0 | 92.8612 | 79.0956 | 24.5923 | 484.5184 | 0 | 76.9245 | 0 | 0 | 0 | 0 | 400.8722 | 0 | 0 | 1158.8642 | 0 | 1158.8689 | -0.0047402 | -0.0047402 | 2.3442 | 0.72886 | 14.3599 | 2.2799 | 0 | 0 | 2.7522 | 0 | 11.8809 | 0 | 0 | 34.346 | 34.3459 | -0.00014049
UT_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 68697.7849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68697.7849 | 0 | 68697.7849 | 0 | 0 | 367.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.3958 | 0 | 367.3958 | 0 | 0 | 68.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.6978 | 0 | 68.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.036 | 0 | 0 | 0 | 2.036 | 2.036 | 0
UT_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 78077.7238 | 96135.6286 | 7115.9093 | 317887.4784 | 4818.0346 | 104293.5004 | 705.7559 | 0 | 0 | 15707.2375 | 7179.8163 | 17482.7416 | 0 | 649403.8264 | 0 | 649405.7714 | -1.945 | 4816.0896 | 0 | 6574.1443 | 8094.6199 | 599.1596 | 26766.1257 | 405.6785 | 8781.5127 | 59.4246 | 0 | 0 | 1322.5494 | 604.5405 | 1472.0468 | 0 | 54679.8022 | 0 | 54679.966 | -0.16377 | 405.5147 | 0 | 266.4012 | 328.0148 | 24.2795 | 1084.6321 | 16.4391 | 355.8494 | 2.408 | 0 | 0 | 53.5931 | 24.4975 | 59.6511 | 0 | 2215.7659 | 0 | 2215.7725 | -0.0066363 | 16.4325 | 4.4351 | 0.32828 | 14.6653 | 4.8114 | 0.032559 | 0.72463 | 3.602 | 0 | 0.33123 | 0 | 0.80654 | 29.9595 | 29.9594 | -8.973e-05
UT_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 341308.9449 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122277.8867 | 0 | 0 | 805777.2464 | 0 | 805777.2464 | 0 | 0 | 1825.3202 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 653.9421 | 0 | 0 | 4309.2967 | 0 | 4309.2967 | 0 | 0 | 341.3089 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.2779 | 0 | 0 | 805.7772 | 0 | 805.7772 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.6148 | 1.6533 | 0 | 0 | 10.8949 | 10.8949 | 0
UT_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 67883.1626 | 78577.8658 | 7115.9093 | 312483.1662 | 4743.0133 | 82870.7513 | 602.949 | 0 | 0 | 20022.3515 | 7179.8163 | 12431.3073 | 0 | 593910.2927 | 0 | 593912.2377 | -1.945 | 4741.0683 | 0 | 5715.7623 | 6616.2563 | 599.1596 | 26311.0826 | 399.3617 | 6977.7173 | 50.7683 | 0 | 0 | 1685.882 | 604.5405 | 1046.7161 | 0 | 50007.2466 | 0 | 50007.4104 | -0.16377 | 399.198 | 0 | 231.6174 | 268.1077 | 24.2795 | 1066.1926 | 16.1832 | 282.755 | 2.0573 | 0 | 0 | 68.3163 | 24.4975 | 42.4156 | 0 | 2026.4219 | 0 | 2026.4286 | -0.0066363 | 16.1765 | 3.6251 | 0.32828 | 14.416 | 3.8231 | 0.027816 | 0.9237 | 3.1317 | 0 | 0.33123 | 0 | 0.5735 | 27.3994 | 27.3993 | -8.973e-05
UT_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 375866.3571 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122230.4958 | 0 | 0 | 840287.2677 | 0 | 840287.2677 | 0 | 0 | 2010.1333 | 0 | 0 | 0 | 1830.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 653.6887 | 0 | 0 | 4493.8563 | 0 | 4493.8563 | 0 | 0 | 375.8664 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.2305 | 0 | 0 | 840.2873 | 0 | 840.2873 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.0821 | 1.6527 | 0 | 0 | 11.3615 | 11.3615 | 0
UT_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 27449.4603 | 90886.9162 | 10691.9246 | 53987.5506 | 0 | 47732.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230748.8487 | 0 | 230746.9037 | 1.945 | 1.945 | 0 | 2311.2446 | 7652.6783 | 900.2601 | 4545.7518 | 0 | 4019.1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19429.0531 | 0 | 19428.8893 | 0.16377 | 0.16377 | 0 | 93.6576 | 310.1062 | 36.4808 | 184.2055 | 0 | 162.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 787.3151 | 0 | 787.3084 | 0.0066363 | 0.0066363 | 12.559 | 1.4774 | 7.4601 | 6.5959 | 0 | 0 | 3.793 | 0 | 0 | 0 | 0 | 31.8852 | 31.8854 | 0.00026876
UT_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 302742.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91625.481 | 0 | 0 | 394367.7473 | 0 | 394367.7473 | 0 | 0 | 1619.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.0131 | 0 | 0 | 2109.0787 | 0 | 2109.0787 | 0 | 0 | 302.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6255 | 0 | 0 | 394.3677 | 0 | 394.3677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2607 | 3.7107 | 0 | 0 | 15.9715 | 15.9715 | 0
UT_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 0 | 25409.9923 | 75249.1429 | 10691.9246 | 53987.5506 | 0 | 45449.0152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210787.6257 | 0 | 210789.5707 | -1.945 | -1.945 | 0 | 2139.5214 | 6335.9778 | 900.2601 | 4545.7518 | 0 | 3826.8071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17748.3181 | 0 | 17748.4818 | -0.16377 | -0.16377 | 0 | 86.6989 | 256.7501 | 36.4808 | 184.2055 | 0 | 155.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719.2074 | 0 | 719.214 | -0.0066363 | -0.0066363 | 10.3981 | 1.4774 | 7.4601 | 6.2803 | 0 | 0 | 3.5112 | 0 | 0 | 0 | 0 | 29.1274 | 29.1271 | -0.00026876
UT_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 328816.7153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91634.9592 | 0 | 0 | 420451.6744 | 0 | 420451.6744 | 0 | 0 | 1758.5118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.0638 | 0 | 0 | 2248.5756 | 0 | 2248.5756 | 0 | 0 | 328.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.635 | 0 | 0 | 420.4517 | 0 | 420.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3167 | 3.7111 | 0 | 0 | 17.0279 | 17.0279 | 0
UT_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 18841.4607 | 62248.2294 | 79203.0433 | 12309.0504 | 154949.5496 | 0 | 53504.08 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 381127.6561 | 0 | 381128.2118 | -0.55571 | -0.55571 | 1586.451 | 5241.3009 | 6668.8962 | 1036.422 | 13046.7521 | 0 | 4505.0435 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 32090.9486 | 0 | 32090.9954 | -0.046791 | -0.046791 | 64.2871 | 212.391 | 270.2408 | 41.9985 | 528.6879 | 0 | 182.5559 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1300.4076 | 0 | 1300.4095 | -0.0018961 | -0.0018961 | 6.2553 | 0.97214 | 12.2376 | 4.2256 | 0.0057056 | 0 | 4.9162 | 1.4881 | 0 | 0 | 0 | 30.1007 | 30.1006 | -4.3889e-05
UT_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 43675.4129 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 614052.7994 | 0 | 0 | 1057223.6502 | 0 | 1057223.6502 | 0 | 0 | 233.5761 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 3283.9544 | 0 | 0 | 5654.0321 | 0 | 5654.0321 | 0 | 0 | 43.6754 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 614.0528 | 0 | 0 | 1057.2237 | 0 | 1057.2237 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.011 | 14.2135 | 0 | 0 | 24.4716 | 24.4716 | 0
UT_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 22689.7755 | 57249.5879 | 50897.7845 | 12309.0504 | 154949.5496 | 0 | 50458.771 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348626.7616 | 0 | 348628.4288 | -1.6671 | -1.6671 | 1910.4791 | 4820.4153 | 4285.5935 | 1036.422 | 13046.7521 | 0 | 4248.6285 | 6.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 29354.3733 | 0 | 29354.5137 | -0.14037 | -0.14037 | 77.4175 | 195.3356 | 173.6632 | 41.9985 | 528.6879 | 0 | 172.1653 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.5145 | 0 | 1189.5202 | -0.0056883 | -0.0056883 | 4.0198 | 0.97214 | 12.2376 | 3.9851 | 0.0057056 | 0 | 4.5214 | 1.792 | 0 | 0 | 0 | 27.5339 | 27.5338 | -0.00013167
UT_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 45296.1802 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 614147.5811 | 0 | 0 | 1058939.1991 | 0 | 1058939.1991 | 0 | 0 | 242.244 | 0 | 0 | 0 | 2136.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.4613 | 0 | 0 | 5663.2068 | 0 | 5663.2068 | 0 | 0 | 45.2962 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 614.1476 | 0 | 0 | 1058.9392 | 0 | 1058.9392 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.0485 | 14.2157 | 0 | 0 | 24.5113 | 24.5113 | 0
UT_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 3050.8662 | 3598.2439 | 8813.6135 | 1586.5616 | 13417.6985 | 0 | 5759.9687 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41231.151 | 0 | 41228.6503 | 2.5007 | 2.5007 | 256.8829 | 302.9721 | 742.1063 | 133.5885 | 1129.7702 | 0 | 484.9894 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3471.6629 | 0 | 3471.4524 | 0.21056 | 0.21056 | 10.4096 | 12.2772 | 30.072 | 5.4133 | 45.7812 | 0 | 19.653 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.6807 | 0 | 140.6722 | 0.0085324 | 0.0085324 | 5.4657 | 0.98389 | 8.3208 | 3.572 | 0 | 0 | 2.2314 | 1.892 | 3.1033 | 0 | 0 | 25.5675 | 25.569 | 0.0015508
UT_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 3724.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3724.9213 | 0 | 3724.9213 | 0 | 0 | 19.9209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9209 | 0 | 19.9209 | 0 | 0 | 3.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7249 | 0 | 3.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67701 | 0 | 0 | 0 | 0.67701 | 0.67701 | 0
UT_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Electricity | 3170.3446 | 3262.0373 | 7127.0235 | 1586.5616 | 13417.6985 | 0 | 5193.1411 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38761.0052 | 0 | 38761.5609 | -0.55571 | -0.55571 | 266.943 | 274.6635 | 600.0954 | 133.5885 | 1129.7702 | 0 | 437.2625 | 0 | 0 | 0 | 0 | 421.3535 | 0 | 0 | 3263.6766 | 0 | 3263.7234 | -0.046791 | -0.046791 | 10.8172 | 11.1301 | 24.3174 | 5.4133 | 45.7812 | 0 | 17.719 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.2525 | 0 | 132.2544 | -0.0018961 | -0.0018961 | 4.4197 | 0.98389 | 8.3208 | 3.2205 | 0 | 0 | 2.0229 | 1.9661 | 3.1033 | 0 | 0 | 24.0375 | 24.0372 | -0.00034462
UT_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | UT-VERNAL-UT | Zone6B | Zone6B(UT-VERNAL-UT) |  |  | UT | 0.0842 | 0.005348 |  |  |  | Natural Gas | 4284.1334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4284.1334 | 0 | 4284.1334 | 0 | 0 | 22.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9115 | 0 | 22.9115 | 0 | 0 | 4.2841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2841 | 0 | 4.2841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77865 | 0 | 0 | 0 | 0.77865 | 0.77865 | 0
VA_3A_LO_2016_EL | 3A | LO | EL |  |  | OfficeLarge | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 824906.4338 | 883167.42 | 95015.8663 | 4077910.5986 | 543459.8574 | 557363.8051 | 114601.9828 | 304264.166 | 265303.104 | 12589.6856 | 0 | 0 | 0 | 7678582.9196 | 0 | 7678578.7517 | 4.1679 | 543464.0253 | 0 | 63517.7954 | 68003.8913 | 7316.2217 | 313999.1161 | 41846.409 | 42917.013 | 8824.3527 | 23428.3408 | 20428.339 | 969.4058 | 0 | 0 | 0 | 591250.8848 | 0 | 591250.5639 | 0.32092 | 41846.7299 | 0 | 2814.5808 | 3013.3672 | 324.1941 | 13913.831 | 1854.285 | 1901.7253 | 391.022 | 1038.1493 | 905.2142 | 42.956 | 0 | 0 | 0 | 26199.3249 | 0 | 26199.3107 | 0.014221 | 1854.2993 | 6.0438 | 0.65022 | 27.9065 | 3.8142 | 0.78426 | 0.086155 | 5.6451 | 0 | 0 | 1.8156 | 0 | 52.547 | 52.547 | 2.8522e-05
VA_3A_LO_2016_NG | 3A | LO | NG |  |  | OfficeLarge | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 897421.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512854.3655 | 0 | 0 | 1410276.0492 | 0 | 1410276.0492 | 0 | 0 | 7572.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.4651 | 0 | 0 | 11899.9093 | 0 | 11899.9093 | 0 | 0 | 897.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512.8544 | 0 | 0 | 1410.276 | 0 | 1410.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7999 | 1.0286 | 0 | 0 | 2.8285 | 2.8285 | 0
VA_3A_LO_2019_EL | 3A | LO | EL |  |  | OfficeLarge | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 771057.8115 | 718131.6733 | 95015.8663 | 4077910.5986 | 543387.6147 | 542818.0085 | 107155.4241 | 275589.3578 | 265183.6256 | 13059.2634 | 0 | 0 | 0 | 7409309.2438 | 0 | 7409307.8546 | 1.3893 | 543389.004 | 0 | 59371.4515 | 55296.1388 | 7316.2217 | 313999.1161 | 41840.8463 | 41796.9867 | 8250.9677 | 21220.3806 | 20419.1392 | 1005.5633 | 0 | 0 | 0 | 570516.8118 | 0 | 570516.7048 | 0.10697 | 41840.9533 | 0 | 2630.8493 | 2450.2653 | 324.1941 | 13913.831 | 1854.0385 | 1852.095 | 365.6143 | 940.3109 | 904.8065 | 44.5582 | 0 | 0 | 0 | 25280.5631 | 0 | 25280.5584 | 0.0047402 | 1854.0433 | 4.9144 | 0.65022 | 27.9065 | 3.7147 | 0.7333 | 0.089369 | 5.2766 | 0 | 0 | 1.8147 | 0 | 50.7043 | 50.7043 | 9.5073e-06
VA_3A_LO_2019_NG | 3A | LO | NG |  |  | OfficeLarge | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 513024.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512958.6253 | 0 | 0 | 1025983.5979 | 0 | 1025983.5979 | 0 | 0 | 4328.9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4328.3449 | 0 | 0 | 8657.2496 | 0 | 8657.2496 | 0 | 0 | 513.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512.9586 | 0 | 0 | 1025.9836 | 0 | 1025.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.029 | 1.0288 | 0 | 0 | 2.0578 | 2.0578 | 0
VA_3A_MA_2016_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 36424.2306 | 28374.723 | 7207.602 | 142004.2074 | 0 | 22264.6548 | 0 | 0 | 0 | 0 | 103176.5166 | 0 | 0 | 339451.9345 | 0 | 339447.7666 | 4.1679 | 4.1679 | 0 | 2804.6658 | 2184.8537 | 554.9854 | 10934.324 | 0 | 1714.3784 | 0 | 0 | 0 | 0 | 7944.5918 | 0 | 0 | 26137.799 | 0 | 26137.478 | 0.32092 | 0.32092 | 0 | 124.2795 | 96.8146 | 24.5923 | 484.5184 | 0 | 75.967 | 0 | 0 | 0 | 0 | 352.0383 | 0 | 0 | 1158.21 | 0 | 1158.1958 | 0.014221 | 0.014221 | 2.8693 | 0.72886 | 14.3599 | 2.2515 | 0 | 0 | 3.6833 | 0 | 10.4335 | 0 | 0 | 34.3261 | 34.3265 | 0.00042147
VA_3A_MA_2016_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 169175.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169175.8777 | 0 | 169175.8777 | 0 | 0 | 1427.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.5061 | 0 | 1427.5061 | 0 | 0 | 169.1759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.1759 | 0 | 169.1759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.014 | 0 | 0 | 0 | 5.014 | 5.014 | 0
VA_3A_MA_2019_EL | 3A | MA | EL |  |  | ApartmentMidRise | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 34648.7265 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 20917.05 | 0 | 0 | 0 | 0 | 103032.0311 | 0 | 0 | 330991.1989 | 0 | 330993.6996 | -2.5007 | -2.5007 | 0 | 2667.9519 | 1784.9818 | 554.9854 | 10934.324 | 0 | 1610.6128 | 0 | 0 | 0 | 0 | 7933.4664 | 0 | 0 | 25486.3223 | 0 | 25486.5149 | -0.19255 | -0.19255 | 0 | 118.2215 | 79.0956 | 24.5923 | 484.5184 | 0 | 71.369 | 0 | 0 | 0 | 0 | 351.5453 | 0 | 0 | 1129.342 | 0 | 1129.3505 | -0.0085324 | -0.0085324 | 2.3442 | 0.72886 | 14.3599 | 2.1152 | 0 | 0 | 3.5038 | 0 | 10.4189 | 0 | 0 | 33.4712 | 33.4709 | -0.00025288
VA_3A_MA_2019_NG | 3A | MA | NG |  |  | ApartmentMidRise | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 59143.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59143.7883 | 0 | 59143.7883 | 0 | 0 | 499.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.0553 | 0 | 499.0553 | 0 | 0 | 59.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.1438 | 0 | 59.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7529 | 0 | 0 | 0 | 1.7529 | 1.7529 | 0
VA_3A_PS_2016_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 146522.1569 | 101200.9557 | 7102.0164 | 317887.4784 | 4818.0346 | 90025.5605 | 597.3918 | 0 | 0 | 21956.2339 | 7179.8163 | 17680.0198 | 0 | 714969.6644 | 0 | 714969.9423 | -0.27786 | 4817.7568 | 0 | 11282.2061 | 7792.4736 | 546.8553 | 24477.3358 | 370.9887 | 6931.9682 | 45.9992 | 0 | 0 | 1690.63 | 552.8459 | 1361.3615 | 0 | 55052.6642 | 0 | 55052.6856 | -0.021395 | 370.9673 | 0 | 499.9336 | 345.2977 | 24.2321 | 1084.6321 | 16.4391 | 307.1672 | 2.0383 | 0 | 0 | 74.9147 | 24.4975 | 60.3242 | 0 | 2439.4765 | 0 | 2439.4774 | -0.00094805 | 16.4382 | 4.6688 | 0.32764 | 14.6653 | 4.1532 | 0.02756 | 1.0129 | 6.7596 | 0 | 0.33123 | 0 | 0.81564 | 32.9842 | 32.9842 | -1.2819e-05
VA_3A_PS_2016_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 361023.541 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 108079.5862 | 0 | 0 | 811293.542 | 0 | 811293.542 | 0 | 0 | 3046.3166 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 911.9755 | 0 | 0 | 6845.6949 | 0 | 6845.6949 | 0 | 0 | 361.0235 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0796 | 0 | 0 | 811.2935 | 0 | 811.2935 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.8814 | 1.4613 | 0 | 0 | 10.9695 | 10.9695 | 0
VA_3A_PS_2019_EL | 3A | PS | EL |  |  | SchoolPrimary | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 136233.1244 | 81659.2962 | 7102.0164 | 312483.1662 | 4745.7919 | 79355.8644 | 441.7921 | 0 | 0 | 23109.3391 | 7179.8163 | 12517.4429 | 0 | 664827.6501 | 0 | 664827.6501 | 0 | 4745.7919 | 0 | 10489.9506 | 6287.7658 | 546.8553 | 24061.2038 | 365.426 | 6110.4016 | 34.018 | 0 | 0 | 1779.4191 | 552.8459 | 963.8431 | 0 | 51191.7291 | 0 | 51191.7291 | 0 | 365.426 | 0 | 464.8274 | 278.6215 | 24.2321 | 1066.1926 | 16.1926 | 270.7622 | 1.5074 | 0 | 0 | 78.8491 | 24.4975 | 42.7095 | 0 | 2268.3919 | 0 | 2268.3919 | 0 | 16.1926 | 3.7672 | 0.32764 | 14.416 | 3.661 | 0.020381 | 1.0661 | 6.2849 | 0 | 0.33123 | 0 | 0.57748 | 30.6709 | 30.6709 | 0
VA_3A_PS_2019_NG | 3A | PS | NG |  |  | SchoolPrimary | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 315272.4086 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 107757.3284 | 0 | 0 | 765220.1518 | 0 | 765220.1518 | 0 | 0 | 2660.2686 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 909.2563 | 0 | 0 | 6456.9276 | 0 | 6456.9276 | 0 | 0 | 315.2724 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7573 | 0 | 0 | 765.2202 | 0 | 765.2202 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.2628 | 1.457 | 0 | 0 | 10.3465 | 10.3465 | 0
VA_3A_RS_2016_EL | 3A | RS | EL |  |  | RetailStandalone | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 55529.6551 | 83501.4859 | 10700.2603 | 53987.5506 | 0 | 37571.7787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241290.7307 | 0 | 241288.5078 | 2.2229 | 2.2229 | 0 | 4275.7834 | 6429.6144 | 823.92 | 4157.0414 | 0 | 2893.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18579.3863 | 0 | 18579.2151 | 0.17116 | 0.17116 | 0 | 189.4672 | 284.9071 | 36.5093 | 184.2055 | 0 | 128.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823.284 | 0 | 823.2764 | 0.0075844 | 0.0075844 | 11.5384 | 1.4786 | 7.4601 | 5.1918 | 0 | 0 | 7.6732 | 0 | 0 | 0 | 0 | 33.3418 | 33.3421 | 0.00030716
VA_3A_RS_2016_NG | 3A | RS | NG |  |  | RetailStandalone | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 221561.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87256.0441 | 0 | 0 | 308817.774 | 0 | 308817.774 | 0 | 0 | 1869.5379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736.2665 | 0 | 0 | 2605.8044 | 0 | 2605.8044 | 0 | 0 | 221.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.256 | 0 | 0 | 308.8178 | 0 | 308.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.973 | 3.5338 | 0 | 0 | 12.5068 | 12.5068 | 0
VA_3A_RS_2019_EL | 3A | RS | EL |  |  | RetailStandalone | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 51936.9684 | 66002.073 | 10700.2603 | 53987.5506 | 0 | 35849.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218475.9197 | 0 | 218475.6418 | 0.27786 | 0.27786 | 0 | 3999.1466 | 5082.1596 | 823.92 | 4157.0414 | 0 | 2760.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16822.6458 | 0 | 16822.6244 | 0.021395 | 0.021395 | 0 | 177.2089 | 225.1991 | 36.5093 | 184.2055 | 0 | 122.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745.4398 | 0 | 745.4389 | 0.00094805 | 0.00094805 | 9.1203 | 1.4786 | 7.4601 | 4.9537 | 0 | 0 | 7.1768 | 0 | 0 | 0 | 0 | 30.1895 | 30.1895 | 3.8395e-05
VA_3A_RS_2019_NG | 3A | RS | NG |  |  | RetailStandalone | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 242053.5361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87265.5222 | 0 | 0 | 329319.0583 | 0 | 329319.0583 | 0 | 0 | 2042.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736.3465 | 0 | 0 | 2778.7942 | 0 | 2778.7942 | 0 | 0 | 242.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2655 | 0 | 0 | 329.3191 | 0 | 329.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8029 | 3.5342 | 0 | 0 | 13.3371 | 13.3371 | 0
VA_3A_SH_2016_EL | 3A | SH | EL |  |  | HotelSmall | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 14806.9819 | 89308.6903 | 80233.8915 | 12309.0504 | 154949.5496 | 0 | 45829.6789 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 397510.0853 | 0 | 397509.2517 | 0.83357 | 0.83357 | 1140.1376 | 6876.7692 | 6178.0096 | 947.7969 | 11931.1153 | 0 | 3528.8853 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 30608.2766 | 0 | 30608.2124 | 0.064185 | 0.064185 | 50.5214 | 304.7213 | 273.758 | 41.9985 | 528.6879 | 0 | 156.3709 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1356.3044 | 0 | 1356.3016 | 0.0028441 | 0.0028441 | 6.3367 | 0.97214 | 12.2376 | 3.6195 | 0.0057056 | 0 | 7.0534 | 1.1694 | 0 | 0 | 0 | 31.3944 | 31.3945 | 6.5834e-05
VA_3A_SH_2016_NG | 3A | SH | NG |  |  | HotelSmall | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 34415.2396 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 529469.5996 | 0 | 0 | 963380.2771 | 0 | 963380.2771 | 0 | 0 | 290.3958 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 4467.6645 | 0 | 0 | 8129.0028 | 0 | 8129.0028 | 0 | 0 | 34.4152 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 529.4696 | 0 | 0 | 963.3803 | 0 | 963.3803 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.79661 | 12.2557 | 0 | 0 | 22.2994 | 22.2994 | 0
VA_3A_SH_2019_EL | 3A | SH | EL |  |  | HotelSmall | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 16921.4711 | 83971.0637 | 51386.8122 | 12309.0504 | 154949.5496 | 0 | 43462.34 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 363072.5298 | 0 | 363073.9191 | -1.3893 | -1.3893 | 1302.9533 | 6465.7719 | 3956.7845 | 947.7969 | 11931.1153 | 0 | 3346.6002 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 27956.5848 | 0 | 27956.6918 | -0.10697 | -0.10697 | 57.7361 | 286.5093 | 175.3318 | 41.9985 | 528.6879 | 0 | 148.2935 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.8035 | 0 | 1238.8082 | -0.0047402 | -0.0047402 | 4.0584 | 0.97214 | 12.2376 | 3.4326 | 0.0057056 | 0 | 6.6319 | 1.3364 | 0 | 0 | 0 | 28.6748 | 28.6747 | -0.00010972
VA_3A_SH_2019_NG | 3A | SH | NG |  |  | HotelSmall | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 35306.1877 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 529507.5123 | 0 | 0 | 964309.1379 | 0 | 964309.1379 | 0 | 0 | 297.9136 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 4467.9844 | 0 | 0 | 8136.8405 | 0 | 8136.8405 | 0 | 0 | 35.3062 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 529.5075 | 0 | 0 | 964.3091 | 0 | 964.3091 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.81724 | 12.2566 | 0 | 0 | 22.3209 | 22.3209 | 0
VA_3A_SO_2016_EL | 3A | SO | EL |  |  | OfficeSmall | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 2106.1535 | 5676.6117 | 9022.006 | 1575.4473 | 13417.6985 | 0 | 4895.8345 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41697.9502 | 0 | 41694.6159 | 3.3343 | 3.3343 | 162.1738 | 437.0991 | 694.6945 | 121.3094 | 1033.1628 | 0 | 376.9793 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 3210.7422 | 0 | 3210.4854 | 0.25674 | 0.25674 | 7.1862 | 19.3686 | 30.7831 | 5.3754 | 45.7812 | 0 | 16.7046 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.2734 | 0 | 142.262 | 0.011377 | 0.011377 | 5.5949 | 0.97699 | 8.3208 | 3.0361 | 0 | 0 | 3.5203 | 1.3061 | 3.1033 | 0 | 0 | 25.8564 | 25.8585 | 0.0020677
VA_3A_SO_2016_NG | 3A | SO | NG |  |  | OfficeSmall | STD2016 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 1649.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1649.2018 | 0 | 1649.2018 | 0 | 0 | 13.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.916 | 0 | 13.916 | 0 | 0 | 1.6492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6492 | 0 | 1.6492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29975 | 0 | 0 | 0 | 0.29975 | 0.29975 | 0
VA_3A_SO_2019_EL | 3A | SO | EL |  |  | OfficeSmall | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 2153.3892 | 5395.9765 | 7246.5019 | 1575.4473 | 13417.6985 | 0 | 4498.4995 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39291.7115 | 0 | 39293.3786 | -1.6671 | -1.6671 | 165.811 | 415.4902 | 557.9806 | 121.3094 | 1033.1628 | 0 | 346.3845 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 3025.4618 | 0 | 3025.5902 | -0.12837 | -0.12837 | 7.3474 | 18.4111 | 24.7251 | 5.3754 | 45.7812 | 0 | 15.3489 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.0633 | 0 | 134.069 | -0.0056883 | -0.0056883 | 4.4938 | 0.97699 | 8.3208 | 2.7897 | 0 | 0 | 3.3463 | 1.3354 | 3.1033 | 0 | 0 | 24.3673 | 24.3663 | -0.0010339
VA_3A_SO_2019_NG | 3A | SO | NG |  |  | OfficeSmall | STD2019 | VA-NORFOLK-VA | Zone3A | Zone3A(VA-NORFOLK-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 1753.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1753.4617 | 0 | 1753.4617 | 0 | 0 | 14.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7957 | 0 | 14.7957 | 0 | 0 | 1.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7535 | 0 | 1.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3187 | 0 | 0 | 0 | 0.3187 | 0.3187 | 0
VA_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 808404.5263 | 879805.3543 | 95174.2446 | 4077910.5986 | 543457.0788 | 589781.3426 | 110867.5892 | 294047.3763 | 291699.4874 | 13751.1265 | 0 | 0 | 0 | 7704898.7246 | 0 | 7704893.7232 | 5.0014 | 543462.0803 | 0 | 62247.1485 | 67745.0123 | 7328.4168 | 313999.1161 | 41846.1951 | 45413.1634 | 8536.8044 | 22641.648 | 22460.8605 | 1058.8367 | 0 | 0 | 0 | 593277.2018 | 0 | 593276.8167 | 0.38511 | 41846.5802 | 0 | 2758.2762 | 3001.8959 | 324.7345 | 13913.831 | 1854.2756 | 2012.3339 | 378.2802 | 1003.2896 | 995.2787 | 46.9188 | 0 | 0 | 0 | 26289.1144 | 0 | 26289.0974 | 0.017065 | 1854.2926 | 6.0208 | 0.65131 | 27.9065 | 4.0361 | 0.7587 | 0.094103 | 5.5322 | 0 | 0 | 1.9962 | 0 | 52.7271 | 52.7271 | 3.4226e-05
VA_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 444516.7511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523195.0502 | 0 | 0 | 967711.8013 | 0 | 967711.8013 | 0 | 0 | 3750.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4414.7198 | 0 | 0 | 8165.5522 | 0 | 8165.5522 | 0 | 0 | 444.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.1951 | 0 | 0 | 967.7118 | 0 | 967.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89155 | 1.0494 | 0 | 0 | 1.9409 | 1.9409 | 0
VA_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 761424.5208 | 716445.0834 | 95174.2446 | 4077910.5986 | 543384.8361 | 566002.3689 | 106999.8244 | 265611.5249 | 291496.6521 | 12264.5933 | 0 | 0 | 0 | 7436714.247 | 0 | 7436710.357 | 3.89 | 543388.7261 | 0 | 58629.6881 | 55166.2714 | 7328.4168 | 313999.1161 | 41840.6324 | 43582.1824 | 8238.9865 | 20452.0874 | 22445.2422 | 944.3737 | 0 | 0 | 0 | 572626.997 | 0 | 572626.6975 | 0.29953 | 41840.9319 | 0 | 2597.9805 | 2444.5106 | 324.7345 | 13913.831 | 1854.0291 | 1931.2001 | 365.0834 | 906.2665 | 994.5866 | 41.8468 | 0 | 0 | 0 | 25374.069 | 0 | 25374.0557 | 0.013273 | 1854.0423 | 4.9029 | 0.65131 | 27.9065 | 3.8733 | 0.73223 | 0.083931 | 5.2107 | 0 | 0 | 1.9948 | 0 | 50.8918 | 50.8919 | 2.662e-05
VA_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 405097.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523166.6157 | 0 | 0 | 928263.6528 | 0 | 928263.6528 | 0 | 0 | 3418.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4414.4799 | 0 | 0 | 7832.6887 | 0 | 7832.6887 | 0 | 0 | 405.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.1666 | 0 | 0 | 928.2637 | 0 | 928.2637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81249 | 1.0493 | 0 | 0 | 1.8618 | 1.8618 | 0
VA_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 38266.4203 | 28374.723 | 7210.3805 | 142004.2074 | 0 | 22222.9763 | 0 | 0 | 0 | 0 | 104993.6992 | 0 | 0 | 343072.4068 | 0 | 343072.6847 | -0.27786 | -0.27786 | 0 | 2946.5144 | 2184.8537 | 555.1993 | 10934.324 | 0 | 1711.1692 | 0 | 0 | 0 | 0 | 8084.5148 | 0 | 0 | 26416.5753 | 0 | 26416.5967 | -0.021395 | -0.021395 | 0 | 130.565 | 96.8146 | 24.6018 | 484.5184 | 0 | 75.8248 | 0 | 0 | 0 | 0 | 358.2385 | 0 | 0 | 1170.5631 | 0 | 1170.564 | -0.00094805 | -0.00094805 | 2.8693 | 0.72914 | 14.3599 | 2.2473 | 0 | 0 | 3.8696 | 0 | 10.6173 | 0 | 0 | 34.6926 | 34.6926 | -2.8098e-05
VA_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 38102.2482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38102.2482 | 0 | 38102.2482 | 0 | 0 | 321.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321.5068 | 0 | 321.5068 | 0 | 0 | 38.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.1022 | 0 | 38.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1293 | 0 | 0 | 0 | 1.1293 | 1.1293 | 0
VA_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 37385.6147 | 23181.5818 | 7210.3805 | 142004.2074 | 0 | 21756.1771 | 0 | 0 | 0 | 0 | 105027.042 | 0 | 0 | 336565.0037 | 0 | 336566.9487 | -1.945 | -1.945 | 0 | 2878.6923 | 1784.9818 | 555.1993 | 10934.324 | 0 | 1675.2256 | 0 | 0 | 0 | 0 | 8087.0822 | 0 | 0 | 25915.5053 | 0 | 25915.655 | -0.14976 | -0.14976 | 0 | 127.5597 | 79.0956 | 24.6018 | 484.5184 | 0 | 74.2321 | 0 | 0 | 0 | 0 | 358.3523 | 0 | 0 | 1148.3598 | 0 | 1148.3664 | -0.0066363 | -0.0066363 | 2.3442 | 0.72914 | 14.3599 | 2.2001 | 0 | 0 | 3.7806 | 0 | 10.6207 | 0 | 0 | 34.0347 | 34.0346 | -0.00019668
VA_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 45447.8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45447.8309 | 0 | 45447.8309 | 0 | 0 | 383.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.4888 | 0 | 383.4888 | 0 | 0 | 45.4478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4478 | 0 | 45.4478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.347 | 0 | 0 | 0 | 1.347 | 1.347 | 0
VA_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 148539.3963 | 97005.32 | 7104.795 | 317887.4784 | 4818.0346 | 94032.2537 | 430.6778 | 0 | 0 | 19622.2379 | 7179.8163 | 17641.1199 | 0 | 714261.1299 | 0 | 714261.1299 | 0 | 4818.0346 | 0 | 11437.5335 | 7469.4096 | 547.0692 | 24477.3358 | 370.9887 | 7240.4835 | 33.1622 | 0 | 0 | 1510.9123 | 552.8459 | 1358.3662 | 0 | 54998.107 | 0 | 54998.107 | 0 | 370.9887 | 0 | 506.8164 | 330.9822 | 24.2416 | 1084.6321 | 16.4391 | 320.838 | 1.4695 | 0 | 0 | 66.9511 | 24.4975 | 60.1915 | 0 | 2437.059 | 0 | 2437.059 | 0 | 16.4391 | 4.4752 | 0.32777 | 14.6653 | 4.3381 | 0.019869 | 0.90525 | 6.8527 | 0 | 0.33123 | 0 | 0.81385 | 32.9515 | 32.9515 | 0
VA_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 187317.0974 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 110032.0895 | 0 | 0 | 639539.6017 | 0 | 639539.6017 | 0 | 0 | 1580.5817 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 928.4508 | 0 | 0 | 5396.4352 | 0 | 5396.4352 | 0 | 0 | 187.3171 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0321 | 0 | 0 | 639.5396 | 0 | 639.5396 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.5327 | 1.4877 | 0 | 0 | 8.6472 | 8.6472 | 0
VA_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 142243.1642 | 78916.8509 | 7104.795 | 312483.1662 | 4743.0133 | 83168.0579 | 250.071 | 0 | 0 | 22767.5754 | 7179.8163 | 12500.7715 | 0 | 671357.2818 | 0 | 671359.7825 | -2.5007 | 4740.5126 | 0 | 10952.7236 | 6076.5975 | 547.0692 | 24061.2038 | 365.212 | 6403.9405 | 19.2555 | 0 | 0 | 1753.1033 | 552.8459 | 962.5594 | 0 | 51694.5107 | 0 | 51694.7033 | -0.19255 | 365.0195 | 0 | 485.3337 | 269.2643 | 24.2416 | 1066.1926 | 16.1832 | 283.7694 | 0.85324 | 0 | 0 | 77.683 | 24.4975 | 42.6526 | 0 | 2290.671 | 0 | 2290.6796 | -0.0085324 | 16.1746 | 3.6407 | 0.32777 | 14.416 | 3.8368 | 0.011537 | 1.0504 | 6.5622 | 0 | 0.33123 | 0 | 0.57671 | 30.9723 | 30.9722 | -0.00011537
VA_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 176511.9823 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 109804.6134 | 0 | 0 | 628507.0104 | 0 | 628507.0104 | 0 | 0 | 1489.4081 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 926.5313 | 0 | 0 | 5303.3422 | 0 | 5303.3422 | 0 | 0 | 176.512 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 109.8046 | 0 | 0 | 628.507 | 0 | 628.507 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 2.3866 | 1.4847 | 0 | 0 | 8.498 | 8.498 | 0
VA_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 56318.7681 | 83245.8578 | 10697.4817 | 53987.5506 | 0 | 38155.2777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242404.9359 | 0 | 242404.6581 | 0.27786 | 0.27786 | 0 | 4336.5451 | 6409.9311 | 823.7061 | 4157.0414 | 0 | 2937.9564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18665.1801 | 0 | 18665.1587 | 0.021395 | 0.021395 | 0 | 192.1596 | 284.0349 | 36.4998 | 184.2055 | 0 | 130.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827.0856 | 0 | 827.0847 | 0.00094805 | 0.00094805 | 11.5031 | 1.4782 | 7.4601 | 5.2724 | 0 | 0 | 7.7823 | 0 | 0 | 0 | 0 | 33.4961 | 33.4961 | 3.8395e-05
VA_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 202302.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87843.6907 | 0 | 0 | 290145.7768 | 0 | 290145.7768 | 0 | 0 | 1707.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.2251 | 0 | 0 | 2448.2501 | 0 | 2448.2501 | 0 | 0 | 202.3021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8437 | 0 | 0 | 290.1458 | 0 | 290.1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.193 | 3.5576 | 0 | 0 | 11.7506 | 11.7506 | 0
VA_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 52990.0452 | 65815.909 | 10697.4817 | 53987.5506 | 0 | 36504.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219995.7956 | 0 | 219994.9621 | 0.83357 | 0.83357 | 0 | 4080.2335 | 5067.825 | 823.7061 | 4157.0414 | 0 | 2810.8703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16939.6763 | 0 | 16939.6121 | 0.064185 | 0.064185 | 0 | 180.802 | 224.5639 | 36.4998 | 184.2055 | 0 | 124.5544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.6257 | 0 | 750.6228 | 0.0028441 | 0.0028441 | 9.0946 | 1.4782 | 7.4601 | 5.0443 | 0 | 0 | 7.3223 | 0 | 0 | 0 | 0 | 30.3994 | 30.3995 | 0.00011518
VA_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 221476.4264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87853.1689 | 0 | 0 | 309329.5953 | 0 | 309329.5953 | 0 | 0 | 1868.8181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.305 | 0 | 0 | 2610.1231 | 0 | 2610.1231 | 0 | 0 | 221.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8532 | 0 | 0 | 309.3296 | 0 | 309.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9696 | 3.558 | 0 | 0 | 12.5275 | 12.5275 | 0
VA_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 13978.969 | 89881.075 | 79103.0149 | 12314.6075 | 154949.5496 | 0 | 46054.7428 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 396354.2015 | 0 | 396353.368 | 0.83357 | 0.83357 | 1076.3806 | 6920.8428 | 6090.9321 | 948.2248 | 11931.1153 | 0 | 3546.2152 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 30519.2735 | 0 | 30519.2093 | 0.064185 | 0.064185 | 47.6962 | 306.6742 | 269.8995 | 42.0174 | 528.6879 | 0 | 157.1388 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1352.3605 | 0 | 1352.3577 | 0.0028441 | 0.0028441 | 6.2474 | 0.97258 | 12.2376 | 3.6373 | 0.0057056 | 0 | 7.0986 | 1.104 | 0 | 0 | 0 | 31.3031 | 31.3032 | 6.5834e-05
VA_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 37524.0798 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 540909.7522 | 0 | 0 | 977929.2699 | 0 | 977929.2699 | 0 | 0 | 316.6282 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 4564.1965 | 0 | 0 | 8251.7672 | 0 | 8251.7672 | 0 | 0 | 37.5241 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 540.9098 | 0 | 0 | 977.9293 | 0 | 977.9293 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.86857 | 12.5205 | 0 | 0 | 22.6362 | 22.6362 | 0
VA_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 16599.1574 | 84376.7344 | 50733.8491 | 12314.6075 | 154949.5496 | 0 | 43748.5324 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 362794.6732 | 0 | 362793.8396 | 0.83357 | 0.83357 | 1278.1351 | 6497.0086 | 3906.5064 | 948.2248 | 11931.1153 | 0 | 3368.637 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 27935.1898 | 0 | 27935.1256 | 0.064185 | 0.064185 | 56.6363 | 287.8934 | 173.1039 | 42.0174 | 528.6879 | 0 | 149.27 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.8554 | 0 | 1237.8526 | 0.0028441 | 0.0028441 | 4.0068 | 0.97258 | 12.2376 | 3.4552 | 0.0057056 | 0 | 6.6639 | 1.311 | 0 | 0 | 0 | 28.6527 | 28.6527 | 6.5834e-05
VA_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 38765.7202 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 540947.6649 | 0 | 0 | 979208.823 | 0 | 979208.823 | 0 | 0 | 327.1051 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 4564.5164 | 0 | 0 | 8262.564 | 0 | 8262.564 | 0 | 0 | 38.7657 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 540.9477 | 0 | 0 | 979.2088 | 0 | 979.2088 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.89731 | 12.5214 | 0 | 0 | 22.6658 | 22.6658 | 0
VA_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 1589.3401 | 5859.9971 | 8805.2778 | 1578.2259 | 13417.6985 | 0 | 4906.9488 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41161.6868 | 0 | 41161.6868 | 0 | 0 | 122.3792 | 451.2198 | 678.0064 | 121.5234 | 1033.1628 | 0 | 377.8351 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 3169.4499 | 0 | 3169.4499 | 0 | 0 | 5.4228 | 19.9943 | 30.0436 | 5.3849 | 45.7812 | 0 | 16.7425 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.4437 | 0 | 140.4437 | 0 | 0 | 5.4605 | 0.97872 | 8.3208 | 3.043 | 0 | 0 | 3.634 | 0.98561 | 3.1033 | 0 | 0 | 25.5259 | 25.5259 | 0
VA_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 1052.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052.077 | 0 | 1052.077 | 0 | 0 | 8.8774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8774 | 0 | 8.8774 | 0 | 0 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0521 | 0 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19122 | 0 | 0 | 0 | 0.19122 | 0.19122 | 0
VA_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 1633.7972 | 5576.5833 | 7099.2379 | 1578.2259 | 13417.6985 | 0 | 4526.2851 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38836.0265 | 0 | 38834.6372 | 1.3893 | 1.3893 | 125.8024 | 429.3969 | 546.6413 | 121.5234 | 1033.1628 | 0 | 348.524 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 2990.374 | 0 | 2990.2671 | 0.10697 | 0.10697 | 5.5745 | 19.0273 | 24.2226 | 5.3849 | 45.7812 | 0 | 15.4437 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.5085 | 0 | 132.5038 | 0.0047402 | 0.0047402 | 4.4025 | 0.97872 | 8.3208 | 2.8069 | 0 | 0 | 3.4583 | 1.0132 | 3.1033 | 0 | 0 | 24.0828 | 24.0837 | 0.00086155
VA_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | VA-RICHMOND-VA | Zone4A | Zone4A(VA-RICHMOND-VA) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 1146.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.8587 | 0 | 1146.8587 | 0 | 0 | 9.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6772 | 0 | 9.6772 | 0 | 0 | 1.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1469 | 0 | 1.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20844 | 0 | 0 | 0 | 0.20844 | 0.20844 | 0
VA_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 563840.644 | 880094.3252 | 95513.2297 | 4077910.5986 | 543457.0788 | 609756.4584 | 82692.923 | 189870.5757 | 380669.1926 | 9524.9266 | 0 | 0 | 0 | 7433329.9528 | 0 | 7433329.9528 | 0 | 543457.0788 | 0 | 43415.7296 | 67767.263 | 7354.5187 | 313999.1161 | 41846.1951 | 46951.2473 | 6367.3551 | 14620.0343 | 29311.5278 | 733.4193 | 0 | 0 | 0 | 572366.4064 | 0 | 572366.4064 | 0 | 41846.1951 | 0 | 1923.8243 | 3002.8818 | 325.8911 | 13913.831 | 1854.2756 | 2080.489 | 282.1483 | 647.8384 | 1298.8433 | 32.499 | 0 | 0 | 0 | 25362.5218 | 0 | 25362.5218 | 0 | 1854.2756 | 6.0228 | 0.65363 | 27.9065 | 4.1728 | 0.56589 | 0.065182 | 3.8585 | 0 | 0 | 2.605 | 0 | 50.8687 | 50.8687 | 0
VA_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 799227.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579068.8695 | 0 | 0 | 1378296.6996 | 0 | 1378296.6996 | 0 | 0 | 6743.8844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4886.1831 | 0 | 0 | 11630.0676 | 0 | 11630.0676 | 0 | 0 | 799.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0689 | 0 | 0 | 1378.2967 | 0 | 1378.2967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.603 | 1.1614 | 0 | 0 | 2.7644 | 2.7644 | 0
VA_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 529408.6457 | 716478.4262 | 95513.2297 | 4077910.5986 | 543384.8361 | 594107.5709 | 79116.9077 | 170270.5663 | 380402.4502 | 9110.9202 | 0 | 0 | 0 | 7195704.1516 | 0 | 7195710.5423 | -6.3907 | 543378.4454 | 0 | 40764.4657 | 55168.8388 | 7354.5187 | 313999.1161 | 41840.6324 | 45746.283 | 6092.0019 | 13110.8336 | 29290.9887 | 701.5409 | 0 | 0 | 0 | 554069.2197 | 0 | 554069.7118 | -0.49208 | 41840.1403 | 0 | 1806.3423 | 2444.6244 | 325.8911 | 13913.831 | 1854.0291 | 2027.095 | 269.9469 | 580.9632 | 1297.9332 | 31.0865 | 0 | 0 | 0 | 24551.7426 | 0 | 24551.7644 | -0.021805 | 1854.0073 | 4.9031 | 0.65363 | 27.9065 | 4.0657 | 0.54142 | 0.062349 | 3.6229 | 0 | 0 | 2.6032 | 0 | 49.2426 | 49.2425 | -4.3734e-05
VA_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 766840.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579078.3476 | 0 | 0 | 1345919.2667 | 0 | 1345919.2667 | 0 | 0 | 6470.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4886.2631 | 0 | 0 | 11356.8668 | 0 | 11356.8668 | 0 | 0 | 766.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0783 | 0 | 0 | 1345.9193 | 0 | 1345.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.538 | 1.1614 | 0 | 0 | 2.6995 | 2.6995 | 0
VA_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 23145.4605 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20250.194 | 0 | 0 | 0 | 0 | 116005.159 | 0 | 0 | 336984.5672 | 0 | 336983.178 | 1.3893 | 1.3893 | 0 | 1782.2005 | 2184.8537 | 554.7714 | 10934.324 | 0 | 1559.2649 | 0 | 0 | 0 | 0 | 8932.3972 | 0 | 0 | 25947.8117 | 0 | 25947.7047 | 0.10697 | 0.10697 | 0 | 78.9723 | 96.8146 | 24.5829 | 484.5184 | 0 | 69.0937 | 0 | 0 | 0 | 0 | 395.8096 | 0 | 0 | 1149.7913 | 0 | 1149.7866 | 0.0047402 | 0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.0478 | 0 | 0 | 2.3405 | 0 | 11.7308 | 0 | 0 | 34.0768 | 34.077 | 0.00014049
VA_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 82128.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82128.3534 | 0 | 82128.3534 | 0 | 0 | 692.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 692.999 | 0 | 692.999 | 0 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1284 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4341 | 0 | 0 | 0 | 2.4341 | 2.4341 | 0
VA_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 21825.6413 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19552.7737 | 0 | 0 | 0 | 0 | 116044.0589 | 0 | 0 | 329813.0866 | 0 | 329817.5323 | -4.4457 | -4.4457 | 0 | 1680.5744 | 1784.9818 | 554.7714 | 10934.324 | 0 | 1505.5636 | 0 | 0 | 0 | 0 | 8935.3925 | 0 | 0 | 25395.6077 | 0 | 25395.95 | -0.34232 | -0.34232 | 0 | 74.4691 | 79.0956 | 24.5829 | 484.5184 | 0 | 66.7141 | 0 | 0 | 0 | 0 | 395.9423 | 0 | 0 | 1125.3223 | 0 | 1125.3374 | -0.015169 | -0.015169 | 2.3442 | 0.72858 | 14.3599 | 1.9772 | 0 | 0 | 2.2071 | 0 | 11.7348 | 0 | 0 | 33.3522 | 33.3518 | -0.00044956
VA_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 95151.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95151.3607 | 0 | 95151.3607 | 0 | 0 | 802.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.8872 | 0 | 802.8872 | 0 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1514 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8201 | 0 | 0 | 0 | 2.8201 | 2.8201 | 0
VA_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 85226.9758 | 96613.5421 | 7107.5736 | 317887.4784 | 4818.0346 | 87894.3999 | 708.5345 | 0 | 0 | 19688.9235 | 7179.8163 | 17630.0056 | 0 | 644755.2844 | 0 | 644755.0065 | 0.27786 | 4818.3125 | 0 | 6562.4771 | 7439.2427 | 547.2832 | 24477.3358 | 370.9887 | 6767.8688 | 54.5572 | 0 | 0 | 1516.0471 | 552.8459 | 1357.5104 | 0 | 49646.1569 | 0 | 49646.1355 | 0.021395 | 371.0101 | 0 | 290.7944 | 329.6454 | 24.251 | 1084.6321 | 16.4391 | 299.8957 | 2.4175 | 0 | 0 | 67.1786 | 24.4975 | 60.1536 | 0 | 2199.905 | 0 | 2199.9041 | 0.00094805 | 16.4401 | 4.4571 | 0.3279 | 14.6653 | 4.0549 | 0.032687 | 0.90832 | 3.9318 | 0 | 0.33123 | 0 | 0.81334 | 29.7449 | 29.7449 | 1.2819e-05
VA_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 400642.2966 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120742.4229 | 0 | 0 | 863575.1344 | 0 | 863575.1344 | 0 | 0 | 3380.6197 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.8246 | 0 | 0 | 7286.847 | 0 | 7286.847 | 0 | 0 | 400.6423 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7424 | 0 | 0 | 863.5751 | 0 | 863.5751 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.4171 | 1.6326 | 0 | 0 | 11.6764 | 11.6764 | 0
VA_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 80445.0626 | 78544.523 | 7107.5736 | 312483.1662 | 4743.0133 | 75635.3637 | 489.0277 | 0 | 0 | 22461.9331 | 7179.8163 | 12495.2144 | 0 | 601584.6938 | 0 | 601589.1395 | -4.4457 | 4738.5676 | 0 | 6194.2698 | 6047.9283 | 547.2832 | 24061.2038 | 365.212 | 5823.923 | 37.6551 | 0 | 0 | 1729.5688 | 552.8459 | 962.1315 | 0 | 46322.0214 | 0 | 46322.3637 | -0.34232 | 364.8697 | 0 | 274.4786 | 267.9939 | 24.251 | 1066.1926 | 16.1832 | 258.0679 | 1.6686 | 0 | 0 | 76.6401 | 24.4975 | 42.6337 | 0 | 2052.607 | 0 | 2052.6221 | -0.015169 | 16.168 | 3.6235 | 0.3279 | 14.416 | 3.4893 | 0.022561 | 1.0363 | 3.7112 | 0 | 0.33123 | 0 | 0.57645 | 27.7535 | 27.7533 | -0.0002051
VA_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 380747.6153 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120505.4686 | 0 | 0 | 843443.4987 | 0 | 843443.4987 | 0 | 0 | 3212.7484 | 0 | 0 | 0 | 2887.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 1016.8251 | 0 | 0 | 7116.9762 | 0 | 7116.9762 | 0 | 0 | 380.7476 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5055 | 0 | 0 | 843.4435 | 0 | 843.4435 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.1481 | 1.6294 | 0 | 0 | 11.4042 | 11.4042 | 0
VA_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 27982.9451 | 83498.7074 | 10680.8103 | 53987.5506 | 0 | 42720.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218870.4761 | 0 | 218871.0319 | -0.55571 | -0.55571 | 0 | 2154.6868 | 6429.4005 | 822.4224 | 4157.0414 | 0 | 3289.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16853.0267 | 0 | 16853.0695 | -0.04279 | -0.04279 | 0 | 95.4778 | 284.8976 | 36.4429 | 184.2055 | 0 | 145.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.7861 | 0 | 746.788 | -0.0018961 | -0.0018961 | 11.5381 | 1.4759 | 7.4601 | 5.9032 | 0 | 0 | 3.8668 | 0 | 0 | 0 | 0 | 30.2441 | 30.244 | -7.679e-05
VA_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 379951.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91180.0069 | 0 | 0 | 471131.4558 | 0 | 471131.4558 | 0 | 0 | 3206.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769.3769 | 0 | 0 | 3975.4072 | 0 | 3975.4072 | 0 | 0 | 379.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.18 | 0 | 0 | 471.1315 | 0 | 471.1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3876 | 3.6927 | 0 | 0 | 19.0803 | 19.0803 | 0
VA_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 0 | 25637.8348 | 65952.0588 | 10680.8103 | 53987.5506 | 0 | 40605.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196864.228 | 0 | 196864.5059 | -0.27786 | -0.27786 | 0 | 1974.1133 | 5078.3085 | 822.4224 | 4157.0414 | 0 | 3126.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15158.5456 | 0 | 15158.567 | -0.021395 | -0.021395 | 0 | 87.4763 | 225.0284 | 36.4429 | 184.2055 | 0 | 138.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 671.7007 | 0 | 671.7017 | -0.00094805 | -0.00094805 | 9.1134 | 1.4759 | 7.4601 | 5.611 | 0 | 0 | 3.5427 | 0 | 0 | 0 | 0 | 27.2032 | 27.2032 | -3.8395e-05
VA_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 408755.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91189.4851 | 0 | 0 | 499945.0963 | 0 | 499945.0963 | 0 | 0 | 3449.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769.4569 | 0 | 0 | 4218.5367 | 0 | 4218.5367 | 0 | 0 | 408.7556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1895 | 0 | 0 | 499.9451 | 0 | 499.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5542 | 3.6931 | 0 | 0 | 20.2472 | 20.2472 | 0
VA_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 25423.8851 | 62926.1997 | 79094.6792 | 12306.2718 | 154949.5496 | 0 | 45768.5504 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380541.3786 | 0 | 380541.6564 | -0.27786 | -0.27786 | 1957.6392 | 4845.3174 | 6090.2903 | 947.5829 | 11931.1153 | 0 | 3524.1784 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 29301.6861 | 0 | 29301.7075 | -0.021395 | -0.021395 | 86.7463 | 214.7042 | 269.871 | 41.989 | 528.6879 | 0 | 156.1623 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.4072 | 0 | 1298.4081 | -0.00094805 | -0.00094805 | 6.2467 | 0.97192 | 12.2376 | 3.6147 | 0.0057056 | 0 | 4.9698 | 2.0079 | 0 | 0 | 0 | 30.0544 | 30.0543 | -2.1945e-05
VA_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605437.1417 | 0 | 0 | 1070682.6533 | 0 | 1070682.6533 | 0 | 0 | 554.7991 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 5108.6786 | 0 | 0 | 9034.4202 | 0 | 9034.4202 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4371 | 0 | 0 | 1070.6827 | 0 | 1070.6827 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0141 | 0 | 0 | 24.7832 | 24.7832 | 0
VA_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 29311.0999 | 58294.329 | 50731.0705 | 12306.2718 | 154949.5496 | 0 | 43317.8546 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348982.4182 | 0 | 348984.0853 | -1.6671 | -1.6671 | 2256.9547 | 4488.6633 | 3906.2924 | 947.5829 | 11931.1153 | 0 | 3335.4748 | 5.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 26871.6462 | 0 | 26871.7746 | -0.12837 | -0.12837 | 100.0095 | 198.9003 | 173.0944 | 41.989 | 528.6879 | 0 | 147.8005 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.728 | 0 | 1190.7337 | -0.0056883 | -0.0056883 | 4.0066 | 0.97192 | 12.2376 | 3.4211 | 0.0057056 | 0 | 4.604 | 2.3149 | 0 | 0 | 0 | 27.562 | 27.5619 | -0.00013167
VA_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605503.4889 | 0 | 0 | 1070749.0005 | 0 | 1070749.0005 | 0 | 0 | 554.7991 | 0 | 0 | 0 | 3370.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 5109.2384 | 0 | 0 | 9034.9801 | 0 | 9034.9801 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5035 | 0 | 0 | 1070.749 | 0 | 1070.749 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0156 | 0 | 0 | 24.7847 | 24.7847 | 0
VA_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 3103.659 | 3061.9805 | 8816.3921 | 1583.783 | 13417.6985 | 0 | 4776.3561 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39764.0678 | 0 | 39766.0128 | -1.945 | -1.945 | 238.9817 | 235.7725 | 678.8622 | 121.9513 | 1033.1628 | 0 | 367.7794 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 3061.8332 | 0 | 3061.983 | -0.14976 | -0.14976 | 10.5897 | 10.4475 | 30.0815 | 5.4039 | 45.7812 | 0 | 16.2969 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.675 | 0 | 135.6816 | -0.0066363 | -0.0066363 | 5.4674 | 0.98216 | 8.3208 | 2.962 | 0 | 0 | 1.8989 | 1.9247 | 3.1033 | 0 | 0 | 24.6604 | 24.6592 | -0.0012062
VA_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 8757.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8757.8302 | 0 | 8757.8302 | 0 | 0 | 73.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8986 | 0 | 73.8986 | 0 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7578 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5918 | 0 | 0 | 0 | 1.5918 | 1.5918 | 0
VA_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Electricity | 3162.0089 | 2861.9237 | 7104.795 | 1583.783 | 13417.6985 | 0 | 4370.6854 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37505.0931 | 0 | 37504.2595 | 0.83357 | 0.83357 | 243.4747 | 220.3681 | 547.0692 | 121.9513 | 1033.1628 | 0 | 336.5428 | 0 | 0 | 0 | 0 | 385.3233 | 0 | 0 | 2887.8922 | 0 | 2887.828 | 0.064185 | 0.064185 | 10.7888 | 9.7649 | 24.2416 | 5.4039 | 45.7812 | 0 | 14.9128 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 127.9674 | 0 | 127.9645 | 0.0028441 | 0.0028441 | 4.406 | 0.98216 | 8.3208 | 2.7104 | 0 | 0 | 1.7748 | 1.9609 | 3.1033 | 0 | 0 | 23.2578 | 23.2583 | 0.00051693
VA_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | VA-ELKINS-WV | Zone5A | Zone5A(VA-ELKINS-WV) |  |  | VA | 0.077 | 0.008438 |  |  |  | Natural Gas | 9127.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.4789 | 0 | 9127.4789 | 0 | 0 | 77.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0177 | 0 | 77.0177 | 0 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1275 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 0 | 0 | 0 | 1.6589 | 1.6589 | 0
VT_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 478013.4978 | 882531.1282 | 96452.3852 | 4077910.5986 | 543459.8574 | 584668.7799 | 75424.1926 | 161690.3524 | 442617.3368 | 11600.5159 | 0 | 0 | 0 | 7354368.6448 | 0 | 7354365.0327 | 3.6121 | 543463.4695 | 0 | 78442.015 | 144823.3581 | 15827.8364 | 669185.1292 | 89181.7626 | 95944.1468 | 12377.11 | 26533.3868 | 72633.505 | 1903.6447 | 0 | 0 | 0 | 1206851.8946 | 0 | 1206851.3019 | 0.59275 | 89182.3554 | 0 | 1630.9821 | 3011.1962 | 329.0955 | 13913.831 | 1854.285 | 1994.8899 | 257.3473 | 551.6875 | 1510.2104 | 39.581 | 0 | 0 | 0 | 25093.1058 | 0 | 25093.0935 | 0.012325 | 1854.2974 | 6.0394 | 0.66006 | 27.9065 | 4.0011 | 0.51615 | 0.079386 | 3.2712 | 0 | 0 | 3.029 | 0 | 50.3283 | 50.3283 | 2.4719e-05
VT_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 1316328.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599740.7609 | 0 | 0 | 1916069.1771 | 0 | 1916069.1771 | 0 | 0 | 10509.5661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4788.3302 | 0 | 0 | 15297.8963 | 0 | 15297.8963 | 0 | 0 | 1316.3284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.7408 | 0 | 0 | 1916.0692 | 0 | 1916.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6401 | 1.2029 | 0 | 0 | 3.843 | 3.843 | 0
VT_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 443681.5278 | 718729.0652 | 96452.3852 | 4077910.5986 | 543387.6147 | 562915.3813 | 71295.2425 | 144635.5101 | 442292.2445 | 10689.146 | 0 | 0 | 0 | 7111988.716 | 0 | 7111988.9938 | -0.27786 | 543387.3368 | 0 | 72808.1387 | 117943.4396 | 15827.8364 | 669185.1292 | 89169.9076 | 92374.4141 | 11699.5493 | 23734.6872 | 72580.1573 | 1754.0889 | 0 | 0 | 0 | 1167077.3483 | 0 | 1167077.3939 | -0.045596 | 89169.862 | 0 | 1513.8414 | 2452.3036 | 329.0955 | 13913.831 | 1854.0385 | 1920.6673 | 243.2594 | 493.4964 | 1509.1011 | 36.4714 | 0 | 0 | 0 | 24266.1055 | 0 | 24266.1064 | -0.00094805 | 1854.0376 | 4.9185 | 0.66006 | 27.9065 | 3.8522 | 0.4879 | 0.073149 | 3.0363 | 0 | 0 | 3.0267 | 0 | 48.6697 | 48.6697 | -1.9015e-06
VT_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 1298566.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599769.1954 | 0 | 0 | 1898335.5188 | 0 | 1898335.5188 | 0 | 0 | 10367.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4788.5573 | 0 | 0 | 15156.3108 | 0 | 15156.3108 | 0 | 0 | 1298.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.7692 | 0 | 0 | 1898.3355 | 0 | 1898.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6045 | 1.2029 | 0 | 0 | 3.8074 | 3.8074 | 0
VT_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 20478.0364 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20322.4367 | 0 | 0 | 0 | 0 | 120109.102 | 0 | 0 | 338490.5504 | 0 | 338491.384 | -0.83357 | -0.83357 | 0 | 3360.4458 | 4656.292 | 1181.8556 | 23302.8904 | 0 | 3334.9119 | 0 | 0 | 0 | 0 | 19709.9036 | 0 | 0 | 55546.2993 | 0 | 55546.4361 | -0.13679 | -0.13679 | 0 | 69.8711 | 96.8146 | 24.5734 | 484.5184 | 0 | 69.3402 | 0 | 0 | 0 | 0 | 409.8123 | 0 | 0 | 1154.9298 | 0 | 1154.9326 | -0.0028441 | -0.0028441 | 2.8693 | 0.72829 | 14.3599 | 2.0551 | 0 | 0 | 2.0708 | 0 | 12.1458 | 0 | 0 | 34.2294 | 34.2293 | -8.4293e-05
VT_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 175943.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175943.292 | 0 | 175943.292 | 0 | 0 | 1404.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.7312 | 0 | 1404.7312 | 0 | 0 | 175.9433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.9433 | 0 | 175.9433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2145 | 0 | 0 | 0 | 5.2145 | 5.2145 | 0
VT_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 18699.7538 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 19461.081 | 0 | 0 | 0 | 0 | 120150.7805 | 0 | 0 | 330699.4494 | 0 | 330703.0615 | -3.6121 | -3.6121 | 0 | 3068.6296 | 3804.0976 | 1181.8556 | 23302.8904 | 0 | 3193.5634 | 0 | 0 | 0 | 0 | 19716.7431 | 0 | 0 | 54267.7796 | 0 | 54268.3724 | -0.59275 | -0.59275 | 0 | 63.8036 | 79.0956 | 24.5734 | 484.5184 | 0 | 66.4012 | 0 | 0 | 0 | 0 | 409.9545 | 0 | 0 | 1128.3465 | 0 | 1128.3588 | -0.012325 | -0.012325 | 2.3442 | 0.72829 | 14.3599 | 1.968 | 0 | 0 | 1.891 | 0 | 12.15 | 0 | 0 | 33.4418 | 33.4414 | -0.00036527
VT_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 201041.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201041.4893 | 0 | 201041.4893 | 0 | 0 | 1605.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1605.1153 | 0 | 1605.1153 | 0 | 0 | 201.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0415 | 0 | 201.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9584 | 0 | 0 | 0 | 5.9584 | 5.9584 | 0
VT_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 68208.2549 | 98213.9965 | 7163.1449 | 317887.4784 | 4818.0346 | 93923.8896 | 1286.4764 | 0 | 0 | 18605.2825 | 7179.8163 | 17613.3342 | 0 | 634899.7084 | 0 | 634898.8748 | 0.83357 | 4818.8682 | 0 | 11192.9746 | 16116.9168 | 1175.4721 | 52165.3352 | 790.6395 | 15412.9103 | 211.1108 | 0 | 0 | 3053.1269 | 1178.2079 | 2890.3481 | 0 | 104187.0421 | 0 | 104186.9054 | 0.13679 | 790.7763 | 0 | 232.7266 | 335.1062 | 24.4407 | 1084.6321 | 16.4391 | 320.4683 | 4.3895 | 0 | 0 | 63.4812 | 24.4975 | 60.0967 | 0 | 2166.2778 | 0 | 2166.275 | 0.0028441 | 16.442 | 4.531 | 0.33046 | 14.6653 | 4.3331 | 0.05935 | 0.85833 | 3.1467 | 0 | 0.33123 | 0 | 0.81257 | 29.2902 | 29.2903 | 3.8456e-05
VT_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 682200.8503 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125206.6416 | 0 | 0 | 1149597.9067 | 0 | 1149597.9067 | 0 | 0 | 5446.6916 | 0 | 0 | 0 | 2732.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 999.6498 | 0 | 0 | 9178.3897 | 0 | 9178.3897 | 0 | 0 | 682.2009 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.2066 | 0 | 0 | 1149.5979 | 0 | 1149.5979 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.224 | 1.6929 | 0 | 0 | 15.5437 | 15.5437 | 0
VT_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 63581.9414 | 80406.1627 | 7163.1449 | 312483.1662 | 4745.7919 | 80270.0129 | 853.02 | 0 | 0 | 22584.19 | 7179.8163 | 12478.543 | 0 | 591745.7892 | 0 | 591745.7892 | 0 | 4745.7919 | 0 | 10433.7966 | 13194.6513 | 1175.4721 | 51278.4876 | 778.7844 | 13172.3091 | 139.9806 | 0 | 0 | 3706.0656 | 1178.2079 | 2047.7289 | 0 | 97105.484 | 0 | 97105.484 | 0 | 778.7844 | 0 | 216.9416 | 274.3458 | 24.4407 | 1066.1926 | 16.1926 | 273.8813 | 2.9105 | 0 | 0 | 77.0573 | 24.4975 | 42.5768 | 0 | 2019.0366 | 0 | 2019.0366 | 0 | 16.1926 | 3.7094 | 0.33046 | 14.416 | 3.7032 | 0.039353 | 1.0419 | 2.9333 | 0 | 0.33123 | 0 | 0.57568 | 27.2994 | 27.2994 | 0
VT_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 671405.2133 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 124960.2091 | 0 | 0 | 1138555.8372 | 0 | 1138555.8372 | 0 | 0 | 5360.4992 | 0 | 0 | 0 | 2732.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 997.6823 | 0 | 0 | 9090.2298 | 0 | 9090.2298 | 0 | 0 | 671.4052 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 124.9602 | 0 | 0 | 1138.5558 | 0 | 1138.5558 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.0781 | 1.6896 | 0 | 0 | 15.3944 | 15.3944 | 0
VT_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 22575.8543 | 90706.3093 | 10789.1744 | 53987.5506 | 0 | 44668.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222727.1267 | 0 | 222725.4596 | 1.6671 | 1.6671 | 0 | 3704.6977 | 14884.9054 | 1770.5035 | 8859.3571 | 0 | 7330.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36549.5215 | 0 | 36549.2479 | 0.27358 | 0.27358 | 0 | 77.0288 | 309.4899 | 36.8127 | 184.2055 | 0 | 152.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759.945 | 0 | 759.9393 | 0.0056883 | 0.0056883 | 12.534 | 1.4909 | 7.4601 | 6.1724 | 0 | 0 | 3.1196 | 0 | 0 | 0 | 0 | 30.7767 | 30.777 | 0.00023037
VT_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 610621.7014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92431.1255 | 0 | 0 | 703052.8269 | 0 | 703052.8269 | 0 | 0 | 4875.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 737.9701 | 0 | 0 | 5613.1738 | 0 | 5613.1738 | 0 | 0 | 610.6217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4311 | 0 | 0 | 703.0528 | 0 | 703.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.7295 | 3.7434 | 0 | 0 | 28.4729 | 28.4729 | 0
VT_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 0 | 21147.671 | 75071.3146 | 10789.1744 | 53987.5506 | 0 | 42764.9198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203760.6305 | 0 | 203762.8534 | -2.2229 | -2.2229 | 0 | 3470.3328 | 12319.2027 | 1770.5035 | 8859.3571 | 0 | 7017.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33437.1195 | 0 | 33437.4842 | -0.36477 | -0.36477 | 0 | 72.1559 | 256.1433 | 36.8127 | 184.2055 | 0 | 145.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695.2313 | 0 | 695.2389 | -0.0075844 | -0.0075844 | 10.3735 | 1.4909 | 7.4601 | 5.9094 | 0 | 0 | 2.9222 | 0 | 0 | 0 | 0 | 28.1564 | 28.1561 | -0.00030716
VT_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 641056.1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92440.6037 | 0 | 0 | 733496.7128 | 0 | 733496.7128 | 0 | 0 | 5118.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 738.0458 | 0 | 0 | 5856.2378 | 0 | 5856.2378 | 0 | 0 | 641.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4406 | 0 | 0 | 733.4967 | 0 | 733.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9621 | 3.7437 | 0 | 0 | 29.7058 | 29.7058 | 0
VT_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 46443.7421 | 54276.5216 | 79183.5933 | 12300.7147 | 154949.5496 | 0 | 45110.0301 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 392336.3941 | 0 | 392338.8948 | -2.5007 | -2.5007 | 7621.4181 | 8906.7772 | 12994.0277 | 2018.5473 | 25427.2211 | 0 | 7402.5559 | 11.855 | 0 | 0 | 0 | 0 | 0 | 0 | 64382.4023 | 0 | 64382.8126 | -0.41037 | -0.41037 | 158.466 | 185.1915 | 270.1744 | 41.97 | 528.6879 | 0 | 153.9154 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.6518 | 0 | 1338.6603 | -0.0085324 | -0.0085324 | 6.2537 | 0.97148 | 12.2376 | 3.5627 | 0.0057056 | 0 | 4.2866 | 3.668 | 0 | 0 | 0 | 30.9861 | 30.9859 | -0.0001975
VT_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 110221.6529 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 629274.7423 | 0 | 0 | 1138991.8331 | 0 | 1138991.8331 | 0 | 0 | 880.0097 | 0 | 0 | 0 | 3189.5716 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.1295 | 0 | 0 | 9093.7108 | 0 | 9093.7108 | 0 | 0 | 110.2217 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 629.2747 | 0 | 0 | 1138.9918 | 0 | 1138.9918 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.5513 | 14.5659 | 0 | 0 | 26.3643 | 26.3643 | 0
VT_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 51956.4184 | 50050.3216 | 50883.8917 | 12300.7147 | 154949.5496 | 0 | 42667.67 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 362880.8087 | 0 | 362883.5873 | -2.7786 | -2.7786 | 8526.0483 | 8213.2578 | 8350.0466 | 2018.5473 | 25427.2211 | 0 | 7001.7646 | 11.855 | 0 | 0 | 0 | 0 | 0 | 0 | 59548.7407 | 0 | 59549.1967 | -0.45596 | -0.45596 | 177.2753 | 170.7717 | 173.6158 | 41.97 | 528.6879 | 0 | 145.5821 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.1493 | 0 | 1238.1588 | -0.0094805 | -0.0094805 | 4.0187 | 0.97148 | 12.2376 | 3.3698 | 0.0057056 | 0 | 3.9529 | 4.1034 | 0 | 0 | 0 | 28.6598 | 28.6595 | -0.00021945
VT_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 106743.1641 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 629360.0459 | 0 | 0 | 1135598.6478 | 0 | 1135598.6478 | 0 | 0 | 852.2374 | 0 | 0 | 0 | 3189.5716 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.8106 | 0 | 0 | 9066.6196 | 0 | 9066.6196 | 0 | 0 | 106.7432 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 629.36 | 0 | 0 | 1135.5986 | 0 | 1135.5986 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.4708 | 14.5678 | 0 | 0 | 26.2858 | 26.2858 | 0
VT_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 4748.5705 | 2731.331 | 8819.1706 | 1592.1187 | 13417.6985 | 0 | 4781.9133 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41095.0012 | 0 | 41094.1677 | 0.83357 | 0.83357 | 779.2404 | 448.2114 | 1447.2259 | 261.2667 | 2201.8443 | 0 | 784.712 | 0 | 0 | 0 | 0 | 821.189 | 0 | 0 | 6743.6897 | 0 | 6743.5529 | 0.13679 | 0.13679 | 16.2021 | 9.3193 | 30.091 | 5.4323 | 45.7812 | 0 | 16.3159 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.2161 | 0 | 140.2133 | 0.0028441 | 0.0028441 | 5.4691 | 0.98733 | 8.3208 | 2.9654 | 0 | 0 | 1.6938 | 2.9448 | 3.1033 | 0 | 0 | 25.4841 | 25.4846 | 0.00051693
VT_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 17752.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17752.6147 | 0 | 17752.6147 | 0 | 0 | 141.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.7369 | 0 | 141.7369 | 0 | 0 | 17.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7526 | 0 | 17.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2266 | 0 | 0 | 0 | 3.2266 | 3.2266 | 0
VT_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Electricity | 4806.9204 | 2484.0386 | 7129.8021 | 1592.1187 | 13417.6985 | 0 | 4331.7855 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38766.5624 | 0 | 38768.5073 | -1.945 | -1.945 | 788.8156 | 407.6307 | 1170.0005 | 261.2667 | 2201.8443 | 0 | 710.846 | 0 | 0 | 0 | 0 | 821.189 | 0 | 0 | 6361.5929 | 0 | 6361.9121 | -0.31917 | -0.31917 | 16.4012 | 8.4755 | 24.3269 | 5.4323 | 45.7812 | 0 | 14.7801 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.2715 | 0 | 132.2781 | -0.0066363 | -0.0066363 | 4.4215 | 0.98733 | 8.3208 | 2.6863 | 0 | 0 | 1.5404 | 2.981 | 3.1033 | 0 | 0 | 24.0418 | 24.0406 | -0.0012062
VT_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | VT-BURLINGTON-VT | Zone6A | Zone6A(VT-BURLINGTON-VT) |  |  | VT | 0.1641 | 0.007984 |  |  |  | Natural Gas | 18823.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18823.648 | 0 | 18823.648 | 0 | 0 | 150.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.288 | 0 | 150.288 | 0 | 0 | 18.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8236 | 0 | 18.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4212 | 0 | 0 | 0 | 3.4212 | 3.4212 | 0
WA_4C_LO_2016_EL | 4C | LO | EL |  |  | OfficeLarge | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 315675.7394 | 885693.1371 | 96902.513 | 4077910.5986 | 543459.8574 | 576980.4859 | 60936.7459 | 114654.7756 | 287220.438 | 0 | 0 | 0 | 0 | 6959434.2909 | 0 | 6959431.2344 | 3.0564 | 543462.9138 | 0 | 28126.7084 | 78915.2585 | 8634.0139 | 363341.8343 | 48422.2733 | 51408.9613 | 5429.4641 | 10215.7405 | 25591.341 | 0 | 0 | 0 | 0 | 620085.5953 | 0 | 620085.323 | 0.27233 | 48422.5456 | 0 | 1077.0856 | 3021.985 | 330.6314 | 13913.831 | 1854.285 | 1968.6574 | 207.9162 | 391.2021 | 979.9961 | 0 | 0 | 0 | 0 | 23745.5898 | 0 | 23745.5794 | 0.010429 | 1854.2955 | 6.0611 | 0.66314 | 27.9065 | 3.9485 | 0.41701 | 0 | 2.1603 | 0 | 0 | 1.9655 | 0 | 47.6257 | 47.6257 | 2.0916e-05
WA_4C_LO_2016_NG | 4C | LO | NG |  |  | OfficeLarge | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 891175.5689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561344.6893 | 0 | 0 | 1452520.2582 | 0 | 1452520.2582 | 0 | 0 | 6837.9901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4307.1978 | 0 | 0 | 11145.1879 | 0 | 11145.1879 | 0 | 0 | 891.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.3447 | 0 | 0 | 1452.5203 | 0 | 1452.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7874 | 1.1259 | 0 | 0 | 2.9133 | 2.9133 | 0
WA_4C_LO_2019_EL | 4C | LO | EL |  |  | OfficeLarge | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 295164.3601 | 720137.7985 | 96902.513 | 4077910.5986 | 543387.6147 | 549075.3407 | 58833.3709 | 102292.9324 | 286962.0313 | 0 | 0 | 0 | 0 | 6730666.5602 | 0 | 6730665.4488 | 1.1114 | 543388.7261 | 0 | 26299.1445 | 64164.2778 | 8634.0139 | 363341.8343 | 48415.8365 | 48922.6129 | 5242.0534 | 9114.3003 | 25568.317 | 0 | 0 | 0 | 0 | 599702.3905 | 0 | 599702.2915 | 0.099028 | 48415.9355 | 0 | 1007.1008 | 2457.1102 | 330.6314 | 13913.831 | 1854.0385 | 1873.4451 | 200.7395 | 349.0235 | 979.1145 | 0 | 0 | 0 | 0 | 22965.0343 | 0 | 22965.0305 | 0.0037922 | 1854.0423 | 4.9281 | 0.66314 | 27.9065 | 3.7575 | 0.40262 | 0 | 2.0199 | 0 | 0 | 1.9638 | 0 | 46.0601 | 46.0601 | 7.6059e-06
WA_4C_LO_2019_NG | 4C | LO | NG |  |  | OfficeLarge | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 1667722.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561363.6457 | 0 | 0 | 2229085.781 | 0 | 2229085.781 | 0 | 0 | 12796.4319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4307.3433 | 0 | 0 | 17103.7752 | 0 | 17103.7752 | 0 | 0 | 1667.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.3636 | 0 | 0 | 2229.0858 | 0 | 2229.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3449 | 1.1259 | 0 | 0 | 4.4708 | 4.4708 | 0
WA_4C_MA_2016_EL | 4C | MA | EL |  |  | ApartmentMidRise | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 11389.3448 | 28374.723 | 7193.7091 | 142004.2074 | 0 | 17710.584 | 0 | 0 | 0 | 0 | 112762.5717 | 0 | 0 | 319435.1401 | 0 | 319434.8622 | 0.27786 | 0.27786 | 0 | 1014.7906 | 2528.1878 | 640.9595 | 12652.5749 | 0 | 1578.013 | 0 | 0 | 0 | 0 | 10047.1451 | 0 | 0 | 28461.671 | 0 | 28461.6462 | 0.024757 | 0.024757 | 0 | 38.8604 | 96.8146 | 24.5449 | 484.5184 | 0 | 60.4285 | 0 | 0 | 0 | 0 | 384.7459 | 0 | 0 | 1089.9127 | 0 | 1089.9117 | 0.00094805 | 0.00094805 | 2.8693 | 0.72745 | 14.3599 | 1.791 | 0 | 0 | 1.1517 | 0 | 11.4029 | 0 | 0 | 32.3023 | 32.3023 | 2.8098e-05
WA_4C_MA_2016_NG | 4C | MA | NG |  |  | ApartmentMidRise | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 137689.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137689.393 | 0 | 137689.393 | 0 | 0 | 1056.4907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.4907 | 0 | 1056.4907 | 0 | 0 | 137.6894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.6894 | 0 | 137.6894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0808 | 0 | 0 | 0 | 4.0808 | 4.0808 | 0
WA_4C_MA_2019_EL | 4C | MA | EL |  |  | ApartmentMidRise | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 15873.9515 | 23181.5818 | 7193.7091 | 142004.2074 | 0 | 17980.105 | 0 | 0 | 0 | 0 | 112568.072 | 0 | 0 | 318801.6269 | 0 | 318801.9047 | -0.27786 | -0.27786 | 0 | 1414.3691 | 2065.4789 | 640.9595 | 12652.5749 | 0 | 1602.0274 | 0 | 0 | 0 | 0 | 10029.8152 | 0 | 0 | 28405.225 | 0 | 28405.2497 | -0.024757 | -0.024757 | 0 | 54.1619 | 79.0956 | 24.5449 | 484.5184 | 0 | 61.3481 | 0 | 0 | 0 | 0 | 384.0823 | 0 | 0 | 1087.7512 | 0 | 1087.7521 | -0.00094805 | -0.00094805 | 2.3442 | 0.72745 | 14.3599 | 1.8182 | 0 | 0 | 1.6052 | 0 | 11.3833 | 0 | 0 | 32.2383 | 32.2383 | -2.8098e-05
WA_4C_MA_2019_NG | 4C | MA | NG |  |  | ApartmentMidRise | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 43011.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43011.9409 | 0 | 43011.9409 | 0 | 0 | 330.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330.0306 | 0 | 330.0306 | 0 | 0 | 43.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.0119 | 0 | 43.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2748 | 0 | 0 | 0 | 1.2748 | 1.2748 | 0
WA_4C_PS_2016_EL | 4C | PS | EL |  |  | SchoolPrimary | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 44006.9391 | 100286.8073 | 7160.3663 | 317887.4784 | 4818.0346 | 87088.6155 | 936.377 | 0 | 0 | 0 | 7179.8163 | 17596.6628 | 0 | 586961.0974 | 0 | 586959.1524 | 1.945 | 4819.9796 | 0 | 3921.0183 | 8935.5545 | 637.9886 | 28323.7743 | 429.2869 | 7759.5956 | 83.4312 | 0 | 0 | 0 | 639.7216 | 1567.8627 | 0 | 52298.2338 | 0 | 52298.0605 | 0.1733 | 429.4602 | 0 | 150.1517 | 342.1786 | 24.4312 | 1084.6321 | 16.4391 | 297.1464 | 3.1949 | 0 | 0 | 0 | 24.4975 | 60.0398 | 0 | 2002.7113 | 0 | 2002.7046 | 0.0066363 | 16.4458 | 4.6266 | 0.33033 | 14.6653 | 4.0177 | 0.043199 | 0 | 2.0302 | 0 | 0.33123 | 0 | 0.8118 | 27.0786 | 27.0787 | 8.973e-05
WA_4C_PS_2016_NG | 4C | PS | NG |  |  | SchoolPrimary | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 581580.5848 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 116240.2916 | 0 | 0 | 1040011.2913 | 0 | 1040011.2913 | 0 | 0 | 4462.4678 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 891.9118 | 0 | 0 | 7980.0066 | 0 | 7980.0066 | 0 | 0 | 581.5806 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2403 | 0 | 0 | 1040.0113 | 0 | 1040.0113 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.8636 | 1.5717 | 0 | 0 | 14.062 | 14.062 | 0
WA_4C_PS_2019_EL | 4C | PS | EL |  |  | SchoolPrimary | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 43076.1193 | 81378.661 | 7160.3663 | 312483.1662 | 4745.7919 | 80400.6055 | 1033.6268 | 0 | 0 | 0 | 7179.8163 | 12484.1001 | 0 | 549942.2535 | 0 | 549942.2535 | 0 | 4745.7919 | 0 | 3838.0822 | 7250.8387 | 637.9886 | 27842.2501 | 422.8501 | 7163.694 | 92.0961 | 0 | 0 | 0 | 639.7216 | 1112.3333 | 0 | 48999.8548 | 0 | 48999.8548 | 0 | 422.8501 | 0 | 146.9757 | 277.664 | 24.4312 | 1066.1926 | 16.1926 | 274.3269 | 3.5267 | 0 | 0 | 0 | 24.4975 | 42.5957 | 0 | 1876.403 | 0 | 1876.403 | 0 | 16.1926 | 3.7543 | 0.33033 | 14.416 | 3.7092 | 0.047685 | 0 | 1.9873 | 0 | 0.33123 | 0 | 0.57594 | 25.3709 | 25.3709 | 0
WA_4C_PS_2019_NG | 4C | PS | NG |  |  | SchoolPrimary | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 671841.2092 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 115927.5119 | 0 | 0 | 1129959.136 | 0 | 1129959.136 | 0 | 0 | 5155.0376 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 889.5118 | 0 | 0 | 8670.1765 | 0 | 8670.1765 | 0 | 0 | 671.8412 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 115.9275 | 0 | 0 | 1129.9591 | 0 | 1129.9591 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.084 | 1.5675 | 0 | 0 | 15.2782 | 15.2782 | 0
WA_4C_RS_2016_EL | 4C | RS | EL |  |  | RetailStandalone | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 12033.9723 | 85424.2541 | 10753.0531 | 53987.5506 | 0 | 39233.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201432.1916 | 0 | 201427.7459 | 4.4457 | 4.4457 | 0 | 1072.2269 | 7611.301 | 958.097 | 4810.2908 | 0 | 3495.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17947.6083 | 0 | 17947.2122 | 0.39611 | 0.39611 | 0 | 41.0599 | 291.4676 | 36.6894 | 184.2055 | 0 | 133.8642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.2866 | 0 | 687.2715 | 0.015169 | 0.015169 | 11.8041 | 1.4859 | 7.4601 | 5.4214 | 0 | 0 | 1.6629 | 0 | 0 | 0 | 0 | 27.8338 | 27.8344 | 0.00061432
WA_4C_RS_2016_NG | 4C | RS | NG |  |  | RetailStandalone | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 226243.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90156.3645 | 0 | 0 | 316400.311 | 0 | 316400.311 | 0 | 0 | 1735.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.7698 | 0 | 0 | 2427.7396 | 0 | 2427.7396 | 0 | 0 | 226.2439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1564 | 0 | 0 | 316.4003 | 0 | 316.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1626 | 3.6512 | 0 | 0 | 12.8139 | 12.8139 | 0
WA_4C_RS_2019_EL | 4C | RS | EL |  |  | RetailStandalone | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 10836.4101 | 67874.8269 | 10753.0531 | 53987.5506 | 0 | 41197.8082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184649.6489 | 0 | 184649.0932 | 0.55571 | 0.55571 | 0 | 965.5241 | 6047.6471 | 958.097 | 4810.2908 | 0 | 3670.7247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16452.2837 | 0 | 16452.2342 | 0.049514 | 0.049514 | 0 | 36.9738 | 231.5889 | 36.6894 | 184.2055 | 0 | 140.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630.0246 | 0 | 630.0227 | 0.0018961 | 0.0018961 | 9.3791 | 1.4859 | 7.4601 | 5.6928 | 0 | 0 | 1.4974 | 0 | 0 | 0 | 0 | 25.5153 | 25.5153 | 7.679e-05
WA_4C_RS_2019_NG | 4C | RS | NG |  |  | RetailStandalone | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 250830.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90175.3208 | 0 | 0 | 341005.6434 | 0 | 341005.6434 | 0 | 0 | 1924.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.9152 | 0 | 0 | 2616.5363 | 0 | 2616.5363 | 0 | 0 | 250.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1753 | 0 | 0 | 341.0056 | 0 | 341.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1584 | 3.652 | 0 | 0 | 13.8104 | 13.8104 | 0
WA_4C_SH_2016_EL | 4C | SH | EL |  |  | HotelSmall | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 10172.3326 | 53048.3951 | 79867.1207 | 12286.8219 | 154949.5496 | 0 | 55860.3046 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 366256.7672 | 0 | 366257.8787 | -1.1114 | -1.1114 | 906.3548 | 4726.612 | 7116.1605 | 1094.7558 | 13806.0049 | 0 | 4977.1531 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 32633.478 | 0 | 32633.577 | -0.099028 | -0.099028 | 34.708 | 181.0011 | 272.5066 | 41.9226 | 528.6879 | 0 | 190.5954 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.6681 | 0 | 1249.6719 | -0.0037922 | -0.0037922 | 6.3077 | 0.97039 | 12.2376 | 4.4117 | 0.0057056 | 0 | 4.1896 | 0.80339 | 0 | 0 | 0 | 28.9263 | 28.9262 | -8.7778e-05
WA_4C_SH_2016_NG | 4C | SH | NG |  |  | HotelSmall | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 23932.3823 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 584935.8574 | 0 | 0 | 1008363.6776 | 0 | 1008363.6776 | 0 | 0 | 183.6332 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4488.2128 | 0 | 0 | 7737.1745 | 0 | 7737.1745 | 0 | 0 | 23.9324 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 584.9359 | 0 | 0 | 1008.3637 | 0 | 1008.3637 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.55396 | 13.5396 | 0 | 0 | 23.3407 | 23.3407 | 0
WA_4C_SH_2019_EL | 4C | SH | EL |  |  | HotelSmall | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 13181.5203 | 48544.3385 | 51220.0982 | 12286.8219 | 154949.5496 | 0 | 53078.9593 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 333333.5306 | 0 | 333334.0863 | -0.55571 | -0.55571 | 1174.4735 | 4325.3006 | 4563.7108 | 1094.7558 | 13806.0049 | 0 | 4729.3353 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 29700.0176 | 0 | 29700.0671 | -0.049514 | -0.049514 | 44.9753 | 165.6333 | 174.763 | 41.9226 | 528.6879 | 0 | 181.1054 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.334 | 0 | 1137.3359 | -0.0018961 | -0.0018961 | 4.0453 | 0.97039 | 12.2376 | 4.1921 | 0.0057056 | 0 | 3.8339 | 1.041 | 0 | 0 | 0 | 26.326 | 26.326 | -4.3889e-05
WA_4C_SH_2019_NG | 4C | SH | NG |  |  | HotelSmall | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 26737.921 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 584983.2483 | 0 | 0 | 1011216.6072 | 0 | 1011216.6072 | 0 | 0 | 205.1601 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4488.5765 | 0 | 0 | 7759.065 | 0 | 7759.065 | 0 | 0 | 26.7379 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 584.9832 | 0 | 0 | 1011.2166 | 0 | 1011.2166 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.6189 | 13.5407 | 0 | 0 | 23.4067 | 23.4067 | 0
WA_4C_SO_2016_EL | 4C | SO | EL |  |  | OfficeSmall | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 1583.783 | 2153.3892 | 8966.4347 | 1603.233 | 13417.6985 | 0 | 4915.2845 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37644.0214 | 0 | 37641.7986 | 2.2229 | 2.2229 | 141.1151 | 191.867 | 798.9093 | 142.8481 | 1195.5169 | 0 | 437.9518 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3354.0823 | 0 | 3353.8843 | 0.19806 | 0.19806 | 5.4039 | 7.3474 | 30.5935 | 5.4702 | 45.7812 | 0 | 16.771 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 128.4414 | 0 | 128.4338 | 0.0075844 | 0.0075844 | 5.5604 | 0.99423 | 8.3208 | 3.0482 | 0 | 0 | 1.3354 | 0.98216 | 3.1033 | 0 | 0 | 23.3431 | 23.3445 | 0.0013785
WA_4C_SO_2016_NG | 4C | SO | NG |  |  | OfficeSmall | STD2016 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 502.3431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502.3431 | 0 | 502.3431 | 0 | 0 | 3.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8545 | 0 | 3.8545 | 0 | 0 | 0.50234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50234 | 0 | 0.50234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091302 | 0 | 0 | 0 | 0.091302 | 0.091302 | 0
WA_4C_SO_2019_EL | 4C | SO | EL |  |  | OfficeSmall | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 1681.0328 | 1972.7823 | 7215.9377 | 1603.233 | 13417.6985 | 0 | 4492.9423 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 35387.8253 | 0 | 35385.0467 | 2.7786 | 2.7786 | 149.78 | 175.7749 | 642.94 | 142.8481 | 1195.5169 | 0 | 400.3212 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3153.0552 | 0 | 3152.8077 | 0.24757 | 0.24757 | 5.7357 | 6.7311 | 24.6208 | 5.4702 | 45.7812 | 0 | 15.3299 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 120.7433 | 0 | 120.7338 | 0.0094805 | 0.0094805 | 4.4749 | 0.99423 | 8.3208 | 2.7862 | 0 | 0 | 1.2234 | 1.0425 | 3.1033 | 0 | 0 | 21.9436 | 21.9453 | 0.0017231
WA_4C_SO_2019_NG | 4C | SO | NG |  |  | OfficeSmall | STD2019 | WA-SEATTLE-WA | Zone4C | Zone4C(WA-SEATTLE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 587.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.6466 | 0 | 587.6466 | 0 | 0 | 4.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.509 | 0 | 4.509 | 0 | 0 | 0.58765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58765 | 0 | 0.58765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10681 | 0 | 0 | 0 | 0.10681 | 0.10681 | 0
WA_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 405040.001 | 882981.256 | 97180.3697 | 4077910.5986 | 543459.8574 | 650276.2964 | 70986.8216 | 124021.3239 | 593429.6006 | 0 | 0 | 0 | 0 | 7445286.1252 | 0 | 7445284.736 | 1.3893 | 543461.2467 | 0 | 36089.0641 | 78673.6299 | 8658.7709 | 363341.8343 | 48422.2733 | 57939.618 | 6324.9258 | 11050.3 | 52874.5774 | 0 | 0 | 0 | 0 | 663374.9938 | 0 | 663374.87 | 0.12379 | 48422.3971 | 0 | 1381.9965 | 3012.732 | 331.5794 | 13913.831 | 1854.285 | 2218.7427 | 242.207 | 423.1608 | 2024.7818 | 0 | 0 | 0 | 0 | 25403.3163 | 0 | 25403.3115 | 0.0047402 | 1854.2898 | 6.0425 | 0.66504 | 27.9065 | 4.4501 | 0.48579 | 0 | 2.7718 | 0 | 0 | 4.061 | 0 | 50.9505 | 50.9505 | 9.5073e-06
WA_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 2169458.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590120.4171 | 0 | 0 | 2759579.0231 | 0 | 2759579.0231 | 0 | 0 | 16646.2559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4527.994 | 0 | 0 | 21174.2498 | 0 | 21174.2498 | 0 | 0 | 2169.4586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.1204 | 0 | 0 | 2759.579 | 0 | 2759.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3512 | 1.1836 | 0 | 0 | 5.5348 | 5.5348 | 0
WA_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 380280.1933 | 718854.1007 | 97180.3697 | 4077910.5986 | 543387.6147 | 625085.8108 | 68338.8476 | 110478.5899 | 593915.8498 | 0 | 0 | 0 | 0 | 7215431.975 | 0 | 7215433.6422 | -1.6671 | 543385.9475 | 0 | 33882.9652 | 64049.9004 | 8658.7709 | 363341.8343 | 48415.8365 | 55695.1457 | 6088.9913 | 9843.6424 | 52917.9022 | 0 | 0 | 0 | 0 | 642894.989 | 0 | 642895.1375 | -0.14854 | 48415.6879 | 0 | 1297.516 | 2452.7302 | 331.5794 | 13913.831 | 1854.0385 | 2132.7928 | 233.1721 | 376.9529 | 2026.4409 | 0 | 0 | 0 | 0 | 24619.0539 | 0 | 24619.0596 | -0.0056883 | 1854.0329 | 4.9194 | 0.66504 | 27.9065 | 4.2777 | 0.46766 | 0 | 2.6024 | 0 | 0 | 4.0644 | 0 | 49.3776 | 49.3775 | -1.1409e-05
WA_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 3149292.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590120.4171 | 0 | 0 | 3739413.4054 | 0 | 3739413.4054 | 0 | 0 | 24164.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4527.994 | 0 | 0 | 28692.5191 | 0 | 28692.5191 | 0 | 0 | 3149.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.1204 | 0 | 0 | 3739.4134 | 0 | 3739.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3164 | 1.1836 | 0 | 0 | 7.5 | 7.5 | 0
WA_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 15484.9521 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 21775.6271 | 0 | 0 | 0 | 0 | 118447.5191 | 0 | 0 | 333283.5164 | 0 | 333281.0157 | 2.5007 | 2.5007 | 0 | 1379.7092 | 2528.1878 | 641.2071 | 12652.5749 | 0 | 1940.2084 | 0 | 0 | 0 | 0 | 10553.674 | 0 | 0 | 29695.5613 | 0 | 29695.3385 | 0.22281 | 0.22281 | 0 | 52.8347 | 96.8146 | 24.5544 | 484.5184 | 0 | 74.2984 | 0 | 0 | 0 | 0 | 404.1429 | 0 | 0 | 1137.1634 | 0 | 1137.1548 | 0.0085324 | 0.0085324 | 2.8693 | 0.72773 | 14.3599 | 2.202 | 0 | 0 | 1.5659 | 0 | 11.9778 | 0 | 0 | 33.7025 | 33.7027 | 0.00025288
WA_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 306685.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306685.1855 | 0 | 306685.1855 | 0 | 0 | 2353.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2353.1954 | 0 | 2353.1954 | 0 | 0 | 306.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306.6852 | 0 | 306.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0894 | 0 | 0 | 0 | 9.0894 | 9.0894 | 0
WA_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 18327.4258 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 20461.365 | 0 | 0 | 0 | 0 | 118294.6979 | 0 | 0 | 329465.7658 | 0 | 329466.8772 | -1.1114 | -1.1114 | 0 | 1632.9736 | 2065.4789 | 641.2071 | 12652.5749 | 0 | 1823.1076 | 0 | 0 | 0 | 0 | 10540.0576 | 0 | 0 | 29355.3997 | 0 | 29355.4988 | -0.099028 | -0.099028 | 0 | 62.5332 | 79.0956 | 24.5544 | 484.5184 | 0 | 69.8142 | 0 | 0 | 0 | 0 | 403.6215 | 0 | 0 | 1124.1372 | 0 | 1124.141 | -0.0037922 | -0.0037922 | 2.3442 | 0.72773 | 14.3599 | 2.0691 | 0 | 0 | 1.8533 | 0 | 11.9623 | 0 | 0 | 33.3168 | 33.3167 | -0.00011239
WA_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 136523.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136523.578 | 0 | 136523.578 | 0 | 0 | 1047.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047.5454 | 0 | 1047.5454 | 0 | 0 | 136.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.5236 | 0 | 136.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0462 | 0 | 0 | 0 | 4.0462 | 4.0462 | 0
WA_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 57655.2587 | 98997.5523 | 7188.152 | 317887.4784 | 4818.0346 | 99189.2734 | 1547.6616 | 0 | 0 | 0 | 7179.8163 | 17546.6486 | 0 | 612009.876 | 0 | 612010.9875 | -1.1114 | 4816.9232 | 0 | 5137.0835 | 8820.6819 | 640.4643 | 28323.7743 | 429.2869 | 8837.7643 | 137.8967 | 0 | 0 | 0 | 639.7216 | 1563.4064 | 0 | 54530.08 | 0 | 54530.179 | -0.099028 | 429.1879 | 0 | 196.7197 | 337.7796 | 24.526 | 1084.6321 | 16.4391 | 338.4338 | 5.2806 | 0 | 0 | 0 | 24.4975 | 59.8692 | 0 | 2088.1777 | 0 | 2088.1815 | -0.0037922 | 16.4353 | 4.5671 | 0.33162 | 14.6653 | 4.576 | 0.071399 | 0 | 2.6598 | 0 | 0.33123 | 0 | 0.80949 | 28.2343 | 28.2343 | -5.1274e-05
WA_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 1016846.6408 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122818.1424 | 0 | 0 | 1481855.1981 | 0 | 1481855.1981 | 0 | 0 | 7802.2643 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 942.3836 | 0 | 0 | 11370.2749 | 0 | 11370.2749 | 0 | 0 | 1016.8466 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8181 | 0 | 0 | 1481.8552 | 0 | 1481.8552 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 13.7488 | 1.6606 | 0 | 0 | 20.0362 | 20.0362 | 0
WA_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 54471.0212 | 80653.4551 | 7188.152 | 312483.1662 | 4745.7919 | 80014.3848 | 1797.7326 | 0 | 0 | 0 | 7179.8163 | 12456.3144 | 0 | 560989.8346 | 0 | 560991.5017 | -1.6671 | 4744.1248 | 0 | 4853.368 | 7186.2228 | 640.4643 | 27842.2501 | 422.8501 | 7129.2817 | 160.178 | 0 | 0 | 0 | 639.7216 | 1109.8576 | 0 | 49984.1943 | 0 | 49984.3428 | -0.14854 | 422.7015 | 0 | 185.8551 | 275.1896 | 24.526 | 1066.1926 | 16.1926 | 273.0091 | 6.1339 | 0 | 0 | 0 | 24.4975 | 42.5009 | 0 | 1914.0973 | 0 | 1914.103 | -0.0056883 | 16.187 | 3.7208 | 0.33162 | 14.416 | 3.6914 | 0.082936 | 0 | 2.5129 | 0 | 0.33123 | 0 | 0.57466 | 25.8806 | 25.8805 | -7.6911e-05
WA_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 1204703.994 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 122552.7536 | 0 | 0 | 1669447.1625 | 0 | 1669447.1625 | 0 | 0 | 9243.6937 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 940.3473 | 0 | 0 | 12809.6681 | 0 | 12809.6681 | 0 | 0 | 1204.704 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 122.5528 | 0 | 0 | 1669.4472 | 0 | 1669.4472 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 16.2888 | 1.657 | 0 | 0 | 22.5726 | 22.5726 | 0
WA_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 18627.511 | 86027.2031 | 10822.5172 | 53987.5506 | 0 | 46846.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216311.4162 | 0 | 216310.8605 | 0.55571 | 0.55571 | 0 | 1659.7112 | 7665.0238 | 964.2863 | 4810.2908 | 0 | 4174.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19273.3472 | 0 | 19273.2977 | 0.049514 | 0.049514 | 0 | 63.5571 | 293.5248 | 36.9264 | 184.2055 | 0 | 159.8407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 738.0546 | 0 | 738.0527 | 0.0018961 | 0.0018961 | 11.8874 | 1.4955 | 7.4601 | 6.4734 | 0 | 0 | 2.574 | 0 | 0 | 0 | 0 | 29.8904 | 29.8904 | 7.679e-05
WA_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 441066.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91862.4353 | 0 | 0 | 532929.1321 | 0 | 532929.1321 | 0 | 0 | 3384.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704.8605 | 0 | 0 | 4089.1652 | 0 | 4089.1652 | 0 | 0 | 441.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8624 | 0 | 0 | 532.9291 | 0 | 532.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8627 | 3.7203 | 0 | 0 | 21.5831 | 21.5831 | 0
WA_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 17057.6209 | 68341.6261 | 10822.5172 | 53987.5506 | 0 | 44640.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194849.7672 | 0 | 194847.2665 | 2.5007 | 2.5007 | 0 | 1519.834 | 6089.2389 | 964.2863 | 4810.2908 | 0 | 3977.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17361.1143 | 0 | 17360.8914 | 0.22281 | 0.22281 | 0 | 58.2006 | 233.1816 | 36.9264 | 184.2055 | 0 | 152.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664.8274 | 0 | 664.8189 | 0.0085324 | 0.0085324 | 9.4436 | 1.4955 | 7.4601 | 6.1685 | 0 | 0 | 2.3571 | 0 | 0 | 0 | 0 | 26.9245 | 26.9248 | 0.00034555
WA_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 473718.9966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91881.3916 | 0 | 0 | 565600.3882 | 0 | 565600.3882 | 0 | 0 | 3634.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.0059 | 0 | 0 | 4339.8518 | 0 | 4339.8518 | 0 | 0 | 473.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8814 | 0 | 0 | 565.6004 | 0 | 565.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1851 | 3.7211 | 0 | 0 | 22.9062 | 22.9062 | 0
WA_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 27874.581 | 50261.4927 | 79467.0071 | 12289.6004 | 154949.5496 | 0 | 51400.7051 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 376315.1786 | 0 | 376313.5115 | 1.6671 | 1.6671 | 2483.6252 | 4478.299 | 7080.5103 | 1095.0034 | 13806.0049 | 0 | 4579.8028 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 33529.6824 | 0 | 33529.5339 | 0.14854 | 0.14854 | 95.1081 | 171.4922 | 271.1414 | 41.9321 | 528.6879 | 0 | 175.3792 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.9874 | 0 | 1283.9817 | 0.0056883 | 0.0056883 | 6.2761 | 0.97061 | 12.2376 | 4.0595 | 0.0057056 | 0 | 3.9695 | 2.2015 | 0 | 0 | 0 | 29.7204 | 29.7206 | 0.00013167
WA_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 57399.8048 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 618194.7602 | 0 | 0 | 1075090.0029 | 0 | 1075090.0029 | 0 | 0 | 440.4287 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4743.4084 | 0 | 0 | 8249.1656 | 0 | 8249.1656 | 0 | 0 | 57.3998 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 618.1948 | 0 | 0 | 1075.09 | 0 | 1075.09 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3286 | 14.3094 | 0 | 0 | 24.8852 | 24.8852 | 0
WA_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 32678.7228 | 46343.7137 | 50978.3629 | 12289.6004 | 154949.5496 | 0 | 48510.9957 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 345823.1879 | 0 | 345823.4657 | -0.27786 | -0.27786 | 2911.6742 | 4129.2249 | 4542.1721 | 1095.0034 | 13806.0049 | 0 | 4322.3297 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 30812.846 | 0 | 30812.8708 | -0.024757 | -0.024757 | 111.4998 | 158.1248 | 173.9382 | 41.9321 | 528.6879 | 0 | 165.5195 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.9487 | 0 | 1179.9497 | -0.00094805 | -0.00094805 | 4.0262 | 0.97061 | 12.2376 | 3.8313 | 0.0057056 | 0 | 3.6601 | 2.5809 | 0 | 0 | 0 | 27.3124 | 27.3124 | -2.1945e-05
WA_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 57835.8007 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 618242.151 | 0 | 0 | 1075573.3896 | 0 | 1075573.3896 | 0 | 0 | 443.7741 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4743.772 | 0 | 0 | 8252.8746 | 0 | 8252.8746 | 0 | 0 | 57.8358 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 618.2422 | 0 | 0 | 1075.5734 | 0 | 1075.5734 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.3387 | 14.3105 | 0 | 0 | 24.8964 | 24.8964 | 0
WA_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 4412.3639 | 2589.6241 | 8885.8563 | 1603.233 | 13417.6985 | 0 | 5345.9623 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41258.9367 | 0 | 41254.491 | 4.4457 | 4.4457 | 393.1416 | 230.7355 | 791.7298 | 142.8481 | 1195.5169 | 0 | 476.3252 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3676.1713 | 0 | 3675.7751 | 0.39611 | 0.39611 | 15.055 | 8.8358 | 30.3185 | 5.4702 | 45.7812 | 0 | 18.2404 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.7755 | 0 | 140.7603 | 0.015169 | 0.015169 | 5.5105 | 0.99423 | 8.3208 | 3.3152 | 0 | 0 | 1.6059 | 2.7363 | 3.1033 | 0 | 0 | 25.5835 | 25.5862 | 0.002757
WA_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 4445.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4445.2623 | 0 | 4445.2623 | 0 | 0 | 34.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.1085 | 0 | 34.1085 | 0 | 0 | 4.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4453 | 0 | 4.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80794 | 0 | 0 | 0 | 0.80794 | 0.80794 | 0
WA_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 4476.2709 | 2411.7959 | 7154.8092 | 1603.233 | 13417.6985 | 0 | 4901.3916 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38969.3977 | 0 | 38967.1749 | 2.2229 | 2.2229 | 398.8357 | 214.891 | 637.4935 | 142.8481 | 1195.5169 | 0 | 436.714 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3472.1733 | 0 | 3471.9753 | 0.19806 | 0.19806 | 15.273 | 8.229 | 24.4122 | 5.4702 | 45.7812 | 0 | 16.7235 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 132.9636 | 0 | 132.956 | 0.0075844 | 0.0075844 | 4.437 | 0.99423 | 8.3208 | 3.0395 | 0 | 0 | 1.4956 | 2.7759 | 3.1033 | 0 | 0 | 24.165 | 24.1664 | 0.0013785
WA_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | WA-SPOKANE-WA | Zone5B | Zone5B(WA-SPOKANE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 4994.9962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4994.9962 | 0 | 4994.9962 | 0 | 0 | 38.3266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.3266 | 0 | 38.3266 | 0 | 0 | 4.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.995 | 0 | 4.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90785 | 0 | 0 | 0 | 0.90785 | 0.90785 | 0
WA_5C_LO_2016_EL | 5C | LO | EL |  |  | OfficeLarge | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 221037.7582 | 885504.1946 | 97044.2199 | 4077910.5986 | 543459.8574 | 574615.9256 | 51000.5915 | 75126.886 | 233744.1436 | 0 | 0 | 0 | 0 | 6759444.1753 | 0 | 6759444.1753 | 0 | 543459.8574 | 0 | 19694.4643 | 78898.4237 | 8646.64 | 363341.8343 | 48422.2733 | 51198.279 | 4544.1527 | 6693.8055 | 20826.6032 | 0 | 0 | 0 | 0 | 602266.476 | 0 | 602266.476 | 0 | 48422.2733 | 0 | 754.1808 | 3021.3403 | 331.1149 | 13913.831 | 1854.285 | 1960.5895 | 174.014 | 256.3329 | 797.535 | 0 | 0 | 0 | 0 | 23063.2235 | 0 | 23063.2235 | 0 | 1854.285 | 6.0598 | 0.66411 | 27.9065 | 3.9323 | 0.34901 | 0 | 1.5126 | 0 | 0 | 1.5996 | 0 | 46.2571 | 46.2571 | 0
WA_5C_LO_2016_NG | 5C | LO | NG |  |  | OfficeLarge | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 860940.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579665.9942 | 0 | 0 | 1440606.197 | 0 | 1440606.197 | 0 | 0 | 6605.9942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4447.7772 | 0 | 0 | 11053.7713 | 0 | 11053.7713 | 0 | 0 | 860.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.666 | 0 | 0 | 1440.6062 | 0 | 1440.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7268 | 1.1626 | 0 | 0 | 2.8894 | 2.8894 | 0
WA_5C_LO_2019_EL | 5C | LO | EL |  |  | OfficeLarge | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 207117.1391 | 720018.3201 | 97044.2199 | 4077910.5986 | 543387.6147 | 545454.8683 | 49063.9305 | 66944.0071 | 233566.3153 | 0 | 0 | 0 | 0 | 6540507.0136 | 0 | 6540507.8472 | -0.83357 | 543386.7811 | 0 | 18454.1371 | 64153.6323 | 8646.64 | 363341.8343 | 48415.8365 | 48600.0288 | 4371.5962 | 5964.711 | 20810.7587 | 0 | 0 | 0 | 0 | 582759.1749 | 0 | 582759.2492 | -0.074271 | 48415.7622 | 0 | 706.6837 | 2456.7025 | 331.1149 | 13913.831 | 1854.0385 | 1861.092 | 167.4061 | 228.413 | 796.9283 | 0 | 0 | 0 | 0 | 22316.2099 | 0 | 22316.2128 | -0.0028441 | 1854.0357 | 4.9273 | 0.66411 | 27.9065 | 3.7327 | 0.33576 | 0 | 1.4174 | 0 | 0 | 1.5984 | 0 | 44.7588 | 44.7588 | -5.7044e-06
WA_5C_LO_2019_NG | 5C | LO | NG |  |  | OfficeLarge | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 1814207.2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579684.9506 | 0 | 0 | 2393892.2218 | 0 | 2393892.2218 | 0 | 0 | 13920.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4447.9226 | 0 | 0 | 18368.335 | 0 | 18368.335 | 0 | 0 | 1814.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.685 | 0 | 0 | 2393.8922 | 0 | 2393.8922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6387 | 1.1627 | 0 | 0 | 4.8013 | 4.8013 | 0
WA_5C_MA_2016_EL | 5C | MA | EL |  |  | ApartmentMidRise | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 8935.8705 | 28374.723 | 7196.4877 | 142004.2074 | 0 | 16557.4789 | 0 | 0 | 0 | 0 | 116355.2584 | 0 | 0 | 319424.0258 | 0 | 319425.1372 | -1.1114 | -1.1114 | 0 | 796.1861 | 2528.1878 | 641.2071 | 12652.5749 | 0 | 1475.2714 | 0 | 0 | 0 | 0 | 10367.2535 | 0 | 0 | 28460.6807 | 0 | 28460.7797 | -0.099028 | -0.099028 | 0 | 30.4892 | 96.8146 | 24.5544 | 484.5184 | 0 | 56.4941 | 0 | 0 | 0 | 0 | 397.0041 | 0 | 0 | 1089.8748 | 0 | 1089.8786 | -0.0037922 | -0.0037922 | 2.8693 | 0.72773 | 14.3599 | 1.6743 | 0 | 0 | 0.90362 | 0 | 11.7662 | 0 | 0 | 32.3013 | 32.3012 | -0.00011239
WA_5C_MA_2016_NG | 5C | MA | NG |  |  | ApartmentMidRise | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 128618.7832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128618.7832 | 0 | 128618.7832 | 0 | 0 | 986.8919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 986.8919 | 0 | 986.8919 | 0 | 0 | 128.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.6188 | 0 | 128.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8119 | 0 | 0 | 0 | 3.8119 | 3.8119 | 0
WA_5C_MA_2019_EL | 5C | MA | EL |  |  | ApartmentMidRise | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 14920.9031 | 23181.5818 | 7196.4877 | 142004.2074 | 0 | 17346.5918 | 0 | 0 | 0 | 0 | 116116.3017 | 0 | 0 | 320766.0735 | 0 | 320765.2399 | 0.83357 | 0.83357 | 0 | 1329.4525 | 2065.4789 | 641.2071 | 12652.5749 | 0 | 1545.5813 | 0 | 0 | 0 | 0 | 10345.9625 | 0 | 0 | 28580.2572 | 0 | 28580.1829 | 0.074271 | 0.074271 | 0 | 50.9101 | 79.0956 | 24.5544 | 484.5184 | 0 | 59.1866 | 0 | 0 | 0 | 0 | 396.1888 | 0 | 0 | 1094.4538 | 0 | 1094.451 | 0.0028441 | 0.0028441 | 2.3442 | 0.72773 | 14.3599 | 1.7541 | 0 | 0 | 1.5089 | 0 | 11.7421 | 0 | 0 | 32.4368 | 32.4369 | 8.4293e-05
WA_5C_MA_2019_NG | 5C | MA | NG |  |  | ApartmentMidRise | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 34083.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34083.5036 | 0 | 34083.5036 | 0 | 0 | 261.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.5227 | 0 | 261.5227 | 0 | 0 | 34.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0835 | 0 | 34.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0102 | 0 | 0 | 0 | 1.0102 | 1.0102 | 0
WA_5C_PS_2016_EL | 5C | PS | EL |  |  | SchoolPrimary | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 27163.2679 | 99870.0223 | 7157.5878 | 317887.4784 | 4818.0346 | 83737.6641 | 794.6701 | 0 | 0 | 14695.8392 | 7179.8163 | 17632.7842 | 0 | 580937.1648 | 0 | 580940.2212 | -3.0564 | 4814.9782 | 0 | 2420.2472 | 8898.419 | 637.7411 | 28323.7743 | 429.2869 | 7461.0259 | 70.8051 | 0 | 0 | 1309.3993 | 639.7216 | 1571.0811 | 0 | 51761.5014 | 0 | 51761.7737 | -0.27233 | 429.0146 | 0 | 92.6811 | 340.7565 | 24.4217 | 1084.6321 | 16.4391 | 285.7129 | 2.7114 | 0 | 0 | 50.1422 | 24.4975 | 60.1631 | 0 | 1982.1576 | 0 | 1982.168 | -0.010429 | 16.4287 | 4.6074 | 0.33021 | 14.6653 | 3.8631 | 0.036661 | 0.67797 | 1.2531 | 0 | 0.33123 | 0 | 0.81347 | 26.8009 | 26.8008 | -0.000141
WA_5C_PS_2016_NG | 5C | PS | NG |  |  | SchoolPrimary | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 384946.4451 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119424.9571 | 0 | 0 | 846561.8171 | 0 | 846561.8171 | 0 | 0 | 2953.6941 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 916.3477 | 0 | 0 | 6495.6688 | 0 | 6495.6688 | 0 | 0 | 384.9464 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.425 | 0 | 0 | 846.5618 | 0 | 846.5618 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.2049 | 1.6147 | 0 | 0 | 11.4464 | 11.4464 | 0
WA_5C_PS_2019_EL | 5C | PS | EL |  |  | SchoolPrimary | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 25762.8703 | 80981.326 | 7157.5878 | 312483.1662 | 4745.7919 | 77038.5398 | 547.3776 | 0 | 0 | 20322.4367 | 7179.8163 | 12500.7715 | 0 | 548719.6841 | 0 | 548720.2399 | -0.55571 | 4745.2362 | 0 | 2295.4717 | 7215.4361 | 637.7411 | 27842.2501 | 422.8501 | 6864.1339 | 48.7713 | 0 | 0 | 1810.7291 | 639.7216 | 1113.8187 | 0 | 48890.9239 | 0 | 48890.9734 | -0.049514 | 422.8005 | 0 | 87.9029 | 276.3083 | 24.4217 | 1066.1926 | 16.1926 | 262.8555 | 1.8677 | 0 | 0 | 69.3402 | 24.4975 | 42.6526 | 0 | 1872.2316 | 0 | 1872.2335 | -0.0018961 | 16.1907 | 3.736 | 0.33021 | 14.416 | 3.5541 | 0.025253 | 0.93755 | 1.1885 | 0 | 0.33123 | 0 | 0.57671 | 25.3145 | 25.3145 | -2.5637e-05
WA_5C_PS_2019_NG | 5C | PS | NG |  |  | SchoolPrimary | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 355573.5926 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 119064.7866 | 0 | 0 | 816828.794 | 0 | 816828.794 | 0 | 0 | 2728.3162 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 913.5841 | 0 | 0 | 6267.5273 | 0 | 6267.5273 | 0 | 0 | 355.5736 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 119.0648 | 0 | 0 | 816.8288 | 0 | 816.8288 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.8077 | 1.6099 | 0 | 0 | 11.0443 | 11.0443 | 0
WA_5C_RS_2016_EL | 5C | RS | EL |  |  | RetailStandalone | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 5081.9985 | 85871.6033 | 10733.6031 | 53987.5506 | 0 | 41970.2497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197645.0053 | 0 | 197644.1717 | 0.83357 | 0.83357 | 0 | 452.8061 | 7651.1599 | 956.364 | 4810.2908 | 0 | 3739.5493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17610.17 | 0 | 17610.0957 | 0.074271 | 0.074271 | 0 | 17.3398 | 292.9939 | 36.6231 | 184.2055 | 0 | 143.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.3648 | 0 | 674.3619 | 0.0028441 | 0.0028441 | 11.8659 | 1.4832 | 7.4601 | 5.7996 | 0 | 0 | 0.70224 | 0 | 0 | 0 | 0 | 27.3109 | 27.3111 | 0.00011518
WA_5C_RS_2016_NG | 5C | RS | NG |  |  | RetailStandalone | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 236802.6293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91236.876 | 0 | 0 | 328039.5052 | 0 | 328039.5052 | 0 | 0 | 1816.9866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.0605 | 0 | 0 | 2517.0471 | 0 | 2517.0471 | 0 | 0 | 236.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2369 | 0 | 0 | 328.0395 | 0 | 328.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5903 | 3.695 | 0 | 0 | 13.2853 | 13.2853 | 0
WA_5C_RS_2019_EL | 5C | RS | EL |  |  | RetailStandalone | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 4073.3788 | 68224.9263 | 10733.6031 | 53987.5506 | 0 | 40125.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177144.7403 | 0 | 177143.0731 | 1.6671 | 1.6671 | 0 | 362.938 | 6078.8409 | 956.364 | 4810.2908 | 0 | 3575.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15783.5964 | 0 | 15783.4478 | 0.14854 | 0.14854 | 0 | 13.8984 | 232.7834 | 36.6231 | 184.2055 | 0 | 136.9075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.4179 | 0 | 604.4122 | 0.0056883 | 0.0056883 | 9.4275 | 1.4832 | 7.4601 | 5.5446 | 0 | 0 | 0.56287 | 0 | 0 | 0 | 0 | 24.4781 | 24.4783 | 0.00023037
WA_5C_RS_2019_NG | 5C | RS | NG |  |  | RetailStandalone | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 270715.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91255.8323 | 0 | 0 | 361971.3581 | 0 | 361971.3581 | 0 | 0 | 2077.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.206 | 0 | 0 | 2777.4062 | 0 | 2777.4062 | 0 | 0 | 270.7155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2558 | 0 | 0 | 361.9714 | 0 | 361.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9637 | 3.6958 | 0 | 0 | 14.6595 | 14.6595 | 0
WA_5C_SH_2016_EL | 5C | SH | EL |  |  | HotelSmall | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 9358.2126 | 48886.1022 | 79828.2208 | 12292.379 | 154949.5496 | 0 | 55068.4131 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360455.12 | 0 | 360455.12 | 0 | 0 | 833.8167 | 4355.7517 | 7112.6945 | 1095.251 | 13806.0049 | 0 | 4906.5956 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 32116.5512 | 0 | 32116.5512 | 0 | 0 | 31.9302 | 166.7994 | 272.3739 | 41.9416 | 528.6879 | 0 | 187.8934 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.8729 | 0 | 1229.8729 | 0 | 0 | 6.3047 | 0.97083 | 12.2376 | 4.3492 | 0.0057056 | 0 | 3.8609 | 0.73909 | 0 | 0 | 0 | 28.468 | 28.468 | 0
WA_5C_SH_2016_NG | 5C | SH | NG |  |  | HotelSmall | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 27098.0915 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605835.2249 | 0 | 0 | 1032428.7543 | 0 | 1032428.7543 | 0 | 0 | 207.9237 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4648.5737 | 0 | 0 | 7921.8258 | 0 | 7921.8258 | 0 | 0 | 27.0981 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.8352 | 0 | 0 | 1032.4288 | 0 | 1032.4288 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.62724 | 14.0233 | 0 | 0 | 23.8977 | 23.8977 | 0
WA_5C_SH_2019_EL | 5C | SH | EL |  |  | HotelSmall | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 12523 | 44359.8171 | 51192.3126 | 12292.379 | 154949.5496 | 0 | 52331.5249 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 327720.8259 | 0 | 327721.1038 | -0.27786 | -0.27786 | 1115.7993 | 3952.4597 | 4561.235 | 1095.251 | 13806.0049 | 0 | 4662.7389 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 29199.9256 | 0 | 29199.9503 | -0.024757 | -0.024757 | 42.7285 | 151.3557 | 174.6682 | 41.9416 | 528.6879 | 0 | 178.5552 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.1835 | 0 | 1118.1844 | -0.00094805 | -0.00094805 | 4.0431 | 0.97083 | 12.2376 | 4.133 | 0.0057056 | 0 | 3.5034 | 0.98904 | 0 | 0 | 0 | 25.8827 | 25.8827 | -2.1945e-05
WA_5C_SH_2019_NG | 5C | SH | NG |  |  | HotelSmall | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 31240.0523 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605882.6158 | 0 | 0 | 1036618.106 | 0 | 1036618.106 | 0 | 0 | 239.7049 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4648.9373 | 0 | 0 | 7953.9707 | 0 | 7953.9707 | 0 | 0 | 31.2401 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.8826 | 0 | 0 | 1036.6181 | 0 | 1036.6181 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 0.72312 | 14.0244 | 0 | 0 | 23.9947 | 23.9947 | 0
WA_5C_SO_2016_EL | 5C | SO | EL |  |  | OfficeSmall | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 1706.0399 | 1455.9689 | 8960.8776 | 1606.0115 | 13417.6985 | 0 | 4684.6634 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 36835.4585 | 0 | 36837.4035 | -1.945 | -1.945 | 152.0082 | 129.7268 | 798.4142 | 143.0956 | 1195.5169 | 0 | 417.4035 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3282.0394 | 0 | 3282.2127 | -0.1733 | -0.1733 | 5.821 | 4.9678 | 30.5745 | 5.4797 | 45.7812 | 0 | 15.9841 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 125.6826 | 0 | 125.6892 | -0.0066363 | -0.0066363 | 5.557 | 0.99595 | 8.3208 | 2.9051 | 0 | 0 | 0.9029 | 1.058 | 3.1033 | 0 | 0 | 22.8443 | 22.8431 | -0.0012062
WA_5C_SO_2016_NG | 5C | SO | NG |  |  | OfficeSmall | STD2016 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 464.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464.4304 | 0 | 464.4304 | 0 | 0 | 3.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5636 | 0 | 3.5636 | 0 | 0 | 0.46443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46443 | 0 | 0.46443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084411 | 0 | 0 | 0 | 0.084411 | 0.084411 | 0
WA_5C_SO_2019_EL | 5C | SO | EL |  |  | OfficeSmall | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 1819.9612 | 1300.3692 | 7210.3805 | 1606.0115 | 13417.6985 | 0 | 4265.0999 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 34623.7194 | 0 | 34621.7744 | 1.945 | 1.945 | 162.1585 | 115.8629 | 642.4449 | 143.0956 | 1195.5169 | 0 | 380.0204 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3084.9734 | 0 | 3084.8001 | 0.1733 | 0.1733 | 6.2097 | 4.4369 | 24.6018 | 5.4797 | 45.7812 | 0 | 14.5525 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 118.1361 | 0 | 118.1295 | 0.0066363 | 0.0066363 | 4.4714 | 0.99595 | 8.3208 | 2.645 | 0 | 0 | 0.80641 | 1.1286 | 3.1033 | 0 | 0 | 21.4703 | 21.4715 | 0.0012062
WA_5C_SO_2019_NG | 5C | SO | NG |  |  | OfficeSmall | STD2019 | WA-QUILLAYUTE-WA | Zone5C | Zone5C(WA-QUILLAYUTE-WA) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 568.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.6903 | 0 | 568.6903 | 0 | 0 | 4.3636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3636 | 0 | 4.3636 | 0 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56869 | 0 | 0.56869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10336 | 0 | 0 | 0 | 0.10336 | 0.10336 | 0
WA_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 392180.7944 | 881903.1722 | 97297.0695 | 4077910.5986 | 543459.8574 | 670195.8409 | 68186.0264 | 107352.7023 | 554098.9892 | 0 | 0 | 0 | 0 | 7392585.051 | 0 | 7392581.4388 | 3.6121 | 543463.4695 | 0 | 34943.3088 | 78577.5726 | 8669.1689 | 363341.8343 | 48422.2733 | 59714.4494 | 6075.375 | 9565.1258 | 49370.2199 | 0 | 0 | 0 | 0 | 658679.328 | 0 | 658679.0062 | 0.32184 | 48422.5951 | 0 | 1338.1209 | 3009.0536 | 331.9776 | 13913.831 | 1854.285 | 2286.7082 | 232.6507 | 366.2874 | 1890.5858 | 0 | 0 | 0 | 0 | 25223.5002 | 0 | 25223.4879 | 0.012325 | 1854.2974 | 6.0352 | 0.66584 | 27.9065 | 4.5864 | 0.46662 | 0 | 2.6838 | 0 | 0 | 3.7919 | 0 | 50.5898 | 50.5899 | 2.4719e-05
WA_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 2538131.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614346.6227 | 0 | 0 | 3152477.6538 | 0 | 3152477.6538 | 0 | 0 | 19475.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4713.8816 | 0 | 0 | 24188.961 | 0 | 24188.961 | 0 | 0 | 2538.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614.3466 | 0 | 0 | 3152.4777 | 0 | 3152.4777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0906 | 1.2322 | 0 | 0 | 6.3228 | 6.3228 | 0
WA_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 361205.333 | 718073.3234 | 97297.0695 | 4077910.5986 | 543387.6147 | 642037.8462 | 66013.1872 | 95596.5867 | 553918.3824 | 0 | 0 | 0 | 0 | 7155439.9418 | 0 | 7155437.1632 | 2.7786 | 543390.3932 | 0 | 32183.3952 | 63980.3331 | 8669.1689 | 363341.8343 | 48415.8365 | 57205.5721 | 5881.775 | 8517.6559 | 49354.1279 | 0 | 0 | 0 | 0 | 637549.6988 | 0 | 637549.4512 | 0.24757 | 48416.084 | 0 | 1232.4326 | 2450.0662 | 331.9776 | 13913.831 | 1854.0385 | 2190.6331 | 225.237 | 326.1756 | 1889.9695 | 0 | 0 | 0 | 0 | 24414.3611 | 0 | 24414.3516 | 0.0094805 | 1854.048 | 4.914 | 0.66584 | 27.9065 | 4.3937 | 0.45175 | 0 | 2.4718 | 0 | 0 | 3.7906 | 0 | 48.967 | 48.967 | 1.9015e-05
WA_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 3667682.6057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614289.7536 | 0 | 0 | 4281972.3594 | 0 | 4281972.3594 | 0 | 0 | 28142.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4713.4453 | 0 | 0 | 32855.5739 | 0 | 32855.5739 | 0 | 0 | 3667.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614.2898 | 0 | 0 | 4281.9724 | 0 | 4281.9724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3561 | 1.2321 | 0 | 0 | 8.5882 | 8.5882 | 0
WA_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 18641.4039 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 20697.5432 | 0 | 0 | 0 | 0 | 122951.5757 | 0 | 0 | 339868.7195 | 0 | 339866.7745 | 1.945 | 1.945 | 0 | 1660.9491 | 2528.1878 | 641.4546 | 12652.5749 | 0 | 1844.1511 | 0 | 0 | 0 | 0 | 10954.9854 | 0 | 0 | 30282.3029 | 0 | 30282.1296 | 0.1733 | 0.1733 | 0 | 63.6045 | 96.8146 | 24.5639 | 484.5184 | 0 | 70.62 | 0 | 0 | 0 | 0 | 419.5108 | 0 | 0 | 1159.6321 | 0 | 1159.6254 | 0.0066363 | 0.0066363 | 2.8693 | 0.72801 | 14.3599 | 2.093 | 0 | 0 | 1.8851 | 0 | 12.4333 | 0 | 0 | 34.3684 | 34.3686 | 0.00019668
WA_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 138210.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138210.6924 | 0 | 138210.6924 | 0 | 0 | 1060.4906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.4906 | 0 | 1060.4906 | 0 | 0 | 138.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.2107 | 0 | 138.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0962 | 0 | 0 | 0 | 4.0962 | 4.0962 | 0
WA_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 17768.9339 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 19669.4735 | 0 | 0 | 0 | 0 | 122937.6829 | 0 | 0 | 332761.1459 | 0 | 332762.813 | -1.6671 | -1.6671 | 0 | 1583.212 | 2065.4789 | 641.4546 | 12652.5749 | 0 | 1752.5501 | 0 | 0 | 0 | 0 | 10953.7475 | 0 | 0 | 29649.0181 | 0 | 29649.1666 | -0.14854 | -0.14854 | 0 | 60.6276 | 79.0956 | 24.5639 | 484.5184 | 0 | 67.1122 | 0 | 0 | 0 | 0 | 419.4634 | 0 | 0 | 1135.381 | 0 | 1135.3867 | -0.0056883 | -0.0056883 | 2.3442 | 0.72801 | 14.3599 | 1.989 | 0 | 0 | 1.7969 | 0 | 12.4319 | 0 | 0 | 33.6501 | 33.6499 | -0.00016859
WA_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 130419.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130419.6357 | 0 | 130419.6357 | 0 | 0 | 1000.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.7099 | 0 | 1000.7099 | 0 | 0 | 130.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4196 | 0 | 130.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8653 | 0 | 0 | 0 | 3.8653 | 3.8653 | 0
WA_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 45832.4574 | 96852.4988 | 7152.0306 | 317887.4784 | 4818.0346 | 97030.3271 | 1303.1478 | 0 | 0 | 23137.1248 | 7179.8163 | 17566.0986 | 0 | 618759.0145 | 0 | 618759.2924 | -0.27786 | 4817.7568 | 0 | 4083.672 | 8629.5576 | 637.2459 | 28323.7743 | 429.2869 | 8645.4021 | 116.1105 | 0 | 0 | 2061.5178 | 639.7216 | 1565.1394 | 0 | 55131.4282 | 0 | 55131.4529 | -0.024757 | 429.2621 | 0 | 156.3803 | 330.4607 | 24.4027 | 1084.6321 | 16.4391 | 331.0675 | 4.4463 | 0 | 0 | 78.9439 | 24.4975 | 59.9355 | 0 | 2111.2058 | 0 | 2111.2067 | -0.00094805 | 16.4382 | 4.4682 | 0.32995 | 14.6653 | 4.4764 | 0.060119 | 1.0674 | 2.1144 | 0 | 0.33123 | 0 | 0.81039 | 28.5456 | 28.5456 | -1.2819e-05
WA_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 567533.9351 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127471.9245 | 0 | 0 | 1037196.2744 | 0 | 1037196.2744 | 0 | 0 | 4354.6879 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 978.0921 | 0 | 0 | 7958.407 | 0 | 7958.407 | 0 | 0 | 567.5339 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.4719 | 0 | 0 | 1037.1963 | 0 | 1037.1963 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.6736 | 1.7235 | 0 | 0 | 14.0239 | 14.0239 | 0
WA_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 42273.1135 | 78994.6508 | 7152.0306 | 312483.1662 | 4745.7919 | 80503.4125 | 989.1697 | 0 | 0 | 20430.8008 | 7179.8163 | 12464.6501 | 0 | 567216.6025 | 0 | 567217.1583 | -0.55571 | 4745.2362 | 0 | 3766.5344 | 7038.4234 | 637.2459 | 27842.2501 | 422.8501 | 7172.8541 | 88.135 | 0 | 0 | 1820.3844 | 639.7216 | 1110.6003 | 0 | 50538.9993 | 0 | 50539.0488 | -0.049514 | 422.8005 | 0 | 144.2359 | 269.5297 | 24.4027 | 1066.1926 | 16.1926 | 274.6776 | 3.375 | 0 | 0 | 69.7099 | 24.4975 | 42.5294 | 0 | 1935.343 | 0 | 1935.3449 | -0.0018961 | 16.1907 | 3.6443 | 0.32995 | 14.416 | 3.7139 | 0.045634 | 0.94255 | 1.9502 | 0 | 0.33123 | 0 | 0.57504 | 26.1678 | 26.1678 | -2.5637e-05
WA_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 689489.5639 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 127197.0575 | 0 | 0 | 1158877.0363 | 0 | 1158877.0363 | 0 | 0 | 5290.4534 | 0 | 0 | 0 | 2625.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 975.983 | 0 | 0 | 8892.0635 | 0 | 8892.0635 | 0 | 0 | 689.4896 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 127.1971 | 0 | 0 | 1158.877 | 0 | 1158.877 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3226 | 1.7198 | 0 | 0 | 15.6692 | 15.6692 | 0
WA_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 16488.0147 | 91000.8374 | 10689.146 | 53987.5506 | 0 | 46671.5846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218837.1333 | 0 | 218838.8005 | -1.6671 | -1.6671 | 0 | 1469.0821 | 8108.1746 | 952.4029 | 4810.2908 | 0 | 4158.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19498.3886 | 0 | 19498.5371 | -0.14854 | -0.14854 | 0 | 56.2571 | 310.4949 | 36.4714 | 184.2055 | 0 | 159.2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.6723 | 0 | 746.678 | -0.0056883 | -0.0056883 | 12.5747 | 1.4771 | 7.4601 | 6.4492 | 0 | 0 | 2.2784 | 0 | 0 | 0 | 0 | 30.2397 | 30.2394 | -0.00023037
WA_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 521204.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93265.2046 | 0 | 0 | 614469.8389 | 0 | 614469.8389 | 0 | 0 | 3999.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 715.6239 | 0 | 0 | 4714.8271 | 0 | 4714.8271 | 0 | 0 | 521.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2652 | 0 | 0 | 614.4698 | 0 | 614.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.1082 | 3.7771 | 0 | 0 | 24.8854 | 24.8854 | 0
WA_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 0 | 14720.8463 | 75299.1571 | 10689.146 | 53987.5506 | 0 | 48302.6032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202999.3032 | 0 | 202997.3583 | 1.945 | 1.945 | 0 | 1311.6274 | 6709.1549 | 952.4029 | 4810.2908 | 0 | 4303.7619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18087.2379 | 0 | 18087.0646 | 0.1733 | 0.1733 | 0 | 50.2275 | 256.9207 | 36.4714 | 184.2055 | 0 | 164.8085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 692.6336 | 0 | 692.627 | 0.0066363 | 0.0066363 | 10.405 | 1.4771 | 7.4601 | 6.6746 | 0 | 0 | 2.0342 | 0 | 0 | 0 | 0 | 28.0507 | 28.0509 | 0.00026876
WA_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 547677.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93284.161 | 0 | 0 | 640961.3274 | 0 | 640961.3274 | 0 | 0 | 4202.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 715.7694 | 0 | 0 | 4918.0963 | 0 | 4918.0963 | 0 | 0 | 547.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2842 | 0 | 0 | 640.9613 | 0 | 640.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1803 | 3.7779 | 0 | 0 | 25.9583 | 25.9583 | 0
WA_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 31547.8461 | 48166.4534 | 79375.3144 | 12292.379 | 154949.5496 | 0 | 51247.8839 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 377651.6692 | 0 | 377652.2249 | -0.55571 | -0.55571 | 2810.9131 | 4291.631 | 7072.3405 | 1095.251 | 13806.0049 | 0 | 4566.1865 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 33648.7637 | 0 | 33648.8132 | -0.049514 | -0.049514 | 107.6413 | 164.3439 | 270.8286 | 41.9416 | 528.6879 | 0 | 174.8578 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1288.5475 | 0 | 1288.5494 | -0.0018961 | -0.0018961 | 6.2689 | 0.97083 | 12.2376 | 4.0474 | 0.0057056 | 0 | 3.8041 | 2.4916 | 0 | 0 | 0 | 29.8262 | 29.8261 | -4.3889e-05
WA_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 73436.8705 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 645671.9785 | 0 | 0 | 1118604.2869 | 0 | 1118604.2869 | 0 | 0 | 563.4811 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.2411 | 0 | 0 | 8583.0507 | 0 | 8583.0507 | 0 | 0 | 73.4369 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 645.672 | 0 | 0 | 1118.6043 | 0 | 1118.6043 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6998 | 14.9454 | 0 | 0 | 25.8924 | 25.8924 | 0
WA_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 36860.4656 | 43965.2606 | 51000.5915 | 12292.379 | 154949.5496 | 0 | 48288.7104 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 347429.1994 | 0 | 347430.5887 | -1.3893 | -1.3893 | 3284.2675 | 3917.3047 | 4544.1527 | 1095.251 | 13806.0049 | 0 | 4302.5241 | 6.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 30955.9417 | 0 | 30956.0655 | -0.12379 | -0.12379 | 125.7679 | 150.0095 | 174.014 | 41.9416 | 528.6879 | 0 | 164.7611 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.4284 | 0 | 1185.4332 | -0.0047402 | -0.0047402 | 4.0279 | 0.97083 | 12.2376 | 3.8137 | 0.0057056 | 0 | 3.4723 | 2.9112 | 0 | 0 | 0 | 27.4393 | 27.4392 | -0.00010972
WA_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 73199.9162 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 645728.8475 | 0 | 0 | 1118424.2016 | 0 | 1118424.2016 | 0 | 0 | 561.663 | 0 | 0 | 0 | 3065.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.6774 | 0 | 0 | 8581.6689 | 0 | 8581.6689 | 0 | 0 | 73.1999 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 645.7288 | 0 | 0 | 1118.4242 | 0 | 1118.4242 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6944 | 14.9467 | 0 | 0 | 25.8883 | 25.8883 | 0
WA_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 5251.491 | 2197.8462 | 8855.292 | 1614.3472 | 13417.6985 | 0 | 5315.3981 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41656.2717 | 0 | 41654.6046 | 1.6671 | 1.6671 | 467.9079 | 195.8281 | 789.0065 | 143.8383 | 1195.5169 | 0 | 473.602 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3711.5738 | 0 | 3711.4253 | 0.14854 | 0.14854 | 17.9181 | 7.4991 | 30.2143 | 5.5082 | 45.7812 | 0 | 18.1361 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.1312 | 0 | 142.1255 | 0.0056883 | 0.0056883 | 5.4915 | 1.0011 | 8.3208 | 3.2963 | 0 | 0 | 1.363 | 3.2566 | 3.1033 | 0 | 0 | 25.8316 | 25.8326 | 0.0010339
WA_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 10084.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10084.7742 | 0 | 10084.7742 | 0 | 0 | 77.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3805 | 0 | 77.3805 | 0 | 0 | 10.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0848 | 0 | 10.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 0 | 0 | 0 | 1.8329 | 1.8329 | 0
WA_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Electricity | 5329.2909 | 1961.6681 | 7152.0306 | 1614.3472 | 13417.6985 | 0 | 4795.8061 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39275.0401 | 0 | 39275.0401 | 0 | 0 | 474.8398 | 174.7846 | 637.2459 | 143.8383 | 1195.5169 | 0 | 427.3063 | 0 | 0 | 0 | 0 | 445.8741 | 0 | 0 | 3499.4061 | 0 | 3499.4061 | 0 | 0 | 18.1835 | 6.6932 | 24.4027 | 5.5082 | 45.7812 | 0 | 16.3633 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 134.0064 | 0 | 134.0064 | 0 | 0 | 4.4352 | 1.0011 | 8.3208 | 2.9741 | 0 | 0 | 1.2165 | 3.3049 | 3.1033 | 0 | 0 | 24.3559 | 24.3559 | 0
WA_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | WA-KALISPELL-MT | Zone6B | Zone6B(WA-KALISPELL-MT) |  |  | WA | 0.0891 | 0.007673 |  |  |  | Natural Gas | 11421.1963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11421.1963 | 0 | 11421.1963 | 0 | 0 | 87.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6348 | 0 | 87.6348 | 0 | 0 | 11.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4212 | 0 | 11.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0758 | 0 | 0 | 0 | 2.0758 | 2.0758 | 0
WI_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 528194.4121 | 881608.6441 | 96057.8288 | 4077910.5986 | 543457.0788 | 583410.0892 | 83771.0069 | 175599.8572 | 407471.2468 | 12097.8793 | 0 | 0 | 0 | 7389578.6418 | 0 | 7389575.5854 | 3.0564 | 543460.1353 | 0 | 58365.4825 | 97417.7552 | 10614.3901 | 450609.1211 | 60052.0072 | 64466.8149 | 9256.6963 | 19403.7842 | 45025.5728 | 1336.8157 | 0 | 0 | 0 | 816548.4399 | 0 | 816548.1022 | 0.33773 | 60052.3449 | 0 | 1802.1993 | 3008.0487 | 327.7493 | 13913.831 | 1854.2756 | 1990.5952 | 285.8267 | 599.1467 | 1390.2919 | 41.278 | 0 | 0 | 0 | 25213.2423 | 0 | 25213.2319 | 0.010429 | 1854.286 | 6.0331 | 0.65735 | 27.9065 | 3.9925 | 0.57327 | 0.08279 | 3.6146 | 0 | 0 | 2.7885 | 0 | 50.5693 | 50.5693 | 2.0916e-05
WI_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 1581802.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597229.0455 | 0 | 0 | 2179031.5589 | 0 | 2179031.5589 | 0 | 0 | 9897.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.8621 | 0 | 0 | 13634.2005 | 0 | 13634.2005 | 0 | 0 | 1581.8025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597.229 | 0 | 0 | 2179.0316 | 0 | 2179.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1726 | 1.1978 | 0 | 0 | 4.3704 | 4.3704 | 0
WI_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 494240.3272 | 717856.5952 | 96057.8288 | 4077910.5986 | 543387.6147 | 565955.1333 | 79397.5429 | 157817.0304 | 407401.7827 | 11069.8097 | 0 | 0 | 0 | 7151094.2635 | 0 | 7151090.6513 | 3.6121 | 543391.2268 | 0 | 54613.5562 | 79323.1538 | 10614.3901 | 450609.1211 | 60044.3314 | 62538.0422 | 8773.4285 | 17438.7819 | 45017.897 | 1223.214 | 0 | 0 | 0 | 790195.9161 | 0 | 790195.517 | 0.39914 | 60044.7306 | 0 | 1686.348 | 2449.3267 | 327.7493 | 13913.831 | 1854.0385 | 1931.0389 | 270.9044 | 538.4717 | 1390.0549 | 37.7702 | 0 | 0 | 0 | 24399.5336 | 0 | 24399.5213 | 0.012325 | 1854.0509 | 4.9125 | 0.65735 | 27.9065 | 3.873 | 0.54334 | 0.075754 | 3.3822 | 0 | 0 | 2.788 | 0 | 48.9372 | 48.9373 | 2.4719e-05
WI_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 1525814.9561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597238.5237 | 0 | 0 | 2123053.4798 | 0 | 2123053.4798 | 0 | 0 | 9547.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.9214 | 0 | 0 | 13283.9456 | 0 | 13283.9456 | 0 | 0 | 1525.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597.2385 | 0 | 0 | 2123.0535 | 0 | 2123.0535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0603 | 1.1979 | 0 | 0 | 4.2581 | 4.2581 | 0
WI_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 20494.7078 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 19983.4516 | 0 | 0 | 0 | 0 | 119672.867 | 0 | 0 | 337729.2231 | 0 | 337730.8903 | -1.6671 | -1.6671 | 0 | 2264.6652 | 3135.4069 | 795.5189 | 15691.4649 | 0 | 2208.1714 | 0 | 0 | 0 | 0 | 13223.8518 | 0 | 0 | 37319.0792 | 0 | 37319.2634 | -0.18422 | -0.18422 | 0 | 69.9279 | 96.8146 | 24.5639 | 484.5184 | 0 | 68.1835 | 0 | 0 | 0 | 0 | 408.3238 | 0 | 0 | 1152.3321 | 0 | 1152.3378 | -0.0056883 | -0.0056883 | 2.8693 | 0.72801 | 14.3599 | 2.0208 | 0 | 0 | 2.0725 | 0 | 12.1017 | 0 | 0 | 34.1524 | 34.1523 | -0.00016859
WI_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 216253.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216253.9541 | 0 | 216253.9541 | 0 | 0 | 1353.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1353.101 | 0 | 1353.101 | 0 | 0 | 216.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.254 | 0 | 216.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4092 | 0 | 0 | 0 | 6.4092 | 6.4092 | 0
WI_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 19458.3025 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 19480.531 | 0 | 0 | 0 | 0 | 119703.4312 | 0 | 0 | 331027.3203 | 0 | 331030.0988 | -2.7786 | -2.7786 | 0 | 2150.1424 | 2561.5648 | 795.5189 | 15691.4649 | 0 | 2152.5987 | 0 | 0 | 0 | 0 | 13227.2292 | 0 | 0 | 36578.5189 | 0 | 36578.8259 | -0.30703 | -0.30703 | 0 | 66.3917 | 79.0956 | 24.5639 | 484.5184 | 0 | 66.4676 | 0 | 0 | 0 | 0 | 408.4281 | 0 | 0 | 1129.4652 | 0 | 1129.4747 | -0.0094805 | -0.0094805 | 2.3442 | 0.72801 | 14.3599 | 1.9699 | 0 | 0 | 1.9677 | 0 | 12.1048 | 0 | 0 | 33.4748 | 33.4746 | -0.00028098
WI_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 238717.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238717.2198 | 0 | 238717.2198 | 0 | 0 | 1493.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1493.6536 | 0 | 1493.6536 | 0 | 0 | 238.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238.7172 | 0 | 238.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.075 | 0 | 0 | 0 | 7.075 | 7.075 | 0
WI_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 77319.1751 | 98080.6253 | 7146.4735 | 317887.4784 | 4818.0346 | 95496.5583 | 1141.9909 | 0 | 0 | 17943.9836 | 7179.8163 | 17632.7842 | 0 | 644646.9203 | 0 | 644650.5324 | -3.6121 | 4814.4225 | 0 | 8543.7688 | 10837.9091 | 789.6853 | 35126.5664 | 532.3928 | 10552.3697 | 126.19 | 0 | 0 | 1982.8102 | 793.3697 | 1948.4227 | 0 | 71233.4847 | 0 | 71233.8838 | -0.39914 | 531.9937 | 0 | 263.813 | 334.6511 | 24.3838 | 1084.6321 | 16.4391 | 325.8343 | 3.8965 | 0 | 0 | 61.2249 | 24.4975 | 60.1631 | 0 | 2199.5353 | 0 | 2199.5476 | -0.012325 | 16.4268 | 4.5248 | 0.32969 | 14.6653 | 4.4056 | 0.052684 | 0.82782 | 3.567 | 0 | 0.33123 | 0 | 0.81347 | 29.7401 | 29.7399 | -0.00016664
WI_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 718331.6389 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 124836.9929 | 0 | 0 | 1185359.0466 | 0 | 1185359.0466 | 0 | 0 | 4494.6011 | 0 | 0 | 0 | 2141.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 781.1051 | 0 | 0 | 7416.7916 | 0 | 7416.7916 | 0 | 0 | 718.3316 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 124.837 | 0 | 0 | 1185.359 | 0 | 1185.359 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.7126 | 1.6879 | 0 | 0 | 16.0272 | 16.0272 | 0
WI_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 73201.3392 | 79947.6992 | 7146.4735 | 312483.1662 | 4745.7919 | 81637.0677 | 866.9128 | 0 | 0 | 22784.2468 | 7182.5949 | 12478.543 | 0 | 602473.8352 | 0 | 602474.3909 | -0.55571 | 4745.2362 | 0 | 8088.748 | 8834.2208 | 789.6853 | 34529.3899 | 524.41 | 9020.896 | 95.7939 | 0 | 0 | 2517.6593 | 793.6767 | 1378.879 | 0 | 66573.3588 | 0 | 66573.4202 | -0.061406 | 524.3486 | 0 | 249.763 | 272.7815 | 24.3838 | 1066.1926 | 16.1926 | 278.5457 | 2.9579 | 0 | 0 | 77.7399 | 24.507 | 42.5768 | 0 | 2055.6407 | 0 | 2055.6426 | -0.0018961 | 16.1907 | 3.6883 | 0.32969 | 14.416 | 3.7662 | 0.039994 | 1.0511 | 3.377 | 0 | 0.33136 | 0 | 0.57568 | 27.7944 | 27.7943 | -2.5637e-05
WI_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 691840.1504 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 124524.2132 | 0 | 0 | 1158554.7785 | 0 | 1158554.7785 | 0 | 0 | 4328.8438 | 0 | 0 | 0 | 2141.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 779.148 | 0 | 0 | 7249.0772 | 0 | 7249.0772 | 0 | 0 | 691.8402 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 124.5242 | 0 | 0 | 1158.5548 | 0 | 1158.5548 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 9.3544 | 1.6837 | 0 | 0 | 15.6648 | 15.6648 | 0
WI_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 26493.6333 | 84637.9197 | 10775.2816 | 53987.5506 | 0 | 46346.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222240.8775 | 0 | 222238.3768 | 2.5007 | 2.5007 | 0 | 2927.5465 | 9352.4901 | 1190.6686 | 5965.6243 | 0 | 5121.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24557.617 | 0 | 24557.3406 | 0.27633 | 0.27633 | 0 | 90.3963 | 288.7846 | 36.7653 | 184.2055 | 0 | 158.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.2859 | 0 | 758.2773 | 0.0085324 | 0.0085324 | 11.6955 | 1.489 | 7.4601 | 6.4043 | 0 | 0 | 3.661 | 0 | 0 | 0 | 0 | 30.7094 | 30.7098 | 0.00034555
WI_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 644638.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92288.953 | 0 | 0 | 736927.8108 | 0 | 736927.8108 | 0 | 0 | 4033.5053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.452 | 0 | 0 | 4610.9573 | 0 | 4610.9573 | 0 | 0 | 644.6389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.289 | 0 | 0 | 736.9278 | 0 | 736.9278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1072 | 3.7376 | 0 | 0 | 29.8448 | 29.8448 | 0
WI_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 24473.6153 | 66999.5784 | 10775.2816 | 53987.5506 | 0 | 44473.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200709.7643 | 0 | 200707.2636 | 2.5007 | 2.5007 | 0 | 2704.3345 | 7403.4534 | 1190.6686 | 5965.6243 | 0 | 4914.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22178.429 | 0 | 22178.1526 | 0.27633 | 0.27633 | 0 | 83.504 | 228.6026 | 36.7653 | 184.2055 | 0 | 151.7444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.8217 | 0 | 684.8132 | 0.0085324 | 0.0085324 | 9.2582 | 1.489 | 7.4601 | 6.1455 | 0 | 0 | 3.3818 | 0 | 0 | 0 | 0 | 27.7342 | 27.7346 | 0.00034555
WI_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 678125.2367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92307.9093 | 0 | 0 | 770433.146 | 0 | 770433.146 | 0 | 0 | 4243.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577.5706 | 0 | 0 | 4820.6002 | 0 | 4820.6002 | 0 | 0 | 678.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3079 | 0 | 0 | 770.4331 | 0 | 770.4331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4634 | 3.7384 | 0 | 0 | 31.2017 | 31.2017 | 0
WI_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 51231.2125 | 56507.7106 | 79155.8076 | 12297.9361 | 154949.5496 | 0 | 45568.4936 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 399782.9528 | 0 | 399779.0628 | 3.89 | 3.89 | 5661.049 | 6244.102 | 8746.7167 | 1358.9219 | 17121.9252 | 0 | 5035.3185 | 7.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 44176.0163 | 0 | 44175.5864 | 0.42984 | 0.42984 | 174.8009 | 192.8043 | 270.0796 | 41.9606 | 528.6879 | 0 | 155.4797 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.0594 | 0 | 1364.0462 | 0.013273 | 0.013273 | 6.2516 | 0.97126 | 12.2376 | 3.5989 | 0.0057056 | 0 | 4.4629 | 4.0461 | 0 | 0 | 0 | 31.5737 | 31.574 | 0.00030722
WI_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 113444.2311 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 626554.5072 | 0 | 0 | 1139494.1762 | 0 | 1139494.1762 | 0 | 0 | 709.8206 | 0 | 0 | 0 | 2499.643 | 0 | 0 | 0 | 0 | 0 | 0 | 3920.3516 | 0 | 0 | 7129.8151 | 0 | 7129.8151 | 0 | 0 | 113.4442 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 626.5545 | 0 | 0 | 1139.4942 | 0 | 1139.4942 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.6259 | 14.5029 | 0 | 0 | 26.376 | 26.376 | 0
WI_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 56710.546 | 52523.246 | 50789.4204 | 12297.9361 | 154949.5496 | 0 | 43115.0192 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 370457.9601 | 0 | 370455.4594 | 2.5007 | 2.5007 | 6266.5153 | 5803.8187 | 5612.231 | 1358.9219 | 17121.9252 | 0 | 4764.2096 | 7.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 40935.6046 | 0 | 40935.3283 | 0.27633 | 0.27633 | 193.4964 | 179.2093 | 173.2935 | 41.9606 | 528.6879 | 0 | 147.1084 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0026 | 0 | 1263.994 | 0.0085324 | 0.0085324 | 4.0112 | 0.97126 | 12.2376 | 3.4051 | 0.0057056 | 0 | 4.1482 | 4.4789 | 0 | 0 | 0 | 29.2578 | 29.258 | 0.0001975
WI_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 109359.1393 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 626639.8107 | 0 | 0 | 1135494.3879 | 0 | 1135494.3879 | 0 | 0 | 684.2601 | 0 | 0 | 0 | 2499.643 | 0 | 0 | 0 | 0 | 0 | 0 | 3920.8853 | 0 | 0 | 7104.7884 | 0 | 7104.7884 | 0 | 0 | 109.3591 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 626.6398 | 0 | 0 | 1135.4944 | 0 | 1135.4944 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.5313 | 14.5049 | 0 | 0 | 26.2834 | 26.2834 | 0
WI_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 5248.7125 | 3036.9734 | 8821.9492 | 1586.5616 | 13417.6985 | 0 | 4931.9559 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42048.0496 | 0 | 42044.4375 | 3.6121 | 3.6121 | 579.9827 | 335.5856 | 974.8254 | 175.3151 | 1482.6557 | 0 | 544.9811 | 0 | 0 | 0 | 0 | 552.9639 | 0 | 0 | 4646.3095 | 0 | 4645.9103 | 0.39914 | 0.39914 | 17.9086 | 10.3622 | 30.1005 | 5.4133 | 45.7812 | 0 | 16.8278 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 143.4679 | 0 | 143.4556 | 0.012325 | 0.012325 | 5.4708 | 0.98389 | 8.3208 | 3.0585 | 0 | 0 | 1.8833 | 3.2549 | 3.1033 | 0 | 0 | 26.0734 | 26.0756 | 0.00224
WI_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 15800.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15800.1114 | 0 | 15800.1114 | 0 | 0 | 98.8613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8613 | 0 | 98.8613 | 0 | 0 | 15.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8001 | 0 | 15.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8717 | 0 | 0 | 0 | 2.8717 | 2.8717 | 0
WI_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 5293.1695 | 2859.1451 | 7113.1307 | 1586.5616 | 13417.6985 | 0 | 4523.5066 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39797.4106 | 0 | 39801.0227 | -3.6121 | -3.6121 | 584.8952 | 315.9355 | 786.0009 | 175.3151 | 1482.6557 | 0 | 499.8475 | 0 | 0 | 0 | 0 | 552.9639 | 0 | 0 | 4397.6139 | 0 | 4398.013 | -0.39914 | -0.39914 | 18.0603 | 9.7554 | 24.27 | 5.4133 | 45.7812 | 0 | 15.4342 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.7888 | 0 | 135.8011 | -0.012325 | -0.012325 | 4.4111 | 0.98389 | 8.3208 | 2.8052 | 0 | 0 | 1.7731 | 3.2825 | 3.1033 | 0 | 0 | 24.6821 | 24.6799 | -0.00224
WI_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | WI-MILWAUKEE-WI | Zone5A | Zone5A(WI-MILWAUKEE-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 16387.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16387.758 | 0 | 16387.758 | 0 | 0 | 102.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5382 | 0 | 102.5382 | 0 | 0 | 16.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3878 | 0 | 16.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9785 | 0 | 0 | 0 | 2.9785 | 2.9785 | 0
WI_6A_LO_2016_EL | 6A | LO | EL |  |  | OfficeLarge | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 534790.7294 | 881325.2303 | 96446.8281 | 4077910.5986 | 543457.0788 | 592020.8673 | 84549.0056 | 173902.153 | 429972.0798 | 12750.8425 | 0 | 0 | 0 | 7427125.4134 | 0 | 7427128.7477 | -3.3343 | 543453.7446 | 0 | 59094.3756 | 97386.4379 | 10657.3745 | 450609.1211 | 60052.0072 | 65418.3058 | 9342.6651 | 19216.1879 | 47511.9148 | 1408.9681 | 0 | 0 | 0 | 820697.3582 | 0 | 820697.7266 | -0.36844 | 60051.6388 | 0 | 1824.706 | 3007.0817 | 329.0766 | 13913.831 | 1854.2756 | 2019.9752 | 288.4812 | 593.3541 | 1467.0647 | 43.5059 | 0 | 0 | 0 | 25341.3519 | 0 | 25341.3633 | -0.011377 | 1854.2642 | 6.0312 | 0.66002 | 27.9065 | 4.0514 | 0.5786 | 0.087258 | 3.6597 | 0 | 0 | 2.9424 | 0 | 50.8263 | 50.8262 | -2.2818e-05
WI_6A_LO_2016_NG | 6A | LO | NG |  |  | OfficeLarge | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 1529445.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605579.3143 | 0 | 0 | 2135024.41 | 0 | 2135024.41 | 0 | 0 | 9569.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3789.1098 | 0 | 0 | 13358.8477 | 0 | 13358.8477 | 0 | 0 | 1529.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5793 | 0 | 0 | 2135.0244 | 0 | 2135.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0676 | 1.2146 | 0 | 0 | 4.2821 | 4.2821 | 0
WI_6A_LO_2019_EL | 6A | LO | EL |  |  | OfficeLarge | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 497574.6072 | 717942.7308 | 96446.8281 | 4077910.5986 | 543387.6147 | 569975.7193 | 79341.9716 | 155471.9201 | 429683.1089 | 11214.2951 | 0 | 0 | 0 | 7178949.3945 | 0 | 7178945.2266 | 4.1679 | 543391.7825 | 0 | 54981.9941 | 79332.6718 | 10657.3745 | 450609.1211 | 60044.3314 | 62982.317 | 8767.2879 | 17179.6472 | 47479.9835 | 1239.1796 | 0 | 0 | 0 | 793273.9081 | 0 | 793273.4475 | 0.46055 | 60044.792 | 0 | 1697.7246 | 2449.6206 | 329.0766 | 13913.831 | 1854.0385 | 1944.7572 | 270.7148 | 530.4702 | 1466.0788 | 38.2632 | 0 | 0 | 0 | 24494.5753 | 0 | 24494.5611 | 0.014221 | 1854.0528 | 4.9131 | 0.66002 | 27.9065 | 3.9005 | 0.54296 | 0.076743 | 3.4051 | 0 | 0 | 2.9405 | 0 | 49.1279 | 49.1279 | 2.8522e-05
WI_6A_LO_2019_NG | 6A | LO | NG |  |  | OfficeLarge | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 1510630.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605560.358 | 0 | 0 | 2116191.2838 | 0 | 2116191.2838 | 0 | 0 | 9452.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.9912 | 0 | 0 | 13241.0089 | 0 | 13241.0089 | 0 | 0 | 1510.6309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5604 | 0 | 0 | 2116.1913 | 0 | 2116.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0298 | 1.2146 | 0 | 0 | 4.2444 | 4.2444 | 0
WI_6A_MA_2016_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 22117.3908 | 28374.723 | 7202.0448 | 142004.2074 | 0 | 20525.2721 | 0 | 0 | 0 | 0 | 121234.4215 | 0 | 0 | 341458.0596 | 0 | 341458.8932 | -0.83357 | -0.83357 | 0 | 2443.9717 | 3135.4069 | 795.826 | 15691.4649 | 0 | 2268.0426 | 0 | 0 | 0 | 0 | 13396.4036 | 0 | 0 | 37731.1156 | 0 | 37731.2077 | -0.092109 | -0.092109 | 0 | 75.4645 | 96.8146 | 24.5734 | 484.5184 | 0 | 70.0322 | 0 | 0 | 0 | 0 | 413.6518 | 0 | 0 | 1165.0549 | 0 | 1165.0577 | -0.0028441 | -0.0028441 | 2.8693 | 0.72829 | 14.3599 | 2.0756 | 0 | 0 | 2.2366 | 0 | 12.2596 | 0 | 0 | 34.5294 | 34.5294 | -8.4293e-05
WI_6A_MA_2016_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 204747.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204747.4543 | 0 | 204747.4543 | 0 | 0 | 1281.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1281.1048 | 0 | 1281.1048 | 0 | 0 | 204.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7475 | 0 | 204.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0682 | 0 | 0 | 0 | 6.0682 | 6.0682 | 0
WI_6A_MA_2019_EL | 6A | MA | EL |  |  | ApartmentMidRise | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 20547.5006 | 23181.5818 | 7202.0448 | 142004.2074 | 0 | 19786.1733 | 0 | 0 | 0 | 0 | 121273.3214 | 0 | 0 | 333994.8295 | 0 | 333995.3852 | -0.55571 | -0.55571 | 0 | 2270.4988 | 2561.5648 | 795.826 | 15691.4649 | 0 | 2186.3722 | 0 | 0 | 0 | 0 | 13400.702 | 0 | 0 | 36906.4287 | 0 | 36906.4901 | -0.061406 | -0.061406 | 0 | 70.1081 | 79.0956 | 24.5734 | 484.5184 | 0 | 67.5104 | 0 | 0 | 0 | 0 | 413.7846 | 0 | 0 | 1139.5904 | 0 | 1139.5923 | -0.0018961 | -0.0018961 | 2.3442 | 0.72829 | 14.3599 | 2.0008 | 0 | 0 | 2.0778 | 0 | 12.2636 | 0 | 0 | 33.7747 | 33.7746 | -5.6196e-05
WI_6A_MA_2019_NG | 6A | MA | NG |  |  | ApartmentMidRise | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 232736.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232736.4938 | 0 | 232736.4938 | 0 | 0 | 1456.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1456.2322 | 0 | 1456.2322 | 0 | 0 | 232.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232.7365 | 0 | 232.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8977 | 0 | 0 | 0 | 6.8977 | 6.8977 | 0
WI_6A_PS_2016_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 80909.0832 | 97699.9617 | 7160.3663 | 317887.4784 | 4818.0346 | 96971.9772 | 1278.1407 | 0 | 0 | 19394.3954 | 7179.8163 | 17632.7842 | 0 | 650932.0381 | 0 | 650931.7603 | 0.27786 | 4818.3125 | 0 | 8940.4537 | 10795.8458 | 791.2205 | 35126.5664 | 532.3928 | 10715.4035 | 141.2345 | 0 | 0 | 2143.0807 | 793.3697 | 1948.4227 | 0 | 71927.9902 | 0 | 71927.9595 | 0.030703 | 532.4235 | 0 | 276.0618 | 333.3523 | 24.4312 | 1084.6321 | 16.4391 | 330.8684 | 4.361 | 0 | 0 | 66.1737 | 24.4975 | 60.1631 | 0 | 2220.9801 | 0 | 2220.9792 | 0.00094805 | 16.4401 | 4.5073 | 0.33033 | 14.6653 | 4.4737 | 0.058965 | 0.89473 | 3.7326 | 0 | 0.33123 | 0 | 0.81347 | 30.0299 | 30.0299 | 1.2819e-05
WI_6A_PS_2016_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 754547.7311 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126590.4545 | 0 | 0 | 1223328.6004 | 0 | 1223328.6004 | 0 | 0 | 4721.2052 | 0 | 0 | 0 | 2141.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 792.0765 | 0 | 0 | 7654.3671 | 0 | 7654.3671 | 0 | 0 | 754.5477 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.5905 | 0 | 0 | 1223.3286 | 0 | 1223.3286 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.2022 | 1.7116 | 0 | 0 | 16.5406 | 16.5406 | 0
WI_6A_PS_2019_EL | 6A | PS | EL |  |  | SchoolPrimary | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 75393.6284 | 80036.6133 | 7160.3663 | 312483.1662 | 4745.7919 | 82831.8514 | 930.8198 | 0 | 0 | 22792.5825 | 7182.5949 | 12478.543 | 0 | 606035.9577 | 0 | 606038.1805 | -2.2229 | 4743.569 | 0 | 8330.9959 | 8844.0458 | 791.2205 | 34529.3899 | 524.41 | 9152.9196 | 102.8556 | 0 | 0 | 2518.5804 | 793.6767 | 1378.879 | 0 | 66966.9733 | 0 | 66967.2189 | -0.24563 | 524.1644 | 0 | 257.2431 | 273.0849 | 24.4312 | 1066.1926 | 16.1926 | 282.6223 | 3.176 | 0 | 0 | 77.7683 | 24.507 | 42.5768 | 0 | 2067.7947 | 0 | 2067.8023 | -0.0075844 | 16.1851 | 3.6924 | 0.33033 | 14.416 | 3.8213 | 0.042942 | 1.0515 | 3.4782 | 0 | 0.33136 | 0 | 0.57568 | 27.9588 | 27.9587 | -0.00010255
WI_6A_PS_2019_NG | 6A | PS | NG |  |  | SchoolPrimary | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 741562.6365 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 126353.5003 | 0 | 0 | 1210106.5516 | 0 | 1210106.5516 | 0 | 0 | 4639.9574 | 0 | 0 | 0 | 2141.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 790.5939 | 0 | 0 | 7571.6367 | 0 | 7571.6367 | 0 | 0 | 741.5626 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 126.3535 | 0 | 0 | 1210.1066 | 0 | 1210.1066 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.0267 | 1.7084 | 0 | 0 | 16.3619 | 16.3619 | 0
WI_6A_RS_2016_EL | 6A | RS | EL |  |  | RetailStandalone | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 28160.7733 | 90817.452 | 10789.1744 | 53987.5506 | 0 | 45799.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229554.065 | 0 | 229554.8986 | -0.83357 | -0.83357 | 0 | 3111.7655 | 10035.3284 | 1192.2038 | 5965.6243 | 0 | 5060.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25365.7242 | 0 | 25365.8163 | -0.092109 | -0.092109 | 0 | 96.0846 | 309.8691 | 36.8127 | 184.2055 | 0 | 156.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783.2385 | 0 | 783.2413 | -0.0028441 | -0.0028441 | 12.5494 | 1.4909 | 7.4601 | 6.3286 | 0 | 0 | 3.8913 | 0 | 0 | 0 | 0 | 31.7204 | 31.7203 | -0.00011518
WI_6A_RS_2016_NG | 6A | RS | NG |  |  | RetailStandalone | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 664334.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92762.8615 | 0 | 0 | 757097.3591 | 0 | 757097.3591 | 0 | 0 | 4156.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.4172 | 0 | 0 | 4737.1582 | 0 | 4737.1582 | 0 | 0 | 664.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7629 | 0 | 0 | 757.0974 | 0 | 757.0974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9048 | 3.7568 | 0 | 0 | 30.6616 | 30.6616 | 0
WI_6A_RS_2019_EL | 6A | RS | EL |  |  | RetailStandalone | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 0 | 26085.184 | 75160.2288 | 10789.1744 | 53987.5506 | 0 | 43876.3465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209898.4843 | 0 | 209899.3179 | -0.83357 | -0.83357 | 0 | 2882.4128 | 8305.2053 | 1192.2038 | 5965.6243 | 0 | 4848.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23193.7825 | 0 | 23193.8746 | -0.092109 | -0.092109 | 0 | 89.0026 | 256.4467 | 36.8127 | 184.2055 | 0 | 149.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.1736 | 0 | 716.1765 | -0.0028441 | -0.0028441 | 10.3858 | 1.4909 | 7.4601 | 6.0629 | 0 | 0 | 3.6045 | 0 | 0 | 0 | 0 | 29.0044 | 29.0043 | -0.00011518
WI_6A_RS_2019_NG | 6A | RS | NG |  |  | RetailStandalone | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 695877.8513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92772.3397 | 0 | 0 | 788650.191 | 0 | 788650.191 | 0 | 0 | 4354.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.4765 | 0 | 0 | 4934.5842 | 0 | 4934.5842 | 0 | 0 | 695.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7723 | 0 | 0 | 788.6502 | 0 | 788.6502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1823 | 3.7572 | 0 | 0 | 31.9395 | 31.9395 | 0
WI_6A_SH_2016_EL | 6A | SH | EL |  |  | HotelSmall | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 53826.3938 | 56813.353 | 79100.2363 | 12300.7147 | 154949.5496 | 0 | 45399.001 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 402461.4911 | 0 | 402461.4911 | 0 | 0 | 5947.8165 | 6277.8755 | 8740.5761 | 1359.229 | 17121.9252 | 0 | 5016.5896 | 7.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 44471.9948 | 0 | 44471.9948 | 0 | 0 | 183.6557 | 193.8472 | 269.89 | 41.97 | 528.6879 | 0 | 154.9014 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.1986 | 0 | 1373.1986 | 0 | 0 | 6.2472 | 0.97148 | 12.2376 | 3.5855 | 0.0057056 | 0 | 4.487 | 4.2511 | 0 | 0 | 0 | 31.7855 | 31.7855 | 0
WI_6A_SH_2016_NG | 6A | SH | NG |  |  | HotelSmall | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 122590.6663 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 635738.8551 | 0 | 0 | 1157824.9593 | 0 | 1157824.9593 | 0 | 0 | 767.0498 | 0 | 0 | 0 | 2499.643 | 0 | 0 | 0 | 0 | 0 | 0 | 3977.818 | 0 | 0 | 7244.5108 | 0 | 7244.5108 | 0 | 0 | 122.5907 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 635.7389 | 0 | 0 | 1157.825 | 0 | 1157.825 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.8376 | 14.7155 | 0 | 0 | 26.8003 | 26.8003 | 0
WI_6A_SH_2019_EL | 6A | SH | EL |  |  | HotelSmall | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 59797.5336 | 52542.696 | 50825.5418 | 12300.7147 | 154949.5496 | 0 | 42951.0838 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 373439.3621 | 0 | 373439.64 | -0.27786 | -0.27786 | 6607.6275 | 5805.9679 | 5616.2224 | 1359.229 | 17121.9252 | 0 | 4746.0948 | 7.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 41265.0495 | 0 | 41265.0802 | -0.030703 | -0.030703 | 204.0292 | 179.2757 | 173.4167 | 41.97 | 528.6879 | 0 | 146.5491 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.1751 | 0 | 1274.1761 | -0.00094805 | -0.00094805 | 4.0141 | 0.97148 | 12.2376 | 3.3922 | 0.0057056 | 0 | 4.1497 | 4.7227 | 0 | 0 | 0 | 29.4935 | 29.4934 | -2.1945e-05
WI_6A_SH_2019_NG | 6A | SH | NG |  |  | HotelSmall | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 118135.9258 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 635786.2459 | 0 | 0 | 1153417.6097 | 0 | 1153417.6097 | 0 | 0 | 739.1765 | 0 | 0 | 0 | 2499.643 | 0 | 0 | 0 | 0 | 0 | 0 | 3978.1145 | 0 | 0 | 7216.934 | 0 | 7216.934 | 0 | 0 | 118.1359 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 635.7862 | 0 | 0 | 1153.4176 | 0 | 1153.4176 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 2.7345 | 14.7166 | 0 | 0 | 26.6982 | 26.6982 | 0
WI_6A_SO_2016_EL | 6A | SO | EL |  |  | OfficeSmall | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 5507.1192 | 3117.5518 | 8796.9421 | 1592.1187 | 13417.6985 | 0 | 4904.1702 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 42339.7991 | 0 | 42339.2434 | 0.55571 | 0.55571 | 608.5367 | 344.4895 | 972.0621 | 175.9291 | 1482.6557 | 0 | 541.9108 | 0 | 0 | 0 | 0 | 552.9639 | 0 | 0 | 4678.5478 | 0 | 4678.4864 | 0.061406 | 0.061406 | 18.7903 | 10.6371 | 30.0152 | 5.4323 | 45.7812 | 0 | 16.733 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 144.4634 | 0 | 144.4615 | 0.0018961 | 0.0018961 | 5.4553 | 0.98733 | 8.3208 | 3.0413 | 0 | 0 | 1.9333 | 3.4152 | 3.1033 | 0 | 0 | 26.2562 | 26.2565 | 0.00034462
WI_6A_SO_2016_NG | 6A | SO | NG |  |  | OfficeSmall | STD2016 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 19619.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19619.8144 | 0 | 19619.8144 | 0 | 0 | 122.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.7612 | 0 | 122.7612 | 0 | 0 | 19.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6198 | 0 | 19.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5659 | 0 | 0 | 0 | 3.5659 | 3.5659 | 0
WI_6A_SO_2019_EL | 6A | SO | EL |  |  | OfficeSmall | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Electricity | 5584.919 | 2864.7022 | 7118.6878 | 1592.1187 | 13417.6985 | 0 | 4437.371 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40019.6959 | 0 | 40021.0852 | -1.3893 | -1.3893 | 617.1336 | 316.5496 | 786.615 | 175.9291 | 1482.6557 | 0 | 490.3295 | 0 | 0 | 0 | 0 | 552.9639 | 0 | 0 | 4422.1764 | 0 | 4422.3299 | -0.15352 | -0.15352 | 19.0557 | 9.7744 | 24.289 | 5.4323 | 45.7812 | 0 | 15.1403 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 136.5472 | 0 | 136.5519 | -0.0047402 | -0.0047402 | 4.4146 | 0.98733 | 8.3208 | 2.7518 | 0 | 0 | 1.7765 | 3.4634 | 3.1033 | 0 | 0 | 24.8186 | 24.8177 | -0.00086155
WI_6A_SO_2019_NG | 6A | SO | NG |  |  | OfficeSmall | STD2019 | WI-GREENBAY-WI | Zone6A | Zone6A(WI-GREENBAY-WI) |  |  | WI | 0.1105 | 0.006257 |  |  |  | Natural Gas | 20757.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20757.1949 | 0 | 20757.1949 | 0 | 0 | 129.8778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.8778 | 0 | 129.8778 | 0 | 0 | 20.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7572 | 0 | 20.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7727 | 0 | 0 | 0 | 3.7727 | 3.7727 | 0
WV_4A_LO_2016_EL | 4A | LO | EL |  |  | OfficeLarge | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 725539.3321 | 879627.526 | 95632.7081 | 4077910.5986 | 543457.0788 | 599286.8192 | 99895.0294 | 262091.0809 | 330893.9491 | 13820.5907 | 0 | 0 | 0 | 7628154.7129 | 0 | 7628156.6579 | -1.945 | 543455.1338 | 0 | 68128.1433 | 82597.0247 | 8979.9113 | 382915.8052 | 51030.6197 | 56273.0323 | 9380.1433 | 24610.3525 | 31070.9418 | 1297.7535 | 0 | 0 | 0 | 716283.7275 | 0 | 716283.9102 | -0.18264 | 51030.4371 | 0 | 2475.5402 | 3001.2891 | 326.2988 | 13913.831 | 1854.2756 | 2044.7666 | 340.8418 | 894.2548 | 1129.0102 | 47.1559 | 0 | 0 | 0 | 26027.2639 | 0 | 26027.2705 | -0.0066363 | 1854.2689 | 6.0196 | 0.65445 | 27.9065 | 4.1011 | 0.68361 | 0.094579 | 4.9651 | 0 | 0 | 2.2644 | 0 | 52.202 | 52.2019 | -1.331e-05
WV_4A_LO_2016_NG | 4A | LO | NG |  |  | OfficeLarge | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 668684.9782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545146.4947 | 0 | 0 | 1213831.4729 | 0 | 1213831.4729 | 0 | 0 | 3579.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2918.1692 | 0 | 0 | 6497.6399 | 0 | 6497.6399 | 0 | 0 | 668.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1465 | 0 | 0 | 1213.8315 | 0 | 1213.8315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3412 | 1.0934 | 0 | 0 | 2.4345 | 2.4345 | 0
WV_4A_LO_2019_EL | 4A | LO | EL |  |  | OfficeLarge | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 683827.4891 | 716081.0911 | 95632.7081 | 4077910.5986 | 543384.8361 | 575049.382 | 96591.3136 | 235625.2332 | 330649.4352 | 12359.0646 | 0 | 0 | 0 | 7367111.1516 | 0 | 7367110.8738 | 0.27786 | 543385.114 | 0 | 64211.4012 | 67240.0145 | 8979.9113 | 382915.8052 | 51023.8361 | 53997.137 | 9069.9243 | 22125.2094 | 31047.982 | 1160.5162 | 0 | 0 | 0 | 691771.7371 | 0 | 691771.711 | 0.026091 | 51023.8622 | 0 | 2333.2194 | 2443.2687 | 326.2988 | 13913.831 | 1854.0291 | 1962.0685 | 329.5696 | 803.9533 | 1128.1759 | 42.1691 | 0 | 0 | 0 | 25136.5832 | 0 | 25136.5823 | 0.00094805 | 1854.03 | 4.9004 | 0.65445 | 27.9065 | 3.9353 | 0.66101 | 0.084577 | 4.6797 | 0 | 0 | 2.2627 | 0 | 50.4155 | 50.4155 | 1.9015e-06
WV_4A_LO_2019_NG | 4A | LO | NG |  |  | OfficeLarge | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 640847.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545118.0602 | 0 | 0 | 1185965.6496 | 0 | 1185965.6496 | 0 | 0 | 3430.4571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2918.017 | 0 | 0 | 6348.4741 | 0 | 6348.4741 | 0 | 0 | 640.8476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1181 | 0 | 0 | 1185.9656 | 0 | 1185.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2853 | 1.0933 | 0 | 0 | 2.3786 | 2.3786 | 0
WV_4A_MA_2016_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 31950.7383 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22103.498 | 0 | 0 | 0 | 0 | 109350.4918 | 0 | 0 | 340988.4818 | 0 | 340984.8697 | 3.6121 | 3.6121 | 0 | 3000.1743 | 2664.3865 | 676.5329 | 13334.1951 | 0 | 2075.5185 | 0 | 0 | 0 | 0 | 10268.0112 | 0 | 0 | 32018.8184 | 0 | 32018.4793 | 0.33918 | 0.33918 | 0 | 109.0159 | 96.8146 | 24.5829 | 484.5184 | 0 | 75.4171 | 0 | 0 | 0 | 0 | 373.1039 | 0 | 0 | 1163.4527 | 0 | 1163.4404 | 0.012325 | 0.012325 | 2.8693 | 0.72858 | 14.3599 | 2.2352 | 0 | 0 | 3.231 | 0 | 11.0579 | 0 | 0 | 34.4815 | 34.4819 | 0.00036527
WV_4A_MA_2016_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 67513.0135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67513.0135 | 0 | 67513.0135 | 0 | 0 | 361.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361.3972 | 0 | 361.3972 | 0 | 0 | 67.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.513 | 0 | 67.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0009 | 0 | 0 | 0 | 2.0009 | 2.0009 | 0
WV_4A_MA_2019_EL | 4A | MA | EL |  |  | ApartmentMidRise | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 30969.9042 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21511.6633 | 0 | 0 | 0 | 0 | 109381.056 | 0 | 0 | 334253.2362 | 0 | 334255.1812 | -1.945 | -1.945 | 0 | 2908.074 | 2176.7505 | 676.5329 | 13334.1951 | 0 | 2019.9452 | 0 | 0 | 0 | 0 | 10270.8812 | 0 | 0 | 31386.3789 | 0 | 31386.5615 | -0.18264 | -0.18264 | 0 | 105.6693 | 79.0956 | 24.5829 | 484.5184 | 0 | 73.3978 | 0 | 0 | 0 | 0 | 373.2082 | 0 | 0 | 1140.472 | 0 | 1140.4787 | -0.0066363 | -0.0066363 | 2.3442 | 0.72858 | 14.3599 | 2.1753 | 0 | 0 | 3.1318 | 0 | 11.061 | 0 | 0 | 33.801 | 33.8008 | -0.00019668
WV_4A_MA_2019_NG | 4A | MA | NG |  |  | ApartmentMidRise | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 78081.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78081.1743 | 0 | 78081.1743 | 0 | 0 | 417.9685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.9685 | 0 | 417.9685 | 0 | 0 | 78.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0812 | 0 | 78.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3141 | 0 | 0 | 0 | 2.3141 | 2.3141 | 0
WV_4A_PS_2016_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 125091.072 | 96446.8281 | 7110.3521 | 317887.4784 | 4818.0346 | 92562.3919 | 533.4848 | 0 | 0 | 21308.8279 | 7179.8163 | 17632.7842 | 0 | 690571.0704 | 0 | 690570.5147 | 0.55571 | 4818.5903 | 0 | 11746.0517 | 9056.3572 | 667.6621 | 29849.6342 | 452.4135 | 8691.6086 | 50.0942 | 0 | 0 | 2000.8989 | 674.1848 | 1655.7184 | 0 | 64844.6235 | 0 | 64844.5713 | 0.052181 | 452.4656 | 0 | 426.8107 | 329.0766 | 24.2605 | 1084.6321 | 16.4391 | 315.8229 | 1.8203 | 0 | 0 | 72.7057 | 24.4975 | 60.1631 | 0 | 2356.2285 | 0 | 2356.2266 | 0.0018961 | 16.441 | 4.4494 | 0.32803 | 14.6653 | 4.2702 | 0.024612 | 0.98305 | 5.7709 | 0 | 0.33123 | 0 | 0.81347 | 31.8586 | 31.8586 | 2.5637e-05
WV_4A_PS_2016_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 310343.7596 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114344.6574 | 0 | 0 | 766878.8318 | 0 | 766878.8318 | 0 | 0 | 1661.2701 | 0 | 0 | 0 | 1831.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 612.087 | 0 | 0 | 4105.1024 | 0 | 4105.1024 | 0 | 0 | 310.3438 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.3447 | 0 | 0 | 766.8788 | 0 | 766.8788 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.1962 | 1.5461 | 0 | 0 | 10.369 | 10.369 | 0
WV_4A_PS_2019_EL | 4A | PS | EL |  |  | SchoolPrimary | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 118914.3183 | 78294.452 | 7110.3521 | 312483.1662 | 4743.0133 | 80892.4118 | 394.5565 | 0 | 0 | 22839.8181 | 7179.8163 | 12495.2144 | 0 | 645347.1191 | 0 | 645348.2305 | -1.1114 | 4741.9019 | 0 | 11166.0545 | 7351.849 | 667.6621 | 29342.1693 | 445.369 | 7595.7975 | 37.0489 | 0 | 0 | 2144.6589 | 674.1848 | 1173.3006 | 0 | 60598.0945 | 0 | 60598.1988 | -0.10436 | 445.2646 | 0 | 405.7357 | 267.1407 | 24.2605 | 1066.1926 | 16.1832 | 276.0049 | 1.3462 | 0 | 0 | 77.9295 | 24.4975 | 42.6337 | 0 | 2201.9244 | 0 | 2201.9282 | -0.0037922 | 16.1794 | 3.612 | 0.32803 | 14.416 | 3.7319 | 0.018202 | 1.0537 | 5.486 | 0 | 0.33123 | 0 | 0.57645 | 29.7723 | 29.7722 | -5.1274e-05
WV_4A_PS_2019_NG | 4A | PS | NG |  |  | SchoolPrimary | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 300344.289 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 114079.2686 | 0 | 0 | 756613.9724 | 0 | 756613.9724 | 0 | 0 | 1607.743 | 0 | 0 | 0 | 1831.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 610.6663 | 0 | 0 | 4050.1546 | 0 | 4050.1546 | 0 | 0 | 300.3443 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0793 | 0 | 0 | 756.614 | 0 | 756.614 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 4.061 | 1.5425 | 0 | 0 | 10.2302 | 10.2302 | 0
WV_4A_RS_2016_EL | 4A | RS | EL |  |  | RetailStandalone | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 45137.8158 | 83240.3007 | 10672.4746 | 53987.5506 | 0 | 42245.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235283.4695 | 0 | 235283.7474 | -0.27786 | -0.27786 | 0 | 4238.4409 | 7816.2642 | 1002.1454 | 5069.431 | 0 | 3966.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22093.1178 | 0 | 22093.1439 | -0.026091 | -0.026091 | 0 | 154.0102 | 284.0159 | 36.4145 | 184.2055 | 0 | 144.1411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.7872 | 0 | 802.7881 | -0.00094805 | -0.00094805 | 11.5023 | 1.4747 | 7.4601 | 5.8376 | 0 | 0 | 6.2373 | 0 | 0 | 0 | 0 | 32.5121 | 32.512 | -3.8395e-05
WV_4A_RS_2016_NG | 4A | RS | NG |  |  | RetailStandalone | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 304381.9899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89161.1565 | 0 | 0 | 393543.1464 | 0 | 393543.1464 | 0 | 0 | 1629.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477.2797 | 0 | 0 | 2106.6365 | 0 | 2106.6365 | 0 | 0 | 304.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1612 | 0 | 0 | 393.5431 | 0 | 393.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3272 | 3.6109 | 0 | 0 | 15.9381 | 15.9381 | 0
WV_4A_RS_2019_EL | 4A | RS | EL |  |  | RetailStandalone | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 42353.6919 | 65802.0162 | 10672.4746 | 53987.5506 | 0 | 40300.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213116.0645 | 0 | 213117.7317 | -1.6671 | -1.6671 | 0 | 3977.0117 | 6178.8093 | 1002.1454 | 5069.431 | 0 | 3784.2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20011.5985 | 0 | 20011.755 | -0.15654 | -0.15654 | 0 | 144.5108 | 224.5165 | 36.4145 | 184.2055 | 0 | 137.5047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727.152 | 0 | 727.1577 | -0.0056883 | -0.0056883 | 9.0927 | 1.4747 | 7.4601 | 5.5688 | 0 | 0 | 5.8525 | 0 | 0 | 0 | 0 | 29.4491 | 29.4489 | -0.00023037
WV_4A_RS_2019_NG | 4A | RS | NG |  |  | RetailStandalone | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 327470.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89170.6346 | 0 | 0 | 416641.4496 | 0 | 416641.4496 | 0 | 0 | 1752.9513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477.3304 | 0 | 0 | 2230.2817 | 0 | 2230.2817 | 0 | 0 | 327.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1706 | 0 | 0 | 416.6414 | 0 | 416.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2622 | 3.6113 | 0 | 0 | 16.8735 | 16.8735 | 0
WV_4A_SH_2016_EL | 4A | SH | EL |  |  | HotelSmall | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 21250.478 | 79622.6069 | 79130.8005 | 12303.4933 | 154949.5496 | 0 | 45965.8286 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 393294.9996 | 0 | 393295.5553 | -0.55571 | -0.55571 | 1995.4199 | 7476.5628 | 7430.3822 | 1155.298 | 14549.7627 | 0 | 4316.1913 | 6.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 36930.4005 | 0 | 36930.4526 | -0.052181 | -0.052181 | 72.5066 | 271.6723 | 269.9943 | 41.9795 | 528.6879 | 0 | 156.8354 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.9225 | 0 | 1341.9244 | -0.0018961 | -0.0018961 | 6.2496 | 0.9717 | 12.2376 | 3.6303 | 0.0057056 | 0 | 6.2884 | 1.6783 | 0 | 0 | 0 | 31.0616 | 31.0616 | -4.3889e-05
WV_4A_SH_2016_NG | 4A | SH | NG |  |  | HotelSmall | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 52452.1994 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 566368.1201 | 0 | 0 | 1018315.7574 | 0 | 1018315.7574 | 0 | 0 | 280.7766 | 0 | 0 | 0 | 2138.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 3031.7685 | 0 | 0 | 5451.0442 | 0 | 5451.0442 | 0 | 0 | 52.4522 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 566.3681 | 0 | 0 | 1018.3158 | 0 | 1018.3158 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2141 | 13.1098 | 0 | 0 | 23.571 | 23.571 | 0
WV_4A_SH_2019_EL | 4A | SH | EL |  |  | HotelSmall | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 24320.7942 | 74451.6943 | 50750.5205 | 12303.4933 | 154949.5496 | 0 | 43592.9327 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 360441.2272 | 0 | 360441.7829 | -0.55571 | -0.55571 | 2283.7226 | 6991.0141 | 4765.4739 | 1155.298 | 14549.7627 | 0 | 4093.3764 | 6.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 33845.4312 | 0 | 33845.4834 | -0.052181 | -0.052181 | 82.9825 | 254.0292 | 173.1608 | 41.9795 | 528.6879 | 0 | 148.7391 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.8255 | 0 | 1229.8274 | -0.0018961 | -0.0018961 | 4.0082 | 0.9717 | 12.2376 | 3.4429 | 0.0057056 | 0 | 5.88 | 1.9208 | 0 | 0 | 0 | 28.4669 | 28.4669 | -4.3889e-05
WV_4A_SH_2019_NG | 4A | SH | NG |  |  | HotelSmall | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 52205.767 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 566424.9891 | 0 | 0 | 1018126.194 | 0 | 1018126.194 | 0 | 0 | 279.4575 | 0 | 0 | 0 | 2138.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 3032.073 | 0 | 0 | 5450.0295 | 0 | 5450.0295 | 0 | 0 | 52.2058 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 566.425 | 0 | 0 | 1018.1262 | 0 | 1018.1262 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2084 | 13.1111 | 0 | 0 | 23.5666 | 23.5666 | 0
WV_4A_SO_2016_EL | 4A | SO | EL |  |  | OfficeSmall | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 2253.4176 | 4723.5634 | 8824.7278 | 1586.5616 | 13417.6985 | 0 | 4931.9559 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40742.1233 | 0 | 40740.734 | 1.3893 | 1.3893 | 211.5959 | 443.5426 | 828.6419 | 148.9781 | 1259.9219 | 0 | 463.1107 | 0 | 0 | 0 | 0 | 469.8942 | 0 | 0 | 3825.6854 | 0 | 3825.5549 | 0.13045 | 0.13045 | 7.6887 | 16.1168 | 30.11 | 5.4133 | 45.7812 | 0 | 16.8278 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 139.0121 | 0 | 139.0074 | 0.0047402 | 0.0047402 | 5.4726 | 0.98389 | 8.3208 | 3.0585 | 0 | 0 | 2.9293 | 1.3974 | 3.1033 | 0 | 0 | 25.2649 | 25.2657 | 0.00086155
WV_4A_SO_2016_NG | 4A | SO | NG |  |  | OfficeSmall | STD2016 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 6302.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6302.9838 | 0 | 6302.9838 | 0 | 0 | 33.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.7399 | 0 | 33.7399 | 0 | 0 | 6.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.303 | 0 | 6.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1456 | 0 | 0 | 0 | 1.1456 | 1.1456 | 0
WV_4A_SO_2019_EL | 4A | SO | EL |  |  | OfficeSmall | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 2308.9889 | 4476.2709 | 7107.5736 | 1586.5616 | 13417.6985 | 0 | 4537.3994 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38438.6915 | 0 | 38438.9693 | -0.27786 | -0.27786 | 216.8141 | 420.3218 | 667.4012 | 148.9781 | 1259.9219 | 0 | 426.0618 | 0 | 0 | 0 | 0 | 469.8942 | 0 | 0 | 3609.3931 | 0 | 3609.4192 | -0.026091 | -0.026091 | 7.8783 | 15.273 | 24.251 | 5.4133 | 45.7812 | 0 | 15.4816 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.1528 | 0 | 131.1538 | -0.00094805 | -0.00094805 | 4.4077 | 0.98389 | 8.3208 | 2.8138 | 0 | 0 | 2.7759 | 1.4319 | 3.1033 | 0 | 0 | 23.8375 | 23.8373 | -0.00017231
WV_4A_SO_2019_NG | 4A | SO | NG |  |  | OfficeSmall | STD2019 | WV-CHARLESTON-WV | Zone4A | Zone4A(WV-CHARLESTON-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 6492.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6492.5473 | 0 | 6492.5473 | 0 | 0 | 34.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7546 | 0 | 34.7546 | 0 | 0 | 6.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4925 | 0 | 6.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 0 | 0 | 0 | 1.18 | 1.18 | 0
WV_5A_LO_2016_EL | 5A | LO | EL |  |  | OfficeLarge | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 563840.644 | 880094.3252 | 95513.2297 | 4077910.5986 | 543457.0788 | 609756.4584 | 82692.923 | 189870.5757 | 380669.1926 | 9524.9266 | 0 | 0 | 0 | 7433329.9528 | 0 | 7433329.9528 | 0 | 543457.0788 | 0 | 52944.6365 | 82640.8571 | 8968.6923 | 382915.8052 | 51030.6197 | 57256.1314 | 7764.8655 | 17828.8471 | 35744.8372 | 894.3906 | 0 | 0 | 0 | 697989.6826 | 0 | 697989.6826 | 0 | 51030.6197 | 0 | 1923.8243 | 3002.8818 | 325.8911 | 13913.831 | 1854.2756 | 2080.489 | 282.1483 | 647.8384 | 1298.8433 | 32.499 | 0 | 0 | 0 | 25362.5218 | 0 | 25362.5218 | 0 | 1854.2756 | 6.0228 | 0.65363 | 27.9065 | 4.1728 | 0.56589 | 0.065182 | 3.8585 | 0 | 0 | 2.605 | 0 | 50.8687 | 50.8687 | 0
WV_5A_LO_2016_NG | 5A | LO | NG |  |  | OfficeLarge | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 799227.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579068.8695 | 0 | 0 | 1378296.6996 | 0 | 1378296.6996 | 0 | 0 | 4278.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.7557 | 0 | 0 | 7378.0222 | 0 | 7378.0222 | 0 | 0 | 799.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0689 | 0 | 0 | 1378.2967 | 0 | 1378.2967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.603 | 1.1614 | 0 | 0 | 2.7644 | 2.7644 | 0
WV_5A_LO_2019_EL | 5A | LO | EL |  |  | OfficeLarge | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 529408.6457 | 716478.4262 | 95513.2297 | 4077910.5986 | 543384.8361 | 594107.5709 | 79116.9077 | 170270.5663 | 380402.4502 | 9110.9202 | 0 | 0 | 0 | 7195704.1516 | 0 | 7195710.5423 | -6.3907 | 543378.4454 | 0 | 49711.4718 | 67277.3242 | 8968.6923 | 382915.8052 | 51023.8361 | 55786.7009 | 7429.0776 | 15988.4062 | 35719.7901 | 855.5154 | 0 | 0 | 0 | 675676.6198 | 0 | 675677.2199 | -0.60009 | 51023.236 | 0 | 1806.3423 | 2444.6244 | 325.8911 | 13913.831 | 1854.0291 | 2027.095 | 269.9469 | 580.9632 | 1297.9332 | 31.0865 | 0 | 0 | 0 | 24551.7426 | 0 | 24551.7644 | -0.021805 | 1854.0073 | 4.9031 | 0.65363 | 27.9065 | 4.0657 | 0.54142 | 0.062349 | 3.6229 | 0 | 0 | 2.6032 | 0 | 49.2426 | 49.2425 | -4.3734e-05
WV_5A_LO_2019_NG | 5A | LO | NG |  |  | OfficeLarge | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 766840.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579078.3476 | 0 | 0 | 1345919.2667 | 0 | 1345919.2667 | 0 | 0 | 4104.8994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.8064 | 0 | 0 | 7204.7058 | 0 | 7204.7058 | 0 | 0 | 766.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579.0783 | 0 | 0 | 1345.9193 | 0 | 1345.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.538 | 1.1614 | 0 | 0 | 2.6995 | 2.6995 | 0
WV_5A_MA_2016_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 23145.4605 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 20250.194 | 0 | 0 | 0 | 0 | 116005.159 | 0 | 0 | 336984.5672 | 0 | 336983.178 | 1.3893 | 1.3893 | 0 | 2173.3587 | 2664.3865 | 676.5329 | 13334.1951 | 0 | 1901.4932 | 0 | 0 | 0 | 0 | 10892.8844 | 0 | 0 | 31642.8509 | 0 | 31642.7204 | 0.13045 | 0.13045 | 0 | 78.9723 | 96.8146 | 24.5829 | 484.5184 | 0 | 69.0937 | 0 | 0 | 0 | 0 | 395.8096 | 0 | 0 | 1149.7913 | 0 | 1149.7866 | 0.0047402 | 0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.0478 | 0 | 0 | 2.3405 | 0 | 11.7308 | 0 | 0 | 34.0768 | 34.077 | 0.00014049
WV_5A_MA_2016_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 82128.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82128.3534 | 0 | 82128.3534 | 0 | 0 | 439.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.6331 | 0 | 439.6331 | 0 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1284 | 0 | 82.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4341 | 0 | 0 | 0 | 2.4341 | 2.4341 | 0
WV_5A_MA_2019_EL | 5A | MA | EL |  |  | ApartmentMidRise | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 21825.6413 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 19552.7737 | 0 | 0 | 0 | 0 | 116044.0589 | 0 | 0 | 329813.0866 | 0 | 329817.5323 | -4.4457 | -4.4457 | 0 | 2049.4277 | 2176.7505 | 676.5329 | 13334.1951 | 0 | 1836.0055 | 0 | 0 | 0 | 0 | 10896.5371 | 0 | 0 | 30969.4488 | 0 | 30969.8663 | -0.41745 | -0.41745 | 0 | 74.4691 | 79.0956 | 24.5829 | 484.5184 | 0 | 66.7141 | 0 | 0 | 0 | 0 | 395.9423 | 0 | 0 | 1125.3223 | 0 | 1125.3374 | -0.015169 | -0.015169 | 2.3442 | 0.72858 | 14.3599 | 1.9772 | 0 | 0 | 2.2071 | 0 | 11.7348 | 0 | 0 | 33.3522 | 33.3518 | -0.00044956
WV_5A_MA_2019_NG | 5A | MA | NG |  |  | ApartmentMidRise | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 95151.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95151.3607 | 0 | 95151.3607 | 0 | 0 | 509.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509.3452 | 0 | 509.3452 | 0 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1514 | 0 | 95.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8201 | 0 | 0 | 0 | 2.8201 | 2.8201 | 0
WV_5A_PS_2016_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 85226.9758 | 96613.5421 | 7107.5736 | 317887.4784 | 4818.0346 | 87894.3999 | 708.5345 | 0 | 0 | 19688.9235 | 7179.8163 | 17630.0056 | 0 | 644755.2844 | 0 | 644755.0065 | 0.27786 | 4818.3125 | 0 | 8002.813 | 9072.0116 | 667.4012 | 29849.6342 | 452.4135 | 8253.2841 | 66.5314 | 0 | 0 | 1848.7899 | 674.1848 | 1655.4575 | 0 | 60542.5212 | 0 | 60542.4951 | 0.026091 | 452.4395 | 0 | 290.7944 | 329.6454 | 24.251 | 1084.6321 | 16.4391 | 299.8957 | 2.4175 | 0 | 0 | 67.1786 | 24.4975 | 60.1536 | 0 | 2199.905 | 0 | 2199.9041 | 0.00094805 | 16.4401 | 4.4571 | 0.3279 | 14.6653 | 4.0549 | 0.032687 | 0.90832 | 3.9318 | 0 | 0.33123 | 0 | 0.81334 | 29.7449 | 29.7449 | 1.2819e-05
WV_5A_PS_2016_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 400642.2966 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120742.4229 | 0 | 0 | 863575.1344 | 0 | 863575.1344 | 0 | 0 | 2144.6382 | 0 | 0 | 0 | 1831.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 646.3342 | 0 | 0 | 4622.7177 | 0 | 4622.7177 | 0 | 0 | 400.6423 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7424 | 0 | 0 | 863.5751 | 0 | 863.5751 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.4171 | 1.6326 | 0 | 0 | 11.6764 | 11.6764 | 0
WV_5A_PS_2019_EL | 5A | PS | EL |  |  | SchoolPrimary | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 80445.0626 | 78544.523 | 7107.5736 | 312483.1662 | 4743.0133 | 75635.3637 | 489.0277 | 0 | 0 | 22461.9331 | 7179.8163 | 12495.2144 | 0 | 601584.6938 | 0 | 601589.1395 | -4.4457 | 4738.5676 | 0 | 7553.7914 | 7375.3307 | 667.4012 | 29342.1693 | 445.369 | 7102.1606 | 45.9197 | 0 | 0 | 2109.1755 | 674.1848 | 1173.3006 | 0 | 56488.8028 | 0 | 56489.2202 | -0.41745 | 444.9515 | 0 | 274.4786 | 267.9939 | 24.251 | 1066.1926 | 16.1832 | 258.0679 | 1.6686 | 0 | 0 | 76.6401 | 24.4975 | 42.6337 | 0 | 2052.607 | 0 | 2052.6221 | -0.015169 | 16.168 | 3.6235 | 0.3279 | 14.416 | 3.4893 | 0.022561 | 1.0363 | 3.7112 | 0 | 0.33123 | 0 | 0.57645 | 27.7535 | 27.7533 | -0.0002051
WV_5A_PS_2019_NG | 5A | PS | NG |  |  | SchoolPrimary | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 380747.6153 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 120505.4686 | 0 | 0 | 843443.4987 | 0 | 843443.4987 | 0 | 0 | 2038.142 | 0 | 0 | 0 | 1831.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 645.0658 | 0 | 0 | 4514.953 | 0 | 4514.953 | 0 | 0 | 380.7476 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5055 | 0 | 0 | 843.4435 | 0 | 843.4435 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 5.1481 | 1.6294 | 0 | 0 | 11.4042 | 11.4042 | 0
WV_5A_RS_2016_EL | 5A | RS | EL |  |  | RetailStandalone | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 27982.9451 | 83498.7074 | 10680.8103 | 53987.5506 | 0 | 42720.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218870.4761 | 0 | 218871.0319 | -0.55571 | -0.55571 | 0 | 2627.5985 | 7840.5286 | 1002.9281 | 5069.431 | 0 | 4011.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20551.9377 | 0 | 20551.9899 | -0.052181 | -0.052181 | 0 | 95.4778 | 284.8976 | 36.4429 | 184.2055 | 0 | 145.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.7861 | 0 | 746.788 | -0.0018961 | -0.0018961 | 11.5381 | 1.4759 | 7.4601 | 5.9032 | 0 | 0 | 3.8668 | 0 | 0 | 0 | 0 | 30.2441 | 30.244 | -7.679e-05
WV_5A_RS_2016_NG | 5A | RS | NG |  |  | RetailStandalone | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 379951.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91180.0069 | 0 | 0 | 471131.4558 | 0 | 471131.4558 | 0 | 0 | 2033.8801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.0866 | 0 | 0 | 2521.9667 | 0 | 2521.9667 | 0 | 0 | 379.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.18 | 0 | 0 | 471.1315 | 0 | 471.1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3876 | 3.6927 | 0 | 0 | 19.0803 | 19.0803 | 0
WV_5A_RS_2019_EL | 5A | RS | EL |  |  | RetailStandalone | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 0 | 25637.8348 | 65952.0588 | 10680.8103 | 53987.5506 | 0 | 40605.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196864.228 | 0 | 196864.5059 | -0.27786 | -0.27786 | 0 | 2407.3927 | 6192.8983 | 1002.9281 | 5069.431 | 0 | 3812.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18485.551 | 0 | 18485.5771 | -0.026091 | -0.026091 | 0 | 87.4763 | 225.0284 | 36.4429 | 184.2055 | 0 | 138.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 671.7007 | 0 | 671.7017 | -0.00094805 | -0.00094805 | 9.1134 | 1.4759 | 7.4601 | 5.611 | 0 | 0 | 3.5427 | 0 | 0 | 0 | 0 | 27.2032 | 27.2032 | -3.8395e-05
WV_5A_RS_2019_NG | 5A | RS | NG |  |  | RetailStandalone | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 408755.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91189.4851 | 0 | 0 | 499945.0963 | 0 | 499945.0963 | 0 | 0 | 2188.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.1373 | 0 | 0 | 2676.2061 | 0 | 2676.2061 | 0 | 0 | 408.7556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1895 | 0 | 0 | 499.9451 | 0 | 499.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5542 | 3.6931 | 0 | 0 | 20.2472 | 20.2472 | 0
WV_5A_SH_2016_EL | 5A | SH | EL |  |  | HotelSmall | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 25423.8851 | 62926.1997 | 79094.6792 | 12306.2718 | 154949.5496 | 0 | 45768.5504 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 380541.3786 | 0 | 380541.6564 | -0.27786 | -0.27786 | 2387.3028 | 5908.7701 | 7426.9904 | 1155.5589 | 14549.7627 | 0 | 4297.6669 | 6.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 35732.8354 | 0 | 35732.8615 | -0.026091 | -0.026091 | 86.7463 | 214.7042 | 269.871 | 41.989 | 528.6879 | 0 | 156.1623 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.4072 | 0 | 1298.4081 | -0.00094805 | -0.00094805 | 6.2467 | 0.97192 | 12.2376 | 3.6147 | 0.0057056 | 0 | 4.9698 | 2.0079 | 0 | 0 | 0 | 30.0544 | 30.0543 | -2.1945e-05
WV_5A_SH_2016_NG | 5A | SH | NG |  |  | HotelSmall | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605437.1417 | 0 | 0 | 1070682.6533 | 0 | 1070682.6533 | 0 | 0 | 351.9601 | 0 | 0 | 0 | 2138.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 3240.905 | 0 | 0 | 5731.3642 | 0 | 5731.3642 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.4371 | 0 | 0 | 1070.6827 | 0 | 1070.6827 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0141 | 0 | 0 | 24.7832 | 24.7832 | 0
WV_5A_SH_2019_EL | 5A | SH | EL |  |  | HotelSmall | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 29311.0999 | 58294.329 | 50731.0705 | 12306.2718 | 154949.5496 | 0 | 43317.8546 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 348982.4182 | 0 | 348984.0853 | -1.6671 | -1.6671 | 2752.3123 | 5473.8375 | 4763.6475 | 1155.5589 | 14549.7627 | 0 | 4067.5465 | 6.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 32769.4491 | 0 | 32769.6056 | -0.15654 | -0.15654 | 100.0095 | 198.9003 | 173.0944 | 41.989 | 528.6879 | 0 | 147.8005 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.728 | 0 | 1190.7337 | -0.0056883 | -0.0056883 | 4.0066 | 0.97192 | 12.2376 | 3.4211 | 0.0057056 | 0 | 4.604 | 2.3149 | 0 | 0 | 0 | 27.562 | 27.5619 | -0.00013167
WV_5A_SH_2019_NG | 5A | SH | NG |  |  | HotelSmall | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 65750.0736 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 605503.4889 | 0 | 0 | 1070749.0005 | 0 | 1070749.0005 | 0 | 0 | 351.9601 | 0 | 0 | 0 | 2138.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 3241.2602 | 0 | 0 | 5731.7194 | 0 | 5731.7194 | 0 | 0 | 65.7501 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 605.5035 | 0 | 0 | 1070.749 | 0 | 1070.749 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.5219 | 14.0156 | 0 | 0 | 24.7847 | 24.7847 | 0
WV_5A_SO_2016_EL | 5A | SO | EL |  |  | OfficeSmall | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 3103.659 | 3061.9805 | 8816.3921 | 1583.783 | 13417.6985 | 0 | 4776.3561 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39764.0678 | 0 | 39766.0128 | -1.945 | -1.945 | 291.4336 | 287.52 | 827.8592 | 148.7172 | 1259.9219 | 0 | 448.4998 | 0 | 0 | 0 | 0 | 469.8942 | 0 | 0 | 3733.846 | 0 | 3734.0286 | -0.18264 | -0.18264 | 10.5897 | 10.4475 | 30.0815 | 5.4039 | 45.7812 | 0 | 16.2969 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 135.675 | 0 | 135.6816 | -0.0066363 | -0.0066363 | 5.4674 | 0.98216 | 8.3208 | 2.962 | 0 | 0 | 1.8989 | 1.9247 | 3.1033 | 0 | 0 | 24.6604 | 24.6592 | -0.0012062
WV_5A_SO_2016_NG | 5A | SO | NG |  |  | OfficeSmall | STD2016 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 8757.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8757.8302 | 0 | 8757.8302 | 0 | 0 | 46.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.8807 | 0 | 46.8807 | 0 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7578 | 0 | 8.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5918 | 0 | 0 | 0 | 1.5918 | 1.5918 | 0
WV_5A_SO_2019_EL | 5A | SO | EL |  |  | OfficeSmall | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Electricity | 3162.0089 | 2861.9237 | 7104.795 | 1583.783 | 13417.6985 | 0 | 4370.6854 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 37505.0931 | 0 | 37504.2595 | 0.83357 | 0.83357 | 296.9126 | 268.7346 | 667.1403 | 148.7172 | 1259.9219 | 0 | 410.4074 | 0 | 0 | 0 | 0 | 469.8942 | 0 | 0 | 3521.7282 | 0 | 3521.65 | 0.078272 | 0.078272 | 10.7888 | 9.7649 | 24.2416 | 5.4039 | 45.7812 | 0 | 14.9128 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 127.9674 | 0 | 127.9645 | 0.0028441 | 0.0028441 | 4.406 | 0.98216 | 8.3208 | 2.7104 | 0 | 0 | 1.7748 | 1.9609 | 3.1033 | 0 | 0 | 23.2578 | 23.2583 | 0.00051693
WV_5A_SO_2019_NG | 5A | SO | NG |  |  | OfficeSmall | STD2019 | WV-ELKINS-WV | Zone5A | Zone5A(WV-ELKINS-WV) |  |  | WV | 0.0939 | 0.005353 |  |  |  | Natural Gas | 9127.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.4789 | 0 | 9127.4789 | 0 | 0 | 48.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8594 | 0 | 48.8594 | 0 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1275 | 0 | 9.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 0 | 0 | 0 | 1.6589 | 1.6589 | 0
WY_5B_LO_2016_EL | 5B | LO | EL |  |  | OfficeLarge | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 412767.1949 | 880080.4324 | 95718.8436 | 4077910.5986 | 543457.0788 | 709940.4587 | 68530.5687 | 120517.5513 | 680495.9876 | 0 | 0 | 0 | 0 | 7589418.7148 | 0 | 7589417.6033 | 1.1114 | 543458.1903 | 0 | 40079.6946 | 85455.81 | 9294.2997 | 395965.1191 | 52769.6824 | 68935.2185 | 6654.3182 | 11702.2542 | 66076.1604 | 0 | 0 | 0 | 0 | 736932.5572 | 0 | 736932.4493 | 0.10792 | 52769.7903 | 0 | 1408.3617 | 3002.8344 | 326.5927 | 13913.831 | 1854.2756 | 2422.3168 | 233.8263 | 411.2059 | 2321.8523 | 0 | 0 | 0 | 0 | 25895.0967 | 0 | 25895.0929 | 0.0037922 | 1854.2793 | 6.0227 | 0.65504 | 27.9065 | 4.8584 | 0.46898 | 0 | 2.8247 | 0 | 0 | 4.6569 | 0 | 51.9369 | 51.9369 | 7.6059e-06
WY_5B_LO_2016_NG | 5B | LO | NG |  |  | OfficeLarge | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 2132380.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603740.5491 | 0 | 0 | 2736120.5493 | 0 | 2736120.5493 | 0 | 0 | 14884.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.109 | 0 | 0 | 19098.1214 | 0 | 19098.1214 | 0 | 0 | 2132.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603.7405 | 0 | 0 | 2736.1205 | 0 | 2736.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2768 | 1.2109 | 0 | 0 | 5.4877 | 5.4877 | 0
WY_5B_LO_2019_EL | 5B | LO | EL |  |  | OfficeLarge | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 386095.7334 | 716767.3971 | 95718.8436 | 4077910.5986 | 543384.8361 | 677528.4784 | 65993.7373 | 107236.0025 | 680679.373 | 0 | 0 | 0 | 0 | 7351315 | 0 | 7351313.8886 | 1.1114 | 543385.9475 | 0 | 37489.8957 | 69598.1143 | 9294.2997 | 395965.1191 | 52762.6676 | 65788.0153 | 6407.9919 | 10412.6158 | 66093.9671 | 0 | 0 | 0 | 0 | 713812.6865 | 0 | 713812.5786 | 0.10792 | 52762.7755 | 0 | 1317.3586 | 2445.6104 | 326.5927 | 13913.831 | 1854.0291 | 2311.7272 | 225.1706 | 365.8892 | 2322.478 | 0 | 0 | 0 | 0 | 25082.6868 | 0 | 25082.683 | 0.0037922 | 1854.0329 | 4.9051 | 0.65504 | 27.9065 | 4.6365 | 0.45162 | 0 | 2.6422 | 0 | 0 | 4.6581 | 0 | 50.3074 | 50.3074 | 7.6059e-06
WY_5B_LO_2019_NG | 5B | LO | NG |  |  | OfficeLarge | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 2952914.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603825.8526 | 0 | 0 | 3556740.6118 | 0 | 3556740.6118 | 0 | 0 | 20611.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.7045 | 0 | 0 | 24826.0495 | 0 | 24826.0495 | 0 | 0 | 2952.9148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603.8259 | 0 | 0 | 3556.7406 | 0 | 3556.7406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9226 | 1.2111 | 0 | 0 | 7.1336 | 7.1336 | 0
WY_5B_MA_2016_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 13778.9122 | 28374.723 | 7207.602 | 142004.2074 | 0 | 21069.8712 | 0 | 0 | 0 | 0 | 121062.1504 | 0 | 0 | 333497.4661 | 0 | 333495.5211 | 1.945 | 1.945 | 0 | 1337.9324 | 2755.1856 | 699.8582 | 13788.6085 | 0 | 2045.8845 | 0 | 0 | 0 | 0 | 11755.1348 | 0 | 0 | 32382.604 | 0 | 32382.4151 | 0.18886 | 0.18886 | 0 | 47.0136 | 96.8146 | 24.5923 | 484.5184 | 0 | 71.8904 | 0 | 0 | 0 | 0 | 413.0641 | 0 | 0 | 1137.8934 | 0 | 1137.8867 | 0.0066363 | 0.0066363 | 2.8693 | 0.72886 | 14.3599 | 2.1307 | 0 | 0 | 1.3934 | 0 | 12.2422 | 0 | 0 | 33.7242 | 33.7244 | 0.00019668
WY_5B_MA_2016_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 322115.6482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322115.6482 | 0 | 322115.6482 | 0 | 0 | 2248.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2248.3672 | 0 | 2248.3672 | 0 | 0 | 322.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322.1156 | 0 | 322.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5467 | 0 | 0 | 0 | 9.5467 | 9.5467 | 0
WY_5B_MA_2019_EL | 5B | MA | EL |  |  | ApartmentMidRise | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 16404.6577 | 23181.5818 | 7207.602 | 142004.2074 | 0 | 20189.0655 | 0 | 0 | 0 | 0 | 120926.0006 | 0 | 0 | 329913.115 | 0 | 329914.2265 | -1.1114 | -1.1114 | 0 | 1592.8923 | 2250.9316 | 699.8582 | 13788.6085 | 0 | 1960.3583 | 0 | 0 | 0 | 0 | 11741.9147 | 0 | 0 | 32034.5635 | 0 | 32034.6714 | -0.10792 | -0.10792 | 0 | 55.9727 | 79.0956 | 24.5923 | 484.5184 | 0 | 68.8851 | 0 | 0 | 0 | 0 | 412.5995 | 0 | 0 | 1125.6635 | 0 | 1125.6673 | -0.0037922 | -0.0037922 | 2.3442 | 0.72886 | 14.3599 | 2.0416 | 0 | 0 | 1.6589 | 0 | 12.2284 | 0 | 0 | 33.362 | 33.3619 | -0.00011239
WY_5B_MA_2019_NG | 5B | MA | NG |  |  | ApartmentMidRise | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 171772.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171772.8967 | 0 | 171772.8967 | 0 | 0 | 1198.9748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.9748 | 0 | 1198.9748 | 0 | 0 | 171.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.7729 | 0 | 171.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0909 | 0 | 0 | 0 | 5.0909 | 5.0909 | 0
WY_5B_PS_2016_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 50353.1854 | 97816.6615 | 7129.8021 | 317887.4784 | 4818.0346 | 107038.7243 | 1194.7837 | 0 | 0 | 0 | 7179.8163 | 17466.0702 | 0 | 610884.5565 | 0 | 610884.2787 | 0.27786 | 4818.3125 | 0 | 4889.2943 | 9497.9978 | 692.3038 | 30866.8742 | 467.8312 | 10393.4601 | 116.0135 | 0 | 0 | 0 | 697.1602 | 1695.9554 | 0 | 59316.8904 | 0 | 59316.8635 | 0.02698 | 467.8581 | 0 | 171.8051 | 333.7504 | 24.3269 | 1084.6321 | 16.4391 | 365.2161 | 4.0766 | 0 | 0 | 0 | 24.4975 | 59.5942 | 0 | 2084.3381 | 0 | 2084.3372 | 0.00094805 | 16.4401 | 4.5126 | 0.32892 | 14.6653 | 4.9381 | 0.05512 | 0 | 2.323 | 0 | 0.33123 | 0 | 0.80577 | 28.1823 | 28.1823 | 1.2819e-05
WY_5B_PS_2016_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 802971.7077 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125225.5979 | 0 | 0 | 1270387.7204 | 0 | 1270387.7204 | 0 | 0 | 5604.7425 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 874.0747 | 0 | 0 | 8867.3063 | 0 | 8867.3063 | 0 | 0 | 802.9717 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.2256 | 0 | 0 | 1270.3877 | 0 | 1270.3877 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 10.857 | 1.6932 | 0 | 0 | 17.1769 | 17.1769 | 0
WY_5B_PS_2019_EL | 5B | PS | EL |  |  | SchoolPrimary | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 46382.6136 | 79580.9284 | 7129.8021 | 312483.1662 | 4743.0133 | 81978.8314 | 1783.8398 | 0 | 0 | 0 | 7179.8163 | 12417.4145 | 0 | 553679.4257 | 0 | 553682.4821 | -3.0564 | 4739.9569 | 0 | 4503.7518 | 7727.3081 | 692.3038 | 30342.1154 | 460.5466 | 7960.1445 | 173.2108 | 0 | 0 | 0 | 697.1602 | 1205.7309 | 0 | 53762.2722 | 0 | 53762.569 | -0.29678 | 460.2498 | 0 | 158.2575 | 271.5301 | 24.3269 | 1066.1926 | 16.1832 | 279.7118 | 6.0865 | 0 | 0 | 0 | 24.4975 | 42.3682 | 0 | 1889.1542 | 0 | 1889.1646 | -0.010429 | 16.1727 | 3.6714 | 0.32892 | 14.416 | 3.782 | 0.082295 | 0 | 2.1398 | 0 | 0.33123 | 0 | 0.57286 | 25.5434 | 25.5433 | -0.000141
WY_5B_PS_2019_NG | 5B | PS | NG |  |  | SchoolPrimary | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 1162232.3089 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125140.2944 | 0 | 0 | 1629563.0181 | 0 | 1629563.0181 | 0 | 0 | 8112.3815 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 873.4793 | 0 | 0 | 11374.3499 | 0 | 11374.3499 | 0 | 0 | 1162.2323 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.1403 | 0 | 0 | 1629.563 | 0 | 1629.563 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 15.7145 | 1.692 | 0 | 0 | 22.0333 | 22.0333 | 0
WY_5B_RS_2016_EL | 5B | RS | EL |  |  | RetailStandalone | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 17732.8126 | 84746.2838 | 10744.7174 | 53987.5506 | 0 | 50111.4501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217322.8145 | 0 | 217320.5916 | 2.2229 | 2.2229 | 0 | 1721.8561 | 8228.8642 | 1043.3121 | 5242.1912 | 0 | 4865.8218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21102.0453 | 0 | 21101.8294 | 0.21584 | 0.21584 | 0 | 60.5044 | 289.1543 | 36.661 | 184.2055 | 0 | 170.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.5054 | 0 | 741.4979 | 0.0075844 | 0.0075844 | 11.7104 | 1.4847 | 7.4601 | 6.9245 | 0 | 0 | 2.4504 | 0 | 0 | 0 | 0 | 30.0299 | 30.0302 | 0.00030716
WY_5B_RS_2016_NG | 5B | RS | NG |  |  | RetailStandalone | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 398443.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92677.558 | 0 | 0 | 491120.9189 | 0 | 491120.9189 | 0 | 0 | 2781.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646.8894 | 0 | 0 | 3428.024 | 0 | 3428.024 | 0 | 0 | 398.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6776 | 0 | 0 | 491.1209 | 0 | 491.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.1365 | 3.7533 | 0 | 0 | 19.8899 | 19.8899 | 0
WY_5B_RS_2019_EL | 5B | RS | EL |  |  | RetailStandalone | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 16004.5441 | 67263.5422 | 10744.7174 | 53987.5506 | 0 | 47755.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195755.5799 | 0 | 195754.7463 | 0.83357 | 0.83357 | 0 | 1554.0412 | 6531.29 | 1043.3121 | 5242.1912 | 0 | 4637.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19007.8668 | 0 | 19007.7859 | 0.08094 | 0.08094 | 0 | 54.6075 | 229.5032 | 36.661 | 184.2055 | 0 | 162.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.918 | 0 | 667.9152 | 0.0028441 | 0.0028441 | 9.2946 | 1.4847 | 7.4601 | 6.5989 | 0 | 0 | 2.2115 | 0 | 0 | 0 | 0 | 27.0499 | 27.05 | 0.00011518
WY_5B_RS_2019_NG | 5B | RS | NG |  |  | RetailStandalone | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 430925.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92687.0362 | 0 | 0 | 523612.0898 | 0 | 523612.0898 | 0 | 0 | 3007.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646.9555 | 0 | 0 | 3654.8124 | 0 | 3654.8124 | 0 | 0 | 430.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.687 | 0 | 0 | 523.6121 | 0 | 523.6121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.452 | 3.7537 | 0 | 0 | 21.2057 | 21.2057 | 0
WY_5B_SH_2016_EL | 5B | SH | EL |  |  | HotelSmall | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 31789.5814 | 49533.5082 | 79275.286 | 12309.0504 | 154949.5496 | 0 | 53551.3157 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 381480.5341 | 0 | 381478.5891 | 1.945 | 1.945 | 3086.7684 | 4809.7037 | 7697.6303 | 1195.2088 | 15045.6013 | 0 | 5199.8328 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 37041.7599 | 0 | 37041.571 | 0.18886 | 0.18886 | 108.4661 | 169.0083 | 270.4873 | 41.9985 | 528.6879 | 0 | 182.7171 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1301.6116 | 0 | 1301.6049 | 0.0066363 | 0.0066363 | 6.261 | 0.97214 | 12.2376 | 4.2294 | 0.0057056 | 0 | 3.912 | 2.5107 | 0 | 0 | 0 | 30.1283 | 30.1285 | 0.00015361
WY_5B_SH_2016_NG | 5B | SH | NG |  |  | HotelSmall | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 53125.1496 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 633776.8736 | 0 | 0 | 1086397.4611 | 0 | 1086397.4611 | 0 | 0 | 370.8135 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4423.7626 | 0 | 0 | 7583.0543 | 0 | 7583.0543 | 0 | 0 | 53.1251 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 633.7769 | 0 | 0 | 1086.3975 | 0 | 1086.3975 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2297 | 14.6701 | 0 | 0 | 25.1469 | 25.1469 | 0
WY_5B_SH_2019_EL | 5B | SH | EL |  |  | HotelSmall | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 36710.423 | 45571.2722 | 50850.5489 | 12309.0504 | 154949.5496 | 0 | 50472.6638 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 350935.7506 | 0 | 350935.4727 | 0.27786 | 0.27786 | 3564.5821 | 4424.9705 | 4937.5883 | 1195.2088 | 15045.6013 | 0 | 4900.8957 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 34075.8614 | 0 | 34075.8344 | 0.02698 | 0.02698 | 125.256 | 155.4892 | 173.5021 | 41.9985 | 528.6879 | 0 | 172.2127 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1197.3928 | 0 | 1197.3918 | 0.00094805 | 0.00094805 | 4.0161 | 0.97214 | 12.2376 | 3.9862 | 0.0057056 | 0 | 3.5991 | 2.8993 | 0 | 0 | 0 | 27.7161 | 27.7161 | 2.1945e-05
WY_5B_SH_2019_NG | 5B | SH | NG |  |  | HotelSmall | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 54167.7484 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 633833.7427 | 0 | 0 | 1087496.929 | 0 | 1087496.929 | 0 | 0 | 378.0909 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.1595 | 0 | 0 | 7590.7286 | 0 | 7590.7286 | 0 | 0 | 54.1677 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 633.8337 | 0 | 0 | 1087.4969 | 0 | 1087.4969 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.2538 | 14.6714 | 0 | 0 | 25.1724 | 25.1724 | 0
WY_5B_SO_2016_EL | 5B | SO | EL |  |  | OfficeSmall | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 3845.5363 | 2342.3317 | 8833.0635 | 1583.783 | 13417.6985 | 0 | 5673.8332 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 40700.4448 | 0 | 40700.7226 | -0.27786 | -0.27786 | 373.4016 | 227.4404 | 857.6905 | 153.7853 | 1302.8585 | 0 | 550.9292 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 3952.0132 | 0 | 3952.0402 | -0.02698 | -0.02698 | 13.121 | 7.992 | 30.1384 | 5.4039 | 45.7812 | 0 | 19.3591 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 138.8699 | 0 | 138.8709 | -0.00094805 | -0.00094805 | 5.4777 | 0.98216 | 8.3208 | 3.5186 | 0 | 0 | 1.4526 | 2.3848 | 3.1033 | 0 | 0 | 25.2401 | 25.2399 | -0.00017231
WY_5B_SO_2016_NG | 5B | SO | NG |  |  | OfficeSmall | STD2016 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 7705.7532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7705.7532 | 0 | 7705.7532 | 0 | 0 | 53.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.7862 | 0 | 53.7862 | 0 | 0 | 7.7058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7058 | 0 | 7.7058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4005 | 0 | 0 | 0 | 1.4005 | 1.4005 | 0
WY_5B_SO_2019_EL | 5B | SO | EL |  |  | OfficeSmall | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 3901.1076 | 2167.282 | 7121.4664 | 1583.783 | 13417.6985 | 0 | 5182.0269 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38377.563 | 0 | 38379.2302 | -1.6671 | -1.6671 | 378.7976 | 210.4431 | 691.4944 | 153.7853 | 1302.8585 | 0 | 503.1748 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 3726.4614 | 0 | 3726.6232 | -0.16188 | -0.16188 | 13.3106 | 7.3948 | 24.2984 | 5.4039 | 45.7812 | 0 | 17.6811 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 130.9442 | 0 | 130.9499 | -0.0056883 | -0.0056883 | 4.4163 | 0.98216 | 8.3208 | 3.2136 | 0 | 0 | 1.344 | 2.4192 | 3.1033 | 0 | 0 | 23.8004 | 23.7994 | -0.0010339
WY_5B_SO_2019_NG | 5B | SO | NG |  |  | OfficeSmall | STD2019 | WY-CHEYENNE-WY | Zone5B | Zone5B(WY-CHEYENNE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 8264.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8264.9653 | 0 | 8264.9653 | 0 | 0 | 57.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.6895 | 0 | 57.6895 | 0 | 0 | 8.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.265 | 0 | 8.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5022 | 0 | 0 | 0 | 1.5022 | 1.5022 | 0
WY_6B_LO_2016_EL | 6B | LO | EL |  |  | OfficeLarge | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 486240.8337 | 879508.0477 | 96024.486 | 4077910.5986 | 543457.0788 | 709968.2444 | 73501.4244 | 133054.4442 | 688973.3946 | 0 | 0 | 0 | 0 | 7688638.5524 | 0 | 7688641.8867 | -3.3343 | 543453.7446 | 0 | 47213.985 | 85400.2314 | 9323.9776 | 395965.1191 | 52769.6824 | 68937.9165 | 7136.9883 | 12919.5865 | 66899.3166 | 0 | 0 | 0 | 0 | 746566.8034 | 0 | 746567.1272 | -0.32376 | 52769.3586 | 0 | 1659.0537 | 3000.8815 | 327.6355 | 13913.831 | 1854.2756 | 2422.4116 | 250.7869 | 453.9818 | 2350.7772 | 0 | 0 | 0 | 0 | 26233.6347 | 0 | 26233.6461 | -0.011377 | 1854.2642 | 6.0188 | 0.65713 | 27.9065 | 4.8585 | 0.50299 | 0 | 3.3275 | 0 | 0 | 4.7149 | 0 | 52.6159 | 52.6159 | -2.2818e-05
WY_6B_LO_2016_NG | 6B | LO | NG |  |  | OfficeLarge | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 2378840.8859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601228.8337 | 0 | 0 | 2980069.7197 | 0 | 2980069.7197 | 0 | 0 | 16604.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.5773 | 0 | 0 | 20800.8866 | 0 | 20800.8866 | 0 | 0 | 2378.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.2288 | 0 | 0 | 2980.0697 | 0 | 2980.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7712 | 1.2059 | 0 | 0 | 5.977 | 5.977 | 0
WY_6B_LO_2019_EL | 6B | LO | EL |  |  | OfficeLarge | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 447846.5993 | 716592.3474 | 96024.486 | 4077910.5986 | 543384.8361 | 680740.5015 | 71053.5072 | 118414.1763 | 688806.6806 | 0 | 0 | 0 | 0 | 7440773.733 | 0 | 7440776.2337 | -2.5007 | 543382.3354 | 0 | 43485.9048 | 69581.1169 | 9323.9776 | 395965.1191 | 52762.6676 | 66099.9027 | 6899.2955 | 11498.0165 | 66883.1287 | 0 | 0 | 0 | 0 | 722499.1295 | 0 | 722499.3723 | -0.24282 | 52762.4248 | 0 | 1528.0526 | 2445.0131 | 327.6355 | 13913.831 | 1854.0291 | 2322.6866 | 242.4346 | 404.0292 | 2350.2084 | 0 | 0 | 0 | 0 | 25387.92 | 0 | 25387.9285 | -0.0085324 | 1854.0205 | 4.9039 | 0.65713 | 27.9065 | 4.6585 | 0.48624 | 0 | 3.0648 | 0 | 0 | 4.7137 | 0 | 50.9197 | 50.9196 | -1.7113e-05
WY_6B_LO_2019_NG | 6B | LO | NG |  |  | OfficeLarge | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 3281134.3497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601200.3992 | 0 | 0 | 3882334.7489 | 0 | 3882334.7489 | 0 | 0 | 22902.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.3788 | 0 | 0 | 27098.6965 | 0 | 27098.6965 | 0 | 0 | 3281.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.2004 | 0 | 0 | 3882.3347 | 0 | 3882.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5809 | 1.2058 | 0 | 0 | 7.7867 | 7.7867 | 0
WY_6B_MA_2016_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 21272.7065 | 28374.723 | 7204.8234 | 142004.2074 | 0 | 22667.547 | 0 | 0 | 0 | 0 | 120439.7514 | 0 | 0 | 341963.7587 | 0 | 341965.148 | -1.3893 | -1.3893 | 0 | 2065.5798 | 2755.1856 | 699.5884 | 13788.6085 | 0 | 2201.0188 | 0 | 0 | 0 | 0 | 11694.6999 | 0 | 0 | 33204.681 | 0 | 33204.8159 | -0.1349 | -0.1349 | 0 | 72.5825 | 96.8146 | 24.5829 | 484.5184 | 0 | 77.3417 | 0 | 0 | 0 | 0 | 410.9404 | 0 | 0 | 1166.7803 | 0 | 1166.7851 | -0.0047402 | -0.0047402 | 2.8693 | 0.72858 | 14.3599 | 2.2922 | 0 | 0 | 2.1512 | 0 | 12.1793 | 0 | 0 | 34.5806 | 34.5805 | -0.00014049
WY_6B_MA_2016_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 180834.0283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180834.0283 | 0 | 180834.0283 | 0 | 0 | 1262.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2215 | 0 | 1262.2215 | 0 | 0 | 180.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.834 | 0 | 180.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3595 | 0 | 0 | 0 | 5.3595 | 5.3595 | 0
WY_6B_MA_2019_EL | 6B | MA | EL |  |  | ApartmentMidRise | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 20080.7014 | 23181.5818 | 7204.8234 | 142004.2074 | 0 | 21547.7846 | 0 | 0 | 0 | 0 | 120436.9728 | 0 | 0 | 334456.0716 | 0 | 334456.0716 | 0 | 0 | 0 | 1949.8361 | 2250.9316 | 699.5884 | 13788.6085 | 0 | 2092.2899 | 0 | 0 | 0 | 0 | 11694.4301 | 0 | 0 | 32475.6845 | 0 | 32475.6845 | 0 | 0 | 0 | 68.5154 | 79.0956 | 24.5829 | 484.5184 | 0 | 73.521 | 0 | 0 | 0 | 0 | 410.931 | 0 | 0 | 1141.1641 | 0 | 1141.1641 | 0 | 0 | 2.3442 | 0.72858 | 14.3599 | 2.179 | 0 | 0 | 2.0306 | 0 | 12.179 | 0 | 0 | 33.8213 | 33.8213 | 0
WY_6B_MA_2019_NG | 6B | MA | NG |  |  | ApartmentMidRise | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 177819.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177819.9699 | 0 | 177819.9699 | 0 | 0 | 1241.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.1834 | 0 | 1241.1834 | 0 | 0 | 177.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177.82 | 0 | 177.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2701 | 0 | 0 | 0 | 5.2701 | 5.2701 | 0
WY_6B_PS_2016_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 66957.8999 | 97016.4343 | 7135.3592 | 317887.4784 | 4818.0346 | 108300.1936 | 1003.0626 | 0 | 0 | 16660.2858 | 7179.8163 | 17474.4059 | 0 | 644432.9706 | 0 | 644433.5264 | -0.55571 | 4817.4789 | 0 | 6501.6121 | 9420.2958 | 692.8434 | 30866.8742 | 467.8312 | 10515.9488 | 97.3974 | 0 | 0 | 1617.7138 | 697.1602 | 1696.7648 | 0 | 62574.4414 | 0 | 62574.4954 | -0.05396 | 467.7772 | 0 | 228.4604 | 331.0201 | 24.3458 | 1084.6321 | 16.4391 | 369.5203 | 3.4224 | 0 | 0 | 56.8449 | 24.4975 | 59.6227 | 0 | 2198.8053 | 0 | 2198.8072 | -0.0018961 | 16.4372 | 4.4757 | 0.32918 | 14.6653 | 4.9963 | 0.046275 | 0.7686 | 3.089 | 0 | 0.33123 | 0 | 0.80616 | 29.7301 | 29.7301 | -2.5637e-05
WY_6B_PS_2016_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 549876.1022 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125187.6852 | 0 | 0 | 1017254.2022 | 0 | 1017254.2022 | 0 | 0 | 3838.1352 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 873.81 | 0 | 0 | 7100.4343 | 0 | 7100.4343 | 0 | 0 | 549.8761 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.1877 | 0 | 0 | 1017.2542 | 0 | 1017.2542 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.4349 | 1.6927 | 0 | 0 | 13.7543 | 13.7543 | 0
WY_6B_PS_2019_EL | 6B | PS | EL |  |  | SchoolPrimary | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 58063.708 | 79283.6217 | 7135.3592 | 312483.1662 | 4743.0133 | 82762.3872 | 889.1413 | 0 | 0 | 20211.294 | 7179.8163 | 12420.1931 | 0 | 585171.7004 | 0 | 585175.8683 | -4.1679 | 4738.8455 | 0 | 5637.986 | 7698.4397 | 692.8434 | 30342.1154 | 460.5466 | 8036.2278 | 86.3356 | 0 | 0 | 1962.5167 | 697.1602 | 1206.0007 | 0 | 56820.1721 | 0 | 56820.5768 | -0.4047 | 460.1419 | 0 | 198.1134 | 270.5157 | 24.3458 | 1066.1926 | 16.1832 | 282.3853 | 3.0338 | 0 | 0 | 68.9609 | 24.4975 | 42.3777 | 0 | 1996.6058 | 0 | 1996.6201 | -0.014221 | 16.1689 | 3.6576 | 0.32918 | 14.416 | 3.8181 | 0.041019 | 0.93242 | 2.6787 | 0 | 0.33123 | 0 | 0.57299 | 26.9963 | 26.9961 | -0.00019228
WY_6B_PS_2019_NG | 6B | PS | NG |  |  | SchoolPrimary | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 578158.965 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 125102.3817 | 0 | 0 | 1045451.7615 | 0 | 1045451.7615 | 0 | 0 | 4035.5496 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 873.2146 | 0 | 0 | 7297.2533 | 0 | 7297.2533 | 0 | 0 | 578.159 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 125.1024 | 0 | 0 | 1045.4518 | 0 | 1045.4518 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.8173 | 1.6915 | 0 | 0 | 14.1356 | 14.1356 | 0
WY_6B_RS_2016_EL | 6B | RS | EL |  |  | RetailStandalone | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 23120.4534 | 91067.523 | 10733.6031 | 53987.5506 | 0 | 49875.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228784.4021 | 0 | 228785.5135 | -1.1114 | -1.1114 | 0 | 2244.996 | 8842.6565 | 1042.2329 | 5242.1912 | 0 | 4842.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22214.9654 | 0 | 22215.0734 | -0.10792 | -0.10792 | 0 | 78.887 | 310.7224 | 36.6231 | 184.2055 | 0 | 170.1744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780.6124 | 0 | 780.6162 | -0.0037922 | -0.0037922 | 12.5839 | 1.4832 | 7.4601 | 6.8919 | 0 | 0 | 3.1948 | 0 | 0 | 0 | 0 | 31.6141 | 31.614 | -0.00015358
WY_6B_RS_2016_NG | 6B | RS | NG |  |  | RetailStandalone | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 422394.6995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92516.4291 | 0 | 0 | 514911.1286 | 0 | 514911.1286 | 0 | 0 | 2948.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.7647 | 0 | 0 | 3594.0797 | 0 | 3594.0797 | 0 | 0 | 422.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5164 | 0 | 0 | 514.9111 | 0 | 514.9111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1065 | 3.7468 | 0 | 0 | 20.8534 | 20.8534 | 0
WY_6B_RS_2019_EL | 6B | RS | EL |  |  | RetailStandalone | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 21281.0422 | 75401.9641 | 10733.6031 | 53987.5506 | 0 | 47555.1688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208959.3288 | 0 | 208956.8281 | 2.5007 | 2.5007 | 0 | 2066.3892 | 7321.5307 | 1042.2329 | 5242.1912 | 0 | 4617.6069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20289.9508 | 0 | 20289.708 | 0.24282 | 0.24282 | 0 | 72.6109 | 257.2715 | 36.6231 | 184.2055 | 0 | 162.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.9692 | 0 | 712.9607 | 0.0085324 | 0.0085324 | 10.4192 | 1.4832 | 7.4601 | 6.5713 | 0 | 0 | 2.9407 | 0 | 0 | 0 | 0 | 28.8742 | 28.8745 | 0.00034555
WY_6B_RS_2019_NG | 6B | RS | NG |  |  | RetailStandalone | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 452753.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92525.9073 | 0 | 0 | 545279.1891 | 0 | 545279.1891 | 0 | 0 | 3160.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.8308 | 0 | 0 | 3806.0487 | 0 | 3806.0487 | 0 | 0 | 452.7533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5259 | 0 | 0 | 545.2792 | 0 | 545.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.336 | 3.7472 | 0 | 0 | 22.0832 | 22.0832 | 0
WY_6B_SH_2016_EL | 6B | SH | EL |  |  | HotelSmall | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 34387.5413 | 52895.5739 | 79169.7005 | 12306.2718 | 154949.5496 | 0 | 53467.9587 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 387248.8385 | 0 | 387245.7821 | 3.0564 | 3.0564 | 3339.0303 | 5136.1602 | 7687.3779 | 1194.939 | 15045.6013 | 0 | 5191.7388 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 37601.8622 | 0 | 37601.5654 | 0.29678 | 0.29678 | 117.3303 | 180.4797 | 270.127 | 41.989 | 528.6879 | 0 | 182.4327 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.293 | 0 | 1321.2826 | 0.010429 | 0.010429 | 6.2527 | 0.97192 | 12.2376 | 4.2228 | 0.0057056 | 0 | 4.1776 | 2.7159 | 0 | 0 | 0 | 30.5838 | 30.5841 | 0.00024139
WY_6B_SH_2016_NG | 6B | SH | NG |  |  | HotelSmall | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 60698.2084 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 630819.6842 | 0 | 0 | 1091013.3305 | 0 | 1091013.3305 | 0 | 0 | 423.6735 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4403.1214 | 0 | 0 | 7615.273 | 0 | 7615.273 | 0 | 0 | 60.6982 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 630.8197 | 0 | 0 | 1091.0133 | 0 | 1091.0133 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.405 | 14.6016 | 0 | 0 | 25.2538 | 25.2538 | 0
WY_6B_SH_2019_EL | 6B | SH | EL |  |  | HotelSmall | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 39683.4894 | 48466.5386 | 50867.2203 | 12306.2718 | 154949.5496 | 0 | 50405.9782 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 356751.2906 | 0 | 356748.7899 | 2.5007 | 2.5007 | 3853.2668 | 4706.1009 | 4939.2071 | 1194.939 | 15045.6013 | 0 | 4894.4205 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 34640.5503 | 0 | 34640.3075 | 0.24282 | 0.24282 | 135.4001 | 165.3678 | 173.559 | 41.989 | 528.6879 | 0 | 171.9852 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.2354 | 0 | 1217.2269 | 0.0085324 | 0.0085324 | 4.0174 | 0.97192 | 12.2376 | 3.981 | 0.0057056 | 0 | 3.8278 | 3.1341 | 0 | 0 | 0 | 28.1752 | 28.1754 | 0.0001975
WY_6B_SH_2019_NG | 6B | SH | NG |  |  | HotelSmall | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 61200.5514 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 630895.5096 | 0 | 0 | 1091591.4989 | 0 | 1091591.4989 | 0 | 0 | 427.1798 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4403.6507 | 0 | 0 | 7619.3087 | 0 | 7619.3087 | 0 | 0 | 61.2006 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 630.8955 | 0 | 0 | 1091.5915 | 0 | 1091.5915 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.4166 | 14.6034 | 0 | 0 | 25.2672 | 25.2672 | 0
WY_6B_SO_2016_EL | 6B | SO | EL |  |  | OfficeSmall | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 4095.6073 | 2953.6164 | 8805.2778 | 1589.3401 | 13417.6985 | 0 | 5782.1973 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41647.936 | 0 | 41646.5467 | 1.3893 | 1.3893 | 397.6835 | 286.7962 | 854.9925 | 154.3249 | 1302.8585 | 0 | 561.4514 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 4044.0146 | 0 | 4043.8797 | 0.1349 | 0.1349 | 13.9742 | 10.0777 | 30.0436 | 5.4228 | 45.7812 | 0 | 19.7289 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 142.1028 | 0 | 142.098 | 0.0047402 | 0.0047402 | 5.4605 | 0.98561 | 8.3208 | 3.5858 | 0 | 0 | 1.8317 | 2.5398 | 3.1033 | 0 | 0 | 25.8266 | 25.8275 | 0.00086155
WY_6B_SO_2016_NG | 6B | SO | NG |  |  | OfficeSmall | STD2016 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 10814.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10814.5933 | 0 | 10814.5933 | 0 | 0 | 75.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4859 | 0 | 75.4859 | 0 | 0 | 10.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8146 | 0 | 10.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9656 | 0 | 0 | 0 | 1.9656 | 1.9656 | 0
WY_6B_SO_2019_EL | 6B | SO | EL |  |  | OfficeSmall | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 4220.6428 | 2670.2026 | 7124.245 | 1589.3401 | 13417.6985 | 0 | 5223.7054 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 39250.033 | 0 | 39250.3108 | -0.27786 | -0.27786 | 409.8244 | 259.2767 | 691.7642 | 154.3249 | 1302.8585 | 0 | 507.2218 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 3811.1782 | 0 | 3811.2052 | -0.02698 | -0.02698 | 14.4008 | 9.1107 | 24.3079 | 5.4228 | 45.7812 | 0 | 17.8233 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 133.9211 | 0 | 133.9221 | -0.00094805 | -0.00094805 | 4.418 | 0.98561 | 8.3208 | 3.2394 | 0 | 0 | 1.6559 | 2.6174 | 3.1033 | 0 | 0 | 24.3406 | 24.3404 | -0.00017231
WY_6B_SO_2019_NG | 6B | SO | NG |  |  | OfficeSmall | STD2019 | WY-CASPER-WY | Zone6B | Zone6B(WY-CASPER-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 11743.4541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11743.4541 | 0 | 11743.4541 | 0 | 0 | 81.9693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9693 | 0 | 81.9693 | 0 | 0 | 11.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7435 | 0 | 11.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1344 | 0 | 0 | 0 | 2.1344 | 2.1344 | 0
WY_7_LO_2016_EL | 7 | LO | EL |  |  | OfficeLarge | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 315322.8614 | 880408.3033 | 96163.4143 | 4077910.5986 | 543457.0788 | 775659.1179 | 56052.0257 | 79972.7063 | 746175.7469 | 11061.474 | 0 | 0 | 0 | 7582183.3271 | 0 | 7582182.2157 | 1.1114 | 543458.1903 | 0 | 30617.8498 | 85487.6462 | 9337.4675 | 395965.1191 | 52769.6824 | 75316.5004 | 5442.6517 | 7765.3498 | 72453.665 | 1074.0691 | 0 | 0 | 0 | 736230.0011 | 0 | 736229.8931 | 0.10792 | 52769.7903 | 0 | 1075.8816 | 3003.9531 | 328.1096 | 13913.831 | 1854.2756 | 2646.5489 | 191.2495 | 272.8669 | 2545.9516 | 37.7417 | 0 | 0 | 0 | 25870.4095 | 0 | 25870.4057 | 0.0037922 | 1854.2793 | 6.0249 | 0.65808 | 27.9065 | 5.3081 | 0.38358 | 0.075697 | 2.1579 | 0 | 0 | 5.1063 | 0 | 51.8873 | 51.8873 | 7.6059e-06
WY_7_LO_2016_NG | 7 | LO | NG |  |  | OfficeLarge | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 1058218.8581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646572.4048 | 0 | 0 | 1704791.2629 | 0 | 1704791.2629 | 0 | 0 | 7386.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4513.0754 | 0 | 0 | 11899.443 | 0 | 11899.443 | 0 | 0 | 1058.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646.5724 | 0 | 0 | 1704.7913 | 0 | 1704.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1224 | 1.2968 | 0 | 0 | 3.4192 | 3.4192 | 0
WY_7_LO_2019_EL | 7 | LO | EL |  |  | OfficeLarge | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 289179.3275 | 717498.1601 | 96163.4143 | 4077910.5986 | 543387.6147 | 744197.4074 | 53837.508 | 70861.7861 | 745883.9974 | 10177.8898 | 0 | 0 | 0 | 7349097.7038 | 0 | 7349094.6474 | 3.0564 | 543390.6711 | 0 | 28079.3127 | 69669.0713 | 9337.4675 | 395965.1191 | 52762.9374 | 72261.5683 | 5227.622 | 6880.6794 | 72425.3361 | 988.2731 | 0 | 0 | 0 | 713597.387 | 0 | 713597.0903 | 0.29678 | 52763.2342 | 0 | 986.6799 | 2448.1037 | 328.1096 | 13913.831 | 1854.0385 | 2539.2016 | 183.6936 | 241.7804 | 2544.9562 | 34.727 | 0 | 0 | 0 | 25075.1214 | 0 | 25075.1109 | 0.010429 | 1854.049 | 4.9101 | 0.65808 | 27.9065 | 5.0928 | 0.36843 | 0.069651 | 1.9789 | 0 | 0 | 5.1043 | 0 | 50.2922 | 50.2923 | 2.0916e-05
WY_7_LO_2019_NG | 7 | LO | NG |  |  | OfficeLarge | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 947608.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646667.1865 | 0 | 0 | 1594275.7867 | 0 | 1594275.7867 | 0 | 0 | 6614.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4513.737 | 0 | 0 | 11128.045 | 0 | 11128.045 | 0 | 0 | 947.6086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646.6672 | 0 | 0 | 1594.2758 | 0 | 1594.2758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9006 | 1.297 | 0 | 0 | 3.1976 | 3.1976 | 0
WY_7_MA_2016_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 17732.8126 | 28374.723 | 7199.2663 | 142004.2074 | 0 | 20944.8357 | 0 | 0 | 0 | 0 | 129172.7865 | 0 | 0 | 345428.6314 | 0 | 345425.8528 | 2.7786 | 2.7786 | 0 | 1721.8561 | 2755.1856 | 699.0488 | 13788.6085 | 0 | 2033.7435 | 0 | 0 | 0 | 0 | 12542.6776 | 0 | 0 | 33541.1201 | 0 | 33540.8503 | 0.2698 | 0.2698 | 0 | 60.5044 | 96.8146 | 24.5639 | 484.5184 | 0 | 71.4638 | 0 | 0 | 0 | 0 | 440.7375 | 0 | 0 | 1178.6025 | 0 | 1178.593 | 0.0094805 | 0.0094805 | 2.8693 | 0.72801 | 14.3599 | 2.118 | 0 | 0 | 1.7932 | 0 | 13.0624 | 0 | 0 | 34.9306 | 34.9309 | 0.00028098
WY_7_MA_2016_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 154418.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154418.3652 | 0 | 154418.3652 | 0 | 0 | 1077.8402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1077.8402 | 0 | 1077.8402 | 0 | 0 | 154.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.4184 | 0 | 154.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5766 | 0 | 0 | 0 | 4.5766 | 4.5766 | 0
WY_7_MA_2019_EL | 7 | MA | EL |  |  | ApartmentMidRise | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 16118.4653 | 23181.5818 | 7199.2663 | 142004.2074 | 0 | 19369.3883 | 0 | 0 | 0 | 0 | 129158.8937 | 0 | 0 | 337031.8029 | 0 | 337031.525 | 0.27786 | 0.27786 | 0 | 1565.103 | 2250.9316 | 699.0488 | 13788.6085 | 0 | 1880.7676 | 0 | 0 | 0 | 0 | 12541.3286 | 0 | 0 | 32725.7881 | 0 | 32725.7611 | 0.02698 | 0.02698 | 0 | 54.9962 | 79.0956 | 24.5639 | 484.5184 | 0 | 66.0884 | 0 | 0 | 0 | 0 | 440.6901 | 0 | 0 | 1149.9525 | 0 | 1149.9516 | 0.00094805 | 0.00094805 | 2.3442 | 0.72801 | 14.3599 | 1.9587 | 0 | 0 | 1.63 | 0 | 13.061 | 0 | 0 | 34.0817 | 34.0818 | 2.8098e-05
WY_7_MA_2019_NG | 7 | MA | NG |  |  | ApartmentMidRise | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 138457.1249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138457.1249 | 0 | 138457.1249 | 0 | 0 | 966.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966.4307 | 0 | 966.4307 | 0 | 0 | 138.4571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.4571 | 0 | 138.4571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1035 | 0 | 0 | 0 | 4.1035 | 4.1035 | 0
WY_7_PS_2016_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 32148.0165 | 95182.5803 | 7124.245 | 317887.4784 | 4818.0346 | 103621.0873 | 966.9412 | 0 | 0 | 20339.1081 | 7179.8163 | 17474.4059 | 0 | 606741.7136 | 0 | 606743.6586 | -1.945 | 4816.0896 | 0 | 3121.5724 | 9242.2285 | 691.7642 | 30866.8742 | 467.8312 | 10061.6076 | 93.89 | 0 | 0 | 1974.9274 | 697.1602 | 1696.7648 | 0 | 58914.6204 | 0 | 58914.8092 | -0.18886 | 467.6423 | 0 | 109.689 | 324.763 | 24.3079 | 1084.6321 | 16.4391 | 353.5551 | 3.2992 | 0 | 0 | 69.397 | 24.4975 | 59.6227 | 0 | 2070.2027 | 0 | 2070.2094 | -0.0066363 | 16.4325 | 4.3911 | 0.32867 | 14.6653 | 4.7804 | 0.044609 | 0.93832 | 1.4831 | 0 | 0.33123 | 0 | 0.80616 | 27.9913 | 27.9912 | -8.973e-05
WY_7_PS_2016_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 536606.6625 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133433.6942 | 0 | 0 | 1012230.7715 | 0 | 1012230.7715 | 0 | 0 | 3745.5145 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 931.3672 | 0 | 0 | 7065.3708 | 0 | 7065.3708 | 0 | 0 | 536.6067 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.4337 | 0 | 0 | 1012.2308 | 0 | 1012.2308 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.2555 | 1.8042 | 0 | 0 | 13.6864 | 13.6864 | 0
WY_7_PS_2019_EL | 7 | PS | EL |  |  | SchoolPrimary | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 27141.0394 | 78188.8664 | 7124.245 | 312483.1662 | 4743.0133 | 79205.8218 | 697.4202 | 0 | 0 | 22725.8969 | 7179.8163 | 12422.9716 | 0 | 551912.2573 | 0 | 551908.6451 | 3.6121 | 4746.6255 | 0 | 2635.3949 | 7592.1389 | 691.7642 | 30342.1154 | 460.5466 | 7690.8853 | 67.7195 | 0 | 0 | 2206.6846 | 697.1602 | 1206.2705 | 0 | 53590.6802 | 0 | 53590.3294 | 0.35074 | 460.8973 | 0 | 92.6052 | 266.7804 | 24.3079 | 1066.1926 | 16.1832 | 270.2503 | 2.3796 | 0 | 0 | 77.5408 | 24.4975 | 42.3872 | 0 | 1883.1246 | 0 | 1883.1123 | 0.012325 | 16.1955 | 3.6071 | 0.32867 | 14.416 | 3.6541 | 0.032175 | 1.0484 | 1.2521 | 0 | 0.33123 | 0 | 0.57312 | 25.4616 | 25.4617 | 0.00016664
WY_7_PS_2019_NG | 7 | PS | NG |  |  | SchoolPrimary | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 527441.2709 | 0 | 0 | 0 | 342190.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 133376.8251 | 0 | 0 | 1003008.5109 | 0 | 1003008.5109 | 0 | 0 | 3681.5401 | 0 | 0 | 0 | 2388.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 930.9702 | 0 | 0 | 7000.9994 | 0 | 7000.9994 | 0 | 0 | 527.4413 | 0 | 0 | 0 | 342.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 133.3768 | 0 | 0 | 1003.0085 | 0 | 1003.0085 | 0 | 0 | 0 | 0 | 4.6268 | 0 | 0 | 0 | 0 | 7.1315 | 1.8034 | 0 | 0 | 13.5617 | 13.5617 | 0
WY_7_RS_2016_EL | 7 | RS | EL |  |  | RetailStandalone | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 13481.6055 | 89675.4611 | 10686.3675 | 53987.5506 | 0 | 48252.589 | 0 | 0 | 0 | 5104.227 | 0 | 0 | 0 | 221187.8008 | 0 | 221187.8008 | 0 | 0 | 0 | 1309.0639 | 8707.4873 | 1037.6463 | 5242.1912 | 0 | 4685.3264 | 0 | 0 | 0 | 495.6204 | 0 | 0 | 0 | 21477.3355 | 0 | 21477.3355 | 0 | 0 | 0 | 45.9992 | 305.9727 | 36.4619 | 184.2055 | 0 | 164.6378 | 0 | 0 | 0 | 17.4156 | 0 | 0 | 0 | 754.6928 | 0 | 754.6928 | 0 | 0 | 12.3916 | 1.4767 | 7.4601 | 6.6677 | 0 | 0.70531 | 1.8629 | 0 | 0 | 0 | 0 | 30.5643 | 30.5643 | 0
WY_7_RS_2016_NG | 7 | RS | NG |  |  | RetailStandalone | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 242555.8792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95151.3607 | 0 | 0 | 337707.2399 | 0 | 337707.2399 | 0 | 0 | 1693.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664.1565 | 0 | 0 | 2357.1965 | 0 | 2357.1965 | 0 | 0 | 242.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1514 | 0 | 0 | 337.7072 | 0 | 337.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8233 | 3.8535 | 0 | 0 | 13.6768 | 13.6768 | 0
WY_7_RS_2019_EL | 7 | RS | EL |  |  | RetailStandalone | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 0 | 11514.3803 | 74212.7375 | 10686.3675 | 53987.5506 | 0 | 49161.1803 | 0 | 0 | 0 | 5248.7125 | 0 | 0 | 0 | 204810.9287 | 0 | 204807.8723 | 3.0564 | 3.0564 | 0 | 1118.0463 | 7206.0568 | 1037.6463 | 5242.1912 | 0 | 4773.5506 | 0 | 0 | 0 | 509.65 | 0 | 0 | 0 | 19887.1412 | 0 | 19886.8444 | 0.29678 | 0.29678 | 0 | 39.2871 | 253.2139 | 36.4619 | 184.2055 | 0 | 167.7379 | 0 | 0 | 0 | 17.9086 | 0 | 0 | 0 | 698.8149 | 0 | 698.8045 | 0.010429 | 0.010429 | 10.2549 | 1.4767 | 7.4601 | 6.7932 | 0 | 0.72528 | 1.5911 | 0 | 0 | 0 | 0 | 28.3008 | 28.3013 | 0.00042234
WY_7_RS_2019_NG | 7 | RS | NG |  |  | RetailStandalone | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 260981.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95170.317 | 0 | 0 | 356151.761 | 0 | 356151.761 | 0 | 0 | 1821.6505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664.2888 | 0 | 0 | 2485.9393 | 0 | 2485.9393 | 0 | 0 | 260.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1703 | 0 | 0 | 356.1518 | 0 | 356.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5695 | 3.8543 | 0 | 0 | 14.4238 | 14.4238 | 0
WY_7_SH_2016_EL | 7 | SH | EL |  |  | HotelSmall | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 33392.8144 | 43115.0192 | 79041.8864 | 12295.1576 | 154949.5496 | 0 | 53337.366 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 376204.036 | 0 | 376203.4802 | 0.55571 | 0.55571 | 3242.4423 | 4186.4684 | 7674.9672 | 1193.8598 | 15045.6013 | 0 | 5179.0582 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 36529.4119 | 0 | 36529.3579 | 0.05396 | 0.05396 | 113.9363 | 147.1084 | 269.6909 | 41.9511 | 528.6879 | 0 | 181.9871 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.6082 | 0 | 1283.6063 | 0.0018961 | 0.0018961 | 6.2426 | 0.97104 | 12.2376 | 4.2125 | 0.0057056 | 0 | 3.4051 | 2.6373 | 0 | 0 | 0 | 29.7117 | 29.7118 | 4.3889e-05
WY_7_SH_2016_NG | 7 | SH | NG |  |  | HotelSmall | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 73398.9578 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 682589.4553 | 0 | 0 | 1155483.851 | 0 | 1155483.851 | 0 | 0 | 512.3247 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4764.4744 | 0 | 0 | 8065.2773 | 0 | 8065.2773 | 0 | 0 | 73.399 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 682.5895 | 0 | 0 | 1155.4839 | 0 | 1155.4839 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.699 | 15.8 | 0 | 0 | 26.7461 | 26.7461 | 0
WY_7_SH_2019_EL | 7 | SH | EL |  |  | HotelSmall | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 38619.2983 | 38716.5482 | 50897.7845 | 12295.1576 | 154949.5496 | 0 | 50055.8788 | 72.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 345606.4597 | 0 | 345605.9039 | 0.55571 | 0.55571 | 3749.9339 | 3759.3768 | 4942.1749 | 1193.8598 | 15045.6013 | 0 | 4860.4258 | 7.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 33558.3872 | 0 | 33558.3333 | 0.05396 | 0.05396 | 131.769 | 132.1009 | 173.6632 | 41.9511 | 528.6879 | 0 | 170.7907 | 0.24649 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.2092 | 0 | 1179.2073 | 0.0018961 | 0.0018961 | 4.0198 | 0.97104 | 12.2376 | 3.9533 | 0.0057056 | 0 | 3.0577 | 3.0501 | 0 | 0 | 0 | 27.2952 | 27.2952 | 4.3889e-05
WY_7_SH_2019_NG | 7 | SH | NG |  |  | HotelSmall | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 73275.7415 | 0 | 0 | 0 | 399495.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 682674.7589 | 0 | 0 | 1155445.9383 | 0 | 1155445.9383 | 0 | 0 | 511.4647 | 0 | 0 | 0 | 2788.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 4765.0698 | 0 | 0 | 8065.0126 | 0 | 8065.0126 | 0 | 0 | 73.2757 | 0 | 0 | 0 | 399.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 682.6748 | 0 | 0 | 1155.4459 | 0 | 1155.4459 | 0 | 0 | 0 | 0 | 9.2472 | 0 | 0 | 0 | 0 | 1.6961 | 15.8019 | 0 | 0 | 26.7452 | 26.7452 | 0
WY_7_SO_2016_EL | 7 | SO | EL |  |  | OfficeSmall | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 4784.6918 | 1739.3827 | 8766.3779 | 1594.8973 | 13417.6985 | 0 | 5796.0901 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 41103.3369 | 0 | 41104.1705 | -0.83357 | -0.83357 | 464.5936 | 168.8941 | 851.2153 | 154.8645 | 1302.8585 | 0 | 562.8003 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 3991.134 | 0 | 3991.215 | -0.08094 | -0.08094 | 16.3254 | 5.9348 | 29.9109 | 5.4418 | 45.7812 | 0 | 19.7763 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 140.2446 | 0 | 140.2474 | -0.0028441 | -0.0028441 | 5.4364 | 0.98906 | 8.3208 | 3.5944 | 0 | 0 | 1.0787 | 2.9672 | 3.1033 | 0 | 0 | 25.4903 | 25.4897 | -0.00051693
WY_7_SO_2016_NG | 7 | SO | NG |  |  | OfficeSmall | STD2016 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 16103.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16103.4129 | 0 | 16103.4129 | 0 | 0 | 112.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4018 | 0 | 112.4018 | 0 | 0 | 16.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.1034 | 0 | 16.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9268 | 0 | 0 | 0 | 2.9268 | 2.9268 | 0
WY_7_SO_2019_EL | 7 | SO | EL |  |  | OfficeSmall | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Electricity | 4912.5059 | 1428.1833 | 7121.4664 | 1594.8973 | 13417.6985 | 0 | 5040.32 | 0 | 0 | 0 | 0 | 5004.1986 | 0 | 0 | 38519.2699 | 0 | 38520.1035 | -0.83357 | -0.83357 | 477.0043 | 138.6766 | 691.4944 | 154.8645 | 1302.8585 | 0 | 489.4151 | 0 | 0 | 0 | 0 | 485.9077 | 0 | 0 | 3740.2211 | 0 | 3740.302 | -0.08094 | -0.08094 | 16.7615 | 4.873 | 24.2984 | 5.4418 | 45.7812 | 0 | 17.1976 | 0 | 0 | 0 | 0 | 17.0743 | 0 | 0 | 131.4277 | 0 | 131.4306 | -0.0028441 | -0.0028441 | 4.4163 | 0.98906 | 8.3208 | 3.1257 | 0 | 0 | 0.88567 | 3.0464 | 3.1033 | 0 | 0 | 23.8878 | 23.8873 | -0.00051693
WY_7_SO_2019_NG | 7 | SO | NG |  |  | OfficeSmall | STD2019 | WY-JACKSONHOLE-WY | Zone7 | Zone7(WY-JACKSONHOLE-WY) |  |  | WY | 0.0971 | 0.00698 |  |  |  | Natural Gas | 17553.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17553.5731 | 0 | 17553.5731 | 0 | 0 | 122.5239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.5239 | 0 | 122.5239 | 0 | 0 | 17.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5536 | 0 | 17.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1904 | 0 | 0 | 0 | 3.1904 | 3.1904 | 0

## Cost Eff Inputs
Commercial Energy Code Adoption Cost Effectiveness - Economic Analysis Parameters | [7 empty] | 1 | [6 empty] | For Scenario 2 energy Escalation
|  |  |  | Sc2 updated for State CE 2019 |  |  |  | 2 | Sc 3 uses a pre-tax discount rate determined from real estate industry surveys; Sc 1 uses the FEMP mandated rate for federal energy projects | [6 empty] | Elec | Gas | [9 empty] | Input Variables for Scalar Ratio Calculations, for 90.1-2022 proposals
Economic Parameter |  |  | Scenario 1 | Scenario 2 | Scenario 3 |  |  | 3 | Sc 3 uses a surveyed inflation rate per Dept Commerce; Sc 1 from NIST is netted against a federal nominal rate and the mandated discount rate | [5 empty] | Sc1 UPV | 18.295 | 19.429 | [9 empty] | No. | Input Economic Variables - Linked | Heating | Cooling
Study Period – Years1 |  |  | 30 | 30 | 40 | Scenario 2 |  | 4 | Annual prices ASHRAE SSPC 90.1 used in development of 90.1-2022 are used | [17 empty] | 1 | Economic Life - Years (1 to 50 yrs) | 40 | 40
Nominal Discount Rate2 |  |  | 0.02 | 0.0525 | 0.081 | 0.070705 | Equivalent Nominal disc pre-tax impact | [7 empty] | Scenario | 1 | 2 | [9 empty] | 2 | Down Payment - $ | 0 | 0
Real Discount Rate2 |  |  | 0.03 | 0.033382 | 0.056386 | 1.0334 | 1 - (1+DiscN)/(1+infl) | [7 empty] | Real Disc Rate | 0.03 | 0.033382 | [9 empty] | 3 | Fuel Escalation Rate - % | var | var
Inflation3 |  |  | -0.01 | 0.0185 | 0.0233 | 1.5727 | [8 empty] | Infl | -0.01 | 0.0185 | [9 empty] | 4 | Discount Rate - % | 0.081 | 0.081
Electricity Price, per kWh4 |  |  | 0.1099 | 0.1099 | 0.1099 | Data Sources: | Scenario 1 | NIST Annual Supplement for 135, 2022 | [6 empty] | Net Disc Rate | 0.040404 | 0.014612 | [9 empty] | 5 | Loan Interest Rate - % | 0.05 | 0.05
Natural Gas Price, per therm4 |  |  | 0.983 | 0.983 | 0.983 | [21 empty] | 6 | Federal Tax Rate - % | 0 | 0
Electricity and Natural Gas Price Escalation5 |  |  | Uniform present value factors | Uniform PV factors | electricity 2.25%/year |  | Scenario 3 | ASHRAE 90.1 SSPC Workplan for 90.1-2022 | [18 empty] | 7 | State Tax Rate - % | 0 | 0
|  |  | Electric 18.30, Gas 19.43 | Electric 16.58, Gas 17.61 | natural gas 2.90%/year | [21 empty] | 8 | Combined State, Fed. Tax Rate - % | 0 | 0
Loan Interest Rate6 |  |  | NA | 0.0525 | 0.05 |  | The combined tax rate is adjusted for the fact that state taxes are typically deductable from federal income | [19 empty] | 9 | Heating - Gas Price - $/Mbtu | 0.983
Federal Corporate Tax Rate7 |  |  | NA | 0.21 | NA 4 |  | While there is some allowance for federal taxes in state taxes, often it is capped, so effectively | [19 empty] | 10 | Cooling - Electric Price - $/kWh |  | 0.1099
State Corporate Tax Rate8 |  |  | NA | 0.0601 | NA 4 |  | only the state tax needs to be adjusted | [5 empty] | Scenario 1 NIST 2022 Energy Price Indices and Discount Factors for Life-Cycle Cost Analysis – 2022
Property Tax Rate |  |  |  | 0 |  |  | Ptax net of Fed Benefit |  | 0 |  |  | Scenario 3 |  | Note: NISTIR 85-3273-37 was published in May 2022 | [12 empty] | 11 | First Cost Scalar - S2
Factors above in italics are calculated for comparison purposes, but not used in the scenario. | [6 empty] | Pvalue Ptax net of Fed Benefit |  |  | 0 |  | Scalar Limit, 40 year life | [6 empty] | Set values @ 3% DR |  |  | UPV values below not used |  |  |  |  | 12 | Htg & Clg Scalars - Sh & Sc | 25.1 | 22
Scenario 3 energy escalation rates include inflation. | [11 empty] | 22.24 | Table A-1. SPV factors for finding the PV of future single costs (non-fuel) |  |  | Table Ba-5; FEMP UPV with 3.0% Discount rate; commercial values |  |  | Table A-2. UPV factors for finding the PV of future single costs (non-fuel) |  |  |  |  | below is updated for 2018 |  |  | 13 | Scalar Ratio - SR | 25.1 | 22 | 22.24 | <--- This is the weighted value. Copy into report table.
PNNL Calculated set values below | [5 empty] | Sc2 Loan Payment on $1k: | 66.9169 | 30 | year term |  |  | Loan Payment on $1k: | [11 empty] | Not used in US analysis |  |  |  |  | 0.07657 | 0.92343
| 30 Years | 40 Year |  |  | Not updated for US analysis-not used; will need update for state analysis |  | Scenario 2 Present Value of Loan and Tax Impacts for $1,000 principal |  | Combined Tax Rate | 0.25748 |  |  | DOE Present Value of Single Future Amount, 3% Real Discount (Set input) |  |  | DOE Present Value of Energy Costs with Escalation over Study Period, Commercial |  |  | DOE Present Value of Non-Energy Costs Escalating at Inflation Rate over Study Period, Commercial (set values) |  |  | DOE Present Value of Non-Energy Costs with no Escalation for Inflation over Study Period, Commercial |  | Scenario 2 Present Value of Energy Costs with Escalation over Study Period, Commercial |  |  |  | Life cycle cost LCC sheet calculation outline: | Note 'Name' indicates a worksheet name according to Excel naming protocol
Replacement Year | Residual Value Factors for Linear Pro-Rating of Initial Cost* |  |  |  | Scenario 2 Present Value of Single Future Amount, Scalar Real Discount | Scenario 2 Present Value of Single Future Amount, Scalar Nominal Discount | PV of Loan Payments | PV of Interest Payments | PV of Interest Deduction | PV of Depreciation Deduction | Scenario 3 Present Value of Single Future Amount, Scalar Real Discount | Scenario 3 Present Value of Single Future Amount, Scalar Nominal Discount | Year | UPV, NIST |  | Year | Electric UPV, NIST | Gas UPV, NIST | Year | UPV, NIST, DR=3.0% | Scenario 2, UPV, DR=3.3% | Year | UPV, NIST | Year | Electric UPV, NIST | Gas UPV, NIST | I. | LCCA Calculations - Scenario 1 (all costs in LCC calc are incremental costs for 90.1-2013 minus 90.1-2010) | see LCC_Results range at LCC!$B$43:$AF$49
1 | 0 | 0 |  |  | 0.9677 | 0.95012 | 63.579 | 49.8812 | 12.8434 | 8.1545 | 0.94662 | 0.92507 | 1 | 0.971 |  | 1 | 0.952 | 0.957 | 1 | 0.971 | 0.9677 | 1 | 0.96 | 1 | 0.94876 | 0.95374 |  | A First cost, net present value equals incremental costs | 1. Values located in 'LCC' First Cost Row 44
2 | 0 | 0 |  |  | 0.93644 | 0.90273 | 60.4076 | 46.7098 | 12.0268 | 7.7478 | 0.8961 | 0.85575 | 2 | 0.943 |  | 2 | 1.851 | 1.855 | 2 | 1.91 | 1.9041 | 2 | 1.89 | 2 | 1.8381 | 1.8421 |  | 1. First Cost in 'LCC' Row 44 | a. From 'LCC' Row 7 in 30 year cost listings on this sheet
3 | 0 | -0.66667 |  |  | 0.90618 | 0.8577 | 57.3944 | 43.6966 | 11.251 | 7.3613 | 0.84827 | 0.79163 | 3 | 0.915 |  | 3 | 2.715 | 2.707 | 3 | 2.83 | 2.8103 | 3 | 2.78 | 3 | 2.6888 | 2.6809 |  | 2. 'LCC' Row 7 First Cost Totals sections in 'Cost Est Summary 30 Year' | a. New Construction in Totals section of prototype/climate location cost tables in 'Cost Est Summary
4 | -0.5 | 0 |  |  | 0.87691 | 0.81491 | 54.5315 | 40.8337 | 10.5138 | 6.9941 | 0.80299 | 0.73231 | 4 | 0.888 |  | 4 | 3.552 | 3.529 | 4 | 3.72 | 3.6872 | 4 | 3.64 | 4 | 3.5076 | 3.4849 |  |  | Example: Small Office, climate zone 2A value 428.3
5 | 0 | 0 |  |  | 0.84858 | 0.77426 | 51.8114 | 38.1136 | 9.8135 | 6.6452 | 0.76013 | 0.67744 | 5 | 0.863 |  | 5 | 4.364 | 4.33 | 5 | 4.58 | 4.5358 | 5 | 4.46 | 5 | 4.2911 | 4.2577 |  |  | i. '=VLOOKUP($B7,Ttl_30_Sm_Off,7,FALSE)
6 | 0 | -0.33333 |  |  | 0.82117 | 0.73564 | 49.227 | 35.5292 | 9.148 | 6.3138 | 0.71955 | 0.62668 | 6 | 0.837 |  | 6 | 5.153 | 5.116 | 6 | 5.42 | 5.357 | 6 | 5.25 | 6 | 5.0555 | 5.0192 |  |  | ii. $B7 is cost item, New Construction
7 | -0.71429 | -0.28571 |  |  | 0.79464 | 0.69895 | 46.7715 | 33.0737 | 8.5158 | 5.9988 | 0.68115 | 0.57972 | 7 | 0.813 |  | 7 | 5.921 | 5.891 | 7 | 6.23 | 6.1516 | 7 | 6.02 | 7 | 5.7873 | 5.758 |  |  | iii. Ttl_30_Sm_Off = 'Example 'Cost Est Summary 30 Year'!$N$77:$X$110
8 | -0.25 | 0 |  |  | 0.76897 | 0.66408 | 44.4385 | 30.7407 | 7.9151 | 5.6996 | 0.64479 | 0.53628 | 8 | 0.789 |  | 8 | 6.666 | 6.652 | 8 | 7.02 | 6.9206 | 8 | 6.75 | 8 | 6.4968 | 6.4832 |  |  | iv. Column 7 is the climate zone 2A costs, and New Construction data is in cell T78
9 | -0.66667 | -0.55556 |  |  | 0.74413 | 0.63096 | 42.2218 | 28.524 | 7.3443 | 5.4153 | 0.61037 | 0.4961 | 9 | 0.766 |  | 9 | 7.392 | 7.409 | 9 | 7.79 | 7.6647 | 9 | 7.46 | 9 | 7.181 | 7.1975 |  | 3. Total New Construction Cost in 'Cost Est Summary 30 Years' | a. Sum of HVAC, Lighting, and Envelope Power Other costs in same tables
10 | 0 | 0 |  |  | 0.72009 | 0.59949 | 40.1158 | 26.418 | 6.8021 | 5.1452 | 0.57779 | 0.45893 | 10 | 0.744 |  | 10 | 8.096 | 8.151 | 10 | 8.53 | 8.3848 | 10 | 8.14 | 10 | 7.8359 | 7.8891 |  |  | Example: Small Office, climate zone 2A value 428.3 in cell T78 = C78+H78+O78
11 | -0.27273 | -0.36364 |  |  | 0.69683 | 0.56958 | 38.1147 | 24.4169 | 6.2868 | 4.8885 | 0.54695 | 0.42454 | 11 | 0.722 |  | 11 | 8.782 | 8.879 | 11 | 9.25 | 9.0817 | 11 | 8.79 | 11 | 8.4759 | 8.5695 |  | 4. New Construction Costs in C78, H78, and O7 | a. Looked up in: HVAC, Lighting, and Power Envelope
12 | -0.5 | -0.66667 |  |  | 0.67432 | 0.54117 | 36.2135 | 22.5157 | 5.7973 | 4.6447 | 0.51776 | 0.39273 | 12 | 0.701 |  | 12 | 9.451 | 9.591 | 12 | 9.95 | 9.756 | 12 | 9.42 | 12 | 9.0913 | 9.226 |  |  | i. 'HVAC <Prototype> Proto' cost summary tables by climate zone
13 | -0.69231 | -0.92308 |  |  | 0.65254 | 0.51418 | 34.4071 | 20.7093 | 5.3322 | 4.413 | 0.49012 | 0.3633 | 13 | 0.681 |  | 13 | 10.096 | 10.279 | 13 | 10.63 | 10.4085 | 13 | 10.03 | 13 | 9.674 | 9.8494 |  |  | ii. 'Int Ltg LPD Proto' doesn't vary by climate zone, so results all in one prototype table
14 | -0.85714 | -0.14286 |  |  | 0.63146 | 0.48853 | 32.6909 | 18.9931 | 4.8903 | 4.1929 | 0.46396 | 0.33608 | 14 | 0.661 |  | 14 | 10.719 | 10.946 | 14 | 11.3 | 11.04 | 14 | 10.61 | 14 | 10.2399 | 10.4568 |  |  | iii. 'Env Pow Other Comp Costs' doesn't vary by climate zone, so results all in one prototype table (one exception for small office 4A which includes vestibule)
15 | 0 | -0.33333 |  |  | 0.61106 | 0.46416 | 31.0602 | 17.3624 | 4.4705 | 3.9837 | 0.4392 | 0.3109 | 15 | 0.642 |  | 15 | 11.321 | 11.596 | 15 | 11.94 | 11.651 | 15 | 11.17 | 15 | 10.7754 | 11.0372 |  |  | b. Example: Small Office, climate zone 2A Mechanical Cost, value -2,129
16 | -0.125 | -0.5 |  |  | 0.59132 | 0.44101 | 29.5109 | 15.8131 | 4.0715 | 3.785 | 0.41575 | 0.2876 | 16 | 0.623 |  | 16 | 11.9 | 12.229 | 16 | 12.56 | 12.2424 | 16 | 11.71 | 16 | 11.2949 | 11.6072 |  |  | i. =VLOOKUP($B78,M_Sm_Off_2A,8,FALSE)
17 | -0.23529 | -0.64706 |  |  | 0.57222 | 0.41901 | 28.0389 | 14.3411 | 3.6925 | 3.5962 | 0.39356 | 0.26605 | 17 | 0.605 |  | 17 | 12.462 | 12.845 | 17 | 13.17 | 12.8146 | 17 | 12.23 | 17 | 11.7868 | 12.149 |  |  | ii. $B78 is cost item, New Construction
18 | -0.33333 | -0.77778 |  |  | 0.55373 | 0.39811 | 26.6402 | 12.9424 | 3.3324 | 3.4168 | 0.37256 | 0.24611 | 18 | 0.587 |  | 18 | 13.006 | 13.445 | 18 | 13.75 | 13.3683 | 18 | 12.73 | 18 | 12.2689 | 12.683 |  |  | iii. M_Sm_Off_2A is summary cost table in 'HVAC Small Office Proto'
19 | -0.42105 | -0.89474 |  |  | 0.53585 | 0.37825 | 25.3114 | 11.6136 | 2.9903 | 3.2464 | 0.35267 | 0.22767 | 19 | 0.57 |  | 19 | 13.532 | 14.028 | 19 | 14.32 | 13.9042 | 19 | 13.21 | 19 | 12.7212 | 13.1874 |  |  | iv. Column is the climate zone 2A small office incremental costs, and New Construction data is in cell O39
20 | -0.5 | 0 |  |  | 0.51854 | 0.35938 | 24.0488 | 10.351 | 2.6652 | 3.0845 | 0.33385 | 0.21061 | 20 | 0.554 |  | 20 | 14.041 | 14.594 | 20 | 14.88 | 14.4227 | 20 | 13.67 | 20 | 13.1422 | 13.6598 |  | 5. New Construction incremental costs in summary tables in prototype cost summary sheets | a. Value in incremental costs column found from difference in 90.1-2013 and 90.1-2010 costs in summary cost sheets
21 | -0.57143 | -0.095238 |  |  | 0.50178 | 0.34146 | 22.8492 | 9.1514 | 2.3563 | 2.9306 | 0.31603 | 0.19483 | 21 | 0.538 |  | 21 | 14.534 | 15.143 | 21 | 15.42 | 14.9245 | 21 | 14.11 | 21 | 13.5557 | 14.1237 |  |  | b. Example: Small Office, climate zone 2A Incremental cost cell O39, value -2,129
22 | -0.63636 | -0.18182 |  |  | 0.48558 | 0.32442 | 21.7095 | 8.0117 | 2.0628 | 2.7844 | 0.29916 | 0.18023 | 22 | 0.522 |  | 22 | 15.008 | 15.676 | 22 | 15.94 | 15.4101 | 22 | 14.54 | 22 | 13.9608 | 14.5821 |  |  | i. 90.1-2013 New Construction cell N39 - 90.1-2010 New Construction cell J39
23 | -0.69565 | -0.26087 |  |  | 0.46989 | 0.30824 | 20.6266 | 6.9288 | 1.784 | 2.6455 | 0.28319 | 0.16673 | 23 | 0.507 |  | 23 | 15.467 | 16.193 | 23 | 16.44 | 15.8799 | 23 | 14.95 | 23 | 14.3349 | 15.0077 |  | 6. New Construction 90.1-2013 and 90.1-2010 costs | a. Values are summed up from costs above, or to the left of the summary tables
24 | -0.75 | -0.33333 |  |  | 0.45471 | 0.29287 | 19.5977 | 5.8999 | 1.5191 | 2.5136 | 0.26807 | 0.15424 | 24 | 0.492 |  | 24 | 15.912 | 16.696 | 24 | 16.94 | 16.3346 | 24 | 15.35 | 24 | 14.706 | 15.4306 |  |  | b. Example: Small Office, climate zone 2A Mechanical Cost, value -2,129
25 | -0.8 | -0.4 |  |  | 0.44002 | 0.27826 | 18.6202 | 4.9224 | 1.2674 | 2.3882 | 0.25377 | 0.14268 | 25 | 0.478 |  | 25 | 16.342 | 17.184 | 25 | 17.41 | 16.7747 | 25 | 15.73 | 25 | 15.0436 | 15.8187 |  |  | i. Sum for system level costs for 90.2010 Costs, Total New Construction, N11 to N31 (marked with x in hidden column a)
26 | -0.84615 | -0.46154 |  |  | 0.42581 | 0.26438 | 17.6914 | 3.9936 | 1.0283 | 2.2691 | 0.24022 | 0.13199 | 26 | 0.464 |  | 26 | 16.759 | 17.659 | 26 | 17.88 | 17.2005 | 26 | 16.1 | 26 | 15.3795 | 16.2054 |  |  | ii. Sum for system level costs for 90.2010 Costs, Total New Construction, J11 to J31 (marked with x in hidden column a)
27 | -0.88889 | -0.51852 |  |  | 0.41205 | 0.25119 | 16.8089 | 3.1111 | 0.80104 | 2.1559 | 0.2274 | 0.1221 | 27 | 0.45 |  | 27 | 17.163 | 18.121 | 27 | 18.83 | 17.6125 | 27 | 16.45 | 27 | 15.7156 | 16.5928
28 | -0.92857 | -0.57143 |  |  | 0.39874 | 0.23866 | 15.9704 | 2.2726 | 0.58516 | 2.0483 | 0.21526 | 0.11295 | 28 | 0.437 |  | 28 | 17.552 | 18.57 | 28 | 18.76 | 18.0113 | 28 | 16.79 | 28 | 16.0153 | 16.9442 |  | B. Replacement, net present value of each year of replacement costs | 1. Values located in 'LCC' First Cost Row 45
29 | -0.96552 | -0.62069 |  |  | 0.38586 | 0.22676 | 15.1738 | 1.476 | 0.38005 | 1.9462 | 0.20377 | 0.10449 | 29 | 0.424 |  | 29 | 17.929 | 19.006 | 29 | 19.19 | 18.3971 | 29 | 17.11 | 29 | 16.3162 | 17.2963 |  |  | a. Value from DOE uniform present value factor for present value (UPV) of an annuity with same value every year, escalated by general inflation rate
30 | 0 | -0.66667 |  |  | 0.37339 | 0.21545 | 14.4169 | 0.71913 | 0.18516 | 1.8491 | 0.19289 | 0.096656 | 30 | 0.412 |  | 30 | 18.295 | 19.429 | 30 | 19.6 | 18.7705 | 30 | 17.43 | 30 | 16.5807 | 17.6084 |  |  | b. Example: Small Office, climate zone 2A Incremental cost cell C45, value 2,572
31 | -0.032258 | -0.70968 |  |  | 0.36133 | 0.2047 |  |  |  |  | 0.1826 | 0.089414 |  |  |  | i | 18.8804 | 20.8997 | [6 empty] | SC2_Elec_PVA_30 | SC2_Gas_PVA_30 |  |  | i. =SUMPRODUCT(C13:C42,DOE_PV_F), product of each year's replacement cost by present value factors for each year
32 | -0.0625 | -0.75 |  |  | 0.34966 | 0.19449 |  |  |  |  | 0.17285 | 0.082714 |  |  |  | 3 | 0.032922 | 0.02511 | [10 empty] | ii. DOE_PV_F = 'Cost Eff Inputs' O37, UPV for 30 years
33 | -0.090909 | -0.78788 |  |  | 0.33836 | 0.18479 |  |  |  |  | 0.16363 | 0.076516 |  |  |  | P/A = [(1+i)n-1]/[i(1+i)n] | [12 empty] | 2. Incremental replacement looked up by same process as new construction costs for each year of 30 years costs
34 | -0.11765 | -0.82353 |  |  | 0.32743 | 0.17557 |  |  |  |  | 0.15489 | 0.070783 |  |  |  | Table Ba-5. FEMP UPV* Discount Factors adjusted for fuel price escalation, by end-use sector and fuel type.
35 | -0.14286 | -0.85714 |  |  | 0.31686 | 0.16681 |  |  |  |  | 0.14662 | 0.065479
36 | -0.16667 | -0.88889 |  |  | 0.30662 | 0.15849 |  |  |  |  | 0.1388 | 0.060572 | [15 empty] | C. Maintenance, net present value of annual maintenance | 1. Values located in 'LCC' First Cost Row 46
37 | -0.18919 | -0.91892 |  |  | 0.29672 | 0.15059 |  |  |  |  | 0.13139 | 0.056034 | [16 empty] | a. Value from DOE uniform present value factor for present value (UPV) of an annuity with same value every year, escalated by general inflation rate
38 | -0.21053 | -0.94737 |  |  | 0.28713 | 0.14307 |  |  |  |  | 0.12438 | 0.051835 | [16 empty] | b. Example: Small Office, climate zone 2A Incremental cost cell C46, value 0
39 | -0.23077 | -0.97436 |  |  | 0.27786 | 0.13594 |  |  |  |  | 0.11774 | 0.047951 | [16 empty] | i. =C8*DOE_PVA_Maint
40 | -0.25 | 0 |  |  | 0.26888 | 0.12916 |  |  |  |  | 0.11145 | 0.044358 | [16 empty] | ii. DOE_PVA_Maint = 'Cost Eff Inputs' O37, UPV for 30 years
* Proportion of first cost as a credit for useful life remaining at year 30 | [6 empty] | SC2_PV_LoanP | SC2_PV_Int | SC2_PV_IntD | SC2_PV_Depr | [18 empty] | 2. Incremental annual maintenance looked up by same process as new construction costs
Note: Replacements with periods beyond analysis period | [5 empty] | Present Values per k$ | 1000 | 589.066 | 151.6721 | 128.258 |  | Present Values per k$
represent residual value at end of analysis period | [27 empty] | D. Incremental energy costs, present value annual cost | 1. Values located in 'LCC' First Cost Row 46
a. Value from DOE uniform present value factor for present value (UPV) of an annuity with varying escalation every year
b. Example: Small Office, climate zone 2A Incremental cost cell C47, value -17,246
i. =-C9*DOE_Electric_PVA_30-C10*DOE_Gas_PVA_30
ii. DOE_Electric_PVA_30 = 'Cost Eff Inputs' K37, UPV for 30 years
iii. DOE_Gas_PVA_30 = 'Cost Eff Inputs' L37, UPV for 30 years
2. Incremental annual maintenance looked up by same process as new construction costs
[28 empty] | E. Net Present Value | 1. Sum of present values for first cost, maintenance, replacements and energy
b. Example: Small Office, climate zone 2A Incremental cost cell C47, value -14,246
i. =SUM(C44:C47)
[27 empty] | II. | Scalar Method | Cost lookups very similar to LCC, except uses 'Cost Est Summary 40 Year'
see Scalar_Results range at 'Scalar'!$B$53:$AF$60
[28 empty] | A. First Cost as is | 1. 'Scalar' row 54
[28 empty] | B. Replacement NPV | 2. 'Scalar' row 55
a. net present value of the 'Scalar' costs over 40 years
i. =SUMPRODUCT(C13:C52,Sca_PV_F) , product of each year's replacement cost by present value factors for each year
ii. Sca_PV_F table for 40 years of present values at ='Cost Eff Inputs'!$D$8:$D$47
[28 empty] | C. Maintenance, just the annual amount | 1. 'Scalar' row 56
[28 empty] | D. Energy cost savings, just the annual amount | 1. 'Scalar' row 57
[28 empty] | E. Scalar Ratio | 1. 'Scalar' row 58
a. First Cost plus Replacement Cost NPV / (Energy Cost Savings - Maintenance Cost)
[28 empty] | F. Scalar Ratio Limit | 1. 'Scalar' row 59, from 90.1-2010 approved value
[28 empty] | G. Result, if scalar ratio is less than scalar ratio limit, is cost effective | 1. 'Scalar' row 60
[27 empty] | III. | Simple Payback | 1. 'Scalar' row 61

## LCC Sc 1
Commercial Energy Code Adoption Cost Effectiveness - LCC Savings Calculation - Scenario 1 | [9 empty] | US National
[26 empty] | 7 | 8 | 9 | 10 | 11
LCC of incremental costs for Scenario 1 without loans or taxes
| Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Maintenance | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0
Electricity Cost Savings | 520.5291 | 485.9106 | 501.7546 | 503.2199 | 531.916 | 77322.8931 | 74089.513 | 75995.1179 | 69367.5679 | 69561.175 | 6261.3389 | 5990.1911 | 5670.3211 | 5488.6808 | 5007.9904 | 11426.0894 | 9895.5487 | 10175.5495 | 8466.2076 | 8008.0162 | 8178.9718 | 6994.0055 | 7573.7891 | 7148.8729 | 7332.1923 | 6315.373 | 5664.704 | 6153.301 | 5522.5361 | 5292.0819
Gas Cost Savings | 0 | 0.55902 | -0.09317 | 4.4722 | 16.8638 | 72.8593 | 359.8242 | 426.2547 | 1600.4815 | 2703.5262 | 68.5734 | 366.0666 | 228.0812 | 1010.5264 | 1537.6847 | -38.7589 | 426.8137 | 191.6516 | 1032.5146 | 1930.2117 | 1262.2729 | 1566.9402 | 1423.1782 | 1932.1682 | 2176.7406 | -0.65219 | -21.1497 | -6.1492 | 321.5311 | 623.776
Total Energy Cost Savings | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
Replacement | [26 empty] | MRA
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902 | 0 | 0 | 0 | 0 | 0 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Life Cycle Costs (LCC)
First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Replacement, PV | -493.5219 | -426.4263 | -446.9562 | -513.1546 | -277.6707 | 100577.3406 | -15582.0031 | -18845.427 | -12654.3015 | -10726.297 | -680.2641 | 815.0432 | 635.9498 | 224.278 | -294.2501 | 1303.0943 | 1090.0328 | -1666.9204 | -6460.0917 | -6058.3263 | 3157.977 | 3173.1366 | 3191.4431 | 145.9598 | 348.2154 | -21778.889 | -22071.8013 | -25999.0555 | -32027.9057 | -30679.1394
Maintenance, PV | 0 | 0 | 0 | 0 | 0 | 7840 | 7840 | 7840 | 7840 | 7840 | 0 | 2642.924 | 2642.924 | 2642.924 | 2642.924 | 7801.3732 | 7795.8551 | 7828.9638 | 7646.866 | 7646.866 | 5247.2213 | 5252.7394 | 5236.185 | -38.6268 | -49.663 | 0 | 0 | 0 | 0 | 0
Energy Cost Increase | -9523.0807 | -8900.5965 | -9177.7895 | -9293.2979 | -10059.051 | -1416037.9124 | -1362458.6639 | -1398612.385 | -1300175.4095 | -1325148.5069 | -115883.5076 | -116702.8546 | -108169.9136 | -120048.9327 | -121496.8596 | -208287.2589 | -189331.6273 | -189885.2762 | -174949.9951 | -184008.7386 | -174158.9883 | -158399.4117 | -166213.4008 | -168328.7271 | -176434.3502 | -115527.078 | -103224.8417 | -112455.169 | -107281.8263 | -108937.982
LCC (net costs)* | -6784.4434 | -6212.6212 | -6434.7185 | -5250.1089 | -5268.144 | -466341.5555 | -803808.8737 | -857002.2787 | -715584.9381 | -743133.118 | -87307.64 | -82241.5292 | -74763.373 | -85438.3905 | -90861.5717 | -100793.2037 | -80647.6133 | -89031.395 | -72600.8128 | -80093.9057 | -93617.24 | -80573.678 | -89337.7925 | -99607.3127 | -107474.9775 | -104708.6253 | -93013.8543 | -110271.009 | -112356.7327 | -111277.642
LCC Cost Effective | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
* If LCC <=0 then the project is cost effective. In the report this indicator is shown as "Life Cycle Cost Net Savings," so the sign is reversed and cost effectiveness is indicated by LCC NPV Savings >= 0.
| Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
Simple Payback | 6.2 | 6.4 | 6.4 | 9 | 9.2 | 10.8 | 7.6 | 7.2 | 8.3 | 8 | 4.6 | 4.8 | 5 | 4.8 | 4.2 | 8.3 | 9.3 | 8.8 | 10.2 | 9.9 | 7.4 | 7.9 | 7.4 | 7.6 | 7.2 | 5.2 | 5.7 | 4.6 | 4.6 | 4.8
LCC Net Savings/sf | 1.23 | 1.13 | 1.17 | 0.95 | 0.96 | 0.94 | 1.61 | 1.72 | 1.44 | 1.49 | 3.54 | 3.33 | 3.03 | 3.46 | 3.68 | 1.36 | 1.09 | 1.2 | 0.98 | 1.08 | 2.17 | 1.87 | 2.07 | 2.31 | 2.49 | 3.1 | 2.76 | 3.27 | 3.33 | 3.3
Floor area, sf | 5502 | 5502 | 5502 | 5502 | 5502 | 498588 | 498588 | 498588 | 498588 | 498588 | 24692 | 24692 | 24692 | 24692 | 24692 | 73959 | 73959 | 73959 | 73959 | 73959 | 43202 | 43202 | 43202 | 43202 | 43202 | 33741 | 33741 | 33741 | 33741 | 33741
Annual Energy Sav/sf | 0.095 | 0.088 | 0.091 | 0.092 | 0.1 | 0.155 | 0.149 | 0.153 | 0.142 | 0.145 | 0.256 | 0.257 | 0.239 | 0.263 | 0.265 | 0.154 | 0.14 | 0.14 | 0.128 | 0.134 | 0.219 | 0.198 | 0.208 | 0.21 | 0.22 | 0.187 | 0.167 | 0.182 | 0.173 | 0.175
SIR (savings to investment ratio) | 3.4773 | 3.3113 | 3.3458 | 2.2985 | 2.0996 | 1.4951 | 2.4593 | 2.6056 | 2.2407 | 2.2943 | 4.0553 | 3.5847 | 3.4303 | 3.6727 | 4.2459 | 2.011 | 1.7994 | 1.9571 | 1.7666 | 1.832 | 2.2433 | 2.1102 | 2.247 | 2.4486 | 2.5574 | 10.6787 | 10.1092 | 51.4867 | Infinite | Infinite
| TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Replacement, PV/sf | -0.089699 | -0.077504 | -0.081235 | -0.093267 | -0.050467 | 0.20172 | -0.031252 | -0.037798 | -0.02538 | -0.021513 | -0.02755 | 0.033008 | 0.025755 | 0.009083 | -0.011917 | 0.017619 | 0.014738 | -0.022538 | -0.087347 | -0.081915 | 0.073098 | 0.073449 | 0.073873 | 0.0033785 | 0.0080602 | -0.64547 | -0.65415 | -0.77055 | -0.94923 | -0.90925
Local Cost Location Price Index of |  | 1 | IS NOT applied on this sheet below! It is applied on "Cost Est Summaray tab" and costs above and on LCC are taken from there!!! - Note that if Cost Est is updated or changed, below should be too!
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Small Office |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Small Office; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | -1155.8408 | -1273.5984 | -1197.9729 | -1591.6563 | -1079.4222 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 4388 | 4388 | 4388 | 6148 | 6148 | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778
Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large Office |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Large Office; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 240685.0162 | -34202.2068 | -47978.4667 | -39447.227 | -43950.3141 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 600594 | 600594 | 600594 | 628852 | 628852 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859
Maintenance | 400 | 400 | 400 | 400 | 400 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902
Standalone Retail |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Standalone Retail; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | -6331.8683 | -4584.6419 | -5460.3332 | -6947.6598 | -10404.3859 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 35588 | 35588 | 35588 | 38691 | 38691 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141
Maintenance | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Primary School |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Primary School; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 3893.5877 | 5302.1261 | 195.8378 | -16126.592 | -14962.7068 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 94496 | 94496 | 94496 | 117289 | 117289 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932
Maintenance | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572
Small Hotel |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Small Hotel; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 2417.55 | 2841.8577 | 1889.9802 | -2100.9186 | -2054.1797 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 69719 | 66558 | 66558 | 70715 | 70715 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203
Maintenance | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mid-rise Apartment |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Mid-rise Apartment; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 0 | 0 | 0 | 0 | 0 | 9858 | 9858 | 9858 | 9858 | 9858 |  | New Construction | 45405 | 45405 | 45405 | 50460 | 50460 | 55263 | 55263 | 55263 | 60318 | 60318
Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LCC Sc 2 (hidden)
State Commercial Energy Code Adoption Cost Effectiveness - LCC Savings Calculation - Scenario 2 | [10 empty] | US National |  |  | Tax deduct override applied to savings: |  |  | 0 | 0 | vs. combined tax rate of: |  | 0.25748
[14 empty] | Note - S1 = W1 when using methodology for states for 90.1-2013 and later | [11 empty] | 7 | 8 | 9 | 10 | 11
LCC of incremental costs for Scenario 2 with loans and taxes |  |  |  |  | 0 0
| Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Maintenance | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0
Electricity Cost Savings | 520.5291 | 485.9106 | 501.7546 | 503.2199 | 531.916 | 77322.8931 | 74089.513 | 75995.1179 | 69367.5679 | 69561.175 | 6261.3389 | 5990.1911 | 5670.3211 | 5488.6808 | 5007.9904 | 11426.0894 | 9895.5487 | 10175.5495 | 8466.2076 | 8008.0162 | 8178.9718 | 6994.0055 | 7573.7891 | 7148.8729 | 7332.1923 | 6315.373 | 5664.704 | 6153.301 | 5522.5361 | 5292.0819
Gas Cost Savings | 0 | 0.55902 | -0.09317 | 4.4722 | 16.8638 | 72.8593 | 359.8242 | 426.2547 | 1600.4815 | 2703.5262 | 68.5734 | 366.0666 | 228.0812 | 1010.5264 | 1537.6847 | -38.7589 | 426.8137 | 191.6516 | 1032.5146 | 1930.2117 | 1262.2729 | 1566.9402 | 1423.1782 | 1932.1682 | 2176.7406 | -0.65219 | -21.1497 | -6.1492 | 321.5311 | 623.776
Total Energy Cost Savings | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
Replacement
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902 | 0 | 0 | 0 | 0 | 0 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LCC Savings
First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Replacement | -469.7376 | -405.8755 | -425.416 | -488.4242 | -264.289 | 96015.3237 | -14697.0798 | -17823.8915 | -11899.4351 | -10062.31 | -647.4802 | 775.7638 | 605.3015 | 213.4693 | -280.0693 | 1255.9414 | 1060.7097 | -1565.8848 | -6126.9658 | -5742.098 | 3005.7847 | 3020.2137 | 3037.6379 | 138.9255 | 331.4338 | -20729.2995 | -21008.0955 | -24746.0836 | -30484.3855 | -29200.6203
Maintenance | 0 | 0 | 0 | 0 | 0 | 7508.2088 | 7508.2088 | 7508.2088 | 7508.2088 | 7508.2088 | 0 | 2531.0747 | 2531.0747 | 2531.0747 | 2531.0747 | 7471.2167 | 7465.9321 | 7497.6396 | 7323.2483 | 7323.2483 | 5025.1572 | 5030.4418 | 5014.5881 | -36.9921 | -47.5613 | 0 | 0 | 0 | 0 | 0
Property Tax (Net) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loan Payments | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Interest Tax Deduct | -490.2285 | -472.3679 | -483.8382 | -691.0704 | -768.762 | -127598.5818 | -85905.8507 | -83816.376 | -89396.2784 | -88713.2856 | -4437.3399 | -4702.3454 | -4569.5274 | -4814.5801 | -4290.2911 | -14922.9585 | -15136.5945 | -14362.1129 | -15343.5181 | -15520.047 | -10941.1043 | -10526.0244 | -10381.6511 | -10406.844 | -10413.933 | -4944.1083 | -4896.3994 | -4274.6084 | -4088.0189 | -4298.3092
Deprecation Tax Deduct | -414.5503 | -399.447 | -409.1466 | -584.3876 | -650.0857 | -107900.7801 | -72644.2894 | -70877.3736 | -75595.8886 | -75018.3316 | -3752.3335 | -3976.4293 | -3864.1149 | -4071.3379 | -3627.9851 | -12619.2536 | -12799.91 | -12144.9875 | -12974.8901 | -13124.1677 | -9252.091 | -8901.0883 | -8779.0023 | -8800.3062 | -8806.3008 | -4180.8705 | -4140.5265 | -3614.7234 | -3456.9383 | -3634.7655
Energy Cost Post Tax | -8630.7416 | -8066.5858 | -8317.8051 | -8422.4901 | -9116.49 | -1283351.2263 | -1234792.5022 | -1267558.5193 | -1178345.3619 | -1200978.4107 | -105024.901 | -105767.4729 | -98034.0922 | -108800.0142 | -110112.2664 | -188770.1642 | -171590.7279 | -172092.4984 | -158556.6946 | -166766.6086 | -157839.8073 | -143556.9468 | -150638.7434 | -152555.8578 | -159901.9615 | -104701.8699 | -93552.3873 | -101917.8072 | -97229.2211 | -98730.1904
LCC (-Savings) | -6773.0988 | -6229.8747 | -6446.1788 | -5630.0286 | -5731.0489 | -574048.0395 | -834139.7201 | -879952.4182 | -758323.9822 | -782362.4432 | -84605.9228 | -80136.051 | -73203.6916 | -83198.048 | -87492.9231 | -109195.6305 | -91202.4645 | -97976.0062 | -84516.4123 | -91503.3799 | -97865.5107 | -85533.5462 | -93299.1907 | -103046.9931 | -110177.5023 | -101958.8064 | -91314.62 | -106370.0071 | -108305.5645 | -107524.4061
LCC Cost Effective | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Simple Payback | 6.2 | 6.4 | 6.4 | 9 | 9.2 | 10.8 | 7.6 | 7.2 | 8.3 | 8 | 4.6 | 4.8 | 5 | 4.8 | 4.2 | 8.3 | 9.3 | 8.8 | 10.2 | 9.9 | 7.4 | 7.9 | 7.4 | 7.6 | 7.2 | 5.2 | 5.7 | 4.6 | 4.6 | 4.8
LCC Savings/sf | 1.23 | 1.13 | 1.17 | 1.02 | 1.04 | 1.15 | 1.67 | 1.76 | 1.52 | 1.57 | 3.43 | 3.25 | 2.96 | 3.37 | 3.54 | 1.48 | 1.23 | 1.32 | 1.14 | 1.24 | 2.27 | 1.98 | 2.16 | 2.39 | 2.55 | 3.02 | 2.71 | 3.15 | 3.21 | 3.19
Floor area, sf | 5502 | 5502 | 5502 | 5502 | 5502 | 498588 | 498588 | 498588 | 498588 | 498588 | 24692 | 24692 | 24692 | 24692 | 24692 | 73959 | 73959 | 73959 | 73959 | 73959 | 43202 | 43202 | 43202 | 43202 | 43202 | 33741 | 33741 | 33741 | 33741 | 33741
Energy Cost needs to be calculated from scenario 2 annual escalation (present value of an annuity), or calculate UPV for the scenario 2 escalation rate
If negtive 1st cost - do negative loan as this is a reductionof the loan effects | [30 empty] | min | avg | max
BCR | 3.0955 | 3.0003 | 3.0207 | 2.2356 | 2.1307 | 1.6824 | 2.4727 | 2.5923 | 2.2866 | 2.3376 | 3.8919 | 3.5848 | 3.4298 | 3.621 | 4.0931 | 2.1098 | 1.9139 | 2.0347 | 1.8355 | 1.8942 | 2.3567 | 2.2325 | 2.3631 | 2.5018 | 2.6047 | 4.1278 | 3.8286 | 4.7742 | 5.0183 | 4.7942 | 1.6824 | 2.9288 | 5.0183
| TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Replacement PV/sf | -0.085376 | -0.073769 | -0.07732 | -0.088772 | -0.048035 | 0.19257 | -0.029477 | -0.035749 | -0.023866 | -0.020182 | -0.026222 | 0.031418 | 0.024514 | 0.0086453 | -0.011343 | 0.016982 | 0.014342 | -0.021172 | -0.082843 | -0.077639 | 0.069575 | 0.069909 | 0.070312 | 0.0032157 | 0.0076717 | -0.61437 | -0.62263 | -0.73341 | -0.90348 | -0.86543
SIR (savings to investment ratio) | 3.1243 | 2.9782 | 3.0087 | 2.0705 | 1.8976 | 1.3612 | 2.2246 | 2.3562 | 2.0274 | 2.0762 | 3.6711 | 3.2486 | 3.1075 | 3.3254 | 3.8413 | 1.8194 | 1.6273 | 1.7674 | 1.5913 | 1.6508 | 2.0337 | 1.9128 | 2.0371 | 2.2194 | 2.3184 | 8.8222 | 8.2976 | 29.652 | Infinite | Infinite
State Cost Location Index |  | 1 | IS NOT applied on this sheet below! It is applied on "Cost Est Summaray tab" and costs above and on LCC are taken from there!!! - Note that if Cost Est is updated or changed, below should be too!
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Small Office |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Small Office; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | -1155.8408 | -1273.5984 | -1197.9729 | -1591.6563 | -1079.4222 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 4388 | 4388 | 4388 | 6148 | 6148 | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778
Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large Office |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Large Office; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 240685.0162 | -34202.2068 | -47978.4667 | -39447.227 | -43950.3141 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 600594 | 600594 | 600594 | 628852 | 628852 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859
Maintenance | 400 | 400 | 400 | 400 | 400 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -162731.0499 | -560.0737 | 347.9293 | -705.6181 | -747.2902
Standalone Retail |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Standalone Retail; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | -6331.8683 | -4584.6419 | -5460.3332 | -6947.6598 | -10404.3859 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 35588 | 35588 | 35588 | 38691 | 38691 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141
Maintenance | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Primary School |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Primary School; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 3893.5877 | 5302.1261 | 195.8378 | -16126.592 | -14962.7068 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 94496 | 94496 | 94496 | 117289 | 117289 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932
Maintenance | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | -834.5083 | -1237.7995 | -1104.0878 | -1056.0828 | -1168.1572
Small Hotel |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Small Hotel; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 2417.55 | 2841.8577 | 1889.9802 | -2100.9186 | -2054.1797 | 0 | 0 | 0 | 0 | 0 |  | New Construction | 69719 | 66558 | 66558 | 70715 | 70715 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203
Maintenance | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mid-rise Apartment |  |  | Mechanical |  |  |  |  | Lighting |  |  |  | 1: Mid-rise Apartment; 4: Envelope, Power and Other; 9: Total
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY |  |  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 0 | 0 | 0 | 0 | 0 | 9858 | 9858 | 9858 | 9858 | 9858 |  | New Construction | 45405 | 45405 | 45405 | 50460 | 50460 | 55263 | 55263 | 55263 | 60318 | 60318
Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A |  | Maintenance | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Replacement | [11 empty] | 1: Replacement; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B52: Reid Hart: First cost not included because loan payments are included
Note on B60: Reid Hart: This formula needs to be updated to properly split costs and savings

## LCC Sc 3
Commercial Energy Code Adoption Cost Effectiveness - LCC Savings Calculation - Scenario 3 | [10 empty] | US National
[26 empty] | 7 | 8 | 9 | 10 | 11
Scalar method based on ASHRAE 90.1 method and economic factors; adjusted to include PV of replacement costs
| Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
| 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
New Construction | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Maintenance | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0 | 5313.2386
Electricity Cost Savings | 520.5291 | 485.9106 | 501.7546 | 503.2199 | 531.916 | 77322.8931 | 74089.513 | 75995.1179 | 69367.5679 | 69561.175 | 6261.3389 | 5990.1911 | 5670.3211 | 5488.6808 | 5007.9904 | 11426.0894 | 9895.5487 | 10175.5495 | 8466.2076 | 8008.0162 | 8178.9718 | 6994.0055 | 7573.7891 | 7148.8729 | 7332.1923 | 6315.373 | 5664.704 | 6153.301 | 5522.5361 | 5292.0819 | 511445.3585
Gas Cost Savings | 0 | 0.55902 | -0.09317 | 4.4722 | 16.8638 | 72.8593 | 359.8242 | 426.2547 | 1600.4815 | 2703.5262 | 68.5734 | 366.0666 | 228.0812 | 1010.5264 | 1537.6847 | -38.7589 | 426.8137 | 191.6516 | 1032.5146 | 1930.2117 | 1262.2729 | 1566.9402 | 1423.1782 | 1932.1682 | 2176.7406 | -0.65219 | -21.1497 | -6.1492 | 321.5311 | 623.776 | 21216.7687
Total Energy Cost Savings | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579 | 532662.1272
Replacement
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -768.7257 | -664.2154 | -696.1934 | -799.3063 | -432.5089 | -11812.2936 | -12351.2534 | -18373.4602 | -6912.4215 | -3751.663 | -1059.6015 | 1269.5377 | 990.576 | 349.3426 | -458.3335 | 2565.283 | 2492.2215 | -1887.9069 | -9188.4898 | -8454.9983 | 4918.9673 | 4942.5804 | 4971.0952 | 227.3517 | 542.3916 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 317442.5841 | -12207.1994 | -11797.8086 | -13051.5282 | -13217.7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -227.3919 | -268.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | -1296.1852 | -1299.723 | -1295.9102 | -1371.3326 | -1355.4119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | -1620.9765 | -1857.3665 | -1718.8944 | -2333.3577 | -1625.6601 | -81021.5631 | -84518.309 | -158303.2592 | -93634.8139 | -98349.8608 | -7878.9301 | -5890.7574 | -6965.3074 | -8743.0956 | -12960.4361 | -110472.3773 | -1493.6383 | -6141.4228 | -31277.4541 | -30271.0718 | 1305.2719 | 1985.9206 | 371.8465 | -4043.3792 | -4056.8571 | -33923.5031 | -34379.7528 | -40496.9712 | -49887.7036 | -47786.8215
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | -273.2549 | -392.9906 | -400.285 | -3822.2039 | -7011.3539 | 0 | 0 | 0 | 0 | 0 | -19.2259 | -56.426 | -56.5268 | -1470.335 | -1738.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 824.4091 | 1016.8392 | 913.8651 | 1289.1364 | 939.6037 | 50649.2979 | 52904.3621 | 100092.1844 | 63752.9825 | 70679.3371 | 259496.806 | 0 | -265381.1643 | 5945.1779 | 8487.5129 | 74519.8252 | 1874.8645 | 3513.4311 | 19049.0932 | 18852.444 | 769.4745 | 323.5798 | 1409.1341 | 2771.37 | 2885.3686 | 11307.8344 | 11459.9176 | 13498.9904 | 16629.2345 | 15928.9405
LCC Savings
First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Replacement , PV | -558.4156 | -536.6662 | -535.4772 | -657.4652 | -398.8149 | 90398.1899 | -20332.3613 | -31814.0582 | -19298.0108 | -18565.9578 | 26936.4896 | -578.714 | -30485.9962 | -870.4522 | -1755.3296 | -11880.1507 | 1007.1477 | -1630.5117 | -8237.2087 | -7795.9961 | 2497.9339 | 2589.9015 | 2412.0682 | -371.2138 | -222.7436 | -20182.4403 | -20453.8814 | -24093.2577 | -29680.1776 | -28430.2793
Maintenance, Annual | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0
Energy Savings, Annual | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
Scalar Ratio | 5.1366 | 5.2989 | 5.2915 | 7.6796 | 8.5094 | 12.1004 | 7.3743 | 6.8507 | 8.0788 | 7.8806 | 8.8773 | 4.8903 | -0.062172 | 4.8509 | 4.1385 | 7.8722 | 10.1571 | 9.3362 | 10.2019 | 9.9004 | 8.1359 | 8.6808 | 8.117 | 7.5132 | 7.1953 | 1.966 | 2.096 | 0.66534 | -0.46666 | -0.015349
Scalar Ratio Limit | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24
Scalar Cost Effective | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Simple Payback | 6.2094 | 6.402 | 6.3589 | 8.9746 | 9.2361 | 10.9263 | 7.6488 | 7.2692 | 8.3523 | 8.1389 | 4.6219 | 4.9833 | 5.2273 | 4.9877 | 4.4123 | 8.9532 | 10.0556 | 9.4998 | 11.1063 | 10.7169 | 7.8636 | 8.3685 | 7.8407 | 7.5541 | 7.2187 | 5.1621 | 5.7203 | 4.5848 | 4.612 | 4.7904
LCC Savings/sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floor area, sf | 5500 | 5500 | 5500 | 5500 | 5500 | 498640 | 498640 | 498640 | 498640 | 498640 | 24690 | 24690 | 24690 | 24690 | 24690 | 73970 | 73970 | 73970 | 73970 | 73970 | 43210 | 43210 | 43210 | 43210 | 43210 | 33740 | 33740 | 33740 | 33740 | 33740
Energy Cost needs to be calculated from scenario 2 annual escalation (present value of an annuity), or calculate UPV for the scenario 2 escalation rate
If negtive 1st cost - do negative loan as this is a reductionof the loan effects
BCR | 0.99841 | 0.9983 | 0.99834 | 0.99831 | 0.99832 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.9997 | 0.99984 | 1 | 0.99985 | 0.99985 | 0.99992 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.99989 | 0.99987 | 0.99988 | 0.99989 | 0.9999 | 0.99994 | 0.99994 | 0.99998 | 1 | 1
| TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Proto |  |  | Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
CZ | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
Dollar Short | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
Buffer | 8902.8246 | 8241.35 | 8502.3994 | 7392.1933 | 7535.101 | 788820.0299 | 1112690.4144 | 1182225.2725 | 1010655.598 | 1043422.7602 | 84584.6279 | 112618.5887 | 134554.4724 | 115360.1697 | 120927.3402 | 169330.2712 | 129530.0515 | 138930.2337 | 119042.7343 | 127447.4968 | 136936.6012 | 119713.048 | 130837.0125 | 133705.2721 | 143020.7008 | 128024.4898 | 113683.7397 | 132622.6983 | 132699.2335 | 131659.4793 | Below not SF/type weighted
40 Y SR
Elec | 1 | 0.99885 | 1.0002 | 0.99119 | 0.96927 | 0.99906 | 0.99517 | 0.99442 | 0.97745 | 0.96259 | 0.98917 | 0.94241 | 0.96133 | 0.84452 | 0.76508 | 1.0034 | 0.95865 | 0.98151 | 0.8913 | 0.80578 | 0.8663 | 0.81697 | 0.84182 | 0.78723 | 0.77108 | 1.0001 | 1.0037 | 1.001 | 0.94498 | 0.89456 | 0.96017 | 18.2
Gas | 0 | 0.0011491 | -0.00018572 | 0.0088088 | 0.03073 | 0.00094139 | 0.0048331 | 0.0055777 | 0.022552 | 0.037411 | 0.010833 | 0.057592 | 0.038668 | 0.15548 | 0.23492 | -0.0034037 | 0.041348 | 0.018486 | 0.1087 | 0.19422 | 0.1337 | 0.18303 | 0.15818 | 0.21277 | 0.22892 | -0.00010328 | -0.0037476 | -0.0010003 | 0.055018 | 0.10544 | 0.039832 | 21.4
SR | 18.2 | 18.2037 | 18.1994 | 18.2282 | 18.2983 | 18.203 | 18.2155 | 18.2178 | 18.2722 | 18.3197 | 18.2347 | 18.3843 | 18.3237 | 18.6976 | 18.9517 | 18.1891 | 18.3323 | 18.2592 | 18.5478 | 18.8215 | 18.6278 | 18.7857 | 18.7062 | 18.8809 | 18.9325 | 18.1997 | 18.188 | 18.1968 | 18.3761 | 18.5374 | 18.9517 | 18.3275
Note: individual Bldg/CZ scalar ratios are calculated for information; however a weighted total single scalar ratio is used; calculated on the LCC_Summary tab and also shown on the Cost Eff Input tab

## LCC_Summary
|  |  | 1 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4
|  | 0.025336 | 0.023024 | 0.009086 | 0.019059 | 0.022135 | 0.017992 | 0.017948 | 0.008483 | 0.037221 | 0.015936 | 0.059235 | 0.058756 | 0.028203 | 0.063391 | 0.078184 | 0.032252 | 0.031014 | 0.011845 | 0.029137 | 0.025519 | 0.010034 | 0.008854 | 0.003509 | 0.010054 | 0.00901 | 0.074155 | 0.058763 | 0.038875 | 0.099679 | 0.07331 | 1
| From LCC1: | [25 empty] | 7 | 8 | 9 | 10 | 11
|  | 5502 | 5502 | 5502 | 5502 | 5502 | 498588 | 498588 | 498588 | 498588 | 498588 | 24692 | 24692 | 24692 | 24692 | 24692 | 73959 | 73959 | 73959 | 73959 | 73959 | 43202 | 43202 | 43202 | 43202 | 43202 | 33741 | 33741 | 33741 | 33741 | 33741
|  | Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
|  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
| New Construction | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
| Maintenance | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0 |  |  | Scalar
| Electricity Cost Savings | 520.5291 | 485.9106 | 501.7546 | 503.2199 | 531.916 | 77322.8931 | 74089.513 | 75995.1179 | 69367.5679 | 69561.175 | 6261.3389 | 5990.1911 | 5670.3211 | 5488.6808 | 5007.9904 | 11426.0894 | 9895.5487 | 10175.5495 | 8466.2076 | 8008.0162 | 8178.9718 | 6994.0055 | 7573.7891 | 7148.8729 | 7332.1923 | 6315.373 | 5664.704 | 6153.301 | 5522.5361 | 5292.0819 | 12262.9552 | 0.95549
| Gas Cost Savings | 0 | 0.55902 | -0.09317 | 4.4722 | 16.8638 | 72.8593 | 359.8242 | 426.2547 | 1600.4815 | 2703.5262 | 68.5734 | 366.0666 | 228.0812 | 1010.5264 | 1537.6847 | -38.7589 | 426.8137 | 191.6516 | 1032.5146 | 1930.2117 | 1262.2729 | 1566.9402 | 1423.1782 | 1932.1682 | 2176.7406 | -0.65219 | -21.1497 | -6.1492 | 321.5311 | 623.776 | 571.2132 | 0.044507
| Total Energy Cost Savings | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
| EL$/sf | 0.094607 | 0.088315 | 0.091195 | 0.091461 | 0.096677 | 0.15508 | 0.1486 | 0.15242 | 0.13913 | 0.13952 | 0.25358 | 0.2426 | 0.22964 | 0.22229 | 0.20282 | 0.15449 | 0.1338 | 0.13758 | 0.11447 | 0.10828 | 0.18932 | 0.16189 | 0.17531 | 0.16548 | 0.16972 | 0.18717 | 0.16789 | 0.18237 | 0.16367 | 0.15684 | 0.17164 | 0.92343
| NG $/SF | 0 | 0.0001016 | -1.6934e-05 | 0.00081283 | 0.003065 | 0.00014613 | 0.00072169 | 0.00085492 | 0.00321 | 0.0054224 | 0.0027772 | 0.014825 | 0.009237 | 0.040925 | 0.062275 | -0.00052406 | 0.005771 | 0.0025913 | 0.013961 | 0.026098 | 0.029218 | 0.03627 | 0.032942 | 0.044724 | 0.050385 | -1.9329e-05 | -0.00062682 | -0.00018225 | 0.0095294 | 0.018487 | 0.014232 | 0.07657
| Table 5.3. Annual Energy Cost Savings, 90.1-2022 Compared to 90.1-2019 | Table 5.3. Annual Energy Cost Savings, 90.1-2022 Compared to 90.1-2019
|  | Prototype |  | Climate Zone and Location
Prototype |  |  |  | 2A | 3A | 3B | 4A | 5A
Floor area |  |  |  | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY
|  | Small Office | Total | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799
5502 |  |  | $/ft² | 0.094607 | 0.088417 | 0.091178 | 0.092274 | 0.099742
|  | Large Office | Total | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012
498588 |  |  | $/ft² | 0.15523 | 0.14932 | 0.15328 | 0.14234 | 0.14494
|  | Standalone Retail | Total | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751
24692 |  |  | $/ft² | 0.25635 | 0.25742 | 0.23888 | 0.26321 | 0.26509
|  | Primary School | Total | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279
73959 |  |  | $/ft² | 0.15397 | 0.13957 | 0.14017 | 0.12843 | 0.13437
|  | Small Hotel | Total | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328
43202 |  |  | $/ft² | 0.21854 | 0.19816 | 0.20825 | 0.2102 | 0.2201
|  | Mid-rise Apartment | Total | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
33741 |  |  | $/ft² | 0.18715 | 0.16726 | 0.18219 | 0.1732 | 0.17533
From LCC1:
Life Cycle Costs (LCC)
| First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
| Replacement, PV | -493.5219 | -426.4263 | -446.9562 | -513.1546 | -277.6707 | 100577.3406 | -15582.0031 | -18845.427 | -12654.3015 | -10726.297 | -680.2641 | 815.0432 | 635.9498 | 224.278 | -294.2501 | 1303.0943 | 1090.0328 | -1666.9204 | -6460.0917 | -6058.3263 | 3157.977 | 3173.1366 | 3191.4431 | 145.9598 | 348.2154 | -21778.889 | -22071.8013 | -25999.0555 | -32027.9057 | -30679.1394
| Maintenance, PV | 0 | 0 | 0 | 0 | 0 | 7840 | 7840 | 7840 | 7840 | 7840 | 0 | 2642.924 | 2642.924 | 2642.924 | 2642.924 | 7801.3732 | 7795.8551 | 7828.9638 | 7646.866 | 7646.866 | 5247.2213 | 5252.7394 | 5236.185 | -38.6268 | -49.663 | 0 | 0 | 0 | 0 | 0
| Energy Cost Increase | -9523.0807 | -8900.5965 | -9177.7895 | -9293.2979 | -10059.051 | -1416037.9124 | -1362458.6639 | -1398612.385 | -1300175.4095 | -1325148.5069 | -115883.5076 | -116702.8546 | -108169.9136 | -120048.9327 | -121496.8596 | -208287.2589 | -189331.6273 | -189885.2762 | -174949.9951 | -184008.7386 | -174158.9883 | -158399.4117 | -166213.4008 | -168328.7271 | -176434.3502 | -115527.078 | -103224.8417 | -112455.169 | -107281.8263 | -108937.982
| LCC (net costs)* | -6784.4434 | -6212.6212 | -6434.7185 | -5250.1089 | -5268.144 | -466341.5555 | -803808.8737 | -857002.2787 | -715584.9381 | -743133.118 | -87307.64 | -82241.5292 | -74763.373 | -85438.3905 | -90861.5717 | -100793.2037 | -80647.6133 | -89031.395 | -72600.8128 | -80093.9057 | -93617.24 | -80573.678 | -89337.7925 | -99607.3127 | -107474.9775 | -104708.6253 | -93013.8543 | -110271.009 | -112356.7327 | -111277.642
| LCC Cost Effective | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
* If LCC <=0 then the project is cost effective. In the report this indicator is shown as "Life Cycle Cost Net Savings," so the sign is reversed and cost effectiveness is indicated by LCC NPV Savings >= 0.
|  | Small Office |  |  |  |  | Large Office |  |  |  |  | Standalone Retail |  |  |  |  | Primary School |  |  |  |  | Small Hotel |  |  |  |  | Mid-rise Apartment
|  | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY | 2A Tampa FL | 3A Atlanta GA | 3B El Paso TX | 4A New York NY | 5A Buffalo NY
| Simple Payback | 6.2 | 6.4 | 6.4 | 9 | 9.2 | 10.8 | 7.6 | 7.2 | 8.3 | 8 | 4.6 | 4.8 | 5 | 4.8 | 4.2 | 8.3 | 9.3 | 8.8 | 10.2 | 9.9 | 7.4 | 7.9 | 7.4 | 7.6 | 7.2 | 5.2 | 5.7 | 4.6 | 4.6 | 4.8
| LCC Net Savings/sf | 1.23 | 1.13 | 1.17 | 0.95 | 0.96 | 0.94 | 1.61 | 1.72 | 1.44 | 1.49 | 3.54 | 3.33 | 3.03 | 3.46 | 3.68 | 1.36 | 1.09 | 1.2 | 0.98 | 1.08 | 2.17 | 1.87 | 2.07 | 2.31 | 2.49 | 3.1 | 2.76 | 3.27 | 3.33 | 3.3
| Floor area, sf | 5502 | 5502 | 5502 | 5502 | 5502 | 498588 | 498588 | 498588 | 498588 | 498588 | 24692 | 24692 | 24692 | 24692 | 24692 | 73959 | 73959 | 73959 | 73959 | 73959 | 43202 | 43202 | 43202 | 43202 | 43202 | 33741 | 33741 | 33741 | 33741 | 33741
| Annual Energy Sav/sf | 0.095 | 0.088 | 0.091 | 0.092 | 0.1 | 0.155 | 0.149 | 0.153 | 0.142 | 0.145 | 0.256 | 0.257 | 0.239 | 0.263 | 0.265 | 0.154 | 0.14 | 0.14 | 0.128 | 0.134 | 0.219 | 0.198 | 0.208 | 0.21 | 0.22 | 0.187 | 0.167 | 0.182 | 0.173 | 0.175
| SIR (savings to investment ratio) | 3.4773 | 3.3113 | 3.3458 | 2.2985 | 2.0996 | 1.4951 | 2.4593 | 2.6056 | 2.2407 | 2.2943 | 4.0553 | 3.5847 | 3.4303 | 3.6727 | 4.2459 | 2.011 | 1.7994 | 1.9571 | 1.7666 | 1.832 | 2.2433 | 2.1102 | 2.247 | 2.4486 | 2.5574 | 10.6787 | 10.1092 | 51.4867 | Infinite | Infinite
|  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
From LCC3:
LCC Savings
| First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
| Replacement , PV | -558.4156 | -536.6662 | -535.4772 | -657.4652 | -398.8149 | 90398.1899 | -20332.3613 | -31814.0582 | -19298.0108 | -18565.9578 | 26936.4896 | -578.714 | -30485.9962 | -870.4522 | -1755.3296 | -11880.1507 | 1007.1477 | -1630.5117 | -8237.2087 | -7795.9961 | 2497.9339 | 2589.9015 | 2412.0682 | -371.2138 | -222.7436 | -20182.4403 | -20453.8814 | -24093.2577 | -29680.1776 | -28430.2793
| Maintenance, Annual | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 0 | 134.8431 | 134.8431 | 134.8431 | 134.8431 | 398.0292 | 397.7477 | 399.4369 | 390.1462 | 390.1462 | 267.7154 | 267.9969 | 267.1523 | -1.9708 | -2.5338 | 0 | 0 | 0 | 0 | 0
| Energy Savings, Annual | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799 | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012 | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751 | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279 | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328 | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
| Scalar Ratio | 5.1366 | 5.2989 | 5.2915 | 7.6796 | 8.5094 | 12.1004 | 7.3743 | 6.8507 | 8.0788 | 7.8806 | 8.8773 | 4.8903 | -0.062172 | 4.8509 | 4.1385 | 7.8722 | 10.1571 | 9.3362 | 10.2019 | 9.9004 | 8.1359 | 8.6808 | 8.117 | 7.5132 | 7.1953 | 1.966 | 2.096 | 0.66534 | -0.46666 | -0.015349
| Scalar Ratio Limit | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24 | 22.24
| Scalar Cost Effective | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Simple Payback | 6.2094 | 6.402 | 6.3589 | 8.9746 | 9.2361 | 10.9263 | 7.6488 | 7.2692 | 8.3523 | 8.1389 | 4.6219 | 4.9833 | 5.2273 | 4.9877 | 4.4123 | 8.9532 | 10.0556 | 9.4998 | 11.1063 | 10.7169 | 7.8636 | 8.3685 | 7.8407 | 7.5541 | 7.2187 | 5.1621 | 5.7203 | 4.5848 | 4.612 | 4.7904
Table 5.4. Cost-effectiveness Analysis Results
| Prototype Model | Climate Zone and Location
| Life Cycle Cost Net Savings, Total $ per Prototype Model | 2A Tampa | 3A Atlanta | 3B El Paso | 4A New York | 5A Buffalo
| Small Office | 6784.4434 | 6212.6212 | 6434.7185 | 5250.1089 | 5268.144
| Large Office | 466341.5555 | 803808.8737 | 857002.2787 | 715584.9381 | 743133.118
| Standalone Retail | 87307.64 | 82241.5292 | 74763.373 | 85438.3905 | 90861.5717
| Primary School | 100793.2037 | 80647.6133 | 89031.395 | 72600.8128 | 80093.9057
| Small Hotel | 93617.24 | 80573.678 | 89337.7925 | 99607.3127 | 107474.9775
| Mid-rise Apartment | 104708.6253 | 93013.8543 | 110271.009 | 112356.7327 | 111277.642
| Life Cycle Cost Net Savings, $/ft2 | 2A Tampa | 3A Atlanta | 3B El Paso | 4A New York | 5A Buffalo | Weighted
| Small Office | 1.2331 | 1.1292 | 1.1695 | 0.95422 | 0.9575 | 1.0864 |  | 0.10725 | 5502
| Large Office | 0.93532 | 1.6122 | 1.7189 | 1.4352 | 1.4905 | 1.4116 |  |  | 498588
| Standalone Retail | 3.5359 | 3.3307 | 3.0278 | 3.4602 | 3.6798 | 3.4676 |  |  | 24692
| Primary School | 1.3628 | 1.0904 | 1.2038 | 0.98164 | 1.083 | 1.1405 |  |  | 73959
| Small Hotel | 2.167 | 1.865 | 2.0679 | 2.3056 | 2.4877 | 2.201 |  |  | 43202
| Mid-rise Apartment | 3.1033 | 2.7567 | 3.2682 | 3.33 | 3.298 | 3.1702 |  |  | 33741
| Weighted Total | 2.5264 | 2.3348 | 2.5927 | 2.6098 | 2.7874 | 2.5751
| Simple Payback Period (years) | 2A Tampa | 3A Atlanta | 3B El Paso | 4A New York | 5A Buffalo | Weighted
| Small Office | 6.2 | 6.4 | 6.4 | 9 | 9.2 | 7.5171
| Large Office | 10.8 | 7.6 | 7.2 | 8.3 | 8 | 8.5564 |  |  |  | 8.5564
| Standalone Retail | 4.6 | 4.8 | 5 | 4.8 | 4.2 | 4.6969 |  |  |  | Instant
| Primary School | 8.3 | 9.3 | 8.8 | 10.2 | 9.9 | 9.6644
| Small Hotel | 7.4 | 7.9 | 7.4 | 7.6 | 7.2 | 7.6162
| Mid-rise Apartment | 5.2 | 5.7 | 4.6 | 4.6 | 4.8 | 4.9571
| Weighted Total | 5.9609 | 6.1467 | 5.5802 | 5.9134 | 5.5171 | 5.8432
| Scalar Ratio, Limit = 22.24 | 2A Tampa | 3A Atlanta | 3B El Paso | 4A New York | 5A Buffalo | Weighted |  | 22.24 | 1 | 2 | 3 | 4 | 5
| Small Office | 5.1366 | 5.2989 | 5.2915 | 7.6796 | 8.5094 | 6.4369 |  | 1 | 0.025336 | 0.023024 | 0.009086 | 0.019059 | 0.022135 | 0.09864
| Large Office | 12.1004 | 7.3743 | 6.8507 | 8.0788 | 7.8806 | 8.5516 |  | 2 | 0.017992 | 0.017948 | 0.008483 | 0.037221 | 0.015936 | 0.09758
| Standalone Retail | 8.8773 | 4.8903 | -0.062172 | 4.8509 | 4.1385 | 5.0127 |  | 3 | 0.059235 | 0.058756 | 0.028203 | 0.063391 | 0.078184 | 0.28777
| Primary School | 7.8722 | 10.1571 | 9.3362 | 10.2019 | 9.9004 | 9.4739 |  | 4 | 0.032252 | 0.031014 | 0.011845 | 0.029137 | 0.025519 | 0.12977
| Small Hotel | 8.1359 | 8.6808 | 8.117 | 7.5132 | 7.1953 | 7.8953 |  | 5 | 0.010034 | 0.008854 | 0.003509 | 0.010054 | 0.00901 | 0.041461
| Mid-rise Apartment | 1.966 | 2.096 | 0.66534 | -0.46666 | -0.015349 | 0.71692 |  | 6 | 0.074155 | 0.058763 | 0.038875 | 0.099679 | 0.07331 | 0.34478
| Weighted Total | 6.1872 | 5.3274 | 2.6937 | 4.1806 | 4.2565 | 4.7158 |  |  | 0.219 | 0.19836 | 0.1 | 0.25854 | 0.22409
1. Scalar ratio limit for an analysis period of 40 years.
Note: a negative scalar ratio indicates that the cost is negative. This occurs, for example, when there are net decreases in costs either from reductions in HVAC capacity or reductions in installed lighting due to lower LPDs.

## State Inputs (hidden)
State Commercial Energy Code Adoption Cost Effectiveness - State Selection and Inputs | [9 empty] | Cost-Effectiveness of ASHRAE Standard 90.1-2019 |  |  |  |  | State of US National |  |  | For 90.1 editions | [23 empty] | Income tax on savings override: | 0 | savings have income tax penalty in Scenario 2 if blank.
|  |  |  | Note: for output of states with CZ-7 (WI, CO) - first refresh PivTbl on EndUse tab, then manually sort 7 last | [13 empty] | BaseName | 90.1-2019 |  | From SSPC 90.1: | 0.1099 | 0.983 | (ASHRAE 2022 rates) |  |  | 5 | 6 | 7 | 8 | 9 | 10 |  |  |  | Weight | [5 empty] | Property tax override: | 0 | Use state property tax value if blank.
Select State | Abbreviation |  |  | After running those states, sort the pivot table by CZ A-Z Export 5 for CO, then manually edit | [13 empty] | TargetName | 90.1-2022 |  |  | TRUE | TRUE | [10 empty] | not used | State | Index
US National |  | Need lookup formula for abb | [18 empty] | Means 2018 | EIA2020 | EIA2020 | 4/30/2021 | 4/30/2021 | Current Location Weighting Factors | [8 empty] | Order | Start
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
[6 empty] | Climate Zone |  |  |  |  | Climate Zone City |  |  |  |  | Modeled City |  |  |  |  | State Construction Cost Index / 100 | Energy Cost - Rate |  | State | State
State | Abbreviation | Base | Target | Comparison | CZ Qty. | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 |  | Electric, $/kWh | Natural Gas, $/therm | Corp Income Tax | Sales Tax, includes avg county & city | Current climate zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types | Weight index+ |  |  | City out of state | 2010 State ERICA Release | Weighting state name order | Weighting match OK |  |  | Commercial property tax rate
Current Values | US | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 5 | 2A | 3A | 3B | 4A | 5A | 0 | 0 | 0 | 0 | 0 | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY | 1 | 0.1099 | 0.983 | 0.0601 | 0.0656 | 2A | 0.025336 | 0.017992 | 0.059235 | 0.032252 | 0.010034 | 0.074155 | 0.219 |  |  | 96 | 0 | 00000 |  |  | EL | Gas | 0
Alabama | AL | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 2A; Climate Zone 2: 3A; Modeled City 1: Mobile; Modeled City 2: Birmingham | 85 | 0.1159 | 1.1735 | 0.065 | 0.0922 | 3A | 0.023024 | 0.017948 | 0.058756 | 0.031014 | 0.008854 | 0.058763 | 0.19836 | 1 | 1 | 1 | FALSE |  | Alabama | TRUE | 0.1159 | 1.1735 | 0.02
Arkansas | AR | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 3A; Climate Zone 2: 4A; Modeled City 1: Little Rock; Modeled City 2: Fayetteville | 81.1 | 0.0858 | 0.7348 | 0.062 | 0.0953 | 3B | 0.009086 | 0.008483 | 0.028203 | 0.011845 | 0.003509 | 0.038875 | 0.1 | 2 | 2 | 6 | TRUE |  | Arkansas | TRUE | 0.0858 | 0.7348 | 0.02
Colorado | CO | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 4 | Climate Zone 1: 4B; Climate Zone 2: 5B; Climate Zone 3: 6B; Climate Zone 4: 7; Modeled City 1: Trinidad; Modeled City 2: Colorado Springs; Modeled City 3: Eagle County; Modeled City 4: Gunnison County | 89.4 | 0.1039 | 0.5844 | 0.0455 | 0.0765 | 4A | 0.019059 | 0.037221 | 0.063391 | 0.029137 | 0.010054 | 0.099679 | 0.25854 | 3 | 3 | 11 | FALSE |  | Colorado | TRUE | 0.1039 | 0.5844 | 0.02
Connecticut | CT | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 5A; Modeled City 1: Hartford Bradley | 107.4 | 0.1696 | 0.9004 | 0.075 | 0.0635 | 5A | 0.022135 | 0.015936 | 0.078184 | 0.025519 | 0.00901 | 0.07331 | 0.22409 | 4 | 4 | 16 | FALSE |  | Connecticut | TRUE | 0.1696 | 0.9004 | 0.02
Delaware | DE | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 4A; Modeled City 1: Wilmington | 104.2 | 0.0934 | 1.113 | 0.087 | 0 |  | 0.09864 | 0.09758 | 0.28777 | 0.12977 | 0.041461 | 0.34478 | 1 |  | 5 | 21 | FALSE |  | Delaware | TRUE | 0.0934 | 1.113 | 0.02
District of Columbia | DC | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 4A; Modeled City 1: Baltimore MD | 95.2 | 0.1195 | 1.0728 | 0.0825 | 0.06 | [7 empty] | 1 |  | 6 | 26 | TRUE |  | District of Columbia | TRUE | 0.1195 | 1.0728 | 0.02
Georgia | GA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 2A; Climate Zone 2: 3A; Modeled City 1: Savannah; Modeled City 2: Atlanta | 86.4 | 0.0985 | 0.7355 | 0.0575 | 0.0731 | [9 empty] | 7 | 31 | TRUE |  | Georgia | TRUE | 0.0985 | 0.7355 | 0.02
Iowa | IA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 5A; Climate Zone 2: 6A; Modeled City 1: Des Moines; Modeled City 2: Mason City | 91.9 | 0.1024 | 0.5518 | 0.098 | 0.0694 | [9 empty] | 8 | 36 | FALSE |  | Iowa | TRUE | 0.1024 | 0.5518 | 0.02
Kentucky | KY | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 4A; Modeled City 1: Lexington | 88.3 | 0.102 | 0.8319 | 0.05 | 0.06 | [9 empty] | 9 | 41 | FALSE |  | Kentucky | TRUE | 0.102 | 0.8319 | 0.02
Massachusetts | MA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 5A; Modeled City 1: Boston | 110.5 | 0.1599 | 1.0498 | 0.08 | 0.0625 | [9 empty] | 10 | 46 | FALSE |  | Massachusetts | TRUE | 0.1599 | 1.0498 | 0.02
Montana | MT | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 6B; Modeled City 1: Helena | 88.9 | 0.1058 | 0.6828 | 0.0675 | 0 | [9 empty] | 11 | 51 | FALSE |  | Montana | TRUE | 0.1058 | 0.6828 | 0.02
Nebraska | NE | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 5A; Modeled City 1: Omaha | 90.3 | 0.0909 | 0.5075 | 0.0781 | 0.0693 | [9 empty] | 12 | 56 | FALSE |  | Nebraska | TRUE | 0.0909 | 0.5075 | 0.02
New Jersey | NJ | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Newark; Modeled City 2: Allentown PA | 114.6 | 0.1244 | 0.8561 | 0.09 | 0.066 | [9 empty] | 13 | 61 | TRUE |  | New Jersey | TRUE | 0.1244 | 0.8561 | 0.02
New York | NY | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 4A; Climate Zone 2: 5A; Climate Zone 3: 6A; Modeled City 1: New York; Modeled City 2: Albany; Modeled City 3: Massena | 130.6 | 0.1454 | 0.671 | 0.065 | 0.0852 | [9 empty] | 14 | 66 | FALSE | 24223 | New York | TRUE | 0.1454 | 0.671 | 0.0323
North Carolina | NC | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3A; Climate Zone 2: 4A; Climate Zone 3: 5A; Modeled City 1: Charlotte; Modeled City 2: Asheville; Modeled City 3: Elkins WV | 85.2 | 0.0877 | 0.88 | 0.025 | 0.0698 | [9 empty] | 15 | 71 | TRUE |  | North Carolina | TRUE | 0.0877 | 0.88 | 0.02
Oklahoma | OK | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3A; Climate Zone 2: 4A; Climate Zone 3: 4B; Modeled City 1: Oklahoma; Modeled City 2: Ponca City; Modeled City 3: Amarillo TX | 83.6 | 0.0757 | 0.7237 | 0.06 | 0.0895 | [9 empty] | 16 | 76 | TRUE |  | Oklahoma | TRUE | 0.0757 | 0.7237 | 0.02
Rhode Island | RI | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 5A; Modeled City 1: Providence | 104.1 | 0.1595 | 1.204 | 0.07 | 0.07 | [9 empty] | 17 | 81 | FALSE |  | Rhode Island | TRUE | 0.1595 | 1.204 | 0.02
South Carolina | SC | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 2A; Climate Zone 2: 3A; Modeled City 1: Beaufort; Modeled City 2: Columbia | 84.9 | 0.1024 | 0.8327 | 0.05 | 0.0746 | [9 empty] | 18 | 86 | FALSE |  | South Carolina | TRUE | 0.1024 | 0.8327 | 0.02
Texas | TX | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 5 | 1A | 2A | 2B | 3A | 3B | [5 empty] | Houston | San Antonio | Fort Worth | El Paso | Amarillo | 83.5 | 0.0774 | 0.6441 | 0.0053 | 0.0819 | [9 empty] | 19 | 91 | FALSE |  | Texas | TRUE | 0.0774 | 0.6441 | 0.02
US National | US | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 5 | 2A | 3A | 3B | 4A | 5A | [5 empty] | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY | 100 | 0.1099 | 0.983 | 0.0601 | 0.0656 | [9 empty] | 20 | 96 | FALSE |  | US National | TRUE | 0.1099 | 0.983 | 0.0204
Utah | UT | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3B; Climate Zone 2: 5B; Climate Zone 3: 6B; Modeled City 1: Saint George; Modeled City 2: Salt Lake City; Modeled City 3: Vernal | 88.7 | 0.0842 | 0.5348 | 0.0495 | 0.0718 | [9 empty] | 21 | 101 | FALSE | 24222 | Utah | TRUE | 0.0842 | 0.5348 | 0.0144
Virginia | VA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3A; Climate Zone 2: 4A; Climate Zone 3: 5A; Modeled City 1: Norfolk; Modeled City 2: Richmond; Modeled City 3: Elkins WV | 88.7 | 0.077 | 0.8438 | 0.06 | 0.0565 | [9 empty] | 22 | 106 | FALSE |  | Virginia | TRUE | 0.077 | 0.8438 | 0.02
Wisconsin | WI | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 5A; Climate Zone 2: 6A; Modeled City 1: Madison; Modeled City 2: Duluth MN | 99.9 | 0.1105 | 0.6257 | 0.079 | 0.0543 | [9 empty] | 23 | 111 | TRUE |  | Wisconsin | TRUE | 0.1105 | 0.6257 | 0.02
California | CA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 5 | 2B | 3B | 3C | 4B | 5B | [5 empty] | Tuscon AZ | Los Angeles | San Francisco | Bishop | Winnemucca NV | 114.4 | 0.1772 | 0.952 | 0.0884 | 0.0868 | [9 empty] | 24 | 116 | [6 empty] | 0.02
Arizona | AZ | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 4 | Climate Zone 1: 2B; Climate Zone 2: 3B; Climate Zone 3: 4B; Climate Zone 4: 5B; Modeled City 1: Tuscon; Modeled City 2: Kingman; Modeled City 3: Prescott; Modeled City 4: Gallup NM | 87.6 | 0.1027 | 0.6719 | 0.049 | 0.084 | [9 empty] | 25 | 121 | [6 empty] | 0.02
Florida | FL | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 1A; Climate Zone 2: 2A; Modeled City 1: Miami; Modeled City 2: Tampa | 82.9 | 0.0915 | 1.1082 | 0.04458 | 0.0705 | [9 empty] | 26 | 126 | [6 empty] | 0.02
Hawaii | HI | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 1A; Modeled City 1: Honolulu | 118.6 | 0.2878 | 2.8803 | 0.064 | 0.0444 | [9 empty] | 27 | 131 | [6 empty] | 0.02 | Min | 81.1 | 0.0757 | 0.5075 | 0.0053 | 0
Idaho | ID | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 5B; Climate Zone 2: 6B; Modeled City 1: Boise; Modeled City 2: Idaho Falls | 92.6 | 0.0775 | 0.5483 | 0.06925 | 0.0603 | [9 empty] | 28 | 136 | [6 empty] | 0.02 | Q2 | 85.8 | 0.0893 | 0.65755 | 0.05375 | 0.06125
Illinois | IL | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: St.Louis MO; Modeled City 2: Peoria | 116.7 | 0.0895 | 0.6982 | 0.095 | 0.088 | [9 empty] | 29 | 141 | [6 empty] | 0.02 | Avg | 94.887 | 0.10877 | 0.81466 | 0.063565 | 0.065522
Indiana | IN | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Evansville; Modeled City 2: Fort Wayne | 91.1 | 0.1092 | 0.6638 | 0.049 | 0.07 | [9 empty] | 30 | 146 | [6 empty] | 0.02 | Q3 | 102.05 | 0.1177 | 0.9417 | 0.07855 | 0.07555
Kansas | KS | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Topeka; Modeled City 2: Goodland | 89.6 | 0.1032 | 0.7935 | 0.04 | 0.0868 | [9 empty] | 31 | 151 | [6 empty] | 0.02 | Max | 130.6 | 0.1696 | 1.204 | 0.098 | 0.0953
Louisiana | LA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 2A; Climate Zone 2: 3A; Modeled City 1: Baton Rouge; Modeled City 2: Shreveport | 84.7 | 0.0876 | 0.8144 | 0.08 | 0.0952 | [9 empty] | 32 | 156 | [6 empty] | 0.02
Maine | ME | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 6A; Climate Zone 2: 7; Modeled City 1: Bangor; Modeled City 2: Caribou | 91.2 | 0.1254 | 1.1081 | 0.0893 | 0.055 | [9 empty] | 33 | 161 | [6 empty] | 0.02
Maryland | MD | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Baltimore; Modeled City 2: Pittsburgh PA | 93.3 | 0.0973 | 1.0625 | 0.0825 | 0.06 | [9 empty] | 34 | 166 | [6 empty] | 0.02
Michigan | MI | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 5A; Climate Zone 2: 6A; Climate Zone 3: 7; Modeled City 1: Lansing; Modeled City 2: Alpena County; Modeled City 3: Sault Ste Marie | 96.4 | 0.1177 | 0.6612 | 0.06 | 0.06 | [9 empty] | 35 | 171 | [6 empty] | 0.02 | CZcount | States
Minnesota | MN | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 5A; Climate Zone 2: 6A; Climate Zone 3: 7; Modeled City 1: Winona; Modeled City 2: Minneapolis-St.Paul; Modeled City 3: Duluth | 103.3 | 0.1057 | 0.6387 | 0.098 | 0.0746 | [9 empty] | 36 | 176 | [6 empty] | 0.02 | 1 | 8
Mississippi | MS | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 2A; Climate Zone 2: 3A; Modeled City 1: Mobile AL; Modeled City 2: Jackson | 81.7 | 0.1047 | 0.8428 | 0.05 | 0.0707 | [9 empty] | 37 | 181 | [6 empty] | 0.02 | 2 | 7
Missouri | MO | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3A; Climate Zone 2: 4A; Climate Zone 3: 5A; Modeled City 1: Memphis TN; Modeled City 2: St.Louis; Modeled City 3: Kirksville | 98.6 | 0.0877 | 0.7268 | 0.04 | 0.082 | [9 empty] | 38 | 186 | [6 empty] | 0.02 | 3 | 5
Nevada | NV | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3B; Climate Zone 2: 4B; Climate Zone 3: 5B; Modeled City 1: Las Vegas; Modeled City 2: Tonopah; Modeled City 3: Winnemucca | 100.7 | 0.0758 | 0.6979 | 0 | 0.0823 | [9 empty] | 39 | 191 | [6 empty] | 0.02 | 4 | 1
New Hampshire | NH | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 5A; Climate Zone 2: 6A; Modeled City 1: Manchester; Modeled City 2: Lebanon | 94.4 | 0.154 | 1.12 | 0.077 | 0 | [9 empty] | 40 | 196 | [6 empty] | 0.02 | 5 | 2
New Mexico | NM | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 3B; Climate Zone 2: 4B; Climate Zone 3: 5B; Modeled City 1: Roswell; Modeled City 2: Albuquerque; Modeled City 3: Gallup | 88.1 | 0.1043 | 0.4825 | 0.059 | 0.0783 | [9 empty] | 41 | 201 | [6 empty] | 0.02
North Dakota | ND | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 6A; Climate Zone 2: 7; Modeled City 1: Bismarck; Modeled City 2: Minot | 91.6 | 0.09 | 0.4933 | 0.0431 | 0.0694 | [9 empty] | 42 | 206 | [6 empty] | 0.02
Ohio | OH | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Columbus; Modeled City 2: Cleveland | 92.5 | 0.0941 | 0.5352 | 0 | 0.0717 | [9 empty] | 43 | 211 | [6 empty] | 0.02
Oregon | OR | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4C; Climate Zone 2: 5B; Modeled City 1: Portland; Modeled City 2: Redmond | 99.7 | 0.09 | 0.7885 | 0.076 | 0 | [9 empty] | 44 | 216 | [6 empty] | 0.02
Pennsylvania | PA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Philadelphia; Modeled City 2: Pittsburgh | 107.5 | 0.085 | 0.9019 | 0.0999 | 0.0634 | [9 empty] | 45 | 221 | [6 empty] | 0.02
South Dakota | SD | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 5A; Climate Zone 2: 6A; Modeled City 1: Sioux City IA; Modeled City 2: Sioux Falls | 87.4 | 0.0956 | 0.4908 | 0 | 0.064 | [9 empty] | 46 | 226 | [6 empty] | 0.02
Tennessee | TN | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 3A; Climate Zone 2: 4A; Modeled City 1: Memphis; Modeled City 2: Bristol | 85.2 | 0.1051 | 0.751 | 0.065 | 0.0955 | [9 empty] | 47 | 231 | [6 empty] | 0.02
Vermont | VT | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 1 | Climate Zone 1: 6A; Modeled City 1: Burlington | 92.5 | 0.1641 | 0.7984 | 0.085 | 0.0622 | [9 empty] | 48 | 236 | [6 empty] | 0.02
Washington | WA | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 4 | Climate Zone 1: 4C; Climate Zone 2: 5B; Climate Zone 3: 5C; Climate Zone 4: 6B; Modeled City 1: Seattle; Modeled City 2: Spokane; Modeled City 3: Quillayute; Modeled City 4: Kalispell MT | 101.8 | 0.0891 | 0.7673 | 0 | 0.0923 | [9 empty] | 49 | 241 | [6 empty] | 0.02
West Virginia | WV | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 2 | Climate Zone 1: 4A; Climate Zone 2: 5A; Modeled City 1: Charleston; Modeled City 2: Elkins | 95.6 | 0.0939 | 0.5353 | 0.065 | 0.065 | [9 empty] | 50 | 246 | [6 empty] | 0.02
Wyoming | WY | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 3 | Climate Zone 1: 5B; Climate Zone 2: 6B; Climate Zone 3: 7; Modeled City 1: Cheyenne; Modeled City 2: Casper; Modeled City 3: Jackson Hole | 88.7 | 0.0971 | 0.698 | 0 | 0.0534 | [9 empty] | 51 | 251 | [6 empty] | 0.02
Alaska | AK | 2019 | 2022 | 90.1-2019 to 90.1-2022 | 4 | Climate Zone 1: 5C; Climate Zone 2: 6A; Climate Zone 3: 7; Climate Zone 4: 8; Modeled City 1: Ketchikan; Modeled City 2: Juneau; Modeled City 3: Anchorage; Modeled City 4: Fairbanks | 117.3 | 0.1988 | 1.0019 | 0.094 | 0.0176 | [9 empty] | 52 | 256 | [6 empty] | 0.02
[15 empty] | CZ | New cities | Old cities
[15 empty] | 0A | Ho Chi Minh City, Vietnam | NA
[15 empty] | 0B | Dubai, UAE | NA
[15 empty] | 1A | Honolulu HI | Miami FL
[15 empty] | 1B | New Deli, India | Riyadh
[15 empty] | 2A | Tampa FL | Houston TX
[15 empty] | 2B | Tucson AZ | Phoenix AZ
[15 empty] | 3A | Atlanta GA | Memphis TN
[15 empty] | 3B | El Paso TX | El Paso TX
[15 empty] | 3C | San Diego CA | San Francisco CA
[15 empty] | 4A | New York NY | Baltimore MD
[15 empty] | 4B | Albuquerque NM | Albuquerque NM
[15 empty] | 4C | Seattle WA | Salem OR
[15 empty] | 5A | Buffalo NY | Chicago IL
[15 empty] | 5B | Denver CO | Boise ID
[15 empty] | 5C | Port Angeles WA | Vancouver BC
[15 empty] | 6A | Rochester MN | Burlington VT
[15 empty] | 6B | Great Falls MT | Helena MT
[15 empty] | 7 | International Falls MN | Duluth MN
[15 empty] | 8 | Fairbanks AK | Fairbanks AK
Note on L6: Reid Hart: does not apear to be used

## StateReport(x) (hidden)
PNNL - 00000
Cost-Effectiveness of
ASHRAE Standard 90.1-2022
for the State of US National
| R Hart | M Halverson
| R Athalye | S Loper
| Y Xie | M Rosenberg
| J Zhuge | E Richman
April 2015
ASHRAE Standard 90.1-2022 Provides Cost-Effective Savings
for Commercial Buildings in the State of US National
Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 shows the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional cost per square foot required by the upgrade, and the simple payback period in years. Average values are weighted averages for all building types considered in all climate zones in the state, based on weightings shown in Table 6.
Table 1. US National Average Savings and Cost Weighted by Climate Zone and Building Type
Weighted Cost Savings and Added Cost per Square Foot
Annual Cost Savings, $/ft2 |  |  |  | 0.1857
Added Construction Cost, $/ft2 |  |  |  | 1.0851
State of US National Average Simple Payback, years |  |  |  | 5.8432
Table 2. US National Average LCC Results Weighted by Climate Zone and Building Type
Weighted Net Life Cycle Cost Savings, by Ownership Scenario
Scenario 1 (Publicly-Owned), $/ft2 |  |  |  | 2.5751
Scenario 2 (Privately-Owned), $/ft2 |  |  |  | 2.5462
Figure 1. Scenario 1: Net Life Cycle Cost Savings |  |  | Figure 2. Scenario 2: Net Life Cycle Cost Savings
The report provides analysis of two Life Cycle Cost (LCC) scenarios:
Scenario 1, representing publicly-owned buildings, considers initial costs, energy, maintenance and replacement costs without borrowing or taxes.
Scenario 2, representing privately-owned buildings, adds borrowing costs and tax impacts.
Table 2 shows the statewide weighted average LCC net present value of savings from both scenarios, that is, the remaining savings after initial and replacement costs have been paid for. Average values are weighted averages of all climate zones and building types in the state as shown in Table 6. Individual building type LCC results are shown in Figures 1 and 2.

## StateReport (2) (hidden)
PNNL - 00000
Cost-Effectiveness of
ASHRAE Standard 90.1-2022
for the State of US National
| R Hart | M Halverson
| R Athalye | S Loper
| Y Xie | M Rosenberg
| J Zhuge | E Richman
April 2015
ASHRAE Standard 90.1-2022 Provides Cost-Effective Savings
for Commercial Buildings in the State of US National
Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 and Figure 1 show the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional cost per square foot required by the upgrade, and the simple payback period in years. Average values are weighted averages for all building types considered in all climate zones in the state, based on weightings shown in Table 6.
Table 1. US National Average Savings and Cost Weighted by Climate Zone and Building Type
Weighted Cost Savings and Added Cost per Square Foot
Annual Cost Savings, $/ft2 |  |  |  | 0.1857 | Annual Energy Savings | 0.1857 | #N/A
Added Construction Cost, $/ft2 |  |  |  | 1.0851 | Added First Costs | 1.0851 | #N/A
State of US National Average Simple Payback, years |  |  |  | 5.8432 | Average Simple Payback | #N/A | 5.8432
Table 2. US National Average LCC Results Weighted by Climate Zone and Building Type
Weighted Net Life Cycle Cost Savings, by Ownership Scenario
Scenario 1 (Publicly-Owned), $/ft2 |  |  |  | 2.5751 | Scenario 1: Publicly-Owned | 2.5751
Scenario 2 (Privately-Owned), $/ft2 |  |  |  | 2.5462 | Scenario 2: Privately-Owned | 2.5462
Figure 1. Statewide Weighted Costs and Savings |  |  | Figure 2. Net Life Cycle Cost Savings
The report provides analysis of two Life Cycle Cost (LCC) scenarios:
Scenario 1, representing publicly-owned buildings, considers initial costs, energy, maintenance and replacement costs without borrowing or taxes.
Scenario 2, representing privately-owned buildings, adds borrowing costs and tax impacts.
Table 2 shows the statewide weighted average LCC net present value of savings from both scenarios, that is, the remaining savings after initial and replacement costs have been paid for. Average values are weighted averages of all climate zones and building types in the state as shown in Table 6. Overall state weighted net LCC results are shown in Figures 2 for both scenarios.

## StateReport (3) (hidden)
PNNL - 00000
Cost-Effectiveness of
ASHRAE Standard 90.1-2022
for the State of US National
| R Hart | M Halverson
| R Athalye | S Loper
| Y Xie | M Rosenberg
| J Zhuge | E Richman
April 2015
ASHRAE Standard 90.1-2022 Provides Cost-Effective Savings
for Commercial Buildings in the State of US National
Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 shows the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional cost per square foot required by the upgrade, and the simple payback period in years. Figure 1 compares annual energy cost savings, first cost for the upgrade, and net annualized LCC savings.The net annualized LCC savings per square foot is the annual energy savings net of an allowance to pay for the added cost under Scenario 1. Average values are weighted averages for all building types considered in all climate zones in the state, based on weightings shown in Table 6.
Table 1. US National Average Savings and Cost Weighted by Climate Zone and Building Type
Weighted Cost Savings and Added Cost per Square Foot
Annual Cost Savings, $/ft2 |  |  |  | 0.1857 | Annual Energy Savings | 0.1857 | #N/A
Added Construction Cost, $/ft2 |  |  |  | 1.0851 | Added First Costs | 1.0851 | #N/A
State of US National Average Simple Payback, years |  |  |  | 5.8432 | Annual Net LCC Savings | 0.13133 | #N/A
0.051
Table 2. US National Average LCC Results Weighted by Climate Zone and Building Type
Weighted Net Life Cycle Cost Savings, by Ownership Scenario
Scenario 1 (Publicly-Owned), $/ft2 |  |  |  | 2.5751 | Scenario 1: Publicly-Owned | 2.5751
Scenario 2 (Privately-Owned), $/ft2 |  |  |  | 2.5462 | Scenario 2: Privately-Owned | 2.5462
Figure 1. Statewide Weighted Costs and Savings |  |  | Figure 2. Overall Net Life Cycle Cost Savings
The report provides analysis of two Life Cycle Cost (LCC) scenarios:
Scenario 1, representing publicly-owned buildings, considers initial costs, energy, maintenance and replacement costs without borrowing or taxes.
Scenario 2, representing privately-owned buildings, adds borrowing costs and tax impacts.
Table 2 shows the statewide weighted average LCC net present value of savings from both scenarios; that is, the remaining savings after initial and replacement costs have been paid for. Overall values are weighted based on Table 6. Figure 2 shows overall state weighted net LCC results for both scenarios. When net LCC is positive, a proposed code is considered cost-effective.

## emissions (hidden)
Index: | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56
vlookup: | US | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sig Figs | 4 | #N/A | #N/A | #N/A | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| outputs from Benefits model | [5 empty] | 1st year | 1st year | 1st year | 1st year | 1st year | 30 year | 30 year | 30 year | 30 year | 30 year |  | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 1st year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | 30 year Social Cost | [6 empty] | Avert Emission rates by State (from ________) | [5 empty] | Egrid Emissions not available from Avert |  | Estimated CO2eq by State from Avert for CO2, and Egrid for CH4 and N2O
[7 empty] | metric tons | metric tons | metric tons | metric tons | metric tons | metric tons | metric tons | metric tons | metric tons | metric tons |  | 14.0163 | 50.164 | 75.2247 | 149.523 | 653.1946 | 1488.3137 | 1964.6306 | 3924.203 | 5608.5016 | 18172.7401 | 26883.2923 | 47762.6628 | 65.4546 |  |  |  | 2140.9463 |  |  |  | 24426.8348 |  |  |  |  | 1 MMT CO2 = 217,480 cars driven/year | . |  |  |  | Avert, 2019 | [5 empty] | Egrid Non Baseload (lb/MWh) |  | Mixed Avert, 2019 and Egrid 2019
|  | comm | comm | comm | comm |  | comm | comm | comm | comm | comm | comm | comm | comm | comm | comm |  | comm | comm | comm | comm | comm | comm | comm | comm | comm | comm | comm | comm | comm |  |  |  | comm |  |  |  | comm |  |  |  |  | comm |  | comm | comm
|  | Electricity MWh, 1st year | Natural Gas, mmcf, 1st year | Electricity MWh, cumul. | Natural Gas, mmcf, cumul. |  | CO2 | CH4 | N2O | NOx | SOx | CO2 | CH4 | N2O | NOx | SOx |  | 5.0%_CO2 | 3.0%_CO2 | 2.5%_CO2 | 3% 95th Pct._CO2 | 5.0%_CH4 | 3.0%_CH4 | 2.5%_CH4 | 3% 95th Pct._CH4 | 5.0%_N2O | 3.0%_N2O | 2.5%_N2O | 3% 95th Pct._N2O | 5.0%_CO2 | 3.0%_CO2 | 2.5%_CO2 | 3% 95th Pct._CO2 | 5.0%_CH4 | 3.0%_CH4 | 2.5%_CH4 | 3% 95th Pct._CH4 | 5.0%_N2O | 3.0%_N2O | 2.5%_N2O | 3% 95th Pct._N2O |  | Number of cars driven per year based on cumulative CO2 |  | 1st year Energy Cost Savings, 2020$ | Cumulative Energy Cost Savings, 2020$ |  | State abb | State | Avoided CO2 Rate (lb/MWh) | Avoided NOx Rate (lb/MWh) | Avoided SO2 Rate (lb/MWh) | Avoided PM2.5 Rate (lb/MWh) | CH4 | N2O | CO2eq
| AL | 9095.5532 | 17.88 | 6447313.1177 | 12674.1336 |  | 7495.2153 | 0.27852 | 0.03899 | 4.0719 | 1.9058 | 5312925.8742 | 197.4291 | 27.6376 | 2886.3524 | 1350.8927 |  | 105055.3856 | 375990.0698 | 563825.6788 | 1120707.4312 | 181.9299 | 414.5301 | 547.1955 | 1092.9821 | 218.6741 | 708.5505 | 1048.1727 | 1862.2541 | 59590817.3769 | 235154779.3552 | 359601192.4638 | 713086103.1659 | 108452.1409 | 282565.646 | 383433.1314 | 751994.9684 | 125386.9674 | 454722.3114 | 689724.227 | 1206221.0588 |  | 1155455.1191 |  | 896787.8916 | 395848810.0112 |  | AL | Alabama | 1581.1401 | 0.79842 | 0.46083 | 0.098146 | 0.063 | 0.009 | 1585.2891
| AK | 1151.9734 | 0.36562 | 829158.2257 | 263.1666 |  | 732.4162 | 0.059417 | 0.0083971 | 4.8521 | 0.53664 | 527172.7142 | 42.7665 | 6.044 | 3492.418 | 386.26 |  | 10265.7849 | 36740.936 | 55095.8252 | 109513.1049 | 38.8107 | 88.4308 | 116.732 | 233.1634 | 47.0953 | 152.5988 | 225.7425 | 401.0692 | 5907915.5789 | 23322350.0966 | 35667476.8754 | 70727152.9966 | 23477.1659 | 61198.5456 | 83052.7789 | 162873.433 | 27398.9114 | 99406.0057 | 150793.2604 | 263697.7469 |  | 114649.5219 |  | 165352.7491 | 83775407.9487 |  | AK | Alaska | 1363.836 | 9.257 | 1.027 | #N/A | 0.113 | 0.016 | 1371.24
| AZ | 24465.4002 | 38.0355 | 17220512.6913 | 26772.1308 |  | 19234.6587 | 1.1603 | 0.1593 | 12.6173 | 3.0423 | 13538739.6758 | 816.711 | 112.1291 | 8880.9532 | 2141.3653 |  | 269599.257 | 964887.6435 | 1446922.3372 | 2876024.7657 | 757.9092 | 1726.9076 | 2279.5836 | 4553.2983 | 893.4528 | 2894.9774 | 4282.5971 | 7608.7496 | 151968468.9985 | 599494036.2172 | 916689518.531 | 1817839904.4525 | 448915.1071 | 1169114.6283 | 1586308.855 | 3111328.6205 | 509076.0741 | 1845502.4011 | 2799029.7606 | 4895370.3429 |  | 2944405.1047 |  | 2163887.5466 | 950728560.084 |  | AZ | Arizona | 1547.0077 | 0.98791 | 0.27326 | 0.077256 | 0.101 | 0.014 | 1553.5457
| AR | 3420.473 | 6.4827 | 2389575.4435 | 4528.8843 |  | 3196.0903 | 0.20222 | 0.028598 | 2.293 | 2.3876 | 2232819.5756 | 141.2712 | 19.9791 | 1601.8896 | 1668.0166 |  | 44797.4458 | 160328.713 | 240425.0875 | 477889.1639 | 132.0874 | 300.9632 | 397.2829 | 793.543 | 160.3943 | 519.7118 | 768.8199 | 1365.9371 | 25053935.8928 | 98848846.212 | 151155201.3095 | 299744153.964 | 77629.0225 | 202210.5 | 274380.3861 | 538141.7261 | 90676.8865 | 328777.1384 | 498667.8931 | 872121.2169 |  | 485593.6013 |  | 271711.7459 | 128028087.647 |  | AR | Arkansas | 1832.9202 | 1.2962 | 1.538 | 0.14366 | 0.126 | 0.018 | 1841.2182
| CA | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | CA | California | 1072.5972 | 0.2971 | 0.065783 | 0.043607 | 0.041 | 0.005 | 1075.0702
| CO | 17167.565 | 38.6612 | 12083770.1017 | 27212.5409 |  | 16764.5471 | 1.0213 | 0.14418 | 9.7702 | 4.4596 | 11800097.0298 | 718.8861 | 101.4815 | 6876.9967 | 3139.0106 |  | 234977.3662 | 840976.9365 | 1261108.8168 | 2506686.1545 | 667.1276 | 1520.0603 | 2006.5373 | 4007.9086 | 808.6117 | 2620.0744 | 3875.9276 | 6886.2333 | 132452704.0624 | 522507114.0714 | 798968406.5074 | 1584393213.1715 | 395144.4868 | 1029079.2011 | 1396302.304 | 2738656.6667 | 460734.9135 | 1670256.0431 | 2533237.7621 | 4430512.7393 |  | 2566285.1021 |  | 1508847.5089 | 666348143.8728 |  | CO | Colorado | 1882.9975 | 1.0387 | 0.57144 | 0.038783 | 0.126 | 0.018 | 1891.2955
| CT | 4553.2952 | 2.0669 | 3191616.4113 | 1448.8005 |  | 2437.3332 | 0.12399 | 0.014671 | 0.59687 | 0.25583 | 1708440.2573 | 86.9105 | 10.2832 | 418.3765 | 179.3265 |  | 34162.4587 | 122266.4136 | 183347.7774 | 364437.4927 | 80.9897 | 184.5363 | 243.5949 | 486.5626 | 82.2795 | 266.6032 | 394.3914 | 700.7023 | 19186027.82 | 75671148.4101 | 115703979.5765 | 229450576.7846 | 47790.3222 | 124426.9216 | 168818.1105 | 331128.4293 | 46708.0895 | 169287.724 | 256740.9493 | 449045.6814 |  | 371551.5871 |  | 635888.6995 | 302726719.9003 |  | CT | Connecticut | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.059 | 0.007 | 1129.3487
| DE | 1694.9679 | 4.8934 | 1190880.3351 | 3438.0989 |  | 1470.6163 | 0.029702 | 0.0035852 | 0.80773 | 0.91951 | 1033251.4095 | 20.8688 | 2.5189 | 567.511 | 646.0432 |  | 20612.638 | 73772.0122 | 110626.7378 | 219891.0263 | 19.4015 | 44.2065 | 58.3543 | 116.5583 | 20.1076 | 65.1528 | 96.3819 | 171.2385 | 11591626.6002 | 45738686.6199 | 69942683.4518 | 138697572.9685 | 11465.8368 | 29870.1381 | 40531.769 | 79493.5382 | 11430.3408 | 41448.8664 | 62868.2826 | 109949.0879 |  | 224711.5165 |  | 176270.7669 | 79814988.5936 |  | DE | Delaware | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.032 | 0.004 | 1568.652
| DC | 1062.7533 | 0.14146 | 746687.8554 | 99.391 |  | 762.8058 | 0.010751 | 0.0009787 | 0.37903 | 0.57574 | 535945.4953 | 7.5536 | 0.68764 | 266.3056 | 404.5127 |  | 10691.7352 | 38265.3992 | 57381.8736 | 114057.0474 | 7.0225 | 16.0008 | 21.1217 | 42.1891 | 5.4891 | 17.7857 | 26.3108 | 46.7455 | 6012554.1597 | 23724567.7401 | 36279133.7946 | 71942161.1867 | 4150.1378 | 10811.7003 | 14670.7503 | 28773.2285 | 3120.3103 | 11314.9143 | 17162.0913 | 30014.4398 |  | 116557.4263 |  | 100142.6956 | 44058202.5944 |  | DC | District of Columbia | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.022 | 0.002 | 1567.842
| FL | 43735.4655 | 61.3572 | 30728431.353 | 43109.3965 |  | 25979.192 | 1.1946 | 0.14524 | 10.7936 | 5.1707 | 18252916.9166 | 839.3071 | 102.0472 | 7583.5693 | 3632.8946 |  | 364132.8382 | 1303220.4917 | 1954278.1508 | 3884487.9343 | 780.2914 | 1777.9058 | 2346.9032 | 4687.764 | 814.5946 | 2639.4599 | 3904.6051 | 6937.1836 | 204772038.3672 | 807997394.5352 | 1235573431.8625 | 2450163873.7077 | 461135.2238 | 1201322.9483 | 1630114.4667 | 3197086.3765 | 463063.9575 | 1679169.1944 | 2546908.8209 | 4454238.1338 |  | 3969644.371 |  | 3798895.3056 | 1699128826.7017 |  | FL | Florida | 1141.4365 | 0.4095 | 0.25985 | 0.083614 | 0.057 | 0.007 | 1144.8875
| GA | 18821.0677 | 47.0775 | 13223636.2557 | 33076.5151 |  | 16199.2013 | 1.2441 | 0.17562 | 9.4906 | 3.075 | 11381519.2924 | 874.0975 | 123.3924 | 6668.0764 | 2160.4937 |  | 227053.2947 | 812616.9223 | 1218580.8207 | 2422153.9257 | 812.6355 | 1851.6024 | 2444.1855 | 4882.0781 | 984.983 | 3191.5549 | 4721.33 | 8388.232 | 127684627.9346 | 503822921.8989 | 770435920.7986 | 1527787998.2431 | 480249.9015 | 1251119.4066 | 1697684.9123 | 3329609.9236 | 559922.8947 | 2030400.4682 | 3079644.9099 | 5385929.6743 |  | 2475252.8157 |  | 1748524.1456 | 784942368.9772 |  | GA | Georgia | 1597.6746 | 0.87175 | 0.35875 | 0.096281 | 0.14 | 0.02 | 1606.8946
| HI | 2331.6674 | 1.6391 | 1678269.0177 | 1179.7744 |  | 1848.3445 | 0.15504 | 0.024492 | 7.0177 | 7.8224 | 1330386.6941 | 111.593 | 17.6288 | 5051.1599 | 5630.3237 |  | 25907.0003 | 92720.3761 | 139041.2492 | 276370.1036 | 101.2708 | 230.7471 | 304.595 | 608.4058 | 137.3646 | 445.0907 | 658.4315 | 1169.8136 | 14909368.531 | 58856885.8095 | 90011366.9881 | 178488872.2752 | 61260.2321 | 159688.658 | 216714.0847 | 424994.4121 | 79915.4325 | 289941.2246 | 439824.3576 | 769137.1075 |  | 289332.4982 |  | 563628.5542 | 287235820.3623 |  | HI | Hawaii | 1663.577 | 6.569 | 7.397 | #N/A | 0.145 | 0.023 | 1673.732
| ID | 6123.9923 | -0.09678 | 4310507.3167 | -68.121 |  | 4525.3292 | 0.091551 | 0.013877 | 3.183 | 2.0774 | 3185252.9949 | 64.4399 | 9.7673 | 2240.4138 | 1462.2575 |  | 63428.492 | 227008.6677 | 340416.7462 | 676641.0107 | 59.8004 | 136.2561 | 179.8632 | 359.2633 | 77.8264 | 252.1742 | 373.0462 | 662.779 | 35753551.1134 | 141042683.4416 | 215669117.2314 | 427682349.9515 | 35420.1949 | 92245.2092 | 125162.5707 | 245489.3239 | 44344.3341 | 160757.0641 | 243816.4299 | 426423.3759 |  | 692728.8213 |  | 341250.2634 | 146908474.7872 |  | ID | Idaho | 1631.283 | 1.1476 | 0.74801 | 0.092353 | 0.033 | 0.005 | 1633.532
| IL | 15247.4061 | 13.7087 | 10632027.5414 | 9559.1084 |  | 12264.9588 | 1.3143 | 0.18813 | 7.1701 | 9.312 | 8552364.8312 | 916.4658 | 131.1852 | 4999.7253 | 6493.2829 |  | 171909.667 | 615259.5351 | 922628.4225 | 1833894 | 858.4968 | 1956.0981 | 2582.1237 | 5157.5995 | 1055.1435 | 3418.8897 | 5057.6309 | 8985.7267 | 95920525.9116 | 378532653.1553 | 578858093.8089 | 1147883401.3888 | 503428.0333 | 1311707.2 | 1779951.9983 | 3490896.2405 | 595137.5187 | 2158391.129 | 3273870.8746 | 5725503.4059 |  | 1859968.3035 |  | 1225060.9513 | 529295897.1719 |  | IL | Illinois | 1665.8038 | 0.95059 | 1.3461 | 0.14612 | 0.188 | 0.027 | 1678.2228
| IN | 8643.1212 | 16.5463 | 6026854.8023 | 11537.7419 |  | 7918.4433 | 0.72674 | 0.10364 | 5.3185 | 6.0283 | 5521536.3913 | 506.7562 | 72.2684 | 3708.5956 | 4203.5374 |  | 110987.4872 | 397220.8833 | 595662.8969 | 1183989.7688 | 474.7025 | 1081.6169 | 1427.7754 | 2851.8748 | 581.2666 | 1883.4277 | 2786.1917 | 4950.1353 | 61927745.7108 | 244386419.539 | 373719561.0152 | 741090926.173 | 278368.594 | 725303.4492 | 984217.6087 | 1930277.6443 | 327854.5359 | 1189033.2903 | 1803538.4809 | 3154115.147 |  | 1200823.7344 |  | 857821.5888 | 373835694.1622 |  | IN | Indiana | 1790.3963 | 1.1731 | 1.5368 | 0.15831 | 0.181 | 0.026 | 1802.3543
| IA | 5413.7406 | 4.5564 | 3781202.217 | 3182.3803 |  | 4780.1669 | 0.46388 | 0.066766 | 3.3488 | 3.9469 | 3338685.5997 | 323.9929 | 46.6324 | 2338.9357 | 2756.6943 |  | 67000.3802 | 239792.3485 | 359586.8469 | 714745.1184 | 303.002 | 690.3947 | 911.3473 | 1820.3482 | 374.457 | 1213.3206 | 1794.8891 | 3188.9205 | 37496589.7261 | 147883283.2303 | 226117701.8291 | 448410216.1685 | 178166.293 | 463852.5549 | 629334.597 | 1234416.6215 | 211826.1654 | 767703.118 | 1164285.8957 | 2036370.1873 |  | 726097.3442 |  | 425610.8709 | 180383605.8662 |  | IA | Iowa | 1845.9516 | 1.2831 | 1.6071 | 0.15941 | 0.187 | 0.027 | 1858.3426
| KS | 4682.7158 | 6.4066 | 3270621.3386 | 4474.635 |  | 4138.7981 | 0.48876 | 0.07075 | 3.1343 | 2.7257 | 2890724.4863 | 341.3708 | 49.4148 | 2189.1383 | 1903.7793 |  | 58010.7452 | 207618.7149 | 311340.0386 | 618845.6964 | 319.2541 | 727.4254 | 960.2291 | 1917.986 | 396.7999 | 1285.7163 | 1901.9854 | 3379.195 | 32465563.7187 | 128041354.9528 | 195778835.0961 | 388245719.183 | 187722.5765 | 488732.1573 | 663090.1394 | 1300626.8741 | 224465.2775 | 813509.9509 | 1233755.7836 | 2157875.0592 |  | 628674.7613 |  | 423548.5972 | 181354210.6589 |  | KS | Kansas | 1784.7041 | 1.3445 | 1.2827 | 0.085385 | 0.227 | 0.033 | 1799.8051
| KY | 6515.2657 | 8.2452 | 4618296.0881 | 5844.5756 |  | 5521.9294 | 0.5641 | 0.080639 | 3.3773 | 4.0501 | 3914177.3052 | 399.8559 | 57.1602 | 2393.985 | 2870.8849 |  | 77397.166 | 277002.1327 | 415385.7457 | 825655.7115 | 368.4651 | 839.5534 | 1108.2423 | 2213.6314 | 452.2629 | 1465.4282 | 2167.8367 | 3851.5244 | 43902179.4203 | 173244935.5323 | 264928000.088 | 525349968.6915 | 219649.5761 | 572283.994 | 776572.2656 | 1523025.4991 | 259326.0296 | 940459.2359 | 1426491.5163 | 2494713.1621 |  | 851255.2803 |  | 499641.3351 | 218477019.1381 |  | KY | Kentucky | 1716.9562 | 1.0215 | 1.3699 | 0.14678 | 0.188 | 0.027 | 1729.3752
| LA | 5025.5602 | 12.7558 | 3510904.8806 | 8911.3329 |  | 4899.9381 | 0.15917 | 0.021843 | 3.4814 | 3.6584 | 3423144.0682 | 111.1991 | 15.2598 | 2432.1061 | 2555.7596 |  | 68679.1322 | 245800.5514 | 368596.6037 | 732653.6701 | 103.9703 | 236.8978 | 312.7141 | 624.6232 | 122.5067 | 396.9477 | 587.2125 | 1043.2812 | 38410283.1123 | 151545536.9797 | 231736606.2177 | 459538886.9948 | 61104.2992 | 159166.3852 | 215973.6226 | 423588.6527 | 69257.5738 | 251114.7858 | 380874.6612 | 666112.4119 |  | 744465.3719 |  | 470372.8573 | 221912890.998 |  | LA | Louisiana | 1845.3 | 1.2838 | 1.6036 | 0.15862 | 0.064 | 0.009 | 1849.477
| ME | 1930.4684 | 1.5985 | 1353155.0719 | 1120.4866 |  | 1072.6647 | 0.18815 | 0.026432 | 0.2845 | 0.10866 | 751880.6068 | 131.8817 | 18.5271 | 199.42 | 76.1671 |  | 15034.8191 | 53809.1659 | 80690.9329 | 160388.0978 | 122.8973 | 280.0233 | 369.6414 | 738.331 | 148.2418 | 480.3349 | 710.5689 | 1262.4444 | 8443726.4795 | 33302697.4399 | 50921053.8678 | 100980668.2813 | 72519.09 | 188810.7615 | 256171.8606 | 502468.5181 | 84153.2381 | 305003.0581 | 462566.1733 | 809038.6169 |  | 163518.9944 |  | 209337.381 | 99612842.6873 |  | ME | Maine | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.213 | 0.03 | 1139.7557
| MD | 8947.8812 | 6.5737 | 6286759.5217 | 4618.6626 |  | 6715.3984 | 0.61556 | 0.085904 | 3.4256 | 4.8489 | 4718222.5457 | 432.4884 | 60.3557 | 2406.8191 | 3406.8354 |  | 94125.2171 | 336871.325 | 505164.1485 | 1004106.8304 | 402.078 | 916.1409 | 1209.3408 | 2415.568 | 481.7905 | 1561.1039 | 2309.3718 | 4102.9851 | 52931816.4638 | 208860399.7488 | 319385139.9067 | 633346356.7753 | 237619.3599 | 619032.2822 | 839985.1846 | 1647433.5056 | 273878.3652 | 993141.6739 | 1506364.7535 | 2634451.3291 |  | 1026119.0392 |  | 780594.454 | 345655548.2973 |  | MD | Maryland | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.15 | 0.021 | 1576.461
| MA | 7976.9682 | 3.7806 | 5591428.0835 | 2649.9703 |  | 4278.6713 | 0.24633 | 0.029336 | 1.0526 | 0.44824 | 2999119.7711 | 172.6624 | 20.5628 | 737.8259 | 314.1945 |  | 59971.2544 | 214635.3183 | 321861.9685 | 639759.9711 | 160.8998 | 366.6126 | 483.9426 | 966.6392 | 164.5295 | 533.1105 | 788.6409 | 1401.1524 | 33680542.8925 | 132838614.833 | 203115146.2683 | 402794161.7524 | 94943.5804 | 247195.1828 | 335385.8086 | 657842.785 | 93399.3697 | 338514.5244 | 513389.5023 | 897929.7597 |  | 652248.5678 |  | 1117741.1646 | 532091855.9787 |  | MA | Massachusetts | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.067 | 0.008 | 1129.8377
| MI | 16157.2738 | 16.8892 | 11266479.011 | 11776.8806 |  | 14391.1167 | 1.2999 | 0.18495 | 9.9608 | 11.8051 | 10034936.3056 | 906.4493 | 128.9663 | 6945.6448 | 8231.7123 |  | 201710.5903 | 721916.1446 | 1082568.1126 | 2151803.6058 | 849.1139 | 1934.7188 | 2553.9023 | 5101.2293 | 1037.2965 | 3361.0617 | 4972.0847 | 8833.7396 | 112548562.5227 | 444152130.8981 | 679204432.4572 | 1346871543.3123 | 497925.8009 | 1297370.8552 | 1760497.9572 | 3452742.3809 | 585071.1968 | 2121883.4999 | 3218495.7103 | 5628660.6456 |  | 2182397.9477 |  | 1587033.6974 | 683538482.0398 |  | MI | Michigan | 1838.5344 | 1.259 | 1.6104 | 0.16303 | 0.175 | 0.025 | 1850.0594
| MN | 8217.1106 | 3.4884 | 5739203.1288 | 2436.4298 |  | 7081.071 | 0.55145 | 0.078622 | 4.9215 | 6.0541 | 4945741.4663 | 385.1549 | 54.9132 | 3437.3726 | 4228.4375 |  | 99250.6029 | 355214.9269 | 532671.7735 | 1058783.3038 | 360.2015 | 820.7247 | 1083.3877 | 2163.9862 | 440.952 | 1428.7783 | 2113.6199 | 3755.199 | 55545343.553 | 219065995.9416 | 334958072.8072 | 664249727.5528 | 211799.8069 | 551416.7685 | 748137.8428 | 1467444.8104 | 249441.5945 | 904029.4408 | 1371036.1499 | 2397982.4472 |  | 1075599.8541 |  | 663241.8621 | 279571300.681 |  | MN | Minnesota | 1849.2094 | 1.2799 | 1.6243 | 0.16335 | 0.147 | 0.021 | 1858.8904
| MS | 4863.8677 | 12.1034 | 3447715.2912 | 8579.3791 |  | 4382.6981 | 0.094241 | 0.012292 | 2.639 | 2.3316 | 3106641.9394 | 66.8018 | 8.7128 | 1870.6428 | 1652.7134 |  | 61429.3281 | 219853.7204 | 329687.359 | 655314.3767 | 61.5575 | 140.2598 | 185.1483 | 369.8198 | 68.9378 | 223.3732 | 330.4403 | 587.0825 | 34844704.566 | 137502708.8837 | 210270606.5221 | 416964822.5798 | 36695.7073 | 95608.4976 | 129737.872 | 254443.9147 | 39528.704 | 143352.8858 | 217438.1065 | 380265.6378 |  | 675632.489 |  | 442223.3456 | 194917806.1747 |  | MS | Mississippi | 1688.2542 | 0.95749 | 1.0555 | 0.12886 | 0.037 | 0.005 | 1690.6152
| MO | 10107.2037 | 18.6409 | 7059329.9917 | 13019.6803 |  | 9389.2703 | 0.94078 | 0.13487 | 6.78 | 6.9127 | 6557892.6425 | 657.0842 | 94.2019 | 4735.4942 | 4828.1579 |  | 131603.0777 | 471003.4626 | 706305.4808 | 1403912.2921 | 614.513 | 1400.1773 | 1848.2871 | 3691.8157 | 756.4389 | 2451.0232 | 3625.8469 | 6441.9231 | 73651322.5156 | 290474399.603 | 444143531.5994 | 880773576.7845 | 361335.88 | 940731.0905 | 1276342.2677 | 2503498.3258 | 427909.0293 | 1550833.4173 | 2351968.4004 | 4113661.7302 |  | 1426210.4919 |  | 837791.8739 | 360582427.8876 |  | MO | Missouri | 1827.0561 | 1.3021 | 1.507 | 0.13657 | 0.201 | 0.029 | 1840.3691
| MT | 4482.6933 | -4.0331 | 3155242.7555 | -2838.8076 |  | 3128.9228 | 0.47151 | 0.0687 | 2.181 | 1.5885 | 2202361.4808 | 331.881 | 48.3562 | 1535.147 | 1118.0991 |  | 43856.0038 | 156959.3205 | 235372.4274 | 467846.0708 | 307.9861 | 701.7511 | 926.338 | 1850.2912 | 385.3052 | 1248.471 | 1846.8877 | 3281.3047 | 24720875.8294 | 97520345.6838 | 149118879.14 | 295709990.7092 | 182422.41 | 475084.7203 | 644616.9438 | 1264328.2801 | 219541.1609 | 795880.5378 | 1207093.1524 | 2111148.6926 |  | 478969.5748 |  | 291016.3509 | 123583886.0139 |  | MT | Montana | 1647.0568 | 1.1592 | 0.78191 | 0.090794 | 0.234 | 0.034 | 1662.6188
| NE | 3315.057 | 5.4934 | 2315386.2876 | 3836.8483 |  | 2988.0449 | 0.37106 | 0.053193 | 2.2422 | 1.8871 | 2086986.2459 | 259.1672 | 37.1524 | 1566.0516 | 1318.0599 |  | 41881.4135 | 149892.3209 | 224774.9245 | 446781.5812 | 242.3763 | 552.258 | 729.0015 | 1456.1261 | 298.3328 | 966.6618 | 1430.0019 | 2540.6374 | 23438824.8574 | 92440683.2805 | 141344406.2258 | 280297717.6807 | 142518.1177 | 371043.2085 | 503414.9875 | 987429.9474 | 168763.5331 | 611634.9712 | 927595.5166 | 1622391.7707 |  | 453877.7688 |  | 253162.0778 | 108198333.4581 |  | NE | Nebraska | 1788.6358 | 1.3323 | 1.2542 | 0.083521 | 0.243 | 0.035 | 1804.7148
| NV | 11181.3827 | 15.2467 | 7870263.3316 | 10731.7512 |  | 9101.8629 | 0.26438 | 0.032016 | 6.4831 | 3.7973 | 6406547.4133 | 186.0889 | 22.5351 | 4563.2675 | 2672.791 |  | 127574.683 | 456585.9589 | 684685.3384 | 1360938.2752 | 172.6908 | 393.4786 | 519.4067 | 1037.4761 | 179.5612 | 581.8165 | 860.6926 | 1529.1643 | 71911656.8655 | 283681277.501 | 433778549.8744 | 860203964.065 | 102286.0018 | 266384.577 | 361442.9271 | 708921.0404 | 102311.2872 | 370898.8416 | 562533.4842 | 983844.3928 |  | 1393295.9314 |  | 714941.4036 | 313462360.9921 |  | NV | Nevada | 1631.283 | 1.1476 | 0.74801 | 0.092353 | 0.049 | 0.006 | 1634.245
| NH | 2084.2821 | 0.56383 | 1460970.3046 | 395.2157 |  | 1094.8895 | 0.18586 | 0.024635 | 0.25658 | 0.117 | 767459.006 | 130.2763 | 17.2681 | 179.8459 | 82.0142 |  | 15346.3292 | 54924.0512 | 82362.7882 | 163711.2183 | 121.4012 | 276.6145 | 365.1416 | 729.3431 | 138.1676 | 447.6924 | 662.2802 | 1176.6514 | 8618674.1254 | 33992704.22 | 51976099.7085 | 103072911.5868 | 71636.2963 | 186512.319 | 253053.4139 | 496351.8381 | 78434.3696 | 284275.723 | 431131.1965 | 754058.1371 |  | 166906.9846 |  | 272659.0971 | 129807362.2345 |  | NH | New Hampshire | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.196 | 0.026 | 1138.2197
| NJ | 8125.2023 | 2.8138 | 5655654.0977 | 1958.6013 |  | 5926.2501 | 0.15033 | 0.018718 | 2.9733 | 4.4022 | 4125044.4423 | 104.6399 | 13.0289 | 2069.5811 | 3064.2377 |  | 83064.2564 | 297284.479 | 445800.6651 | 886110.9683 | 98.1954 | 223.7397 | 295.3449 | 589.9294 | 104.9799 | 340.1574 | 503.2015 | 894.0216 | 46367414.9382 | 182803394.3996 | 279489854.8962 | 554267655.5044 | 57581.93 | 149841.0672 | 203276.7826 | 398751.273 | 59230.8017 | 214577.3043 | 325393.9742 | 569162.5182 |  | 897114.6653 |  | 847577.4179 | 410335400.0725 |  | NJ | New Jersey | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.04 | 0.005 | 1569.141
| NM | 8203.0778 | 2.1164 | 5773917.6338 | 1489.6629 |  | 6242.3776 | 0.57512 | 0.082066 | 4.2412 | 2.387 | 4393835.4505 | 404.8116 | 57.7636 | 2985.26 | 1680.1148 |  | 87495.2027 | 313142.7027 | 469581.2765 | 933379.3155 | 375.6659 | 855.9604 | 1129.9002 | 2256.8913 | 460.2646 | 1491.3554 | 2206.1915 | 3919.6679 | 49319542.4709 | 194558593.4709 | 297500579.8228 | 589958120.6801 | 222509.6055 | 579484.2513 | 786271.0609 | 1542163.5248 | 262251.9156 | 950715.5504 | 1441927.7471 | 2521863.2645 |  | 955571.3338 |  | 596048.4581 | 257349703.7725 |  | NM | New Mexico | 1647.0009 | 1.1153 | 0.64146 | 0.078178 | 0.154 | 0.022 | 1657.1429
| NY | 18431.8761 | 2.8091 | 12829750.1364 | 1955.2767 |  | 9577.7122 | 0.32058 | 0.042089 | 3.7947 | 1.6863 | 6666692.744 | 223.1418 | 29.2964 | 2641.3167 | 1173.7889 |  | 134244.3417 | 480456.467 | 720480.9792 | 1432088.7072 | 209.3991 | 477.119 | 629.8152 | 1258.0089 | 236.0542 | 764.866 | 1131.4813 | 2010.2658 | 74936722.0293 | 295437801.9647 | 451697675.9276 | 895779962.8405 | 122791.9426 | 319532.1124 | 433482.362 | 850326.5425 | 133184.3184 | 482491.0557 | 731669.5613 | 1279799.0223 |  | 1449872.338 |  | 2237269.4316 | 1082723693.4024 |  | NY | New York | 1127.4907 | 0.43932 | 0.20164 | 0.056817 | 0.038 | 0.005 | 1129.8797
| NC | 21261.0198 | 51.4256 | 14937940.6556 | 36131.5138 |  | 19198.7697 | 1.2878 | 0.17892 | 11.8678 | 6.7459 | 13489008.7259 | 904.834 | 125.7112 | 8338.2744 | 4739.6811 |  | 269096.2247 | 963087.3062 | 1444222.5947 | 2870658.5299 | 841.2107 | 1916.7114 | 2530.1319 | 5053.7497 | 1003.4926 | 3251.5297 | 4810.0519 | 8545.8613 | 151327693.2654 | 597114639.5496 | 913095746.8348 | 1810684945.4982 | 497137.2239 | 1295113.287 | 1757381.65 | 3446691.0432 | 570444.8072 | 2068555.1788 | 3137516.725 | 5487140.5395 |  | 2933589.6177 |  | 1817950.2381 | 817571208.2952 |  | NC | North Carolina | 1700.8692 | 0.99862 | 0.69818 | 0.12541 | 0.128 | 0.018 | 1709.2232
| ND | 1426.0168 | -3.4175 | 995994.9088 | -2386.9693 |  | 990.5476 | 0.13807 | 0.020339 | 0.69836 | 0.94688 | 691843.403 | 96.4321 | 14.2054 | 487.7691 | 661.3465 |  | 13883.8383 | 49689.8403 | 74513.6912 | 148109.6917 | 90.1845 | 205.4867 | 271.2503 | 541.8022 | 114.0688 | 369.6072 | 546.7672 | 971.4233 | 7770054.2509 | 30644417.0496 | 46856176.0721 | 92919695.6777 | 53028.8076 | 138059.492 | 187313.0025 | 367407.5521 | 64527.4407 | 233861.1819 | 354670.014 | 620328.2592 |  | 150462.1033 |  | 77629.1137 | 31331680.4003 |  | ND | North Dakota | 1819.2372 | 1.3099 | 1.4656 | 0.12712 | 0.219 | 0.032 | 1833.8492
| OH | 16588.2861 | 26.8941 | 11567024.1481 | 18753.3041 |  | 13249.9314 | 1.3446 | 0.19088 | 6.991 | 8.9933 | 9239186.9992 | 937.5791 | 133.1015 | 4874.8067 | 6271.0353 |  | 185715.3655 | 664669.7153 | 996722.7422 | 1981170.1135 | 878.2746 | 2001.162 | 2641.6098 | 5276.4186 | 1070.5569 | 3468.8324 | 5131.5121 | 9116.9891 | 103623698.6432 | 408931802.7021 | 625344951.9793 | 1240067467.6516 | 515025.8448 | 1341925.8845 | 1820957.9543 | 3571318.3744 | 603831.2181 | 2189920.6548 | 3321695.1984 | 5809140.8917 |  | 2009338.3886 |  | 1501423.369 | 649929761.1588 |  | OH | Ohio | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.175 | 0.025 | 1578.221
| OK | 4412.9707 | 10.3116 | 3082943.9378 | 7203.7618 |  | 4139.5065 | 0.17286 | 0.02309 | 3.1333 | 2.6044 | 2891899.2454 | 120.7651 | 16.1312 | 2188.9518 | 1819.4718 |  | 58020.6753 | 207654.2544 | 311393.3328 | 618951.6285 | 112.9145 | 257.2773 | 339.6158 | 678.3572 | 129.5026 | 419.6159 | 620.7461 | 1102.8591 | 32449311.666 | 128026870.9989 | 195772921.996 | 388222094.6708 | 66360.8766 | 172858.882 | 234553.0365 | 460028.4215 | 73212.6166 | 265455.0185 | 402624.9984 | 704151.6175 |  | 628930.2479 |  | 381264.4085 | 180042794.4397 |  | OK | Oklahoma | 1787.9619 | 1.3413 | 1.2999 | 0.089322 | 0.081 | 0.011 | 1793.1449
| OR | 4628.7047 | 14.5913 | 3331612.1766 | 10502.3921 |  | 4218.4492 | 0.23144 | 0.030911 | 3.0443 | 1.5742 | 3036321.7267 | 166.5812 | 22.2486 | 2191.166 | 1133.0581 |  | 59127.1608 | 211614.3327 | 317331.7711 | 630755.3689 | 151.1728 | 344.4495 | 454.6864 | 908.2021 | 173.3621 | 561.7302 | 830.9785 | 1476.3723 | 34027429.6214 | 134328193.4079 | 205431601.5431 | 407362493.3835 | 91446.6536 | 238376.3968 | 323501.5141 | 634413.4763 | 100857.8868 | 365922.5546 | 555083.7165 | 970695.4078 |  | 660339.2491 |  | 423325.6843 | 219745614.2662 |  | OR | Oregon | 1631.283 | 1.1476 | 0.74801 | 0.092353 | 0.103 | 0.014 | 1637.877
| PA | 13311.7242 | 21.9243 | 9265800.9536 | 15260.6934 |  | 10651.4017 | 0.68091 | 0.092843 | 5.625 | 7.217 | 7414048.4354 | 473.9555 | 64.6245 | 3915.3542 | 5023.4974 |  | 149293.5237 | 534317.0376 | 801248.9973 | 1592630.0261 | 444.7659 | 1013.4058 | 1337.7342 | 2672.0242 | 520.7092 | 1687.2087 | 2495.9211 | 4434.421 | 83337347.0247 | 328557240.8267 | 502334302.1904 | 996199508.0571 | 260811.3809 | 678689.576 | 920721.1079 | 1806102.5427 | 293789.6827 | 1064321.2041 | 1613981.0661 | 2823093.2373 |  | 1612407.2537 |  | 1180239.0111 | 573026361.4149 |  | PA | Pennsylvania | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.109 | 0.015 | 1573.723
| RI | 1508.0639 | -0.25043 | 1057072.1692 | -175.5413 |  | 756.3669 | 0.011366 | 0.0013417 | 0.15698 | 0.084479 | 530172.7558 | 7.9667 | 0.94049 | 110.0335 | 59.2151 |  | 10601.4856 | 37942.3987 | 56897.5099 | 113094.2853 | 7.4239 | 16.9155 | 22.3292 | 44.6008 | 7.5251 | 24.383 | 36.0703 | 64.0849 | 5953915.6832 | 23482694.8814 | 35905907.4171 | 71204388.9673 | 4380.705 | 11405.607 | 15474.7301 | 30352.9227 | 4271.8323 | 15482.7305 | 23481.0347 | 41068.8566 |  | 115301.9709 |  | 198212.8697 | 94396824.1199 |  | RI | Rhode Island | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.017 | 0.002 | 1126.8477
| SC | 10024.4752 | 19.2907 | 7043171.8173 | 13553.5958 |  | 8807.8215 | 0.57022 | 0.079298 | 5.4224 | 3.0853 | 6188353.9281 | 400.6336 | 55.7149 | 3809.7939 | 2167.7395 |  | 123453.3028 | 441835.6631 | 662566.1491 | 1316972.3106 | 372.4631 | 848.6629 | 1120.2672 | 2237.6502 | 444.7451 | 1441.0689 | 2131.8017 | 3787.502 | 69424621.4882 | 273938344.934 | 418901030.199 | 830688119.6898 | 220117.5882 | 573437.6738 | 778116.3667 | 1526092.3612 | 252819.5551 | 916777.9133 | 1390538.7032 | 2431885.4557 |  | 1345843.2123 |  | 947637.3341 | 423765326.0692 |  | SC | South Carolina | 1706.4597 | 1.008 | 0.6775 | 0.12495 | 0.121 | 0.017 | 1714.3527
| SD | 1555.7934 | 1.5323 | 1086636.7568 | 1070.2534 |  | 1371.4671 | 0.072861 | 0.010038 | 0.94992 | 0.84086 | 957894.8961 | 50.8897 | 7.0109 | 663.4668 | 587.2915 |  | 19222.9308 | 68798.292 | 103168.2664 | 205065.94 | 47.5927 | 108.4407 | 143.1458 | 285.9231 | 56.2975 | 182.4159 | 269.8515 | 479.4363 | 10758063.5696 | 42428865.4913 | 64874929.3804 | 128652382.6842 | 27984.6828 | 72857.5892 | 98849.9494 | 193890.5332 | 31846.8758 | 115419.8575 | 175043.8536 | 306156.835 |  | 208322.982 |  | 118985.7712 | 50459315.9139 |  | SD | South Dakota | 1825.5667 | 1.2518 | 1.1911 | 0.093422 | 0.101 | 0.014 | 1832.1047
| TN | 11761.3016 | 23.744 | 8336908.379 | 16830.7186 |  | 9457.8356 | 0.73951 | 0.10382 | 4.108 | 4.1879 | 6704114.1676 | 524.1979 | 73.5929 | 2911.8889 | 2968.5834 |  | 132564.1117 | 474442.9742 | 711463.2898 | 1414164.3879 | 483.0457 | 1100.6269 | 1452.8693 | 2901.998 | 582.2816 | 1886.7165 | 2791.0568 | 4958.779 | 75194657.8019 | 296729998.722 | 453762673.5582 | 899807518.5256 | 287953.3762 | 750245.5101 | 1018060.7209 | 1996636.3806 | 333878.3163 | 1210826.9531 | 1836586.117 | 3211905.2284 |  | 1458010.7492 |  | 1025847.5807 | 450804908.8362 |  | TN | Tennessee | 1530.8895 | 0.57635 | 0.78394 | 0.10455 | 0.134 | 0.019 | 1539.6765
| TX | 27182.7099 | 54.71 | 18990103.6334 | 38220.9019 |  | 19776.7016 | 1.1173 | 0.15364 | 11.3384 | 8.8095 | 13816194.7192 | 780.5247 | 107.3343 | 7921.0825 | 6154.4125 |  | 277196.7071 | 992078.6893 | 1487697.3764 | 2957072.6695 | 729.7845 | 1662.825 | 2194.9921 | 4384.3331 | 861.6892 | 2792.0566 | 4130.3443 | 7338.247 | 155028225.5515 | 611654843.0411 | 935315023.642 | 1854750667.0141 | 428901.1579 | 1117215.1191 | 1515954.4913 | 2973238.6421 | 487144.9592 | 1766294.9392 | 2679001.8928 | 4685311.4528 |  | 3004746.0275 |  | 2243030.5169 | 1056230002.9469 |  | TX | Texas | 1362.7204 | 0.72652 | 0.7134 | 0.072999 | 0.086 | 0.012 | 1368.3084
| UT | 10024.2841 | 2.808 | 7055813.9593 | 1976.4607 |  | 7603.22 | 0.76214 | 0.1094 | 5.3245 | 3.3773 | 5351694.4604 | 536.4475 | 77.0041 | 3747.7566 | 2377.1684 |  | 106569.2143 | 381408.0173 | 571950.3028 | 1136856.6185 | 497.8243 | 1134.3001 | 1497.3192 | 2990.7834 | 613.5743 | 1988.1114 | 2941.0524 | 5225.2712 | 60071235.0758 | 236972494.4489 | 362355901.34 | 718569377.9124 | 294864.9002 | 767919.9535 | 1041949.3458 | 2043641.6341 | 349605.4752 | 1267389.6432 | 1922219.8397 | 3361871.3628 |  | 1163886.5112 |  | 608237.5713 | 263022335.1997 |  | UT | Utah | 1638.8345 | 1.1443 | 0.74272 | 0.090746 | 0.167 | 0.024 | 1649.8705
| VT | 797.22 | 0.18161 | 558808.615 | 127.301 |  | 416.9329 | 0.35957 | 0.047382 | 0.096656 | 0.044744 | 292247.684 | 252.0402 | 33.2123 | 67.7505 | 31.3632 |  | 5843.868 | 20915.0282 | 31363.674 | 62341.0814 | 234.8699 | 535.1547 | 706.4245 | 1411.0303 | 265.7428 | 861.0631 | 1273.7877 | 2263.0967 | 3281983.184 | 12944390.5183 | 19792450.9886 | 39250069.9798 | 138591.8069 | 360837.7405 | 489572.0701 | 960271.5613 | 150855.6901 | 546757.8889 | 829210.3889 | 1450307.5772 |  | 63558.0263 |  | 98855.4852 | 47068699.7131 |  | VT | Vermont | 1125.8417 | 0.24547 | 0.12362 | 0.032952 | 0.994 | 0.131 | 1188.3887
| VA | 15143.4484 | 21.6678 | 10639749.9151 | 15223.7753 |  | 11938.9216 | 0.63383 | 0.084673 | 6.2565 | 8.2092 | 8388257.1497 | 445.3299 | 59.4914 | 4395.8023 | 5767.7644 |  | 167339.8229 | 598904.2002 | 898102.3552 | 1785143.9218 | 414.0166 | 943.3431 | 1245.2488 | 2487.2915 | 474.8913 | 1538.7488 | 2276.3015 | 4044.2301 | 94104439.4568 | 371320921.0671 | 567816515.0881 | 1125990148.6117 | 244674.8008 | 637412.7107 | 864926.1903 | 1696349.426 | 269956.4091 | 978919.8202 | 1484793.5117 | 2596725.8138 |  | 1824278.1649 |  | 1140220.1336 | 508628509.0532 |  | VA | Virginia | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.089 | 0.012 | 1572.368
| WA | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | WA | Washington | 1631.283 | 1.1476 | 0.74801 | 0.092353 | 0.132 | 0.019 | 1640.014
| WV | 3722.8409 | 8.6107 | 2615658.9629 | 6049.8285 |  | 3113.7593 | 0.40575 | 0.058303 | 1.6811 | 2.019 | 2187719.6982 | 285.0769 | 40.9632 | 1181.1082 | 1418.5657 |  | 43643.4673 | 156198.6588 | 234231.7574 | 465578.779 | 265.0317 | 603.8788 | 797.143 | 1592.2336 | 326.9897 | 1059.5164 | 1567.3635 | 2784.6833 | 24543135.9834 | 96843251.0926 | 148090759.8397 | 293666584.6256 | 156627.9798 | 408038.1996 | 553680.4013 | 1085913.9674 | 185880.4027 | 674042.1944 | 1022365.1174 | 1787994.0009 |  | 475785.28 |  | 335187.8272 | 150482317.5511 |  | WV | West Virginia | 1566.696 | 0.77363 | 1.1945 | 0.13642 | 0.235 | 0.034 | 1582.286
| WI | 8514.1048 | 7.6705 | 5936891.599 | 5348.6696 |  | 7560.2605 | 0.6258 | 0.089609 | 5.2734 | 6.2873 | 5271775.23 | 436.374 | 62.4847 | 3677.153 | 4384.1481 |  | 105967.0795 | 379252.9951 | 568718.6831 | 1130433.179 | 408.7721 | 931.3935 | 1229.4747 | 2455.7841 | 502.5742 | 1628.4476 | 2408.9946 | 4279.9815 | 59126506.2392 | 233331844.9395 | 356814731.4657 | 707568421.3472 | 239706.581 | 624567.6193 | 847521.7503 | 1662185.5503 | 283469.2931 | 1028060.8909 | 1559373.8146 | 2727108.1934 |  | 1146505.677 |  | 800895.8682 | 343944405.0909 |  | WI | Wisconsin | 1849.861 | 1.2792 | 1.6278 | 0.16413 | 0.16 | 0.023 | 1860.436
| WY | 2534.2202 | -1.8697 | 1783766.903 | -1316.0485 |  | 1883.0227 | 0.28538 | 0.04118 | 1.19 | 0.78207 | 1325407.1798 | 200.8684 | 28.9855 | 837.5828 | 550.4796 |  | 26393.0616 | 94459.9749 | 141649.9098 | 281555.2972 | 186.4062 | 424.7294 | 560.6589 | 1119.8744 | 230.9581 | 748.3534 | 1107.0539 | 1966.8662 | 14877315.3734 | 58688897.1118 | 89741504.6462 | 177961768.8799 | 110409.7549 | 287541.3581 | 390149.4272 | 765224.9279 | 131596.4635 | 477063.4522 | 723550.8334 | 1265456.1025 |  | 288249.5535 |  | 159423.9004 | 67937092.1288 |  | WY | Wyoming | 1726.9345 | 1.1062 | 0.68092 | 0.071997 | 0.25 | 0.036 | 1743.4745
Table 7. Greenhouse Gas Emission Factors by Fuel Type
| GHG | Electricity | Natural Gas
|  | lb/MWh | (lb/mmcf)
| CO2 | #N/A | 120000
| SO2 | #N/A | 0.6
| NOX | #N/A | 96
| N2O | #N/A | 0.23
| CH4 | #N/A | 2.3
Table 8. Societal Benefits of Standard 90.1-2019
| Statewide Impact | First Year | 30 Years Cumulative
| Energy cost savings, $ | #N/A | #N/A
| CO2 emission reduction, Metric tons | #N/A | #N/A |  | #N/A | MMT CO2 emission reduction
| Social cost of carbon savings, $ | #N/A | #N/A
| CH4 emissions reductions, Metric tons | #N/A | #N/A
| Social Cost of CH4 savings, $ | #N/A | #N/A
| N2O emissions reductions, Metric tons | #N/A | #N/A
| Social Cost of N2O savings, $ | #N/A | #N/A
| NOx emissions reductions, Metric tons | #N/A | #N/A
| SOx emissions reductions, Metric tons | #N/A | #N/A
Table 9. Jobs Created from Standard 90.1-2019
| Statewide Impact | First Year | 30 Years Cumulative
Jobs Created Reduction in Utility Bills (millions)
Jobs Created Construction Related Activities (millions)

## Jobs (hidden)
State | US
Table 9. Jobs Created from Standard 90.1-2019
Statewide Impact | First Year | 30 Years Cumulative |  |  | COM | COM | COM | COM
Jobs Created Reduction in Utility Bills | #NAME? | #NAME? | #NAME? |  | 1 | 1 | 30 | 30
Jobs Created Construction Related Activities | #NAME? | #NAME? |  | state | cost | savings | cost | savings
|  |  |  | AK | -8 | 11.2 | -262 | 368.1
|  |  |  | AL | 56.7 | 69.5 | 1827 | 2237.9
|  |  |  | AR | 25 | 23.6 | 791.1 | 747.7
|  |  |  | AZ | 408.8 | 199.6 | 13031.1 | 6364
|  |  |  | CO | 210.3 | 136.9 | 6704.1 | 4362.6
|  |  |  | CT | 68 | 49.4 | 2154.5 | 1565.3
|  |  |  | DC | 3.8 | 4.9 | 122.3 | 156
|  |  |  | DE | 26.1 | 18.1 | 832.9 | 576.5
|  |  |  | FL | 652.9 | 393.8 | 20816 | 12555.6
|  |  |  | GA | 351.4 | 165 | 11205.2 | 5261.6
|  |  |  | HI | 2.7 | 69.2 | 88.4 | 2266.2
|  |  |  | IA | 12.5 | 31.5 | 395.7 | 994.1
|  |  |  | ID | 24.7 | 30.4 | 787.1 | 968.8
|  |  |  | IL | 417.4 | 91.5 | 13205.7 | 2894.8
|  |  |  | IN | 91.9 | 77.5 | 2907.8 | 2452.5
|  |  |  | KS | 28.6 | 32.3 | 901.9 | 1019
|  |  |  | KY | 41.9 | 40.9 | 1349.9 | 1318.1
|  |  |  | LA | 44 | 48.4 | 1394.7 | 1533
|  |  |  | MA | 142.2 | 92.1 | 4505.7 | 2920.1
|  |  |  | MD | 133.9 | 60.4 | 4269.2 | 1925.4
|  |  |  | ME | 11.5 | 22.7 | 364 | 718.4
|  |  |  | MI | 186.4 | 126.7 | 5895.7 | 4007.9
|  |  |  | MN | 138.2 | 42.3 | 4361.9 | 1335.6
|  |  |  | MO | 173.1 | 72.9 | 5465 | 2302.9
|  |  |  | MS | -2.5 | 37.7 | -81.3 | 1215
|  |  |  | MT | 23.2 | 24.7 | 738.7 | 788.5
|  |  |  | NC | 325 | 164.6 | 10362.4 | 5249.4
|  |  |  | ND | -2 | 3.2 | -64 | 102.6
|  |  |  | NE | 4.4 | 15.8 | 140.4 | 499.6
|  |  |  | NH | 16.1 | 25 | 508.7 | 792.8
|  |  |  | NJ | 182.1 | 78.7 | 5711.9 | 2469.4
|  |  |  | NM | -5.3 | 45.7 | -168.5 | 1457.3
|  |  |  | NV | 146.4 | 66.3 | 4666.9 | 2112.6
|  |  |  | NY | 383.6 | 182.5 | 12030.1 | 5723.7
|  |  |  | OH | 335.5 | 133.7 | 10612.9 | 4229.7
|  |  |  | OK | 34.4 | 29.7 | 1091.3 | 941.8
|  |  |  | OR | 82.2 | 48.8 | 2693.2 | 1597.9
|  |  |  | PA | 267.2 | 112.2 | 8380.2 | 3519.3
|  |  |  | RI | 227 | 118.4 | 7118.9 | 3712.2
|  |  |  | SC | 98.4 | 88.4 | 3138.8 | 2817.9
|  |  |  | SD | 2.3 | 8.8 | 72 | 276.8
|  |  |  | TN | 93.9 | 93.3 | 3024.8 | 3005.5
|  |  |  | TX | 353.9 | 173.2 | 11212.7 | 5487.4
|  |  |  | UT | 159.7 | 56.8 | 5091.8 | 1809.1
|  |  |  | VA | 213.5 | 92.4 | 6806.7 | 2946.6
|  |  |  | VT | -4.7 | 9.3 | -148.8 | 295.1
|  |  |  | WI | 106.1 | 71.3 | 3358 | 2255.5
|  |  |  | WV | 41.6 | 29.2 | 1325.9 | 931.2
|  |  |  | WY | -10.7 | 10 | -340.4 | 317.8

## reportNo (hidden)
state | abbr | code | Report Number:
Alabama | AL | 31490 | PNNL-
Alaska | AK | 31491
Arizona | AZ | 31492
Arkansas | AR | 31493
California | CA
Colorado | CO | 31494
Connecticut | CT | 31495
Delaware | DE | 31496
District of Columbia | DC | 31497
Florida | FL | 31498
Georgia | GA | 31499
Hawaii | HI | 31500
Idaho | ID | 31501
Illinois | IL | 31502
Indiana | IN | 31503
Iowa | IA | 31504
Kansas | KS | 31505
Kentucky | KY | 31506
Louisiana | LA | 31507
Maine | ME | 31508
Maryland | MD | 31509
Massachusetts | MA | 31510
Michigan | MI | 31511
Minnesota | MN | 31512
Mississippi | MS | 31513
Missouri | MO | 31514
Montana | MT | 31515
Nebraska | NE | 31516
Nevada | NV | 31517
New Hampshire | NH | 31518
New Jersey | NJ | 31519
New Mexico | NM | 31520
New York | NY | 31521
North Carolina | NC | 31522
North Dakota | ND | 31523
Ohio | OH | 31524
Oklahoma | OK | 31525
Oregon | OR | 31526
Pennsylvania | PA | 31527
Rhode Island | RI | 31528
South Carolina | SC | 31529
South Dakota | SD | 31530
Tennessee | TN | 31531
Texas | TX | 31532
US National | US
Utah | UT | 31533
Vermont | VT | 31534
Virginia | VA | 31535
Washington | WA
West Virginia | WV | 31536
Wisconsin | WI | 31537
Wyoming | WY | 31487

## Instructions (hidden)
Setup:
Update state energy prices, HVAC data & Energy Savings
Update cost effectiveness inputs
Extrapolating State reports
| 1 | Select state on State Inputs tab
| 2 | On EndUse Tables tab, refresh pivot table to right (right-click on table)
| 3 | On developer tab select appropriate Export Macro: based on # of climate zones in state
|  |  | Export_1 | 1 CZ | should be OK
|  |  | Export_2 | 2 CZ | needs row deletions on Result Tables to be updated
|  |  | Export_3 | 3 CZ | Has been verified
|  |  | Export_4 | 4 CZ | needs to be created
|  |  | Export_5 | 5 CZ | should be OK
| 4 | Review results in new spreadsheet
| 5 | Rename spreadsheet with state abbreviation at beginning of filename (save as)
| 6 | With new spreadsheet selected, use the "Print_PDF" Macro
| 7 | You will have to select names for the three pdf files saved from the spreadsheet; usually add state abbreviation and 1,2,3
| 8 | Look over the pdf printouts to make sure the results aligned properly
| 9 | Using AcrobatPro, paste the pages into one document in order, removing blank pages where necessary.
| 10 | Insert disclaimer sheet into pdf after cover before first page
| 11 | Insert references sheet into pdf (references from spreadsheet will not have proper hyperlinks)
| 12 | Insert footers into pdf using the following:
Footers start on 3rd page
|  |  | Left | paste values from | $k$1 | StateInputs tab
|  |  | Center | Page #
|  |  | Right | paste values from | $p$1 | StateInputs tab

## StateReport (hidden)
PNNL - 00000
Cost-Effectiveness of
ASHRAE Standard 90.1-2022
for the State of US National
M Tyler
R Hart
Y Xie
M Rosenberg
April 2020
ASHRAE Standard 90.1-2022 Provides Cost-Effective Savings
for Commercial Buildings in the State of US National | [5 empty] | Phrases to be insert at bookmarks on certain conditions:
Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 shows the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional construction cost per square foot required by the upgrade, and the simple payback period in years. The results shown are weighted averages for all building types in all climate zones in the state, based on weightings shown in Table 6. |  |  |  | Cost effetiveness highlight: |  | for all building types and climate zones in
|  |  |  | Table call-out: |  | Tables 15.A through 15.E show
Tables 13.A and 13.B show
Tables 14.A and 14.B show
Table 13.A
Table 14.A
Table 1. US National Average Savings and Cost (Weighted by Climate Zone and Building Type) | [5 empty] | net of an allowance to pay for the added cost
US National Average Savings and Cost (Weighted by Climate Zone and Building Type)
Annual Cost Savings, $/ft2 |  |  | 0.1857 |  | Annual Energy Savings | 0.1857 | #N/A
Added Construction Cost, $/ft2 |  |  | 1.0851 |  | Added First Costs | 1.0851 | #N/A
State of US National Average Simple Payback, years |  |  | 5.8432 |  | Annual Net LCC Savings | 0.13133 | #N/A
0.051
—
Table 2. US National Average LCC Results (Weighted by Climate Zone and Building Type)
Weighted Net Life Cycle Cost Savings, by Ownership Scenario
Scenario 1 (Publicly-Owned), $/ft2 |  |  | 2.5751 |  | Scenario 1: Publicly-Owned | 2.5751
Scenario 2 (Privately-Owned), $/ft2 |  |  | 2.5462 |  | Scenario 2: Privately-Owned | 2.5462
Figure 1. Statewide Weighted Costs and Savings |  | Figure 2. Overall Net Life Cycle Cost Savings
The report provides analysis of two Life Cycle Cost (LCC) scenarios:
Scenario 1, representing publicly-owned buildings, considers initial costs, energy costs, maintenance costs, and replacement costs—without borrowing or taxes.
Scenario 2, representing privately-owned buildings, adds borrowing costs and tax impacts.
Table 2 shows the statewide weighted average LCC net present value of savings from both scenarios; that is, the remaining savings after initial and replacement costs have been paid for. Figure 1 compares annual energy cost savings, first cost for the upgrade, and net annualized LCC savings. The net annualized LCC savings per square foot is the annual energy savings net of an allowance to pay for the added cost under Scenario 1. Figure 2 shows overall state weighted net LCC results for both scenarios. When net LCC is positive, a proposed code is considered cost-effective.

## Result Tables (hidden)
3 CZ | 1 | 2 | 3 | 4 | 5 | 6
Cost-Effectiveness Results for Standard 90.1-2022 in the State of US National
Life Cycle Cost (LCC) savings is the primary measure DOE uses to assess the economic impact of building energy codes.
Table 3 shows that the value today of the total
LCC savings over 30 years for buildings in scenario 1
averages $2.58 per square foot for 90.1-2022.
Table 4 shows that the LCC savings over 30 years
averages $2.55 per square foot for scenario 2.
Table 5 shows that the primary benefit of ASHRAE
Standard 90.1-2022—annual energy cost savings—
averages $0.186 per square foot for both scenarios.
3 CZ: Table 1. LCC Savings (30 Years) from ASHRAE Standard 90.1-2019, Scenario 1 ($/ft2) |  | 1.093 | 0.34478
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 1.23 | 0.94 | 3.54 | 1.36 | 2.17 | 3.1 | 2.5264 | 1
3A | 1.13 | 1.61 | 3.33 | 1.09 | 1.87 | 2.76 | 2.3348 | 2
3B | 1.17 | 1.72 | 3.03 | 1.2 | 2.07 | 3.27 | 2.5927 | 3
4A | 0.95 | 1.44 | 3.46 | 0.98 | 2.31 | 3.33 | 2.6098 | 4
5A | 0.96 | 1.49 | 3.68 | 1.08 | 2.49 | 3.3 | 2.7874 | 5
State Average | 1.0864 | 1.4116 | 3.4676 | 1.1405 | 2.201 | 3.1702 | 2.5751 |  | 1.0864
0.94
3 CZ: Table 2. LCC Savings (30 Years) from ASHRAE Standard 90.1-2019, Scenario 2 ($/ft2) |  |  |  |  | Public LCC | [8 empty] | Private LCC
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types |  |  |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 1.23 | 1.15 | 3.43 | 1.48 | 2.27 | 3.02 | 2.509 | 1 |  |  | 2A | -6784.4434 | -466341.5555 | -87307.64 | -100793.2037 | -93617.24 | -104708.6253 | -117298.2315 |  | 2A | -6773.0988 | -574048.0395 | -84605.9228 | -109195.6305 | -97865.5107 | -101958.8064 | -125915.612
3A | 1.13 | 1.67 | 3.25 | 1.23 | 1.98 | 2.71 | 2.3285 | 2 |  |  | 3A | -6212.6212 | -803808.8737 | -82241.5292 | -80647.6133 | -80573.678 | -93013.8543 | -141573.4194 |  | 3A | -6229.8747 | -834139.7201 | -80136.051 | -91202.4645 | -85533.5462 | -91314.62 | -145064.4458
3B | 1.17 | 1.76 | 2.96 | 1.32 | 2.16 | 3.15 | 2.5471 | 3 |  |  | 3B | -6434.7185 | -857002.2787 | -74763.373 | -89031.395 | -89337.7925 | -110271.009 | -150916.6534 |  | 3B | -6446.1788 | -879952.4182 | -73203.6916 | -97976.0062 | -93299.1907 | -106370.0071 | -152106.6463
4A | 1.02 | 1.52 | 3.37 | 1.14 | 2.39 | 3.21 | 2.5793 | 4 |  |  | 4A | -5250.1089 | -715584.9381 | -85438.3905 | -72600.8128 | -99607.3127 | -112356.7327 | -179728.9497 |  | 4A | -5630.0286 | -758323.9822 | -83198.048 | -84516.4123 | -103046.9931 | -108305.5645 | -185275.3206
5A | 1.04 | 1.57 | 3.54 | 1.24 | 2.55 | 3.19 | 2.7367 | 5 |  |  | 5A | -5268.144 | -743133.118 | -90861.5717 | -80093.9057 | -107474.9775 | -111277.642 | -134912.7184 |  | 5A | -5731.0489 | -782362.4432 | -87492.9231 | -91503.3799 | -110177.5023 | -107524.4061 | -136752.968
State Average | 1.1179 | 1.5084 | 3.3639 | 1.2821 | 2.2887 | 3.0729 | 2.5462 |  | 1.1179 |  | State Average | -5982.0366 | -702648.961 | -85597.6456 | -84504.1545 | -94933.6127 | -106950.4713 | -145563.5387 |  | State Average | -6161.4895 | -752791.0763 | -83050.0281 | -94850.6628 | -98777.5784 | -103660.3271 | -150108.6142
1.02
3 CZ: Table 3. Annual Energy Cost Savings from ASHRAE Standard 90.1-2019, Scenarios 1 and 2 ($/ft2) |  |  |  |  | Public replacement costs | [8 empty] | Private replacement costs
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types |  |  |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 0.095 | 0.155 | 0.256 | 0.154 | 0.219 | 0.187 | 0.189 | 1 |  |  | 2A | -0.089699 | 0.20172 | -0.02755 | 0.017619 | 0.073098 | -0.64547 | -0.21387 |  | 2A | -0.085376 | 0.19257 | -0.026222 | 0.016982 | 0.069575 | -0.61437 | -0.20348
3A | 0.088 | 0.149 | 0.257 | 0.14 | 0.198 | 0.167 | 0.18002 | 2 |  |  | 3A | -0.077504 | -0.031252 | 0.033008 | 0.014738 | 0.073449 | -0.65415 | -0.19025 |  | 3A | -0.073769 | -0.029477 | 0.031418 | 0.014342 | 0.069909 | -0.62263 | -0.18101
3B | 0.091 | 0.153 | 0.239 | 0.14 | 0.208 | 0.182 | 0.18328 | 3 |  |  | 3B | -0.081235 | -0.037798 | 0.025755 | -0.022538 | 0.073873 | -0.77055 | -0.30295 |  | 3B | -0.07732 | -0.035749 | 0.024514 | -0.021172 | 0.070312 | -0.73341 | -0.2883
4A | 0.092 | 0.142 | 0.263 | 0.128 | 0.21 | 0.173 | 0.181 | 4 |  |  | 4A | -0.093267 | -0.02538 | 0.009083 | -0.087347 | 0.0033785 | -0.94923 | -0.38398 |  | 4A | -0.088772 | -0.023866 | 0.0086453 | -0.082843 | 0.0032157 | -0.90348 | -0.3654
5A | 0.1 | 0.145 | 0.265 | 0.134 | 0.22 | 0.175 | 0.194 | 5 |  |  | 5A | -0.050467 | -0.021513 | -0.011917 | -0.081915 | 0.0080602 | -0.90925 | -0.31713 |  | 5A | -0.048035 | -0.020182 | -0.011343 | -0.077639 | 0.0076717 | -0.86543 | -0.30179
State Average | 0.09354 | 0.14713 | 0.25853 | 0.13961 | 0.21162 | 0.17643 | 0.1857 |  |  |  | State Average | -0.077958 | 0.014966 | 0.002356 | -0.029877 | 0.042198 | -0.80496 | -0.28521 |  | State Average | -0.074201 | 0.014578 | 0.0022424 | -0.028153 | 0.040165 | -0.76617 | -0.2714
Costs and Weightings for Standard 90.1-2022 in the State of US National
Weighting factors are for just the analyzed prototypes, not all prototypes
based on data from 2003-2007
DE had no apartments; MT had no large office
Table 4. Construction Weights by Building Type
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 0.025336 | 0.017992 | 0.059235 | 0.032252 | 0.010034 | 0.074155 | 0.219 | 1
3A | 0.023024 | 0.017948 | 0.058756 | 0.031014 | 0.008854 | 0.058763 | 0.19836 | 2
3B | 0.009086 | 0.008483 | 0.028203 | 0.011845 | 0.003509 | 0.038875 | 0.1 | 3
4A | 0.019059 | 0.037221 | 0.063391 | 0.029137 | 0.010054 | 0.099679 | 0.25854 | 4
5A | 0.022135 | 0.015936 | 0.078184 | 0.025519 | 0.00901 | 0.07331 | 0.22409 | 5
State Average | 0.09864 | 0.09758 | 0.28777 | 0.12977 | 0.041461 | 0.34478 | 1
Incremental Construction Cost
Cost estimates were developed for the differences between the Base Code and ASHRAE Standard 90.1-2022 as implemented in the six prototype models. Costs for the initial construction include material, labor, commissioning, construction equipment, overhead and profit. These costs were developed using a commercial cost estimation firm, engineering design consultants and RS Means 2012 and 2014 cost data (RS Means 2012a,b,c, 2014a,b,c; Hart et al. 2015). Table 7 shows incremental initial cost for individual building types in state-specific climate zones and weighted average costs by climate zone and building type for moving to ASHRAE Standard 90.1-2022 from the Base Code. The incremental cost may be negative for some building types and climate zones based on fewer lighting fixtures or the downsizing of heating, ventilating, and air-conditioning (HVAC) equipment resulting from reductions in heating and cooling loads due to improvements in ASHRAE Standard 90.1-2022, such as more efficient lighting systems and building thermal envelope.
Table 5. Incremental Construction Cost of ASHRAE Standard 90.1-2019 ($/ft2)
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types |  |  |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 0.58745 | 1.6873 | 1.1848 | 1.3303 | 1.6698 | 0.9661 | 1.1266 | 1 |  |  | 2A | 3232.1592 | 841279.0162 | 29256.1317 | 98389.5877 | 72136.55 | 32597.3417 | 106233.2378
3A | 0.56605 | 1.136 | 1.2556 | 1.3494 | 1.6064 | 0.95678 | 1.1065 | 2 |  |  | 3A | 3114.4016 | 566391.7932 | 31003.3581 | 99798.1261 | 69399.8577 | 32282.7888 | 89058.6166
3B | 0.57979 | 1.1084 | 1.2201 | 1.2803 | 1.5844 | 0.83528 | 1.0228 | 3 |  |  | 3B | 3190.0271 | 552615.5333 | 30127.6668 | 94691.8378 | 68447.9802 | 28183.2154 | 80238.6378
4A | 0.82812 | 1.1821 | 1.2856 | 1.3678 | 1.5882 | 0.79882 | 1.0703 | 4 |  |  | 4A | 4556.3437 | 589404.773 | 31743.3402 | 101162.408 | 68614.0814 | 26952.9993 | 117433.5195
5A | 0.92122 | 1.1731 | 1.1456 | 1.3836 | 1.5893 | 0.83991 | 1.0703 | 5 |  |  | 5A | 5068.5778 | 584901.6859 | 28286.6141 | 102326.2932 | 68660.8203 | 28339.4794 | 75647.7762
State Average | 0.70315 | 1.2589 | 1.2143 | 1.3492 | 1.6117 | 0.87457 | 1.0851 |  |  |  | State Average | 3868.7437 | 627679.4205 | 29982.7764 | 99785.4512 | 69630.4578 | 29508.8698 | 96268.7148
Table 6. Simple Payback from ASHRAE Standard 90.1-2022, Scenarios 1 and 2 (Years)
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
2A | 6.2 | 10.8 | 4.6 | 8.3 | 7.4 | 5.2 | 5.9609 | 1
3A | 6.4 | 7.6 | 4.8 | 9.3 | 7.9 | 5.7 | 6.1467 | 2
3B | 6.4 | 7.2 | 5 | 8.8 | 7.4 | 4.6 | 5.5802 | 3
4A | 9 | 8.3 | 4.8 | 10.2 | 7.6 | 4.6 | 5.9134 | 4
5A | 9.2 | 8 | 4.2 | 9.9 | 7.2 | 4.8 | 5.5171 | 5
State Average | 7.5171 | 8.5564 | 4.6969 | 9.6644 | 7.6162 | 4.9571 | 5.8432
[11 empty] | Public Savings to investment ratios | [9 empty] | Private Savings to investment ratios
[11 empty] | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types | numbers? |  | Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-Rise Apartment | All Building Types
[8 empty] | 1 |  |  | 2A | 3.4773 | 1.4951 | 4.0553 | 2.011 | 2.2433 | 10.6787 | 23.2827 |  |  | 2A | 3.1243 | 1.3612 | 3.6711 | 1.8194 | 2.0337 | 8.8222 | 20.4049
[8 empty] | 2 |  |  | 3A | 3.3113 | 2.4593 | 3.5847 | 1.7994 | 2.1102 | 10.1092 | 22.5305 |  |  | 3A | 2.9782 | 2.2246 | 3.2486 | 1.6273 | 1.9128 | 8.2976 | 19.6987
[8 empty] | 3 |  |  | 3B | 3.3458 | 2.6056 | 3.4303 | 1.9571 | 2.247 | 51.4867 | 0 |  |  | 3B | 3.0087 | 2.3562 | 3.1075 | 1.7674 | 2.0371 | 29.652 | 0
[8 empty] | 4 |  |  | 4A | 2.2985 | 2.2407 | 3.6727 | 1.7666 | 2.4486 | Infinite | 0 |  |  | 4A | 2.0705 | 2.0274 | 3.3254 | 1.5913 | 2.2194 | Infinite | 0
[8 empty] | 5 |  |  | 5A | 2.0996 | 2.2943 | 4.2459 | 1.832 | 2.5574 | Infinite | 0 |  |  | 5A | 1.8976 | 2.0762 | 3.8413 | 1.6508 | 2.3184 | Infinite | 0
[11 empty] | State Average | 2.8895 | 2.1839 | 3.8655 | 1.8654 | 2.3333 | 9.825 | 0 |  |  | State Average | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | numbers? | [9 empty] | numbers?
[12 empty] | FALSE | [9 empty] | FALSE
Table 8 shows simple payback results in years. Simple payback is the number of years required for energy cost savings to exceed the incremental first costs of a new code. Simple payback is not used as a measure of cost-effectiveness as it does not account for the time value of money, the value of energy cost savings that occur after payback is achieved, or any maintenance or replacement costs that occur after the initial investment.
Savings are computed for two scenarios:
Scenario 1 (publicly-owned) includes costs for initial equipment and construction, energy, maintenance and replacement and does not include loans or taxes.
Scenario 2 (privately-owned) includes the same costs as scenario 1, plus the initial investment is financed through a loan amortized over 30 years with corresponding federal and state corporate income tax deductions for interest and depreciation.
Both scenarios include the residual value of equipment
with remaining useful life at the end of the 30 years. Totals for building types, climate zones, and the state overall are averages based on Table 6 weightings.
Factors such as inflation and discount rates are
different between the two scenarios, as described
in the Cost-Effectiveness Methodology section.
Construction Weighting of Results
Energy and economic impacts were determined and reported separately for each building type and climate zone. Cost-effectiveness results are also reported as averages for all prototypes and climate zones in the state. To determine these averages, results were combined across the different building types and climate zones using weighting factors shown in Table 6. These weighting factors are based on the floor area of new construction and major renovations for the six analyzed building prototypes in state-specific climate zones. The weighting factors were developed from construction start data from 2003 to 2007 based on an approach developed by Jarnagin and Bandyopadhyay (McGraw Hill Construction 2007, Jarnagin and Bandyopadhyay 2010).
The U.S. Department of Energy (DOE) provides estimates of energy and cost savings from code adoption at the National, Climate Zone, and State levels. For more information on how these estimates were developed, visit the DOE Building Energy Codes website: www.energycodes.gov/development/commercial
U.S Department of Energy
Energy Efficiency and Renewable Energy
BUILDING TECHNOLOGIES OFFICE
Building Energy Codes
For information on Building Energy
Codes, visit www.energycodes.gov
EERE Information Center
www.energy.gov/eere

## Ian's Results (hidden)
State | Type | Public | Private | State | Type | Public | Private | State | State Abbr | City | Climate Label | Population (2010) | State | State Abbr | City | Climate Zone | Type | Public | Private | State | State Abbr | City | Climate Zone | Type | Public | Private
Alabama | Annual reduction in energy bills ($/ft2) | 0.079058 | 0.079058 | US National | Annual reduction in energy bills ($/ft2) | 0.1857 | 0.1857 | Alabama | AL | Birmingham | 3A | 212237 | US National | US | Memphis | 3A | Annual reduction in energy bills ($/ft2) | 0.18002 | 0.18002 | Alabama | AL | Birmingham | 3A | Annual reduction in energy bills ($/ft2) | 0.077044 | 0.077044
Alabama | Added construction cost ($/ft2) | -1.0575 | -1.0575 | US National | Added construction cost ($/ft2) | 1.0851 | 1.0851 | Arkansas | AR | Little Rock | 3A | 193524 | US National | US | Memphis | 3A | Added construction cost ($/ft2) | #NAME? | #NAME? | Alabama | AL | Birmingham | 3A | Added construction cost ($/ft2) | -1.0587 | -1.0587
Alabama | Present value of replacement costs / sf | -2.0265 | -1.9382 | US National | Present value of replacement costs / sf | -0.28521 | -0.2714 | Florida | FL | Tampa | 2A | 335709 | US National | US | Memphis | 3A | Present value of replacement costs / sf | #NAME? | #NAME? | Alabama | AL | Birmingham | 3A | Present value of replacement costs / sf | -1.9691 | -1.8832
Alabama | Net present value of LCC savings ($/sf) | 4.5674 | 4.0348 | US National | Net present value of LCC savings ($/sf) | 2.5751 | 2.5462 | Florida | FL | Miami | 1A | 399457 | US National | US | Memphis | 3A | Net present value of LCC savings ($/sf) | #NAME? | #NAME? | Alabama | AL | Birmingham | 3A | Net present value of LCC savings ($/sf) | 4.4715 | 3.9436
Alabama | Simple payback | Immediate | Immediate | US National | Simple payback | 5.8432 | 5.8432 | Georgia | GA | Atlanta | 3A | 420003 | US National | US | Memphis | 3A | Simple payback | #NAME? | #NAME? | Alabama | AL | Birmingham | 3A | Simple payback | Immediate | Immediate
Alabama | Savings-to-investment ratio | Infinite | Infinite | US National | Savings-to-investment ratio | Infinite | Infinite | Idaho | ID | Boise | 5B | 205671 | US National | US | Memphis | 3A | Savings-to-investment ratio | Infinite | Infinite | Alabama | AL | Birmingham | 3A | Savings-to-investment ratio | Infinite | Infinite
Arkansas | Annual reduction in energy bills ($/ft2) | 0.062203 | 0.062203 |  |  |  |  | Iowa | IA | Des Moines | 5A | 203433 | [7 empty] | Arkansas | AR | Little Rock | 3A | Annual reduction in energy bills ($/ft2) | 0.066203 | 0.066203
Arkansas | Added construction cost ($/ft2) | -1.1205 | -1.1205 |  |  |  |  | Kentucky | KY | Lexington | 4A | 597337 | [7 empty] | Arkansas | AR | Little Rock | 3A | Added construction cost ($/ft2) | -1.1194 | -1.1194
Arkansas | Present value of replacement costs / sf | -1.9419 | -1.8573 |  |  |  |  | Louisiana | LA | Baton Rouge | 2A | 229493 | [7 empty] | Arkansas | AR | Little Rock | 3A | Present value of replacement costs / sf | -2.0001 | -1.9131
Arkansas | Net present value of LCC savings ($/sf) | 4.2378 | 3.7241 |  |  |  |  | Maryland | MD | Baltimore | 4A | 620961 | [7 empty] | Arkansas | AR | Little Rock | 3A | Net present value of LCC savings ($/sf) | 4.3774 | 3.855
Arkansas | Simple payback | Immediate | Immediate |  |  |  |  | Michigan | MI | Lansing | 5A | 188040 | [7 empty] | Arkansas | AR | Little Rock | 3A | Simple payback | Immediate | Immediate
Arkansas | Savings-to-investment ratio | Infinite | Infinite |  |  |  |  | Minnesota | MN | Minneapolis | 6A | 382578 | [7 empty] | Arkansas | AR | Little Rock | 3A | Savings-to-investment ratio | Infinite | Infinite
Colorado | Annual reduction in energy bills ($/ft2) | 0.042177 | 0.042177 |  |  |  |  | Nevada | NV | Las Vegas | 3B | 583756 | [7 empty] | Florida | FL | Tampa | 2A | Annual reduction in energy bills ($/ft2) | 0.065625 | 0.065625
Colorado | Added construction cost ($/ft2) | -0.96371 | -0.96371 |  |  |  |  | New Jersey | NJ | Newark | 4A | 277140 | [7 empty] | Florida | FL | Tampa | 2A | Added construction cost ($/ft2) | -0.8971 | -0.8971
Colorado | Present value of replacement costs / sf | -1.8568 | -1.7749 |  |  |  |  | New Mexico | NM | Albuquerque | 4B | 545852 | [7 empty] | Florida | FL | Tampa | 2A | Present value of replacement costs / sf | -1.6155 | -1.5442
Colorado | Net present value of LCC savings ($/sf) | 3.5028 | 3.0927 |  |  |  |  | North Carolina | NC | Charlotte | 3A | 731424 | [7 empty] | Florida | FL | Tampa | 2A | Net present value of LCC savings ($/sf) | 3.6879 | 3.2618
Colorado | Simple payback | Immediate | Immediate |  |  |  |  | Ohio | OH | Columbus | 5A | 787033 | [7 empty] | Florida | FL | Tampa | 2A | Simple payback | Immediate | Immediate
Colorado | Savings-to-investment ratio | Infinite | Infinite |  |  |  |  | Oklahoma | OK | Oklahoma City | 3A | 579999 | [7 empty] | Florida | FL | Tampa | 2A | Savings-to-investment ratio | Infinite | Infinite
Connecticut | Annual reduction in energy bills ($/ft2) | 0.081988 | 0.081988 |  |  |  |  | Pennsylvania | PA | Harrisburg | 5A | 305704 | [7 empty] | Florida | FL | Miami | 1A | Annual reduction in energy bills ($/ft2) | 0.05984 | 0.05984
Connecticut | Added construction cost ($/ft2) | -1.1992 | -1.1992 |  |  |  |  | South Carolina | SC | Columbia | 3A | 237772 | [7 empty] | Florida | FL | Miami | 1A | Added construction cost ($/ft2) | -0.90968 | -0.90968
Connecticut | Present value of replacement costs / sf | -1.866 | -1.7836 |  |  |  |  | Tennessee | TN | Memphis | 3A | 646889 | [7 empty] | Florida | FL | Miami | 1A | Present value of replacement costs / sf | -1.4753 | -1.41
Connecticut | Net present value of LCC savings ($/sf) | 4.5024 | 3.9287 |  |  |  |  | Texas | TX | Houston | 2A | 2099451 | [7 empty] | Florida | FL | Miami | 1A | Net present value of LCC savings ($/sf) | 3.4359 | 3.0265
Connecticut | Simple payback | Immediate | Immediate |  |  |  |  | Utah | UT | Salt Lake City | 5B | 186440 | [7 empty] | Florida | FL | Miami | 1A | Simple payback | Immediate | Immediate
Connecticut | Savings-to-investment ratio | Infinite | Infinite |  |  |  |  | Virginia | VA | Richmond | 4A | 204214 | [7 empty] | Florida | FL | Miami | 1A | Savings-to-investment ratio | Infinite | Infinite
Delaware | Annual reduction in energy bills ($/ft2) | 0.046127 | 0.046127 |  |  |  |  | Wisconsin | WI | Madison | 6A | 594833 | [7 empty] | Georgia | GA | Atlanta | 3A | Annual reduction in energy bills ($/ft2) | 0.060688 | 0.060688
Delaware | Added construction cost ($/ft2) | -1.241 | -1.241 | [16 empty] | Georgia | GA | Atlanta | 3A | Added construction cost ($/ft2) | -0.9978 | -0.9978
Delaware | Present value of replacement costs / sf | -2.119 | -2.0265 | [16 empty] | Georgia | GA | Atlanta | 3A | Present value of replacement costs / sf | -1.567 | -1.4976
Delaware | Net present value of LCC savings ($/sf) | 4.1413 | 3.5935 | [16 empty] | Georgia | GA | Atlanta | 3A | Net present value of LCC savings ($/sf) | 3.6676 | 3.2139
Delaware | Simple payback | Immediate | Immediate | [16 empty] | Georgia | GA | Atlanta | 3A | Simple payback | Immediate | Immediate
Delaware | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Georgia | GA | Atlanta | 3A | Savings-to-investment ratio | Infinite | Infinite
District of Columbia | Annual reduction in energy bills ($/ft2) | 0.049551 | 0.049551 | [16 empty] | Idaho | ID | Boise | 5B | Annual reduction in energy bills ($/ft2) | 0.040459 | 0.040459
District of Columbia | Added construction cost ($/ft2) | -1.4141 | -1.4141 | [16 empty] | Idaho | ID | Boise | 5B | Added construction cost ($/ft2) | -1.2009 | -1.2009
District of Columbia | Present value of replacement costs / sf | -1.2002 | -1.1464 | [16 empty] | Idaho | ID | Boise | 5B | Present value of replacement costs / sf | -1.7973 | -1.7182
District of Columbia | Net present value of LCC savings ($/sf) | 3.4697 | 2.9071 | [16 empty] | Idaho | ID | Boise | 5B | Net present value of LCC savings ($/sf) | 3.7041 | 3.2104
District of Columbia | Simple payback | Immediate | Immediate | [16 empty] | Idaho | ID | Boise | 5B | Simple payback | Immediate | Immediate
District of Columbia | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Idaho | ID | Boise | 5B | Savings-to-investment ratio | Infinite | Infinite
Georgia | Annual reduction in energy bills ($/ft2) | 0.061902 | 0.061902 | [16 empty] | Iowa | IA | Des Moines | 5A | Annual reduction in energy bills ($/ft2) | 0.056556 | 0.056556
Georgia | Added construction cost ($/ft2) | -1.0088 | -1.0088 | [16 empty] | Iowa | IA | Des Moines | 5A | Added construction cost ($/ft2) | -1.1727 | -1.1727
Georgia | Present value of replacement costs / sf | -1.6447 | -1.5722 | [16 empty] | Iowa | IA | Des Moines | 5A | Present value of replacement costs / sf | -1.9919 | -1.9049
Georgia | Net present value of LCC savings ($/sf) | 3.7826 | 3.32 | [16 empty] | Iowa | IA | Des Moines | 5A | Net present value of LCC savings ($/sf) | 4.1804 | 3.6248
Georgia | Simple payback | Immediate | Immediate | [16 empty] | Iowa | IA | Des Moines | 5A | Simple payback | Immediate | Immediate
Georgia | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Iowa | IA | Des Moines | 5A | Savings-to-investment ratio | Infinite | Infinite
Iowa | Annual reduction in energy bills ($/ft2) | 0.056719 | 0.056719 | [16 empty] | Kentucky | KY | Lexington | 4A | Annual reduction in energy bills ($/ft2) | 0.061548 | 0.061548
Iowa | Added construction cost ($/ft2) | -1.1667 | -1.1667 | [16 empty] | Kentucky | KY | Lexington | 4A | Added construction cost ($/ft2) | -1.1572 | -1.1572
Iowa | Present value of replacement costs / sf | -2.0309 | -1.9424 | [16 empty] | Kentucky | KY | Lexington | 4A | Present value of replacement costs / sf | -2.0356 | -1.947
Iowa | Net present value of LCC savings ($/sf) | 4.2173 | 3.6617 | [16 empty] | Kentucky | KY | Lexington | 4A | Net present value of LCC savings ($/sf) | 4.314 | 3.8061
Iowa | Simple payback | Immediate | Immediate | [16 empty] | Kentucky | KY | Lexington | 4A | Simple payback | Immediate | Immediate
Iowa | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Kentucky | KY | Lexington | 4A | Savings-to-investment ratio | Infinite | Infinite
Kentucky | Annual reduction in energy bills ($/ft2) | 0.061548 | 0.061548 | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Annual reduction in energy bills ($/ft2) | 0.064789 | 0.064789
Kentucky | Added construction cost ($/ft2) | -1.1572 | -1.1572 | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Added construction cost ($/ft2) | -1.0506 | -1.0506
Kentucky | Present value of replacement costs / sf | -2.0356 | -1.947 | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Present value of replacement costs / sf | -2.0637 | -1.9741
Kentucky | Net present value of LCC savings ($/sf) | 4.314 | 3.8061 | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Net present value of LCC savings ($/sf) | 4.3207 | 3.8065
Kentucky | Simple payback | Immediate | Immediate | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Simple payback | Immediate | Immediate
Kentucky | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Louisiana | LA | Baton Rouge | 2A | Savings-to-investment ratio | Infinite | Infinite
Massachusetts | Annual reduction in energy bills ($/ft2) | 0.059368 | 0.059368 | [16 empty] | Maryland | MD | Baltimore | 4A | Annual reduction in energy bills ($/ft2) | 0.034198 | 0.034198
Massachusetts | Added construction cost ($/ft2) | -1.0136 | -1.0136 | [16 empty] | Maryland | MD | Baltimore | 4A | Added construction cost ($/ft2) | -0.94139 | -0.94139
Massachusetts | Present value of replacement costs / sf | -1.8728 | -1.7909 | [16 empty] | Maryland | MD | Baltimore | 4A | Present value of replacement costs / sf | -1.5352 | -1.4677
Massachusetts | Net present value of LCC savings ($/sf) | 3.8239 | 3.3432 | [16 empty] | Maryland | MD | Baltimore | 4A | Net present value of LCC savings ($/sf) | 2.9813 | 2.5801
Massachusetts | Simple payback | Immediate | Immediate | [16 empty] | Maryland | MD | Baltimore | 4A | Simple payback | Immediate | Immediate
Massachusetts | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Maryland | MD | Baltimore | 4A | Savings-to-investment ratio | Infinite | Infinite
Montana | Annual reduction in energy bills ($/ft2) | 0.060446 | 0.060446 | [16 empty] | Michigan | MI | Lansing | 5A | Annual reduction in energy bills ($/ft2) | 0.07284 | 0.07284
Montana | Added construction cost ($/ft2) | -1.1327 | -1.1327 | [16 empty] | Michigan | MI | Lansing | 5A | Added construction cost ($/ft2) | -1.0132 | -1.0132
Montana | Present value of replacement costs / sf | -2.7133 | -2.597 | [16 empty] | Michigan | MI | Lansing | 5A | Present value of replacement costs / sf | -2.5481 | -2.4391
Montana | Net present value of LCC savings ($/sf) | 4.9627 | 4.4179 | [16 empty] | Michigan | MI | Lansing | 5A | Net present value of LCC savings ($/sf) | 4.8735 | 4.3546
Montana | Simple payback | Immediate | Immediate | [16 empty] | Michigan | MI | Lansing | 5A | Simple payback | Immediate | Immediate
Montana | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Michigan | MI | Lansing | 5A | Savings-to-investment ratio | Infinite | Infinite
Nebraska | Annual reduction in energy bills ($/ft2) | 0.052044 | 0.052044 | [16 empty] | Minnesota | MN | Minneapolis | 6A | Annual reduction in energy bills ($/ft2) | 0.056718 | 0.056718
Nebraska | Added construction cost ($/ft2) | -1.1418 | -1.1418 | [16 empty] | Minnesota | MN | Minneapolis | 6A | Added construction cost ($/ft2) | -0.83772 | -0.83772
Nebraska | Present value of replacement costs / sf | -1.968 | -1.8823 | [16 empty] | Minnesota | MN | Minneapolis | 6A | Present value of replacement costs / sf | -3.8506 | -3.6885
Nebraska | Net present value of LCC savings ($/sf) | 4.0443 | 3.5271 | [16 empty] | Minnesota | MN | Minneapolis | 6A | Net present value of LCC savings ($/sf) | 5.6862 | 5.1611
Nebraska | Simple payback | Immediate | Immediate | [16 empty] | Minnesota | MN | Minneapolis | 6A | Simple payback | Immediate | Immediate
Nebraska | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Minnesota | MN | Minneapolis | 6A | Savings-to-investment ratio | Infinite | Infinite
New Jersey | Annual reduction in energy bills ($/ft2) | 0.047517 | 0.047517 | [16 empty] | Nevada | NV | Las Vegas | 3B | Annual reduction in energy bills ($/ft2) | 0.04594 | 0.04594
New Jersey | Added construction cost ($/ft2) | -1.0681 | -1.0681 | [16 empty] | Nevada | NV | Las Vegas | 3B | Added construction cost ($/ft2) | -1.3358 | -1.3358
New Jersey | Present value of replacement costs / sf | -1.9815 | -1.8945 | [16 empty] | Nevada | NV | Las Vegas | 3B | Present value of replacement costs / sf | -1.606 | -1.5338
New Jersey | Net present value of LCC savings ($/sf) | 3.765 | 3.2747 | [16 empty] | Nevada | NV | Las Vegas | 3B | Net present value of LCC savings ($/sf) | 3.7463 | 3.2922
New Jersey | Simple payback | Immediate | Immediate | [16 empty] | Nevada | NV | Las Vegas | 3B | Simple payback | Immediate | Immediate
New Jersey | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Nevada | NV | Las Vegas | 3B | Savings-to-investment ratio | Infinite | Infinite
New York | Annual reduction in energy bills ($/ft2) | 0.064444 | 0.064444 | [16 empty] | New Jersey | NJ | Newark | 4A | Annual reduction in energy bills ($/ft2) | 0.046483 | 0.046483
New York | Added construction cost ($/ft2) | -1.3673 | -1.3673 | [16 empty] | New Jersey | NJ | Newark | 4A | Added construction cost ($/ft2) | -1.0586 | -1.0586
New York | Present value of replacement costs / sf | -2.7277 | -2.6098 | [16 empty] | New Jersey | NJ | Newark | 4A | Present value of replacement costs / sf | -1.992 | -1.9047
New York | Net present value of LCC savings ($/sf) | 5.1617 | 4.5488 | [16 empty] | New Jersey | NJ | Newark | 4A | Net present value of LCC savings ($/sf) | 3.7438 | 3.2585
New York | Simple payback | Immediate | Immediate | [16 empty] | New Jersey | NJ | Newark | 4A | Simple payback | Immediate | Immediate
New York | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | New Jersey | NJ | Newark | 4A | Savings-to-investment ratio | Infinite | Infinite
North Carolina | Annual reduction in energy bills ($/ft2) | 0.053228 | 0.053228 | [16 empty] | New Mexico | NM | Albuquerque | 4B | Annual reduction in energy bills ($/ft2) | 0.060271 | 0.060271
North Carolina | Added construction cost ($/ft2) | -0.97859 | -0.97859 | [16 empty] | New Mexico | NM | Albuquerque | 4B | Added construction cost ($/ft2) | -1.2252 | -1.2252
North Carolina | Present value of replacement costs / sf | -1.5126 | -1.4459 | [16 empty] | New Mexico | NM | Albuquerque | 4B | Present value of replacement costs / sf | -1.9067 | -1.8225
North Carolina | Net present value of LCC savings ($/sf) | 3.4535 | 3.0508 | [16 empty] | New Mexico | NM | Albuquerque | 4B | Net present value of LCC savings ($/sf) | 4.2317 | 3.7016
North Carolina | Simple payback | Immediate | Immediate | [16 empty] | New Mexico | NM | Albuquerque | 4B | Simple payback | Immediate | Immediate
North Carolina | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | New Mexico | NM | Albuquerque | 4B | Savings-to-investment ratio | Infinite | Infinite
Oklahoma | Annual reduction in energy bills ($/ft2) | 0.055788 | 0.055788 | [16 empty] | North Carolina | NC | Charlotte | 3A | Annual reduction in energy bills ($/ft2) | 0.053571 | 0.053571
Oklahoma | Added construction cost ($/ft2) | -1.1503 | -1.1503 | [16 empty] | North Carolina | NC | Charlotte | 3A | Added construction cost ($/ft2) | -0.98031 | -0.98031
Oklahoma | Present value of replacement costs / sf | -2.058 | -1.9687 | [16 empty] | North Carolina | NC | Charlotte | 3A | Present value of replacement costs / sf | -1.4864 | -1.4208
Oklahoma | Net present value of LCC savings ($/sf) | 4.2663 | 3.7522 | [16 empty] | North Carolina | NC | Charlotte | 3A | Net present value of LCC savings ($/sf) | 3.4377 | 3.0352
Oklahoma | Simple payback | Immediate | Immediate | [16 empty] | North Carolina | NC | Charlotte | 3A | Simple payback | Immediate | Immediate
Oklahoma | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | North Carolina | NC | Charlotte | 3A | Savings-to-investment ratio | Infinite | Infinite
Rhode Island | Annual reduction in energy bills ($/ft2) | 0.078966 | 0.078966 | [16 empty] | Ohio | OH | Columbus | 5A | Annual reduction in energy bills ($/ft2) | 0.057331 | 0.057331
Rhode Island | Added construction cost ($/ft2) | -1.0349 | -1.0349 | [16 empty] | Ohio | OH | Columbus | 5A | Added construction cost ($/ft2) | -1.2745 | -1.2745
Rhode Island | Present value of replacement costs / sf | -2.1361 | -2.0435 | [16 empty] | Ohio | OH | Columbus | 5A | Present value of replacement costs / sf | -1.8981 | -1.814
Rhode Island | Net present value of LCC savings ($/sf) | 4.5431 | 4.0173 | [16 empty] | Ohio | OH | Columbus | 5A | Net present value of LCC savings ($/sf) | 4.2159 | 3.743
Rhode Island | Simple payback | Immediate | Immediate | [16 empty] | Ohio | OH | Columbus | 5A | Simple payback | Immediate | Immediate
Rhode Island | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Ohio | OH | Columbus | 5A | Savings-to-investment ratio | Infinite | Infinite
South Carolina | Annual reduction in energy bills ($/ft2) | 0.063508 | 0.063508 | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Annual reduction in energy bills ($/ft2) | 0.056257 | 0.056257
South Carolina | Added construction cost ($/ft2) | -0.95352 | -0.95352 | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Added construction cost ($/ft2) | -1.1561 | -1.1561
South Carolina | Present value of replacement costs / sf | -1.6588 | -1.5857 | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Present value of replacement costs / sf | -2.0363 | -1.9478
South Carolina | Net present value of LCC savings ($/sf) | 3.7708 | 3.325 | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Net present value of LCC savings ($/sf) | 4.262 | 3.7461
South Carolina | Simple payback | Immediate | Immediate | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Simple payback | Immediate | Immediate
South Carolina | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Oklahoma | OK | Oklahoma City | 3A | Savings-to-investment ratio | Infinite | Infinite
Texas | Annual reduction in energy bills ($/ft2) | 0.052781 | 0.052781 | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Annual reduction in energy bills ($/ft2) | 0.046095 | 0.046095
Texas | Added construction cost ($/ft2) | -1.0128 | -1.0128 | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Added construction cost ($/ft2) | -1.3592 | -1.3592
Texas | Present value of replacement costs / sf | -1.6709 | -1.5973 | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Present value of replacement costs / sf | -2.3069 | -2.206
Texas | Net present value of LCC savings ($/sf) | 3.6292 | 3.2277 | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Net present value of LCC savings ($/sf) | 4.4651 | 3.8619
Texas | Simple payback | Immediate | Immediate | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Simple payback | Immediate | Immediate
Texas | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Pennsylvania | PA | Harrisburg | 5A | Savings-to-investment ratio | Infinite | Infinite
US National | Annual reduction in energy bills ($/ft2) | 0.064224 | 0.064224 | [16 empty] | South Carolina | SC | Columbia | 3A | Annual reduction in energy bills ($/ft2) | 0.06314 | 0.06314
US National | Added construction cost ($/ft2) | -1.1234 | -1.1234 | [16 empty] | South Carolina | SC | Columbia | 3A | Added construction cost ($/ft2) | -0.95386 | -0.95386
US National | Present value of replacement costs / sf | -1.8948 | -1.8114 | [16 empty] | South Carolina | SC | Columbia | 3A | Present value of replacement costs / sf | -1.6313 | -1.5592
US National | Net present value of LCC savings ($/sf) | 4.1519 | 3.6441 | [16 empty] | South Carolina | SC | Columbia | 3A | Net present value of LCC savings ($/sf) | 3.736 | 3.2918
US National | Simple payback | Immediate | Immediate | [16 empty] | South Carolina | SC | Columbia | 3A | Simple payback | Immediate | Immediate
US National | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | South Carolina | SC | Columbia | 3A | Savings-to-investment ratio | Infinite | Infinite
Utah | Annual reduction in energy bills ($/ft2) | 0.042193 | 0.042193 | [16 empty] | Tennessee | TN | Memphis | 3A | Annual reduction in energy bills ($/ft2) | 0.069991 | 0.069991
Utah | Added construction cost ($/ft2) | -1.068 | -1.068 | [16 empty] | Tennessee | TN | Memphis | 3A | Added construction cost ($/ft2) | -1.0233 | -1.0233
Utah | Present value of replacement costs / sf | -1.7253 | -1.6494 | [16 empty] | Tennessee | TN | Memphis | 3A | Present value of replacement costs / sf | -1.5893 | -1.5196
Utah | Net present value of LCC savings ($/sf) | 3.5086 | 3.0714 | [16 empty] | Tennessee | TN | Memphis | 3A | Net present value of LCC savings ($/sf) | 3.901 | 3.4174
Utah | Simple payback | Immediate | Immediate | [16 empty] | Tennessee | TN | Memphis | 3A | Simple payback | Immediate | Immediate
Utah | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Tennessee | TN | Memphis | 3A | Savings-to-investment ratio | Infinite | Infinite
Virginia | Annual reduction in energy bills ($/ft2) | 0.036978 | 0.036978 | [16 empty] | Texas | TX | Houston | 2A | Annual reduction in energy bills ($/ft2) | 0.052254 | 0.052254
Virginia | Added construction cost ($/ft2) | -1.007 | -1.007 | [16 empty] | Texas | TX | Houston | 2A | Added construction cost ($/ft2) | -0.98735 | -0.98735
Virginia | Present value of replacement costs / sf | -1.5609 | -1.4921 | [16 empty] | Texas | TX | Houston | 2A | Present value of replacement costs / sf | -1.6234 | -1.5519
Virginia | Net present value of LCC savings ($/sf) | 3.1764 | 2.7613 | [16 empty] | Texas | TX | Houston | 2A | Net present value of LCC savings ($/sf) | 3.5373 | 3.1451
Virginia | Simple payback | Immediate | Immediate | [16 empty] | Texas | TX | Houston | 2A | Simple payback | Immediate | Immediate
Virginia | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Texas | TX | Houston | 2A | Savings-to-investment ratio | Infinite | Infinite
Wisconsin | Annual reduction in energy bills ($/ft2) | 0.055032 | 0.055032 | [16 empty] | Utah | UT | Salt Lake City | 5B | Annual reduction in energy bills ($/ft2) | 0.041882 | 0.041882
Wisconsin | Added construction cost ($/ft2) | -1.1443 | -1.1443 | [16 empty] | Utah | UT | Salt Lake City | 5B | Added construction cost ($/ft2) | -1.0816 | -1.0816
Wisconsin | Present value of replacement costs / sf | -1.9028 | -1.8192 | [16 empty] | Utah | UT | Salt Lake City | 5B | Present value of replacement costs / sf | -1.6252 | -1.5533
Wisconsin | Net present value of LCC savings ($/sf) | 3.9898 | 3.4722 | [16 empty] | Utah | UT | Salt Lake City | 5B | Net present value of LCC savings ($/sf) | 3.4162 | 2.9797
Wisconsin | Simple payback | Immediate | Immediate | [16 empty] | Utah | UT | Salt Lake City | 5B | Simple payback | Immediate | Immediate
Wisconsin | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Utah | UT | Salt Lake City | 5B | Savings-to-investment ratio | Infinite | Infinite
California | Annual reduction in energy bills ($/ft2) | 0.065546 | 0.065546 | [16 empty] | Virginia | VA | Richmond | 4A | Annual reduction in energy bills ($/ft2) | 0.033965 | 0.033965
California | Added construction cost ($/ft2) | -1.2453 | -1.2453 | [16 empty] | Virginia | VA | Richmond | 4A | Added construction cost ($/ft2) | -1.0213 | -1.0213
California | Present value of replacement costs / sf | -1.9978 | -1.9095 | [16 empty] | Virginia | VA | Richmond | 4A | Present value of replacement costs / sf | -1.5375 | -1.4696
California | Net present value of LCC savings ($/sf) | 4.35 | 3.7728 | [16 empty] | Virginia | VA | Richmond | 4A | Net present value of LCC savings ($/sf) | 3.0994 | 2.6878
California | Simple payback | Immediate | Immediate | [16 empty] | Virginia | VA | Richmond | 4A | Simple payback | Immediate | Immediate
California | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Virginia | VA | Richmond | 4A | Savings-to-investment ratio | Infinite | Infinite
Arizona | Annual reduction in energy bills ($/ft2) | 0.061256 | 0.061256 | [16 empty] | Wisconsin | WI | Madison | 6A | Annual reduction in energy bills ($/ft2) | 0.06236 | 0.06236
Arizona | Added construction cost ($/ft2) | -1.0989 | -1.0989 | [16 empty] | Wisconsin | WI | Madison | 6A | Added construction cost ($/ft2) | -1.2916 | -1.2916
Arizona | Present value of replacement costs / sf | -1.6118 | -1.5403 | [16 empty] | Wisconsin | WI | Madison | 6A | Present value of replacement costs / sf | -2.2209 | -2.1231
Arizona | Net present value of LCC savings ($/sf) | 3.8114 | 3.336 | [16 empty] | Wisconsin | WI | Madison | 6A | Net present value of LCC savings ($/sf) | 4.6499 | 4.0561
Arizona | Simple payback | Immediate | Immediate | [16 empty] | Wisconsin | WI | Madison | 6A | Simple payback | Immediate | Immediate
Arizona | Savings-to-investment ratio | Infinite | Infinite | [16 empty] | Wisconsin | WI | Madison | 6A | Savings-to-investment ratio | Infinite | Infinite
Florida | Annual reduction in energy bills ($/ft2) | 0.064107 | 0.064107
Florida | Added construction cost ($/ft2) | -0.9004 | -0.9004
Florida | Present value of replacement costs / sf | -1.5787 | -1.509
Florida | Net present value of LCC savings ($/sf) | 3.6218 | 3.2001
Florida | Simple payback | Immediate | Immediate
Florida | Savings-to-investment ratio | Infinite | Infinite
Hawaii | Annual reduction in energy bills ($/ft2) | 0.20293 | 0.20293
Hawaii | Added construction cost ($/ft2) | -1.2447 | -1.2447
Hawaii | Present value of replacement costs / sf | -2.1162 | -2.0222
Hawaii | Net present value of LCC savings ($/sf) | 7.1185 | 6.3138
Hawaii | Simple payback | Immediate | Immediate
Hawaii | Savings-to-investment ratio | Infinite | Infinite
Idaho | Annual reduction in energy bills ($/ft2) | 0.039552 | 0.039552
Idaho | Added construction cost ($/ft2) | -1.2143 | -1.2143
Idaho | Present value of replacement costs / sf | -1.8536 | -1.7719
Idaho | Net present value of LCC savings ($/sf) | 3.7536 | 3.2557
Idaho | Simple payback | Immediate | Immediate
Idaho | Savings-to-investment ratio | Infinite | Infinite
Illinois | Annual reduction in energy bills ($/ft2) | 0.045713 | 0.045713
Illinois | Added construction cost ($/ft2) | -1.4441 | -1.4441
Illinois | Present value of replacement costs / sf | -2.021 | -1.931
Illinois | Net present value of LCC savings ($/sf) | 4.2169 | 3.6035
Illinois | Simple payback | Immediate | Immediate
Illinois | Savings-to-investment ratio | Infinite | Infinite
Indiana | Annual reduction in energy bills ($/ft2) | 0.062853 | 0.062853
Indiana | Added construction cost ($/ft2) | -1.127 | -1.127
Indiana | Present value of replacement costs / sf | -1.9723 | -1.8859
Indiana | Net present value of LCC savings ($/sf) | 4.2308 | 3.7305
Indiana | Simple payback | Immediate | Immediate
Indiana | Savings-to-investment ratio | Infinite | Infinite
Kansas | Annual reduction in energy bills ($/ft2) | 0.063263 | 0.063263
Kansas | Added construction cost ($/ft2) | -1.1102 | -1.1102
Kansas | Present value of replacement costs / sf | -2.1815 | -2.0873
Kansas | Net present value of LCC savings ($/sf) | 4.4389 | 3.9439
Kansas | Simple payback | Immediate | Immediate
Kansas | Savings-to-investment ratio | Infinite | Infinite
Louisiana | Annual reduction in energy bills ($/ft2) | 0.065569 | 0.065569
Louisiana | Added construction cost ($/ft2) | -1.0452 | -1.0452
Louisiana | Present value of replacement costs / sf | -2.1178 | -2.0259
Louisiana | Net present value of LCC savings ($/sf) | 4.3861 | 3.8699
Louisiana | Simple payback | Immediate | Immediate
Louisiana | Savings-to-investment ratio | Infinite | Infinite
Maine | Annual reduction in energy bills ($/ft2) | 0.067527 | 0.067527
Maine | Added construction cost ($/ft2) | -1.1456 | -1.1456
Maine | Present value of replacement costs / sf | -2.3985 | -2.2939
Maine | Net present value of LCC savings ($/sf) | 4.7876 | 4.2183
Maine | Simple payback | Immediate | Immediate
Maine | Savings-to-investment ratio | Infinite | Infinite
Maryland | Annual reduction in energy bills ($/ft2) | 0.03433 | 0.03433
Maryland | Added construction cost ($/ft2) | -0.94212 | -0.94212
Maryland | Present value of replacement costs / sf | -1.5399 | -1.4722
Maryland | Net present value of LCC savings ($/sf) | 2.9898 | 2.5879
Maryland | Simple payback | Immediate | Immediate
Maryland | Savings-to-investment ratio | Infinite | Infinite
Michigan | Annual reduction in energy bills ($/ft2) | 0.062533 | 0.062533
Michigan | Added construction cost ($/ft2) | -1.1979 | -1.1979
Michigan | Present value of replacement costs / sf | -1.907 | -1.8221
Michigan | Net present value of LCC savings ($/sf) | 4.2247 | 3.6978
Michigan | Simple payback | Immediate | Immediate
Michigan | Savings-to-investment ratio | Infinite | Infinite
Minnesota | Annual reduction in energy bills ($/ft2) | 0.044765 | 0.044765
Minnesota | Added construction cost ($/ft2) | -1.1487 | -1.1487
Minnesota | Present value of replacement costs / sf | -2.0053 | -1.9155
Minnesota | Net present value of LCC savings ($/sf) | 3.8721 | 3.3505
Minnesota | Simple payback | Immediate | Immediate
Minnesota | Savings-to-investment ratio | Infinite | Infinite
Mississippi | Annual reduction in energy bills ($/ft2) | 0.078576 | 0.078576
Mississippi | Added construction cost ($/ft2) | -1.0187 | -1.0187
Mississippi | Present value of replacement costs / sf | -2.2289 | -2.1325
Mississippi | Net present value of LCC savings ($/sf) | 4.7313 | 4.219
Mississippi | Simple payback | Immediate | Immediate
Mississippi | Savings-to-investment ratio | Infinite | Infinite
Missouri | Annual reduction in energy bills ($/ft2) | 0.049556 | 0.049556
Missouri | Added construction cost ($/ft2) | -1.193 | -1.193
Missouri | Present value of replacement costs / sf | -1.937 | -1.8517
Missouri | Net present value of LCC savings ($/sf) | 3.9829 | 3.5012
Missouri | Simple payback | Immediate | Immediate
Missouri | Savings-to-investment ratio | Infinite | Infinite
Nevada | Annual reduction in energy bills ($/ft2) | 0.045491 | 0.045491
Nevada | Added construction cost ($/ft2) | -1.3192 | -1.3192
Nevada | Present value of replacement costs / sf | -1.7068 | -1.6303
Nevada | Net present value of LCC savings ($/sf) | 3.8246 | 3.3697
Nevada | Simple payback | Immediate | Immediate
Nevada | Savings-to-investment ratio | Infinite | Infinite
New Hampshire | Annual reduction in energy bills ($/ft2) | 0.08093 | 0.08093
New Hampshire | Added construction cost ($/ft2) | -0.94542 | -0.94542
New Hampshire | Present value of replacement costs / sf | -2.0393 | -1.9507
New Hampshire | Net present value of LCC savings ($/sf) | 4.4105 | 3.9064
New Hampshire | Simple payback | Immediate | Immediate
New Hampshire | Savings-to-investment ratio | Infinite | Infinite
New Mexico | Annual reduction in energy bills ($/ft2) | 0.063819 | 0.063819
New Mexico | Added construction cost ($/ft2) | -1.2208 | -1.2208
New Mexico | Present value of replacement costs / sf | -2.2847 | -2.1853
New Mexico | Net present value of LCC savings ($/sf) | 4.6849 | 4.1331
New Mexico | Simple payback | Immediate | Immediate
New Mexico | Savings-to-investment ratio | Infinite | Infinite
North Dakota | Annual reduction in energy bills ($/ft2) | 0.048156 | 0.048156
North Dakota | Added construction cost ($/ft2) | -1.0026 | -1.0026
North Dakota | Present value of replacement costs / sf | -2.875 | -2.7518
North Dakota | Net present value of LCC savings ($/sf) | 4.7064 | 4.2374
North Dakota | Simple payback | Immediate | Immediate
North Dakota | Savings-to-investment ratio | Infinite | Infinite
Ohio | Annual reduction in energy bills ($/ft2) | 0.05388 | 0.05388
Ohio | Added construction cost ($/ft2) | -1.2254 | -1.2254
Ohio | Present value of replacement costs / sf | -1.8325 | -1.7516
Ohio | Net present value of LCC savings ($/sf) | 4.0232 | 3.57
Ohio | Simple payback | Immediate | Immediate
Ohio | Savings-to-investment ratio | Infinite | Infinite
Oregon | Annual reduction in energy bills ($/ft2) | 0.039215 | 0.039215
Oregon | Added construction cost ($/ft2) | -1.0148 | -1.0148
Oregon | Present value of replacement costs / sf | -1.9267 | -1.8427
Oregon | Net present value of LCC savings ($/sf) | 3.5948 | 3.1442
Oregon | Simple payback | Immediate | Immediate
Oregon | Savings-to-investment ratio | Infinite | Infinite
Pennsylvania | Annual reduction in energy bills ($/ft2) | 0.040793 | 0.040793
Pennsylvania | Added construction cost ($/ft2) | -1.2892 | -1.2892
Pennsylvania | Present value of replacement costs / sf | -2.0747 | -1.9836
Pennsylvania | Net present value of LCC savings ($/sf) | 4.0327 | 3.4707
Pennsylvania | Simple payback | Immediate | Immediate
Pennsylvania | Savings-to-investment ratio | Infinite | Infinite
South Dakota | Annual reduction in energy bills ($/ft2) | 0.054331 | 0.054331
South Dakota | Added construction cost ($/ft2) | -1.1055 | -1.1055
South Dakota | Present value of replacement costs / sf | -2.1225 | -2.0298
South Dakota | Net present value of LCC savings ($/sf) | 4.2138 | 3.7708
South Dakota | Simple payback | Immediate | Immediate
South Dakota | Savings-to-investment ratio | Infinite | Infinite
Tennessee | Annual reduction in energy bills ($/ft2) | 0.068029 | 0.068029
Tennessee | Added construction cost ($/ft2) | -1.0289 | -1.0289
Tennessee | Present value of replacement costs / sf | -1.7194 | -1.6441
Tennessee | Net present value of LCC savings ($/sf) | 3.9972 | 3.5096
Tennessee | Simple payback | Immediate | Immediate
Tennessee | Savings-to-investment ratio | Infinite | Infinite
Vermont | Annual reduction in energy bills ($/ft2) | 0.066409 | 0.066409
Vermont | Added construction cost ($/ft2) | -0.69944 | -0.69944
Vermont | Present value of replacement costs / sf | -2.4704 | -2.365
Vermont | Net present value of LCC savings ($/sf) | 4.2819 | 3.8519
Vermont | Simple payback | Immediate | Immediate
Vermont | Savings-to-investment ratio | Infinite | Infinite
Washington | Annual reduction in energy bills ($/ft2) | 0.033502 | 0.033502
Washington | Added construction cost ($/ft2) | -1.1077 | -1.1077
Washington | Present value of replacement costs / sf | -1.686 | -1.6118
Washington | Net present value of LCC savings ($/sf) | 3.3314 | 2.9473
Washington | Simple payback | Immediate | Immediate
Washington | Savings-to-investment ratio | Infinite | Infinite
West Virginia | Annual reduction in energy bills ($/ft2) | 0.065582 | 0.065582
West Virginia | Added construction cost ($/ft2) | -1.3474 | -1.3474
West Virginia | Present value of replacement costs / sf | -2.1576 | -2.0631
West Virginia | Net present value of LCC savings ($/sf) | 4.7387 | 4.1421
West Virginia | Simple payback | Immediate | Immediate
West Virginia | Savings-to-investment ratio | Infinite | Infinite
Wyoming | Annual reduction in energy bills ($/ft2) | 0.063472 | 0.063472
Wyoming | Added construction cost ($/ft2) | -1.1498 | -1.1498
Wyoming | Present value of replacement costs / sf | -3.5331 | -3.383
Wyoming | Net present value of LCC savings ($/sf) | 5.875 | 5.3511
Wyoming | Simple payback | Immediate | Immediate
Wyoming | Savings-to-investment ratio | Infinite | Infinite
Alaska | Annual reduction in energy bills ($/ft2) | 0.10659 | 0.10659
Alaska | Added construction cost ($/ft2) | -1.6308 | -1.6308
Alaska | Present value of replacement costs / sf | -2.6339 | -2.5189
Alaska | Net present value of LCC savings ($/sf) | 6.258 | 5.4528
Alaska | Simple payback | Immediate | Immediate
Alaska | Savings-to-investment ratio | Infinite | Infinite

## Result Tables 1CZ (hidden)
3 CZ | 1 | 2 | 3 | 4 | 5 | 6
Cost-Effectiveness Results for Standard 90.1-2022 in the State of US National
Life Cycle Cost (LCC) savings is the primary measure DOE uses to assess the economic impact of building energy codes.
Table 3 shows that the value today of the total
LCC savings over 30 years for buildings in scenario 1
average $2.53 per square foot for 90.1-2013.
Table 4 shows that the LCC savings over 30 years
average $2.51 per square foot for scenario 2.
Table 5 shows that the primary benefit of ASHRAE
Standard 90.1-2013, annual energy cost savings,
average $0.189 per square foot for both scenarios.
Table 1. LCC Savings (30 Years) from ASHRAE Standard 90.1-2019, Scenario 1 ($/ft2)
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
Climate zone 2A | 1.23 | 0.94 | 3.54 | 1.36 | 2.17 | 3.1 | 2.5264 | 1
0.94
Table 2. LCC Savings (30 Years) from ASHRAE Standard 90.1-2019, Scenario 2 ($/ft2)
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
Climate zone 2A | 1.23 | 1.15 | 3.43 | 1.48 | 2.27 | 3.02 | 2.509 | 1
Table 3. Annual Energy Cost Savings from ASHRAE Standard 90.1-2019, Scenarios 1 and 2 ($/ft2)
Climate Zone | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
Climate zone 2A | 0.095 | 0.155 | 0.256 | 0.154 | 0.219 | 0.187 | 0.189 | 1
Costs and Weightings for Standard 90.1-2013 in the State of US National
Weighting factors are for just the analyzed prototypes, not all prototypes
based on data from 2003-2007
DE had no apartments; MT had no large office
Table 6. Construction Weights by Building Type
Climate Zone & Representative City | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
2A Tampa FL | 0.025336 | 0.017992 | 0.059235 | 0.032252 | 0.010034 | 0.074155 | 0.219 | 1
Table 7. Incremental Construction Cost of ASHRAE 90.1-2013 ($/ft2)
Climate Zone & Representative City | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
2A Tampa FL | 0.58745 | 1.6873 | 1.1848 | 1.3303 | 1.6698 | 0.9661 | 1.1266 | 1
Table 8. Simple Payback from ASHRAE Standard 90.1-2013, Scenarios 1 and 2 (Years)
Climate Zone & Representative City | Small Office | Large Office | Stand-Alone Retail | Primary School | Small Hotel | Mid-rise Apartment | All Building Types
2A Tampa FL | 6.2 | 10.8 | 4.6 | 8.3 | 7.4 | 5.2 | 5.8432 | 1
Table 8 shows simple payback results in years. Simple payback is the number of years required for energy cost savings to exceed the incremental first costs of a new code or code change proposals. Simple payback is not used as a measure of cost-effectiveness as it does not account for the time value of money, the value of energy cost savings that occur after payback is achieved, or any maintenance or replacement costs that occur after the initial investment.
Savings are computed for two scenarios:
Scenario 1 (publicly-owned) includes costs for initial equipment and construction, energy, maintenance and replacement and does not include loans or taxes.
Scenario 2 (privately-owned) includes the same costs as scenario 1 plus the initial investment is financed through a loan amortized over 30 years with corresponding tax deductions for interest and depreciation. Federal and state corporate income and local property taxes are accounted for.
Both scenarios include the residual value of equipment
with remaining useful life at the end of the 30 years. Totals for all building types in the state overall are averages based on Table 6 weightings.
Factors such as inflation and discount rates are
different between the two scenarios, as described
in the Cost-Effectiveness Methodology section.
Construction Weighting of Results
Energy and economic impacts were determined and reported separately for each building type. Cost-effectiveness results are also reported as an average for all analyzed building prototypes in the state. To determine these averages, results were combined across the different building types using weighting factors shown in Table 6. These weighting factors are based on the floor area of new construction and major renovations for the six analyzed building prototypes in the state. The weighting factors were developed from construction start data from 2003 to 2007 based on an approach developed by Jarnagin and Bandyopadhyay (McGraw Hill Construction 2007, Jarnagin and Bandyopadhyay 2009).
Incremental Construction Cost
Cost estimates were developed for the differences between the Base Code and ASHRAE Standard 90.1-2013 as implemented in the six prototype models. Costs for the initial construction include material, labor, commissioning, construction equipment, overhead and profit. These costs were developed using a commercial cost estimation firm, engineering design consultants and RS Means 2012 Cost Data (RS Means 2012a,b,c; 2004, Thornton et al. 2013).
Table 7 shows incremental initial cost for individual building types in the state and weighted average costs for all building types for moving to ASHRAE Standard 90.1-2013 from the Base Code. The incremental cost may be negative for some building types based on the downsizing of HVAC equipment resulting from reductions in heating and cooling loads due to improvements in ASHRAE Standard 90.1-2013, such as more efficient lighting systems and changes to the building thermal envelope.
The U.S. Department of Energy (DOE) provides estimates of energy and cost savings from code adoption at the National, Climate Zone, and State levels. For more information on how these estimates were developed, visit the DOE Building Energy Codes website: www.energycodes.gov/development/commercial
U.S Department of Energy
Energy Efficiency and Renewable Energy
BUILDING TECHNOLOGIES OFFICE
Building Energy Codes
For information on Building Energy
Codes, visit www.energycodes.gov
EERE Information Center
1-877-EERE-INFO (1-877-337-3463)
www.eere.energy.gov/informationcenter

## LCC Methodology (hidden)
| 1 | 2 | 3 | 4 | 5 | 6
Cost-Effectiveness Methodology for Standard 90.1 in the State of US National
LCC savings is the primary measure DOE uses to assess the cost-effectiveness of building energy codes.
This analysis demonstrates that for all building types in climate zones in the State of US National, ASHRAE Standard 90.1-2019 results in savings over the Base Code (ASHRAE Standard 90.1-2016).
Hence, ASHRAE Standard 90.1-2019 is cost-effective in the State of US National.
Table 9. Building Prototypes
| Building Prototype | Floor Area (ft²) | Number of Floors
| Small Office | 5500 | 1
| Large Office | 498640 | 13
| Stand-Alone Retail | 24690 | 1
| Primary School | 73970 | 1
| Small Hotel | 43210 | 4
| Mid-Rise Apartment | 33740 | 4
Figure 3. National Climate Zones
Table 10. LCC Economic Parameters
Economic Parameter |  | Scenario 1 | Scenario 2
Study Period – Years1 |  | 30 | 30
Nominal Discount Rate2 |  | 0.02 | 0.0525
Real Discount Rate2 |  | 0.03 | 0.033382
Effective Inflation Rate3 |  | -0.01 | 0.0185
Electricity Prices4 | per kWh | 0.1099 | 0.1099
Natural Gas Prices4 | per therm | 0.983 | 0.983
Energy Price Escalation Factors5 |  | Uniform present value factors | Uniform present value factors
Electricity Price UPV5 |  | 18.295 | 16.5807
Natural Gas Price UPV5 |  | 19.429 | 17.6084
Loan Interest Rate6 |  | NA | 0.0525
Federal Corporate Tax Rate7 |  | NA | 0.21
State Corporate Tax Rate8 |  | NA | 0.0601
Combined Income Tax Impact9 |  | NA | 0.25748
State and Average Local Sales Tax10 |  | 0.0656 | 0.0656
Detailed Energy Use and Cost
On the following pages, specific detailed results for US National are included:
Table 11 shows the average energy rates used.
Tables 12.A and 12.B show the per square foot energy costs for 90.1-2019 and 90.1-2022 and the cost savings from 90.1-2022.
Tables 13.A and 13.B show the per square foot energy use for 90.1-2019 and 90.1-2022 and the energy use savings from 90.1-2022.
Tables 14.A through 14.E show the energy end use by energy type for each climate zone in the state.
5 | Tables 14.A through 14.E show
1 | Table 14 shows
2 | Tables 14.A through 14.B show
3 | Tables 14.A through 14.C show
4 | Tables 14.A through 14.D show
5 | Tables 14.A through 14.E show
5 | Tables 12.A and 12.B show |  | Table 12.A.
1 | Table 12 shows |  | Table 12.
2 | Table 12 shows |  | Table 12.
3 | Table 12 shows |  | Table 12.
4 | Tables 12.A and 12.B show |  | Table 12.A.
5 | Tables 12.A and 12.B show |  | Table 12.A.
5 | Tables 13.A and 13.B show |  | Table 13.A.
1 | Table 13 shows |  | Table 13.
2 | Table 13 shows |  | Table 13.
3 | Table 13 shows |  | Table 13.
4 | Tables 13.A and 13.B show |  | Table 13.A.
5 | Tables 13.A and 13.B show |  | Table 13.A.
The cost-effectiveness analysis compares the cost for new buildings meeting ASHRAE Standard 90.1-2019 compared to new buildings meeting a Base Code, ASHRAE Standard 90.1-2016 (ASHRAE 2019, ASHRAE 2016). The analysis includes energy savings estimates from building energy simulations and LCC and simple payback calculations using standard economic analysis parameters. The analysis builds on work documented in ANSI/ASHRAE/IES Standard 90.1-2019 Determination of Energy Savings: Quantitative Analysis and the cost-effectiveness analysis documented in National Cost-effectiveness of ANSI/ASHRAE/IES Standard 90.1-2016 (Hart et al. 2020).
Building Prototypes and Energy Modeling
The cost-effectiveness analysis uses six building types represented by six prototype building energy models. These six are a subset of 16 prototype building energy models and represent 80% of commercial floor space. These models provide coverage of the significant changes in ASHRAE Standard 90.1 and are used to show the impacts of the changes on energy savings. The prototypes represent common construction practice and include the primary conventional HVAC systems most commonly used in commercial buildings. More information on the prototype buildings and savings analysis can be found at: www.energycodes.gov/development/commercial/90.1_models.
Each prototype building is analyzed for each of the climate zones found within the state. Using the U.S. Department of Energy (DOE) EnergyPlus™ software, the six building prototypes summarized in Table 9 are simulated with characteristics meeting the requirements of the Base Code and then modified to meet the requirements of the next edition of the code. The energy use and cost are then compared between the two sets of models.
Cost-Effectiveness
DOE uses standard economic Life Cycle Cost (LCC) cost-effectiveness analysis methods in comparing ASHRAE Standard 90.1-2013 and the Base Code. A detailed cost-effectiveness methodology has been established (Hart et al. 2015).
LCC Savings: LCC is the calculation of the present value of costs over a 30-year period including initial equipment and construction costs, energy savings, maintenance and replacement costs, and residual value of components at the end of the 30-year period. A separate LCC is determined for the Base Code and for ASHRAE Standard 90.1-2013. The LCC savings is the Base Code LCC minus the ASHRAE Standard 90.1-2013 LCC. Two cost scenarios are analyzed:
Scenario 1 includes the costs and savings listed above without borrowing or tax impacts.
Scenario 2 incudes the same costs as scenario 1 plus financing of the incremental first costs through increased borrowing with tax impacts including mortgage interest and depreciation deductions. Corporate tax rates are applied. Economic analysis factors such as discount rates are also different, as described in Table 10.
While not a true cost-effectiveness metric, simple payback is also calculated. Simple payback is the number of years required for accumulated annual energy cost savings to exceed the incremental first costs of a new code.
Cost-Effectiveness Method and Parameters
The DOE cost-effectiveness methodology accounts for the benefits of energy-efficient building construction over a multi-year analysis period, balancing initial costs against longer term energy savings. DOE evaluates energy codes and code proposals based on LCC analysis over a multi-year study period, accounting for energy savings, incremental investment for energy efficiency measures, and other economic impacts. The value of future savings and costs are discounted to a present value, with improvements deemed cost-effective when the net LCC savings (present value of savings minus cost) is positive.
The U.S. DOE Building Technologies Office (BTO) uses an LCC analysis similar to the method used for many federal building projects, as well as other public and private building projects (Fuller and Petersen 1995). The LCC analysis method consists of identifying costs (and revenues if any) and in what year they occur; then determining their value in today’s dollars (known as the present value). This method uses fundamental engineering economics relationships about the time value of money (money today is normally worth more than money tomorrow, which is why we pay interest on a loan and earn interest on savings). Future costs are discounted to the present based on a discount rate. The discount rate may reflect the interest rate at which money can be borrowed for projects with the same level of risk or the interest rate that can be earned on other conventional investments with similar risk.
The LCC for both scenarios includes incremental initial costs, repairs, maintenance and replacements. Scenario 2 also includes loan costs and tax impacts including mortgage interest and depreciation deductions. The residual value of equipment (or other component such as roof membrane) that has remaining useful life at end of the 30-year study period is also included for both scenarios. The residual value is calculated by multiplying the initial cost of the component by the years of useful life remaining for the component at year 30 divided by the total useful life, a simplified approach included in the Federal Energy Management Program (FEMP) LCC method (Fuller and Petersen 1995). The component in place at year 30 may be the original component if it has a longer than 30-year life or equipment that has already been replaced one or more times during the 30-year period that has a useful life that does not divide evenly into 30 years.
The financial and economic parameters used for the LCC calculations are shown in Table 10.
1 A 30-year study period captures most building components useful lives and is a commonly used study period for building project economic analysis. This period is consistent with previous and related national 90.1 cost-effectiveness analysis (Hart et al. 2015). It is also consistent with the cost-effectiveness analysis that was done for the residential energy code as described in multiple state reports and a summary report (DOE 2012). The federal building LCC method uses 25 years and the ASHRAE Standard 90.1 development process uses up to 40 years for building envelope code improvement analysis. Because of the time value of money, results are typically similar for any study periods of 20 years or more.
2 The scenario 1 real and nominal discount rates are from the National Institute of Standards and Technology (NIST) 2014 annual LCC update for the federal LCC method (Rushing et al. 2014). The scenario 2 nominal discount rate is assumed to be the marginal cost of capital, which is set equal to the loan interest rate (see footnote 6). The real discount rate for Scenario 2 is calculated from the nominal discount rate and inflation.
3 The scenario 1 effective inflation rate is from the NIST 2014 annual LCC update for the federal LCC method (Rushing et al. 2014). The scenario 2 inflation rate is the Producer Price Index for non-residential construction, June 1984 to June 2014 (Bureau of Labor Statistics 2015).
4 Scenario 1 and 2 electricity and natural gas prices are state average annual prices for 2014 from the United States Energy Information Agency (EIA) Electricity Power Monthly (EIA 2015a) and Natural Gas Monthly (EIA 2015b).
5 Scenario 1 energy price escalation rates are from the NIST 2014 annual update for the FEMP LCC method (Rushing et al. 2014). The NIST uniform present value (UPV) factors are multiplied by the first year annual energy cost to determine the present value of 30 years of energy costs and are based on a series of different annual escalation rates for 30 years. Scenario 2 UPV factors are based on NIST UPVs with an adjustment made for the scenario difference in discount rates.
6 The loan interest rate is estimated from multiple online sources listed in the references (Commercial Loan Direct 2015; Watts 2015).
7 The highest federal marginal corporate income tax rate is assumed to apply.
8 The highest marginal state corporate income tax rate is assumed to apply from the Federation of Tax Administrators (FTA 2015).
9 The combined tax impact is based on state tax being a deduction for federal tax, and is applied to depreciation and loan interest.
10 The state and average local sales tax is included in material costs in the cost estimate (Tax Foundation 2015).
Climate Zones
Climate zones are defined in ASHRAE Standard 90.1 and include eight primary climate zones, the hottest being climate zone 1 and the coldest being climate zone 8. Letters A, B, and C are applied in some cases to denote the level of moisture, with A indicating moist or humid, B indicating dry, and C indicating marine. Figure 3 shows the national climate zones. For this state analysis, savings is analyzed for each climate zone in the state using weather data from a selected city within the climate zone and state, or where necessary, a city in an adjoining state with more robust weather data.

## Energy Results (hidden)
State Commercial Energy Code Cost Effectiveness - Energy Cost Savings Results | [8 empty] | per square foot at right | [15 empty] | Table 11. Energy Rates for the State of US National, Average $ per unit
[26 empty] | Electricity | 0.1099 | kWh
[26 empty] | Gas | 0.983 | therm
Source: Energy Information Administration, annual average prices for 2014 (EIA 2015a,b)
Energy Cost | [5 empty] | G |  |  |  | J |  |  |  | M |  |  |  | P |  |  |  | S | S
Cost/therm | 0.983 |  | Energy Saving Results for ASHRAE Standard 90.1 in US National State | [21 empty] | Table 12.A. Energy Cost Saving Results for ASHRAE Standard 90.1 in the State of US National, $ per square foot | [12 empty] | Table 10.B. Energy Cost Saving Results for ASHRAE Standard 90.1 in the State of US National, $ per square foot
Cost/kWh | 0.1099 |  |  | 2A |  |  |  | 3A |  |  |  | 3B |  |  |  | 4A |  |  |  | 5A |  |  |  |  | Climate Zone: | 2A |  |  |  | 3A |  |  |  | 3B |  |  |  | Climate Zone: | 4A |  |  |  | 5A
|  |  |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  |  | Code: | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings |  | Code: | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings
| SO |  | Small Office | [20 empty] | 5502 | Small Office | [12 empty] | Small Office
| SO |  | Electricity | 5074.9378 | 4554.4087 | 520.5291 | 0.10257 | 4717.1523 | 4231.2416 | 485.9106 | 0.10301 | 4780.3448 | 4278.5902 | 501.7546 | 0.10496 | 4715.3206 | 4212.1007 | 503.2199 | 0.10672 | 4782.787 | 4250.871 | 531.916 | 0.11121 | 5502 | Electricity | 0.922 | 0.828 | 0.095 | 0.10304 | 0.857 | 0.769 | 0.088 | 0.10268 | 0.869 | 0.778 | 0.091 | 0.10472 | Electricity | 0.857 | 0.766 | 0.091 | 0.10618 | 0.869 | 0.773 | 0.097 | 0.11162
| SO |  | Gas | 0 | 0 | 0 | #DIV/0! | 15.4663 | 14.9073 | 0.55902 | 0.036145 | 2.0497 | 2.1429 | -0.09317 | -0.045455 | 29.535 | 25.0628 | 4.4722 | 0.15142 | 129.3205 | 112.4567 | 16.8638 | 0.1304 | 5502 | Gas | 0 | 0 | 0 | - | 0.003 | 0.003 | 0 | 0 | 0 | 0 | 0 | - | Gas | 0.005 | 0.005 | 0.001 | 0.2 | 0.024 | 0.02 | 0.003 | 0.125
| SO |  | Totals | 5074.9378 | 4554.4087 | 520.5291 | 0.10257 | 4732.6186 | 4246.1489 | 486.4697 | 0.10279 | 4782.3945 | 4280.7331 | 501.6614 | 0.1049 | 4744.8556 | 4237.1635 | 507.6921 | 0.107 | 4912.1075 | 4363.3277 | 548.7799 | 0.11172 | 5502 | Totals | 0.922 | 0.828 | 0.095 | 0.10304 | 0.86 | 0.772 | 0.088 | 0.10233 | 0.869 | 0.778 | 0.091 | 0.10472 | Totals | 0.862 | 0.77 | 0.092 | 0.10673 | 0.893 | 0.793 | 0.1 | 0.11198
| LO |  | Large Office | [20 empty] | 498588 | Large Office | [12 empty] | Large Office
| LO |  | Electricity | 877007.502 | 799684.6089 | 77322.8931 | 0.088167 | 829062.1002 | 754972.5873 | 74089.513 | 0.089365 | 871439.5406 | 795444.4226 | 75995.1179 | 0.087206 | 800959.4489 | 731591.881 | 69367.5679 | 0.086606 | 780146.5257 | 710585.3507 | 69561.175 | 0.089164 | 498588 | Electricity | 1.759 | 1.604 | 0.155 | 0.088118 | 1.663 | 1.514 | 0.149 | 0.089597 | 1.748 | 1.595 | 0.152 | 0.086957 | Electricity | 1.606 | 1.467 | 0.139 | 0.08655 | 1.565 | 1.425 | 0.14 | 0.089457
| LO |  | Gas | 6705.4753 | 6632.6161 | 72.8593 | 0.010866 | 10700.7162 | 10340.8921 | 359.8242 | 0.033626 | 10093.2451 | 9666.9904 | 426.2547 | 0.042232 | 15438.3391 | 13837.8575 | 1600.4815 | 0.10367 | 21908.9318 | 19205.4056 | 2703.5262 | 0.1234 | 498588 | Gas | 0.013 | 0.013 | 0 | 0 | 0.021 | 0.021 | 0.001 | 0.047619 | 0.02 | 0.019 | 0.001 | 0.05 | Gas | 0.031 | 0.028 | 0.003 | 0.096774 | 0.044 | 0.039 | 0.005 | 0.11364
| LO |  | Totals | 883712.9774 | 806317.225 | 77395.7524 | 0.08758 | 839762.8165 | 765313.4793 | 74449.3372 | 0.088655 | 881532.7857 | 805111.413 | 76421.3726 | 0.086691 | 816397.788 | 745429.7386 | 70968.0494 | 0.086928 | 802055.4575 | 729790.7563 | 72264.7012 | 0.090099 | 498588 | Totals | 1.772 | 1.617 | 0.155 | 0.087472 | 1.684 | 1.535 | 0.149 | 0.08848 | 1.768 | 1.615 | 0.153 | 0.086538 | Totals | 1.637 | 1.495 | 0.142 | 0.086744 | 1.609 | 1.464 | 0.145 | 0.090118
| RS |  | Standalone Retail | [20 empty] | 24692 | Stand-Alone Retail | [12 empty] | Standalone Retail
| RS |  | Electricity | 28765.7147 | 22504.3758 | 6261.3389 | 0.21767 | 23988.4227 | 17998.2316 | 5990.1911 | 0.24971 | 24603.8627 | 18933.5416 | 5670.3211 | 0.23046 | 22417.158 | 16928.4772 | 5488.6808 | 0.24484 | 21076.6832 | 16068.6928 | 5007.9904 | 0.23761 | 24692 | Electricity | 1.165 | 0.911 | 0.254 | 0.21803 | 0.972 | 0.729 | 0.243 | 0.25 | 0.996 | 0.767 | 0.23 | 0.23092 | Electricity | 0.908 | 0.686 | 0.222 | 0.24449 | 0.854 | 0.651 | 0.203 | 0.2377
| RS |  | Gas | 975.1216 | 906.5482 | 68.5734 | 0.070323 | 2684.3331 | 2318.2665 | 366.0666 | 0.13637 | 1542.9022 | 1314.821 | 228.0812 | 0.14783 | 5054.1228 | 4043.5964 | 1010.5264 | 0.19994 | 7214.6517 | 5676.967 | 1537.6847 | 0.21313 | 24692 | Gas | 0.039 | 0.037 | 0.003 | 0.076923 | 0.109 | 0.094 | 0.015 | 0.13761 | 0.062 | 0.053 | 0.009 | 0.14516 | Gas | 0.205 | 0.164 | 0.041 | 0.2 | 0.292 | 0.23 | 0.062 | 0.21233
| RS |  | Totals | 29740.8363 | 23410.924 | 6329.9123 | 0.21284 | 26672.7557 | 20316.498 | 6356.2577 | 0.23831 | 26146.7649 | 20248.3626 | 5898.4023 | 0.22559 | 27471.2807 | 20972.0735 | 6499.2072 | 0.23658 | 28291.3349 | 21745.6599 | 6545.6751 | 0.23137 | 24692 | Totals | 1.204 | 0.948 | 0.256 | 0.21262 | 1.08 | 0.823 | 0.257 | 0.23796 | 1.059 | 0.82 | 0.239 | 0.22568 | Totals | 1.113 | 0.849 | 0.263 | 0.2363 | 1.146 | 0.881 | 0.265 | 0.23124
| PS |  | Primary School | [20 empty] | 73959 | Primary School | [12 empty] | Primary School
| PS |  | Electricity | 89265.0546 | 77838.9652 | 11426.0894 | 0.128 | 73907.14 | 64011.5913 | 9895.5487 | 0.13389 | 71982.6689 | 61807.1194 | 10175.5495 | 0.14136 | 67932.8539 | 59466.6463 | 8466.2076 | 0.12463 | 62599.0405 | 54591.0243 | 8008.0162 | 0.12793 | 73959 | Electricity | 1.207 | 1.052 | 0.154 | 0.12759 | 0.999 | 0.866 | 0.134 | 0.13413 | 0.973 | 0.836 | 0.138 | 0.14183 | Electricity | 0.919 | 0.804 | 0.114 | 0.12405 | 0.846 | 0.738 | 0.108 | 0.12766
| PS |  | Gas | 5511.6827 | 5550.4416 | -38.7589 | -0.0070321 | 9062.9665 | 8636.1528 | 426.8137 | 0.047094 | 6158.1923 | 5966.5407 | 191.6516 | 0.031121 | 10283.2196 | 9250.7049 | 1032.5146 | 0.10041 | 14083.548 | 12153.3363 | 1930.2117 | 0.13705 | 73959 | Gas | 0.075 | 0.075 | -0.001 | -0.013333 | 0.123 | 0.117 | 0.006 | 0.04878 | 0.083 | 0.081 | 0.003 | 0.036145 | Gas | 0.139 | 0.125 | 0.014 | 0.10072 | 0.19 | 0.164 | 0.026 | 0.13684
| PS |  | Totals | 94776.7373 | 83389.4068 | 11387.3305 | 0.12015 | 82970.1066 | 72647.7442 | 10322.3624 | 0.12441 | 78140.8612 | 67773.6601 | 10367.2011 | 0.13267 | 78216.0735 | 68717.3512 | 9498.7222 | 0.12144 | 76682.5885 | 66744.3606 | 9938.2279 | 0.1296 | 73959 | Totals | 1.281 | 1.128 | 0.154 | 0.12022 | 1.122 | 0.982 | 0.14 | 0.12478 | 1.057 | 0.916 | 0.14 | 0.13245 | Totals | 1.058 | 0.929 | 0.128 | 0.12098 | 1.037 | 0.902 | 0.134 | 0.12922
| SH |  | Small Hotel | [20 empty] | 43202 | Small Hotel | [12 empty] | Small Hotel
| SH |  | Electricity | 44294.8901 | 36115.9183 | 8178.9718 | 0.18465 | 40311.6256 | 33317.6201 | 6994.0055 | 0.1735 | 40600.4184 | 33026.6293 | 7573.7891 | 0.18654 | 39804.5592 | 32655.6863 | 7148.8729 | 0.1796 | 40347.0378 | 33014.8456 | 7332.1923 | 0.18173 | 43202 | Electricity | 1.025 | 0.836 | 0.189 | 0.18439 | 0.933 | 0.771 | 0.162 | 0.17363 | 0.94 | 0.764 | 0.175 | 0.18617 | Electricity | 0.921 | 0.756 | 0.165 | 0.17915 | 0.934 | 0.764 | 0.17 | 0.18201
| SH |  | Gas | 11979.1076 | 10716.8347 | 1262.2729 | 0.10537 | 12885.2831 | 11318.343 | 1566.9402 | 0.12161 | 12558.4413 | 11135.2631 | 1423.1782 | 0.11332 | 13789.8748 | 11857.7066 | 1932.1682 | 0.14011 | 14618.3462 | 12441.6056 | 2176.7406 | 0.1489 | 43202 | Gas | 0.277 | 0.248 | 0.029 | 0.10469 | 0.298 | 0.262 | 0.036 | 0.12081 | 0.291 | 0.258 | 0.033 | 0.1134 | Gas | 0.319 | 0.274 | 0.045 | 0.14107 | 0.338 | 0.288 | 0.05 | 0.14793
| SH |  | Totals | 56273.9977 | 46832.753 | 9441.2446 | 0.16777 | 53196.9087 | 44635.963 | 8560.9457 | 0.16093 | 53158.8597 | 44161.8924 | 8996.9673 | 0.16925 | 53594.434 | 44513.3928 | 9081.0412 | 0.16944 | 54965.384 | 45456.4512 | 9508.9328 | 0.173 | 43202 | Totals | 1.303 | 1.084 | 0.219 | 0.16807 | 1.231 | 1.033 | 0.198 | 0.16084 | 1.23 | 1.022 | 0.208 | 0.16911 | Totals | 1.241 | 1.03 | 0.21 | 0.16922 | 1.272 | 1.052 | 0.22 | 0.17296
| MA |  | Mid-rise Apartment | [20 empty] | 33741 | Mid-Rise Apartment | [12 empty] | Mid-Rise Apartment
| MA |  | Electricity | 40812.2812 | 34496.9081 | 6315.373 | 0.15474 | 37917.332 | 32252.628 | 5664.704 | 0.1494 | 38616.4181 | 32463.117 | 6153.301 | 0.15934 | 37522.9131 | 32000.377 | 5522.5361 | 0.14718 | 36839.0909 | 31547.0089 | 5292.0819 | 0.14365 | 33741 | Electricity | 1.21 | 1.022 | 0.187 | 0.15455 | 1.124 | 0.956 | 0.168 | 0.14947 | 1.144 | 0.962 | 0.182 | 0.15909 | Electricity | 1.112 | 0.948 | 0.164 | 0.14748 | 1.092 | 0.935 | 0.157 | 0.14377
| MA |  | Gas | 46.0262 | 46.6784 | -0.65219 | -0.01417 | 709.4928 | 730.6425 | -21.1497 | -0.02981 | 222.0251 | 228.1744 | -6.1492 | -0.027696 | 1927.3234 | 1605.7922 | 321.5311 | 0.16683 | 3310.4383 | 2686.6623 | 623.776 | 0.18843 | 33741 | Gas | 0.001 | 0.001 | 0 | 0 | 0.021 | 0.022 | -0.001 | -0.047619 | 0.007 | 0.007 | 0 | 0 | Gas | 0.057 | 0.048 | 0.01 | 0.17544 | 0.098 | 0.08 | 0.018 | 0.18367
| MA |  | Totals | 40858.3073 | 34543.5865 | 6314.7208 | 0.15455 | 38626.8247 | 32983.2705 | 5643.5543 | 0.1461 | 38838.4432 | 32691.2914 | 6147.1518 | 0.15827 | 39450.2364 | 33606.1692 | 5844.0672 | 0.14814 | 40149.5291 | 34233.6713 | 5915.8579 | 0.14735 | 33741 | Totals | 1.211 | 1.024 | 0.187 | 0.15442 | 1.145 | 0.978 | 0.167 | 0.14585 | 1.151 | 0.969 | 0.182 | 0.15812 | Totals | 1.169 | 0.996 | 0.173 | 0.14799 | 1.19 | 1.015 | 0.175 | 0.14706
Energy Use | [5 empty] | G |  |  |  | J |  |  |  | M |  |  |  | P |  |  |  | S
kBtu/kWh | 3.413 |  | Energy Use Saving Results for ASHRAE Standard 90.1 in US National State | [21 empty] | Table 13.A. Energy Use Saving Results for ASHRAE Standard 90.1 in the State of US National, Energy Use per Square Foot | [12 empty] | Table 11.B. Energy Use Saving Results for ASHRAE Standard 90.1 in the State of US National, Energy Use per Square Foot
kBtu/therm | 100 |  |  | 2A |  |  |  | 3A |  |  |  | 3B |  |  |  | 4A |  |  |  | 5A |  |  |  |  | Climate Zone: | 2A |  |  |  | 3A |  |  |  | 3B |  |  |  | Climate Zone: | 4A |  |  |  | 5A
|  |  |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  | 2019 | 2022 | Savings |  |  | Code: | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings |  | Code: | 90.1-2019 | 90.1-2022 | Savings |  | 90.1-2019 | 90.1-2022 | Savings
| SO |  | Small Office | [20 empty] | 5502 | Small Office | [12 empty] | Small Office
| SO |  | Electricity, kWh | 46177.7781 | 41441.3892 | 4736.3889 | 0.10257 | 42922.2226 | 38500.8336 | 4421.3889 | 0.10301 | 43497.2226 | 38931.667 | 4565.5556 | 0.10496 | 42905.5559 | 38326.667 | 4578.8889 | 0.10672 | 43519.4448 | 38679.4448 | 4840 | 0.11121 | 5502 | Electricity, kWh/ft2 | 8.393 | 7.532 | 0.861 | 0.10259 | 7.801 | 6.998 | 0.804 | 0.10306 | 7.906 | 7.076 | 0.83 | 0.10498 | Electricity, kWh/ft2 | 7.798 | 6.966 | 0.832 | 0.10669 | 7.91 | 7.03 | 0.88 | 0.11125
| SO |  | Gas, therm | 0 | 0 | 0 | #DIV/0! | 15.7338 | 15.1651 | 0.56869 | 0.036145 | 2.0852 | 2.18 | -0.094782 | -0.045455 | 30.0458 | 25.4963 | 4.5495 | 0.15142 | 131.557 | 114.4015 | 17.1555 | 0.1304 | 5502 | Gas, therm/ft2 | 0 | 0 | 0 | - | 0.003 | 0.003 | 0 | 0 | 0 | 0 | 0 | - | Gas, therm/ft2 | 0.005 | 0.005 | 0.001 | 0.2 | 0.024 | 0.021 | 0.003 | 0.125
| SO |  | Totals, kBtu | 157604.7568 | 141439.4614 | 16165.2954 | 0.10257 | 148066.922 | 132919.8526 | 15147.0694 | 0.1023 | 148664.5404 | 133091.7773 | 15572.7631 | 0.10475 | 149441.2426 | 133358.5424 | 16082.7001 | 0.10762 | 161687.5667 | 143453.0976 | 18234.4691 | 0.11278 | 5502 | Totals, kBtu/ft2 | 28.645 | 25.707 | 2.938 | 0.10257 | 26.911 | 24.158 | 2.753 | 0.1023 | 27.02 | 24.19 | 2.83 | 0.10474 | Totals, kBtu/ft2 | 27.161 | 24.238 | 2.923 | 0.10762 | 29.387 | 26.073 | 3.314 | 0.11277
| LO |  | Large Office | [20 empty] | 498588 | Large Office | [12 empty] | Large Office
| LO | Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 shows the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional cost per square foot required by the upgrade, and the simple payback period in years. Figure 1 includes annual energy cost savings, first cost for the upgrade, and net annualized LCC savings per square foot for Scenario 2. Average values are weighted averages for all building types considered in all climate zones in the state, based on weightings shown in Table 6. | Electricity, kWh | 7980050.0638 | 7276475.0582 | 703575.0056 | 0.088167 | 7543786.1715 | 6869632.2772 | 674153.8943 | 0.089365 | 7929386.1745 | 7237892.8357 | 691493.3389 | 0.087206 | 7288075.0583 | 6656886.9977 | 631188.0606 | 0.086606 | 7098694.5012 | 6465744.7739 | 632949.7273 | 0.089164 | 498588 | Electricity, kWh/ft2 | 16.005 | 14.594 | 1.411 | 0.08816 | 15.13 | 13.778 | 1.352 | 0.089359 | 15.904 | 14.517 | 1.387 | 0.087211 | Electricity, kWh/ft2 | 14.617 | 13.351 | 1.266 | 0.086611 | 14.238 | 12.968 | 1.269 | 0.089128
| LO |  | Gas, therm | 6821.4398 | 6747.3205 | 74.1193 | 0.010866 | 10885.7744 | 10519.7274 | 366.047 | 0.033626 | 10267.7976 | 9834.1713 | 433.6263 | 0.042232 | 15705.3297 | 14077.1694 | 1628.1602 | 0.10367 | 22287.8248 | 19537.5439 | 2750.2809 | 0.1234 | 498588 | Gas, therm/ft2 | 0.014 | 0.014 | 0 | 0 | 0.022 | 0.021 | 0.001 | 0.045455 | 0.021 | 0.02 | 0.001 | 0.047619 | Gas, therm/ft2 | 0.031 | 0.028 | 0.003 | 0.096774 | 0.045 | 0.039 | 0.006 | 0.13333
| LO |  | Totals, kBtu | 27918054.8492 | 25509341.4251 | 2408713.4241 | 0.086278 | 26835519.6437 | 24498027.7053 | 2337491.9384 | 0.087104 | 28089774.778 | 25686345.3792 | 2403429.3988 | 0.085562 | 26444733.1418 | 24127672.2661 | 2317060.8757 | 0.087619 | 26456626.8122 | 24021341.2993 | 2435285.5129 | 0.092048 | 498588 | Totals, kBtu/ft2 | 55.994 | 51.163 | 4.831 | 0.086277 | 53.823 | 49.135 | 4.688 | 0.0871 | 56.339 | 51.518 | 4.82 | 0.085554 | Totals, kBtu/ft2 | 53.039 | 48.392 | 4.647 | 0.087615 | 53.063 | 48.179 | 4.884 | 0.092042
| RS |  | Standalone Retail | [20 empty] | 24692 | Stand-Alone Retail | [12 empty] | Standalone Retail
| RS |  | Electricity, kWh | 261744.4465 | 204771.3905 | 56973.056 | 0.21767 | 218275.0017 | 163769.168 | 54505.8338 | 0.24971 | 223875.0018 | 172279.7236 | 51595.2782 | 0.23046 | 203977.7794 | 154035.279 | 49942.5004 | 0.24484 | 191780.5571 | 146211.9456 | 45568.6115 | 0.23761 | 24692 | Electricity, kWh/ft2 | 10.6 | 8.293 | 2.307 | 0.21764 | 8.84 | 6.632 | 2.207 | 0.24966 | 9.067 | 6.977 | 2.09 | 0.23051 | Electricity, kWh/ft2 | 8.261 | 6.238 | 2.023 | 0.24489 | 7.767 | 5.921 | 1.845 | 0.23754
| RS |  | Gas, therm | 991.9854 | 922.2261 | 69.7593 | 0.070323 | 2730.7559 | 2358.3586 | 372.3973 | 0.13637 | 1569.5852 | 1337.5595 | 232.0256 | 0.14783 | 5141.5287 | 4113.5263 | 1028.0024 | 0.19994 | 7339.4219 | 5775.1445 | 1564.2774 | 0.21313 | 24692 | Gas, therm/ft2 | 0.04 | 0.037 | 0.003 | 0.075 | 0.111 | 0.096 | 0.015 | 0.13514 | 0.064 | 0.054 | 0.009 | 0.14062 | Gas, therm/ft2 | 0.208 | 0.167 | 0.042 | 0.20192 | 0.297 | 0.234 | 0.063 | 0.21212
| RS |  | Totals, kBtu | 992532.3358 | 791107.3616 | 201424.9742 | 0.20294 | 1018048.1714 | 794780.0261 | 223268.1453 | 0.21931 | 921043.8962 | 721746.6486 | 199297.2476 | 0.21638 | 1210329.036 | 937075.0373 | 273253.9987 | 0.22577 | 1388489.2282 | 1076535.8198 | 311953.4085 | 0.22467 | 24692 | Totals, kBtu/ft2 | 40.197 | 32.039 | 8.157 | 0.20293 | 41.23 | 32.188 | 9.042 | 0.21931 | 37.301 | 29.23 | 8.071 | 0.21637 | Totals, kBtu/ft2 | 49.017 | 37.951 | 11.066 | 0.22576 | 56.232 | 43.599 | 12.634 | 0.22468
| PS |  | Primary School | [20 empty] | 73959 | Primary School | [12 empty] | Primary School
| PS |  | Electricity, kWh | 812238.8954 | 708270.839 | 103968.0564 | 0.128 | 672494.4498 | 582453.0602 | 90041.3896 | 0.13389 | 654983.3386 | 562394.1712 | 92589.1674 | 0.14136 | 618133.3383 | 541097.7821 | 77035.5562 | 0.12463 | 569600.0046 | 496733.6151 | 72866.3895 | 0.12793 | 73959 | Electricity, kWh/ft2 | 10.982 | 9.577 | 1.406 | 0.12803 | 9.093 | 7.875 | 1.217 | 0.13384 | 8.856 | 7.604 | 1.252 | 0.14137 | Electricity, kWh/ft2 | 8.358 | 7.316 | 1.042 | 0.12467 | 7.702 | 6.716 | 0.985 | 0.12789
| PS |  | Gas, therm | 5607.0017 | 5646.4309 | -39.4292 | -0.0070321 | 9219.7015 | 8785.5064 | 434.195 | 0.047094 | 6264.692 | 6069.7261 | 194.966 | 0.031121 | 10461.0576 | 9410.6866 | 1050.3709 | 0.10041 | 14327.1088 | 12363.5161 | 1963.5927 | 0.13705 | 73959 | Gas, therm/ft2 | 0.076 | 0.076 | -0.001 | -0.013158 | 0.125 | 0.119 | 0.006 | 0.048 | 0.085 | 0.082 | 0.003 | 0.035294 | Gas, therm/ft2 | 0.141 | 0.127 | 0.014 | 0.099291 | 0.194 | 0.167 | 0.027 | 0.13918
| PS |  | Totals, kBtu | 3332871.5236 | 2981971.4664 | 350900.0572 | 0.10528 | 3217193.7044 | 2866462.9394 | 350730.765 | 0.10902 | 2861927.3382 | 2526423.9117 | 335503.4265 | 0.11723 | 3155794.8389 | 2787835.3924 | 367959.4465 | 0.1166 | 3376755.696 | 2931703.436 | 445052.26 | 0.1318 | 73959 | Totals, kBtu/ft2 | 45.064 | 40.319 | 4.745 | 0.10529 | 43.5 | 38.757 | 4.742 | 0.10901 | 38.696 | 34.16 | 4.536 | 0.11722 | Totals, kBtu/ft2 | 42.67 | 37.694 | 4.975 | 0.11659 | 45.657 | 39.64 | 6.018 | 0.13181
| SH |  | Small Hotel | [20 empty] | 43202 | Small Hotel | [12 empty] | Small Hotel
| SH |  | Electricity, kWh | 403047.2254 | 328625.2804 | 74421.945 | 0.18465 | 366802.7807 | 303163.058 | 63639.7227 | 0.1735 | 369430.5585 | 300515.2802 | 68915.2783 | 0.18654 | 362188.8918 | 297140.0024 | 65048.8894 | 0.1796 | 367125.0029 | 300408.058 | 66716.945 | 0.18173 | 43202 | Electricity, kWh/ft2 | 9.329 | 7.607 | 1.723 | 0.18469 | 8.49 | 7.017 | 1.473 | 0.1735 | 8.551 | 6.956 | 1.595 | 0.18653 | Electricity, kWh/ft2 | 8.384 | 6.878 | 1.506 | 0.17963 | 8.498 | 6.954 | 1.544 | 0.18169
| SH |  | Gas, therm | 12186.2743 | 10902.1716 | 1284.1026 | 0.10537 | 13108.1212 | 11514.0824 | 1594.0388 | 0.12161 | 12775.627 | 11327.8363 | 1447.7907 | 0.11332 | 14028.3568 | 12062.7737 | 1965.5831 | 0.14011 | 14871.1558 | 12656.7707 | 2214.3851 | 0.1489 | 43202 | Gas, therm/ft2 | 0.282 | 0.252 | 0.03 | 0.10638 | 0.303 | 0.267 | 0.037 | 0.12211 | 0.296 | 0.262 | 0.034 | 0.11486 | Gas, therm/ft2 | 0.325 | 0.279 | 0.045 | 0.13846 | 0.344 | 0.293 | 0.051 | 0.14826
| SH |  | Totals, kBtu | 2594227.608 | 2211815.2461 | 382412.3618 | 0.14741 | 2562710.0112 | 2186103.7543 | 376606.2569 | 0.14696 | 2538429.1922 | 2158442.2822 | 379986.91 | 0.14969 | 2638986.3725 | 2220416.1986 | 418570.1739 | 0.15861 | 2740113.2181 | 2290969.7712 | 449143.447 | 0.16391 | 43202 | Totals, kBtu/ft2 | 60.049 | 51.197 | 8.852 | 0.14741 | 59.319 | 50.602 | 8.717 | 0.14695 | 58.757 | 49.962 | 8.796 | 0.1497 | Totals, kBtu/ft2 | 61.085 | 51.396 | 9.689 | 0.15862 | 63.426 | 53.029 | 10.396 | 0.16391
| MA |  | Mid-rise Apartment | [20 empty] | 33741 | Mid-Rise Apartment | [12 empty] | Mid-Rise Apartment
| MA |  | Electricity, kWh | 371358.3363 | 313893.6136 | 57464.7227 | 0.15474 | 345016.6694 | 293472.5023 | 51544.1671 | 0.1494 | 351377.7806 | 295387.7801 | 55990.0004 | 0.15934 | 341427.7805 | 291177.2246 | 50250.556 | 0.14718 | 335205.5582 | 287051.9467 | 48153.6115 | 0.14365 | 33741 | Electricity, kWh/ft2 | 11.006 | 9.303 | 1.703 | 0.15473 | 10.225 | 8.698 | 1.528 | 0.14944 | 10.414 | 8.755 | 1.659 | 0.1593 | Electricity, kWh/ft2 | 10.119 | 8.63 | 1.489 | 0.14715 | 9.935 | 8.508 | 1.427 | 0.14363
| MA |  | Gas, therm | 46.8222 | 47.4856 | -0.66347 | -0.01417 | 721.7627 | 743.2782 | -21.5154 | -0.02981 | 225.8648 | 232.1204 | -6.2556 | -0.027696 | 1960.6545 | 1633.5628 | 327.0917 | 0.16683 | 3367.689 | 2733.1254 | 634.5636 | 0.18843 | 33741 | Gas, therm/ft2 | 0.001 | 0.001 | 0 | 0 | 0.021 | 0.022 | -0.001 | -0.047619 | 0.007 | 0.007 | 0 | 0 | Gas, therm/ft2 | 0.058 | 0.048 | 0.01 | 0.17241 | 0.1 | 0.081 | 0.019 | 0.19
| MA |  | Totals, kBtu | 1272128.2184 | 1076067.4671 | 196060.7513 | 0.15412 | 1249718.1664 | 1075949.4691 | 173768.6974 | 0.13905 | 1221838.8471 | 1031370.5349 | 190468.3122 | 0.15589 | 1361358.4643 | 1157144.148 | 204214.3163 | 0.15001 | 1480825.4712 | 1253020.8389 | 227804.6322 | 0.15384 | 33741 | Totals, kBtu/ft2 | 37.703 | 31.892 | 5.811 | 0.15413 | 37.039 | 31.888 | 5.15 | 0.13904 | 36.212 | 30.567 | 5.645 | 0.15589 | Totals, kBtu/ft2 | 40.347 | 34.295 | 6.052 | 0.15 | 43.888 | 37.136 | 6.752 | 0.15385

## EndUse Tables (hidden)
[8 empty] | Column Offset | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
[8 empty] | Floor area, sf | 5502 | 5502 | 498588 | 498588 | 24692 | 24692 | 73959 | 73959 | 43202 | 43202 | 33741 | 33741 | sf
[8 empty] | Conversion divider | 1 | 100 | 1 | 100 | 1 | 100 | 1 | 100 | 1 | 100 | 1 | 100 |  | 1: Do not mess with; 5: CZ; 6: Prototype; 7: Fuel Type
[6 empty] | CZ | CZ offset | ASHRAE 90.1-2019 | [13 empty] | 1: Pivot table to right!!; 5: 2A; 17: 3A; 29: 3B; 41: 4A; 53: 5A
[6 empty] | 2A | 0 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1: Except must refresh; 5: SO; 7: LO; 9: RS; 11: PS; 13: SH; 15: MA; 17: SO; 19: LO; 21: RS; 23: PS; 25: SH; 27: MA; 29: SO; 31: LO; 33: RS; 35: PS; 37: SH; 39: MA; 41: SO; 43: LO; 45: RS; 47: PS; 49: SH; 51: MA; 53: SO; 55: LO; 57: RS; 59: PS; 61: SH; 63: MA
[6 empty] | 3A | 12 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | after state change |  | A.std.year | Data | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG | EL | NG
[6 empty] | 3B | 24 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1: STD2019; 2: 1; 3: STD2019
[6 empty] | 4A | 36 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.htg | 2 |  | Sum of B.htg | 83.3333 | 0 | 0 | 70925.1551 | 0 | 16198.1946 | 0 | 100914.0888 | 2116.6667 | 3990.3101 | 0 | 4682.2166 | 1727.7778 | 1573.3764 | 0 | 418224.3042 | 0 | 186511.4529 | 0 | 449369.5748 | 15588.889 | 28718.8587 | 0 | 72176.2737 | 702.7778 | 208.5198 | 0 | 371563.2674 | 0 | 71332.7165 | 0 | 157053.2968 | 6236.1112 | 12776.5748 | 0 | 22586.482 | 3341.6667 | 3004.5803 | 0 | 853575.6638 | 0 | 424792.6768 | 0 | 564235.5315 | 35502.7781 | 67835.2713 | 0 | 196065.4494 | 5533.3334 | 13155.7016 | 0 | 1472301.2015 | 0 | 642231.4023 | 0 | 943182.2943 | 59441.6671 | 107217.0726 | 0 | 336768.9009
[6 empty] | 5A | 48 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.clg | 3 |  | Sum of B.clg | 10700.0001 | 0 | 1278305.5658 | 0 | 98269.4452 | 0 | 301227.7802 | 0 | 144080.5567 | 0 | 75686.1117 | 0 | 5725 | 0 | 807900.0065 | 0 | 54113.8893 | 0 | 169541.668 | 0 | 95338.8897 | 0 | 44241.667 | 0 | 6463.8889 | 0 | 879747.2293 | 0 | 54041.6671 | 0 | 155222.2235 | 0 | 96908.3341 | 0 | 50672.2226 | 0 | 4291.6667 | 0 | 601619.4493 | 0 | 36305.5558 | 0 | 108397.2231 | 0 | 73327.7784 | 0 | 33241.6669 | 0 | 2558.3334 | 0 | 440350.0035 | 0 | 20330.5557 | 0 | 64183.3338 | 0 | 55194.4449 | 0 | 20866.6668 | 0
[8 empty] | ASHRAE 90.1-2022 | [13 empty] | Sum of B.intLgt | 4 |  | Sum of B.intLgt | 7394.4445 | 0 | 682308.3388 | 0 | 62308.3338 | 0 | 78172.2228 | 0 | 48975.0004 | 0 | 20277.7779 | 0 | 7427.7778 | 0 | 683780.561 | 0 | 62802.7783 | 0 | 79038.8895 | 0 | 49186.1115 | 0 | 20277.7779 | 0 | 7444.4445 | 0 | 682994.4499 | 0 | 64861.1116 | 0 | 80119.4451 | 0 | 49255.5559 | 0 | 20277.7779 | 0 | 7344.4445 | 0 | 684355.561 | 0 | 64775.0005 | 0 | 79377.7784 | 0 | 48761.1115 | 0 | 20277.7779 | 0 | 7336.1112 | 0 | 683655.561 | 0 | 64719.445 | 0 | 78475.0006 | 0 | 48708.3337 | 0 | 20277.7779 | 0
[6 empty] | 2A | 0 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.extLgt | 5 |  | Sum of B.extLgt | 2744.4445 | 0 | 97358.3341 | 0 | 12102.7779 | 0 | 8308.3334 | 0 | 14488.889 | 0 | 9172.2223 | 0 | 2766.6667 | 0 | 98152.7786 | 0 | 12113.889 | 0 | 8333.3334 | 0 | 14497.2223 | 0 | 9177.7779 | 0 | 2722.2222 | 0 | 96608.3341 | 0 | 12111.1112 | 0 | 8283.3334 | 0 | 14497.2223 | 0 | 9177.7779 | 0 | 2744.4445 | 0 | 97658.3341 | 0 | 12175.0001 | 0 | 8327.7778 | 0 | 14475.0001 | 0 | 9163.889 | 0 | 2763.8889 | 0 | 98133.3341 | 0 | 12133.3334 | 0 | 8327.7778 | 0 | 14480.5557 | 0 | 9166.6667 | 0
[6 empty] | 3A | 12 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.intEqp | 6 |  | Sum of B.intEqp | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 122138.8899 | 399495.4379 | 125580.5566 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 122138.8899 | 399495.4379 | 125580.5566 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 122138.8899 | 399495.4379 | 125580.5566 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 122138.8899 | 399495.4379 | 125580.5566 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 122138.8899 | 399495.4379 | 125580.5566 | 0
[6 empty] | 3B | 24 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.extEqp | 7 |  | Sum of B.extEqp | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4744.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4744.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0
[6 empty] | 4A | 36 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.fans | 8 |  | Sum of B.fans | 5336.1112 | 0 | 578358.338 | 0 | 35091.6669 | 0 | 72483.3339 | 0 | 71175.0006 | 0 | 35080.5558 | 0 | 5163.8889 | 0 | 646741.6718 | 0 | 35272.2225 | 0 | 66347.2228 | 0 | 69980.5561 | 0 | 28511.1113 | 0 | 6102.7778 | 0 | 758438.895 | 0 | 38888.8892 | 0 | 74466.6673 | 0 | 80322.2229 | 0 | 31447.2225 | 0 | 4922.2223 | 0 | 617022.2272 | 0 | 36750.0003 | 0 | 70625.0006 | 0 | 67911.1117 | 0 | 26719.4447 | 0 | 4941.6667 | 0 | 620355.5605 | 0 | 40625.0003 | 0 | 67794.445 | 0 | 67088.8894 | 0 | 25136.1113 | 0
[6 empty] | 5A | 48 | Total Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sum of B.pumps | 9 |  | Sum of B.pumps | 0 | 0 | 186600.0015 | 0 | 0 | 0 | 119.4444 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 134530.5566 | 0 | 0 | 0 | 386.1111 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 139966.6678 | 0 | 0 | 0 | 163.8889 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 113919.4454 | 0 | 0 | 0 | 441.6667 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 90044.4452 | 0 | 0 | 0 | 719.4445 | 0 | 72.2222 | 0 | 0 | 0
[22 empty] | Sum of B.heatRej | 10 |  | Sum of B.heatRej | 0 | 0 | 441794.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287894.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267875.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203600.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147002.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | Sum of B.humid | 11 |  | Sum of B.humid | 0 | 0 | 94158.3341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266897.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496619.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350750.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401683.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | Sum of B.heatRec | 12 |  | Sum of B.heatRec | 0 | 0 | 14030.5557 | 0 | 0 | 0 | 15058.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10752.7779 | 0 | 0 | 0 | 12025.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12013.889 | 0 | 0 | 0 | 14147.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10333.3334 | 0 | 0 | 0 | 13305.5557 | 0 | 0 | 0 | 0 | 0
[6 empty] | .A |  | Table 12.A. Annual Energy Usage for Buildings in the State of US National in Climate Zone 2A | [13 empty] | Sum of B.swh | 13 |  | Sum of B.swh | 6502.7778 | 0 | 0 | 611218.8262 | 0 | 83000.3452 | 7177.7778 | 117595.6701 | 0 | 815141.6795 | 105561.112 | 0 | 6694.4445 | 0 | 0 | 670353.1363 | 0 | 86564.1376 | 7177.7778 | 130410.1575 | 0 | 882597.824 | 117227.7787 | 0 | 6644.4445 | 0 | 0 | 655216.4969 | 0 | 85625.7986 | 7177.7778 | 127225.492 | 0 | 865290.6834 | 114222.2231 | 0 | 6844.4445 | 0 | 0 | 716957.3041 | 0 | 89360.1981 | 7177.7778 | 139679.809 | 0 | 935504.9756 | 126444.4455 | 0 | 6969.4445 | 0 | 0 | 756481.278 | 0 | 91710.7845 | 7180.5556 | 147338.1713 | 0 | 980403.0726 | 134177.7789 | 0
[8 empty] | Energy | Small Office |  | Large Office |  | Stand-Alone Retail |  | Primary School |  | Small Hotel |  | Mid-Rise Apartment |  |  | Sum of B.refrg | 14 |  | Sum of B.refrg | 0 | 0 | 0 | 0 | 0 | 0 | 12555.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12505.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12411.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12502.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12477.7779 | 0 | 0 | 0 | 0 | 0
[8 empty] | End-Use | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas |  | Sum of B.total | 15 |  | Sum of B.total | 46177.7781 | 0 | 7980050.0638 | 682143.9813 | 261744.4465 | 99198.5398 | 812238.8954 | 560700.1737 | 403047.2254 | 1218627.4275 | 371358.3363 | 4682.2166 | 42922.2226 | 1573.3764 | 7543786.1715 | 1088577.4405 | 218275.0017 | 273075.5904 | 672494.4498 | 921970.1471 | 366802.7807 | 1310812.1206 | 345016.6694 | 72176.2737 | 43497.2226 | 208.5198 | 7929386.1745 | 1026779.7643 | 223875.0018 | 156958.5151 | 654983.3386 | 626469.2036 | 369430.5585 | 1277562.696 | 351377.7806 | 22586.482 | 42905.5559 | 3004.5803 | 7288075.0583 | 1570532.9678 | 203977.7794 | 514152.8749 | 618133.3383 | 1046105.7553 | 362188.8918 | 1402835.6848 | 341427.7805 | 196065.4494 | 43519.4448 | 13155.7016 | 7098694.5012 | 2228782.4795 | 191780.5571 | 733942.1869 | 569600.0046 | 1432710.8804 | 367125.0029 | 1487115.5831 | 335205.5582 | 336768.9009
[5 empty] | Climate zone: | 2A |  |  | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ |  | Sum of B.extEqp.rev | 16 |  | Sum of B.extEqp.rev | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4744.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4744.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530358.3376 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0
[9 empty] | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr |  | Sum of B.sum | 17 |  | Sum of B.sum | 46177.7781 | 0 | 7980050.0638 | 682143.9813 | 261744.4465 | 99198.5398 | 812238.8954 | 560700.1737 | 403047.2254 | 1218627.4275 | 371358.3363 | 4682.2166 | 42922.2226 | 1573.3764 | 7543786.1715 | 1088577.4405 | 218275.0017 | 273075.5904 | 672494.4498 | 921970.1471 | 366802.7807 | 1310812.1206 | 345016.6694 | 72176.2737 | 43497.2226 | 208.5198 | 7929386.1745 | 1026779.7643 | 223875.0018 | 156958.5151 | 654983.3386 | 626469.2036 | 369430.5585 | 1277562.696 | 351377.7806 | 22586.482 | 42905.5559 | 3004.5803 | 7288075.0583 | 1570532.9678 | 203977.7794 | 514152.8749 | 618133.3383 | 1046105.7553 | 362188.8918 | 1402835.6848 | 341427.7805 | 196065.4494 | 43519.4448 | 13155.7016 | 7098694.5012 | 2228782.4795 | 191780.5571 | 733942.1869 | 569600.0046 | 1432710.8804 | 367125.0029 | 1487115.5831 | 335205.5582 | 336768.9009
| End Uses |  | End Use Indices |  |  | ColOfst |  | ASHRAE 90.1-2019 | [13 empty] | 1: Std2022; 2: 18; 3: STD2022
htg | humid |  | 2 | 11 | 1 | 0 |  | Heating, Humidification | #VALUE! | 0.00015146 | 0 | 0.0018885 | 2.8724 | 0 | 0.21902 | 0 | 2.3359 | 0.00048995 | 0.11826 | 0 |  | Sum of B.htg | 19 |  | Sum of B.htg | 77.7778 | 0 | 0 | 63503.747 | 0 | 9222.2606 | 0 | 104857.008 | 2000 | 37.9127 | 0 | 4748.5638 | 1666.6667 | 1516.5074 | 0 | 381600.6507 | 0 | 149271.7182 | 0 | 405940.5943 | 14480.5557 | 4141.9608 | 0 | 74327.8186 | 702.7778 | 217.9979 | 0 | 328191.156 | 0 | 48130.1534 | 0 | 137556.6986 | 5727.7778 | 151.6507 | 0 | 23212.0413 | 2916.6667 | 2549.6281 | 0 | 690731.2044 | 0 | 321992.432 | 0 | 459226.8728 | 32313.8891 | 14236.2131 | 0 | 163356.2806 | 4813.8889 | 11440.1526 | 0 | 1197235.1951 | 0 | 485813.143 | 0 | 746841.9779 | 54716.6671 | 35600.011 | 0 | 273312.5447
clg | heatRej |  | 3 | 10 | 1 | 0 |  | Cooling | #VALUE! | 0.019447 | 0 | 0.034499 | 0 | 0.039798 | 0 | 0.040729 | 0 | 0.03335 | 0 | 0.022431 |  | Sum of B.clg | 20 |  | Sum of B.clg | 9777.7779 | 0 | 1191736.1206 | 0 | 84894.4451 | 0 | 274613.8911 | 0 | 127822.2232 | 0 | 65427.7783 | 0 | 5197.2223 | 0 | 748405.5615 | 0 | 46230.5559 | 0 | 155088.8901 | 0 | 88172.2229 | 0 | 39969.4448 | 0 | 5880.5556 | 0 | 815747.2287 | 0 | 47222.2226 | 0 | 147066.6678 | 0 | 91583.3341 | 0 | 45877.7781 | 0 | 3908.3334 | 0 | 557408.3378 | 0 | 31652.778 | 0 | 97913.8897 | 0 | 64838.8894 | 0 | 28708.3336 | 0 | 2219.4445 | 0 | 387850.0031 | 0 | 17355.5557 | 0 | 59258.3338 | 0 | 47647.2226 | 0 | 18452.7779 | 0
fans | pumps | heatRec | 8 | 9 | 12 | 0 |  | Fans, Pumps, Heat Recovery | #VALUE! | 0.0096985 | 0 | 0.015624 | 0 | 0.014212 | 0 | 0.011853 | 0 | 0.016492 | 0 | 0.010397 |  | Sum of B.intLgt | 21 |  | Sum of B.intLgt | 5391.6667 | 0 | 475586.1149 | 0 | 46583.3337 | 0 | 68561.1117 | 0 | 43594.4448 | 0 | 15900.0001 | 0 | 5413.8889 | 0 | 476594.4483 | 0 | 40625.0003 | 0 | 69272.2228 | 0 | 45511.1115 | 0 | 15900.0001 | 0 | 5458.3334 | 0 | 490958.3373 | 0 | 48436.1115 | 0 | 73866.6673 | 0 | 43819.4448 | 0 | 15900.0001 | 0 | 5352.7778 | 0 | 476997.226 | 0 | 41841.667 | 0 | 69666.6672 | 0 | 45669.4448 | 0 | 15900.0001 | 0 | 5347.2223 | 0 | 476502.7816 | 0 | 48336.1115 | 0 | 65497.2227 | 0 | 43947.2226 | 0 | 15900.0001 | 0
intLgt | extLgt |  | 4 | 5 | 1 | 0 |  | Lighting, Interior & Exterior | #VALUE! | 0.018428 | 0 | 0.015637 | 0 | 0.030136 | 0 | 0.011693 | 0 | 0.01469 | 0 | 0.0087283 |  | Sum of B.extLgt | 22 |  | Sum of B.extLgt | 1927.7778 | 0 | 73427.7784 | 0 | 8225.0001 | 0 | 5833.3334 | 0 | 10308.3334 | 0 | 6336.1112 | 0 | 1941.6667 | 0 | 73952.7784 | 0 | 8230.5556 | 0 | 5850 | 0 | 10313.889 | 0 | 6341.6667 | 0 | 1911.1111 | 0 | 72950.0006 | 0 | 8230.5556 | 0 | 5819.4445 | 0 | 10313.889 | 0 | 6341.6667 | 0 | 1927.7778 | 0 | 73786.1117 | 0 | 8275.0001 | 0 | 5850 | 0 | 10297.2223 | 0 | 6330.5556 | 0 | 1938.8889 | 0 | 74002.7784 | 0 | 8247.2223 | 0 | 5850 | 0 | 10300.0001 | 0 | 6333.3334 | 0
intEqp | extEqp.rev | refrg | 6 | 16 | 14 | 0 |  | Plugs, Refrigeration, Other | #VALUE! | 0.024385 | 0 | 0.092404 | 0 | 0.021858 | 0 | 0.044578 | 7.9207 | 0.028272 | 11.8401 | 0.037219 |  | Sum of B.intEqp | 23 |  | Sum of B.intEqp | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 105516.6675 | 399495.4379 | 117269.4454 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 105516.6675 | 399495.4379 | 117269.4454 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 105516.6675 | 399495.4379 | 117269.4454 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 105516.6675 | 399495.4379 | 117269.4454 | 0 | 13416.6668 | 0 | 4076777.8104 | 0 | 53972.2227 | 0 | 312394.4469 | 342190.4148 | 105516.6675 | 399495.4379 | 117269.4454 | 0
swh |  |  | 13 | 1 | 1 | 0 |  | Service Water Heating (SWH) | #VALUE! | 0.011819 | 0 | 0 | 24.7537 | 0 | 1.1222 | 0.00097051 | 2.722 | 0 | 24.1588 | 0.031286 |  | Sum of B.extEqp | 24 |  | Sum of B.extEqp | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334363.8916 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4738.8889 | 0 | 0 | 0 | 0 | 0
total |  |  | 15 | 1 | 1 | 0 |  | Total | #VALUE! | 0.083929 | 0 | 0.16005 | 27.6261 | 0.106 | 1.3413 | 0.10982 | 12.9786 | 0.093294 | 36.1171 | 0.11006 |  | Sum of B.fans | 25 |  | Sum of B.fans | 5150 | 0 | 563352.7823 | 0 | 32805.5558 | 0 | 72361.1117 | 0 | 68255.5561 | 0 | 33194.4447 | 0 | 4947.2223 | 0 | 624638.8939 | 0 | 35716.667 | 0 | 66327.7783 | 0 | 67102.7783 | 0 | 27047.2224 | 0 | 5855.5556 | 0 | 734255.5614 | 0 | 39683.3337 | 0 | 74288.8895 | 0 | 77166.6673 | 0 | 30013.8891 | 0 | 4636.1111 | 0 | 599333.3381 | 0 | 36508.3336 | 0 | 71430.5561 | 0 | 62716.6672 | 0 | 25008.3335 | 0 | 4625 | 0 | 603352.7826 | 0 | 35841.667 | 0 | 68033.3339 | 0 | 61594.4449 | 0 | 23527.778 | 0
[6 empty] | 0 |  | ASHRAE 90.1-2022 | [13 empty] | Sum of B.pumps | 26 |  | Sum of B.pumps | 0 | 0 | 179419.4459 | 0 | 0 | 0 | 122.2222 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 127863.8899 | 0 | 0 | 0 | 794.4445 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 135425.0011 | 0 | 0 | 0 | 311.1111 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 108847.2231 | 0 | 0 | 0 | 836.1111 | 0 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 85550.0007 | 0 | 0 | 0 | 1427.7778 | 0 | 72.2222 | 0 | 0 | 0
shift: | 17 |  | 19 | 28 | 18 | 0 |  | Heating, Humidification | #VALUE! | 0.00014136 | 0 | 0.0018864 | 2.5718 | 0 | 0.12469 | 0 | 2.4271 | 0.00046294 | 0.0011236 | 0 |  | Sum of B.heatRej | 27 |  | Sum of B.heatRej | 0 | 0 | 431069.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281800.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263938.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198902.7794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142841.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20 | 27 | 18 | 0 |  | Cooling | #VALUE! | 0.017771 | 0 | 0.032548 | 0 | 0.034381 | 0 | 0.037131 | 0 | 0.029587 | 0 | 0.019391 |  | Sum of B.humid | 28 |  | Sum of B.humid | 0 | 0 | 94055.5563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266638.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496616.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350380.5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401177.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 26 | 29 | 0 |  | Fans, Pumps, Heat Recovery | #VALUE! | 0.0093602 | 0 | 0.015179 | 0 | 0.013286 | 0 | 0.011821 | 0 | 0.015816 | 0 | 0.009838 |  | Sum of B.heatRec | 29 |  | Sum of B.heatRec | 0 | 0 | 14058.3334 | 0 | 0 | 0 | 14944.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10869.4445 | 0 | 0 | 0 | 11227.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12130.5557 | 0 | 0 | 0 | 13150.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10480.5556 | 0 | 0 | 0 | 12419.4445 | 0 | 0 | 0 | 0 | 0
|  |  | 21 | 22 | 18 | 0 |  | Lighting, Interior & Exterior | #VALUE! | 0.013303 | 0 | 0.011011 | 0 | 0.022197 | 0 | 0.010059 | 0 | 0.012477 | 0 | 0.0065902 |  | Sum of B.swh | 30 |  | Sum of B.swh | 6505.5556 | 0 | 0 | 611228.3043 | 0 | 83000.3452 | 7177.7778 | 117595.6701 | 0 | 690683.8135 | 97408.3341 | 0 | 6697.2223 | 0 | 0 | 670372.0926 | 0 | 86564.1376 | 7177.7778 | 130419.6357 | 0 | 747770.8387 | 107886.112 | 0 | 6644.4445 | 0 | 0 | 655225.9751 | 0 | 85625.7986 | 7177.7778 | 127225.492 | 0 | 733136.5423 | 105172.2231 | 0 | 6844.4445 | 0 | 0 | 716985.7386 | 0 | 89360.1981 | 7177.7778 | 139651.3745 | 0 | 792545.7194 | 116119.4454 | 0 | 6969.4445 | 0 | 0 | 756519.1907 | 0 | 91701.3064 | 7180.5556 | 147319.215 | 0 | 830581.6204 | 123055.5565 | 0
|  |  | 23 | 33 | 31 | 0 |  | Plugs, Refrigeration, Other | #VALUE! | 0.024385 | 0 | 0.088473 | 0 | 0.021858 | 0 | 0.044578 | 7.9207 | 0.024424 | 11.8401 | 0.034756 |  | Sum of B.refrg | 31 |  | Sum of B.refrg | 0 | 0 | 0 | 0 | 0 | 0 | 12555.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12505.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12413.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12502.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12480.5557 | 0 | 0 | 0 | 0 | 0
|  |  | 30 | 18 | 18 | 0 |  | Service Water Heating (SWH) | #VALUE! | 0.011824 | 0 | 0 | 24.7541 | 0 | 1.1222 | 0.00097051 | 2.722 | 0 | 20.4702 | 0.028869 |  | Sum of B.total | 32 |  | Sum of B.total | 42247.2226 | 0 | 7433841.7261 | 674732.0514 | 226480.5574 | 92222.6058 | 773305.5617 | 564643.0929 | 357569.4473 | 1090217.1641 | 335536.1138 | 4748.5638 | 39280.5559 | 1516.5074 | 7021900.0562 | 1051972.7433 | 184775.0015 | 235835.8558 | 645380.5607 | 878550.6449 | 331169.4471 | 1151408.2374 | 314413.8914 | 74327.8186 | 39869.4448 | 217.9979 | 7421033.3927 | 983417.131 | 197544.446 | 133755.952 | 638080.5607 | 606972.6055 | 334200.0027 | 1132783.631 | 320575.0026 | 23212.0413 | 39002.7781 | 2549.6281 | 6788922.2765 | 1407716.943 | 172250.0014 | 411352.6301 | 595663.8937 | 941068.6621 | 321425.0026 | 1206277.3705 | 309336.1136 | 163356.2806 | 39330.5559 | 11440.1526 | 6592894.4972 | 1953754.3858 | 163752.7791 | 577514.4494 | 549280.5599 | 1236351.6077 | 323794.447 | 1265677.0694 | 304538.8913 | 273312.5447
|  |  | 32 | 18 | 18 | 0 |  | Total | #VALUE! | 0.076785 | 0 | 0.1491 | 27.3259 | 0.091722 | 1.2469 | 0.10456 | 13.0698 | 0.082767 | 32.3113 | 0.099445 |  | Sum of B.extEqp.rev | 33 |  | Sum of B.extEqp.rev | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334363.8916 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4741.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334358.336 | 0 | 0 | 0 | 4738.8889 | 0 | 0 | 0 | 0 | 0
[8 empty] | Total Savings | 0.71439 | 0.0071439 | 0 | 0.010955 | 0.30018 | 0.014282 | 0.094322 | 0.0052642 | -0.091267 | 0.010527 | 3.8058 | 0.010617 |  | Sum of B.sum | 34 |  | Sum of B.sum | 41441.3892 | 0 | 7276475.0582 | 674732.0514 | 204771.3905 | 92222.6058 | 708270.839 | 564643.0929 | 328625.2804 | 1090217.1641 | 313893.6136 | 4748.5638 | 38500.8336 | 1516.5074 | 6869632.2772 | 1051972.7433 | 163769.168 | 235835.8558 | 582453.0602 | 878550.6449 | 303163.058 | 1151408.2374 | 293472.5023 | 74327.8186 | 38931.667 | 217.9979 | 7237892.8357 | 983417.131 | 172279.7236 | 133755.952 | 562394.1712 | 606972.6055 | 300515.2802 | 1132783.631 | 295387.7801 | 23212.0413 | 38326.667 | 2549.6281 | 6656886.9977 | 1407716.943 | 154035.279 | 411352.6301 | 541097.7821 | 941068.6621 | 297140.0024 | 1206277.3705 | 291177.2246 | 163356.2806 | 38679.4448 | 11440.1526 | 6465744.7739 | 1953754.3858 | 146211.9456 | 577514.4494 | 496733.6151 | 1236351.6077 | 300408.058 | 1265677.0694 | 287051.9467 | 273312.5447
| Moving to the ANSI/ASHRAE/IES Standard 90.1-2022 version from the Base Code (90.1-2019) is cost-effective for all building types and climate zones in the State of US National. Table 1 shows the statewide economic impact of upgrading to 90.1-2022 in terms of the annual energy cost savings in dollars per square foot, the additional cost per square foot required by the upgrade, and the simple payback period in years. Figure 1 includes annual energy cost savings, first cost for the upgrade, and net annualized LCC savings per square foot for Scenario 2. Average values are weighted averages for all building types considered in all climate zones in the state, based on weightings shown in Table 6. |  |  |  |  | B |  | Table 12.B. Annual Energy Usage for Buildings in the State of US National in Climate Zone 3A
[8 empty] | Energy | Small Office |  | Large Office |  | Stand-Alone Retail |  | Primary School |  | Small Hotel |  | Mid-Rise Apartment
[8 empty] | End-Use | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas
[5 empty] | Climate zone: | 3A |  |  | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/
[9 empty] | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr
|  |  | End Uses |  |  | ColOfst |  | ASHRAE 90.1-2019
|  |  | 2 | 11 | 1 | 12 |  | Heating, Humidification | 0.851 | 0.0031403 | 0.0031557 | 0.0053531 | 16.9376 | 0 | 2.5218 | 0 | 10.4016 | 0.0036084 | 0.85116 | 0
|  |  | 3 | 10 | 1 | 12 |  | Cooling | 0 | 0.010405 | 0 | 0.021978 | 0 | 0.021916 | 0 | 0.022924 | 0 | 0.022068 | 0 | 0.013112
|  |  | 8 | 9 | 12 | 12 |  | Fans, Pumps, Heat Recovery | 0 | 0.0093855 | 0 | 0.015885 | 0 | 0.014285 | 0 | 0.010649 | 0 | 0.016215 | 0 | 0.00845
|  |  | 4 | 5 | 1 | 12 |  | Lighting, Interior & Exterior | 0 | 0.018529 | 0 | 0.015683 | 0 | 0.03034 | 0 | 0.011814 | 0 | 0.014741 | 0 | 0.0087299
|  |  | 6 | 16 | 14 | 12 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.092404 | 0 | 0.021858 | 0 | 0.044571 | 7.9207 | 0.028272 | 11.8401 | 0.037219
|  |  | 13 | 1 | 1 | 12 |  | Service Water Heating (SWH) | 0 | 0.012167 | 0 | 0 | 27.1486 | 0 | 1.1704 | 0.00097051 | 3.0186 | 0 | 26.158 | 0.034743
|  |  | 15 | 1 | 1 | 12 |  | Total | 0.851 | 0.078012 | 0.0031557 | 0.1513 | 44.0862 | 0.088399 | 3.6923 | 0.090928 | 21.3409 | 0.084904 | 38.8492 | 0.10225
[6 empty] | 12 |  | ASHRAE 90.1-2022
|  |  | 19 | 28 | 18 | 12 |  | Heating, Humidification | 0.86306 | 0.0030292 | 0.0030416 | 0.0053479 | 15.4544 | 0 | 2.0183 | 0 | 9.3963 | 0.0033518 | 0.12276 | 0
|  |  | 20 | 27 | 18 | 12 |  | Cooling | 0 | 0.0094461 | 0 | 0.020662 | 0 | 0.018723 | 0 | 0.02097 | 0 | 0.020409 | 0 | 0.011846
|  |  | 25 | 26 | 29 | 12 |  | Fans, Pumps, Heat Recovery | 0 | 0.0089917 | 0 | 0.015311 | 0 | 0.014465 | 0 | 0.010594 | 0 | 0.015549 | 0 | 0.0080161
|  |  | 21 | 22 | 18 | 12 |  | Lighting, Interior & Exterior | 0 | 0.013369 | 0 | 0.011042 | 0 | 0.019786 | 0 | 0.010157 | 0 | 0.012922 | 0 | 0.0065919
|  |  | 23 | 33 | 31 | 12 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.088473 | 0 | 0.021858 | 0 | 0.044571 | 7.9207 | 0.024424 | 11.8401 | 0.034756
|  |  | 30 | 18 | 18 | 12 |  | Service Water Heating (SWH) | 0 | 0.012172 | 0 | 0 | 27.1494 | 0 | 1.1704 | 0.00097051 | 3.0188 | 0 | 22.1621 | 0.031975
|  |  | 32 | 18 | 18 | 12 |  | Total | 0.86306 | 0.071393 | 0.0030416 | 0.14084 | 42.6038 | 0.074832 | 3.1887 | 0.087262 | 20.3359 | 0.076656 | 34.1249 | 0.093185
[8 empty] | Total Savings | -0.012059 | 0.0066188 | 0.00011406 | 0.010467 | 1.4825 | 0.013567 | 0.50352 | 0.0036661 | 1.005 | 0.0082481 | 4.7243 | 0.0090699
[6 empty] | C |  | Table 12.C. Annual Energy Usage for Buildings in the State of US National in Climate Zone 3B
[8 empty] | Energy | Small Office |  | Large Office |  | Stand-Alone Retail |  | Primary School |  | Small Hotel |  | Mid-Rise Apartment
[8 empty] | End-Use | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas
[5 empty] | Climate zone: | 3B |  |  | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/
[9 empty] | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr
|  |  | End Uses |  |  | ColOfst |  | ASHRAE 90.1-2019
|  |  | 2 | 11 | 1 | 24 |  | Heating, Humidification | 13.1182 | 0.0012773 | 0.00041822 | 0.0099605 | 15.0479 | 0 | 0.96449 | 0 | 3.6353 | 0.0014435 | 0.37867 | 0
|  |  | 3 | 10 | 1 | 24 |  | Cooling | 0 | 0.011748 | 0 | 0.023017 | 0 | 0.021886 | 0 | 0.020988 | 0 | 0.022431 | 0 | 0.015018
|  |  | 8 | 9 | 12 | 24 |  | Fans, Pumps, Heat Recovery | 0 | 0.011092 | 0 | 0.018019 | 0 | 0.01575 | 0 | 0.010091 | 0 | 0.018609 | 0 | 0.0093202
|  |  | 4 | 5 | 1 | 24 |  | Lighting, Interior & Exterior | 0 | 0.018478 | 0 | 0.015636 | 0 | 0.031173 | 0 | 0.011953 | 0 | 0.014757 | 0 | 0.0087299
|  |  | 6 | 16 | 14 | 24 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.092404 | 0 | 0.021858 | 0 | 0.044558 | 7.9207 | 0.028272 | 11.8401 | 0.037219
|  |  | 13 | 1 | 1 | 24 |  | Service Water Heating (SWH) | 0 | 0.012076 | 0 | 0 | 26.5356 | 0 | 1.1577 | 0.00097051 | 2.9449 | 0 | 25.6451 | 0.033853
|  |  | 15 | 1 | 1 | 24 |  | Total | 13.1182 | 0.079057 | 0.00041822 | 0.15904 | 41.5835 | 0.090667 | 2.1222 | 0.08856 | 14.5009 | 0.085512 | 37.8638 | 0.10414
[6 empty] | 24 |  | ASHRAE 90.1-2022
|  |  | 19 | 28 | 18 | 24 |  | Heating, Humidification | 13.5092 | 0.0012773 | 0.00043723 | 0.0099605 | 13.2914 | 0 | 0.65077 | 0 | 3.184 | 0.0013258 | 0.0044946 | 0
|  |  | 20 | 27 | 18 | 24 |  | Cooling | 0 | 0.010688 | 0 | 0.021655 | 0 | 0.019125 | 0 | 0.019885 | 0 | 0.021199 | 0 | 0.013597
|  |  | 25 | 26 | 29 | 24 |  | Fans, Pumps, Heat Recovery | 0 | 0.010643 | 0 | 0.017443 | 0 | 0.016071 | 0 | 0.010087 | 0 | 0.017879 | 0 | 0.0088954
|  |  | 21 | 22 | 18 | 24 |  | Lighting, Interior & Exterior | 0 | 0.013394 | 0 | 0.01131 | 0 | 0.022949 | 0 | 0.010774 | 0 | 0.01253 | 0 | 0.0065919
|  |  | 23 | 33 | 31 | 24 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.088473 | 0 | 0.021858 | 0 | 0.044558 | 7.9207 | 0.024424 | 11.8401 | 0.034756
|  |  | 30 | 18 | 18 | 24 |  | Service Water Heating (SWH) | 0 | 0.012076 | 0 | 0 | 26.536 | 0 | 1.1577 | 0.00097051 | 2.9449 | 0 | 21.7284 | 0.03117
|  |  | 32 | 18 | 18 | 24 |  | Total | 13.5092 | 0.072464 | 0.00043723 | 0.14884 | 39.8274 | 0.080003 | 1.8085 | 0.086275 | 14.0496 | 0.077358 | 33.5729 | 0.095011
[8 empty] | Total Savings | -0.39105 | 0.0065936 | -1.901e-05 | 0.010196 | 1.7561 | 0.010664 | 0.31372 | 0.0022854 | 0.45129 | 0.0081548 | 4.2909 | 0.0091292
[6 empty] | D |  | Table 12.D. Annual Energy Usage for Buildings in the State of US National in Climate Zone 4A
[8 empty] | Energy | Small Office |  | Large Office |  | Stand-Alone Retail |  | Primary School |  | Small Hotel |  | Mid-Rise Apartment
[8 empty] | End-Use | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas
[5 empty] | Climate zone: | 4A |  |  | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/
[9 empty] | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr
|  |  | End Uses |  |  | ColOfst |  | ASHRAE 90.1-2019
|  |  | 2 | 11 | 1 | 36 |  | Heating, Humidification | 4.1051 | 0.0060735 | 0.0060262 | 0.0070349 | 34.5689 | 0 | 5.7436 | 0 | 13.0604 | 0.0082179 | 2.0105 | 0
|  |  | 3 | 10 | 1 | 36 |  | Cooling | 0 | 0.0078002 | 0 | 0.01615 | 0 | 0.014703 | 0 | 0.014656 | 0 | 0.016973 | 0 | 0.009852
|  |  | 8 | 9 | 12 | 36 |  | Fans, Pumps, Heat Recovery | 0 | 0.0089462 | 0 | 0.014901 | 0 | 0.014883 | 0 | 0.011522 | 0 | 0.015736 | 0 | 0.007919
|  |  | 4 | 5 | 1 | 36 |  | Lighting, Interior & Exterior | 0 | 0.018337 | 0 | 0.015685 | 0 | 0.031164 | 0 | 0.011859 | 0 | 0.014637 | 0 | 0.0087258
|  |  | 6 | 16 | 14 | 36 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.092404 | 0 | 0.021858 | 0 | 0.04457 | 7.9207 | 0.028272 | 11.8401 | 0.037219
|  |  | 13 | 1 | 1 | 36 |  | Service Water Heating (SWH) | 0 | 0.01244 | 0 | 0 | 29.036 | 0 | 1.2082 | 0.00097051 | 3.2332 | 0 | 27.7261 | 0.037475
|  |  | 15 | 1 | 1 | 36 |  | Total | 4.1051 | 0.077982 | 0.0060262 | 0.14617 | 63.6049 | 0.082609 | 6.9519 | 0.083578 | 24.2143 | 0.083836 | 41.5766 | 0.10119
[6 empty] | 36 |  | ASHRAE 90.1-2022
|  |  | 19 | 28 | 18 | 36 |  | Heating, Humidification | 4.2188 | 0.0053011 | 0.0051137 | 0.0070275 | 27.9739 | 0 | 4.3537 | 0 | 10.6298 | 0.0074797 | 0.42193 | 0
|  |  | 20 | 27 | 18 | 36 |  | Cooling | 0 | 0.0071035 | 0 | 0.015169 | 0 | 0.012819 | 0 | 0.013239 | 0 | 0.015008 | 0 | 0.0085084
|  |  | 25 | 26 | 29 | 36 |  | Fans, Pumps, Heat Recovery | 0 | 0.0084262 | 0 | 0.014447 | 0 | 0.014785 | 0 | 0.011549 | 0 | 0.014534 | 0 | 0.0074119
|  |  | 21 | 22 | 18 | 36 |  | Lighting, Interior & Exterior | 0 | 0.013233 | 0 | 0.011047 | 0 | 0.020297 | 0 | 0.010211 | 0 | 0.012955 | 0 | 0.0065886
|  |  | 23 | 33 | 31 | 36 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.088473 | 0 | 0.021858 | 0 | 0.04457 | 7.9207 | 0.024424 | 11.8401 | 0.034756
|  |  | 30 | 18 | 18 | 36 |  | Service Water Heating (SWH) | 0 | 0.01244 | 0 | 0 | 29.0372 | 0 | 1.2082 | 0.00097051 | 3.2325 | 0 | 23.4891 | 0.034415
|  |  | 32 | 18 | 18 | 36 |  | Total | 4.2188 | 0.070888 | 0.0051137 | 0.13616 | 57.0111 | 0.069759 | 5.5619 | 0.08054 | 21.783 | 0.0744 | 35.7511 | 0.09168
[8 empty] | Total Savings | -0.1137 | 0.0070934 | 0.00091248 | 0.010011 | 6.5939 | 0.012849 | 1.39 | 0.0030381 | 2.4313 | 0.0094356 | 5.8255 | 0.0095112
[6 empty] | E |  | Table 12.E. Annual Energy Usage for Buildings in the State of US National in Climate Zone 5A
[8 empty] | Energy | Small Office |  | Large Office |  | Stand-Alone Retail |  | Primary School |  | Small Hotel |  | Mid-Rise Apartment
[8 empty] | End-Use | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas | Electric | Gas
[5 empty] | Climate zone: | 5A |  |  | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/ | kWh/ | therms/
[9 empty] | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr | ft2·yr
|  |  | End Uses |  |  | ColOfst |  | ASHRAE 90.1-2019
|  |  | 2 | 11 | 1 | 48 |  | Heating, Humidification | 35.6353 | 0.010057 | 0.026386 | 0.0080564 | 59.6266 | 0 | 8.6836 | 0 | 21.8319 | 0.013759 | 3.1776 | 0
|  |  | 3 | 10 | 1 | 48 |  | Cooling | 0 | 0.0046498 | 0 | 0.01178 | 0 | 0.0082337 | 0 | 0.0086782 | 0 | 0.012776 | 0 | 0.0061844
|  |  | 8 | 9 | 12 | 48 |  | Fans, Pumps, Heat Recovery | 0 | 0.0089816 | 0 | 0.014455 | 0 | 0.016453 | 0 | 0.011063 | 0 | 0.015546 | 0 | 0.0074497
|  |  | 4 | 5 | 1 | 48 |  | Lighting, Interior & Exterior | 0 | 0.018357 | 0 | 0.01568 | 0 | 0.031125 | 0 | 0.011737 | 0 | 0.014626 | 0 | 0.0087266
|  |  | 6 | 16 | 14 | 48 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.092404 | 0 | 0.021858 | 0 | 0.044567 | 7.9207 | 0.028272 | 11.8401 | 0.037219
|  |  | 13 | 1 | 1 | 48 |  | Service Water Heating (SWH) | 0 | 0.012667 | 0 | 0 | 30.6367 | 0 | 1.24 | 0.00097088 | 3.4104 | 0 | 29.0567 | 0.039767
|  |  | 15 | 1 | 1 | 48 |  | Total | 35.6353 | 0.079098 | 0.026386 | 0.14238 | 90.2633 | 0.077669 | 9.9236 | 0.077016 | 33.1631 | 0.084979 | 44.0744 | 0.099347
[6 empty] | 48 |  | ASHRAE 90.1-2022
|  |  | 19 | 28 | 18 | 48 |  | Heating, Humidification | 29.6903 | 0.0087493 | 0.022945 | 0.0080463 | 48.4868 | 0 | 6.5687 | 0 | 17.2872 | 0.012665 | 1.0551 | 0
|  |  | 20 | 27 | 18 | 48 |  | Cooling | 0 | 0.0040339 | 0 | 0.010644 | 0 | 0.0070288 | 0 | 0.0080123 | 0 | 0.011029 | 0 | 0.0054689
|  |  | 25 | 26 | 29 | 48 |  | Fans, Pumps, Heat Recovery | 0 | 0.008406 | 0 | 0.014027 | 0 | 0.014515 | 0 | 0.011071 | 0 | 0.014274 | 0 | 0.0069731
|  |  | 21 | 22 | 18 | 48 |  | Lighting, Interior & Exterior | 0 | 0.013243 | 0 | 0.011041 | 0 | 0.022916 | 0 | 0.0096469 | 0 | 0.012557 | 0 | 0.0065894
|  |  | 23 | 33 | 31 | 48 |  | Plugs, Refrigeration, Other | 0 | 0.024385 | 0 | 0.088473 | 0 | 0.021858 | 0 | 0.044567 | 7.9207 | 0.024424 | 11.8401 | 0.034756
|  |  | 30 | 18 | 18 | 48 |  | Service Water Heating (SWH) | 0 | 0.012667 | 0 | 0 | 30.6382 | 0 | 1.2399 | 0.00097088 | 3.41 | 0 | 24.6164 | 0.036471
|  |  | 32 | 18 | 18 | 48 |  | Total | 29.6903 | 0.071484 | 0.022945 | 0.13223 | 79.125 | 0.066318 | 7.8086 | 0.074268 | 28.6179 | 0.074949 | 37.5115 | 0.090258
[8 empty] | Total Savings | 5.945 | 0.0076134 | 0.0034408 | 0.010145 | 11.1383 | 0.011351 | 2.1151 | 0.0027474 | 4.5451 | 0.01003 | 6.5629 | 0.0090888

## _Summary (hidden)
Worksheet | StateReport | StateReport | StateReport | StateReport | State Inputs | State Inputs | State Inputs | State Inputs | State Inputs | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables | Result Tables
Range | $G$51 | $G$52 | $G$63 | $G$64 | $G$8 | $H$8 | $I$8 | $J$8 | $K$8 | $I$20 | $I$21 | $I$22 | $I$23 | $I$24 | $I$30 | $I$31 | $I$32 | $I$33 | $I$34
Item Num | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Item Count | 19
State | Highlights |  |  |  | State Climate Zones |  |  |  |  | LCC Savings Scenario 1 |  |  |  |  | LCC Savings Scenario 2
| Annual Energy Cost Savings | Added Construction Cost | LCC Savings Scenario 1 | LCC Savings Scenario 2 | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 5 | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ1 | CZ2 | CZ3 | CZ4 | CZ5
Alabama | 0.145 | -0.99358 | 3.3789 | 2.5645 | 2A | 3A | 0 | 0 | 0 | 6.0246 | 2.9531 | 0 | 0 | 0 | 4.2303 | 2.2964 | 0 | 0 | 0
Arkansas | 0.11588 | -0.16067 | 1.946 | 1.5604 | 3A | 4A | 0 | 0 | 0 | 2.2772 | 1.3389 | 0 | 0 | 0 | 1.7077 | 1.2904 | 0 | 0 | 0
Colorado | 0.10659 | 0.29316 | 1.6302 | 1.4354 | 4B | 5B | 6B | 7 | 0 | 2.0293 | 1.7172 | 0.89439 | 0.37119 | 0 | 1.9105 | 1.498 | 0.89839 | 0.53287 | 0
Connecticut | 0.19295 | -1.1713 | 4.5333 | 3.4794 | 5A | 0 | 0 | 0 | 0 | 4.5333 | 0 | 0 | 0 | 0 | 3.4794 | 0 | 0 | 0 | 0
Delaware | 0.14373 | -3.4191 | 5.9547 | 4.0478 | 4A | 0 | 0 | 0 | 0 | 5.9547 | 0 | 0 | 0 | 0 | 4.0478 | 0 | 0 | 0 | 0
District of Columbia | 0.053714 | -23.1645 | 24.3529 | 13.9202 | 4A | 0 | 0 | 0 | 0 | 24.3529 | 0 | 0 | 0 | 0 | 13.9202 | 0 | 0 | 0 | 0
Georgia | 0.12776 | -0.20713 | 2.3993 | 1.9543 | 2A | 3A | 4A | 0 | 0 | 3.2322 | 2.334 | 2.1393 | 0 | 0 | 2.6656 | 1.8818 | 1.9658 | 0 | 0
Iowa | 0.13115 | -1.2545 | 3.4936 | 2.5371 | 5A | 6A | 0 | 0 | 0 | 3.7346 | 1.9083 | 0 | 0 | 0 | 2.666 | 1.6888 | 0 | 0 | 0
Kentucky | 0.13949 | -0.019491 | 2.3649 | 1.9525 | 4A | 0 | 0 | 0 | 0 | 2.3649 | 0 | 0 | 0 | 0 | 1.9525 | 0 | 0 | 0 | 0
Massachusetts | 0.15073 | -2.9 | 5.6314 | 3.9417 | 5A | 0 | 0 | 0 | 0 | 5.6314 | 0 | 0 | 0 | 0 | 3.9417 | 0 | 0 | 0 | 0
Montana | 0.15082 | 0.48046 | 1.7037 | 1.4855 | 6B | 0 | 0 | 0 | 0 | 1.7037 | 0 | 0 | 0 | 0 | 1.4855 | 0 | 0 | 0 | 0
Nebraska | 0.12975 | -0.75994 | 2.8021 | 2.1109 | 5A | 0 | 0 | 0 | 0 | 2.8021 | 0 | 0 | 0 | 0 | 2.1109 | 0 | 0 | 0 | 0
New Jersey | 0.14315 | 0.074569 | 2.502 | 2.1123 | 4A | 5A | 0 | 0 | 0 | 2.904 | 1.6939 | 0 | 0 | 0 | 2.3321 | 1.6706 | 0 | 0 | 0
New York | 0.15385 | 0.59702 | 2.1162 | 1.9234 | 4A | 5A | 6A | 0 | 0 | 1.4178 | 3.247 | 3.3841 | 0 | 0 | 1.4331 | 2.7569 | 2.6897 | 0 | 0
North Carolina | 0.12491 | -1.2307 | 3.319 | 2.3679 | 3A | 4A | 5A | 0 | 0 | 4.1817 | 1.7111 | 2.1603 | 0 | 0 | 2.8342 | 1.4066 | 1.7431 | 0 | 0
Oklahoma | 0.11852 | -0.97019 | 2.7907 | 2.0668 | 3A | 4B | 0 | 0 | 0 | 2.7983 | 1.8941 | 0 | 0 | 0 | 2.0721 | 1.4539 | 0 | 0 | 0
Rhode Island | 0.1564 | -2.7314 | 5.3788 | 3.7382 | 5A | 0 | 0 | 0 | 0 | 5.3788 | 0 | 0 | 0 | 0 | 3.7382 | 0 | 0 | 0 | 0
South Carolina | 0.12975 | -0.97251 | 3.1106 | 2.3552 | 3A | 0 | 0 | 0 | 0 | 3.1106 | 0 | 0 | 0 | 0 | 2.3552 | 0 | 0 | 0 | 0
Texas | 0.10532 | -0.24034 | 1.9704 | 1.5859 | 2A | 2B | 3A | 3B | 4B | 2.5225 | 1.8665 | 2.1026 | 2.0172 | 1.9063 | 2.1421 | 1.5167 | 1.6695 | 1.5948 | 1.5667
US National | 0.13788 | 0.061542 | 2.3176 | 1.9495 | 2A | 3A | 3B | 4A | 5A | 3.1816 | 2.5978 | 2.5099 | 1.4831 | 2.1593 | 2.584 | 2.0736 | 1.9667 | 1.4019 | 1.8904
Utah | 0.10855 | 0.12834 | 1.9365 | 1.6581 | 3B | 5B | 6B | 0 | 0 | 2.7372 | 2.0068 | 0.74557 | 0 | 0 | 2.2295 | 1.7085 | 0.80557 | 0 | 0
Virginia | 0.087472 | -3.4406 | 5.0328 | 3.347 | 4A | 0 | 0 | 0 | 0 | 5.0328 | 0 | 0 | 0 | 0 | 3.347 | 0 | 0 | 0 | 0
Wisconsin | 0.13906 | -3.1085 | 5.2528 | 3.5371 | 6A | 7 | 0 | 0 | 0 | 5.3349 | 2.4286 | 0 | 0 | 0 | 3.5815 | 2.0105 | 0 | 0 | 0
California | 0.14385 | -0.42253 | 3.054 | 2.4514 | 2B | 3B | 3C | 4B | 5B | 3.9824 | 3.0793 | 2.962 | 2.581 | 2.6295 | 2.9483 | 2.4788 | 2.3411 | 2.3224 | 2.4503
Arizona | 0.12003 | -1.6785 | 3.6485 | 2.6118 | 2B | 3B | 4B | 5B | 0 | 3.8058 | 2.3759 | 2.0182 | 2.1087 | 0 | 2.708 | 1.7247 | 1.6444 | 1.8546 | 0
Florida | 0.15491 | -0.75532 | 3.5142 | 2.7611 | 1A | 2A | 0 | 0 | 0 | 6.3899 | 2.9028 | 0 | 0 | 0 | 4.5699 | 2.3765 | 0 | 0 | 0
Hawaii | 0.59257 | -0.00014919 | 11.4311 | 9.7124 | 1A | 0 | 0 | 0 | 0 | 11.4311 | 0 | 0 | 0 | 0 | 9.7124 | 0 | 0 | 0 | 0
Idaho | 0.10025 | -0.0063169 | 1.8373 | 1.5321 | 5B | 6B | 0 | 0 | 0 | 2.046 | 0.76274 | 0 | 0 | 0 | 1.673 | 0.80649 | 0 | 0 | 0
Illinois | 0.11013 | 0.64096 | 0.97255 | 0.94546 | 4A | 5A | 0 | 0 | 0 | 0.87239 | 0.98029 | 0 | 0 | 0 | 0.92821 | 0.94679 | 0 | 0 | 0
Indiana | 0.14388 | 0.57874 | 1.8885 | 1.7166 | 4A | 5A | 0 | 0 | 0 | 2.3785 | 1.8028 | 0 | 0 | 0 | 1.951 | 1.6756 | 0 | 0 | 0
Kansas | 0.14172 | -0.62599 | 3.0918 | 2.4283 | 4A | 5A | 0 | 0 | 0 | 3.1316 | 1.8291 | 0 | 0 | 0 | 2.4542 | 1.6059 | 0 | 0 | 0
Louisiana | 0.13708 | -1.517 | 3.7296 | 2.704 | 2A | 3A | 0 | 0 | 0 | 3.9764 | 2.451 | 0 | 0 | 0 | 2.8771 | 1.8075 | 0 | 0 | 0
Maine | 0.17467 | -0.55533 | 3.4581 | 2.7178 | 6A | 7 | 0 | 0 | 0 | 3.4654 | 3.1591 | 0 | 0 | 0 | 2.7186 | 2.6843 | 0 | 0 | 0
Maryland | 0.098398 | -4.5004 | 6.4201 | 4.1832 | 4A | 5A | 0 | 0 | 0 | 6.4242 | 0.90718 | 0 | 0 | 0 | 4.1852 | 1.3699 | 0 | 0 | 0
Michigan | 0.17164 | 0.038996 | 2.407 | 2.0477 | 5A | 6A | 7 | 0 | 0 | 2.4276 | 2.1904 | 0 | 0 | 0 | 2.0656 | 1.8596 | 0 | 0 | 0
Minnesota | 0.11283 | -4.1332 | 6.2988 | 3.9855 | 6A | 7 | 0 | 0 | 0 | 6.2988 | 0 | 0 | 0 | 0 | 3.9855 | 0 | 0 | 0 | 0
Mississippi | 0.14401 | -0.41858 | 2.8123 | 2.2447 | 2A | 3A | 0 | 0 | 0 | 3.4037 | 2.6789 | 0 | 0 | 0 | 2.7993 | 2.1197 | 0 | 0 | 0
Missouri | 0.15173 | -1.786 | 3.9755 | 2.8122 | 4A | 5A | 0 | 0 | 0 | 4.0395 | 1.9121 | 0 | 0 | 0 | 2.8492 | 1.6181 | 0 | 0 | 0
Nevada | 0.10283 | -1.2539 | 2.8153 | 2.0659 | 3B | 5B | 0 | 0 | 0 | 3.011 | 1.8663 | 0 | 0 | 0 | 2.1722 | 1.5499 | 0 | 0 | 0
New Hampshire | 0.20731 | -0.10545 | 3.588 | 2.9555 | 5A | 6A | 0 | 0 | 0 | 3.7335 | 3.3255 | 0 | 0 | 0 | 3.0928 | 2.708 | 0 | 0 | 0
New Mexico | 0.13735 | 0.19437 | 2.3085 | 2.0178 | 3B | 4B | 5B | 0 | 0 | 2.8315 | 2.0995 | 0 | 0 | 0 | 2.2397 | 1.9292 | 0 | 0 | 0
North Dakota | 0.14002 | 0.15657 | 1.9513 | 1.6267 | 6A | 7 | 0 | 0 | 0 | 2.6131 | 1.5879 | 0 | 0 | 0 | 2.0286 | 1.4061 | 0 | 0 | 0
Ohio | 0.14427 | -0.018216 | 2.3829 | 1.9631 | 4A | 5A | 0 | 0 | 0 | 5.9788 | 1.9105 | 0 | 0 | 0 | 4.1895 | 1.6706 | 0 | 0 | 0
Oregon | 0.097106 | -0.25258 | 1.8866 | 1.4948 | 4C | 5B | 0 | 0 | 0 | 1.9573 | 1.4524 | 0 | 0 | 0 | 1.5284 | 1.2883 | 0 | 0 | 0
Pennsylvania | 0.12978 | -1.7579 | 3.8598 | 2.7026 | 4A | 5A | 6A | 0 | 0 | 7.0525 | 1.8089 | 0 | 0 | 0 | 4.3974 | 1.6139 | 0 | 0 | 0
South Dakota | 0.1597 | 0.53649 | 2.0169 | 1.7668 | 5A | 6A | 0 | 0 | 0 | 2.5352 | 1.9735 | 0 | 0 | 0 | 2.1034 | 1.7386 | 0 | 0 | 0
Tennessee | 0.13065 | 0.24257 | 1.955 | 1.6843 | 3A | 4A | 0 | 0 | 0 | 3.1141 | 1.7186 | 0 | 0 | 0 | 2.358 | 1.5469 | 0 | 0 | 0
Vermont | 0.12991 | 0.60277 | 1.9678 | 1.8344 | 6A | 0 | 0 | 0 | 0 | 1.9678 | 0 | 0 | 0 | 0 | 1.8344 | 0 | 0 | 0 | 0
Washington | 0.074972 | -3.6753 | 5.0162 | 3.4245 | 4C | 5B | 6B | 0 | 0 | 5.5367 | 1.2105 | 1.4327 | 0 | 0 | 3.7475 | 1.0621 | 1.2227 | 0 | 0
West Virginia | 0.12975 | 0.29548 | 1.4727 | 1.2463 | 4A | 5A | 0 | 0 | 0 | 1.5125 | 1.4492 | 0 | 0 | 0 | 1.2916 | 1.2195 | 0 | 0 | 0
Wyoming | 0.10778 | 0.52823 | 1.3003 | 1.1872 | 5B | 6B | 7 | 0 | 0 | 2.1398 | 1.3962 | 0.54391 | 0 | 0 | 2.0123 | 1.225 | 0.80781 | 0 | 0
Alaska | 0.23106 | -5.5374 | 9.6673 | 6.5647 | 7 | 8 | 0 | 0 | 0 | 12.2261 | 5.182 | 0 | 0 | 0 | 7.6467 | 4.6679 | 0 | 0 | 0
Get Key Results for All States

## _PrintToWord (hidden)
Cross-Reference Table
| Work Folder | C:\Users\poeh439\Desktop\Working Folder\038. Commercial Codes (Matthew Tyler)\2021 IECC\
| Excel Workbook | #VALUE!
| Word Document | State_Template_wBookmarks_comm_2021-07-19_Clean.docx
| Total Number of Bookmars | 111
| Output Document Name Prefix | US
| Number of Climate Zones to Report | 5
| Date | July 2021
| Report Title | Cost-Effectiveness of Standard 90.1-2019 for US National
Number | Bookmark | Start Char | End Char | Text | Item Type | Worksheet | Range | Copy/Paste As | Formating | Paste Value | Table | Worksheet | Ref Row | Ref Col
1 | b01_state_name | 85 | 92 | Arizona | Text | State Inputs | $A$4 | Value |  | US National | 1 | Result Tables | 19 | 2
2 | b02_state_name | 1997 | 2004 | Arizona | Text | State Inputs | $A$4 | Value |  | US National | 2 | Result Tables | 29 | 2
3 | b04_state_name | 3023 | 3043 | the state of Arizona | Text | State Inputs | $A$4 | Value |  | US National | 3 | Result Tables | 39 | 2
4 | b05_t1_annual_cost_savings | 4170 | 4176 | $0.120 | Text | StateReport | $G$51 | Value | $0.000 | $0.186 | 4 | Result Tables | 64 | 2
5 | b06_t1_added_construction_cost | 4211 | 4219 | ($1.679) | Text | StateReport | $G$52 | Value | $0.000 | $1.085 | 5 | Result Tables | 83 | 2
6 | b07_t1_LCC_s1 | 4264 | 4267 | X.X | Text | StateReport | $G$63 | Value | 0.00 | 2.58 | 6 | Result Tables | 97 | 2
7 | b07_t1_LCC_s2 | 4313 | 4316 | X.X | Text | StateReport | $G$64 | Value | 0.00 | 2.55 | 10 | Energy Results | 6 | 30
8 | b10_f1 | 5520 | 5521 | / | Chart | StateReport | Chart 3 | Picture |  | Chart 3 | 11 | Energy Results | 35 | 30
9 | b11_f2 | 5522 | 5523 | / | Chart | StateReport | Chart 4 | Picture |  | Chart 4 | 12.A | EndUse Tables | 19 | 10
10 | b12_state_name | 5684 | 5691 | Arizona | Text | State Inputs | $A$4 | Value |  | US National | 12.B | EndUse Tables | 43 | 10
11 | b13_public_LCC_savings | 7773 | 7778 | $3.64 | Text | Result Tables | $I$25 | Value | $0.00 | $2.58 | 12.C | EndUse Tables | 67 | 10
12 | b14_private_LCC_savings | 7958 | 7963 | $2.61 | Text | Result Tables | $I$35 | Value | $0.00 | $2.55 | 12.D | EndUse Tables | 91 | 10
13 | b15_energy_cost_savings | 8307 | 8313 | $0.120 | Text | Result Tables | $I$45 | Value | $0.000 | $0.186 | 12.E | EndUse Tables | 115 | 10
14 | b16_t3 | 7876 | 7878 | / | Table | Result Tables | $B$19:$I$25 | Picture |  | Table $B$19:$I$25
15 | b17_t4 | 8053 | 8055 | / | Table | Result Tables | $B$29:$I$35 | Picture |  | Table $B$29:$I$35
16 | b18_t5 | 8387 | 8389 | / | Table | Result Tables | $B$39:$I$45 | Picture |  | Table $B$39:$I$45
17 | b20_t6 | 9188 | 9190 | / | Table | Result Tables | $B$64:$I$70 | Picture |  | Table $B$64:$I$70
18 | b21_t7 | 10955 | 10957 | / | Table | Result Tables | $B$83:$I$89 | Picture |  | Table $B$83:$I$89
19 | b22_t8 | 11587 | 11589 | / | Table | Result Tables | $B$97:$I$103 | Picture |  | Table $B$97:$I$103
20 | b26_t10_public_elec_price | 26663 | 26670 | $0.1005 | Text | LCC Methodology | $D$118 | Value | $0.0000 | $0.1099
21 | b27_t10_public_gas_price | 26712 | 26719 | $0.8509 | Text | LCC Methodology | $D$119 | Value | $0.0000 | $0.9830
22 | b28_t10_state_sales_tax | 27077 | 27082 | 8.17% | Text | LCC Methodology | $D$127 | Value | 0.00% | 6.56%
23 | b29_t10_private_elec_price | 26671 | 26678 | $0.1005 | Text | LCC Methodology | $E$118 | Value | $0.0000 | $0.1099
24 | b30_t10_private_gas_price | 26720 | 26727 | $0.8509 | Text | LCC Methodology | $E$119 | Value | $0.0000 | $0.9830
25 | b31_t10_state_corporate_tax | 26995 | 27000 | 6.50% | Text | LCC Methodology | $E$125 | Value | 0.00% | 6.01%
26 | b32_t10_state_combined_tax | 27033 | 27039 | 38.29% | Text | LCC Methodology | $E$126 | Value | 0.00% | 25.75%
27 | b33_t10_private_sales_tax | 27083 | 27088 | 8.17% | Text | LCC Methodology | $E$127 | Value | 0.00% | 6.56%
28 | b34_t11_state_elec_price | 30737 | 30744 | $0.1611 | Text | Energy Results | $AF$2 | Value | $0.0000 | $0.1099
29 | b35_t11_state_gas_price | 30754 | 30761 | $0.8080 | Text | Energy Results | $AF$3 | Value | $0.0000 | $0.9830
30 | b36_t11_state_name | 30697 | 30704 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
31 | b37_t12_state_name | 30907 | 30914 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
32 | b38_t12 | 30934 | 30936 | / | Table | Energy Results | $AD$7:$AP$32 | Picture |  | Table $AD$7:$AP$32
33 | b39_t13_state_name | 31055 | 31062 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
34 | b40_t13 | 31091 | 31093 | / | Table | Energy Results | $AD$36:$AP$61 | Picture |  | Table $AD$36:$AP$61
35 | b41_t14a_state_name | 31227 | 31234 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
36 | b42_t14a | 31254 | 31256 | / | Table | EndUse Tables | $J$20:$V$40 | Picture |  | Table $J$20:$V$40
37 | b43_t14b_state_name | 31308 | 31315 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
38 | b44_t14b | 31335 | 31337 | / | Table | EndUse Tables | $J$44:$V$64 | Picture |  | Table $J$44:$V$64
39 | b45_t14c_state_name | 31389 | 31396 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
40 | b46_t14c | 31416 | 31418 | / | Table | EndUse Tables | $J$68:$V$88 | Picture |  | Table $J$68:$V$88
41 | b47_t12_text_ref | 30568 | 30597 | Tables 15.A through 15.E show | Text | StateReport | $O$44 | Value |  | Tables 15.A through 15.E show
42 | b48_t14a_cz_name | 31251 | 31253 | 4A | Text | EndUse Tables | $H$22 | Value | #0 | 2A
43 | b49_t14b_cz_name | 31332 | 31334 | 5A | Text | EndUse Tables | $H$46 | Value | #0 | 3A
44 | b50_t14c_cz_name | 31413 | 31415 | 6A | Text | EndUse Tables | $H$70 | Value | #0 | 3B
45 | b51_t14d_state_name | 31470 | 31477 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
46 | b52_t14d_cz_name | 31494 | 31496 | 6A | Text | EndUse Tables | $H$94 | Value | #0 | 4A
47 | b53_t14d | 31498 | 31500 | / | Table | EndUse Tables | $J$92:$V$112 | Picture |  | Table $J$92:$V$112
48 | b54_t14e_state_name | 31552 | 31559 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
49 | b55_t14e_cz_name | 31576 | 31578 | 6A | Text | EndUse Tables | $H$118 | Value | #0 | 5A
50 | b56_t14e | 31580 | 31582 | / | Table | EndUse Tables | $J$116:$V$136 | Picture |  | Table $J$116:$V$136
51 | b66_t10_public_const_cost_index | 27122 | 27127 | 0.882 | Text | State Inputs | $V$8 | Value | 0.000 | 1.000
52 | b67_t10_private_const_cost_index | 27128 | 27133 | 0.882 | Text | State Inputs | $V$8 | Value | 0.000 | 1.000
53 | b71_t10b | 31009 | 31011 | / | Table | Energy Results | $AQ$7:$AY$32 | Picture |  | Table $AQ$7:$AY$32
54 | b72_t10b_state_name | 30982 | 30989 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
55 | b73_t10_name | 30864 | 30874 | Table 13.A | Text | StateReport | $O$47 | Value |  | Table 13.A
56 | b74_t10_text_ref | 30239 | 30287 |  REF _Ref432147652 s 13.A and 13.B show | Text | StateReport | $O$45 | Value |  | Tables 13.A and 13.B show
57 | b75_t11_text_ref | 30413 | 30438 | Tables 14.A and 14.B show | Text | StateReport | $O$46 | Value |  | Tables 14.A and 14.B show
58 | b76_t11_name | 31013 | 31023 | Table 14.A | Text | StateReport | $O$48 | Value |  | Table 14.A
59 | b77_t11b_state_name | 31138 | 31145 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
60 | b78_t11b | 31174 | 31176 | / | Table | Energy Results | $AQ$36:$AY$61 | Picture |  | Table $AQ$36:$AY$61
61 | b80_state_name | 30169 | 30176 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
62 | b82_state_name | 7848 | 7855 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
63 | b83_state_name | 8025 | 8032 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
64 | b84_state_name | 8371 | 8378 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
65 | b85_state_name | 10939 | 10946 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
66 | b86_state_name | 11571 | 11578 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
67 | b87_date | 93 | 104 | July 2021 | Text |  |  |  |  | July 2021
68 | b88_date | 2007 | 2019 | July 2021 | Text |  |  |  |  | July 2021
69 | b89_annualEnergyCostSavings | 3111 | 3116 | 0.120 | Text | StateReport | $G$51 | Value | #,##0.000 | 0.186
70 | b90_MMTofCO2_30yr | 3204 | 3207 | YYY | Text | emissions | $F$76 | Value | #,###.0 | #N/A
71 | b91_Cars | 3270 | 3273 | ZZZ | Text | emissions | $AR$3 | Value | #,### | #N/A
72 | b92_EnergyCostSavings_1 | 4408 | 4411 | XXX | Text | emissions | $C$75 | Value | #,### | #N/A
73 | b93_EnergyCostSavings_30 | 4412 | 4415 | XXX | Text | emissions | $D$75 | Value | #,### | #N/A
74 | b94_emissionsMMT_CO2_1 | 4453 | 4456 | XXX | Text | emissions | $C$76 | Value | #,### | #N/A
75 | b95_emissionsMMT_CO2_30 | 4457 | 4460 | XXX | Text | emissions | $D$76 | Value | #,### | #N/A
76 | b96_emissionsMMT_CH4_1 | 4500 | 4503 | XXX | Text | emissions | $C$78 | Value | #,##0.00 | #N/A
77 | b97_emissionsMMT_CH4_30 | 4504 | 4507 | XXX | Text | emissions | $D$78 | Value | #,### | #N/A
78 | b98_emissionsMMT_N20_1 | 4547 | 4550 | XXX | Text | emissions | $C$80 | Value | #,##0.000 | #N/A
79 | b99_000_emissionsMMT_N20_30 | 4551 | 4554 | XXX | Text | emissions | $D$80 | Value | #,### | #N/A
80 | b99_001_emissionsMMT_NOx_1 | 4594 | 4597 | XXX | Text | emissions | $C$82 | Value | #,##0.00 | #N/A
81 | b99_002_emissionsMMT_NOx_30 | 4598 | 4601 | XXX | Text | emissions | $D$82 | Value | #,### | #N/A
82 | b99_003_emissionsMMT_SOx_1 | 4641 | 4644 | XXX | Text | emissions | $C$83 | Value | #,##0.00 | #N/A
83 | b99_004_emissionsMMT_SOx_30 | 4645 | 4648 | XXX | Text | emissions | $D$83 | Value | #,### | #N/A
84 | b99_011_jobs_utility_1 | 4755 | 4758 | XXX | Text | jobs | $C$6 | Value | #,### | #NAME?
85 | b99_012_jobs_utility_30 | 4759 | 4762 | XXX | Text | jobs | $D$6 | Value | #,### | #NAME?
86 | b99_013_jobs_construction_1 | 4809 | 4812 | XXX | Text | jobs | $C$7 | Value | #,### | #NAME?
87 | b99_014_jobs_construction_30 | 4813 | 4816 | XXX | Text | jobs | $D$7 | Value | #,### | #NAME?
88 | b99_015_state | 12353 | 12360 | Arizona | Text | State Inputs | $A$4 | Value |  | US National
89 | b99_016_EnergyCostSavings_1 | 16320 | 16323 | XXX | Text | emissions | $C$75 | Value | #,### | #N/A
90 | b99_017_EnergyCostSavings_30 | 16324 | 16327 | XXX | Text | emissions | $D$75 | Value | #,### | #N/A
91 | b99_018_emissionsMMT_CO2_1 | 16365 | 16368 | XXX | Text | emissions | $C$76 | Value | #,### | #N/A
92 | b99_019_emissionsMMT_CO2_30 | 16369 | 16372 | XXX | Text | emissions | $D$76 | Value | #,### | #N/A
93 | b99_020_emissionsMMT_CH4_1 | 16412 | 16415 | XXX | Text | emissions | $C$78 | Value | #,##0.00 | #N/A
94 | b99_021_emissionsMMT_CH4_30 | 16416 | 16419 | XXX | Text | emissions | $D$78 | Value | #,### | #N/A
95 | b99_022_emissionsMMT_N2O_1 | 16459 | 16462 | XXX | Text | emissions | $C$80 | Value | #,##0.000 | #N/A
96 | b99_023_emissionsMMT_N2O_30 | 16463 | 16466 | XXX | Text | emissions | $D$80 | Value | #,### | #N/A
97 | b99_024_emissionsMMT_NOx_1 | 16506 | 16509 | XXX | Text | emissions | $C$82 | Value | #,##0.00 | #N/A
98 | b99_025_emissionsMMT_NOx_30 | 16510 | 16513 | XXX | Text | emissions | $D$82 | Value | #,### | #N/A
99 | b99_026_emissionsMMT_SOx_1 | 16553 | 16556 | XXX | Text | emissions | $C$83 | Value | #,##0.00 | #N/A
100 | b99_027_emissionsMMT_SOx_30 | 16557 | 16560 | XXX | Text | emissions | $D$83 | Value | #,### | #N/A
101 | b99_034_emissionFactors_CO2 | 15901 | 15904 | XXX | Text | emissions | $C$65 | Value | #,##0 | #N/A
102 | b99_035_emissionFactors_SO2 | 15918 | 15921 | XXX | Text | emissions | $C$66 | Value | #,##0.000 | #N/A
103 | b99_036_emissionFactors_NOx | 15931 | 15934 | XXX | Text | emissions | $C$67 | Value | #,##0.000 | #N/A
104 | b99_037_emissionFactors_N2O | 15943 | 15946 | XXX | Text | emissions | $C$68 | Value | #,##0.000 | #N/A
105 | b99_038_emissionFactors_CH4 | 15957 | 15960 | XXX | Text | emissions | $C$69 | Value | #,##0.000 | #N/A
106 | b99_039_jobs_utility_1 | 17829 | 17832 | XXX | Text | jobs | $C$6 | Value | #,### | #NAME?
107 | b99_040_jobs_utility_30 | 17833 | 17836 | XXX | Text | jobs | $D$6 | Value | #,### | #NAME?
108 | b99_041_jobs_construction_1 | 17883 | 17886 | XXX | Text | jobs | $C$7 | Value | #,### | #NAME?
109 | b99_042_jobs_construction_30 | 17887 | 17890 | XXX | Text | jobs | $D$7 | Value | #,### | #NAME?
110 | b99_043_PNNL_ReportNo | 7 | 19 | PNNL-XXXXX | Text | reportNo | $E$2 | Value | #,### | PNNL-
111 | b99_044_PNNL_ReportNo |  |  | PNNL-XXXXX | Text | reportNo | $E$2 | Value | #,### | PNNL-
List Bookmarks from Word Document
Generate Word and PDF Reports for Current State
Generate Word and PDF Reports for All States

## oldBookmarks (hidden)
Number | Bookmark | Start Char | End Char | Text | Item Type | Worksheet | Range | Copy/Paste As | Formating | Paste Value
1 | b01_state_name | 85 | 92 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
2 | b02_state_name | 1986 | 1993 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
3 | b04_state_name | 3096 | 3116 | the state of Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
4 | b05_t1_annual_cost_savings | 4243 | 4249 | $0.120 | Text | StateReport | $G$51 | Value | $0.000 | $0.068 | TRUE
5 | b06_t1_added_construction_cost | 4284 | 4292 | ($1.679) | Text | StateReport | $G$52 | Value | $0.000 | -$1.029 | TRUE
6 | b07_t1_LCC_s1 | 4337 | 4340 | X.X | Text | StateReport | $G$63 | Value | 0.00 | 4.00 | TRUE
7 | b07_t1_LCC_s2 | 4386 | 4389 | X.X | Text | StateReport | $G$64 | Value | 0.00 | 3.51 | TRUE
8 | b10_f1 | 5709 | 5710 | / | Chart | StateReport | Chart 3 | Picture |  | Chart 3 | TRUE
9 | b11_f2 | 5711 | 5712 | / | Chart | StateReport | Chart 4 | Picture |  | Chart 4 | TRUE
10 | b12_state_name | 5874 | 5881 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
11 | b13_public_LCC_savings | 7963 | 7968 | $3.64 | Text | Result Tables | $I$25 | Value | $0.00 | $4.00 | TRUE
12 | b14_private_LCC_savings | 8148 | 8153 | $2.61 | Text | Result Tables | $I$35 | Value | $0.00 | $3.51 | TRUE
13 | b15_energy_cost_savings | 8497 | 8503 | $0.120 | Text | Result Tables | $I$45 | Value | $0.000 | $0.068 | TRUE
14 | b16_t3 | 8066 | 8068 | / | Table | Result Tables | $B$19:$I$25 | Picture |  | Table $B$19:$I$25 | TRUE
15 | b17_t4 | 8243 | 8245 | / | Table | Result Tables | $B$29:$I$35 | Picture |  | Table $B$29:$I$35 | TRUE
16 | b18_t5 | 8577 | 8579 | / | Table | Result Tables | $B$39:$I$45 | Picture |  | Table $B$39:$I$45 | TRUE
17 | b20_t6 | 9378 | 9380 | / | Table | Result Tables | $B$64:$I$70 | Picture |  | Table $B$64:$I$70 | TRUE
18 | b21_t7 | 11145 | 11147 | / | Table | Result Tables | $B$83:$I$89 | Picture |  | Table $B$83:$I$89 | TRUE
19 | b22_t8 | 11777 | 11779 | / | Table | Result Tables | $B$97:$I$103 | Picture |  | Table $B$97:$I$103 | TRUE
20 | b26_t10_public_elec_price | 29638 | 29645 | $0.1005 | Text | LCC Methodology | $D$118 | Value | $0.0000 | $0.1051 | TRUE
21 | b27_t10_public_gas_price | 29687 | 29694 | $0.8509 | Text | LCC Methodology | $D$119 | Value | $0.0000 | $0.7510 | TRUE
22 | b28_t10_state_sales_tax | 30052 | 30057 | 8.17% | Text | LCC Methodology | $D$127 | Value | 0.00% | 9.55% | TRUE
23 | b29_t10_private_elec_price | 29646 | 29653 | $0.1005 | Text | LCC Methodology | $E$118 | Value | $0.0000 | $0.1051 | TRUE
24 | b30_t10_private_gas_price | 29695 | 29702 | $0.8509 | Text | LCC Methodology | $E$119 | Value | $0.0000 | $0.7510 | TRUE
25 | b31_t10_state_corporate_tax | 29970 | 29975 | 6.50% | Text | LCC Methodology | $E$125 | Value | 0.00% | 6.50% | TRUE
26 | b32_t10_state_combined_tax | 30008 | 30014 | 38.29% | Text | LCC Methodology | $E$126 | Value | 0.00% | 26.14% | TRUE
27 | b33_t10_private_sales_tax | 30058 | 30063 | 8.17% | Text | LCC Methodology | $E$127 | Value | 0.00% | 9.55% | TRUE
28 | b34_t11_state_elec_price | 33712 | 33719 | $0.1611 | Text | Energy Results | $AF$2 | Value | $0.0000 | $0.1051 | TRUE
29 | b35_t11_state_gas_price | 33729 | 33736 | $0.8080 | Text | Energy Results | $AF$3 | Value | $0.0000 | $0.7510 | TRUE
30 | b36_t11_state_name | 33672 | 33679 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
31 | b37_t12_state_name | 33882 | 33889 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
32 | b38_t12 | 33909 | 33911 | / | Table | Energy Results | $AD$7:$AP$32 | Picture |  | Table $AD$7:$AP$32 | TRUE
33 | b39_t13_state_name | 34030 | 34037 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
34 | b40_t13 | 34066 | 34068 | / | Table | Energy Results | $AD$36:$AP$61 | Picture |  | Table $AD$36:$AP$61 | TRUE
35 | b41_t14a_state_name | 34202 | 34209 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
36 | b42_t14a | 34229 | 34231 | / | Table | EndUse Tables | $J$20:$V$40 | Picture |  | Table $J$20:$V$40 | TRUE
37 | b43_t14b_state_name | 34283 | 34290 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
38 | b44_t14b | 34310 | 34312 | / | Table | EndUse Tables | $J$44:$V$64 | Picture |  | Table $J$44:$V$64 | TRUE
39 | b45_t14c_state_name | 34364 | 34371 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
40 | b46_t14c | 34391 | 34393 | / | Table | EndUse Tables | $J$68:$V$88 | Picture |  | Table $J$68:$V$88 | TRUE
41 | b47_t12_text_ref | 33543 | 33572 | Tables 13.A through 13.E show | Text | StateReport | $O$44 | Value |  | Tables 12.A and 12.B show | TRUE
42 | b48_t14a_cz_name | 34226 | 34228 | 4A | Text | EndUse Tables | $H$22 | Value | #0 | 3B | TRUE
43 | b49_t14b_cz_name | 34307 | 34309 | 5A | Text | EndUse Tables | $H$46 | Value | #0 | 5B | TRUE
44 | b50_t14c_cz_name | 34388 | 34390 | 6A | Text | EndUse Tables | $H$70 | Value | #0 | 6B | TRUE
45 | b51_t14d_state_name | 34445 | 34452 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
46 | b52_t14d_cz_name | 34469 | 34471 | 6A | Text | EndUse Tables | $H$94 | Value | #0 | 0 | TRUE
47 | b53_t14d | 34473 | 34475 | / | Table | EndUse Tables | $J$92:$V$112 | Picture |  | Table $J$92:$V$112 | TRUE
48 | b54_t14e_state_name | 34527 | 34534 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
49 | b55_t14e_cz_name | 34551 | 34553 | 6A | Text | EndUse Tables | $H$118 | Value | #0 | 0 | TRUE
50 | b56_t14e | 34555 | 34557 | / | Table | EndUse Tables | $J$116:$V$136 | Picture |  | Table $J$116:$V$136 | TRUE
51 | b66_t10_public_const_cost_index | 30097 | 30102 | 0.882 | Text | State Inputs | $V$8 | Value | 0.000 | 0.852 | TRUE
52 | b67_t10_private_const_cost_index | 30103 | 30108 | 0.882 | Text | State Inputs | $V$8 | Value | 0.000 | 0.852 | TRUE
53 | b71_t10b | 33984 | 33986 | / | Text | State Inputs | $A$4 | Value |  |  | TRUE
54 | b72_t10b_state_name | 33957 | 33964 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
55 | b73_t10_name | 33839 | 33849 | Table 11.A | Text | State Inputs | $A$4 | Value |  | Table 11.A | TRUE
56 | b74_t10_text_ref | 33214 | 33262 |  REF _Ref432147652 s 11.A and 11.B show | Text | State Inputs | $V$8 | Value | 0.000 | Tables 11.A shows | TRUE
57 | b75_t11_text_ref | 33388 | 33413 | Tables 12.A and 12.B show | Text | State Inputs | $V$8 | Value | 0.000 | Tables 12.A shows | TRUE
58 | b76_t11_name | 33988 | 33998 | Table 12.A | Text | StateReport | $O$43 | Value |  | Table 12.A | TRUE
59 | b77_t11b_state_name | 34113 | 34120 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
60 | b78_t11b | 34149 | 34151 | / | Table | Energy Results | $AQ$7:$AY$32 | Picture |  | Table $AQ$7:$AY$32 | TRUE
61 | b80_state_name | 33144 | 33151 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
62 | b82_state_name | 8038 | 8045 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
63 | b83_state_name | 8215 | 8222 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
64 | b84_state_name | 8561 | 8568 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
65 | b85_state_name | 11129 | 11136 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
66 | b86_state_name | 11761 | 11768 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
67 | b87_date | 93 | 103 | May 2021 | Text |  |  |  |  | June 2021 | TRUE
68 | b88_date | 1996 | 2007 | May 2021 | Text |  |  |  |  | June 2021 | TRUE
69 | b89_annualEnergyCostSavings | 3184 | 3189 | 0.120 | Text | StateReport | $G$51 | Value | #,##0.000 | 0.068 | TRUE
70 | b90_MMTofCO2_30yr | 3277 | 3280 | YYY | Text | emissions | $F$76 | Value | #,###.0 | 6.7 | TRUE
71 | b91_Cars | 3343 | 3346 | ZZZ | Text | emissions | $AR$2 | Value | #,### | 1,458,011 | TRUE
72 | b92_EnergyCostSavings_1 | 4477 | 4480 | XXX | Text | emissions | $C$75 | Value | #,### | 1,025,848 | TRUE
73 | b93_EnergyCostSavings_30 | 4481 | 4484 | XXX | Text | emissions | $D$75 | Value | #,### | 450,804,909 | TRUE
74 | b94_emissionsMMT_CO2_1 | 4522 | 4525 | XXX | Text | emissions | $C$76 | Value | #,### | 9,458 | TRUE
75 | b95_emissionsMMT_CO2_30 | 4526 | 4529 | XXX | Text | emissions | $D$76 | Value | #,### | 6,704,114 | TRUE
76 | b96_emissionsMMT_CH4_1 | 4611 | 4614 | XXX | Text | emissions | $C$78 | Value | #,##0.00 | 0.74 | TRUE
77 | b97_emissionsMMT_CH4_30 | 4615 | 4618 | XXX | Text | emissions | $D$78 | Value | #,### | 524 | TRUE
78 | b98_emissionsMMT_N20_1 | 4697 | 4700 | XXX | Text | emissions | $C$80 | Value | #,##0.000 | 0.104 | TRUE
79 | b99_000_emissionsMMT_N20_30 | 4701 | 4704 | XXX | Text | emissions | $D$80 | Value | #,### | 74 | TRUE
80 | b99_001_emissionsMMT_NOx_1 | 4783 | 4786 | XXX | Text | emissions | $C$82 | Value | #,##0.00 | 4.11 | TRUE
81 | b99_002_emissionsMMT_NOx_30 | 4787 | 4790 | XXX | Text | emissions | $D$82 | Value | #,### | 2,912 | TRUE
82 | b99_003_emissionsMMT_SOx_1 | 4830 | 4833 | XXX | Text | emissions | $C$83 | Value | #,##0.00 | 4.19 | TRUE
83 | b99_004_emissionsMMT_SOx_30 | 4834 | 4837 | XXX | Text | emissions | $D$83 | Value | #,### | 2,969 | TRUE
84 | b99_005_SCC_CO2_1 | 4564 | 4567 | XXX | Text | emissions | $C$77 | Value | #,### | 132,564 | FALSE
85 | b99_006_SCC_CO2_30 | 4568 | 4571 | XXX | Text | emissions | $D$77 | Value | #,### | 75,194,658 | FALSE
86 | b99_007_SCC_CH4_1 | 4650 | 4653 | XXX | Text | emissions | $C$79 | Value | #,### | 483 | FALSE
87 | b99_008_SCC_CH4_30 | 4654 | 4657 | XXX | Text | emissions | $D$79 | Value | #,### | 287,953 | FALSE
88 | b99_009_SCC_N2O_1 | 4736 | 4739 | XXX | Text | emissions | $C$81 | Value | #,### | 582 | FALSE
89 | b99_010_SCC_N2O_30 | 4740 | 4743 | XXX | Text | emissions | $D$81 | Value | #,### | 333,878 | FALSE
90 | b99_011_jobs_utility_1 | 4944 | 4947 | XXX | Text | jobs | $C$6 | Value | #,### | 93 | TRUE
91 | b99_012_jobs_utility_30 | 4948 | 4951 | XXX | Text | jobs | $D$6 | Value | #,### | 3,006 | TRUE
92 | b99_013_jobs_construction_1 | 4998 | 5001 | XXX | Text | jobs | $C$7 | Value | #,### | 94 | TRUE
93 | b99_014_jobs_construction_30 | 5002 | 5005 | XXX | Text | jobs | $D$7 | Value | #,### | 3,025 | TRUE
94 | b99_015_state | 12543 | 12550 | Arizona | Text | State Inputs | $A$4 | Value |  | Tennessee | TRUE
95 | b99_016_EnergyCostSavings_1 | 19177 | 19180 | XXX | Text | emissions | $C$75 | Value | #,### | 1,025,848 | TRUE
96 | b99_017_EnergyCostSavings_30 | 19181 | 19184 | XXX | Text | emissions | $D$75 | Value | #,### | 450,804,909 | TRUE
97 | b99_018_emissionsMMT_CO2_1 | 19222 | 19225 | XXX | Text | emissions | $C$76 | Value | #,### | 9,458 | TRUE
98 | b99_019_emissionsMMT_CO2_30 | 19226 | 19229 | XXX | Text | emissions | $D$76 | Value | #,### | 6,704,114 | TRUE
99 | b99_020_emissionsMMT_CH4_1 | 19311 | 19314 | XXX | Text | emissions | $C$78 | Value | #,##0.00 | 0.74 | TRUE
100 | b99_021_emissionsMMT_CH4_30 | 19315 | 19318 | XXX | Text | emissions | $D$78 | Value | #,### | 524 | TRUE
101 | b99_022_emissionsMMT_N2O_1 | 19397 | 19400 | XXX | Text | emissions | $C$80 | Value | #,##0.000 | 0.104 | TRUE
102 | b99_023_emissionsMMT_N2O_30 | 19401 | 19404 | XXX | Text | emissions | $D$80 | Value | #,### | 74 | TRUE
103 | b99_024_emissionsMMT_NOx_1 | 19483 | 19486 | XXX | Text | emissions | $C$82 | Value | #,##0.00 | 4.11 | TRUE
104 | b99_025_emissionsMMT_NOx_30 | 19487 | 19490 | XXX | Text | emissions | $D$82 | Value | #,### | 2,912 | TRUE
105 | b99_026_emissionsMMT_SOx_1 | 19530 | 19533 | XXX | Text | emissions | $C$83 | Value | #,##0.00 | 4.19 | TRUE
106 | b99_027_emissionsMMT_SOx_30 | 19534 | 19537 | XXX | Text | emissions | $D$83 | Value | #,### | 2,969 | TRUE
107 | b99_028_SCC_CO2_1 | 19264 | 19267 | XXX | Text | emissions | $C$77 | Value | #,### | 132,564 | FALSE
108 | b99_029_SCC_CO2_30 | 19268 | 19271 | XXX | Text | emissions | $D$77 | Value | #,### | 75,194,658 | FALSE
109 | b99_030_SCC_CH4_1 | 19350 | 19353 | XXX | Text | emissions | $C$79 | Value | #,### | 483 | FALSE
110 | b99_031_SCC_CH4_30 | 19354 | 19357 | XXX | Text | emissions | $D$79 | Value | #,### | 287,953 | FALSE
111 | b99_032_SCC_N2O_1 | 19436 | 19439 | XXX | Text | emissions | $C$81 | Value | #,### | 582 | FALSE
112 | b99_033_SCC_N2O_30 | 19440 | 19443 | XXX | Text | emissions | $D$81 | Value | #,### | 333,878 | FALSE
113 | b99_034_emissionFactors_CO2 | 18812 | 18815 | XXX | Text | emissions | $C$65 | Value | #,##0 | 1,531 | FALSE
114 | b99_035_emissionFactors_SO2 | 18829 | 18832 | XXX | Text | emissions | $C$66 | Value | #,##0.000 | 0.784 | FALSE
115 | b99_036_emissionFactors_NOx | 18842 | 18845 | XXX | Text | emissions | $C$67 | Value | #,##0.000 | 0.576 | FALSE
116 | b99_037_emissionFactors_N2O | 18854 | 18857 | XXX | Text | emissions | $C$68 | Value | #,##0.000 | 0.019 | FALSE
117 | b99_038_emissionFactors_CH4 | 18868 | 18871 | XXX | Text | emissions | $C$69 | Value | #,##0.000 | 0.134 | FALSE
118 | b99_039_jobs_utility_1 | 20806 | 20809 | XXX | Text | jobs | $C$6 | Value | #,### | 93 | FALSE
119 | b99_040_jobs_utility_30 | 20810 | 20813 | XXX | Text | jobs | $D$6 | Value | #,### | 3,006 | FALSE
120 | b99_041_jobs_construction_1 | 20860 | 20863 | XXX | Text | jobs | $C$7 | Value | #,### | 94 | FALSE
121 | b99_042_jobs_construction_30 | 20864 | 20867 | XXX | Text | jobs | $D$7 | Value | #,### | 3,025 | FALSE

## Sheet1 (hidden)
Number | Bookmark | Start Char | End Char | Text
1 | b01_state_name | 85 | 92 | Arizona
2 | b02_state_name | 1986 | 1993 | Arizona
3 | b04_state_name | 3096 | 3116 | the state of Arizona
4 | b05_t1_annual_cost_savings | 4243 | 4249 | $0.120
5 | b06_t1_added_construction_cost | 4284 | 4292 | ($1.679)
6 | b07_t1_LCC_s1 | 4337 | 4340 | X.X
7 | b07_t1_LCC_s2 | 4386 | 4389 | X.X
8 | b10_f1 | 5739 | 5739
9 | b11_f2 | 5741 | 5741
10 | b12_state_name | 5904 | 5911 | Arizona
11 | b13_public_LCC_savings | 7993 | 7998 | $3.64
12 | b14_private_LCC_savings | 8178 | 8183 | $2.61
13 | b15_energy_cost_savings | 8527 | 8533 | $0.120
14 | b16_t3 | 8096 | 8098 | /
15 | b17_t4 | 8273 | 8275 | /
16 | b18_t5 | 8607 | 8609 | /
17 | b20_t6 | 9408 | 9410 | /
18 | b21_t7 | 11175 | 11177 | /
19 | b22_t8 | 11807 | 11809 | /
20 | b26_t10_public_elec_price | 29690 | 29697 | $0.1005
21 | b27_t10_public_gas_price | 29739 | 29746 | $0.8509
22 | b28_t10_state_sales_tax | 30104 | 30109 | 8.17%
23 | b29_t10_private_elec_price | 29698 | 29705 | $0.1005
24 | b30_t10_private_gas_price | 29747 | 29754 | $0.8509
25 | b31_t10_state_corporate_tax | 30022 | 30027 | 6.50%
26 | b32_t10_state_combined_tax | 30060 | 30066 | 38.29%
27 | b33_t10_private_sales_tax | 30110 | 30115 | 8.17%
28 | b34_t11_state_elec_price | 33764 | 33771 | $0.1611
29 | b35_t11_state_gas_price | 33781 | 33788 | $0.8080
30 | b36_t11_state_name | 33724 | 33731 | Arizona
31 | b37_t12_state_name | 33934 | 33941 | Arizona
32 | b38_t12 | 33961 | 33963 | /
33 | b39_t13_state_name | 34082 | 34089 | Arizona
34 | b40_t13 | 34118 | 34120 | /
35 | b41_t14a_state_name | 34254 | 34261 | Arizona
36 | b42_t14a | 34281 | 34283 | /
37 | b43_t14b_state_name | 34335 | 34342 | Arizona
38 | b44_t14b | 34362 | 34364 | /
39 | b45_t14c_state_name | 34416 | 34423 | Arizona
40 | b46_t14c | 34443 | 34445 | /
41 | b47_t12_text_ref | 33595 | 33624 | Tables 13.A through 13.E show
42 | b48_t14a_cz_name | 34278 | 34280 | 4A
43 | b49_t14b_cz_name | 34359 | 34361 | 5A
44 | b50_t14c_cz_name | 34440 | 34442 | 6A
45 | b51_t14d_state_name | 34497 | 34504 | Arizona
46 | b52_t14d_cz_name | 34521 | 34523 | 6A
47 | b53_t14d | 34525 | 34527 | /
48 | b54_t14e_state_name | 34579 | 34586 | Arizona
49 | b55_t14e_cz_name | 34603 | 34605 | 6A
50 | b56_t14e | 34607 | 34609 | /
51 | b66_t10_public_const_cost_index | 30149 | 30154 | 0.882
52 | b67_t10_private_const_cost_index | 30155 | 30160 | 0.882
53 | b71_t10b | 34036 | 34038 | /
54 | b72_t10b_state_name | 34009 | 34016 | Arizona
55 | b73_t10_name | 33891 | 33901 | Table 11.A
56 | b74_t10_text_ref | 33266 | 33314 | Tables 11.A and 11.B show
57 | b75_t11_text_ref | 33440 | 33465 | Tables 12.A and 12.B show
58 | b76_t11_name | 34040 | 34050 | Table 12.A
59 | b77_t11b_state_name | 34165 | 34172 | Arizona
60 | b78_t11b | 34201 | 34203 | /
61 | b80_state_name | 33196 | 33203 | Arizona
62 | b82_state_name | 8068 | 8075 | Arizona
63 | b83_state_name | 8245 | 8252 | Arizona
64 | b84_state_name | 8591 | 8598 | Arizona
65 | b85_state_name | 11159 | 11166 | Arizona
66 | b86_state_name | 11791 | 11798 | Arizona
67 | b78_t11b | 20178 | 20179 | 
68 | b79_first_cost_conditional | 2390 | 2435 | net of an allowance to pay for the added cost
69 | Table_10B | 19853 | 19957 | Table 10.B. Energy Cost Saving Results for ASHRAE Standard 90.1-2013 in Arizona, $ per square foot 
70 | Table_11B | 20068 | 20180 | Table 11.B. Energy Use Saving Results for ASHRAE Standard 90.1-2013 in Arizona, Energy Use per Square Foot 
71 | Table_14A | 20181 | 20259 | Table 12.A. Annual Energy Usage for Buildings in Arizona in Climate Zone 4A 
72 | Table_14B | 20259 | 20339 | Table 12.B. Annual Energy Usage for Buildings in Arizona in Climate Zone 5A 
73 | Table_14C | 20339 | 20419 | Table 12.C. Annual Energy Usage for Buildings in Arizona in Climate Zone 6A 
74 | Table_14D | 20419 | 20500 | Table 12.D. Annual Energy Usage for Buildings in Arizona in Climate Zone 6A 
75 | Table_14E | 20500 | 20581 | Table 12.E. Annual Energy Usage for Buildings in Arizona in Climate Zone 6A 

## first cost summary (hidden)
Note the first costs in column M are hard coded. Use the Cost Est Summary worksheet instead.
| Table 4.7 | Incremental cost
[9 empty] | Prototype | Building First Cost | Incremental Cost for 90.1-2022
| Value | 2A | 3A | 3B | 4A | 5A |  |  |  |  | 2A | 3A | 3B | 4A | 5A | All
|  | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY |  |  |  |  | Tampa FL | Atlanta GA | El Paso TX | New York NY | Buffalo NY | CZ
Small Office | First Cost | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 |  |  |  | $/ft2 | $/ft2 | $/ft2 | $/ft2 | $/ft2 | $/ft2 | $/ft2
| $/ft2 | 0.58745 | 0.56605 | 0.57979 | 0.82812 | 0.92122 |  | 5502 | Small Office | 220 | 0.58745 | 0.56605 | 0.57979 | 0.82812 | 0.92122 | 0.70315
Large Office | First Cost | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859 |  |  |  |  | 0.0026702 | 0.0025729 | 0.0026354 | 0.0037642 | 0.0041874 | 0.0031961
| $/ft2 | 1.6873 | 1.136 | 1.1084 | 1.1821 | 1.1731 |  | 498588 | Large Office | 180 | 1.6873 | 1.136 | 1.1084 | 1.1821 | 1.1731 | 1.2589
Standalone Retail | First Cost | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141 |  |  |  |  | 0.009374 | 0.0063111 | 0.0061576 | 0.0065675 | 0.0065173 | 0.006994
| $/ft2 | 1.1848 | 1.2556 | 1.2201 | 1.2856 | 1.1456 |  | 24692 | Standalone Retail | 116 | 1.1848 | 1.2556 | 1.2201 | 1.2856 | 1.1456 | 1.2143
Primary School | First Cost | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932 |  |  |  |  | 0.010214 | 0.010824 | 0.010518 | 0.011083 | 0.0098757 | 0.010468
| $/ft2 | 1.3303 | 1.3494 | 1.2803 | 1.3678 | 1.3836 |  | 73959 | Primary School | 225 | 1.3303 | 1.3494 | 1.2803 | 1.3678 | 1.3836 | 1.3492
Small Hotel | First Cost | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203 |  |  |  |  | 0.0059126 | 0.0059972 | 0.0056904 | 0.0060792 | 0.0061491 | 0.0059964
| $/ft2 | 1.6698 | 1.6064 | 1.5844 | 1.5882 | 1.5893 |  | 43202 | Small Hotel | 197 | 1.6698 | 1.6064 | 1.5844 | 1.5882 | 1.5893 | 1.6117
Mid-rise Apartment | First Cost | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794 |  |  |  |  | 0.0084759 | 0.0081543 | 0.0080425 | 0.008062 | 0.0080675 | 0.0081814
| $/ft2 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991 |  | 33741 | Mid-rise Apartment | 218 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991 | 0.87457
[11 empty] | 0.0044317 | 0.0043889 | 0.0038316 | 0.0036643 | 0.0038528 | 0.0040118
[9 empty] | All Building Types | 185.1743 | 1.1266 | 1.1065 | 1.0228 | 1.0703 | 1.0703 | 1.0851
Named area: |  | Floor Area Sq ft | [8 empty] | 0.0060839 | 0.0059757 | 0.0055233 | 0.0057801 | 0.0057801 | 0.0058598
Small Office | sfSO | 5502
Large Office | sfLO | 498588 | [7 empty] | Square foot costs are size-adjusted SF costs from Means Building 2020, page 897
Standalone Retail | sfRS | 24692
Primary School | sfPS | 73959
Small Hotel | sfSH | 43202
Mid-rise Apartment | sfMA | 33741
Construction weighting Factors
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6
| First Cost | 2A | 3A | 3B | 4A | 5A | Typ |  | 1 |  | 2A | 3A | 3B | 4A | 5A | All CZ
Small Office | $/ft2 | 0.58745 | 0.56605 | 0.57979 | 0.82812 | 0.92122 | 220 | 0.70315 | 2 | Small Office | 0.025336 | 0.023024 | 0.009086 | 0.019059 | 0.022135 | 0.09864
Large Office | $/ft2 | 1.6873 | 1.136 | 1.1084 | 1.1821 | 1.1731 | 180 | 1.2589 | 3 | Large Office | 0.017992 | 0.017948 | 0.008483 | 0.037221 | 0.015936 | 0.09758
Standalone Retail | $/ft2 | 1.1848 | 1.2556 | 1.2201 | 1.2856 | 1.1456 | 116 | 1.2143 | 4 | Stand-Alone Retail | 0.059235 | 0.058756 | 0.028203 | 0.063391 | 0.078184 | 0.28777
Primary School | $/ft2 | 1.3303 | 1.3494 | 1.2803 | 1.3678 | 1.3836 | 225 | 1.3492 | 5 | Primary School | 0.032252 | 0.031014 | 0.011845 | 0.029137 | 0.025519 | 0.12977
Small Hotel | $/ft2 | 1.6698 | 1.6064 | 1.5844 | 1.5882 | 1.5893 | 197 | 1.6117 | 6 | Small Hotel | 0.010034 | 0.008854 | 0.003509 | 0.010054 | 0.00901 | 0.041461
Mid-rise Apartment | $/ft2 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991 | 218 | 0.87457 | 7 | Mid-rise Apartment | 0.074155 | 0.058763 | 0.038875 | 0.099679 | 0.07331 | 0.34478
[7 empty] | All Build | 1.0851 |  | All Build | 0.219 | 0.19836 | 0.1 | 0.25854 | 0.22409 | 1
| First Cost | 2A | 3A | 3B | 4A | 5A | Typ | 0
Small Office | $/ft2 | 0.9661 | 0.95678 | 0.83528 | 0.79882 | 0.83991 | 218 | 0.89124
Large Office | 0 | 0 | 0 | 0 | 0 | 0 | 185.1743 | 0
Standalone Retail | sfSO | 5502 | 0 | 0 | 0 | 0 | 0 | 1132.5437
Primary School | sfRS | 24692 | 0 | 0 | 0 | 0 | 0 | 6136.8945
Small Hotel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mid-rise Apartment | sfSH | 43202 | 0 | 0 | 0 | 0 | 0 | 9291.7969
[7 empty] | All Build | 0
Note on J35: Zheng, Feng (Richard): modified formula to output zero instead of #DIV/0! When S35:S40 contain zero vaues.
Note on J45: Zheng, Feng (Richard): modified formula to output zero instead of #DIV/0! When S35:S40 contain zero vaues.

## Cost Eff Results (hidden)
Life cycle cost summary
Prototype |  | Climate Zone | [6 empty] | Scenario 1 | NPV > 0 | pass | 55 |  |  |  |  | Envelope reductions needed
|  | 2A Tampa | 3A Atlanta | 3B El Paso | 4A New York | 5A Buffalo |  |  |  |  | Out of | 55 |  |  |  | 2A | 3A | 3B | 4A | 5A
Life Cycle Cost Net Savings
Small Office | Total | 6800 | 6200 | 6400 | 5300 | 5300
| $/ft2 | 1.2359 | 1.1269 | 1.1632 | 0.96329 | 0.96329 |  | 5502
Large Office | Total | 470000 | 800000 | 860000 | 720000 | 740000
| $/ft2 | 0.94266 | 1.6045 | 1.7249 | 1.4441 | 1.4842 |  | 498588
Standalone Retail | Total | 87000 | 82200 | 74800 | 85000 | 91000
| $/ft2 | 3.5234 | 3.329 | 3.0293 | 3.4424 | 3.6854 |  | 24692
Primary School | Total | 101000 | 81000 | 89000 | 73000 | 80000 |  |  | Lighting increase in food prep and library not included
| $/ft2 | 1.3656 | 1.0952 | 1.2034 | 0.98703 | 1.0817 |  | 73959
Small Hotel | Total | 93620 | 81000 | 89000 | 99600 | 107000 |  |  | Lighting increase LPD in Hotel guest room not included
| $/ft2 | 2.167 | 1.8749 | 2.0601 | 2.3054 | 2.4767 |  | 43202
Mid-rise Apartment | Total | 104700 | 93000 | 110300 | 112400 | 111300 | [9 empty] | Weighted Partials | [6 empty] | Area weighted partials
| $/ft2 | 3.103 | 2.7563 | 3.269 | 3.3313 | 3.2987 |  | 33741 | [14 empty] | 2.5245 | 2.3335 | 2.592 | 2.6082 | 2.7884
Simple Payback, Years | [9 empty] | 2A | 3A | 3B | 4A | 5A | SUM | 2A | 3A | 3B | 4A | 5A |  | sf | 2A | 3A | 3B | 4A | 5A
Small Office |  | 6.2 | 6.4 | 6.4 | 9 | 9.2 | 7.4793 |  | OfficeSmall | 0.025336 | 0.023024 | 0.0090861 | 0.019059 | 0.022135 | 0.09864 | 172.2848 | 142.75 | 58.151 | 101.0138 | 117.3144 |  | 5502 | 0.031313 | 0.025945 | 0.010569 | 0.018359 | 0.021322 | OfficeSmall | 1.0899
Large Office |  | 10.8 | 7.6 | 7.2 | 8.3 | 8 | 8.4876 |  | OfficeLarge | 0.017992 | 0.017948 | 0.0084833 | 0.037221 | 0.015936 | 0.09758 | 8456.099 | 14358.64 | 7295.638 | 26798.976 | 11792.492 |  | 498588 | 0.01696 | 0.028799 | 0.014633 | 0.05375 | 0.023652 | OfficeLarge | 1.4121
Standalone Retail |  | 4.6 | 4.8 | 5 | 4.8 | 4.2 | 4.6154 |  | RetailStandalone | 0.059235 | 0.058756 | 0.028203 | 0.063391 | 0.078184 | 0.28777 | 5153.4798 | 4829.7103 | 2109.5994 | 5388.2605 | 7114.7804 |  | 24692 | 0.20871 | 0.1956 | 0.085437 | 0.21822 | 0.28814 | RetailStandalone | 3.4615
Primary School |  | 8.3 | 9.3 | 8.8 | 10.2 | 9.9 | 9.3259 |  | SchoolPrimary | 0.032252 | 0.031014 | 0.011845 | 0.029137 | 0.025519 | 0.12977 | 3257.4722 | 2512.1259 | 1054.1694 | 2126.9937 | 2041.512 |  | 73959 | 0.044044 | 0.033966 | 0.014253 | 0.028759 | 0.027603 | SchoolPrimary | 1.1453
Small Hotel |  | 7.4 | 7.9 | 7.4 | 7.6 | 7.2 | 7.5118 |  | HotelSmall | 0.010034 | 0.0088539 | 0.003509 | 0.010054 | 0.0090099 | 0.041461 | 939.3737 | 717.1659 | 312.301 | 1001.4083 | 964.0593 |  | 43202 | 0.021744 | 0.0166 | 0.0072289 | 0.02318 | 0.022315 | HotelSmall | 2.1965
Mid-rise Apartment |  | 5.2 | 5.7 | 4.6 | 4.6 | 4.8 | 4.9591 |  | ApartmentMidRise | 0.074155 | 0.058763 | 0.038875 | 0.099679 | 0.07331 | 0.34478 | 7764.0599 | 5464.9869 | 4287.9566 | 11203.8859 | 8159.3919 |  | 33741 | 0.23011 | 0.16197 | 0.12708 | 0.33206 | 0.24182 | ApartmentMidRise | 3.1702
Scalar Ratio (Limit 22.24) | [9 empty] | 0.219 | 0.19836 | 0.1 | 0.25854 | 0.22409 | [5 empty] | Total Code NPV across 5 CZ & 6 building types: | 145696.052 |  |  |  |  | Total Code NPV across 5 CZ & 6 building types: | 2.5741
Small Office |  | 5.1366 | 5.2989 | 5.2915 | 7.6796 | 8.5094 | 6.4369 |  | Scenario 3 | 22.24 | <= Scalar Limit |  |  | 1
Large Office |  | 12.1004 | 7.3743 | 6.8507 | 8.0788 | 7.8806 | 8.5516
Standalone Retail |  | 8.8773 | 4.8903 | -0.062172 | 4.8509 | 4.1385 | 5.0127
Primary School |  | 7.8722 | 10.1571 | 9.3362 | 10.2019 | 9.9004 | 9.4739
Small Hotel |  | 8.1359 | 8.6808 | 8.117 | 7.5132 | 7.1953 | 7.8953
Mid-rise Apartment |  | 1.966 | 2.096 | 0.66534 | -0.46666 | -0.015349 | 0.71693
|  | 6.1872 | 5.3274 | 2.6937 | 4.1806 | 4.2565 | 4.7158
First costs |  |  |  | HVAC |  |  |  |  | Lighting | [6 empty] | Envelope, Power, Other | [5 empty] | Total
|  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 2A | 3A | 3B | 4A | 5A | 2A | 3A | 3B | 4A | 5A |  |  | 0
Small Office |  | -1155.8408 | -1273.5984 | -1197.9729 | -1591.6563 | -1079.4222 | 0 | 0 | 0 | 0 | 0 |  |  | 4388 | 4388 | 4388 | 6148 | 6148 | 3232.1592 | 3114.4016 | 3190.0271 | 4556.3437 | 5068.5778 |  |  | 0
Large Office |  | 240685.0162 | -34202.2068 | -47978.4667 | -39447.227 | -43950.3141 | 0 | 0 | 0 | 0 | 0 |  |  | 600594 | 600594 | 600594 | 628852 | 628852 | 841279.0162 | 566391.7932 | 552615.5333 | 589404.773 | 584901.6859
Standalone Retail |  | -6331.8683 | -4584.6419 | -5460.3332 | -6947.6598 | -10404.3859 | 0 | 0 | 0 | 0 | 0 |  |  | 35588 | 35588 | 35588 | 38691 | 38691 | 29256.1317 | 31003.3581 | 30127.6668 | 31743.3402 | 28286.6141
Primary School |  | 3893.5877 | 5302.1261 | 195.8378 | -16126.592 | -14962.7068 | 0 | 0 | 0 | 0 | 0 |  |  | 94496 | 94496 | 94496 | 117289 | 117289 | 98389.5877 | 99798.1261 | 94691.8378 | 101162.408 | 102326.2932
Small Hotel |  | 2417.55 | 2841.8577 | 1889.9802 | -2100.9186 | -2054.1797 | 0 | 0 | 0 | 0 | 0 |  |  | 69719 | 66558 | 66558 | 70715 | 70715 | 72136.55 | 69399.8577 | 68447.9802 | 68614.0814 | 68660.8203
Mid-rise Apartment |  | -22665.6583 | -22980.2112 | -27079.7846 | -33365.0007 | -31978.5206 | 9858 | 9858 | 9858 | 9858 | 9858 |  |  | 45405 | 45405 | 45405 | 50460 | 50460 | 32597.3417 | 32282.7888 | 28183.2154 | 26952.9993 | 28339.4794
Annual Energy cost Savings (Table 5.3)
Prototype |  | Climate Zone
|  | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago
Life Cycle Cost Net Savings
Small Office | Total | 520.5291 | 486.4697 | 501.6614 | 507.6921 | 548.7799
| $/ft2 | 0.094642 | 0.088449 | 0.091211 | 0.092308 | 0.099778 |  | 5500
Large Office | Total | 77395.7524 | 74449.3372 | 76421.3726 | 70968.0494 | 72264.7012
| $/ft2 | 0.15521 | 0.1493 | 0.15326 | 0.14232 | 0.14492 |  | 498640
Standalone Retail | Total | 6329.9123 | 6356.2577 | 5898.4023 | 6499.2072 | 6545.6751
| $/ft2 | 0.25638 | 0.25744 | 0.2389 | 0.26323 | 0.26511 |  | 24690
Primary School | Total | 11387.3305 | 10322.3624 | 10367.2011 | 9498.7222 | 9938.2279
| $/ft2 | 0.15395 | 0.13955 | 0.14015 | 0.12841 | 0.13435 |  | 73970
Small Hotel | Total | 9441.2446 | 8560.9457 | 8996.9673 | 9081.0412 | 9508.9328
| $/ft2 | 0.2185 | 0.19812 | 0.20821 | 0.21016 | 0.22006 |  | 43210
Mid-rise Apartment | Total | 6314.7208 | 5643.5543 | 6147.1518 | 5844.0672 | 5915.8579
| $/ft2 | 0.18716 | 0.16727 | 0.18219 | 0.17321 | 0.17534 |  | 33740

## Changes_QC (hidden)
90.1-2010-16 CE starts below at row 91
90.1-2010-13 CE starts below at row 56
| 90.1 2007-10 CE |  |  | Adjustments October/November 2013
Issue | National Fix | State Fix | By | Tab affected | Columns affected | Notes/Change
| 41577 | 41597 |  | LCC/Scalar | fix hiRise apartment was referenced to small office
| 41577 | 41597 |  | LCC | 4A/sm_Ofc wrong index on/@ 30 year
| 41577 | NA |  | Scalar | Test "Yes" replaced with formula
| 41577 |  |  | HVAC Costs Comp | U:AS/131:156 | Update Duct M&L costs & put formula in for hours
| 41577 | OK |  | Int Ltg LPD Proto | AP/AS/BI/BL | Ballast labor referred to Lamp Labor
| 41577 | OK |  | Int Ltg LPD Proto | AP/AS/BI/BL | Row 2-3 each 2007 space no material cost due to references
| 41578 | 41597 |  | Ext Lighting Proto | Repeated replacements incorrect at 20,28 years
| 41578 | 41597 |  | Other Prototype tabs | Check for above - seems to be a general problem
| 41578 | 41597 |  | costeffInputs | ResValue30 | Added explanation that replacements with periods beyond analysis period represent residual value remaining from the first cost
| 41582 | 41597 |  | Int Lighting Comp | U | Lamp replacement labor hours consistent with replacement multiplier
| 41582 | OK |  | Chicago first cost mechanical delta |  | Not changed; correct based on heat recovery requirements
| 41582 | OK |  | CHW Flow costs double |  | Not changed; correct based on change in pipe sizing criteria - added pipe & insulation costs
| 41586 | 41597 |  | Int Lighting Comp |  | Normalized to standard hours, moving added labor to replacement cost adjustments
| 41586 | OK |  | Int Ltg LPD Proto | AV/BO | Formulas added for ballast cost adjustments
| 41586 | 41597 |  | Int Ltg LPD Proto | AV/BO | Formulas adjusted to include added labor hours in all replacement cost adjustments
| 41586 | OK |  | Int Ltg LPD Proto | AV/BO | Material cost adjustments for replacements corrected for 2010
| 41586 | 41597 |  | Int Lighting Comp |  | Costs standardized to labor rate and adjustments made to match 2007 and 2010 tables
| 41589 | 41597 |  | Int Light space type |  | Retail adjusted to use same fixture types, exlcude wall wash add in 2010 for better consistency
| 41589 | OK |  | Int Ltg LPD Proto | AO | Ballast life referred to Lamp Life
| 41597 | 41597 |  | Int Lighting Comp |  | Ballast cost added for 18" task light
| 41597 | 41597 |  | Int Ltg LPD Space Type Comp | R | Lamp Costs added
| NA | 41602 |  | LCC |  | Envelope references still from state for CZ
| see LPD below | 41598 |  | LPD |  | For closed offices made consistent 2-lamp fixtures pre and post since no real change in LPD
| 41602 | 41598 |  | Light Comp |  | Reducing ballast hours so 1.65 replacement multiplier brings it back to 1, as ballast labor must be for replacement.
| NA | 41598 |  | Weightings |  | 0 lg ofice in MT and 0 apartments in DE indicate weights were not blended; placeholder at 0.001% to avoid % zero; revised text
| 41599 | NA |  | Envelope & power | $4K | Small office in Baltimore - Vestibule cost in small office, CZ 4A only
| 41599 | NA |  | Envelope & power | 232 | Elevator
|  | 41600 |  | Occ Sensor Proto |  | Cost included not used column; formula fixed
| NA | 41600 |  | Env Pow Other Comp Costs |  | Copy Green items column A in from Jian so gets flagged for first cost and replacement
| NA | 41600 |  | State Inputs |  | Texas 3A 3B zones swapped; checked others
| NA | 41600 |  | Env Pow Other Comp Costs |  | Jian checked multiple items to verify Brian had finished
| NA | 41600 |  | Env Pow Other Comp Costs |  | Error in reference for first cost/maint sm cz_5th instead revered to CZ_1st column; fixed all prototypes
| NA | 41601 |  | HVAC Data |  | IECC paste needs replacing with 90.1 - only Alabama small Hotel
| NA | 41601 |  | HVAC Comp/LO proto |  | Chilled Water piping cost curve fit
| NA | 41601 |  | HVAC Comp/LO proto |  | Heating Water piping cost curve fits added for large office and schools - Reheat data added to HVAC_Data
| NA | 41601 |  | HVAC Comp/PS proto |  | Heating Water piping cost curve fits added for large office and schools
| No longer issue-See LPD | 41601 |  | State Report/Result Tables |  | for many states small office (lesser mid-Apartments) are not cost effective - so added variable language
| OK | 41601 |  | Env Pow Other Comp Costs |  | Receptacle control still based on plug strips; convert to relays to match national
| 41601 | 41601 |  | Env Pow Other Comp Costs |  | Air barrier sealing had adders even though it is based on a quoted commissioning cost; moved to Cx
| 41601 | 41601 |  | HVAC Proto |  | Ductwork life corrected from 20 to 30 years, all prototypes
| NA | NA |  | HVAC SmOfc Proto |  | Greater mechanical reduction National as loads different, and National rounded to nearest half ton.
| OK | 41602 |  | Int Lighting Proto |  | Repeated replacements incorrect at 20,28 years - missed 2007 columns
| NA | OK |  | LCC Sc1 |  | Mid apt replacements not match on cost est summary and LCC 1; intentional - costs on Cost Est Summary used - warning added to LCC sheets
| 41602 | 41602 |  | Cost Est Summary |  | Vestibule replacement life was missing -so vestibule residual is missed; set at 40 years; on Nat sheet 30 year analysis not set up with residual for 4A - fixed
| 41602 | NA |  | PriSch Light |  | School not CE - receptacle labor OK increase; check light - lamp costs included now - change legit
| No longer issue-See LPD | OK |  | HVAC Proto |  | School not CE - National HVAC much greater than state - State method would show ductwork cost decrease
| OK | NA |  | HVAC Proto |  | School not CE - National HVAC much greater than state - ERV enhancemeent not active in National analysis
| see LPD below | OK |  | Apt Light |  | Nat: Mid-rise apartment; general cost increase; now some not CE; biggest increase in lighting; due to lamps included in first cost
| 41610 | 41602 |  | IntLtg Space/Proto |  | Look at changes in lighting where 2010 has ballast/fixture increase or 90.1 LSC design results in imbalanced costs relative to LPD change
| ?? | Hold for RFI |  | Cost Eff Inputs |  | Combined tax rate does not account for state tax deduction from federal taxes
| 90.1-2010-13 CE starts below at row 56 |  |  |  | Adjustments August/September 2014
A few unnoted changes/updates - would need to do a file compare as of 8/15
| 41876 |  |  | Int Lighting Comp | U&Y | Fixed some transfers not made by Ivy rows 47-52
| 41876 |  |  | Int Ltg Lpd Space . . . | N111:AJ121 | Values in col "o" typed in rather than copied, loss of precision
| 41877 |  |  | Int Ltg Lpd Space . . . | O146:147 | Value mismatch; updated to match Susal L values for 2013
| 41877 |  |  | Int Ltg Lpd Space . . . | see check | Reviewed cost changes with no LPD changes - revert to 2013 for both
| 41877 |  |  | Int Ltg LPD Proto . . . | see check | unused LPD space/fixture ref removed from LPD proto to get rid of #NA
| 41878 |  |  | Int Ltg LPD Proto . . . |  | discrepency in SF
| 41878 |  |  | Int Ltg LPD Proto . . . |  | Ballast replacement references are wrong-same as fixture costs; not sure where this was introduced, as the formulas were correct in the 2010 national and state spreadsheets.
| 41878 |  |  | LPD |  | Multiple lighting discrepencies fixed - final cross check requested
| Rahul |  |  |  |  | Foundation costs off
| 41884 |  |  |  |  | Appears not to be CE for many cases
| 41884 |  |  |  |  | Verified hidden sheets not in total
| 41884 |  |  |  |  | Added Scenario 3: Scalar | Roof deck insulation comparison
| 41884 |  |  | HVAC comp |  | Fixed CHW/CW piping | R | U |  | M | L
| 41886 |  |  | Daylighting |  | No formula for baseyear costs; added | 25.641 | 0.039 | 8" concrete slab, normal weight, XPSinsulation | 20.3286 | 9.1548 | 3BLORoof - Insulation Entirely Above Deck2013
| 41886 |  |  | Int Ltg LPD Proto . . . |  | Areas with increased LPD not included in cost effectiveness | 31.25 | 0.032 | 8" concrete slab, normal weight, XPSinsulation | 21.2505 | 9.2211 | 4ALORoof - Insulation Entirely Above Deck2013
| 41886 |  |  |  |  | Verified no new daylighting for large retail | 5.609 |  |  | 0.9219 | 0.066241
| 41886 |  |  | HVAC LG OFC | Duct airflow | Problems with inconsistent regresson formulas and 0 canceling out | Polyiso | 2" |  | 0.78 | 0.27 | Means 2012 Bldg 07 22 16.10
| 41886 |  |  | ENV_Comp |  | Inflation factors added | R-5 per | 3" |  | 1.23 | 0.3 | Means 2012
[5 empty] | To do items: | AQ: economizer | 3/4" | delta 1" |  | 0.45 | 0.03 | Means values are about half of the database!
[5 empty] | All done | Split/Furnace inflation labor & material
[6 empty] | VFDs by proto | XPS | 3" |  | 1.28 | 0.3 | Means 2012 Bldg 07 22 16.10
[6 empty] | Energy recovery | R-5 per | 4" |  | 1.7 | 0.3 | Means 2012
[6 empty] | cooling towers | inch | delta 1" |  | 0.42 | 0 | Means values are about half of the database!
[6 empty] | chiller eff | 40 psi
motor eff
several mechanical items in characterization
| 41918 |  |  | Inflation adjustments made to replacement costs
| 42096 |  |  | For the national level (90.1-2013) we left the refrigeration costs out. Primary School.
| 42117 |  |  | Export 3 macro has been updated; export 2 & sheet for 1 need new row deletions
Changes to 90.1-2016 Cost effectiveness:
Issue | National Fix | State Fix | By | Tab affected | Columns/area affected | Notes/Change
| 43307 |  | MM | State Inputs |  | Changed BaseName (cell T2) to 90.1-2013
| 43307 |  | MM | State Inputs |  | Changed TargetName (cell T3) to 90.1-2016
| 43307 |  | MM | State Inputs |  | These cells feed into named formulas BaseName and TargetName.
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | Inserted more rows for fixtures
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | Inserted new fixture list
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | Retained the LAST SET of fixture types, but changed those fixture types to ###-2013. This retains all of the OLD data as a reference point, but the formulas do not pull it.
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | Because of the other changes I made in State Inputs, it now says “90.1-2013 Look up Values” at the top
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | I copied the Fixture Watts/ft2 from 2013 below and compared and updated the set
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | Basically, as of now, both the top and bottom versions of this spreadsheet are identical values at this time
| 43307 |  | MM | Int Ltg LPD Space Type 90_1 All Tab |  | I also inserted a check into Int Ltg LPD column E to make sure individual LPD values sum to the space type LPD
| 43348 |  | PRH | HVAC Large Office Proto | K92 | Fixed missing material & project multiplier portions of HW formula for Base in first CA
| 43361 |  | PRH | Cost_Inflation |  | Updated to 2012-2018 & fixed text
| 43361 |  | PRH | Lighting tabs |  | Fixed lead lighting formulas to ref base/target 2013/2016
| 43361 |  | PRH | Lighting Occ Sensor tabs |  | Zeroed and Hid the Occ sensor tabs
| 43361 |  | PRH | Env Power tabs |  | Verified Envelope currently zeroed out - need to add doors & SHGC
| 43362 |  | PRH | Daylighting tabs |  | Zeroed and Hid the Daylighting tabs
| 43394 |  | PRH | Daylighting tabs |  | Added egress control
| 43394 |  | PRH | H Apt Proto |  | Fixed PTHP quantity control
| 43394 |  | PRH | H Comp |  | Removed old efficiency improvements; fixed some labor hours
| 43394 |  | PRH | Inflation |  | Updated inflation factors
| 43394 |  | PRH | LO_Proto |  | Fixed multipliers for MID
| 43395 |  | PRH | Crews |  | Crew labor data updated to 2018
| 43397 |  | PRH | Lite Comp |  | Added lumen data
| 43397 |  | PRH | HVAC data |  | Updated with 10/20 E+ outputs including radiant adjustment
| 43397 |  | PRH | Energy Data |  | Updated with 10/20 E+ outputs including radiant adjustment
| 43402 |  | PRH | Int Lite |  | Add Dwelling Unit
| 43402 |  | PRH | Lite Proto |  | Corrected all replacements that previously used SmOfc hours for all Proto
| 43486 |  | MT | HVAC Large Office Proto | Y24, AI24, BC24 | In climates 3A, 3B, 5A the equation for total new construction cost includes this term …*inf_mat_DUCT*0+… and the *0 should not be there, thus removed the errant 0
National analysis for 90.1-2019 begins:
| 43852 |  | PRH | Cost Eff Inputs | various | US National Factors for 2019 input
| 43852 |  | PRH | State Inputs | various | US National Prices for 2019 input
| 43927 |  | PRH | State Inputs |  | Col B/C need to be correct code 2016/2019 for US
| 43927 |  | PRH | Int Ltg LPD summary |  | If base/target code above are corrected, none of lighting changes get read correctly; need to rectify all conditional formulas on lighting summary sheet; or need to deal with cosmetics throughout whever headings are incorrect. MM is updating formulas in the main cost spreadsheet.
43928 | 43931 |  | PRH | HVAC Costs Comp |  | HVAC Costs comp; VAV vent optimization should be "oranged" out - old addenda; row 258
43928 | 43931 |  | PRH | HVAC Costs Comp |  | Many old addenda not marked for hiding
43928 | 43931 |  | PRH | HVAC Costs Comp |  | Better description addm g in spreadsheet row 344
43928 | 43931 |  | PRH | HVAC Costs Comp | 16 h & ay Res ERV | Costs look like per apartment not central system, and are not multiplied by # of apartments
43928 | 43931 |  | PRH | HVAC Large Office | 16ap SAT | CZ 2A is required above 10k cfm and qualifies. ; also correct on HVAC COSTS COMP
43928 | 43931 |  | PRH | HVAC Large Office | System sizing | Rows 14/15 @ col k:R, etc showing "out of range"; Need to divide by floor multiplier for lookup and then multiply back
43928 | 43931 |  | PRH | HVAC Costs Comp | 16be | Better to show separate prices for 20 ton units and 2.5 ton units, then multiply by quantities in Large Office
43928 | 43931 |  | PRH | HVAC Costs Comp | 16bq | Identify addendum in visible part of spreadsheet
43928 | 43931 |  | PRH | HVAC Costs Comp | 16bo | Identify addendum in visible part of spreadsheet
43928 | 43931 |  | PRH | HVAC Costs Comp | 16bo | Apt mat cost much too low; labor cost for large vs. apt should be different
43935 | 43935 |  | PRH | HVAC Costs Comp | rows 376-377 | There are different chiller material costs in AP & Bk, even though this is supposed to be just a capture of capacity change. Not sure how the logic carries through to prototype sheets. Not clear how inflation factors are applied in
43935 | 43935 |  | PRH | HVAC Costs Comp | rows 439-455 | There are different hydronic piping costs in AI & BC, even though this is supposed to be just a capture of capacity change. So, these two sets of values go back to 2007 & 2010, I think - so may just need a note here to clarify that those x values in W and AC are not current values, just prior calculated values to develop the regressions.
43935 | 43935 |  | PRH | HVAC Large Office proto | Row 98 | Not seeing where inflation factor gets applied; it is on costComp, but unless you ran new regressions, it is not factoring in what gets used on the prototype tab. Need inflation to carry forward there.
43935 | 43935 |  | PRH | HVAC Pri School proto |  | Same as large office for schools
National analysis for 90.1-2022 begins:
| 44994 |  | MT | State Inputs | various | US National Prices for 2022 input
|  |  | MT | State Inputs |  | Col B/C need to be correct code 2019/2022 for US